## Staff 3-3 Attachment 1
Unit Name | Event Type | Start Date | End Date | Description
Big Sandy 1 | PO | 2021-10-08 22:00 | 2021-12-21 07:47 | General Boiler Inspection & Repair, Turbine Exhaust High Energy Piping (HEP) inspections, Boiler corrosion fatigue inspections, Main and Auxiliary Condenser eddy current testing, and Cooling Tower repairs.
Big Sandy 1 | FO | 2022-01-19 03:11 | 2022-01-19 22:01 | Deaerator level control valve Regulating Valve RV-101 stuck in the open position. Valve positioner replaced and unit returned to service.
Big Sandy 1 | MO | 2022-02-10 00:25 | 2022-02-18 15:00 | Boiler Inspection/Repair, Vibration Probe Inspection/Repair, Regulating Valve RV-101 (Hotwell level control) repair, Regulating Valve RV-5 (Start-up Steam Attemperator Valve) Inspection/Repair, Nash Vacuum Pump Inspection/Repair, #5 High Pressure Heater Feedwater Header leak repair.
Big Sandy 1 | MO | 2022-02-22 00:58 | 2022-02-27 11:55 | Requesting a Maintenance Outage until 2-27-2022 @1600 for Boiler inspection, Drum door repairs, Boiler Feed Pump Turbine Y vibration probe repair, Clean cooling tower screens, Nash pump level float repair, Circulating water vent replacement.
Big Sandy 1 | MO | 2022-03-17 | 2022-03-27 12:00 | Boiler Inspection/Repair, State Drum inspection, Boiler Feed Pump Turbine 2Y vibration probe repair, Boiler Feed Pump Turbine Gasket replacement on Duplex Strainer, Boiler Penthouse inspection
Big Sandy 1 | MO | 2022-03-30 01:27 | 2022-04-05 06:56 | Boiler inspection
Big Sandy 1 | FO | 2022-04-06 04:42 | 2022-04-08 16:00 | condenser leak.
Big Sandy 1 | MO | 2022-04-08 16:00 | 2022-04-14 13:40 | Drum door repairs
Big Sandy 1 | MO | 2022-05-24 07:00 | 2022-05-28 16:00 | Boiler Inspection/Repair; Deaerator Positive Closing Check Valve repairs; Inspect 2Y vibration pickup on Boiler Feed Pump Turbine; Repair Drip Pot drain line to Boiler Feed Pump Turbine; Replace Seal on South Positive closing check valve; Inspect Auxiliary Condenser Water Boxes.
Big Sandy 1 | MO | 2022-06-02 07:00 | 2022-06-05 16:00 | Boiler Inspection/Repair, Boiler Feed Pump Turbine 2Y Vibration Probe Inspection/Repair, Regulating Valve RV-101 Inspection/Repair, 5N High Pressure Heater leak repair, Turbine Valve Trip Logic Inspection/Repair, Stroke Regulating Valve RV-910, Re-pack East Circulating Water Pump, North Heater Drain Pump coupling alignment check.
Big Sandy 1 | MO | 2022-07-03 07:00 | 2022-07-09 14:00 | Boiler Inspection/Repair, #2 Governor Valve - replace Servo, Lower Right Reheat Stop/Intercept Valve Linear Variable Differential Transducer replacement, 5N Heater leak repair, West Air Compressor Oil Cooler - clean and replace Oil Pump, Auxiliary Condenser Tube Sheet cleaning.
Big Sandy 1 | MO | 2022-07-26 07:00 | 2022-07-30 16:00 | to troubleshoot and repair Governor Valve #1 and #2, Regulating Valve RV-101; Boiler Inspection/Repair; West Condensate Booster Pump Mechanical Seal Repair; Measure Electrohydraulic Control Hoses for fall outage repair; Turbine Room Crane repair
Big Sandy 1 | MO | 2022-08-15 | 2022-08-17 08:00 | Boiler Inspection/Repair, North Gland Seal leak Off Exhauster Inspection/Repair, Regulating Valve RV-1003 (Low Pressure Steam Seal Regulator) positioner replacement.
Big Sandy 1 | MO | 2022-08-27 | 2022-09-03 08:21 | Remove 600V Feed (both A and B Bus) for measurements and to complete last stage blade inspection of the Boiler Feedpump Turbine and Main Turbine Double Flow Low Pressure Turbine Section.
Big Sandy 1 | MO | 2022-09-08 | 2022-09-10 | Pre-Planned Outage preparation.
Big Sandy 1 | PO | 2022-09-10 | 2023-01-14 11:47 | Boiler Inspection/Repair, Generator Field Out inspection/possible rewedge, Turbine Valve Inspection/Repair, Corrosion Fatigue Inspection/Repair, Cooling Tower Inspection/Repair, ReHeat Attemperator Inspection/Repair, Gas valve Inspection/Repair, Forced Draft Fan and Motor Inspection/Repair, High Energy Piping (HEP) Inspection/Repair, Flow Accelerated Corrosion (FAC) Inspection/Repair, Core Loop testing.
Big Sandy 1 | PO | 2023-01-14 11:47 | 2023-01-16 | Boiler Inspection/Repair, Generator Field Out inspection/possible rewedge, Turbine Valve Inspection/Repair, Corrosion Fatigue Inspection/Repair, Cooling Tower Inspection/Repair, ReHeat Attemperator Inspection/Repair, Gas valve Inspection/Repair, Forced Draft Fan and Motor Inspection/Repair, High Energy Piping (HEP) Inspection/Repair, Flow Accelerated Corrosion (FAC) Inspection/Repair, Core Loop testing.
Big Sandy 1 | FO | 2023-01-29 07:21 | 2023-01-29 16:08 | West Air Heater Upper Guide Bearing elevated vibration.
Big Sandy 1 | MO | 2023-02-09 00:35 | 2023-02-09 14:17 | Request MO for Intrument Control Technician to troubleshoot/repair issue with Boiler Feed Pump Turbine Governor Valve controls
Mitchell 1 | PO | 2021-10-16 | 2021-12-12 13:31 | Boiler Inspection/Repair, Balance of Plant repairs, Selective Catalytic Reduction Catalyst #4 layer replacement, Boiler Feed Pump Element replacement.
Mitchell 1 | MO | 2021-12-19 07:00 | 2021-12-23 08:32 | to dewater cooling tower and install 11B Circulating Water Pump
Mitchell 1 | FO | 2022-03-24 13:00 | 2022-03-27 03:41 | Auxiliary Boiler Out of Service
Mitchell 1 | FO | 2022-03-27 11:00 | 2022-03-29 16:30 | #16 Pulverizer Primary Air Ductwork failed.
Mitchell 1 | FO | 2022-04-05 13:30 | 2022-04-05 15:24 | Unit failed to start, original // time 0930
Mitchell 1 | FO | 2022-04-13 17:24 | 2022-04-14 14:25 | Extreme low deaerator alarm
Mitchell 1 | MO | 2022-04-14 14:26 | 2022-04-19 23:00 | Deaerator Level control valve Inspection/Repair; Boiler casing air test; Boiler Inspection/Repair; Repair Electrohydraulic Control leak on Reheat stop valve; Main Turbine 1st Reheat and High Pressure Exhaust Steam Leads.
Mitchell 1 | FO | 2022-06-27 03:07 | 2022-07-05 02:00 | Economizer tube leak
Mitchell 1 | FO | 2022-07-05 02:00 | 2022-07-05 03:06 | Exciter field breaker breaker is tripping the turbine when attempting to parallel.
Mitchell 1 | FO | 2022-07-05 05:34 | 2022-07-06 04:00 | Possible leak in High Pressure steam line
Mitchell 1 | FO | 2022-07-06 04:00 | 2022-07-06 14:17 | Condensate booster pump and control valve issues
Mitchell 1 | MO | 2022-09-24 | 2022-10-08 | Repair feed pump turbine steam supply regulating valve.
Mitchell 1 | PO | 2022-10-08 | 2022-11-19 17:32 | Boiler Inspection/Repair, Precip Inspection/Repair, Pulverizer/Feeder Mercury & Air Toxics Standards Inspection/Repair, Economizer wash, Replace Precip Transformer power cables, Replace Selective Catalytic Reduction Expansion Joint s 14,15 and 115, Replace Exit Duct Expansion Joint FGX-71009, Water Cannon upgrades, Ovation Evergreen upgrade, Inter-lock testing, High Energy Piping Inspection/Repair.
Mitchell 1 | FO | 2022-11-29 11:45 | 2022-11-29 18:03 | Unable to get firing permissives.
Mitchell 1 | MO | 2022-12-03 01:47 | 2022-12-08 09:18 | Economizer tube leak repair
Mitchell 1 | FO | 2022-12-08 11:45 | 2022-12-09 | PH Issues
Mitchell 1 | FO | 2022-12-09 | 2022-12-10 08:01 | Due to Urea from Hydrolyzer system entering the Condensate Return System. Samples will be collected and tested once the unit cools. Hydrolyzer will need pressurized to search for potential leaks.
Mitchell 1 | FO | 2022-12-10 13:07 | 2022-12-13 16:30 | Due to Primary Superheater Outlet valve . packing blew out. Superheater Bypass Control valve URV-4, controller failed closed due to burned up controller.
Mitchell 1 | FO | 2022-12-14 02:45 | 2022-12-14 19:15 | Start Failure- due to the 1-2 circ water booster pump and RMO-8 causing Ops to Trip the Boiler Feed Pump
Mitchell 1 | MO | 2022-12-30 | 2023-01-22 17:59 | Boiler Inspection/Repair, Boiler Hydro, Duct repairs, Clinker Removal, IK Soot Blower Repairs, 12 Induced Draft Fan Stall margin probe Inspection/Repair.
Mitchell 1 | FO | 2023-01-24 12:09 | 2023-02-03 16:27 | UMO-1 Primary Superheater Outlet Valve packing failed.
Mitchell 1 | MO | 2023-03-16 01:28 | 2023-03-16 14:53 | Main Steam Lead greylock drain line leak
Mitchell 1 | MO | 2023-03-16 14:53 | 2023-03-21 23:17 | Main Steam Line Above Seat Drain steam leak
Mitchell 2 | FO | 2021-11-30 11:30 | 2021-12-02 05:38 | Valve issue. Packing blew out on FRV-101(Main Steam Attemperator)
Mitchell 2 | FO | 2021-12-04 08:00 | 2021-12-05 10:19 | UMO-1 packing leak (super heater bypass line)
Mitchell 2 | FO | 2021-12-22 00:18 | 2021-12-22 16:18 | #1 Control valve Linear Variable Differential Transducer positioner arm broke causing #1 control valve to close and become inoperable.
Mitchell 2 | MO | 2022-02-20 19:45 | 2022-03-26 05:00 | Boiler Inspection/Repair, Hydro test, Precipitator Inspection/Repair, Roof Outlet Header Safety Valve (SV)-54 replacement, Deaerator leak repair, Drain Flue Gas Desulfurization Absorber to replace 2H Agitator Seal, Flue Gas Desulfurization Absorber Inlet Duct repairs, repair Reheat Attemperator Block Valves FMO-201 and 202 (Water Induction Protection Valves).
Mitchell 2 | FO | 2022-04-15 16:03 | 2022-04-16 05:07 | During Pressurization, Super heater bypass valves failed to respond causing the unit to trip on sub critical pressure.
Mitchell 2 | FO | 2022-05-22 06:06 | 2022-05-23 11:19 | Unit Forced Out Steam leak on drain line to drip tank.
Mitchell 2 | MO | 2022-06-08 | 2022-06-13 02:00 | Boiler inspection
Mitchell 2 | MO | 2022-06-25 | 2022-07-02 14:34 | Repair leaks
Mitchell 2 | FO | 2022-07-11 15:00 | 2022-07-11 22:47 | Induced Draft fan - Improper valve lineup for oil cooler.
Mitchell 2 | MO | 2022-07-16 03:33 | 2022-07-24 00:31 | #21 Induced Draft Fan Thrust Bearing and Radial Bearing
Mitchell 2 | MO | 2022-09-03 | 2022-09-10 | Pre Planned Outage prep work.
Mitchell 2 | PO | 2022-09-10 | 2022-12-16 14:25 | Boiler Inspection/Repair, Cooling Tower Inspection/Repair, Low Pressure Turbine A"&"B" Valve replacement
Mitchell 2 | PO | 2022-12-16 14:52 | 2022-12-16 15:28 | Boiler Inspection/Repair, Cooling Tower Inspection/Repair, Low Pressure Turbine A"&"B" Valve replacement
Mitchell 2 | FO | 2022-12-17 14:12 | 2022-12-20 16:08 | A Bus Relay Primary Air Fan
Mitchell 2 | MO | 2023-01-07 | 2023-01-29 19:04 | Precipitator Inspection/Repair, Balance Shot on Low Pressure turbines., Boiler Inspection/Repair, Duct Repairs.
Mitchell 2 | FO | 2023-03-23 09:10 | 2023-04-04 14:00 | Feedwater Pump Thrust Bearing Failure