## Data
Upgrade Id | Parent PJM ID | Name of Project | Sub Region | Description | Project Type | Voltage | Cost Estimate | Required Date | Transmission Owner | Proposal IDs | Units | Related Upgrades | Cost Allocation Percent | State | Location | Equipment | Task | Status | Status Title | Status Detail | TEAC Cost | Reason/Issues Addressed | Projected File By Date | Projected Construction Start Date | Projected In Service Date | Actual In Service Date | Immediate Need | Schedule12Methodology | Initial TEAC Date | Latest TEAC Date | Applicable Rating | Revised Description | Percent Complete | ISA In-Service Date | Revised In-Service Date | Comments | Last Updated | TEAC Materials
b3281 | b3281 | Dewey Station Upgrades (Baseline) | West | Install 138 kV circuit switcher on the 138/69 kV transformer #1 and 138/34.5 kV transformer #2 at Dewey. Install 138 kV 2000 A 40 kA breaker on Stanville line at Dewey 138 kV substation. | Baseline | 138 | 1.4 | 12/1/2025 | AEP |  |  |  | AEP: 100.00 | KY | Dewey | Circuit Switcher | Install | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 1.4 | TO Criteria Violation | 2024-08-03 | 2024-12-01 | 12/1/2025 |  | No |  | 2/17/2021 |  | 40 kA |  | 0 | 12/1/2025 |  |  | 6/29/2023 | https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2021/20210217/20210217-reliability-analysis-update.ashx
b3283 | b3283 | Inez Station Improvement | West | Replace the existing Inez 138/69 kV 50 MVA autotransformer with a 138/69 kV 90 MVA autotransformer. | Baseline | 138/69 | 2.96 | 12/1/2025 | AEP |  |  |  | AEP: 100.00 | KY | Inez | Transformer | Replace | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 2.96 | TO Criteria Violation | 2024-08-03 | 2024-12-01 | 12/1/2025 |  | No |  | 2/17/2021 |  | 05INEZ 138/69/13KV SN/SE/WN/WE (MVA): 136.6/138.3/154.4/160.9 |  | 0 | 12/1/2025 |  |  | 6/29/2023 | https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2021/20210217/20210217-reliability-analysis-update.ashx
b3288.1 | b3288 | Belfry Project (Baseline) | West | Construct ~ 2.75 mi Orinoco - Stone 69 kV transmission line in the clear between Orinoco station and Stone station. | Baseline | 69 | 9.23 | 12/1/2025 | AEP |  |  |  | AEP: 100.00 | KY | Orinoco - Stone | Transmission Line | Build | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 9.23 | TO Criteria Violation | 2024-08-03 | 2024-12-01 | 12/1/2025 |  | No |  | 1/15/2021 |  | 05ORINOCO – 05STONE 69KV: 102/142/129/160 & 05ORINOCO – 05NEWCAMP 69KV: 102/142/129/150 (SN/SE/WN/WE (MVA)) |  | 0 | 12/1/2025 |  |  | 6/29/2023 | https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2021/20210115/20210115-item-06-reliability-analysis-update.ashx, https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2021/20210115/20210115-reliability-analysis-update.ashx
b3288.2 | b3288 | Belfry Project (Baseline) | West | Construct ~ 3.25 mi Orinoco – New Camp 69 kV transmission line in the clear between Orinoco station and New Camp station. | Baseline | 69 | 9.95 | 12/1/2025 | AEP |  |  |  | AEP: 100.00 | KY | Orinoco – New Camp | Transmission Line | Build | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 9.95 | TO Criteria Violation | 2024-08-03 | 2024-12-01 | 12/1/2025 |  | No |  | 1/15/2021 |  | 05ORINOCO – 05STONE 69KV: 102/142/129/160 & 05ORINOCO – 05NEWCAMP 69KV: 102/142/129/150 (SN/SE/WN/WE (MVA)) |  | 0 | 12/1/2025 |  |  | 6/29/2023 | https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2021/20210115/20210115-item-06-reliability-analysis-update.ashx, https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2021/20210115/20210115-reliability-analysis-update.ashx
b3288.3 | b3288 | Belfry Project (Baseline) | West | At Stone substation, circuit breaker A to remain in place and be utilized as T1 low side breaker, circuit breaker B to remain in place and be utilized as new Hatfield (via Orinoco and New Camp) 69 kV line breaker. Add new 69 kV circuit breaker E for Coleman Line exit. | Baseline | 69 | 0.66 | 12/1/2025 | AEP |  |  |  | AEP: 100.00 | KY | Stone | Circuit Breaker | Install | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 0.66 | TO Criteria Violation | 2024-08-03 | 2024-12-01 | 12/1/2025 |  | No |  | 1/15/2021 |  | 05ORINOCO – 05STONE 69KV: 102/142/129/160 & 05ORINOCO – 05NEWCAMP 69KV: 102/142/129/150 (SN/SE/WN/WE (MVA)) |  | 0 | 12/1/2025 |  |  | 6/29/2023 | https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2021/20210115/20210115-item-06-reliability-analysis-update.ashx, https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2021/20210115/20210115-reliability-analysis-update.ashx
b3288.4 | b3288 | Belfry Project (Baseline) | West | Reconfigure the New Camp 69 kV tap which includes access road improvements/installation, temporary wire and permanent wire work along with dead end structures installation. | Baseline | 69 | 0.45 | 12/1/2025 | AEP |  |  |  | AEP: 100.00 | KY | New Camp | Substation | Modify | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 0.45 | TO Criteria Violation | 2024-08-03 | 2024-12-01 | 12/1/2025 |  | No |  | 1/15/2021 |  | 05ORINOCO – 05STONE 69KV: 102/142/129/160 & 05ORINOCO – 05NEWCAMP 69KV: 102/142/129/150 (SN/SE/WN/WE (MVA)) |  | 0 | 12/1/2025 |  |  | 6/29/2023 | https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2021/20210115/20210115-item-06-reliability-analysis-update.ashx, https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2021/20210115/20210115-reliability-analysis-update.ashx
b3288.5 | b3288 | Belfry Project (Baseline) | West | At New Camp substation, rebuild the 69 kV bus, add 69 kV MOAB W and replace the 69 kV ground switch Z1 with a 69 kV circuit switcher on the New Camp transformer. | Baseline | 69 | 1.18 | 12/1/2025 | AEP |  |  |  | AEP: 100.00 | KY | New Camp | Substation | Modify | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 1.18 | TO Criteria Violation | 2024-08-03 | 2024-12-01 | 12/1/2025 |  | No |  | 1/15/2021 |  | 05ORINOCO – 05STONE 69KV: 102/142/129/160 & 05ORINOCO – 05NEWCAMP 69KV: 102/142/129/150 (SN/SE/WN/WE (MVA)) |  | 0 | 12/1/2025 |  |  | 6/29/2023 | https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2021/20210115/20210115-item-06-reliability-analysis-update.ashx, https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2021/20210115/20210115-reliability-analysis-update.ashx
b3307 | b3307 | Fleming Station Rebuild | West | Rebuild Fleming station in the clear; Replace 138/69kV Fleming Transformer #1 with 138/69 kV 130 MVA transformer with high side 138 kV CB; Install a 5 breaker 69 kV ring bus on the low side of the transformer, replace 69 kV circuit switcher AA, replace 69/12kV transformer #3 with 69/12 kV 30 MVA transformer, replace 12 kV CB A and D. Retire existing Fleming substation. | Baseline | 138/69 | 21.1 | 12/1/2025 | AEP |  |  |  | AEP: 100.00 | KY | Fleming subtation | Substation | Rebuild | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 21.1 | TO Criteria Violation | 2024-08-03 | 2024-12-01 | 12/1/2025 |  | No |  | 1/15/2021 |  | 05JACKHORN 138/69 kV: 130/130/130/130 & 05JACKHORN – 05BEEFHI 138 kV: 221/278/279/322 & 05JACKHORN – 05JENKINS 69 kV: 87/101/110/120 (SN/SE/WN/WE (MVA)) |  | 0 | 12/1/2025 |  |  | 6/29/2023 | https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2021/20210115/20210115-item-06-reliability-analysis-update.ashx, https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2021/20210115/20210115-reliability-analysis-update.ashx
b3349 | b3349 | Bellefonte Station Upgrades (Baseline) | West | Replace Bellefonte 69 kV risers on the section between Bellefonte TR #3 and 69 kV Bus #2. | Baseline | 69 | 0.54 | 6/1/2026 | AEP |  |  |  | AEP: 100.00 | KY | Bellefonte | Relay | Replace | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 0.54 | TO Criteria Violation | 2025-02-01 | 2025-06-01 | 6/1/2026 |  | No |  | 11/19/2021 |  | From Bus #243676, To Bus # 244660, (SN/SE/WN/WE: 179/210/227/250) |  | 0 | 6/1/2026 |  |  | 10/17/2022 | https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2021/20211119/20211119-reliability-analysis-update.ashx
b3352 | b3352 | 47th Street Upgrades | West | Replace MOAB W, MOAB Y, line and bus side jumpers of both W and Y at 47th Street 69 kV station. Upgrade the 69 kV strain bus between MOABs W and Y to 795 KCM AAC. Change the connectors on the tap to MOAB X1 to accommodate the larger 795 KCM AAC. | Baseline | 69 | 0 | 6/1/2026 | AEP |  |  |  | AEP: 100.00 | KY | 47th 69kV station | Disconnect Switch | Replace | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 0 | TO Criteria Violation | 2024-08-03 | 2024-12-01 | 12/1/2025 |  | No |  | 11/19/2021 |  | From Bus #244685, To Bus # 244720, (SN/SE/WN/WE: 102/102/129/129) |  | 0 | 6/1/2026 |  |  | 10/17/2022 | https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2021/20211119/20211119-reliability-analysis-update.ashx
b3353.1 | b3353 | Allen Station Improvement | West | Allen substation: Rebuild Allen station to the northwest of its current footprint utilizing a standard air-insulated substation with equipment raised by 7’ concrete platforms and control house raised by a 10’ platform to mitigate flooding concerns. Install five 69 kV 3000A 40 kA circuit breakers in a ring bus (operated at 46 kV) configuration with a 13.2 MVAR capacitor bank. Existing Allen station will be retired (does not include the distribution cost). Distribution scope of work: Install 69/46 kV-12 kV 20 MVA transformer along with 2-12 kV breakers on 7’ concrete platforms (conversion of S2405.1). | Baseline | 46 | 10.55 | 12/1/2026 | AEP |  |  |  | AEP: 100.00 | KY | Allen | Substation | Rebuild | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 10.55 | TO Criteria Violation | 2023-07-19 | 2023-11-16 | 11/15/2024 |  | No |  | 11/19/2021 |  | From Bus #243753, To Bus # 244010, (SN/SE/WN/WE: 50/50/63/63), From Bus #243753, To Bus # 244010, (SN/SE/WN/WE: 53/60/67/73) |  | 0 | 12/1/2026 |  |  | 8/8/2023 | https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2021/20211119/20211119-reliability-analysis-update.ashx
b3353.2 | b3353 | Allen Station Rebuild | West | Allen-East Prestonsburg: A 0.20 mile segment of this 46 kV line will be relocated to the new station (SN/SE/WN/WE: 53/61/67/73MVA). (Conversion of S2405.2) | Baseline | 46 | 0.33 | 12/1/2026 | AEP |  |  |  | AEP: 100.00 | KY | Allen – East Prestonsburg | Transmission Line | Modify | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 0.33 | TO Criteria Violation | 2022-12-27 | 2023-04-26 | 4/25/2024 |  | No |  | 11/19/2021 |  | From Bus #243753, To Bus # 244010, (SN/SE/WN/WE: 50/50/63/63), From Bus #243753, To Bus # 244010, (SN/SE/WN/WE: 53/60/67/73) |  | 0 | 12/1/2026 |  |  | 8/8/2023 | https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2021/20211119/20211119-reliability-analysis-update.ashx
b3353.3 | b3353 | Allen Station Rebuild | West | McKinney-Allen: The new line extension will walk around the south and east sides of the existing Allen station to the new Allen station being built in the clear. A short segment of new single circuit 69 kV line and a short segment of new double circuit 69 kV line (both operated at 46 kV) will be added to the line to tie into the new Allen station bays. (Conversion of S2405.3) | Baseline | 46 | 1.95 | 12/1/2026 | AEP |  |  |  | AEP: 100.00 | KY | McKinney – Allen | Transmission Line | Install | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 1.95 | TO Criteria Violation | 2022-12-07 | 2023-04-06 | 4/5/2024 |  | No |  | 11/19/2021 |  | From Bus #243753, To Bus # 244010, (SN/SE/WN/WE: 50/50/63/63), From Bus #243753, To Bus # 244010, (SN/SE/WN/WE: 53/60/67/73) |  | 0 | 12/1/2026 |  |  | 8/8/2023 | https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2021/20211119/20211119-reliability-analysis-update.ashx
b3353.4 | b3353 | Allen Station Rebuild | West | Stanville-Allen: A segment of this line will have to be relocated to the new station (SN/SE/WN/WE: 50/50/63/63MVA). (Conversion of S2405.4) | Baseline | 46 | 0.17 | 12/1/2026 | AEP |  |  |  | AEP: 100.00 | KY | Stanville – Allen | Transmission Line | Modify | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 0.17 | TO Criteria Violation | 2023-07-19 | 2023-11-16 | 11/15/2024 |  | No |  | 11/19/2021 |  | From Bus #243753, To Bus # 244010, (SN/SE/WN/WE: 50/50/63/63), From Bus #243753, To Bus # 244010, (SN/SE/WN/WE: 53/60/67/73) |  | 0 | 12/1/2026 |  |  | 8/8/2023 | https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2021/20211119/20211119-reliability-analysis-update.ashx
b3353.5 | b3353 | Allen Station Rebuild | West | Allen-Prestonsburg: 0.25 mile segment of this existing single circuit will be relocated. The relocated line segment will require construction of one custom self-supporting double circuit dead-end structure and single circuit suspension structure. A short segment of new double circuit 69 kV line (energized at 46 kV) will be added to tie into the new Allen station bays, which will carry Allen-Prestonsburg 46 kV and Allen-East Prestonsburg 46 kV lines. A temporary 0.15 mile section double circuit line will be constructed to keep Allen-Prestonsburg and Allen-East Prestonsburg 46 kV lines energized during construction. (Conversion of S2405.5) | Baseline | 46 | 2.66 | 12/1/2026 | AEP |  |  |  | AEP: 100.00 | KY | Allen – Prestonsburg | Transmission Line | Modify | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 2.66 | TO Criteria Violation | 2024-06-20 | 2024-10-18 | 10/18/2025 |  | No |  | 11/19/2021 |  | From Bus #243753, To Bus # 244010, (SN/SE/WN/WE: 50/50/63/63), From Bus #243753, To Bus # 244010, (SN/SE/WN/WE: 53/60/67/73) |  | 0 | 12/1/2026 |  |  | 1/26/2023 | https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2021/20211119/20211119-reliability-analysis-update.ashx
b3353.6 | b3353 | Allen Station Rebuild | West | Remote end work will be required at Prestonsburg, Stanville and McKinney stations. (Conversion of S2405.6) | Baseline | 46 | 0.34 | 12/1/2026 | AEP |  |  |  | AEP: 100.00 | KY | Prestonsburg, Stanville, McKinney | Substation | Modify | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 0.34 | TO Criteria Violation | 2023-07-19 | 2023-11-16 | 11/15/2024 |  | No |  | 11/19/2021 |  | From Bus #243753, To Bus # 244010, (SN/SE/WN/WE: 50/50/63/63), From Bus #243753, To Bus # 244010, (SN/SE/WN/WE: 53/60/67/73) |  | 0 | 12/1/2026 |  |  | 8/8/2023 | https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2021/20211119/20211119-reliability-analysis-update.ashx
b3360 | b3360 | Thelma Transformer Replacement Project | West | Replace Thelma Transformer #1 with a 138/69/46 kV 130/130/90 MVA transformer and replace 46 kV risers and relaying toward Kenwood substation. Existing TR#1 to be used as spare. | Baseline | 69 | 3.54 | 12/1/2026 | AEP |  |  |  | AEP: 100.00 | KY | Thelma | Transformer | Replace | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 3.54 | TO Criteria Violation | 2025-02-01 | 2025-06-01 | 6/1/2026 |  | No |  | 11/19/2021 |  | Thelma TR#1 138KV and 69KV windings: 130/130/130/130 MVA 46kV winding:90/90/90/90 MVA |  | 0 | 12/1/2026 |  |  | 10/17/2022 | https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2021/20211119/20211119-reliability-analysis-update.ashx
b3361 | b3361 | Prestonburg Thelma Project | West | Rebuild Prestonsburg-Thelma 46 kV circuit, approximately 14 miles. Retire Jenny Wiley SS. | Baseline | 46 | 33.01 | 12/1/2026 | AEP |  |  |  | AEP: 100.00 | KY | Prestonsburg - Thelma | Transmission Line | Rebuild | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 33.01 | TO Criteria Violation | 2025-01-01 | 2025-05-01 | 5/1/2026 |  | No |  | 11/19/2021 |  | 05Thelma – 05KENWDTAP -05PRESTNSB 46KV 68/85/86/101 |  | 0 | 12/1/2026 |  |  | 10/17/2022 | https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2021/20211119/20211119-reliability-analysis-update.ashx
b3736.1 | b3736 | Breaks-Dorton Conversion | West | Establish 69kV bus and new 69 kV line CB at Dorton substation. | Baseline | 69 | 1.13 | 12/1/2027 | AEP |  |  |  | AEP: 100.00 | KY | Dorton | Bus | Construct | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 1.13 | TO Criteria Violation | 2026-04-02 | 2026-07-31 | 7/31/2027 |  | No |  | 11/18/2022 |  |  |  | 0 | 12/1/2027 |  |  | 6/29/2023
b3736.10 | b3736 | Breaks-Dorton Conversion | West | Henry Clay S.S Retirement: | Baseline | 46 | 0.3 | 12/1/2027 | AEP |  |  |  | AEP: 100.00 | KY | Henry Clay | Substation | Retire | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 0.3 | TO Criteria Violation | 2026-04-02 | 2026-07-31 | 7/31/2027 |  | No |  | 11/18/2022 |  |  |  | 0 | 12/1/2027 |  |  | 6/29/2023
b3736.11 | b3736 | Breaks-Dorton Conversion | West | Cedar Creek substation work | Baseline | 46 | 0.44 | 12/1/2027 | AEP |  |  |  | AEP: 100.00 | KY | Cedar Creek | Substation | Modify | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 0.44 | TO Criteria Violation | 2026-04-02 | 2026-07-31 | 7/31/2027 |  | No |  | 11/18/2022 |  |  |  | 0 | 12/1/2027 |  |  | 6/29/2023
b3736.12 | b3736 | Breaks-Dorton Conversion | West | Breaks substation retire 46kV equipment: | Baseline | 46 | 0.25 | 12/1/2027 | AEP |  |  |  | AEP: 100.00 | KY | Breaks | Substation | Retire | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 0.25 | TO Criteria Violation | 2026-04-02 | 2026-07-31 | 7/31/2027 |  | No |  | 11/18/2022 |  |  |  | 0 | 12/1/2027 |  |  | 6/29/2023
b3736.13 | b3736 | Breaks-Dorton Conversion | West | Retire Pike 29 SS and Rob Fork SS | Baseline | 46 | 0.42 | 12/1/2027 | AEP |  |  |  | AEP: 100.00 | KY | Pike 29, Rob Fork | Substation | Retire | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 0.42 | TO Criteria Violation | 2026-04-02 | 2026-07-31 | 7/31/2027 |  | No |  | 11/18/2022 |  |  |  | 0 | 12/1/2027 |  |  | 6/29/2023
b3736.14 | b3736 | Breaks-Dorton Conversion | West | Serve Pike 29 and Rob Fork customers from nearby 34kV Distribution sources. | Baseline | 46 | 0 | 12/1/2027 | AEP |  |  |  | AEP: 100.00 | KY | Pike 29 load, Rob Fork load | Distribution Line | Provide | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 0 | TO Criteria Violation | 2026-04-02 | 2026-07-31 | 7/31/2027 |  | No |  | 11/18/2022 |  |  |  | 0 | 12/1/2027 |  |  | 6/29/2023
b3736.15 | b3736 | Breaks-Dorton Conversion | West | Poor Bottom substation install | Baseline | 69 | 0 | 12/1/2027 | AEP |  |  |  | AEP: 100.00 | KY | Poor Bottom | Substation | Install | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 0 | TO Criteria Violation | 2026-04-02 | 2026-07-31 | 7/31/2027 |  | No |  | 11/18/2022 |  |  |  | 0 | 12/1/2027 |  |  | 6/29/2023
b3736.16 | b3736 | Breaks-Dorton Conversion | West | Henry Clay 46kV substation retirement | Baseline | 46 | 0 | 12/1/2027 | AEP |  |  |  | AEP: 100.00 | KY | Henry Clay | Substation | Retire | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 0 | TO Criteria Violation | 2026-04-02 | 2026-07-31 | 7/31/2027 |  | No |  | 11/18/2022 |  |  |  | 0 | 12/1/2027 |  |  | 6/29/2023
b3736.17 | b3736 | Breaks-Dorton Conversion | West | New Draffin 69kV substation install | Baseline | 69 | 0 | 12/1/2027 | AEP |  |  |  | AEP: 100.00 | KY | New Draffin | Substation | Install | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 0 | TO Criteria Violation | 2026-04-02 | 2026-07-31 | 7/31/2027 |  | No |  | 11/18/2022 |  |  |  | 0 | 12/1/2027 |  |  | 6/29/2023
b3736.18 | b3736 | Breaks-Dorton Conversion | West | Draffin 46kV substation retirement | Baseline | 46 | 0 | 12/1/2027 | AEP |  |  |  | AEP: 100.00 | KY | Draffin | Substation | Retire | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 0 | TO Criteria Violation | 2026-04-02 | 2026-07-31 | 7/31/2027 |  | No |  | 11/18/2022 |  |  |  | 0 | 12/1/2027 |  |  | 6/29/2023
b3736.2 | b3736 | Breaks-Dorton Conversion | West | At Breaks substation, reuse 72kV breaker A as the new 69kV line breaker. | Baseline | 69 | 0.71 | 12/1/2027 | AEP |  |  |  | AEP: 100.00 | KY | Breaks | Circuit Breaker | Modify | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 0.71 | TO Criteria Violation | 2026-04-02 | 2026-07-31 | 7/31/2027 |  | No |  | 11/18/2022 |  |  |  | 0 | 12/1/2027 |  |  | 6/29/2023
b3736.3 | b3736 | Breaks-Dorton Conversion | West | Rebuild ~16.7 mi Dorton – Breaks 46kV line to 69kV | Baseline | 69 | 58.52 | 12/1/2027 | AEP |  |  |  | AEP: 100.00 | KY | Dorton - Breaks | Transmission Line | Rebuild | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 58.52 | TO Criteria Violation | 2026-04-02 | 2026-07-31 | 7/31/2027 |  | No |  | 11/18/2022 |  |  |  | 0 | 12/1/2027 |  |  | 6/29/2023
b3736.4 | b3736 | Breaks-Dorton Conversion | West | Retire ~17.2 mi Cedar Creek – Elwood 46kV circuit. | Baseline | 46 | 11.15 | 12/1/2027 | AEP |  |  |  | AEP: 100.00 | KY | Cedar Creek - Elwood | Transmission Line | Retire | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 11.15 | TO Criteria Violation | 2026-04-02 | 2026-07-31 | 7/31/2027 |  | No |  | 11/18/2022 |  |  |  | 0 | 12/1/2027 |  |  | 6/29/2023
b3736.5 | b3736 | Breaks-Dorton Conversion | West | Retire ~ 6.2 mi Henry Clay – Elwood 46kV line section. | Baseline | 46 | 4.3 | 12/1/2027 | AEP |  |  |  | AEP: 100.00 | KY | Henry Clay - Elwood | Transmission Line | Retire | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 4.3 | TO Criteria Violation | 2026-04-02 | 2026-07-31 | 7/31/2027 |  | No |  | 11/18/2022 |  |  |  | 0 | 12/1/2027 |  |  | 6/29/2023
b3736.6 | b3736 | Breaks-Dorton Conversion | West | Retire Henry Clay 46 kV substation and replace with Poor Bottom 69 kV station. Install a new 0.7 mi double circuit extension to Poor Bottom 69kV. | Baseline | 69 | 3.42 | 12/1/2027 | AEP |  |  |  | AEP: 100.00 | KY | Henry clay, Poor Bottom | Substation | Replace | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 3.42 | TO Criteria Violation | 2026-04-02 | 2026-07-31 | 7/31/2027 |  | No |  | 11/18/2022 |  |  |  | 0 | 12/1/2027 |  |  | 6/29/2023
b3736.7 | b3736 | Breaks-Dorton Conversion | West | Retire Draffin substation and replace with a new substation. Install a new 0.25 mi double circuit extension to New Draffin substation. | Baseline | 69 | 2.01 | 12/1/2027 | AEP |  |  |  | AEP: 100.00 | KY | Draffin, New Darffin | Substation | Replace | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 2.01 | TO Criteria Violation | 2026-04-02 | 2026-07-31 | 7/31/2027 |  | No |  | 11/18/2022 |  |  |  | 0 | 12/1/2027 |  |  | 6/29/2023
b3736.8 | b3736 | Breaks-Dorton Conversion | West | Remote End work at Jenkins substation | Baseline | 69 | 0.03 | 12/1/2027 | AEP |  |  |  | AEP: 100.00 | KY | Jenkins | Substation | Modify | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 0.03 | TO Criteria Violation | 2026-04-02 | 2026-07-31 | 7/31/2027 |  | No |  | 11/18/2022 |  |  |  | 0 | 12/1/2027 |  |  | 6/29/2023
b3736.9 | b3736 | Breaks-Dorton Conversion | West | Provide Transition fiber to Dorton, Breaks, Poor Bottom, Jenkins and New Draffin substations | Baseline | 69 | 0.41 | 12/1/2027 | AEP |  |  |  | AEP: 100.00 | KY | Dorton, Breaks, Poor bottom, Jenkins, New Draffin | Communication Equipment | Provide | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 0.41 | TO Criteria Violation | 2026-04-02 | 2026-07-31 | 7/31/2027 |  | No |  | 11/18/2022 |  |  |  | 0 | 12/1/2027 |  |  | 6/29/2023
s1547 | s1547 | Leslie Transformer Replacement | West | Replace existing 90 MVA Leslie 161/69 kV transformer with a new 130 MVA 161/69 kV transformer. A second 161/69 kV transformer will be purchased as a non--switchable spare on site. Replace Leslie 161 kV 3000 A 50 kA circuit breaker “K” with a new 3000 A 40 kA 161 kV circuit breaker. | Supplemental | 161/69 | 6.3 |  | AEP |  |  |  |  | KY | Leslie | Transformer | Replace | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 6.3 | Equipment Material Condition, Performance and Risk | 2023-07-31 | 2023-11-28 | 11/27/2024 |  | No |  | 3/9/2018 | 3/27/2018 | 130 MVA, 3000A 40 kA |  | 0.5 |  |  |  | 8/8/2023 | https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/20180309/20180309-reliability-analysis-update.ashx, https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/20180327/20180327-reliability-analysis-update.ashx
s2188.1 | s2188 | Garrett Area Improvement | West | Construct 10.3 miles of single circuit 138kV from Soft Shell to Garrett picking up Salt Lick Co-op via Snag Fork along the way. Complete associated remote end relaying. | Supplemental | 138 | 35.3 |  | AEP |  |  |  |  | KY | Soft Shell - Garrett | Transmission Line | Construct | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 35.3 | Equipment Material Condition, Performance and Risk, Operational Flexibility and Efficiency | 2023-07-19 | 2023-11-16 | 11/15/2024 |  | No |  | 2/21/2020 |  |  |  | 0 |  |  |  | 9/30/2022 | https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2020/20200221/20200221-reliability-analysis-update.ashx
s2188.10 | s2188 | Garrett Area Improvement | West | Install a 138kV breaker (3000A 40kA) with an exit towards Garrett station (via Snag Fork) at Softshell substation. | Supplemental | 138 | 0 |  | AEP |  |  |  |  | KY | Softshell | Circuit Breaker | Install | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 0.8 | Equipment Material Condition, Performance and Risk, Operational Flexibility and Efficiency | 2023-07-19 | 2023-11-16 | 11/15/2024 |  | No |  | 2/21/2020 |  | 40 kA |  | 0 |  |  |  | 9/30/2022 | https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2020/20200221/20200221-reliability-analysis-update.ashx
s2188.11 | s2188 | Garrett Area Improvement | West | Retire the ~25 miles of the 46kV Beaver Creek – McKinney #1 46 KV circuit. Retire Spring Fork Tap. | Supplemental | 46 | 17.3 |  | AEP |  |  |  |  | KY | Beaver Creek – McKinney #1 | Transmission Line | Remove | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 17.3 | Equipment Material Condition, Performance and Risk, Operational Flexibility and Efficiency | 2023-07-19 | 2023-11-16 | 11/15/2024 |  | No |  | 2/21/2020 |  |  |  | 0 |  |  |  | 9/30/2022 | https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2020/20200221/20200221-reliability-analysis-update.ashx
s2188.2 | s2188 | Garrett Area Improvement | West | Construct ~3 miles of single circuit 138kV from the Eastern station to Garrett station. A short extension will be required from the new station to the existing Hays Branch metering point. Construct short extension to existing Morgan Fork – Hays Branch 138 kV circuit from Eastern station | Supplemental | 138 | 11.5 |  | AEP |  |  |  |  | KY | Eastern station - Garrett, Morgan Fork - Hays Bran | Transmission Line | Construct | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 11.5 | Equipment Material Condition, Performance and Risk, Operational Flexibility and Efficiency | 2023-07-19 | 2023-11-16 | 11/15/2024 |  | No |  | 2/21/2020 |  |  |  | 0 |  |  |  | 9/30/2022 | https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2020/20200221/20200221-reliability-analysis-update.ashx
s2188.3 | s2188 | Garrett Area Improvement | West | Double circuit cut into existing Hays Branch - Morgan Fork line to tie into new Eastern Station. | Supplemental | 138 | 1.3 |  | AEP |  |  |  |  | KY | Hays Branch - Morgan Fork | Transmission Line | Modify | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 1.3 | Equipment Material Condition, Performance and Risk, Operational Flexibility and Efficiency | 2023-07-19 | 2023-11-16 | 11/15/2024 |  | No |  | 2/21/2020 |  |  |  | 0 |  |  |  | 9/30/2022 | https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2020/20200221/20200221-reliability-analysis-update.ashx
s2188.4 | s2188 | Garrett Area Improvement | West | Construct ~1.4 mi of double circuit 138kV line between Eastern and the tap point on the Morgan Fork-Hays Branch line. The proposed line will establish a direct feed to Hays Branch from Eastern and establishing a through path line between Eastern and Morgan Fork.. | Supplemental | 138 | 1.6 |  | AEP |  |  |  |  | KY | Hays Branch S.S – Eastern | Transmission Line | Construct | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 1.6 | Equipment Material Condition, Performance and Risk, Operational Flexibility and Efficiency | 2023-07-19 | 2023-11-16 | 11/15/2024 |  | No |  | 2/21/2020 |  |  |  | 0 |  |  |  | 9/30/2022 | https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2020/20200221/20200221-reliability-analysis-update.ashx
s2188.5 | s2188 | Garrett Area Improvement | West | New relaying at Hays Branch to accommodate new line from Eastern station | Supplemental | 138 | 0.5 |  | AEP |  |  |  |  | KY | Hays Branch | Circuit Switcher | Install | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 0.5 | Equipment Material Condition, Performance and Risk, Operational Flexibility and Efficiency | 2023-07-19 | 2023-11-16 | 11/15/2024 |  | No |  | 2/21/2020 |  |  |  | 0 |  |  |  | 9/30/2022 | https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2020/20200221/20200221-reliability-analysis-update.ashx
s2188.6 | s2188 | Garrett Area Improvement | West | Expand the Garrett station,Install a straight bus arrangement with two 138kV breakers and a circuit switcher on the high side of the transformer, 138/12kV 30MVA transformer | Supplemental | 138/12 | 0 |  | AEP |  |  |  |  | KY | Garrett | Substation | Modify | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 5.8 | Equipment Material Condition, Performance and Risk, Operational Flexibility and Efficiency | 2023-07-19 | 2023-11-16 | 11/15/2024 |  | No |  | 2/21/2020 |  | 30 MVA |  | 0 |  |  |  | 9/30/2022 | https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2020/20200221/20200221-reliability-analysis-update.ashx
s2188.7 | s2188 | Garrett Area Improvement | West | Establish a new 138 kV substation Eastern south of the existing Hays Branch station. Install three 138kV breakers (3000A 40kA) at the new Eastern station in a ring bus arrangement. | Supplemental | 138 | 6 |  | AEP |  |  |  |  | KY | Eastern | Substation | Build | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 6 | Equipment Material Condition, Performance and Risk, Operational Flexibility and Efficiency | 2023-07-19 | 2023-11-16 | 11/15/2024 |  | No |  | 2/21/2020 |  | 40 kA |  | 0 |  |  |  | 9/30/2022 | https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2020/20200221/20200221-reliability-analysis-update.ashx
s2188.8 | s2188 | Garrett Area Improvement | West | Establish Snag Fork S.S. Install a 3 way phase over phase motorized (automated) switching structure near Saltlick to serve the EKPC co-op. | Supplemental | 138 | 1.1 |  | AEP |  |  |  |  | KY | Snag Fork S.S. | Circuit Switcher | Install | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 1.1 | Equipment Material Condition, Performance and Risk, Operational Flexibility and Efficiency | 2023-07-19 | 2023-11-16 | 11/15/2024 |  | No |  | 2/21/2020 |  |  |  | 0 |  |  |  | 9/30/2022 | https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2020/20200221/20200221-reliability-analysis-update.ashx
s2188.9 | s2188 | Garrett Area Improvement | West | Move the existing 69kV rated CB G to the Beaver Creek – McKinney #2 circuit exit at McKinney substation. | Supplemental | 69 | 0 |  | AEP |  |  |  |  | KY | Beaver Creek – McKinney #2 | Circuit Breaker | Modify | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 0 | Equipment Material Condition, Performance and Risk, Operational Flexibility and Efficiency | 2023-07-19 | 2023-11-16 | 11/15/2024 |  | No |  | 2/21/2020 |  |  |  | 0 |  |  |  | 9/30/2022 | https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2020/20200221/20200221-reliability-analysis-update.ashx
s2219 | s2219 | Fleming Station Rebuild (Phase 20 | West | Rebuild Fleming station in the clear; Replace 138/69kV Fleming Transformer #1 with 138/69kV 130 MVA transformer with high side 138 kV CB; Install a 5 breaker 69 kV ring bus on the low side of the transformer, replace 69 kV circuit switcher AA, replace 69/12kV transformer #3 with 69/12kV 30 MVA transformer, Replace 12 kV CB A and D. Retire existing Fleming substation. | Supplemental | 138/69/12 | 21.1 |  | AEP |  |  |  |  | KY | Fleming | Substation | Rebuild | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 21.1 | Equipment Material Condition, Performance and Risk, Operational Flexibility and Efficiency | 2023-04-01 | 2023-07-30 | 7/29/2024 |  | No |  | 3/19/2020 |  | 130 MVA |  | 0.25 |  |  |  | 8/8/2023 | https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2020/20200319/20200319-reliability-analysis-update.ashx
s2251.2 | s2251 | Tygart Station | West | Retire Siloam Station. | Supplemental | 69 | 0 |  | AEP |  |  |  |  | KY | Siloam | Substation | Remove | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 0 | Customer Service | 2022-09-21 | 2023-01-19 | 1/19/2024 |  | No |  | 4/20/2020 |  |  |  | 0.15 |  |  |  | 8/8/2023 | https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2020/20200420/20200420-reliability-analysis-update.ashx
s2251.3 | s2251 | Tygart Station | West | Remote end relaying at Millbrook Park to coordinate with new breakers. | Supplemental | 69 | 0.4 |  | AEP |  |  |  |  | KY | Millbrook Park | Relay | Modify | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 0.4 | Customer Service | 2023-01-22 | 2023-05-22 | 5/21/2024 |  | No |  | 4/20/2020 |  |  |  | 0 |  |  |  | 9/30/2022 | https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2020/20200420/20200420-reliability-analysis-update.ashx
s2251.4 | s2251 | Tygart Station | West | Tap the 69kV Central Portsmouth – Millbrook Park line and install 3 custom T-line structures due to proximity to the Railroad. | Supplemental | 69 | 0.9 |  | AEP |  |  |  |  | KY | Central Portsmouth – Millbrook Park | Transmission Line | Modify | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 0.9 | Customer Service | 2023-01-22 | 2023-05-22 | 5/21/2024 |  | No |  | 4/20/2020 |  |  |  | 0 |  |  |  | 9/30/2022 | https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2020/20200420/20200420-reliability-analysis-update.ashx
s2428.1 | s2428 | Wooton-Pineville Project | West | At Wooton station, upgrade relaying to accommodate new OPGW fiber protection. | Supplemental | 161 | 1.1 |  | AEP |  |  |  |  | KY | Wooton | Relay | Upgrade | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 1.1 | Equipment Material Condition, Performance and Risk | 2026-08-02 | 2026-11-30 | 11/30/2027 |  | No |  | 11/20/2020 |  |  |  | 0 |  |  |  | 9/30/2022 | https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2020/20201120/20201120-item-03-reliability-analysis-update.ashx
s2428.2 | s2428 | Wooton-Pineville Project | West | At Leslie station, reconductor the 161kV Bus, Relaying upgrades towards Wooton and Pineville, Replace 161kV MOAB W, Replace 161kV XF#1 high side switch. Install DICM. | Supplemental | 161 | 1.2 |  | AEP |  |  |  |  | KY | Leslie | Substation | Upgrade | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 1.2 | Equipment Material Condition, Performance and Risk | 2026-08-02 | 2026-11-30 | 11/30/2027 |  | No |  | 11/20/2020 |  |  |  | 0 |  |  |  | 9/30/2022 | https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2020/20201120/20201120-item-03-reliability-analysis-update.ashx
s2428.3 | s2428 | Wooton-Pineville Project | West | Remote end work at Hazard substation. | Supplemental | 161 | 0.03 |  | AEP |  |  |  |  | KY | Hazard | Substation | Modify | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 0.03 | Equipment Material Condition, Performance and Risk | 2026-08-02 | 2026-11-30 | 11/30/2027 |  | No |  | 11/20/2020 |  |  |  | 0 |  |  |  | 9/30/2022 | https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2020/20201120/20201120-item-03-reliability-analysis-update.ashx
s2428.4 | s2428 | Wooton-Pineville Project | West | Rebuild approximately ~40 miles of Wooton – Pineville 161kV line to address the identified asset condition needs. This work also includes line removal work as well as access road construction. Majority of proposed line rebuild is to be constructed on existing center line. | Supplemental | 161 | 115 |  | AEP |  |  |  |  | KY | Wooton – Pineville | Transmission Line | Rebuild | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 115 | Equipment Material Condition, Performance and Risk | 2026-08-02 | 2026-11-30 | 11/30/2027 |  | No |  | 11/20/2020 |  |  |  | 0 |  |  |  | 9/30/2022 | https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2020/20201120/20201120-item-03-reliability-analysis-update.ashx
s2428.5 | s2428 | Wooton-Pineville Project | West | Expand existing ROW for the Wooton – Pineville 161kV line. | Supplemental | 161 | 8.5 |  | AEP |  |  |  |  | KY | Wooton – Pineville | Transmission Line | Upgrade | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 8.5 | Equipment Material Condition, Performance and Risk | 2026-08-02 | 2026-11-30 | 11/30/2027 |  | No |  | 11/20/2020 |  |  |  | 0 |  |  |  | 9/30/2022 | https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2020/20201120/20201120-item-03-reliability-analysis-update.ashx
s2428.6 | s2428 | Wooton-Pineville Project | West | Relocate ~0.32 mi 69kV Leslie – Clover Fork which includes of one structure and reconfiguration of the existing line to cross underneath the proposed Wooton-Stinnett 161kV Line. | Supplemental | 161 | 0.7 |  | AEP |  |  |  |  | KY | Leslie – Clover Fork | Transmission Line | Modify | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 0.7 | Equipment Material Condition, Performance and Risk | 2026-08-02 | 2026-11-30 | 11/30/2027 |  | No |  | 11/20/2020 |  |  |  | 0 |  |  |  | 9/30/2022 | https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2020/20201120/20201120-item-03-reliability-analysis-update.ashx
s2428.7 | s2428 | Wooton-Pineville Project | West | At Stinnett station, upgrade relaying to accommodate new OPGW fiber protection. Provide transition, entry and termination for OPGW connectivity to the Hazard-Pineville fiber route. | Supplemental | 161 | 0.7 |  | AEP |  |  |  |  | KY | Stinnett | Relay | Upgrade | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 0.7 | Equipment Material Condition, Performance and Risk | 2026-08-02 | 2026-11-30 | 11/30/2027 |  | No |  | 11/20/2020 |  |  |  | 0 |  |  |  | 9/30/2022 | https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2020/20201120/20201120-item-03-reliability-analysis-update.ashx
s2428.8 | s2428 | Wooton-Pineville Project | West | Provide transition, entry and termination for OPGW connectivity at Leslie substation. | Supplemental | 161 | 0.1 |  | AEP |  |  |  |  | KY | Leslie | Substation | Modify | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 0.1 | Equipment Material Condition, Performance and Risk | 2026-08-02 | 2026-11-30 | 11/30/2027 |  | No |  | 11/20/2020 |  |  |  | 0 |  |  |  | 9/30/2022 | https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2020/20201120/20201120-item-03-reliability-analysis-update.ashx
s2436.1 | s2436 | Burton Station Replacement | West | Construct a greenfield 69/12 KV Osborne Station to replace Burton Station, including a high-side 69KV Phase Over Phase switch, fiber connectivity, a circuit switcher, and one 69/12kV 12/16/20MVA transformer and associated distribution feeders. | Supplemental | 69/12 | 0.74 |  | AEP |  |  |  |  | KY | Osborne, Burton | Substation | Construct | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 0.74 | Equipment Material Condition, Performance and Risk, Operational Flexibility and Efficiency | 2023-08-03 | 2023-12-01 | 11/30/2024 |  | No |  | 12/18/2020 |  |  |  | 0 |  |  |  | 9/30/2022 | https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2020/20201218/20201218-item-04-reliability-analysis-update.ashx, https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2020/20201218/20201218-reliability-analysis-update.ashx
s2436.10 | s2436 | Burton Station Replacement | West | Reconfigure the existing Beaver Creek - Fremont 138kV circuit to facilitate the construction of the new double circuit Myra Extension 138kV Line to feed the proposed Myra Substation. | Supplemental | 138 | 1 |  | AEP |  |  |  |  | KY | Beaver Creek - Fremont | Transmission Line | Modify | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 1 | Equipment Material Condition, Performance and Risk, Operational Flexibility and Efficiency | 2023-08-03 | 2023-12-01 | 11/30/2024 |  | No |  | 12/18/2020 |  |  |  | 0 |  |  |  | 9/30/2022 | https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2020/20201218/20201218-item-04-reliability-analysis-update.ashx, https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2020/20201218/20201218-reliability-analysis-update.ashx
s2436.11 | s2436 | Burton Station Replacement | West | Install two replacement structures in order to bypass Elwood station. Transfer wires from old structure to new structure. Tie new structure to Cedar Creek-Henry Clay 46kV Line. | Supplemental | 46 | 1.35 |  | AEP |  |  |  |  | KY | Elwood, Cedar Creek-Henry Clay | Transmission Structures | Install | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 1.35 | Equipment Material Condition, Performance and Risk, Operational Flexibility and Efficiency | 2023-08-03 | 2023-12-01 | 11/30/2024 |  | No |  | 12/18/2020 |  |  |  | 0 |  |  |  | 9/30/2022 | https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2020/20201218/20201218-item-04-reliability-analysis-update.ashx, https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2020/20201218/20201218-reliability-analysis-update.ashx
s2436.12 | s2436 | Burton Station Replacement | West | Retire ~10.48 mi Beaver Creek – Elwood 46kV line. | Supplemental | 46 | 6.47 |  | AEP |  |  |  |  | KY | Beaver Creek – Elwood | Transmission Line | Remove | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 6.47 | Equipment Material Condition, Performance and Risk, Operational Flexibility and Efficiency | 2023-08-03 | 2023-12-01 | 11/30/2024 |  | No |  | 12/18/2020 |  |  |  | 0 |  |  |  | 9/30/2022 | https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2020/20201218/20201218-item-04-reliability-analysis-update.ashx, https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2020/20201218/20201218-reliability-analysis-update.ashx
s2436.2 | s2436 | Elwood Station Improvement | West | Construct a greenfield 138KV Myra Station to replace Elwood Station. Install 138KV double box bay with two 138kV circuit breakers and line exits to Fremont & Beaver Creek. Install 138/34.5 kV transformer with high-side circuit switcher and associated 34.5kV breakers. Install fiber connectivity for upgraded relaying. | Supplemental | 138/34.5 | 3.43 |  | AEP |  |  |  |  | KY | Myra, Elwood | Substation | Construct | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 3.43 | Equipment Material Condition, Performance and Risk, Operational Flexibility and Efficiency | 2023-08-03 | 2023-12-01 | 11/30/2024 |  | No |  | 12/18/2020 |  |  |  | 0 |  |  |  | 9/30/2022 | https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2020/20201218/20201218-item-04-reliability-analysis-update.ashx, https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2020/20201218/20201218-reliability-analysis-update.ashx
s2436.3 | s2436 | Burton Station Replacement | West | Remote end relaying work at Beaver Creek substation. Remove 46KV Elwood Line 46kV circuit breaker "G“ and associated equipment. | Supplemental | 46 | 0.17 |  | AEP |  |  |  |  | KY | Beaver Creek | Relay | Modify | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 0.17 | Equipment Material Condition, Performance and Risk, Operational Flexibility and Efficiency | 2023-08-03 | 2023-12-01 | 11/30/2024 |  | No |  | 12/18/2020 |  |  |  | 0 |  |  |  | 9/30/2022 | https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2020/20201218/20201218-item-04-reliability-analysis-update.ashx, https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2020/20201218/20201218-reliability-analysis-update.ashx
s2436.4 | s2436 | Burton Station Replacement | West | Remote end relaying work at Fremont substation. | Supplemental | 138 | 0.42 |  | AEP |  |  |  |  | KY | Fremont | Relay | Modify | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 0.42 | Equipment Material Condition, Performance and Risk, Operational Flexibility and Efficiency | 2023-08-03 | 2023-12-01 | 11/30/2024 |  | No |  | 12/18/2020 |  |  |  | 0 |  |  |  | 9/30/2022 | https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2020/20201218/20201218-item-04-reliability-analysis-update.ashx, https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2020/20201218/20201218-reliability-analysis-update.ashx
s2436.5 | s2436 | Burton Station Replacement | West | At Burton station, retire and remove all existing equipment. | Supplemental | 46 | 0 |  | AEP |  |  |  |  | KY | Burton | Substation | Remove | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 0 | Equipment Material Condition, Performance and Risk, Operational Flexibility and Efficiency | 2023-08-03 | 2023-12-01 | 11/30/2024 |  | No |  | 12/18/2020 |  |  |  | 0 |  |  |  | 9/30/2022 | https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2020/20201218/20201218-item-04-reliability-analysis-update.ashx, https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2020/20201218/20201218-reliability-analysis-update.ashx
s2436.6 | s2436 | Burton Station Replacement | West | At Elwood station, retire and remove all existing equipment. | Supplemental | 46 | 0 |  | AEP |  |  |  |  | KY | Elwood | Substation | Remove | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 0 | Equipment Material Condition, Performance and Risk, Operational Flexibility and Efficiency | 2023-08-03 | 2023-12-01 | 11/30/2024 |  | No |  | 12/18/2020 |  |  |  | 0 |  |  |  | 9/30/2022 | https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2020/20201218/20201218-item-04-reliability-analysis-update.ashx, https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2020/20201218/20201218-reliability-analysis-update.ashx
s2436.7 | s2436 | Burton Station Replacement | West | Construct a new ~0.5 mi double circuit 69 kV line to the proposed Osborne substation. | Supplemental | 69 | 2.56 |  | AEP |  |  |  |  | KY | Osborne | Transmission Line | Construct | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 2.56 | Equipment Material Condition, Performance and Risk, Operational Flexibility and Efficiency | 2023-08-03 | 2023-12-01 | 11/30/2024 |  | No |  | 12/18/2020 |  |  |  | 0 |  |  |  | 9/30/2022 | https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2020/20201218/20201218-item-04-reliability-analysis-update.ashx, https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2020/20201218/20201218-reliability-analysis-update.ashx
s2436.8 | s2436 | Burton Station Replacement | West | Reconfigure the existing Beaver Creek - Fleming 69kV line to facilitate the construction of the new double circuit Osborne 69kV line to feed the proposed Osborne Substation. | Supplemental | 69 | 1.22 |  | AEP |  |  |  |  | KY | Beaver Creek - Fleming | Transmission Line | Modify | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 1.22 | Equipment Material Condition, Performance and Risk, Operational Flexibility and Efficiency | 2023-08-03 | 2023-12-01 | 11/30/2024 |  | No |  | 12/18/2020 |  |  |  | 0 |  |  |  | 9/30/2022 | https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2020/20201218/20201218-item-04-reliability-analysis-update.ashx, https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2020/20201218/20201218-reliability-analysis-update.ashx
s2436.9 | s2436 | Burton Station Replacement | West | Construct a new ~2 mi double circuit 138 kV line to the proposed Myra substation. | Supplemental | 138 | 8.8 |  | AEP |  |  |  |  | KY | Myra | Transmission Line | Construct | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 8.8 | Equipment Material Condition, Performance and Risk, Operational Flexibility and Efficiency | 2023-08-03 | 2023-12-01 | 11/30/2024 |  | No |  | 12/18/2020 |  |  |  | 0 |  |  |  | 9/30/2022 | https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2020/20201218/20201218-item-04-reliability-analysis-update.ashx, https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2020/20201218/20201218-reliability-analysis-update.ashx
s2446.1 | s2446 | Belfry Project- (Supplemental) | West | Replace Belfry substation with Orinoco substation by installing a 69KV box bay and 12KV rural bay to be built in the clear southwest of existing Belfry station. Install 69/12kV 20 MVA transformer and two 12kV breakers. | Supplemental | 69/12 | 0.65 |  | AEP |  |  |  |  | KY | Belfry, Orinoco | Substation | Replace | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 0.65 | Equipment Material Condition, Performance and Risk | 2023-09-03 | 2024-01-01 | 12/31/2024 |  | No |  | 1/15/2021 |  |  |  | 0 |  |  |  | 9/30/2022 | https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2021/20210115/20210115-item-06-reliability-analysis-update.ashx, https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2021/20210115/20210115-reliability-analysis-update.ashx
s2446.2 | s2446 | Belfry Project- (Supplemental) | West | Retire Belfry 46kV substation. | Supplemental | 46 | 0 |  | AEP |  |  |  |  | KY | Belfry | Substation | Remove | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 0 | Equipment Material Condition, Performance and Risk | 2023-09-03 | 2024-01-01 | 12/31/2024 |  | No |  | 1/15/2021 |  |  |  | 0 |  |  |  | 9/30/2022 | https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2021/20210115/20210115-item-06-reliability-analysis-update.ashx, https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2021/20210115/20210115-reliability-analysis-update.ashx
s2446.3 | s2446 | Belfry Project- (Supplemental) | West | Retire 46kV equipment from Stone substation. | Supplemental | 46 | 0.07 |  | AEP |  |  |  |  | KY | Stone | Substation | Remove | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 0.07 | Equipment Material Condition, Performance and Risk | 2023-09-03 | 2024-01-01 | 12/31/2024 |  | No |  | 1/15/2021 |  |  |  | 0 |  |  |  | 9/30/2022 | https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2021/20210115/20210115-item-06-reliability-analysis-update.ashx, https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2021/20210115/20210115-reliability-analysis-update.ashx
s2446.4 | s2446 | Belfry Project- (Supplemental) | West | At Hatfield substation, replace MOAB Y with a 69KV Circuit Breaker towards Stone 69kV line via New Camp and Orinoco. | Supplemental | 69 | 0.85 |  | AEP |  |  |  |  | KY | Hatfield | Circuit Breaker | Install | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 0.85 | Equipment Material Condition, Performance and Risk | 2023-09-03 | 2024-01-01 | 12/31/2024 |  | No |  | 1/15/2021 |  |  |  | 0 |  |  |  | 9/30/2022 | https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2021/20210115/20210115-item-06-reliability-analysis-update.ashx, https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2021/20210115/20210115-reliability-analysis-update.ashx
s2446.5 | s2446 | Belfry Project- (Supplemental) | West | Retire the 46kV equipment at Sprigg station towards Stone (via Belfry). | Supplemental | 46 | 0.05 |  | AEP |  |  |  |  | KY | Sprigg | Substation | Modify | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 0.05 | Equipment Material Condition, Performance and Risk | 2023-09-03 | 2024-01-01 | 12/31/2024 |  | No |  | 1/15/2021 |  |  |  | 0 |  |  |  | 9/30/2022 | https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2021/20210115/20210115-item-06-reliability-analysis-update.ashx, https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2021/20210115/20210115-reliability-analysis-update.ashx
s2446.6 | s2446 | Belfry Project- (Supplemental) | West | Retire Turkey Creek Tap. | Supplemental | 69 | 0.76 |  | AEP |  |  |  |  | KY | Turkey Creek Tap | Circuit Switcher | Remove | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 0.76 | Equipment Material Condition, Performance and Risk | 2023-09-03 | 2024-01-01 | 12/31/2024 |  | No |  | 1/15/2021 |  |  |  | 0 |  |  |  | 9/30/2022 | https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2021/20210115/20210115-item-06-reliability-analysis-update.ashx, https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2021/20210115/20210115-reliability-analysis-update.ashx
s2446.7 | s2446 | Belfry Project- (Supplemental) | West | Retire the ~8.23 miles of the 46kV Sprigg – Stone 46 KV circuit. | Supplemental | 46 | 6.73 |  | AEP |  |  |  |  | KY | Sprigg – Stone | Transmission Line | Remove | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 6.73 | Equipment Material Condition, Performance and Risk | 2023-09-03 | 2024-01-01 | 12/31/2024 |  | No |  | 1/15/2021 |  |  |  | 0 |  |  |  | 9/30/2022 | https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2021/20210115/20210115-item-06-reliability-analysis-update.ashx, https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2021/20210115/20210115-reliability-analysis-update.ashx
s2470.1 | s2470 | Kenwood Loop | West | A green field line is to be constructed (Kenwood 69kV Extension) and to be operated at 46kV. The new extension will provide looped service into Kenwood substation. It will be approximately 2.25 miles of single circuit construction through mountainous terrain in Floyd and Johnson Counties in Kentucky. The extension will tap the existing Prestonsburg-Thelma 46kV Line around structure K346-50. (SN:53 MVA , SE:61 MVA, WN:67 MVA, WE:73 MVA) | Supplemental | 46 | 5.8 |  | AEP |  |  |  |  | KY | Kenwood 69kV Extension, Prestonsburg-Thelma | Transmission Line | Build | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 5.8 | Equipment Material Condition, Performance and Risk | 2025-07-19 | 2025-11-16 | 11/16/2026 |  | No |  | 3/19/2021 |  | SN:53 MVA , SE:61 MVA, WN:67 MVA, WE:73 MVA |  | 0 |  |  | Reviewing effiency | 8/8/2023 | https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2021/20210319/20210319-reliability-analysis-update.ashx
s2470.2 | s2470 | Kenwood Loop | West | Rebuild the existing ~1.77 mi Kenwood Tap line from Kenwood to Van Lear Tap Structure on the existing center line. (SN:53 MVA , SE:61 MVA, WN:67 MVA, WE:73 MVA) | Supplemental | 46 | 4.9 |  | AEP |  |  |  |  | KY | Kenwood Tap-Van Lear Tap | Transmission Line | Rebuild | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 4.9 | Equipment Material Condition, Performance and Risk | 2025-07-19 | 2025-11-16 | 11/16/2026 |  | No |  | 3/19/2021 |  | SN:53 MVA , SE:61 MVA, WN:67 MVA, WE:73 MVA |  | 0 |  |  |  | 8/8/2023 | https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2021/20210319/20210319-reliability-analysis-update.ashx
s2470.3 | s2470 | Kenwood Loop | West | Provide splicing for 2.25 miles of 96ct OPGW on the Kenwood 69kV Extension Line and 1.77 mi Kenwood TAP line. This extension spans from Kenwood Station to the Prestonsburg-Thelma 46kV line. | Supplemental | 46 | 0.1 |  | AEP |  |  |  |  | KY | Kenwood 69kV Extension, Kenwood Tap lines | Transmission Line | Modify | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 0.1 | Equipment Material Condition, Performance and Risk | 2025-07-19 | 2025-11-16 | 11/16/2026 |  | No |  | 3/19/2021 |  |  |  | 0 |  |  |  | 8/8/2023 | https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2021/20210319/20210319-reliability-analysis-update.ashx
s2470.4 | s2470 | Kenwood Loop | West | At Kenwood substation, Extend the walk bus and add second 46KV line to set up Kenwood station as a looped station with MOABS protecting each exit. Add new H-Frame dead end with MOAB and single phase CCVT. Add MOAB and single phase CCVT to existing line. Relocate 3 phase CCVT's from cap bank AA to 46KV Bus. Add 3-bay transclosure, and separate battery enclosure. Replace Battery and Charger. | Supplemental | 46 | 0 |  | AEP |  |  |  |  | KY | Kenwood | Substation | Upgrade | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 0 | Equipment Material Condition, Performance and Risk | 2025-07-19 | 2025-11-16 | 11/16/2026 |  | No |  | 3/19/2021 |  |  |  | 0 |  |  |  | 8/8/2023 | https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2021/20210319/20210319-reliability-analysis-update.ashx
s2470.5 | s2470 | Kenwood Loop | West | Retire Van Lear SS. | Supplemental | 46 | 0.1 |  | AEP |  |  |  |  | KY | Van Lear SS | Circuit Switcher | Remove | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 0.1 | Equipment Material Condition, Performance and Risk | 2025-07-19 | 2025-11-16 | 11/16/2026 |  | No |  | 3/19/2021 |  |  |  | 0 |  |  |  | 8/8/2023 | https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2021/20210319/20210319-reliability-analysis-update.ashx
s2470.6 | s2470 | Kenwood Loop | West | Remote end work at Prestonsburg substation. | Supplemental | 46 | 0 |  | AEP |  |  |  |  | KY | Prestonsburg | Substation | Upgrade | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 0 | Equipment Material Condition, Performance and Risk | 2025-07-19 | 2025-11-16 | 11/16/2026 |  | No |  | 3/19/2021 |  |  |  | 0 |  |  |  | 8/8/2023 | https://www.pjm.com//-/media/committees-groups/committees/srrtep-w/2021/20210319/20210319-reliability-analysis-update.ashx
s2813.1 | s2813 | Dewey Station Upgrades (Supplemental) | West | At Dewey substation: Replace 138kV CB B towards Thelma with new 138kV 40kA circuit breaker. Provide new DICM with new relays for all equipment at station so that existing control house can be removed. Upgrade station service. | Supplemental | 138 | 2.4 |  | AEP |  |  |  |  | KY | Dewey | Circuit Breaker | Replace | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 2.4 | Equipment Material Condition, Performance and Risk | 2024-08-03 | 2024-12-01 | 12/1/2025 |  | No |  | 8/19/2022 |  |  |  | 0 |  |  |  | 2/9/2023
s2813.2 | s2813 | Dewey Station Upgrades (Supplemental) | West | At Dewey substation: Provide Transition fiber via underground from the existing Control House to the new DICM at Dewey Station. Retire existing fiber. | Supplemental | 138 | 0.18 |  | AEP |  |  |  |  | KY | Dewey | Communication Equipment | Replace | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 0.18 | Equipment Material Condition, Performance and Risk | 2024-08-03 | 2024-12-01 | 12/1/2025 |  | No |  | 8/19/2022 |  |  |  | 0 |  |  |  | 2/9/2023
s2813.3 | s2813 | Dewey Station Upgrades (Supplemental) | West | At Thelma substation, Remote end relaying to replace line protection for Breaker A towards (Dewey) to match upgrade at Dewey Station. Provide MOS on existing 138kV HS of transformer XF #1 & #3 to provide additional control to stability system | Supplemental | 138 | 0.4 |  | AEP |  |  |  |  | KY | Thelma | Relay | Replace | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 0.4 | Equipment Material Condition, Performance and Risk | 2024-08-03 | 2024-12-01 | 12/1/2025 |  | No |  | 8/19/2022 |  |  |  | 0 |  |  |  | 2/9/2023
s2814.1 | s2814 | Bellefonte Station Upgrades (Supplemental) | West | Bellefonte: Replace XFR #2 with a 200MVA Auto unit and retire XFR #1 & #5. The U/G feeder for XFR #3 69kV riser is getting reconductored under B3349. Reconductor sections of 138kV Bus #1 and 138kV Bus #2. Replace remaining oil PTs connected to Bus #1 and Bus #2. Upgrade Primary and back up station service. Replace 69kV bus tie breaker H. Replace the hook stick disconnects switches for the tie breaker H and 69kV tie breaker location will be relocated one bay south of the existing location and 69kV buses will be reconfigured. Replace the hook stick disconnects switches for Raceland breaker D. Relocate the Raceland feeder to bus #1 after extending the 69kV bus #1. The cap bank switcher/moab Mark 5 combo unit will get replaced with 69kV breaker and set of breaker disconnects and relocated to bus #1. 69kV breaker is needed instead of circuit switcher due to the high fault current. Relocate the cap bank to bus #1 after extending the 69kV bus #1. 69kV Air Products line MOABs will be replaced with 2000A SW. Replace hook-stick switches for Oil CB – AB, JJ, I, G, Z, T and C. These Breakers are replaced as part of B3350. Install 16'x48' DICM for 69kV Yard and a 16'x48' DICM for the 138kV Yard. Replace cable trench, single phase AC system & cable work, entire fence replacement and ground grid extension for 100'X10' expansion toward the Northwest of the 69kV yard. Both 138kV and 69kV control house will be retired. | Supplemental | 138/69 | 12.59 |  | AEP |  |  |  |  | KY | Bellefonte | Transformer | Replace | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 12.59 | Equipment Material Condition, Performance and Risk | 2024-08-03 | 2024-12-01 | 12/1/2025 |  | No |  | 8/19/2022 |  |  |  | 0 |  |  |  | 2/9/2023
s2814.2 | s2814 | Bellefonte Station Upgrades (Supplemental) | West | The customer served out of 34.5 kV Yard has plans for demolition of their facilities. Retire entire 34kV Yard, contingent on the timing of the customer being removed from service. | Supplemental | 34 | 2.67 |  | AEP |  |  |  |  | KY | Bellefonte | Transmission Structures | Retire | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 2.67 | Equipment Material Condition, Performance and Risk | 2024-08-03 | 2024-12-01 | 12/1/2025 |  | No |  | 8/19/2022 |  |  |  | 0 |  |  |  | 2/9/2023
s2814.3 | s2814 | Bellefonte Station Upgrades (Supplemental) | West | Retirement of the Bellefonte 34.5kV Bus Tie Line that connects the Bellefonte 138kV Station to the Bellefonte 34kV Station. This removal involves removing 3- Double Circuit Lattice Towers, 1-Triple Circuit Lattice Towers, and 1 Single Wood Pole Structure. | Supplemental | 34.5 | 0.46 |  | AEP |  |  |  |  | KY | Bellefonte | Bus Tie | Retire | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 0.46 | Equipment Material Condition, Performance and Risk | 2024-08-03 | 2024-12-01 | 12/1/2025 |  | No |  | 8/19/2022 |  |  |  | 0 |  |  |  | 2/9/2023
s2814.4 | s2814 | Bellefonte Station Upgrades (Supplemental) | West | Retire the existing Bellefonte – Armco 34.5kV operated line. The major removal work involves removing 4 lattice steel towers, 1 H-Frame wood structure, and 2 single wood poles. The line being removed is approximately 0.55 miles long. | Supplemental | 34.5 | 1 |  | AEP |  |  |  |  | KY | Bellefonte - Armco | Transmission Line | Retire | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 1 | Equipment Material Condition, Performance and Risk | 2024-08-03 | 2024-12-01 | 12/1/2025 |  | No |  | 8/19/2022 |  |  |  | 0 |  |  |  | 2/9/2023
s2814.5 | s2814 | Bellefonte Station Upgrades (Supplemental) | West | Remote end relaying at Raceland substation to install 2 new CCVTs on a custom two-phase single column stand for the Bellefonte 69kV line exit. The existing CCVT mounted on a single phase CCVT stand will be reused and will remain as it is. | Supplemental | 69 | 0.37 |  | AEP |  |  |  |  | KY | Raceland | Relay | Install | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 0.37 | Equipment Material Condition, Performance and Risk | 2024-08-03 | 2024-12-01 | 12/1/2025 |  | No |  | 8/19/2022 |  |  |  | 0 |  |  |  | 2/9/2023
s2814.6 | s2814 | Bellefonte Station Upgrades (Supplemental) | West | Provide 0.2 miles of fiber from Distribution structures outside the station to the new DICMs. | Supplemental | 69 | 0.49 |  | AEP |  |  |  |  | KY | Bellefonte - Raceland | Communication Equipment | Install | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 0.49 | Equipment Material Condition, Performance and Risk | 2024-08-03 | 2024-12-01 | 12/1/2025 |  | No |  | 8/19/2022 |  |  |  | 0 |  |  |  | 2/9/2023
s2815.1 | s2815 | Hatfield Station Upgrades | West | At Hatfield Substation, expand the substation yard. Relocate 138/69/46kV XF#1. Replace 138/69/46kV XF#1 Bushings, 138kV 3 phase Bus CCVTs, MOAB X1 and GND Switch Z1 with a new 138kV Circuit Switcher. Replace 138KV Sprigg Line metering, Line Switch "11" with a 138kV Circuit Breaker. Replace and relocate 69kV CB-B to standard Bay position. Replace 69KV CB-A and add 3 phase CCVTs to John's Creek 69kV line. Add 138kV Backup and 69kV Primary Station Service transformers and Station Service. Expand yard and install a 16' X 27' base DICM. Remove 111MVA 46/7.2KV Transformer #2 and associated equipment and 7.2KV 3 phase station service. Remove the control building. | Supplemental | 138/69 | 4.95 |  | AEP |  |  |  |  | KY | Hatfield | Substation | Expand | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 4.95 | Equipment Material Condition, Performance and Risk | 2023-04-04 | 2023-08-02 | 8/1/2024 |  | No |  | 8/19/2022 |  |  |  | 0 |  |  |  | 2/9/2023
s2815.2 | s2815 | Hatfield Station Expansion Project | West | On the Leslie No.1 – Hatfield 69kV circuit, remove existing guyed dead-end structure K357-29 and install a new single pole, single circuit, custom dead-end to remove the guy wires conflicting with station footprint plans. The existing guy anchors would conflict with station expansion plans, and it is not feasible to span guy over top of proposed control house as the anchors would land in the proposed station drive path. The proposed custom dead-end structure will be placed 20' downhill from existing structure K357-29. | Supplemental | 69 | 0.5 |  | AEP |  |  |  |  | KY | Hatfield | Transmission Structures | Remove | EP | Engineering & Procurement | 0-25 % Includes engineering, detailed design, material procurement & resource planning. | 0.5 | Equipment Material Condition, Performance and Risk | 2023-04-04 | 2023-08-02 | 8/1/2024 |  | No |  | 8/19/2022 |  |  |  | 0 |  |  |  | 2/9/2023
| b3087 | Kenwanee-Enterprise Park | West | This project will address thermal and voltage violations identified on the Pikeville 46kV network by establishing a new substation (Kewanee) to the west (~1.5 mi.) of the existing Fords Branch Station, potentially in/near the new Kentucky Enterprise Industrial Park. This new station will consist of 4 -138 kV breaker ring bus and 2 step-down distribution voltage transformers and a 28.8 MVAR Cap Bank. The project will construct approximately 5 miles of new double circuit 138 kV line in order to loop the new substation into the existing Beaver Creek – Cedar Creek 138 kV circuit | Baseline | [8 empty] | KY | [7 empty] | TO Criteria Violation | 2018-08-10 | 2023-12-02 | 2024-12-01
| s1412 | Hazard-Wooton |  | Install a new 3000A 40 kA 138 kV circuit breaker at Hazard station on the line exit towards Beckham station. (s1412.1) Add a 138 kV circuit switcher to the high side of transformer #4. (s1412.2) Replace 138 kV capacitor bank and switcher BB with a new switcher and 43.2 MVAR capacitor bank. (s1412.3) Replace 138/69 kV transformers #1 and #2 with new 138/69 kV 130 MVA transformers with 138 kV circuit switchers on the high side and 3000A 40 kA 69 kV breakers on the low side. (s1412.4) Replaces 69 kV circuit breakers S, E, and F with 3000A 40 kA 69 kV circuit breakers with a bus tie 3000A 69 kV circuit breaker being installed between the existing 69 kV box bays. (s1412.5) Replace 69 kV capacitor bank and switcher CC with a new switcher and 28.8 MVAR capacitor bank. 69 kV capacitor bank and switcher AA will be retired. Replace 161 kV circuit breaker M towards Wooton with a 161 kV 3000 A 40 kA breaker. (s1412.6) Add a 3000A 40 kA 138 kV circuit breaker to the low side of 161/138 kV transformer #3. (s1412.7) Address safety and access issues associated with existing equipment platforms and drainage issues at the station. (s1412.8) | Supplemental | [8 empty] | KY | [7 empty] | Equipment Material Condition Performance and Risk | 2017-11-17 | 2022-11-30 | 2023-11-30
| b2761 | Hazard-Wooton |  | Rebuild the Hazard – Wooton 161 kV line utilizing 795 26/7 ACSR conductor (300 MVA rating). | Baseline | [8 empty] | KY | [7 empty] | TO Criteria Violation | 2022-08-02 | 2022-11-30 | 2023-11-30
| s2428 | Stinnett-Pineville |  | The proposed project would rebuild the approximately 30-mile Stinnett – Pineville 161 kV line. The project would address equipment material conditions, performance, and risk concerns associated with the 1940’s wood structure line. | Supplemental | [8 empty] | KY | [7 empty] | Equipment Material Condition Performance and Risk | 2029-08-02 | 2029-11-30 | 2030-11-30
Missing Projects
Hazard-Wooton
Kewanee-Enterpise Park
Middle Creek-Prestonburg
Myra
Stinnett-Pineville
Make it aesthetic
Check IRP Discovery for naming |  | ARCs search Kamran Ali
Formulas:
Projected File By Date = [Projected Construction Start Date]-120
Projected Construction Start Date = [Projected In Service Date]-365

## Final View
Parent PJM ID | Name of Project | Projected File By Date | Projected Construction Start Date | Projected In Service Date | Description | Reason/Issues Addressed
b3281 | Dewey Station Upgrades (Baseline) | 2024-08-03 | 2024-12-01 | 12/1/2025 | Install 138 kV circuit switcher on the 138/69 kV transformer #1 and 138/34.5 kV transformer #2 at Dewey. Install 138 kV 2000 A 40 kA breaker on Stanville line at Dewey 138 kV substation. | TO Criteria Violation
b3283 | Inez Station Improvement | 2024-08-03 | 2024-12-01 | 12/1/2025 | Replace the existing Inez 138/69 kV 50 MVA autotransformer with a 138/69 kV 90 MVA autotransformer. | TO Criteria Violation
b3288 | Belfry Project (Baseline) | 2024-08-03 | 2024-12-01 | 12/1/2025 | At New Camp substation, rebuild the 69 kV bus, add 69 kV MOAB W and replace the 69 kV ground switch Z1 with a 69 kV circuit switcher on the New Camp transformer. | TO Criteria Violation
[5 empty] | At Stone substation, circuit breaker A to remain in place and be utilized as T1 low side breaker, circuit breaker B to remain in place and be utilized as new Hatfield (via Orinoco and New Camp) 69 kV line breaker. Add new 69 kV circuit breaker E for Coleman Line exit. | TO Criteria Violation
[5 empty] | Construct ~ 2.75 mi Orinoco - Stone 69 kV transmission line in the clear between Orinoco station and Stone station. | TO Criteria Violation
[5 empty] | Construct ~ 3.25 mi Orinoco – New Camp 69 kV transmission line in the clear between Orinoco station and New Camp station. | TO Criteria Violation
[5 empty] | Reconfigure the New Camp 69 kV tap which includes access road improvements/installation, temporary wire and permanent wire work along with dead end structures installation. | TO Criteria Violation
b3307 | Fleming Station Rebuild | 2024-08-03 | 2024-12-01 | 12/1/2025 | Rebuild Fleming station in the clear; Replace 138/69kV Fleming Transformer #1 with 138/69 kV 130 MVA transformer with high side 138 kV CB; Install a 5 breaker 69 kV ring bus on the low side of the transformer, replace 69 kV circuit switcher AA, replace 69/12kV transformer #3 with 69/12 kV 30 MVA transformer, replace 12 kV CB A and D. Retire existing Fleming substation. | TO Criteria Violation
b3349 | Bellefonte Station Upgrades (Baseline) | 2025-02-01 | 2025-06-01 | 6/1/2026 | Replace Bellefonte 69 kV risers on the section between Bellefonte TR #3 and 69 kV Bus #2. | TO Criteria Violation
b3352 | 47th Street Upgrades | 2024-08-03 | 2024-12-01 | 12/1/2025 | Replace MOAB W, MOAB Y, line and bus side jumpers of both W and Y at 47th Street 69 kV station. Upgrade the 69 kV strain bus between MOABs W and Y to 795 KCM AAC. Change the connectors on the tap to MOAB X1 to accommodate the larger 795 KCM AAC. | TO Criteria Violation
b3353 | Allen Station Improvement | 2023-07-19 | 2023-11-16 | 11/15/2024 | Allen substation: Rebuild Allen station to the northwest of its current footprint utilizing a standard air-insulated substation with equipment raised by 7’ concrete platforms and control house raised by a 10’ platform to mitigate flooding concerns. Install five 69 kV 3000A 40 kA circuit breakers in a ring bus (operated at 46 kV) configuration with a 13.2 MVAR capacitor bank. Existing Allen station will be retired (does not include the distribution cost). Distribution scope of work: Install 69/46 kV-12 kV 20 MVA transformer along with 2-12 kV breakers on 7’ concrete platforms (conversion of S2405.1). | TO Criteria Violation
| Allen Station Rebuild | 2022-12-07 | 2023-04-06 | 4/5/2024 | McKinney-Allen: The new line extension will walk around the south and east sides of the existing Allen station to the new Allen station being built in the clear. A short segment of new single circuit 69 kV line and a short segment of new double circuit 69 kV line (both operated at 46 kV) will be added to the line to tie into the new Allen station bays. (Conversion of S2405.3) | TO Criteria Violation
|  | 2022-12-27 | 2023-04-26 | 4/25/2024 | Allen-East Prestonsburg: A 0.20 mile segment of this 46 kV line will be relocated to the new station (SN/SE/WN/WE: 53/61/67/73MVA). (Conversion of S2405.2) | TO Criteria Violation
|  | 2023-07-19 | 2023-11-16 | 11/15/2024 | Remote end work will be required at Prestonsburg, Stanville and McKinney stations. (Conversion of S2405.6) | TO Criteria Violation
[5 empty] | Stanville-Allen: A segment of this line will have to be relocated to the new station (SN/SE/WN/WE: 50/50/63/63MVA). (Conversion of S2405.4) | TO Criteria Violation
|  | 2024-06-20 | 2024-10-18 | 10/18/2025 | Allen-Prestonsburg: 0.25 mile segment of this existing single circuit will be relocated. The relocated line segment will require construction of one custom self-supporting double circuit dead-end structure and single circuit suspension structure. A short segment of new double circuit 69 kV line (energized at 46 kV) will be added to tie into the new Allen station bays, which will carry Allen-Prestonsburg 46 kV and Allen-East Prestonsburg 46 kV lines. A temporary 0.15 mile section double circuit line will be constructed to keep Allen-Prestonsburg and Allen-East Prestonsburg 46 kV lines energized during construction. (Conversion of S2405.5) | TO Criteria Violation
b3360 | Thelma Transformer Replacement Project | 2025-02-01 | 2025-06-01 | 6/1/2026 | Replace Thelma Transformer #1 with a 138/69/46 kV 130/130/90 MVA transformer and replace 46 kV risers and relaying toward Kenwood substation. Existing TR#1 to be used as spare. | TO Criteria Violation
b3361 | Prestonburg Thelma Project | 2025-01-01 | 2025-05-01 | 5/1/2026 | Rebuild Prestonsburg-Thelma 46 kV circuit, approximately 14 miles. Retire Jenny Wiley SS. | TO Criteria Violation
b3736 | Breaks-Dorton Conversion | 2026-04-02 | 2026-07-31 | 7/31/2027 | At Breaks substation, reuse 72kV breaker A as the new 69kV line breaker. | TO Criteria Violation
[5 empty] | Breaks substation retire 46kV equipment: | TO Criteria Violation
[5 empty] | Cedar Creek substation work | TO Criteria Violation
[5 empty] | Draffin 46kV substation retirement | TO Criteria Violation
[5 empty] | Establish 69kV bus and new 69 kV line CB at Dorton substation. | TO Criteria Violation
[5 empty] | Henry Clay 46kV substation retirement | TO Criteria Violation
[5 empty] | Henry Clay S.S Retirement: | TO Criteria Violation
[5 empty] | New Draffin 69kV substation install | TO Criteria Violation
[5 empty] | Poor Bottom substation install | TO Criteria Violation
[5 empty] | Provide Transition fiber to Dorton, Breaks, Poor Bottom, Jenkins and New Draffin substations | TO Criteria Violation
[5 empty] | Rebuild ~16.7 mi Dorton – Breaks 46kV line to 69kV | TO Criteria Violation
[5 empty] | Remote End work at Jenkins substation | TO Criteria Violation
[5 empty] | Retire ~ 6.2 mi Henry Clay – Elwood 46kV line section. | TO Criteria Violation
[5 empty] | Retire ~17.2 mi Cedar Creek – Elwood 46kV circuit. | TO Criteria Violation
[5 empty] | Retire Draffin substation and replace with a new substation. Install a new 0.25 mi double circuit extension to New Draffin substation. | TO Criteria Violation
[5 empty] | Retire Henry Clay 46 kV substation and replace with Poor Bottom 69 kV station. Install a new 0.7 mi double circuit extension to Poor Bottom 69kV. | TO Criteria Violation
[5 empty] | Retire Pike 29 SS and Rob Fork SS | TO Criteria Violation
[5 empty] | Serve Pike 29 and Rob Fork customers from nearby 34kV Distribution sources. | TO Criteria Violation
s1547 | Leslie Transformer Replacement | 2023-07-31 | 2023-11-28 | 11/27/2024 | Replace existing 90 MVA Leslie 161/69 kV transformer with a new 130 MVA 161/69 kV transformer. A second 161/69 kV transformer will be purchased as a non--switchable spare on site. Replace Leslie 161 kV 3000 A 50 kA circuit breaker “K” with a new 3000 A 40 kA 161 kV circuit breaker. | Equipment Material Condition, Performance and Risk
s2188 | Garrett Area Improvement | 2023-07-19 | 2023-11-16 | 11/15/2024 | Construct ~1.4 mi of double circuit 138kV line between Eastern and the tap point on the Morgan Fork-Hays Branch line. The proposed line will establish a direct feed to Hays Branch from Eastern and establishing a through path line between Eastern and Morgan Fork.. | Equipment Material Condition, Performance and Risk, Operational Flexibility and Efficiency
[5 empty] | Construct ~3 miles of single circuit 138kV from the Eastern station to Garrett station. A short extension will be required from the new station to the existing Hays Branch metering point. Construct short extension to existing Morgan Fork – Hays Branch 138 kV circuit from Eastern station | Equipment Material Condition, Performance and Risk, Operational Flexibility and Efficiency
[5 empty] | Construct 10.3 miles of single circuit 138kV from Soft Shell to Garrett picking up Salt Lick Co-op via Snag Fork along the way. Complete associated remote end relaying. | Equipment Material Condition, Performance and Risk, Operational Flexibility and Efficiency
[5 empty] | Double circuit cut into existing Hays Branch - Morgan Fork line to tie into new Eastern Station. | Equipment Material Condition, Performance and Risk, Operational Flexibility and Efficiency
[5 empty] | Establish a new 138 kV substation Eastern south of the existing Hays Branch station. Install three 138kV breakers (3000A 40kA) at the new Eastern station in a ring bus arrangement. | Equipment Material Condition, Performance and Risk, Operational Flexibility and Efficiency
[5 empty] | Establish Snag Fork S.S. Install a 3 way phase over phase motorized (automated) switching structure near Saltlick to serve the EKPC co-op. | Equipment Material Condition, Performance and Risk, Operational Flexibility and Efficiency
[5 empty] | Expand the Garrett station,Install a straight bus arrangement with two 138kV breakers and a circuit switcher on the high side of the transformer, 138/12kV 30MVA transformer | Equipment Material Condition, Performance and Risk, Operational Flexibility and Efficiency
[5 empty] | Install a 138kV breaker (3000A 40kA) with an exit towards Garrett station (via Snag Fork) at Softshell substation. | Equipment Material Condition, Performance and Risk, Operational Flexibility and Efficiency
[5 empty] | Move the existing 69kV rated CB G to the Beaver Creek – McKinney #2 circuit exit at McKinney substation. | Equipment Material Condition, Performance and Risk, Operational Flexibility and Efficiency
[5 empty] | New relaying at Hays Branch to accommodate new line from Eastern station | Equipment Material Condition, Performance and Risk, Operational Flexibility and Efficiency
[5 empty] | Retire the ~25 miles of the 46kV Beaver Creek – McKinney #1 46 KV circuit. Retire Spring Fork Tap. | Equipment Material Condition, Performance and Risk, Operational Flexibility and Efficiency
s2219 | Fleming Station Rebuild (Phase 20 | 2023-04-01 | 2023-07-30 | 7/29/2024 | Rebuild Fleming station in the clear; Replace 138/69kV Fleming Transformer #1 with 138/69kV 130 MVA transformer with high side 138 kV CB; Install a 5 breaker 69 kV ring bus on the low side of the transformer, replace 69 kV circuit switcher AA, replace 69/12kV transformer #3 with 69/12kV 30 MVA transformer, Replace 12 kV CB A and D. Retire existing Fleming substation. | Equipment Material Condition, Performance and Risk, Operational Flexibility and Efficiency
s2251 | Tygart Station | 2022-09-21 | 2023-01-19 | 1/19/2024 | Retire Siloam Station. | Customer Service
|  | 2023-01-22 | 2023-05-22 | 5/21/2024 | Remote end relaying at Millbrook Park to coordinate with new breakers. | Customer Service
[5 empty] | Tap the 69kV Central Portsmouth – Millbrook Park line and install 3 custom T-line structures due to proximity to the Railroad. | Customer Service
s2428 | Wooton-Pineville Project | 2026-08-02 | 2026-11-30 | 11/30/2027 | At Leslie station, reconductor the 161kV Bus, Relaying upgrades towards Wooton and Pineville, Replace 161kV MOAB W, Replace 161kV XF#1 high side switch. Install DICM. | Equipment Material Condition, Performance and Risk
[5 empty] | At Stinnett station, upgrade relaying to accommodate new OPGW fiber protection. Provide transition, entry and termination for OPGW connectivity to the Hazard-Pineville fiber route. | Equipment Material Condition, Performance and Risk
[5 empty] | At Wooton station, upgrade relaying to accommodate new OPGW fiber protection. | Equipment Material Condition, Performance and Risk
[5 empty] | Expand existing ROW for the Wooton – Pineville 161kV line. | Equipment Material Condition, Performance and Risk
[5 empty] | Provide transition, entry and termination for OPGW connectivity at Leslie substation. | Equipment Material Condition, Performance and Risk
[5 empty] | Rebuild approximately ~40 miles of Wooton – Pineville 161kV line to address the identified asset condition needs. This work also includes line removal work as well as access road construction. Majority of proposed line rebuild is to be constructed on existing center line. | Equipment Material Condition, Performance and Risk
[5 empty] | Relocate ~0.32 mi 69kV Leslie – Clover Fork which includes of one structure and reconfiguration of the existing line to cross underneath the proposed Wooton-Stinnett 161kV Line. | Equipment Material Condition, Performance and Risk
[5 empty] | Remote end work at Hazard substation. | Equipment Material Condition, Performance and Risk
| Stinnett-Pineville | 2029-08-02 | 2029-11-30 | 2030-11-30 | The proposed project would rebuild the approximately 30-mile Stinnett – Pineville 161 kV line. The project would address equipment material conditions, performance, and risk concerns associated with the 1940’s wood structure line. | Equipment Material Condition Performance and Risk
s2436 | Burton Station Replacement | 2023-08-03 | 2023-12-01 | 11/30/2024 | At Burton station, retire and remove all existing equipment. | Equipment Material Condition, Performance and Risk, Operational Flexibility and Efficiency
[5 empty] | At Elwood station, retire and remove all existing equipment. | Equipment Material Condition, Performance and Risk, Operational Flexibility and Efficiency
[5 empty] | Construct a greenfield 69/12 KV Osborne Station to replace Burton Station, including a high-side 69KV Phase Over Phase switch, fiber connectivity, a circuit switcher, and one 69/12kV 12/16/20MVA transformer and associated distribution feeders. | Equipment Material Condition, Performance and Risk, Operational Flexibility and Efficiency
[5 empty] | Construct a new ~0.5 mi double circuit 69 kV line to the proposed Osborne substation. | Equipment Material Condition, Performance and Risk, Operational Flexibility and Efficiency
[5 empty] | Construct a new ~2 mi double circuit 138 kV line to the proposed Myra substation. | Equipment Material Condition, Performance and Risk, Operational Flexibility and Efficiency
[5 empty] | Install two replacement structures in order to bypass Elwood station. Transfer wires from old structure to new structure. Tie new structure to Cedar Creek-Henry Clay 46kV Line. | Equipment Material Condition, Performance and Risk, Operational Flexibility and Efficiency
[5 empty] | Reconfigure the existing Beaver Creek - Fleming 69kV line to facilitate the construction of the new double circuit Osborne 69kV line to feed the proposed Osborne Substation. | Equipment Material Condition, Performance and Risk, Operational Flexibility and Efficiency
[5 empty] | Reconfigure the existing Beaver Creek - Fremont 138kV circuit to facilitate the construction of the new double circuit Myra Extension 138kV Line to feed the proposed Myra Substation. | Equipment Material Condition, Performance and Risk, Operational Flexibility and Efficiency
[5 empty] | Remote end relaying work at Beaver Creek substation. Remove 46KV Elwood Line 46kV circuit breaker "G“ and associated equipment. | Equipment Material Condition, Performance and Risk, Operational Flexibility and Efficiency
[5 empty] | Remote end relaying work at Fremont substation. | Equipment Material Condition, Performance and Risk, Operational Flexibility and Efficiency
[5 empty] | Retire ~10.48 mi Beaver Creek – Elwood 46kV line. | Equipment Material Condition, Performance and Risk, Operational Flexibility and Efficiency
| Elwood Station Improvement | 2023-08-03 | 2023-12-01 | 11/30/2024 | Construct a greenfield 138KV Myra Station to replace Elwood Station. Install 138KV double box bay with two 138kV circuit breakers and line exits to Fremont & Beaver Creek. Install 138/34.5 kV transformer with high-side circuit switcher and associated 34.5kV breakers. Install fiber connectivity for upgraded relaying. | Equipment Material Condition, Performance and Risk, Operational Flexibility and Efficiency
s2446 | Belfry Project- (Supplemental) | 2023-09-03 | 2024-01-01 | 12/31/2024 | At Hatfield substation, replace MOAB Y with a 69KV Circuit Breaker towards Stone 69kV line via New Camp and Orinoco. | Equipment Material Condition, Performance and Risk
[5 empty] | Replace Belfry substation with Orinoco substation by installing a 69KV box bay and 12KV rural bay to be built in the clear southwest of existing Belfry station. Install 69/12kV 20 MVA transformer and two 12kV breakers. | Equipment Material Condition, Performance and Risk
[5 empty] | Retire 46kV equipment from Stone substation. | Equipment Material Condition, Performance and Risk
[5 empty] | Retire Belfry 46kV substation. | Equipment Material Condition, Performance and Risk
[5 empty] | Retire the ~8.23 miles of the 46kV Sprigg – Stone 46 KV circuit. | Equipment Material Condition, Performance and Risk
[5 empty] | Retire the 46kV equipment at Sprigg station towards Stone (via Belfry). | Equipment Material Condition, Performance and Risk
[5 empty] | Retire Turkey Creek Tap. | Equipment Material Condition, Performance and Risk
s2470 | Kenwood Loop | 2025-07-19 | 2025-11-16 | 11/16/2026 | A green field line is to be constructed (Kenwood 69kV Extension) and to be operated at 46kV. The new extension will provide looped service into Kenwood substation. It will be approximately 2.25 miles of single circuit construction through mountainous terrain in Floyd and Johnson Counties in Kentucky. The extension will tap the existing Prestonsburg-Thelma 46kV Line around structure K346-50. (SN:53 MVA , SE:61 MVA, WN:67 MVA, WE:73 MVA) | Equipment Material Condition, Performance and Risk
[5 empty] | At Kenwood substation, Extend the walk bus and add second 46KV line to set up Kenwood station as a looped station with MOABS protecting each exit. Add new H-Frame dead end with MOAB and single phase CCVT. Add MOAB and single phase CCVT to existing line. Relocate 3 phase CCVT's from cap bank AA to 46KV Bus. Add 3-bay transclosure, and separate battery enclosure. Replace Battery and Charger. | Equipment Material Condition, Performance and Risk
[5 empty] | Provide splicing for 2.25 miles of 96ct OPGW on the Kenwood 69kV Extension Line and 1.77 mi Kenwood TAP line. This extension spans from Kenwood Station to the Prestonsburg-Thelma 46kV line. | Equipment Material Condition, Performance and Risk
[5 empty] | Rebuild the existing ~1.77 mi Kenwood Tap line from Kenwood to Van Lear Tap Structure on the existing center line. (SN:53 MVA , SE:61 MVA, WN:67 MVA, WE:73 MVA) | Equipment Material Condition, Performance and Risk
[5 empty] | Remote end work at Prestonsburg substation. | Equipment Material Condition, Performance and Risk
[5 empty] | Retire Van Lear SS. | Equipment Material Condition, Performance and Risk
s2813 | Dewey Station Upgrades (Supplemental) | 2024-08-03 | 2024-12-01 | 12/1/2025 | At Dewey substation: Provide Transition fiber via underground from the existing Control House to the new DICM at Dewey Station. Retire existing fiber. | Equipment Material Condition, Performance and Risk
[5 empty] | At Dewey substation: Replace 138kV CB B towards Thelma with new 138kV 40kA circuit breaker. Provide new DICM with new relays for all equipment at station so that existing control house can be removed. Upgrade station service. | Equipment Material Condition, Performance and Risk
[5 empty] | At Thelma substation, Remote end relaying to replace line protection for Breaker A towards (Dewey) to match upgrade at Dewey Station. Provide MOS on existing 138kV HS of transformer XF #1 & #3 to provide additional control to stability system | Equipment Material Condition, Performance and Risk
s2814 | Bellefonte Station Upgrades (Supplemental) | 2024-08-03 | 2024-12-01 | 12/1/2025 | Bellefonte: Replace XFR #2 with a 200MVA Auto unit and retire XFR #1 & #5. The U/G feeder for XFR #3 69kV riser is getting reconductored under B3349. Reconductor sections of 138kV Bus #1 and 138kV Bus #2. Replace remaining oil PTs connected to Bus #1 and Bus #2. Upgrade Primary and back up station service. Replace 69kV bus tie breaker H. Replace the hook stick disconnects switches for the tie breaker H and 69kV tie breaker location will be relocated one bay south of the existing location and 69kV buses will be reconfigured. Replace the hook stick disconnects switches for Raceland breaker D. Relocate the Raceland feeder to bus #1 after extending the 69kV bus #1. The cap bank switcher/moab Mark 5 combo unit will get replaced with 69kV breaker and set of breaker disconnects and relocated to bus #1. 69kV breaker is needed instead of circuit switcher due to the high fault current. Relocate the cap bank to bus #1 after extending the 69kV bus #1. 69kV Air Products line MOABs will be replaced with 2000A SW. Replace hook-stick switches for Oil CB – AB, JJ, I, G, Z, T and C. These Breakers are replaced as part of B3350. Install 16'x48' DICM for 69kV Yard and a 16'x48' DICM for the 138kV Yard. Replace cable trench, single phase AC system & cable work, entire fence replacement and ground grid extension for 100'X10' expansion toward the Northwest of the 69kV yard. Both 138kV and 69kV control house will be retired. | Equipment Material Condition, Performance and Risk
[5 empty] | Provide 0.2 miles of fiber from Distribution structures outside the station to the new DICMs. | Equipment Material Condition, Performance and Risk
[5 empty] | Remote end relaying at Raceland substation to install 2 new CCVTs on a custom two-phase single column stand for the Bellefonte 69kV line exit. The existing CCVT mounted on a single phase CCVT stand will be reused and will remain as it is. | Equipment Material Condition, Performance and Risk
[5 empty] | Retire the existing Bellefonte – Armco 34.5kV operated line. The major removal work involves removing 4 lattice steel towers, 1 H-Frame wood structure, and 2 single wood poles. The line being removed is approximately 0.55 miles long. | Equipment Material Condition, Performance and Risk
[5 empty] | Retirement of the Bellefonte 34.5kV Bus Tie Line that connects the Bellefonte 138kV Station to the Bellefonte 34kV Station. This removal involves removing 3- Double Circuit Lattice Towers, 1-Triple Circuit Lattice Towers, and 1 Single Wood Pole Structure. | Equipment Material Condition, Performance and Risk
[5 empty] | The customer served out of 34.5 kV Yard has plans for demolition of their facilities. Retire entire 34kV Yard, contingent on the timing of the customer being removed from service. | Equipment Material Condition, Performance and Risk
s2815 | Hatfield Station Expansion Project | 2023-04-04 | 2023-08-02 | 8/1/2024 | On the Leslie No.1 – Hatfield 69kV circuit, remove existing guyed dead-end structure K357-29 and install a new single pole, single circuit, custom dead-end to remove the guy wires conflicting with station footprint plans. The existing guy anchors would conflict with station expansion plans, and it is not feasible to span guy over top of proposed control house as the anchors would land in the proposed station drive path. The proposed custom dead-end structure will be placed 20' downhill from existing structure K357-29. | Equipment Material Condition, Performance and Risk
| Hatfield Station Upgrades | 2023-04-04 | 2023-08-02 | 8/1/2024 | At Hatfield Substation, expand the substation yard. Relocate 138/69/46kV XF#1. Replace 138/69/46kV XF#1 Bushings, 138kV 3 phase Bus CCVTs, MOAB X1 and GND Switch Z1 with a new 138kV Circuit Switcher. Replace 138KV Sprigg Line metering, Line Switch "11" with a 138kV Circuit Breaker. Replace and relocate 69kV CB-B to standard Bay position. Replace 69KV CB-A and add 3 phase CCVTs to John's Creek 69kV line. Add 138kV Backup and 69kV Primary Station Service transformers and Station Service. Expand yard and install a 16' X 27' base DICM. Remove 111MVA 46/7.2KV Transformer #2 and associated equipment and 7.2KV 3 phase station service. Remove the control building. | Equipment Material Condition, Performance and Risk
b3087 | Kenwanee-Enterprise Park | 2018-08-10 | 2023-12-02 | 2024-12-01 | This project will address thermal and voltage violations identified on the Pikeville 46kV network by establishing a new substation (Kewanee) to the west (~1.5 mi.) of the existing Fords Branch Station, potentially in/near the new Kentucky Enterprise Industrial Park. This new station will consist of 4 -138 kV breaker ring bus and 2 step-down distribution voltage transformers and a 28.8 MVAR Cap Bank. The project will construct approximately 5 miles of new double circuit 138 kV line in order to loop the new substation into the existing Beaver Creek – Cedar Creek 138 kV circuit | TO Criteria Violation
s1412 | Hazard-Wooton | 2017-11-17 | 2022-11-30 | 2023-11-30 | Install a new 3000A 40 kA 138 kV circuit breaker at Hazard station on the line exit towards Beckham station. (s1412.1) Add a 138 kV circuit switcher to the high side of transformer #4. (s1412.2) Replace 138 kV capacitor bank and switcher BB with a new switcher and 43.2 MVAR capacitor bank. (s1412.3) Replace 138/69 kV transformers #1 and #2 with new 138/69 kV 130 MVA transformers with 138 kV circuit switchers on the high side and 3000A 40 kA 69 kV breakers on the low side. (s1412.4) Replaces 69 kV circuit breakers S, E, and F with 3000A 40 kA 69 kV circuit breakers with a bus tie 3000A 69 kV circuit breaker being installed between the existing 69 kV box bays. (s1412.5) Replace 69 kV capacitor bank and switcher CC with a new switcher and 28.8 MVAR capacitor bank. 69 kV capacitor bank and switcher AA will be retired. Replace 161 kV circuit breaker M towards Wooton with a 161 kV 3000 A 40 kA breaker. (s1412.6) Add a 3000A 40 kA 138 kV circuit breaker to the low side of 161/138 kV transformer #3. (s1412.7) Address safety and access issues associated with existing equipment platforms and drainage issues at the station. (s1412.8) | Equipment Material Condition Performance and Risk
b2761 | Hazard-Wooton | 2022-08-02 | 2022-11-30 | 2023-11-30 | Rebuild the Hazard – Wooton 161 kV line utilizing 795 26/7 ACSR conductor (300 MVA rating). | TO Criteria Violation
(blank) | (blank) | (blank) | (blank) | (blank) | (blank) | (blank)