## AG-KIUC 1-2
Kentucky Power Company Mitchell Unit 1 and Mitchell Unit 2 Winter Storm Elliott December 23-27, 2023
Unit Name | Event Type | Start Date | End Date | Duration (Hours) | Loss (MWH) | Description
Mitchell 1 | D3 | 2022-12-22 | 2022-12-30 | 120 | 4200.1 | Large clinker growing on North side of Boiler
Mitchell 1 | D1 | 2022-12-24 06:48 | 2022-12-24 07:06 | 0.3 | 139.4 | Reagent slurry feed tanks have frozen level indications and tanks were lower than expected
Mitchell 1 | D1 | 2022-12-24 07:06 | 2022-12-24 07:43 | 0.62 | 60.1 | Reagent slurry feed tanks have frozen level indications and tanks were lower than expected
Mitchell 1 | D1 | 2022-12-24 07:43 | 2022-12-24 08:20 | 0.62 | 286.5 | Reagent slurry feed tanks have frozen level indications and tanks were lower than expected
Mitchell 1 | D1 | 2022-12-24 08:20 | 2022-12-24 12:00 | 3.67 | 513.7 | Reagent slurry feed tanks have frozen level indications and tanks were lower than expected
Mitchell 1 | D1 | 2022-12-24 13:48 | 2022-12-24 19:34 | 5.77 | 462.1 | Opacity
Mitchell 1 | D1 | 2022-12-24 19:34 | 2022-12-25 09:00 | 13.43 | 1210.6 | Opacity
Mitchell 1 | D1 | 2022-12-25 10:07 | 2022-12-25 12:31 | 2.4 | 324.2 | Frozen lumps of coal causing conveyor trip out outs
Mitchell 1 | D1 | 2022-12-26 00:20 | 2022-12-26 08:29 | 8.15 | 367.3 | Opacity
Mitchell 1 | D1 | 2022-12-26 08:29 | 2022-12-26 08:46 | 0.28 | 16.9 | Opacity
Mitchell 1 | D1 | 2022-12-26 08:46 | 2022-12-27 | 15.23 | 1296.1 | Opacity
Mitchell 1 | D3 | 2022-12-27 | 2022-12-27 01:40 | 1.67 | 141.7 | Opacity
Mitchell 1 | D3 | 2022-12-27 01:40 | 2022-12-27 02:02 | 0.37 | 49.3 | Opacity
Mitchell 1 | D3 | 2022-12-27 02:02 | 2022-12-27 02:53 | 0.85 | 131.7 | Opacity
Mitchell 1 | D3 | 2022-12-27 02:53 | 2022-12-27 04:43 | 1.83 | 339.6 | Opacity
Mitchell 1 | D3 | 2022-12-27 04:43 | 2022-12-27 07:22 | 2.65 | 543.7 | Opacity
Mitchell 1 | D3 | 2022-12-27 07:22 | 2022-12-27 11:03 | 3.68 | 865.6 | Opacity
Mitchell 1 | D3 | 2022-12-27 11:03 | 2022-12-28 | 12.95 | 3174.4 | Opacity
Mitchell 2 | D1 | 2022-12-23 10:10 | 2022-12-23 10:28 | 0.3 | 28.4 | 25 Pulv issue
Mitchell 2 | D1 | 2022-12-23 10:28 | 2022-12-23 17:44 | 7.27 | 654.3 | 25 Pulv issue, could not get dampers to operate
Mitchell 2 | D1 | 2022-12-23 12:07 | 2022-12-23 13:56 | 1.82 | 45.8 | Opacity
Mitchell 2 | D1 | 2022-12-23 13:56 | 2022-12-23 14:53 | 0.95 | 47.4 | Opacity
Mitchell 2 | D1 | 2022-12-23 14:53 | 2022-12-23 19:22 | 4.48 | 448 | Opacity
Mitchell 2 | D1 | 2022-12-23 19:22 | 2022-12-23 21:08 | 1.77 | 158.8 | Opacity
Mitchell 2 | D1 | 2022-12-23 21:08 | 2022-12-24 02:46 | 5.63 | 844.7 | Opacity
Mitchell 2 | D1 | 2022-12-24 02:46 | 2022-12-24 04:41 | 1.92 | 172.3 | Opacity
Mitchell 2 | D1 | 2022-12-24 04:41 | 2022-12-24 14:08 | 9.45 | 708.8 | Opacity
Mitchell 2 | D1 | 2022-12-24 06:48 | 2022-12-24 07:08 | 0.33 | 138.3 | Reagent slurry feed tanks have frozen level indications and tanks were lower than expected
Mitchell 2 | D1 | 2022-12-24 07:08 | 2022-12-24 12:00 | 4.87 | 1023.3 | Reagent slurry feed tanks have frozen level indications and tanks were lower than expected
Mitchell 2 | D1 | 2022-12-24 14:08 | 2022-12-25 | 9.87 | 888.2 | Opacity
Mitchell 2 | D3 | 2022-12-25 | 2022-12-26 | 24 | 4565 | Anticipated opacity
Mitchell 2 | D3 | 2022-12-26 | 2022-12-27 12:38 | 36.63 | 6968 | Opacity
Mitchell 2 | D3 | 2022-12-27 12:38 | 2022-12-27 14:02 | 1.4 | 294 | Opacity
Mitchell 2 | D3 | 2022-12-27 14:02 | 2022-12-27 15:12 | 1.17 | 268.7 | Opacity
Mitchell 2 | D3 | 2022-12-27 15:12 | 2022-12-27 16:08 | 0.93 | 317.7 | Opacity
Mitchell 2 | D3 | 2022-12-27 16:08 | 2022-12-28 23:40 | 7.87 | 2871.6 | Opacity