## Export
Unit | Event Type | Month | Scheduled Hours | Forced Hours | Actual Hours | Event Duration Hours | Event Start | Event End | Event Description
East Bend 2 | PO | September | 1705.967 |  | 1705.967 | 1705.967 | 2021-09-11 03:02 | 2021-11-21 05:00 | Planned Fall Outage
East Bend 2 | PE | November | 669.467 |  | 669.467 | 669.467 | 2021-11-21 05:00 | 2021-12-19 02:28 | Unit 2 Planned Fall Outage Extension for Turbine/Generator Work
East Bend 2 | U1 | December |  | 168.2 | 168.2 | 168.2 | 2021-12-19 02:28 | 2021-12-26 02:40 | Exciter repairs
East Bend 2 | PO | December | 1.733 |  | 1.733 | 1.733 | 2021-12-26 02:44 | 2021-12-26 04:28 | 5 MW Trip to Test Relays
East Bend 2 | U1 | December |  | 13.233 | 13.233 | 13.233 | 2021-12-26 14:54 | 2021-12-27 04:08 | Lost drop 25/75 Feedwater Controls
East Bend 2 | U1 | December |  | 10.233 | 10.233 | 10.233 | 2021-12-27 08:46 | 2021-12-27 19:00 | turbine vibration trip
East Bend 2 | MO | December | 26.767 |  | 26.767 | 26.767 | 2021-12-31 02:14 | 2022-01-01 05:00 | Generator Vibration
East Bend 2 | MO | January | 17.45 |  | 17.45 | 17.45 | 2022-01-01 05:01 | 2022-01-01 22:28 | Generator Vibration
East Bend 2 | MO | January | 23.3 |  | 23.3 | 23.3 | 2022-01-03 03:01 | 2022-01-04 02:19 | #9 Balance shot
East Bend 2 | U1 | January |  | 31 | 31 | 31 | 2022-01-18 21:59 | 2022-01-20 04:59 | Loss of EH due to pipe failure on Governor valves
East Bend 2 | U1 | January |  | 0.6 | 0.6 | 0.6 | 2022-01-20 05:04 | 2022-01-20 05:40 | Feedwater trip
East Bend 2 | MO | February | 73.567 |  | 73.567 | 73.567 | 2022-02-01 04:24 | 2022-02-04 05:58 | 2-2 SAH Basket failure
East Bend 2 | U1 | February |  | 10.133 | 10.133 | 10.133 | 2022-02-08 07:28 | 2022-02-08 17:36 | 2-2 preheat coil pump failure caused low voltage and tripped 2 out of 3 feeders
East Bend 2 | MO | April | 406.7 |  | 406.7 | 406.7 | 2022-04-20 05:34 | 2022-05-07 04:16 | Spring Maintenance Outage- Secondary Air Heater baskets and FGD duct work/ misc. C
Woodsdale CT-1 | PO | December | 83.233 |  | 83.233 | 83.233 | 2021-12-11 11:00 | 2021-12-14 22:14 | Perform Eddy Current Testing on row 4 turbine blades.
Woodsdale CT-1 | PO | March | 178.85 |  | 178.85 | 178.85 | 2022-03-18 10:00 | 2022-03-25 20:51 | Boroscope inspection
Woodsdale CT-1 | MO | April | 204.967 |  | 204.967 | 204.967 | 2022-04-06 10:00 | 2022-04-14 22:58 | TB39 Bank Ourage to find GT1 Bus Ground
Woodsdale CT-2 | SF | January |  | 1.5 | 1.5 | 1.5 | 2022-01-07 12:45 | 2022-01-07 14:15 | Starting Breaker would not close.
Woodsdale CT-2 | U1 | March |  | 3.05 | 3.05 | 3.05 | 2022-03-15 13:12 | 2022-03-15 16:15 | Rotor bar stopped
Woodsdale CT-2 | PO | March | 178.817 |  | 178.817 | 178.817 | 2022-03-18 10:00 | 2022-03-25 20:49 | Boroscope inspection
Woodsdale CT-2 | MO | April | 204.967 |  | 204.967 | 204.967 | 2022-04-06 10:00 | 2022-04-14 22:58 | TB39 Bank Outage to find GT1 Bus Ground
Woodsdale CT-3 | U1 | November |  | 14.333 | 14.333 | 14.333 | 2021-11-12 02:11 | 2021-11-12 16:31 | Low SF6 Gas in 1504 Breaker (OMC)
Woodsdale CT-3 | PO | March |  |  |  |  | 2022-03-18 10:00 |  | Generator Field Rewind
Woodsdale CT-4 | U1 | November |  | 14.333 | 14.333 | 14.333 | 2021-11-12 02:11 | 2021-11-12 16:31 | Low SF6 Gas in 1504 Breaker (OMC)
Woodsdale CT-4 | SF | January |  | 1.683 | 1.683 | 1.683 | 2022-01-23 08:30 | 2022-01-23 10:11 | Gen Exciter Synchronizer blocked.
Woodsdale CT-4 | PO | March | 178.8 |  | 178.8 | 178.8 | 2022-03-18 10:00 | 2022-03-25 20:48 | Boroscope inspection
Woodsdale CT-4 | PO | March | 58 |  | 58 | 58 | 2022-03-30 13:00 | 2022-04-01 23:00 | Opened Bank 1602 to move crane for GT3 Gen lift.
Woodsdale CT-5 | U1 | December |  | 1.217 | 1.217 | 1.217 | 2021-12-08 01:03 | 2021-12-08 02:16 | Exhaust TC Temp Spread High Trip
Woodsdale CT-5 | U1 | December |  | 29.883 | 29.883 | 29.883 | 2021-12-21 09:25 | 2021-12-22 15:18 | Variable Inlet Guide Vanes problem.
Woodsdale CT-5 | PO | April | 126.633 |  | 126.633 | 126.633 | 2022-04-23 10:00 | 2022-04-28 16:38 | Boroscope inspection
Woodsdale CT-6 | SF | November |  | 3.917 | 3.917 | 3.917 | 2021-11-05 09:55 | 2021-11-05 13:50 | Synchronizer problem
Woodsdale CT-6 | U1 | November |  | 1.6 | 1.6 | 1.6 | 2021-11-11 14:03 | 2021-11-11 15:39 | Failed start, fuel oil preheater did not come on
Woodsdale CT-6 | U1 | March |  | 5.567 | 5.567 | 5.567 | 2022-03-29 10:00 | 2022-03-29 15:34 | Rotor bar stopped.
Woodsdale CT-6 | PO | April | 129.2 |  | 129.2 | 129.2 | 2022-04-23 10:00 | 2022-04-28 19:12 | Boroscope inspection
Event Type Legend:
PO | Planned Outage
PE | Planned Outage Extension
MO | Maintenance Outage
ME | Maintenance Outage Extension
U1 | Unplanned (Forced) Outage – Immediate
U2 | Unplanned (Forced) Outage – Delayed
U3 | Unplanned (Forced) Outage – Postponed
SF | Startup Failure