## RFQ responses
| Action | Completion Date
| RFP Release | 2021-11-09
| Pre-Proposal Conference Calls | Per request
| RFP Inquiries Deadline | 2022-01-28
| Proposal Submission Deadline – 4:00 P.M. (Eastern) | 2022-02-04
| Responses Evaluated | 2022-06-15
| Notice of Award | TBD
| Contract Negotiations/Contract Execution/Notice to Proceed | TBD
| Desired Project Completion (System Installed, Tested, Functional and Accepted by Inter-County Energy) | 2025-12-31
Landis + Gyr
| 1.1.1 General System Requirements | YES | NO | Yes | No | Notes
1 | The AMI System can be deployed using an in house non-hosted model. |  |  | X
2 | The AMI System can be deployed using Microsoft SQL. |  |  | X
3 | The AMI System can be deployed using Oracle. |  |  | X
4 | The AMI System can be used by multiple browsers. |  |  | X
5 | The AMI System supports the use of iPad’s for in field viewing of system. |  |  | X
6 | Currently provides Pre-Pay functionality. |  |  | X
7 | Currently provides distribution automation functionality. |  |  | X
8 | The AMI System provides/allows for member load control. |  |  | X
9 | The AMI System fully supports Multispeak 3. |  |  | X
10 | The AMI System fully supports Multispeak 4. |  |  |  | X
| 1.1.1 All Electric Meters | YES | NO | YES | NO
11 | Meter has nonvolatile data storage capable of storing up to 30 days of 15-minute interval data. |  |  | X
12 | Support for ANSI Reading and Programming Standards C12.18. |  |  | X
13 | Support for ANSI Reading and Programming Standards C12.19. |  |  | X
14 | Support for ANSI Reading and Programming Standards C12.22. |  |  | X
15 | Approval of Underwriters Laboratories (UL). |  |  | X
16 | Compliant to UL 2735 Standard for Safety, Electric Utility Meters. |  |  | X
17 | Meter has ability to report auto detection of zero use. |  |  | X
18 | Meter has ability to be programmed to meter bi-directional energy. The meter has two registers (delivered and received) for this operation and the registers are synced to a clock. |  |  | X
19 | The meter display has an alphanumeric display and a watt disk emulator that provides both direction and magnitude of energy registration. |  |  | X
20 | Meter has the ability to report tamper detection including reverse consumption, tilt, and unexpected consumption/diversion. |  |  | X
21 | Meter has backup battery. |  |  |  | X
22 | Meter has optional super capacitor as alternative to the backup battery. |  |  | X
23 | The meter’s voltage reporting/ monitoring capability is guaranteed by the manufacturer to have +/- .5 volts accuracy of applied voltage as compared to a standard verified against NIST. |  |  | X
24 | The meter is built to function according to ANSI C12.1 Meter Temperature Requirements with a range of -40°F to +185°F. |  |  | X
25 | Meter has the ability to capture a log of up to 200 events (alerts, diagnostics, cautions, communication and meter operations). |  |  | X
26 | Meter & Module have documented mfg. lifecycle of at least 10 years. |  |  | X
27 | Meter has built in functionality to communicate with other equipment to allow member load control. |  |  | X
28 | Meter has current limiting functionality. |  |  | X
29 | Meter has the ability to detect and report voltage fluctuations and send alarm notifications within 3 minutes. |  |  | X
30 | The meter’s voltage monitoring supports measurements of instantaneous voltage data (line-to-line and line-to-neutral) up to three phases depending on meter form. |  |  | X
| 1.1.2 Single Phase Electric Meters | YES | NO | YES | NO
31 | Meter Includes safety button/switch for reconnects. |  |  | X
32 | Meter has ability to collect and report TOU metering measures, Critical Peak, Peak Rebate & Real-Time Usage. |  |  | X
33 | The meter is capable of rolling demand with the minimal capability to roll 5 into 15-minute demand intervals. |  |  | X
| 3.2.4 Poly Phase Electric Meters | YES | NO | YES | NO
34 | Meters proposed to meet specification also report KVA with no additional cost. |  |  | X
35 | Meter has ability to report TOU metering measures, Critical Peak, Peak Rebate & Real-Time Usage. |  |  | X
36 | The meter is capable of rolling demand with the minimal capability to roll 5 into 15-minute demand intervals. |  |  | X
37 | Meter has capability of showing instantaneous demand measurement on display. |  |  | X
38 | Meter is capable of providing Power Factor at peak KW |  |  | X
| 3.2.5 General Network & Meter Data Requirements | YES | NO | YES | NO
39 | AMI System included is capable of capturing all meter errors and events aligned with IEC 61698-9 and can forward these to the integration platform allowing external systems to subscribe to required data in near real-time. |  |  | X
40 | The AMI System supports measurement of other power quality data including RMS voltage/current, over/under voltage, sag/swell, voltage imbalance, and under frequency alerts. |  |  | X
41 | The AMI System provides aggregate daily meter reads to the integration bus to provide scheduled Revenue Residential Electric Meter Reads and is capable of providing 15-minute interval data, delivered at minimum every 4 hours. |  |  | X
42 | The AMI System provides aggregate daily meter reads to the integration bus to provide scheduled commercial electric meter reads and is capable of providing 15-minute interval data, delivered at minimum every 4 hours. |  |  | X
43 | The AMI System provides aggregate daily meter reads to the integration bus in kWh, KW, kvar, TOU, KVA, Power Factor and Demand Data. |  |  | X
44 | Within a selected meter type, Inter-County Energy may desire to utilize different interval durations for endpoints. The AMI solution provides capabilities that allow different groups of meters to be configured at 5, 15 & 30 minute or other intervals. |  |  | X
45 | The AMI System can perform “Gap-filling” to ensure the maximum number of reads are received from the field to minimize the use of VEE in filling meter data gaps by the MDMS. |  |  | X
46 | The AMI System provides an on request (real-time) reading service that allows for retrieval of available meter reading data across the entire population of meters, including the most recent data stored. The following data is available on an “On-Request Meter Reading” query: |  |  | X
| a. Date and time of reading |  |  | X
| b. Meter number |  |  | X
| c. Cumulative kWh read |  |  | X
| d. Voltage |  |  | X
| e. Power Factor at peak KW (where available on meter) |  |  | X
| f. KW Demand (must be programmable up to a total of six digits) |  |  | X
| g. Remote disconnect status |  |  | X
47 | On-Request (Real Time) Meter Reading – meters respond within 15 seconds. |  |  | X
48 | System is capable of generating temperature alert. |  |  | X
49 | 1.2.6 General Billing Data | YES | NO | YES | NO
50 | System has ability to provide billing determinants supporting batch scheduled meter read delivery based on a configurable billing cycle schedule, off-cycle bills, and a final bill process. |  |  | X
51 | Peak demand reset can be performed to coincide with the billing determinant delivery. |  |  | X
52 | The AMI System utilizes a web-based utility portal allowing Inter-County Energy to access each included sub-system using a single sign-on methodology integrated to Inter-County Energy’s Active Directory authentication system. |  |  | X
53 | Service Oriented Architecture (SOA) integration adheres to NERC/CIP security compliance. |  |  | X
54 | System uses secure file-based integration utilizing file transfer over https, sFTP, SCP, or FTPs. |  |  | X
55 | 3.2.7 AMI System Features | YES | NO | YES | NO
56 | The AMI System does not require a network path that traverses infrastructure that is not reliably backed up. For example, hopping through non-battery backed up end devices. |  |  | X
57 | The AMI System is capable of remote, over-the-air support firmware upgradeability to system devices without affecting the normal operations of system such as regularly scheduled data retrieval. |  |  | X
58 | The AMI System does not require any changes or additional infrastructure in case of consumer “opt out” scenarios. |  |  | X
59 | The AMI System supports accurate time stamping. |  |  | X
60 | The AMI infrastructure supports optional packaging of the Local Area Network radio and Wide-area Network private, wireless data backhaul in a single enclosure, where the AMI backhaul is also capable of supporting near-real time Distribution Automation applications such as Capacitor Bank Control, Reclosers, Fault Detection Isolation and Recovery, etc. |  |  | X
61 | The AMI System supports the following security attributes: |  |  | X
| a. Mutual entity authentication of all devices throughout the system |  |  | X
| b. Message authentication using AES 128 based CMAC or similar. |  |  | X
| c. Message confidentiality of the application data using at least AES 128-bit encryption |  |  | X
| d. Message confidentiality of the link layer using 3-key Triple DES or similar |  |  | X
| e. Limited anonymity by not disclosing the Meter ID over the air |  |  | X
| f. Verification of authentic firmware upgrade. |  |  | X
| g. Symmetric key algorithms with no over-the-air key exchange |  |  | X
| h. SSL encryption for backend IP-infrastructure |  |  | X
| i. Device keys shall be securely provisioned during manufacturing |  |  | X
62 | Capable of integration with Security Light controls. |  |  | X
63 | Will the system export data to Google Earth? |  |  | X
64 | After the AMI infrastructure is installed, meters within the coverage area are “plug-and-play” and do not require any processes or additional configuration after being powered on. |  |  | X
65 | Does the system perform “self-healing” functions? |  |  | X
66 | The network infrastructure supports two-way communication to multiple types of field device endpoints including electric meters. |  |  | X
67 | The devices on the network avoid connection redundancy by finding primary and alternate AMI infrastructure devices upon installation.
68 | Does the AMI System require licensed frequencies for operation? |  |  |  | X
If yes, does Inter-County Energy have to acquire and own license?
69 | All device emissions levels are significantly under FCC OET Bulletin 65 guidelines even if device is stuck in transmitting mode. |  |  | X
70 | Does the system support Phase detection? |  |  | X
71 | 3.2.8 Outage Notification and Monitoring Requirements | YES | NO | YES | NO
72 | The system will not false alarm on a momentary outage event. Duration for momentary outage is a parameter that Inter-County Energy can set. |  |  | X
73 | System will provide restoration notice after power has been restored. |  |  | X
74 | The system provides full integration with Futura’s OMS and SEDC’s CIS/MDM systems. |  |  | X
75 | Last gasp performance does not degrade in the case of a large grid outage. |  |  | X
76 | Minimum and maximum durations for meter to switch to secondary path if primary signal path is lost. |  |  | X
77 | Restoration performance (i.e. the amount of time that it takes for a restored meter to report restoration) does not degrade in the case of a large grid outage. |  |  | X
78 | The system detects an outage or power loss on monitored meters. When an outage is detected the system will: |  |  | X
| A. Notify a designated Inter-County Energy representative |  |  | X
| B. Update GIS map with current status |  |  | X
| C. Update status on a map |  |  | X
| D. Log outage information in the system. |  |  | X
79 | Inter-County Energy will have the ability to obtain status of meters within the electrical network (ping); response will be received in 15 seconds or less. |  |  | X
80 | During power restoration the AMI head-end receives and forwards all power up notifications. |  |  | X
81 | Does the system provide a real time status map? |  |  | X
82 | The system provides trouble shooting capabilities such as:
| a. Current Meter route |  |  | X
| b. Real time trace |  |  | X
| c. Neighbor listing |  |  | X
| Log outage information in the system. |  |  | X
83 | Polling accuracy of routers and collectors greater than 99%. |  |  | X
| 3.2.9 Asset Monitoring Functionality Requirements | YES | NO | YES | NO
84 | The system provides visualization of the wireless communications network during operation. |  |  | X
85 | Head-end System will store GPS and required data to link the meter to SEDC’s Meridian. |  |  | X
86 | System can update meter status on Inter-County Energy’s monitoring and mapping screen. |  |  | X
87 | Head-end System can display meter problems/communication problems. |  |  | X
88 | Inter-County Energy will have the ability to query each meter from Head-end System for detailed information. |  |  | X
| 4.2.1 Meter Installation/ End of Life Testing Requirements | YES | NO | YES | NO
89 | GPS data on installed meter will be provided without additional cost. |  |  |  |  | NO QUOTE
90 | Digital images of the in meter and the out meter are available. |  |  |  |  | NO QUOTE
91 | Naming convention for image files will be by Inter-County Energy meter number. |  |  |  |  | NO QUOTE
92 | Vendor trains all employees in safety, customer relations, hazardous conditions, and identification of meter tampering. |  |  |  |  | NO QUOTE
93 | Meter jaw tension testing |  |  |  |  | NO QUOTE
| 5.2.1 Meter Data Management System Requirements | YES | NO | YES | NO
94 | The MDMS supports time dynamic pricing (TOU, Critical Peak, Peak Rebate, Real-time Pricing) and load control rebate rates, inclining block rate, Bi-directional, and demand side management elements. |  |  |  |  | HARRIS SMART WORKS
95 | The MDMS supports Prepayment (pay-as-you-go). |  |  |  |  | HARRIS SMART WORKS
96 | The MDMS has the capability to aggregate usage across multiple meters. |  |  |  |  | HARRIS SMART WORKS
97 | The MDMS will receive, validate, estimate and edit AMI collected meter readings for every meter, every day, to ensure accurate billing data. |  |  |  |  | HARRIS SMART WORKS
98 | The MDMS tracks which intervals have been provided for billing and supports exception processes for subsequent edits or replacements of the data. |  |  |  |  | HARRIS SMART WORKS
| 6.2.1 Meter Data Management System Requirements | YES | NO | YES | NO
99 | The MDMS captures and stores all meter events that are provided by the AMI System. |  |  |  |  | HARRIS SMART WORKS
100 | The MDMS has the capability to identify unauthorized consumptions extracted from the AMI System status and alerts and from disconnect status information extracted from the existing SEDC Meridian system. |  |  |  |  | HARRIS SMART WORKS
101 | The MDMS has the capability to identify theft of service as indicated by AMI status and alerts extracted from the AMI System. |  |  |  |  | HARRIS SMART WORKS
102 | The MDMS stores meter read intervals in the increment supplied by the meter: 5 min, 15 min, 30 min, hourly, daily, monthly from AMI System. |  |  |  |  | HARRIS SMART WORKS
103 | The MDMS supports consumer lifecycle-move in/move out, disconnect/ connect at pole, disconnect/connect at meter. |  |  |  |  | HARRIS SMART WORKS
104 | All reads that are presented to the consumer through NISC’s MDM must be validated through the MDMS before presentation. |  |  |  |  | HARRIS SMART WORKS
105 | The MDMS supports the meter provisioning process through SEDC Meridian. |  |  |  |  | HARRIS SMART WORKS
106 | The MDMS has the capability to store latitude and longitude coordinates for meter location. |  |  |  |  | HARRIS SMART WORKS
107 | The MDMS provides the capability for users to create new validation and estimation rules. |  |  |  |  | HARRIS SMART WORKS
108 | The MDMS includes validation rules such as sum check, spike check, kvar check, hi-lo check, and missing data check. |  |  |  |  | HARRIS SMART WORKS
109 | The MDMS has the flexibility to apply validation and estimation rules to various configured groups. |  |  |  |  | HARRIS SMART WORKS
110 | The MDMS allows configuration thresholds and boundaries for estimation on specific accounts by meter/consumer, group, tariff/rate, or service provider. |  |  |  |  | HARRIS SMART WORKS
111 | The MDMS provides reports on edited interval data, including original and new values, reason, process, and user. |  |  |  |  | HARRIS SMART WORKS
112 | The MDMS adjusts meter estimates based on recent interval values that are received after the fact to ensure accurate billing data. |  |  |  |  | HARRIS SMART WORKS
113 | The MDMS has the ability to perform line loss analysis. |  |  |  |  | HARRIS SMART WORKS
114 | The MDMS allows line loss analysis to be broken down by substation and feeder. |  |  |  |  | HARRIS SMART WORKS
115 | The MDMS has the ability to perform transformer loading analysis. |  |  |  |  | HARRIS SMART WORKS

## Pricing
Yellow designates revised bid pricing: |  |  |  |  | Yellow designates revised bid pricing:
240
QUOTES FROM VENDORS:
L+G
|  | qnty | $ each | Extended |  |  | Extended
COLLECTOR NETWORK
0
| Network Gateway Radio & Modem | 31 | 4800 | 148800 |  |  | 0
| RF Router | 460 | 1545 | 710700 |  |  | 0
| Qnty Tool Kits? More recommended |  |  | 0 |  |  | 0
| RF tool TechStudio Software Lic/user | 3 | 1100 | 3300 |  |  | 0
| RF tool TechStudio An Maint /license | 3 | 220 | 660 |  |  | 0
| Field Tool Kit | 3 | 1600 | 4800 |  |  | 0
0
0
0
0
0
|  |  |  | 868260 |  |  | 0
|  |  |  | 0 |  |  | 0
|  |  |  | 0 |  |  | 0
| NETWORK SERVER & SOFTWARE |  |  | 0 |  |  | 0
| Command Center Monthly software | 12 | 3570 | 42840 |  |  | 0
| based on 27020 points |  |  | 0 |  |  | 0
| ?? Annual Maint fee ^ ?? |  |  | 0 |  |  | 0
|  |  |  | 0 |  |  | 0
|  |  |  | 0 |  |  | 0
|  |  |  | 0 |  |  | 0
|  |  |  | 42840 |  |  | 0
|  |  |  | 0 |  |  | 0
|  |  |  | 0 |  |  | 0
| SERVICES |  |  | 0 |  |  | 0
| Project Delivery Services | 1 | 69000 | 69000 |  |  | 0
|  |  |  | 0 |  |  | 0
| RF Training | 1 | 27000 | 27000 |  |  | 0
0
|  |  |  | 96000 |  |  | 0
METERS
| RF FOCUS AXE-SD | 26566 | 125 | 3320750 |  |  | 0
|  |  |  | 0 |  |  | 0
| RF S4X (Forms 5,6,8,9,12,16) | 454 | 285.7 | 129707.8 |  |  | 0
| Note no Form 4S |  |  | 0 |  |  | 0
|  |  |  | 0 |  |  | 0
|  |  |  | 0 |  |  | 0
|  |  |  | 0 |  |  | 0
|  |  |  | 0 |  |  | 0
|  |  |  | 3450457.8 |  |  | 0
| Customer Loyalty Discount |  |  | -25000 |  |  | 0
|  |  |  | 0 |  |  | 0
|  |  |  | 4432557.8 |  |  | 0
|  |  |  | 0 |  |  | 0
|  |  |  | 0 |  |  | 0
|  |  |  | 0 |  |  | 0
(Above)
|  |  |  | 5181897.8 |  |  | 0
OPTIONS:
| AGA Project Delivery Services | 1 | 50000 | 50000 |  |  | 0
| AGA Asset Loading | 1 | 800 | 800 |  |  | 0
| AGA Voltage Visualization | 1 | 800 | 800 |  |  | 0
| AGA Capacity Contribution | 1 | 800 | 800 |  |  | 0
| AGA Revenue Protection | 1 | 800 | 800 |  |  | 0
| AGA Meter Analytics + Montly SaaS Fee | 12 | 3590.07 | 43080.84 |  |  | 0
| AGA Meter Analytics + Ann. Subscrip. Fee | 1 | 6933.33 | 6933.33 |  |  | 0
| Street Light Controller | 100 | 174 | 17400 |  |  | 0
| Premium Support Service yr 1 | 28003 | 1.2 | 33603.6 |  |  | 0
| Premium Support Service yr 2 | 28003 | 1.3 | 36403.9 |  |  | 0
| Premium Support Service yr 3 | 28003 | 1.4 | 39204.2 |  |  | 0
|  |  |  | 0 |  |  | 0
|  |  |  | 0 |  |  | 0
| NEMA 3R enclosures | 31 | 900 | 27900 |  |  | 0
| Router Arms | 460 | 100 | 46000 |  |  | 0
|  |  |  | 0 |  |  | 0
| Meter Swap turn key w SEDC integration |  |  | 0 |  |  | 0
| Mat. & Labor Est. for gateways | 31 | 3000 | 93000 |  |  | 0
| Mat. & Labor Est. for Routers | 460 | 1250 | 575000
| Using ACLARA Cellular Backhaul 250MB | 31 | 240 | 7440
|  |  |  | 749340 |  |  | 0
L+G
300 AMI customers
20+ million devices
1 watt power
24MB memory in devices
2017 became a publicly traded company
Self Find system
RF 900-928 MHz unlicensed
200 Kbps data rate
Remote configuration capability
Remote firmware upgrade capability
95% on demand read accuracy
99.9% billing delivery over 72 hrs
2 hop average design / Max 6 hops
Supports RS232,RS485,DNP3, Modbut, and IP
Focus Meters
320 disconnect available
Zigbee 2.4 Ghz included in home communications ready
Capable of collecting internal meter temperature
45' Gateway mounting heights at Substations
20' Gateway mounting heights on poles
20' router mounting height
Gateway will support 5,000 meters at 88% capacity
Gateways require either Ethernet or cellular connection
50 month equipment warranty
Integrates w SEDC/CRC/Futura
Brooks has a single meter base guts block replacement during meter chgs
May need hand tools for terminating cables
Security lt arms are $100 on 3/30/22
Note on AH71: Andy White's email says cell service included above. If more than 24hr downloads/meter occur then the fee is $8/mtr/month. Estimate is probably high here.
Note on M84: David Phelps: Tim $885 - 2'x3' via Irby 6/2/22
Note on M85: David Phelps: From Tim - $75 via Irby 6/2/22

## 15 year cost
Landis & Gyr
2022-05-31
| Year 1 | Year 2 | Year 3 | Year 4 | Year 5 | Year 6 | Year 7 | Year 8 | Year 9 | Year 10 | Year 11 | Year 12 | Year 13 | Year 14 | Year 15 | Totals
Collector Network | 868260 | [14 empty] | 868260
Network Server & Software | 42840 | 43957 | 45275.71 | 46633.9813 | 48033.0007 | 49473.9908 | 50958.2105 | 52486.9568 | 54061.5655 | 55683.4125 | 57353.9148 | 59074.5323 | 60846.7683 | 62672.1713 | 64552.3364 | 793903.5512
Project Delivery Services | 96000 | [14 empty] | 96000
Meters | 1725228.9 | 1725228.9 | [13 empty] | 3450457.8
Discount | -25000 | [14 empty] | -25000
Cellular | 7440 | 7440 | 7440 | 7440 | 7440 | 7663.2 | 7893.096 | 8129.8889 | 8373.7855 | 8624.9991 | 8883.7491 | 9150.2616 | 9424.7694 | 9707.5125 | 9998.7379 | 125049.9999
Options/Extras | 741900 | [14 empty] | 741900
Annual Costs: | 3456668.9 | 1776625.9 | 52715.71 | 54073.9813 | 55473.0007 | 57137.1908 | 58851.3065 | 60616.8457 | 62435.351 | 64308.4116 | 66237.6639 | 68224.7938 | 70271.5377 | 72379.6838 | 74551.0743 | 6050571.3511
15 year cost: | 6050571.3511
Options/Extras included above:
NEMA 3R enclosures
Router Arms
Meter Swap turn key w SEDC integration
Mat. & Labor Est. for gateways
Mat. & Labor Est. for Routers