## Capital
CONFIDENTIAL INFORMATION REDACTED
2020-02-11
| M501JAC | F Class Peaker | 2X F Class | Notes
| 2020-01-01 | 2020-01-01 | 2020-01-01
Capacity MW | 585 | 220 | 440 | New & Clean
Capacity MW Ave Life | 568.152 | 213.664 | 427.328 | Degraded
$/kW
EPC Cost (,000) |  |  |  | Peaker scaled from 2 unit estimate
Options
Gas Compression
SCR to 2 ppm Nox |  |  |  | NGCC BACT for Nox
Ti Condenser
EPC Cost W/ Options (,000)
Owner's Cost
Project Development |  |  |  | Developed from CR7 Experience |  |  | CR7 Actual | 1748
T Line Relocation |  |  |  | Developed from CR7 Experience |  |  | CR7 Actual | 11471
Elec Direct Interconection |  |  |  | Developed from CR7 Experience |  |  | CR7 Actual | 2435
NG Pipeline |  |  |  | Developed from CR7 Experience |  |  | CR7 Actual | 30038
NG FO&M Start-up period |  |  |  | Estimate for firm gas transport on interstate PL
Const. Power |  |  |  | Developed Fr. 4-22-16 HDR Report
Const Power Infrastructure |  |  |  | Developed Fr. 4-22-16 HDR Report
Owner's Operators Prior COD |  |  |  | Developed from CR7 Experience |  |  | CR7 Actual | 5047
Owner's Project Management |  |  |  | Developed from CR7 Experience |  |  | CR7 Actual | 8196
Owner's Engineer |  |  |  | Developed from CR7 Experience |  |  | CR7 Actual | 2572
Owner's Legal |  |  |  | Developed from CR7 Experience |  |  | CR7 Actual | 619
Operator Training |  |  |  | Developed Fr. 4-22-16 HDR Report |  |  |  | 280
Startup & Testing Net Cost |  |  |  | inc. VO&M Water Chem fr 4-22-16 HDR Report
Site Security |  |  |  | Developed Fr. 4-22-16 HDR Report
LTSA Initial Payment |  |  |  | Developed Fr. 4-22-16 HDR Report
Perm Plant Eq. & Furn. |  |  |  | Developed from CR7 Experience |  |  | CR7 Actual | 2856
IT & Telecom |  |  |  | Developed Fr. 4-22-16 HDR Report
NERC Cyber Security |  |  |  | Rapidly evolving requirement
Prop. Tax during Const. |  |  |  | Developed by consullting LG&E Tax Dept for CR7
Sales Tax |  |  |  | Developed by consullting LG&E Tax Dept for CR7
Total Owner's Cost
Owner's Cost Contingency
Owner's EPC Contingency
Total Owner's Cost & Cont.
Owner's Cost % of EPC
Total Project Cost | 617100 | 168465 | 259325
$/kW | 1086.153 | 788.4576 | 606.8523
| 2019 NREL ATB Real $/kW (2017$) |  |  |  | 2019 NREL ATB Nominal $/kW
Year | NGCC | NGCC | SCCT |  | NGCC | NGCC | SCCT
2019 | 893.5582 | 893.5582 | 896.2936 |  | 929.658 | 929.658 | 932.5039
2020 | 887.1186 | 887.1186 | 902.7138 |  | 941.4173 | 941.4173 | 957.9671
2021 | 880.6789 | 880.6789 | 891.8617 |  | 953.2752 | 953.2752 | 965.3798
2022 | 874.2393 | 874.2393 | 885.2088 |  | 965.2308 | 965.2308 | 977.342
2023 | 860.9934 | 860.9934 | 867.7605 |  | 969.6184 | 969.6184 | 977.2393
2024 | 854.3285 | 854.3285 | 859.6886 |  | 981.3549 | 981.3549 | 987.512
2025 | 851.0011 | 851.0011 | 854.8936 |  | 997.0834 | 997.0834 | 1001.6441
2026 | 847.6053 | 847.6053 | 850.1477 |  | 1012.9667 | 1012.9667 | 1016.0052
2027 | 844.0261 | 844.0261 | 845.3332 |  | 1028.8631 | 1028.8631 | 1030.4565
2028 | 840.9638 | 840.9638 | 841.6625 |  | 1045.6328 | 1045.6328 | 1046.5015
2029 | 836.1832 | 836.1832 | 836.2827 |  | 1060.4825 | 1060.4825 | 1060.6087
2030 | 833.4704 | 833.4704 | 833.2917 |  | 1078.1828 | 1078.1828 | 1077.9516
2031 | 830.954 | 830.954 | 830.5755 |  | 1096.4261 | 1096.4261 | 1095.9267
2032 | 827.5466 | 827.5466 | 826.7715 |  | 1113.7687 | 1113.7687 | 1112.7256
2033 | 824.8677 | 824.8677 | 823.8682 |  | 1132.3666 | 1132.3666 | 1130.9945
2034 | 822.558 | 822.558 | 821.2067 |  | 1151.7798 | 1151.7798 | 1149.8877
2035 | 819.5666 | 819.5666 | 818.0247 |  | 1170.5429 | 1170.5429 | 1168.3407
2036 | 816.7137 | 816.7137 | 814.8851 |  | 1189.7977 | 1189.7977 | 1187.1337
2037 | 814.1077 | 814.1077 | 812.193 |  | 1209.7213 | 1209.7213 | 1206.8761
2038 | 812.3713 | 812.3713 | 810.5601 |  | 1231.2839 | 1231.2839 | 1228.5387
2039 | 810.2019 | 810.2019 | 808.4952 |  | 1252.5557 | 1252.5557 | 1249.9171
2040 | 808.1344 | 808.1344 | 806.5318 |  | 1274.3465 | 1274.3465 | 1271.8194
2041 | 806.8998 | 806.8998 | 805.3998 |  | 1297.8476 | 1297.8476 | 1295.435
2042 | 803.8455 | 803.8455 | 802.4515 |  | 1318.7938 | 1318.7938 | 1316.5067
2043 | 803.0307 | 803.0307 | 801.7388 |  | 1343.8062 | 1343.8062 | 1341.6442
2044 | 800.1487 | 800.1487 | 798.9621 |  | 1365.763 | 1365.763 | 1363.7377
2045 | 799.1572 | 799.1572 | 798.0732 |  | 1391.3521 | 1391.3521 | 1389.4648
2046 | 796.5878 | 796.5878 | 795.6086 |  | 1414.6163 | 1414.6163 | 1412.8773
2047 | 794.7605 | 794.7605 | 793.885 |  | 1439.5986 | 1439.5986 | 1438.0128
2048 | 792.9203 | 792.9203 | 792.1487 |  | 1464.9907 | 1464.9907 | 1463.5651
2049 | 791.0095 | 791.0095 | 790.3418 |  | 1490.6896 | 1490.6896 | 1489.4311
2050 | 783.0167 | 783.0167 | 782.4572 |  | 1505.1393 | 1505.1393 | 1504.0638
Nominal CAGR (2019-2026) |  |  |  |  | 1.234% | 1.234% | 1.233%
Nominal CAGR (2026-2050) |  |  |  |  | 1.664% | 1.664% | 1.648%
[5 empty] | 1x1 NGCC | Single SCCT | Multiple SCCT
$/kW Scaled to 2026 NREL Build, 2026$ |  |  |  |  | 1192.0766 | 865.3494 | 656.4906
$/kW Using Long-Term NREL Escalation Rate, 2019$ |  |  |  |  | 1062.0449 | 770.9571 | 585.5139

## Fixed O&M
Fixed O&M
| NGCC | SCCT
NREL 2019 ATB Fixed O&M ($/kW-yr, 2017$) | 10.56 | 12.23
NREL 2019 ATB Fixed O&M ($/kW-yr, 2019$) | 10.9866 | 12.7241

## Firm Gas Transport
Trimble County Gas Turbines + Plant | 2019 | April | May | June | July | August | September | October
Summer | SNS Capacity | 110000 | 110000 | 110000 | 110000 | 110000 | 110000 | 110000
| Demand | 0.355 | 0.355 | 0.355 | 0.355 | 0.355 | 0.355 | 0.355
| Daily Charge | 39050 | 39050 | 39050 | 39050 | 39050 | 39050 | 39050
| Days in Month | 30 | 31 | 30 | 31 | 31 | 30 | 31
| Monthly Charge | 1171500 | 1210550 | 1171500 | 1210550 | 1210550 | 1171500 | 1210550
| 2019 | April | May | June | July | August | September | October
| STF Capacity | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000
| Demand | 0.2856 | 0.2856 | 0.2856 | 0.2856 | 0.2856 | 0.2856 | 0.2856
| Daily Charge | 14280 | 14280 | 14280 | 14280 | 14280 | 14280 | 14280
| Days in Month | 30 | 31 | 30 | 31 | 31 | 30 | 31
| Monthly Charge | 428400 | 442680 | 428400 | 442680 | 442680 | 428400 | 442680
Trimble County Gas Turbines + Plant | 2019 | Jan | Feb | Mar | Nov | Dec
Winter | WNS Capacity | 228000 | 228000 | 113500 | 114500 | 229000
| Demand | 0.5 | 0.5 | 0.185 | 0.185 | 0.5
| Daily Charge | 114000 | 114000 | 20997.5 | 21182.5 | 114500
| Days in Month | 31 | 28 | 31 | 30 | 31
| Monthly Charge | 3534000 | 3192000 | 650922.5 | 635475 | 3549500
Cane Run + Paddys Run | Demand | April | May | June | July | August | September | October
Summer | SNS Capacity | 72000 | 72000 | 72000 | 72000 | 72000 | 72000 | 72000
| Demand | 0.3425 | 0.3425 | 0.3425 | 0.3425 | 0.3425 | 0.3425 | 0.3425
| Daily Charge | 24660 | 24660 | 24660 | 24660 | 24660 | 24660 | 24660
| Days in Month | 30 | 31 | 30 | 31 | 31 | 30 | 31
| Monthly Charge | 739800 | 764460 | 739800 | 764460 | 764460 | 739800 | 764460
Cane Run + Paddys Run | Demand | April | May | June | July | August | September | October
Summer | STF Capacity | 34000 | 34000 | 34000 | 34000 | 34000 | 34000 | 34000
| Demand | 0.19 | 0.19 | 0.19 | 0.19 | 0.19 | 0.19 | 0.19
| Daily Charge | 6460 | 6460 | 6460 | 6460 | 6460 | 6460 | 6460
| Days in Month | 30 | 31 | 30 | 31 | 31 | 30 | 31
| Monthly Charge | 193800 | 200260 | 193800 | 200260 | 200260 | 193800 | 200260
Cane Run + Paddys Run | 2019 | Jan | Feb | Mar | Nov | Dec
Winter | WNS Capacity | 107000 | 107000 | 107000 | 107000 | 107000
| Demand | 0.375 | 0.375 | 0.375 | 0.375 | 0.375
| Daily Charge | 40125 | 40125 | 40125 | 40125 | 40125
| Days in Month | 31 | 28 | 31 | 30 | 31
| Monthly Charge | 1243875 | 1123500 | 1243875 | 1203750 | 1243875
| Cane Run 7 / NGCC | Trimble County CTs / SCCT
Firm Gas Total (2019 Actual, 2019$) | 12718555 | 22974517.5
Average Max Capacity (MW) | 672.5 | 1014
Firm Gas ($/kW-yr, 2019$) | 18.9123 | 22.6573

## Start Cost
Escalation Rate (%) |  | 2%
Cost Year |  | 2019
| As-Spent $ | As-Spent Year | Cost Year $ | Source
TC6 MI #1 | 8162209 | 2010 | 9754595.3194 | Budget Actuals
TC5 MI #1 | 11131715 | 2011 | 13042578.3064 | Budget Actuals
TC8 MI #1 | 4323329 | 2011 | 5065468.98 | Budget Actuals
TC7 MI #1 | 4049066 | 2012 | 4651104.0816 | Budget Actuals
TC9 MI #1 | 3847708 | 2012 | 4419807.0329 | Budget Actuals
TC10 MI #1 | 3814905 | 2013 | 4296202.6441 | Budget Actuals
TC5 MI #2 | 5420850 | 2021 | 5210351.7878 | Projected from Bid Process
Average Expected MI Cost |  |  | 6634301.1646
TC6 HGP #1 | 3923977 | 2016 | 4164155.7842 | Budget Actuals
TC5 HGP #1 | 4078916 | 2017 | 4243704.2064 | Budget Actuals
TC7 HGP #1 | 4167543 | 2018 | 4250893.86 | Budget Actuals
TC9 HGP #1 | 4317446 | 2016 | 4581708.2348 | Expected Under Current Contract
TC8 HGP #1 | 3554101.0048 | 2016 | 3771640.4191 | Expected Under Current Contract
TC10 HGP #1 | 3554101.0048 | 2016 | 3771640.4191 | Expected Under Current Contract
Average Expected HGP Cost |  |  | 4130623.8206
New Combustion Hardware | 5840440.872 | 2016 | 6197922.5769 | GE Parts List w/ Discount Per Current Contract
New HGP Hardware | 15734229.768 | 2016 | 16697290.5036 | GE Parts List w/ Discount Per Current Contract
Parts Refurb Not Needed | -1618000 | 2021 | -1555171.088 | Line-Item of Parts Refurb from Current Contract
Rotor Refurb Cost | 7020800 | 2021 | 6748173.7793 | Estimate based on vendor feedback
| TC5-6 |  |  |  | TC7-10
| Cost Year $ |  |  |  | Cost Year $
Major Inspection #1 | 6634301.1646 |  |  | Major Inspection #1 | 6634301.1646
Hot Gas Path Inspection #1 | 4130623.8206 |  |  | Hot Gas Path Inspection #1 | 4130623.8206
Major Inspection #2 + Rotor Inspection (Total) | 38194768.63 |  |  | Hot Gas Path Inspection #2 (Total) | 28017732.3944
MI #2 Outage | 6634301.1646 |  |  | HGP #2 Outage | 4130623.8206
Parts Refurb Not Needed | -1555171.088 |  |  | Parts Refurb Not Needed | -1555171.088
New Combustion Hardware | 6197922.5769 |  |  | New Combustion Hardware | 6197922.5769
New HGP Hardware | 16697290.5036 |  |  | New HGP Hardware | 16697290.5036
Rotor Refurb | 6748173.7793 |  |  | Contingency (10%) | 2547066.5813
Contingency (10%) | 3472251.6936
Hot Gas Path Inspection #2 | 4130623.8206 |  |  | Major Inspection #2 + Rotor Inspection (Total) | 14720722.4383
|  |  |  | MI #2 Outage | 6634301.1646
|  |  |  | Rotor Refurb | 6748173.7793
|  |  |  | Contingency (10%) | 1338247.4944
Hot Gas Path Inspection #3 | 4130623.8206 |  |  | Hot Gas Path Inspection #3 | 4130623.8206
Total | 57220941.2564 |  |  |  | 57634003.6385
Estimated Starts In Usable Life | 5157.7657
Outage Costs Over Unit's Lifecycle | 57496316.1778
Outage Cost Per Start | 11147.5238
Average MW | 169
Outage Cost Per MWh On 12-hour Run At Max Load | 5.4968
Note on B23: Author: MI/HGP costs include parts refurbishing that will not be necessary in the outage where combustion and HGP hardware are being replaced
Note on C56: Author: plant estimate based on historical consumed rotor factored starts and the expected rotor life of 7,400 rotor factored starts
Note on C57: Author: weighted 2x for TC5-6 and 4x for TC7-10