## 2018
UnitName | EventType | CauseCode | EventStart | EventEnd | MW On Outage | Cause
TC2 | U1 | 1000 | 2018-01-01 | 2018-01-01 11:56 | 570 | Waterwall (Furnace wall)
TC7 | SF | 5130 | 2018-01-01 03:27 | 2018-01-01 12:45 | 179 | Starting system (including motor)
BR5 | SF | 5130 | 2018-01-02 07:58 | 2018-01-02 08:58 | 130 | Starting system (including motor)
BR6 | U1 | 5048 | 2018-01-02 09:06 | 2018-01-02 12:24 | 171 | Gas fuel system including controls and instrumentation
BR6 | U1 | 5248 | 2018-01-02 12:53 | 2018-01-02 18:40 | 171 | Gas Turbine Control System - logic problems
BR6 | U1 | 5248 | 2018-01-02 18:48 | 2018-01-02 19:15 | 171 | Gas Turbine Control System - logic problems
BR6 | U1 | 5248 | 2018-01-02 19:24 | 2018-01-03 10:17 | 171 | Gas Turbine Control System - logic problems
OF2 | U1 | 9135 | 2018-01-03 08:56 | 2018-01-11 15:24 | 12.58 | Lack of water
TC7 | U1 | 3681 | 2018-01-03 09:22 | 2018-01-03 15:01 | 179 | Other voltage circuit breakers
TC5 | U1 | 3681 | 2018-01-03 09:22 | 2018-01-03 15:01 | 179 | Other voltage circuit breakers
TC6 | U1 | 3681 | 2018-01-03 09:22 | 2018-01-04 20:29 | 179 | Other voltage circuit breakers
OF3 | U1 | 9135 | 2018-01-03 11:02 | 2018-01-05 10:03 | 12.58 | Lack of water
HA1 | U1 | 5510 | 2018-01-03 11:12 | 2018-01-03 12:12 | 13.6667 | Lube oil system
OF8 | U1 | 9135 | 2018-01-03 12:27 | 2018-01-04 13:53 | 12.58 | Lack of water
HA1 | U1 | 3610 | 2018-01-03 14:34 | 2018-01-03 16:43 | 13.6667 | Switchyard circuit breakers - external (not OMC)
HA2 | SF | 3610 | 2018-01-03 14:34 | 2018-01-03 16:43 | 13.6667 | Switchyard circuit breakers - external (not OMC)
TC5 | U1 | 3681 | 2018-01-04 06:33 | 2018-01-04 17:07 | 179 | Other voltage circuit breakers
BR3 | U1 | 1090 | 2018-01-04 17:21 | 2018-01-05 19:29 | 416 | Other boiler tube leaks
BR5 | U1 | 7920 | 2018-01-08 13:22 | 2018-01-08 15:52 | 130 | Lube oil system
OF5 | U1 | 9135 | 2018-01-08 14:42 | 2018-01-09 08:30 | 12.58 | Lack of water
OF4 | U1 | 9135 | 2018-01-10 10:58 | 2018-01-11 13:47 | 12.58 | Lack of water
TC5 | U1 | 4619 | 2018-01-10 11:27 | 2018-01-10 11:52 | 179 | Other hydrogen system problems
OF5 | U1 | 9135 | 2018-01-10 12:36 | 2018-01-11 13:36 | 12.58 | Lack of water
OF3 | U1 | 9135 | 2018-01-10 14:46 | 2018-01-11 14:56 | 12.58 | Lack of water
TC7 | U1 | 5240 | 2018-01-11 05:35 | 2018-01-11 08:18 | 179 | Fire detection and extinguishing system (including hazardous gas detection system)
TC5 | U1 | 5240 | 2018-01-11 06:19 | 2018-01-11 07:39 | 179 | Fire detection and extinguishing system (including hazardous gas detection system)
OF6 | U1 | 7110 | 2018-01-11 07:33 | 2018-01-11 13:23 | 12.58 | Intake channel or flume (including trash racks)
OF8 | U1 | 7110 | 2018-01-11 07:35 | 2018-01-11 13:02 | 12.58 | Intake channel or flume (including trash racks)
BR3 | U1 | 1090 | 2018-01-11 16:30 | 2018-01-15 14:57 | 416 | Other boiler tube leaks
OF1 | U1 | 7050 | 2018-01-11 23:31 | 2018-01-12 08:27 | 12.58 | Turbine governor
BR6 | SF | 5050 | 2018-01-12 15:07 | 2018-01-14 13:16 | 171 | Ignition system
TC7 | U1 | 5100 | 2018-01-13 07:41 | 2018-01-13 12:36 | 179 | Chamber
TC9 | U1 | 5109 | 2018-01-13 09:01 | 2018-01-13 11:52 | 179 | Other exhaust problems (including high exhaust system temperature not attributable to a specific problem)
TC6 | U1 | 5081 | 2018-01-13 14:18 | 2018-01-13 15:04 | 179 | High pressure bearings
OF1 | U1 | 9000 | 2018-01-13 21:48 | 2018-01-20 13:24 | 12.58 | Flood
OF2 | U1 | 9000 | 2018-01-13 21:49 | 2018-01-20 13:11 | 12.58 | Flood
OF5 | U1 | 9000 | 2018-01-14 04:12 | 2018-01-20 09:55 | 12.58 | Flood
OF4 | U1 | 9000 | 2018-01-14 04:15 | 2018-01-20 12:55 | 12.58 | Flood
OF8 | U1 | 9000 | 2018-01-14 04:19 | 2018-01-20 10:08 | 12.58 | Flood
OF6 | U1 | 9000 | 2018-01-14 04:20 | 2018-01-20 10:22 | 12.58 | Flood
OF3 | U1 | 9000 | 2018-01-14 04:20 | 2018-01-20 12:44 | 12.58 | Flood
BR3 | U1 | 1710 | 2018-01-15 16:48 | 2018-01-15 21:06 | 416 | "Combustion/steam condition controls (report local controls - burners, pulverizers, etc., - with component or system)"
BR11 | U1 | 5070 | 2018-01-18 10:19 | 2018-01-31 14:10 | 128 | Combustor casing
OF2 | U1 | 4750 | 2018-01-20 14:02 | 2018-01-20 14:28 | 12.58 | Other generator controls and metering problems
MC4 | U1 | 800 | 2018-01-23 03:45 | 2018-01-23 04:24 | 486 | Drums and drum internals (single drum only)
OF5 | U1 | 9000 | 2018-01-24 07:17 | 2018-01-30 10:48 | 12.58 | Flood
OF1 | U1 | 9000 | 2018-01-24 07:19 | 2018-02-02 11:55 | 12.58 | Flood
OF4 | U1 | 9000 | 2018-01-24 08:22 | 2018-02-01 13:07 | 12.58 | Flood
OF3 | U1 | 9000 | 2018-01-24 08:34 | 2018-02-01 13:00 | 12.58 | Flood
OF2 | U1 | 9000 | 2018-01-24 08:36 | 2018-02-02 11:23 | 12.58 | Flood
OF8 | U1 | 9000 | 2018-01-24 15:01 | 2018-01-29 13:33 | 12.58 | Flood
OF6 | U1 | 9000 | 2018-01-24 15:04 | 2018-01-29 14:09 | 12.58 | Flood
PR12 | U1 | 3821 | 2018-01-24 22:26 | 2018-01-25 08:31 | 28 | Closed cooling water piping
TC1 | U1 | 4470 | 2018-01-31 22:03 | 2018-02-01 05:08 | 369.75 | Differential expansion
BR6 | U1 | 5170 | 2018-02-02 06:43 | 2018-02-02 16:18 | 171 | Cooling water system
TC8 | U1 | 4810 | 2018-02-02 07:08 | 2018-02-02 21:32 | 179 | Generator output breaker
TC7 | U1 | 5160 | 2018-02-02 09:05 | 2018-02-02 09:13 | 179 | Cooling and seal air system
GH1 | U1 | 1450 | 2018-02-07 18:31 | 2018-02-07 21:21 | 479 | Other air supply problems
OF1 | U1 | 9000 | 2018-02-08 03:17 | 2018-03-12 12:13 | 12.58 | Flood
BR6 | SF | 5450 | 2018-02-08 06:15 | 2018-02-08 14:39 | 171 | Ignition system
OF4 | U1 | 9000 | 2018-02-08 15:46 | 2018-03-12 09:04 | 12.58 | Flood
OF2 | U1 | 9000 | 2018-02-08 20:08 | 2018-03-12 10:51 | 12.58 | Flood
OF3 | U1 | 9000 | 2018-02-08 20:11 | 2018-03-12 10:29 | 12.58 | Flood
OF5 | U1 | 9000 | 2018-02-08 20:13 | 2018-03-12 08:53 | 12.58 | Flood
OF6 | U1 | 9000 | 2018-02-08 23:59 | 2018-03-11 10:40 | 12.58 | Flood
OF8 | U1 | 9000 | 2018-02-09 08:08 | 2018-03-11 12:14 | 12.58 | Flood
TC5 | U1 | 5240 | 2018-02-14 06:05 | 2018-02-14 06:52 | 179 | Fire detection and extinguishing system (including hazardous gas detection system)
TC7 | U1 | 5041 | 2018-02-15 10:09 | 2018-02-15 12:15 | 179 | Fuel piping and valves
TC7 | U1 | 5240 | 2018-02-15 19:13 | 2018-02-15 19:24 | 179 | Fire detection and extinguishing system (including hazardous gas detection system)
MC2 | U1 | 3211 | 2018-02-19 10:23 | 2018-02-20 15:03 | 297 | Circulating water pump motors
MC3 | U1 | 1050 | 2018-02-19 22:37 | 2018-02-22 09:16 | 394 | Second superheater
BR6 | U1 | 5510 | 2018-02-23 10:22 | 2018-02-23 12:38 | 171 | Lube oil system
CR7 | U1 | 5247 | 2018-02-24 11:53 | 2018-02-24 13:15 | 683 | Gas Turbine Control System - internal and termination wiring
CR7 | SF | 5247 | 2018-02-24 13:15 | 2018-02-25 01:50 | 683 | Gas Turbine Control System - internal and termination wiring
GH1 | U1 | 1000 | 2018-02-24 17:00 | 2018-02-27 03:43 | 479 | Waterwall (Furnace wall)
TC7 | SF | 5041 | 2018-02-24 17:39 | 2018-02-24 18:59 | 179 | Fuel piping and valves
MC4 | U1 | 800 | 2018-02-25 06:50 | 2018-02-25 08:50 | 486 | Drums and drum internals (single drum only)
TC7 | U1 | 5240 | 2018-02-26 13:35 | 2018-02-26 14:12 | 179 | Fire detection and extinguishing system (including hazardous gas detection system)
GH1 | U1 | 3520 | 2018-02-28 15:45 | 2018-02-28 17:45 | 479 | HP Extraction steam piping
GH3 | U1 | 3220 | 2018-03-03 11:30 | 2018-03-04 03:22 | 478.5 | Circulating water piping
BR5 | U1 | 5530 | 2018-03-04 20:44 | 2018-03-23 12:53 | 120 | Starting system (including motor)
BR9 | U1 | 5065 | 2018-03-05 06:37 | 2018-03-05 14:37 | 118 | NOx water injection system including pump
MC4 | SF | 8280 | 2018-03-07 02:33 | 2018-03-07 07:56 | 481.5 | Reagent feed piping
TC1 | U1 | 1400 | 2018-03-07 03:01 | 2018-03-07 15:03 | 369.75 | Forced draft fans
BR3 | U1 | 3621 | 2018-03-12 01:42 | 2018-03-13 05:45 | 414 | Unit auxiliaries transformer
TC5 | SF | 5050 | 2018-03-12 06:00 | 2018-03-12 06:10 | 169 | Ignition system
BR3 | SF | 3621 | 2018-03-13 05:45 | 2018-03-13 07:09 | 414 | Unit auxiliaries transformer
TC5 | U1 | 5050 | 2018-03-14 00:17 | 2018-03-14 03:13 | 169 | Ignition system
OF1 | U1 | 7110 | 2018-03-19 13:00 | 2018-03-20 12:15 | 12.58 | Intake channel or flume (including trash racks)
TC5 | U1 | 9930 | 2018-03-23 03:57 | 2018-03-23 05:39 | 169 | Operating procedure error
OF4 | U1 | 9000 | 2018-03-23 10:37 | 2018-04-15 10:56 | 12.58 | Flood
OF2 | U1 | 9000 | 2018-03-23 12:00 | 2018-04-15 12:50 | 12.58 | Flood
OF1 | U1 | 9000 | 2018-03-23 12:03 | 2018-04-15 13:38 | 12.58 | Flood
OF5 | U1 | 9000 | 2018-03-23 12:51 | 2018-04-15 09:10 | 12.58 | Flood
OF3 | U1 | 9000 | 2018-03-23 12:54 | 2018-04-15 11:26 | 12.58 | Flood
OF6 | U1 | 9000 | 2018-03-24 12:58 | 2018-03-27 09:06 | 12.58 | Flood
OF8 | U1 | 9000 | 2018-03-24 13:01 | 2018-03-27 08:55 | 12.58 | Flood
MC1 | U1 | 3344 | 2018-03-26 12:53 | 2018-03-26 17:48 | 300 | Deaerator (including level control)
OF6 | U1 | 9000 | 2018-03-28 06:20 | 2018-04-15 09:25 | 12.58 | Flood
OF8 | U1 | 9000 | 2018-03-28 06:24 | 2018-04-15 08:32 | 12.58 | Flood
Dix 3 | U1 | 7053 | 2018-04-10 00:06 | 2018-04-10 01:57 | 11.2 | Governor oil system
BR11 | U1 | 3979 | 2018-04-11 04:29 | 2018-04-11 12:59 | 118 | Other DCS problems
Dix 3 | U1 | 7299 | 2018-04-14 07:20 | 2018-04-14 15:18 | 11.2 | Other miscellaneous hydro turbine/pump problems (use generator codes and balance of plant electrical and auxiliary codes as appropriate)
Dix 3 | U1 | 7299 | 2018-04-15 07:13 | 2018-04-15 13:42 | 11.2 | Other miscellaneous hydro turbine/pump problems (use generator codes and balance of plant electrical and auxiliary codes as appropriate)
OF1 | U1 | 9000 | 2018-04-16 11:46 | 2018-05-01 08:00 | 12.58 | Flood
OF2 | U1 | 9000 | 2018-04-16 11:50 | 2018-05-01 07:38 | 12.58 | Flood
OF4 | U1 | 9000 | 2018-04-16 21:55 | 2018-04-30 14:01 | 12.58 | Flood
OF3 | U1 | 9000 | 2018-04-17 03:19 | 2018-04-30 13:42 | 12.58 | Flood
TC9 | U1 | 5048 | 2018-04-17 04:06 | 2018-04-17 05:04 | 169 | Gas fuel system including controls and instrumentation
TC10 | U1 | 5048 | 2018-04-17 04:06 | 2018-04-17 05:04 | 169 | Gas fuel system including controls and instrumentation
OF5 | U1 | 9000 | 2018-04-17 05:41 | 2018-04-30 12:46 | 12.58 | Flood
OF6 | U1 | 9000 | 2018-04-17 05:45 | 2018-04-30 12:23 | 12.58 | Flood
OF8 | U1 | 9000 | 2018-04-17 05:50 | 2018-04-30 12:02 | 12.58 | Flood
BR6 | SF | 5450 | 2018-04-23 05:26 | 2018-04-23 15:00 | 157 | Ignition system
GH3 | U1 | 3412 | 2018-04-29 07:41 | 2018-04-29 09:43 | 478.5 | Feedwater pump drive - steam turbine
BR10 | SF | 3611 | 2018-05-01 17:00 | 2018-05-01 17:35 | 118 | Switchyard circuit breakers - external (OMC)
TC1 | U1 | 4261 | 2018-05-01 18:31 | 2018-05-04 00:25 | 369.75 | Control valves
TC6 | U1 | 5246 | 2018-05-03 12:31 | 2018-05-03 14:22 | 169 | Gas Turbine Control System - hardware problems (including card failure)
TC8 | SF | 5016 | 2018-05-04 05:33 | 2018-05-04 06:51 | 169 | High pressure compressor bleed valves
OF1 | U1 | 7110 | 2018-05-04 10:04 | 2018-05-04 12:55 | 12.58 | Intake channel or flume (including trash racks)
TC1 | U1 | 3618 | 2018-05-06 00:28 | 2018-05-06 07:33 | 369.75 | Other switchyard equipment - external (not OMC)
OF4 | U1 | 9000 | 2018-05-08 05:28 | 2018-05-12 09:31 | 12.58 | Flood
OF1 | U1 | 9000 | 2018-05-08 05:30 | 2018-05-12 10:28 | 12.58 | Flood
OF3 | U1 | 9000 | 2018-05-08 06:53 | 2018-05-12 09:51 | 12.58 | Flood
OF2 | U1 | 9000 | 2018-05-08 06:55 | 2018-05-12 10:09 | 12.58 | Flood
OF5 | U1 | 9000 | 2018-05-08 14:01 | 2018-05-12 07:55 | 12.58 | Flood
OF6 | U1 | 9000 | 2018-05-08 14:05 | 2018-05-12 07:32 | 12.58 | Flood
OF8 | U1 | 9000 | 2018-05-08 14:10 | 2018-05-12 07:12 | 12.58 | Flood
TC2 | U1 | 9900 | 2018-05-13 00:19 | 2018-05-13 06:35 | 559.5 | Operator error
MC4 | U1 | 1470 | 2018-05-14 19:03 | 2018-05-14 21:52 | 481.5 | Induced draft fan motors and drives
MC4 | U1 | 3864 | 2018-05-15 00:12 | 2018-05-15 03:27 | 481.5 | Fire protection system instrumentation and controls
BR10 | U1 | 5047 | 2018-05-15 20:43 | 2018-05-15 23:00 | 118 | Liquid fuel purge system
OF1 | U1 | 7110 | 2018-05-17 09:33 | 2018-05-17 13:05 | 12.58 | Intake channel or flume (including trash racks)
OF1 | U1 | 9000 | 2018-05-19 08:39 | 2018-05-28 10:28 | 12.58 | Flood
OF2 | U1 | 9000 | 2018-05-19 20:45 | 2018-05-28 09:51 | 12.58 | Flood
BR5 | U1 | 3972 | 2018-05-20 13:32 | 2018-05-20 14:13 | 120 | DCS - hardware problems (including card failure)
OF5 | U1 | 9000 | 2018-05-21 06:43 | 2018-05-28 07:02 | 12.58 | Flood
OF3 | U1 | 9000 | 2018-05-21 06:59 | 2018-05-21 13:46 | 12.58 | Flood
OF4 | U1 | 9000 | 2018-05-21 07:00 | 2018-05-21 13:59 | 12.58 | Flood
OF6 | U1 | 9000 | 2018-05-21 07:06 | 2018-05-22 09:35 | 12.58 | Flood
OF8 | U1 | 9000 | 2018-05-21 07:11 | 2018-05-22 09:18 | 12.58 | Flood
OF4 | U1 | 7110 | 2018-05-21 22:08 | 2018-05-28 07:26 | 12.58 | Intake channel or flume (including trash racks)
OF3 | U1 | 7110 | 2018-05-21 22:55 | 2018-05-28 09:27 | 12.58 | Intake channel or flume (including trash racks)
BR7 | U1 | 3972 | 2018-05-23 16:32 | 2018-05-23 20:17 | 157 | DCS - hardware problems (including card failure)
OF6 | U1 | 9000 | 2018-05-25 06:04 | 2018-05-27 15:10 | 12.58 | Flood
MC2 | U1 | 4302 | 2018-05-27 06:28 | 2018-05-27 16:13 | 297 | Turbine trip devices (including instruments)
TC2 | U1 | 1420 | 2018-05-27 17:29 | 2018-05-28 10:16 | 559.5 | Other forced draft fan problems
BR8 | SF | 5250 | 2018-05-29 13:32 | 2018-05-29 13:40 | 118 | Other controls and instrumentation problems
TC2 | U1 | 3414 | 2018-05-29 20:05 | 2018-05-30 07:10 | 559.5 | Feedwater pump local controls
PR12 | U1 | 3611 | 2018-05-30 10:54 | 2018-05-30 12:30 | 25.5 | Switchyard circuit breakers - external (OMC)
OF1 | U1 | 7110 | 2018-05-31 08:40 | 2018-05-31 13:11 | 12.58 | Intake channel or flume (including trash racks)
OF5 | U1 | 3820 | 2018-06-01 16:03 | 2018-06-01 16:55 | 12.58 | Closed cooling water pumps and motors
OF6 | U1 | 7190 | 2018-06-07 08:43 | 2018-06-07 19:44 | 12.58 | Dewatering and rewatering equipment
OF8 | U1 | 7190 | 2018-06-07 08:46 | 2018-06-07 20:01 | 12.58 | Dewatering and rewatering equipment
PR12 | SF | 4810 | 2018-06-07 10:00 | 2018-07-06 12:38 | 23 | Generator output breaker
MC4 | U1 | 3499 | 2018-06-07 15:11 | 2018-06-07 19:43 | 477 | Other feedwater system problems
OF3 | U1 | 7053 | 2018-06-09 15:50 | 2018-06-09 16:56 | 12.58 | Governor oil system
OF3 | U1 | 7053 | 2018-06-09 18:29 | 2018-06-10 07:57 | 12.58 | Governor oil system
MC1 | U1 | 800 | 2018-06-11 19:07 | 2018-06-11 22:31 | 300 | Drums and drum internals (single drum only)
BR5 | SF | 7930 | 2018-06-12 10:16 | 2018-06-12 11:30 | 130 | Controls and instrumentation
TC10 | U1 | 5109 | 2018-06-12 16:47 | 2018-06-12 16:50 | 159 | Other exhaust problems (including high exhaust system temperature not attributable to a specific problem)
TC10 | U1 | 5109 | 2018-06-12 16:51 | 2018-06-12 16:53 | 159 | Other exhaust problems (including high exhaust system temperature not attributable to a specific problem)
TC10 | U1 | 5109 | 2018-06-12 16:55 | 2018-06-12 18:37 | 159 | Other exhaust problems (including high exhaust system temperature not attributable to a specific problem)
GH4 | U1 | 3320 | 2018-06-13 13:18 | 2018-06-14 20:21 | 478 | Condensate piping
MC2 | U1 | 1799 | 2018-06-15 00:48 | 2018-06-15 02:36 | 297 | Other boiler instrumentation and control problems
GH3 | U1 | 4535 | 2018-06-16 23:21 | 2018-06-17 06:07 | 481 | "Stator, General"
TC7 | SF | 9900 | 2018-06-17 10:00 | 2018-06-17 10:50 | 159 | Operator error
BR8 | SF | 5246 | 2018-06-17 12:37 | 2018-06-17 16:54 | 121 | Gas Turbine Control System - hardware problems (including card failure)
OF5 | U1 | 7053 | 2018-06-17 19:23 | 2018-06-18 09:05 | 12.58 | Governor oil system
BR7 | U1 | 5016 | 2018-06-18 12:58 | 2018-06-19 08:00 | 146 | High pressure compressor bleed valves
PR13 | U1 | 4640 | 2018-06-20 06:18 | 2018-06-20 09:42 | 147 | Seal oil system and seals
OF1 | U1 | 9000 | 2018-06-23 06:39 | 2018-06-28 12:29 | 12.58 | Flood
OF2 | U1 | 9000 | 2018-06-24 06:45 | 2018-06-28 13:20 | 12.58 | Flood
OF4 | U1 | 9000 | 2018-06-24 11:01 | 2018-06-27 11:57 | 12.58 | Flood
OF3 | U1 | 9000 | 2018-06-25 00:40 | 2018-06-27 12:22 | 12.58 | Flood
OF5 | U1 | 9000 | 2018-06-25 02:48 | 2018-06-27 09:24 | 12.58 | Flood
OF6 | U1 | 9000 | 2018-06-25 07:09 | 2018-06-27 07:43 | 12.58 | Flood
OF8 | U1 | 9000 | 2018-06-25 09:10 | 2018-06-27 07:07 | 12.58 | Flood
OF1 | U1 | 9000 | 2018-06-29 10:50 | 2018-07-03 10:09 | 12.58 | Flood
MC4 | U1 | 3211 | 2018-06-29 14:10 | 2018-06-29 15:41 | 477 | Circulating water pump motors
OF4 | U1 | 9000 | 2018-06-29 18:09 | 2018-07-02 09:00 | 12.58 | Flood
OF2 | U1 | 9000 | 2018-06-29 22:09 | 2018-07-02 12:21 | 12.58 | Flood
BR7 | SF | 4810 | 2018-07-03 09:07 | 2018-07-03 10:26 | 146 | Generator output breaker
OF1 | U1 | 9135 | 2018-07-11 05:47 | 2018-07-16 13:26 | 12.58 | Lack of water
OF3 | U1 | 9135 | 2018-07-11 07:16 | 2018-07-19 07:12 | 12.58 | Lack of water
OF2 | U1 | 9135 | 2018-07-11 09:59 | 2018-07-13 06:39 | 12.58 | Lack of water
BR5 | SF | 5050 | 2018-07-11 12:05 | 2018-07-11 15:35 | 130 | Ignition system
OF4 | U1 | 9135 | 2018-07-11 13:28 | 2018-07-13 06:56 | 12.58 | Lack of water
OF5 | U1 | 9135 | 2018-07-14 03:17 | 2018-07-16 07:22 | 12.58 | Lack of water
OF2 | U1 | 9135 | 2018-07-14 04:15 | 2018-07-16 12:47 | 12.58 | Lack of water
OF4 | U1 | 9135 | 2018-07-14 05:22 | 2018-07-19 07:26 | 12.58 | Lack of water
OF6 | U1 | 9135 | 2018-07-14 07:11 | 2018-07-16 07:04 | 12.58 | Lack of water
OF8 | U1 | 9135 | 2018-07-14 13:50 | 2018-07-16 06:54 | 12.58 | Lack of water
OF5 | U1 | 9135 | 2018-07-16 12:48 | 2018-07-17 14:01 | 12.58 | Lack of water
OF6 | U1 | 9135 | 2018-07-16 13:27 | 2018-07-17 12:54 | 12.58 | Lack of water
OF8 | U1 | 9135 | 2018-07-16 15:00 | 2018-07-17 11:46 | 12.58 | Lack of water
OF1 | U1 | 9135 | 2018-07-16 16:23 | 2018-07-21 09:45 | 12.58 | Lack of water
OF2 | U1 | 9135 | 2018-07-16 17:44 | 2018-07-18 09:07 | 12.58 | Lack of water
OF2 | U1 | 9135 | 2018-07-20 09:49 | 2018-07-21 09:01 | 12.58 | Lack of water
OF5 | U1 | 9135 | 2018-07-20 11:14 | 2018-07-21 06:59 | 12.58 | Lack of water
OF3 | U1 | 9135 | 2018-07-20 13:07 | 2018-08-01 07:00 | 12.58 | Lack of water
BR3 | U2 | 3245 | 2018-07-20 18:20 | 2018-08-05 08:48 | 412 | Other cooling tower problems
TC6 | U1 | 4609 | 2018-07-24 14:05 | 2018-07-24 15:35 | 159 | Other exciter problems
OF6 | U1 | 3814 | 2018-07-28 00:47 | 2018-07-28 09:06 | 12.58 | Service water system fouling
OF6 | U1 | 3814 | 2018-07-29 00:25 | 2018-07-29 09:09 | 12.58 | Service water system fouling
BR9 | SF | 3619 | 2018-08-07 11:07 | 2018-08-07 13:12 | 121 | Other switchyard equipment - external (OMC)
OF1 | U1 | 9135 | 2018-08-08 15:00 | 2018-08-13 06:40 | 12.58 | Lack of water
OF2 | U1 | 9135 | 2018-08-08 15:00 | 2018-08-09 13:41 | 12.58 | Lack of water
MC3 | U1 | 1480 | 2018-08-13 07:07 | 2018-08-13 09:13 | 391 | Other induced draft fan problems
OF5 | U1 | 9135 | 2018-08-14 09:54 | 2018-08-16 09:10 | 12.58 | Lack of water
OF1 | U1 | 9135 | 2018-08-15 13:46 | 2018-08-16 07:50 | 12.58 | Lack of water
BR3 | U1 | 1455 | 2018-08-17 09:42 | 2018-08-17 11:26 | 412 | Induced draft fans
OF1 | U1 | 7110 | 2018-08-20 07:46 | 2018-08-20 15:16 | 12.58 | Intake channel or flume (including trash racks)
OF2 | U1 | 7110 | 2018-08-20 08:20 | 2018-08-20 15:03 | 12.58 | Intake channel or flume (including trash racks)
OF3 | U1 | 7110 | 2018-08-20 08:22 | 2018-08-20 14:44 | 12.58 | Intake channel or flume (including trash racks)
OF4 | U1 | 7110 | 2018-08-20 08:39 | 2018-08-20 14:13 | 12.58 | Intake channel or flume (including trash racks)
OF5 | U1 | 7110 | 2018-08-20 08:41 | 2018-08-20 14:01 | 12.58 | Intake channel or flume (including trash racks)
OF6 | U1 | 7110 | 2018-08-20 08:44 | 2018-08-20 13:48 | 12.58 | Intake channel or flume (including trash racks)
OF8 | U1 | 7110 | 2018-08-20 08:47 | 2018-08-20 13:34 | 12.58 | Intake channel or flume (including trash racks)
TC5 | U1 | 4899 | 2018-08-20 10:51 | 2018-08-20 11:25 | 159 | Other miscellaneous generator problems
TC6 | U1 | 4899 | 2018-08-20 12:13 | 2018-08-20 12:14 | 159 | Other miscellaneous generator problems
BR3 | U1 | 1480 | 2018-08-21 12:31 | 2018-08-21 15:25 | 412 | Other induced draft fan problems
OF5 | U1 | 9720 | 2018-08-22 11:59 | 2018-08-22 13:27 | 12.58 | Other safety problems
OF6 | U1 | 9720 | 2018-08-22 12:02 | 2018-08-22 13:13 | 12.58 | Other safety problems
OF8 | U1 | 9720 | 2018-08-22 12:05 | 2018-08-22 12:58 | 12.58 | Other safety problems
OF6 | U1 | 3814 | 2018-08-22 13:52 | 2018-08-22 14:32 | 12.58 | Service water system fouling
BR5 | U1 | 5111 | 2018-08-23 19:00 | 2018-08-24 13:33 | 130 | Lube oil pumps
OF1 | U1 | 9135 | 2018-08-26 17:50 | 2018-09-17 13:00 | 12.58 | Lack of water
OF2 | U1 | 9135 | 2018-08-29 09:02 | 2018-09-17 12:34 | 12.58 | Lack of water
OF3 | U1 | 9135 | 2018-08-29 11:52 | 2018-08-30 06:53 | 12.58 | Lack of water
OF4 | U1 | 9135 | 2018-08-29 11:54 | 2018-09-01 08:18 | 12.58 | Lack of water
BR8 | SF | 5048 | 2018-09-04 12:39 | 2018-09-04 13:27 | 118 | Gas fuel system including controls and instrumentation
OF4 | U1 | 9135 | 2018-09-06 10:19 | 2018-09-08 13:52 | 12.58 | Lack of water
OF5 | U1 | 9135 | 2018-09-06 12:19 | 2018-09-08 13:38 | 12.58 | Lack of water
BR10 | SF | 3610 | 2018-09-07 16:35 | 2018-09-07 20:13 | 118 | Switchyard circuit breakers - external (not OMC)
GH2 | U1 | 1040 | 2018-09-07 17:03 | 2018-09-11 16:01 | 485.5 | First superheater
TC10 | U1 | 5041 | 2018-09-07 21:47 | 2018-09-08 20:45 | 169 | Fuel piping and valves
OF6 | U1 | 3814 | 2018-09-08 13:57 | 2018-09-08 14:20 | 12.58 | Service water system fouling
OF4 | U1 | 9000 | 2018-09-09 02:48 | 2018-09-17 10:31 | 12.58 | Flood
OF3 | U1 | 9000 | 2018-09-09 03:59 | 2018-09-17 11:12 | 12.58 | Flood
OF5 | U1 | 9000 | 2018-09-09 06:00 | 2018-09-17 09:26 | 12.58 | Flood
OF6 | U1 | 9000 | 2018-09-09 08:56 | 2018-09-17 10:14 | 12.58 | Flood
OF8 | U1 | 9000 | 2018-09-09 09:01 | 2018-09-17 15:00 | 12.58 | Flood
TC1 | U3 | 3110 | 2018-09-12 22:40 | 2018-09-14 16:03 | 369.75 | Condenser tube leaks
BR9 | SF | 3611 | 2018-09-18 09:36 | 2018-09-18 10:07 | 118 | Switchyard circuit breakers - external (OMC)
OF1 | U1 | 9000 | 2018-09-19 00:03 | 2018-10-04 13:02 | 12.58 | Flood
MC4 | U1 | 4810 | 2018-09-19 04:27 | 2018-09-20 02:00 | 481.5 | Generator output breaker
OF2 | U1 | 9000 | 2018-09-19 16:21 | 2018-09-24 10:33 | 12.58 | Flood
OF3 | U1 | 9000 | 2018-09-19 16:30 | 2018-09-24 10:22 | 12.58 | Flood
OF4 | U1 | 9000 | 2018-09-19 16:35 | 2018-09-24 10:10 | 12.58 | Flood
OF5 | U1 | 9000 | 2018-09-20 06:05 | 2018-09-24 09:57 | 12.58 | Flood
OF6 | U1 | 9000 | 2018-09-20 09:43 | 2018-09-24 09:49 | 12.58 | Flood
OF8 | U1 | 9000 | 2018-09-20 09:45 | 2018-09-24 09:36 | 12.58 | Flood
Dix 1 | U1 | 7053 | 2018-09-23 11:43 | 2018-09-23 13:19 | 11.2 | Governor oil system
OF2 | U1 | 9000 | 2018-09-24 20:24 | 2018-10-04 12:43 | 12.58 | Flood
OF3 | U1 | 9000 | 2018-09-24 22:07 | 2018-10-04 10:00 | 12.58 | Flood
OF4 | U1 | 9000 | 2018-09-24 22:16 | 2018-10-04 09:29 | 12.58 | Flood
OF5 | U1 | 9000 | 2018-09-24 23:58 | 2018-10-04 09:06 | 12.58 | Flood
OF6 | U1 | 9000 | 2018-09-25 05:36 | 2018-10-04 08:00 | 12.58 | Flood
OF8 | U1 | 9000 | 2018-09-25 07:12 | 2018-10-04 07:35 | 12.58 | Flood
BR5 | SF | 5073 | 2018-10-02 11:44 | 2018-10-02 12:03 | 120 | Flame scanners
GH1 | U1 | 1475 | 2018-10-02 19:11 | 2018-10-02 21:02 | 477 | Induced draft fan controls
TC9 | U1 | 5111 | 2018-10-03 11:32 | 2018-10-03 13:06 | 169 | Lube oil pumps
BR3 | U1 | 4609 | 2018-10-03 12:12 | 2018-10-03 14:00 | 414 | Other exciter problems
TC1 | U1 | 3618 | 2018-10-05 11:17 | 2018-10-05 13:53 | 369.75 | Other switchyard equipment - external (not OMC)
TC9 | SF | 5130 | 2018-10-05 11:17 | 2018-10-05 16:50 | 169 | Starting system (including motor)
TC9 | SF | 5130 | 2018-10-06 10:57 | 2018-10-07 15:40 | 169 | Starting system (including motor)
OF1 | U1 | 7110 | 2018-10-07 09:01 | 2018-10-11 16:55 | 12.58 | Intake channel or flume (including trash racks)
OF2 | U1 | 7110 | 2018-10-07 09:03 | 2018-10-11 17:12 | 12.58 | Intake channel or flume (including trash racks)
BR6 | U1 | 3621 | 2018-10-07 17:28 | 2018-10-07 18:52 | 157 | Unit auxiliaries transformer
BR9 | U1 | 3621 | 2018-10-07 17:28 | 2018-10-07 19:44 | 118 | Unit auxiliaries transformer
BR10 | U1 | 3621 | 2018-10-07 17:28 | 2018-10-07 19:44 | 118 | Unit auxiliaries transformer
BR8 | U1 | 3621 | 2018-10-07 17:28 | 2018-10-07 19:44 | 118 | Unit auxiliaries transformer
BR7 | U1 | 3621 | 2018-10-07 17:28 | 2018-10-07 18:52 | 157 | Unit auxiliaries transformer
BR5 | U1 | 3621 | 2018-10-07 17:34 | 2018-10-07 18:52 | 120 | Unit auxiliaries transformer
OF3 | U1 | 7110 | 2018-10-10 08:01 | 2018-10-11 07:27 | 12.58 | Intake channel or flume (including trash racks)
OF4 | U1 | 7110 | 2018-10-10 08:05 | 2018-10-10 18:11 | 12.58 | Intake channel or flume (including trash racks)
OF8 | U1 | 7110 | 2018-10-10 09:00 | 2018-10-10 16:51 | 12.58 | Intake channel or flume (including trash racks)
OF5 | U1 | 7110 | 2018-10-10 09:10 | 2018-10-10 17:42 | 12.58 | Intake channel or flume (including trash racks)
OF6 | U1 | 7110 | 2018-10-10 09:12 | 2018-10-10 17:20 | 12.58 | Intake channel or flume (including trash racks)
OF3 | U1 | 7110 | 2018-10-11 11:43 | 2018-10-11 13:01 | 12.58 | Intake channel or flume (including trash racks)
OF1 | U1 | 7110 | 2018-10-11 16:59 | 2018-10-12 13:26 | 12.58 | Intake channel or flume (including trash racks)
OF2 | U1 | 7110 | 2018-10-11 17:15 | 2018-10-13 16:46 | 12.58 | Intake channel or flume (including trash racks)
OF3 | U1 | 7110 | 2018-10-12 13:16 | 2018-10-13 11:53 | 12.58 | Intake channel or flume (including trash racks)
OF4 | U1 | 7110 | 2018-10-13 08:36 | 2018-10-13 11:39 | 12.58 | Intake channel or flume (including trash racks)
OF1 | U1 | 7110 | 2018-10-13 11:22 | 2018-10-14 19:37 | 12.58 | Intake channel or flume (including trash racks)
OF4 | U1 | 7110 | 2018-10-13 14:53 | 2018-10-13 16:38 | 12.58 | Intake channel or flume (including trash racks)
OF5 | U1 | 7110 | 2018-10-13 14:55 | 2018-10-13 17:55 | 12.58 | Intake channel or flume (including trash racks)
OF2 | U1 | 7110 | 2018-10-14 18:43 | 2018-10-14 19:27 | 12.58 | Intake channel or flume (including trash racks)
OF3 | U1 | 7110 | 2018-10-14 18:44 | 2018-10-14 19:12 | 12.58 | Intake channel or flume (including trash racks)
TC10 | SF | 4899 | 2018-10-15 10:09 | 2018-10-15 12:53 | 169 | Other miscellaneous generator problems
TC6 | SF | 3618 | 2018-10-16 05:10 | 2018-10-16 06:15 | 169 | Other switchyard equipment - external (not OMC)
TC5 | SF | 3618 | 2018-10-16 05:10 | 2018-10-16 06:05 | 169 | Other switchyard equipment - external (not OMC)
BR5 | SF | 5130 | 2018-10-18 04:43 | 2018-10-18 05:28 | 120 | Starting system (including motor)
OF4 | U1 | 7110 | 2018-10-19 11:03 | 2018-10-19 13:37 | 12.58 | Intake channel or flume (including trash racks)
OF3 | U1 | 3814 | 2018-10-21 17:18 | 2018-10-21 18:06 | 12.58 | Service water system fouling
BR5 | U1 | 5150 | 2018-10-23 09:22 | 2018-10-24 17:04 | 120 | Turning gear and motor
Dix 3 | U1 | 7052 | 2018-10-24 14:12 | 2018-10-26 10:53 | 11.2 | "Other turbine control problems (Report specific wicket gate controls, etc., using the code for the appropriate equipment item.)"
OF8 | U1 | 4650 | 2018-10-27 16:42 | 2018-10-28 11:23 | 12.58 | Other cooling system problems
TC10 | U1 | 5245 | 2018-10-29 15:55 | 2018-10-29 17:55 | 169 | Gas Turbine Control System - data highway
TC9 | U1 | 5245 | 2018-10-29 15:55 | 2018-10-29 17:55 | 169 | Gas Turbine Control System - data highway
TC2 | U1 | 3671 | 2018-11-01 00:42 | 2018-11-01 18:24 | 559.5 | 12-15kV circuit breakers
OF2 | U1 | 9000 | 2018-11-01 09:53 | 2018-12-09 17:12 | 12.58 | Flood
OF1 | U1 | 9000 | 2018-11-01 12:43 | 2018-12-09 17:12 | 12.58 | Flood
TC2 | U1 | 1488 | 2018-11-01 23:23 | 2018-11-03 04:22 | 559.5 | Air heater (regenerative)
OF6 | U1 | 9000 | 2018-11-02 00:19 | 2018-12-09 11:18 | 12.58 | Flood
OF5 | U1 | 9000 | 2018-11-02 00:22 | 2018-12-09 10:25 | 12.58 | Flood
OF4 | U1 | 9000 | 2018-11-02 00:30 | 2018-12-09 07:56 | 12.58 | Flood
OF3 | U1 | 9000 | 2018-11-02 05:29 | 2018-12-09 15:38 | 12.58 | Flood
OF8 | U1 | 9000 | 2018-11-02 10:24 | 2018-11-30 23:59 | 12.58 | Flood
Dix 1 | U1 | 7052 | 2018-11-05 14:19 | 2018-11-05 15:08 | 11.2 | "Other turbine control problems (Report specific wicket gate controls, etc., using the code for the appropriate equipment item.)"
TC8 | U1 | 5041 | 2018-11-13 06:44 | 2018-11-13 12:39 | 169 | Fuel piping and valves
TC8 | U1 | 5041 | 2018-11-13 12:53 | 2018-11-14 05:30 | 169 | Fuel piping and valves
BR10 | SF | 5130 | 2018-11-14 03:55 | 2018-11-14 04:25 | 118 | Starting system (including motor)
TC1 | SF | 4609 | 2018-11-14 11:00 | 2018-11-14 21:53 | 369.75 | Other exciter problems
GH3 | U1 | 1040 | 2018-11-20 00:40 | 2018-11-27 05:56 | 478.5 | First superheater
MC4 | U1 | 3415 | 2018-11-25 22:16 | 2018-11-28 04:03 | 481.5 | Feedwater pump/drive lube oil system
OF7 | U1 | 9000 | 2018-11-27 14:56 | 2018-12-09 09:00 | 12.58 | Flood
GH3 | U1 | 1350 | 2018-11-27 16:39 | 2018-11-30 09:16 | 478.5 | Other miscellaneous boiler tube problems
TC7 | U1 | 5041 | 2018-11-28 18:50 | 2018-11-28 21:35 | 169 | Fuel piping and valves
TC9 | U1 | 5122 | 2018-11-28 20:00 | 2018-12-02 00:22 | 169 | Hydraulic oil system piping/valves
GH3 | U1 | 1350 | 2018-12-01 18:04 | 2018-12-04 13:50 | 476 | Other miscellaneous boiler tube problems
MC2 | SF | 1475 | 2018-12-03 01:00 | 2018-12-04 02:27 | 297 | Induced draft fan controls
HA2 | SF | 5510 | 2018-12-06 13:00 | 2018-12-07 11:01 | 13.6667 | Lube oil system
HA1 | SF | 5130 | 2018-12-06 13:00 | 2018-12-11 11:25 | 13.6667 | Starting system (including motor)
Dix 1 | U1 | 3684 | 2018-12-07 16:09 | 2018-12-07 21:43 | 11.2 | Other voltage protection devices
OF4 | U1 | 7009 | 2018-12-09 08:11 | 2018-12-09 12:58 | 12.58 | Bearing oil system
Dix 1 | U1 | 7009 | 2018-12-10 11:53 | 2018-12-10 13:57 | 11.2 | Bearing oil system
Dix 1 | U1 | 7009 | 2018-12-10 13:59 | 2018-12-10 16:21 | 11.2 | Bearing oil system
OF7 | U1 | 3814 | 2018-12-12 14:54 | 2018-12-12 15:34 | 12.58 | Service water system fouling
Dix 2 | U1 | 7009 | 2018-12-12 18:08 | 2018-12-12 20:25 | 11.2 | Bearing oil system
Dix 2 | U1 | 7009 | 2018-12-13 01:30 | 2018-12-13 08:51 | 11.2 | Bearing oil system
TC2 | U1 | 1060 | 2018-12-16 21:52 | 2018-12-18 16:59 | 570 | First reheater
OF2 | U1 | 9000 | 2018-12-17 00:17 | 2019-01-01 | 12.58 | Flood
OF1 | U1 | 9000 | 2018-12-17 00:21 | 2019-01-01 | 12.58 | Flood
OF5 | U1 | 9000 | 2018-12-17 13:26 | 2019-01-01 | 12.58 | Flood
OF4 | U1 | 9000 | 2018-12-17 13:35 | 2019-01-01 | 12.58 | Flood
OF3 | U1 | 9000 | 2018-12-17 13:41 | 2019-01-01 | 12.58 | Flood
OF8 | U1 | 9000 | 2018-12-17 14:28 | 2019-01-01 | 12.58 | Flood
OF6 | U1 | 9000 | 2018-12-17 14:33 | 2019-01-01 | 12.58 | Flood
OF7 | U1 | 9000 | 2018-12-17 14:35 | 2019-01-01 | 12.58 | Flood
HA1 | U1 | 5445 | 2018-12-19 12:50 | 2019-01-01 | 13.6667 | Liquid fuel oil transfer/forwarding pump
TC7 | U1 | 5150 | 2018-12-19 13:57 | 2018-12-23 11:00 | 179 | Turning gear and motor
MC3 | U1 | 359 | 2018-12-20 20:37 | 2018-12-20 20:52 | 394 | Gas burner piping and valves
BR11 | U1 | 5550 | 2018-12-29 02:42 | 2018-12-29 16:43 | 128 | Turning gear and motor
Note: The "MW on Outage" value is the Seasonal Net Unit Rating for Fossil Fuel units and the Generator Nameplate Rating for Hydro and Solar units.

## 2019
UnitName | EventType | CauseCode | EventStart | EventEnd | MW On Outage | Cause
OF1 | U1 | 9000 | 2019-01-01 | 2019-01-15 09:12 | 12.58 | Flood
HA1 | U1 | 5445 | 2019-01-01 | 2019-03-22 10:32 | 13.6667 | Liquid fuel oil transfer/forwarding pump
OF3 | U1 | 9000 | 2019-01-01 | 2019-01-15 13:34 | 12.58 | Flood
OF2 | U1 | 9000 | 2019-01-01 | 2019-01-16 20:28 | 12.58 | Flood
OF6 | U1 | 9000 | 2019-01-01 | 2019-01-14 16:39 | 12.58 | Flood
OF5 | U1 | 9000 | 2019-01-01 | 2019-01-15 08:39 | 12.58 | Flood
OF7 | U1 | 9000 | 2019-01-01 | 2019-01-14 15:53 | 12.58 | Flood
OF4 | U1 | 9000 | 2019-01-01 | 2019-01-15 08:56 | 12.58 | Flood
OF8 | U1 | 9000 | 2019-01-01 | 2019-01-16 14:54 | 12.58 | Flood
TC2 | U1 | 4610 | 2019-01-09 06:10 | 2019-01-10 02:27 | 570 | Hydrogen cooling system piping and valves
MC1 | U1 | 540 | 2019-01-14 11:01 | 2019-01-18 15:38 | 300 | Hot reheat steam piping up to turbine stop valves
OF1 | U1 | 7110 | 2019-01-16 19:17 | 2019-01-17 10:17 | 12.58 | Intake channel or flume (including trash racks)
BR6 | SF | 5050 | 2019-01-19 15:22 | 2019-01-19 20:38 | 171 | Ignition system
OF2 | U1 | 9000 | 2019-01-20 03:55 | 2019-01-31 23:59 | 12.58 | Flood
OF1 | U1 | 9000 | 2019-01-20 04:00 | 2019-01-31 23:59 | 12.58 | Flood
BR5 | SF | 5050 | 2019-01-20 09:42 | 2019-01-20 09:58 | 130 | Ignition system
BR10 | U1 | 5039 | 2019-01-20 12:10 | 2019-01-20 12:26 | 138 | Other compressor problems
OF3 | U1 | 9000 | 2019-01-20 16:35 | 2019-01-31 23:59 | 12.58 | Flood
OF4 | U1 | 9000 | 2019-01-20 16:36 | 2019-01-31 23:59 | 12.58 | Flood
OF5 | U1 | 9000 | 2019-01-20 17:02 | 2019-01-31 23:59 | 12.58 | Flood
OF6 | U1 | 9000 | 2019-01-20 17:05 | 2019-01-31 23:59 | 12.58 | Flood
OF7 | U1 | 9000 | 2019-01-20 17:20 | 2019-01-31 23:59 | 12.58 | Flood
OF8 | U1 | 9000 | 2019-01-20 17:22 | 2019-01-31 23:59 | 12.58 | Flood
TC8 | SF | 5001 | 2019-01-20 18:04 | 2019-01-20 19:54 | 179 | Inlet air vanes/nozzles
TC10 | U1 | 5240 | 2019-01-24 00:17 | 2019-01-24 03:02 | 179 | Fire detection and extinguishing system (including hazardous gas detection system)
MC4 | U1 | 1080 | 2019-01-27 07:55 | 2019-01-28 12:50 | 486 | Economizer
MC4 | SF | 3344 | 2019-01-28 12:50 | 2019-01-28 17:05 | 486 | Deaerator (including level control)
BR10 | U1 | 4555 | 2019-01-29 20:54 | 2019-01-29 21:30 | 138 | Bearing cooling system
OF1 | U1 | 9000 | 2019-02-01 | 2019-02-03 15:44 | 12.58 | Flood
OF3 | U1 | 9000 | 2019-02-01 | 2019-02-03 14:04 | 12.58 | Flood
OF2 | U1 | 9000 | 2019-02-01 | 2019-02-03 14:53 | 12.58 | Flood
OF6 | U1 | 9000 | 2019-02-01 | 2019-02-03 10:04 | 12.58 | Flood
OF5 | U1 | 9000 | 2019-02-01 | 2019-02-03 10:16 | 12.58 | Flood
OF8 | U1 | 9000 | 2019-02-01 | 2019-02-03 10:51 | 12.58 | Flood
OF7 | U1 | 9000 | 2019-02-01 | 2019-02-03 12:14 | 12.58 | Flood
OF4 | U1 | 9000 | 2019-02-01 | 2019-02-03 13:03 | 12.58 | Flood
CR7 | U1 | 3210 | 2019-02-02 23:05 | 2019-02-03 00:42 | 683 | Circulating water pumps
OF8 | U1 | 4550 | 2019-02-03 22:27 | 2019-02-04 09:13 | 12.58 | Generator bearings and lube oil system (including thrust bearings on hydro units)
OF1 | U1 | 7110 | 2019-02-04 10:51 | 2019-02-04 14:37 | 12.58 | Intake channel or flume (including trash racks)
OF2 | U1 | 7110 | 2019-02-04 11:03 | 2019-02-04 14:52 | 12.58 | Intake channel or flume (including trash racks)
OF1 | U1 | 9000 | 2019-02-06 07:05 | 2019-03-08 11:32 | 12.58 | Flood
OF2 | U1 | 9000 | 2019-02-06 14:01 | 2019-03-08 11:40 | 12.58 | Flood
OF3 | U1 | 9000 | 2019-02-07 07:40 | 2019-03-08 11:13 | 12.58 | Flood
OF4 | U1 | 9000 | 2019-02-07 07:49 | 2019-03-07 13:46 | 12.58 | Flood
OF5 | U1 | 9000 | 2019-02-07 07:56 | 2019-03-07 13:10 | 12.58 | Flood
OF6 | U1 | 9000 | 2019-02-07 08:04 | 2019-03-06 14:52 | 12.58 | Flood
OF7 | U1 | 9000 | 2019-02-07 08:10 | 2019-03-06 10:56 | 12.58 | Flood
OF8 | U1 | 9000 | 2019-02-07 08:16 | 2019-03-06 13:16 | 12.58 | Flood
MC2 | U1 | 9270 | 2019-02-13 04:46 | 2019-02-13 06:34 | 297 | Wet coal (OMC)
TC8 | U1 | 9291 | 2019-02-13 05:22 | 2019-02-13 08:01 | 179 | Other fuel quality problems (not OMC)
BR6 | U1 | 5248 | 2019-02-13 06:47 | 2019-02-13 06:57 | 171 | Gas Turbine Control System - logic problems
BR6 | U1 | 5248 | 2019-02-13 06:58 | 2019-02-13 07:01 | 171 | Gas Turbine Control System - logic problems
BR6 | U1 | 5248 | 2019-02-13 07:02 | 2019-02-13 07:04 | 171 | Gas Turbine Control System - logic problems
BR6 | U1 | 5248 | 2019-02-13 07:05 | 2019-02-13 07:20 | 171 | Gas Turbine Control System - logic problems
BR6 | U1 | 5248 | 2019-02-13 07:21 | 2019-02-13 07:25 | 171 | Gas Turbine Control System - logic problems
BR6 | U1 | 5248 | 2019-02-13 07:26 | 2019-02-13 07:40 | 171 | Gas Turbine Control System - logic problems
BR6 | U1 | 5248 | 2019-02-13 07:41 | 2019-02-13 07:43 | 171 | Gas Turbine Control System - logic problems
BR6 | U1 | 5248 | 2019-02-13 07:44 | 2019-02-13 13:39 | 171 | Gas Turbine Control System - logic problems
Dix 3 | U1 | 7053 | 2019-02-17 12:33 | 2019-02-17 14:40 | 11.2 | Governor oil system
MC3 | U1 | 4630 | 2019-02-18 13:04 | 2019-02-18 23:18 | 394 | Liquid cooling system
BR6 | SF | 5050 | 2019-02-19 06:03 | 2019-02-19 12:05 | 171 | Ignition system
MC4 | U1 | 3634 | 2019-02-19 13:31 | 2019-02-19 15:33 | 486 | 400-700 volt protection devices
BR3 | U1 | 3149 | 2019-02-26 11:24 | 2019-02-26 11:57 | 416 | "Loss of vacuum not attributable to a particular component such as air ejectors or valves, or high back pressure not attributable to high circulating water temperature, or vacuum losses from a known cause."
BR9 | SF | 5130 | 2019-03-04 16:50 | 2019-03-04 20:00 | 118 | Starting system (including motor)
BR10 | SF | 5050 | 2019-03-04 17:12 | 2019-03-04 19:05 | 118 | Ignition system
OF1 | U1 | 9000 | 2019-03-08 12:49 | 2019-03-22 11:58 | 12.58 | Flood
OF2 | U1 | 9000 | 2019-03-08 20:16 | 2019-03-22 13:39 | 12.58 | Flood
OF3 | U1 | 9000 | 2019-03-10 12:32 | 2019-03-19 12:35 | 12.58 | Flood
OF4 | U1 | 9000 | 2019-03-10 12:38 | 2019-03-19 12:13 | 12.58 | Flood
OF5 | U1 | 9000 | 2019-03-10 13:26 | 2019-03-18 13:16 | 12.58 | Flood
OF6 | U1 | 9000 | 2019-03-10 13:40 | 2019-03-18 12:49 | 12.58 | Flood
OF7 | U1 | 9000 | 2019-03-10 14:12 | 2019-03-18 12:15 | 12.58 | Flood
OF8 | U1 | 9000 | 2019-03-10 14:15 | 2019-03-22 09:41 | 12.58 | Flood
TC8 | U1 | 5111 | 2019-03-10 21:27 | 2019-03-10 22:29 | 169 | Lube oil pumps
TC7 | U1 | 5111 | 2019-03-10 21:27 | 2019-03-11 02:24 | 169 | Lube oil pumps
OF1 | U1 | 7110 | 2019-03-23 07:43 | 2019-03-26 13:50 | 12.58 | Intake channel or flume (including trash racks)
OF2 | U1 | 7110 | 2019-03-26 20:38 | 2019-03-27 09:37 | 12.58 | Intake channel or flume (including trash racks)
OF1 | U1 | 7110 | 2019-03-26 21:39 | 2019-03-27 15:27 | 12.58 | Intake channel or flume (including trash racks)
OF3 | U1 | 7110 | 2019-03-27 03:07 | 2019-03-27 10:04 | 12.58 | Intake channel or flume (including trash racks)
OF4 | U1 | 7110 | 2019-03-27 09:45 | 2019-03-27 10:57 | 12.58 | Intake channel or flume (including trash racks)
OF1 | U1 | 7008 | 2019-03-28 03:26 | 2019-03-28 06:48 | 12.58 | Bearing cooling system
OF7 | U1 | 7008 | 2019-03-30 14:29 | 2019-03-30 15:32 | 12.58 | Bearing cooling system
OF7 | U1 | 7008 | 2019-03-31 01:42 | 2019-03-31 06:36 | 12.58 | Bearing cooling system
OF1 | U1 | 7110 | 2019-03-31 06:30 | 2019-04-02 13:37 | 12.58 | Intake channel or flume (including trash racks)
BR6 | U1 | 5079 | 2019-04-01 03:16 | 2019-04-01 13:18 | 157 | Other combustor problems
OF2 | U1 | 7110 | 2019-04-01 04:30 | 2019-04-02 14:19 | 12.58 | Intake channel or flume (including trash racks)
BR5 | SF | 5130 | 2019-04-02 04:20 | 2019-04-02 04:49 | 120 | Starting system (including motor)
TC1 | U1 | 8817 | 2019-04-02 09:19 | 2019-04-03 09:33 | 369.75 | SCR NOx Control system
OF1 | U1 | 9000 | 2019-04-02 23:46 | 2019-04-03 12:17 | 12.58 | Flood
OF2 | U1 | 7110 | 2019-04-03 22:11 | 2019-04-04 13:02 | 12.58 | Intake channel or flume (including trash racks)
OF1 | U1 | 7110 | 2019-04-03 22:12 | 2019-04-04 11:59 | 12.58 | Intake channel or flume (including trash racks)
OF1 | U1 | 7110 | 2019-04-04 13:05 | 2019-04-04 19:30 | 12.58 | Intake channel or flume (including trash racks)
PR13 | U1 | 3611 | 2019-04-04 18:51 | 2019-04-04 21:53 | 161 | Switchyard circuit breakers - external (OMC)
OF1 | U1 | 7110 | 2019-04-05 04:37 | 2019-04-05 16:26 | 12.58 | Intake channel or flume (including trash racks)
OF1 | U1 | 7110 | 2019-04-06 07:52 | 2019-04-06 16:15 | 12.58 | Intake channel or flume (including trash racks)
PR13 | U1 | 3972 | 2019-04-11 06:00 | 2019-04-11 07:00 | 161 | DCS - hardware problems (including card failure)
OF6 | U1 | 7053 | 2019-04-12 01:43 | 2019-04-12 07:13 | 12.58 | Governor oil system
OF7 | U1 | 7110 | 2019-04-12 10:59 | 2019-04-12 14:35 | 12.58 | Intake channel or flume (including trash racks)
OF8 | U1 | 7110 | 2019-04-12 11:01 | 2019-04-12 15:06 | 12.58 | Intake channel or flume (including trash racks)
OF1 | U1 | 7110 | 2019-04-13 08:38 | 2019-04-13 09:46 | 12.58 | Intake channel or flume (including trash racks)
OF8 | U1 | 7009 | 2019-04-14 04:34 | 2019-04-14 10:13 | 12.58 | Bearing oil system
OF5 | U1 | 3710 | 2019-04-15 12:10 | 2019-04-15 14:47 | 12.58 | Transmission line (connected to powerhouse switchyard to 1st Substation)
OF6 | U1 | 3710 | 2019-04-15 12:13 | 2019-04-15 14:26 | 12.58 | Transmission line (connected to powerhouse switchyard to 1st Substation)
OF7 | U1 | 3710 | 2019-04-15 12:18 | 2019-04-15 14:07 | 12.58 | Transmission line (connected to powerhouse switchyard to 1st Substation)
OF8 | U1 | 3710 | 2019-04-15 12:21 | 2019-04-15 13:48 | 12.58 | Transmission line (connected to powerhouse switchyard to 1st Substation)
OF1 | U1 | 7110 | 2019-04-15 14:49 | 2019-05-11 08:54 | 12.58 | Intake channel or flume (including trash racks)
OF2 | U1 | 7110 | 2019-04-17 12:05 | 2019-05-11 08:43 | 12.58 | Intake channel or flume (including trash racks)
OF3 | U1 | 9000 | 2019-04-19 11:32 | 2019-05-10 07:33 | 12.58 | Flood
OF4 | U1 | 9000 | 2019-04-19 11:35 | 2019-05-10 07:22 | 12.58 | Flood
OF8 | U1 | 9000 | 2019-04-20 08:32 | 2019-05-03 09:03 | 12.58 | Flood
OF5 | U1 | 9000 | 2019-04-20 08:35 | 2019-05-03 10:25 | 12.58 | Flood
OF6 | U1 | 9000 | 2019-04-20 08:40 | 2019-05-03 09:54 | 12.58 | Flood
OF7 | U1 | 9000 | 2019-04-20 08:45 | 2019-05-03 09:19 | 12.58 | Flood
GH2 | U1 | 360 | 2019-04-20 11:49 | 2019-04-22 00:22 | 485.5 | Burners
MC3 | U1 | 3129 | 2019-04-20 12:39 | 2019-04-24 20:30 | 392.5 | Other condenser casing or shell and internal problems
MC2 | U1 | 3650 | 2019-04-20 17:42 | 2019-04-20 22:00 | 297 | DC instrument power battery chargers
MC2 | U1 | 1455 | 2019-04-20 22:28 | 2019-04-20 23:58 | 297 | Induced draft fans
GH3 | U1 | 4609 | 2019-04-22 01:22 | 2019-04-22 23:17 | 478.5 | Other exciter problems
MC3 | U1 | 1050 | 2019-04-25 15:01 | 2019-04-27 18:16 | 392.5 | Second superheater
GH3 | U1 | 4609 | 2019-04-26 01:55 | 2019-04-26 17:32 | 478.5 | Other exciter problems
OF5 | U1 | 7140 | 2019-05-03 10:41 | 2019-05-29 07:37 | 12.58 | Wicket gate assembly
TC2 | U1 | 4551 | 2019-05-06 | 2019-05-10 11:26 | 559.5 | Generator bearings
MC1 | U1 | 4640 | 2019-05-06 18:00 | 2019-05-08 08:55 | 300 | Seal oil system and seals
OF8 | U1 | 9000 | 2019-05-07 15:55 | 2019-05-10 06:27 | 12.58 | Flood
OF7 | U1 | 9000 | 2019-05-07 15:57 | 2019-05-10 06:48 | 12.58 | Flood
OF6 | U1 | 9000 | 2019-05-07 15:59 | 2019-05-10 07:10 | 12.58 | Flood
MC1 | U1 | 9900 | 2019-05-08 10:01 | 2019-05-08 10:33 | 300 | Operator error
TC10 | U1 | 5246 | 2019-05-08 12:40 | 2019-05-08 14:50 | 169 | Gas Turbine Control System - hardware problems (including card failure)
MC1 | U1 | 4420 | 2019-05-10 08:36 | 2019-05-10 18:36 | 300 | Vibration of the turbine generator unit that cannot be attributed to a specific cause such as bearings or blades (use this code for balance moves)
TC2 | SF | 4240 | 2019-05-10 11:26 | 2019-05-10 19:47 | 559.5 | Bearings
GH1 | U1 | 4613 | 2019-05-10 13:54 | 2019-05-11 15:52 | 477 | Hydrogen seals
TC2 | SF | 4240 | 2019-05-10 19:47 | 2019-05-12 05:49 | 559.5 | Bearings
GH1 | U1 | 4560 | 2019-05-11 18:00 | 2019-05-14 11:54 | 477 | Generator vibration (excluding vibration due to failed bearing and other components)
TC2 | SF | 4551 | 2019-05-12 05:49 | 2019-05-13 12:02 | 559.5 | Generator bearings
OF1 | U1 | 9000 | 2019-05-12 15:32 | 2019-05-12 16:45 | 12.58 | Flood
OF1 | U1 | 7110 | 2019-05-12 21:50 | 2019-05-21 10:29 | 12.58 | Intake channel or flume (including trash racks)
OF2 | U1 | 7110 | 2019-05-13 02:47 | 2019-05-21 10:20 | 12.58 | Intake channel or flume (including trash racks)
TC2 | U1 | 4551 | 2019-05-13 14:04 | 2019-05-14 04:29 | 559.5 | Generator bearings
BR9 | U1 | 5150 | 2019-05-13 19:20 | 2019-05-14 15:42 | 118 | Turning gear and motor
TC2 | U1 | 370 | 2019-05-14 05:31 | 2019-05-14 14:32 | 559.5 | Burner instruments and controls (except light off)
OF3 | U1 | 7110 | 2019-05-14 06:08 | 2019-05-14 10:06 | 12.58 | Intake channel or flume (including trash racks)
TC2 | U1 | 370 | 2019-05-14 14:48 | 2019-05-14 17:07 | 559.5 | Burner instruments and controls (except light off)
TC2 | SF | 3402 | 2019-05-14 17:07 | 2019-05-16 01:30 | 559.5 | Startup feedwater pump drives - all types
OF4 | U1 | 7110 | 2019-05-15 06:27 | 2019-05-20 09:38 | 12.58 | Intake channel or flume (including trash racks)
OF3 | U1 | 7110 | 2019-05-15 11:46 | 2019-05-20 09:49 | 12.58 | Intake channel or flume (including trash racks)
MC1 | U1 | 4299 | 2019-05-16 01:28 | 2019-05-16 02:15 | 300 | Other hydraulic system problems
TC2 | U1 | 3402 | 2019-05-16 06:53 | 2019-05-16 14:52 | 559.5 | Startup feedwater pump drives - all types
TC2 | U1 | 3402 | 2019-05-16 17:05 | 2019-05-18 10:13 | 559.5 | Startup feedwater pump drives - all types
OF8 | U1 | 3972 | 2019-05-17 06:00 | 2019-05-17 06:56 | 12.58 | DCS - hardware problems (including card failure)
BR5 | SF | 5450 | 2019-05-17 11:10 | 2019-05-17 12:28 | 120 | Ignition system
TC7 | U1 | 5081 | 2019-05-17 12:41 | 2019-05-17 13:09 | 169 | High pressure bearings
OF1 | U1 | 7110 | 2019-05-22 08:55 | 2019-05-22 13:34 | 12.58 | Intake channel or flume (including trash racks)
TC8 | U1 | 5248 | 2019-05-24 03:24 | 2019-05-24 07:12 | 169 | Gas Turbine Control System - logic problems
Dix 3 | U1 | 9930 | 2019-05-24 09:22 | 2019-05-24 09:41 | 11.2 | Operating procedure error
TC2 | U1 | 1700 | 2019-05-25 18:24 | 2019-05-25 22:25 | 559.5 | "Feedwater controls (report local controls - feedwater pump, feedwater regulator valve, etc., - with component or system)"
OF6 | U1 | 7008 | 2019-05-27 21:12 | 2019-05-28 06:24 | 12.58 | Bearing cooling system
PR13 | U1 | 4551 | 2019-05-28 17:00 | 2019-06-10 07:32 | 161 | Generator bearings
TC10 | U1 | 5048 | 2019-05-30 14:45 | 2019-05-30 15:18 | 169 | Gas fuel system including controls and instrumentation
TC8 | U1 | 5048 | 2019-05-30 14:45 | 2019-05-30 15:18 | 169 | Gas fuel system including controls and instrumentation
TC6 | U1 | 5048 | 2019-05-30 14:45 | 2019-05-30 15:18 | 169 | Gas fuel system including controls and instrumentation
TC9 | U1 | 5048 | 2019-05-30 14:45 | 2019-05-30 15:18 | 169 | Gas fuel system including controls and instrumentation
TC7 | U1 | 5048 | 2019-05-30 14:45 | 2019-05-30 15:18 | 169 | Gas fuel system including controls and instrumentation
TC5 | U1 | 5048 | 2019-05-30 14:45 | 2019-05-30 15:18 | 169 | Gas fuel system including controls and instrumentation
OF1 | U1 | 9000 | 2019-05-31 13:12 | 2019-06-05 16:21 | 12.58 | Flood
OF2 | U1 | 9000 | 2019-06-01 06:03 | 2019-06-05 16:14 | 12.58 | Flood
OF3 | U1 | 9000 | 2019-06-01 06:04 | 2019-06-04 12:28 | 12.58 | Flood
BR6 | U1 | 5660 | 2019-06-02 10:25 | 2019-06-02 10:52 | 146 | Major overhaul (use for non-specific overhaul only; see page B-CCGT-2)
BR6 | U1 | 5441 | 2019-06-02 12:09 | 2019-06-02 12:11 | 146 | Fuel piping and valves
BR6 | U1 | 5441 | 2019-06-03 01:09 | 2019-06-03 06:26 | 146 | Fuel piping and valves
OF4 | U1 | 9000 | 2019-06-03 05:58 | 2019-06-04 12:07 | 12.58 | Flood
BR6 | U1 | 5441 | 2019-06-03 08:35 | 2019-06-04 06:56 | 146 | Fuel piping and valves
BR6 | U1 | 5441 | 2019-06-04 09:16 | 2019-06-04 15:53 | 146 | Fuel piping and valves
TC1 | U1 | 9900 | 2019-06-05 22:56 | 2019-06-06 01:26 | 369.75 | Operator error
BR6 | U1 | 5441 | 2019-06-07 12:58 | 2019-06-07 13:44 | 146 | Fuel piping and valves
Dix 3 | SF | 7121 | 2019-06-07 22:36 | 2019-06-07 23:55 | 11.2 | Shutoff valves
TC1 | U1 | 1035 | 2019-06-08 10:57 | 2019-06-12 04:43 | 369.75 | Platen superheater
OF1 | U1 | 9000 | 2019-06-09 13:28 | 2019-06-11 14:31 | 12.58 | Flood
OF2 | U1 | 9000 | 2019-06-10 11:44 | 2019-06-11 14:47 | 12.58 | Flood
OF5 | U1 | 4750 | 2019-06-11 04:43 | 2019-06-11 07:12 | 12.58 | Other generator controls and metering problems
PR13 | U1 | 3624 | 2019-06-13 13:02 | 2019-06-14 08:56 | 147 | Auxiliary generator voltage supply system
OF1 | U1 | 9000 | 2019-06-16 21:14 | 2019-06-28 15:00 | 12.58 | Flood
OF2 | U1 | 9000 | 2019-06-16 22:32 | 2019-06-28 13:32 | 12.58 | Flood
OF3 | U1 | 9000 | 2019-06-17 00:18 | 2019-06-28 12:46 | 12.58 | Flood
OF4 | U1 | 9000 | 2019-06-17 06:25 | 2019-06-28 11:58 | 12.58 | Flood
OF5 | U1 | 9000 | 2019-06-17 13:18 | 2019-06-28 10:08 | 12.58 | Flood
OF6 | U1 | 9000 | 2019-06-17 15:10 | 2019-06-28 09:20 | 12.58 | Flood
OF7 | U1 | 9000 | 2019-06-17 15:19 | 2019-06-28 08:00 | 12.58 | Flood
OF8 | U1 | 9000 | 2019-06-17 15:21 | 2019-06-28 07:32 | 12.58 | Flood
BR6 | U1 | 5449 | 2019-06-21 18:57 | 2019-06-22 10:30 | 146 | Other fuel system problems
TC1 | U1 | 1700 | 2019-06-23 22:24 | 2019-06-23 23:06 | 369.75 | "Feedwater controls (report local controls - feedwater pump, feedwater regulator valve, etc., - with component or system)"
BR5 | U1 | 5120 | 2019-06-27 00:20 | 2019-06-27 02:30 | 130 | Hydraulic oil system
BR6 | U1 | 5051 | 2019-06-28 11:57 | 2019-06-28 12:12 | 146 | Pilot fuel piping and valves
GH1 | U1 | 350 | 2019-06-29 03:18 | 2019-06-29 11:12 | 475 | Pulverized fuel and air piping (from pulverizer to wind box) (see code 0898 for pulverizer reject system problems)
OF1 | U1 | 7110 | 2019-06-29 08:58 | 2019-06-29 13:53 | 12.58 | Intake channel or flume (including trash racks)
OF2 | U1 | 7110 | 2019-06-29 10:38 | 2019-06-29 13:26 | 12.58 | Intake channel or flume (including trash racks)
GH1 | U1 | 4308 | 2019-06-29 11:54 | 2019-06-29 18:10 | 475 | Automatic turbine control systems - digital control and monitoring
BR7 | U1 | 4511 | 2019-06-30 09:00 | 2019-08-04 13:26 | 146 | "Rotor, General"
BR3 | U1 | 8545 | 2019-07-01 06:01 | 2019-07-01 10:56 | 412 | Electrical failures
BR3 | SF | 4420 | 2019-07-01 10:56 | 2019-07-03 07:11 | 412 | Vibration of the turbine generator unit that cannot be attributed to a specific cause such as bearings or blades (use this code for balance moves)
OF1 | U1 | 7110 | 2019-07-01 20:05 | 2019-07-02 14:28 | 12.58 | Intake channel or flume (including trash racks)
OF2 | U1 | 7110 | 2019-07-01 21:01 | 2019-07-02 13:58 | 12.58 | Intake channel or flume (including trash racks)
BR6 | U1 | 5041 | 2019-07-03 16:51 | 2019-07-03 22:28 | 146 | Fuel piping and valves
BR6 | U1 | 5048 | 2019-07-08 19:23 | 2019-07-09 10:31 | 146 | Gas fuel system including controls and instrumentation
OF8 | U1 | 4550 | 2019-07-11 20:06 | 2019-07-12 07:06 | 12.58 | Generator bearings and lube oil system (including thrust bearings on hydro units)
TC2 | U1 | 3431 | 2019-07-13 03:45 | 2019-07-13 12:27 | 549 | Other feedwater valves
OF8 | U1 | 7008 | 2019-07-16 21:51 | 2019-07-17 07:31 | 12.58 | Bearing cooling system
BR3 | U1 | 9020 | 2019-07-19 00:31 | 2019-07-19 14:21 | 412 | Lightning
OF1 | U1 | 7110 | 2019-07-19 07:26 | 2019-07-19 13:51 | 12.58 | Intake channel or flume (including trash racks)
OF1 | U1 | 7110 | 2019-07-22 08:43 | 2019-07-22 15:11 | 12.58 | Intake channel or flume (including trash racks)
OF8 | U1 | 4550 | 2019-07-22 12:58 | 2019-07-22 15:26 | 12.58 | Generator bearings and lube oil system (including thrust bearings on hydro units)
OF2 | U1 | 7110 | 2019-07-23 03:44 | 2019-07-23 15:35 | 12.58 | Intake channel or flume (including trash racks)
OF1 | U1 | 7110 | 2019-07-23 03:45 | 2019-07-23 15:50 | 12.58 | Intake channel or flume (including trash racks)
OF3 | U1 | 7110 | 2019-07-23 06:38 | 2019-07-23 15:06 | 12.58 | Intake channel or flume (including trash racks)
OF4 | U1 | 7110 | 2019-07-23 06:48 | 2019-07-23 14:36 | 12.58 | Intake channel or flume (including trash racks)
OF5 | U1 | 7110 | 2019-07-23 07:03 | 2019-07-23 14:15 | 12.58 | Intake channel or flume (including trash racks)
OF6 | U1 | 7110 | 2019-07-23 07:18 | 2019-07-23 13:58 | 12.58 | Intake channel or flume (including trash racks)
OF7 | U1 | 7110 | 2019-07-23 07:27 | 2019-07-23 13:36 | 12.58 | Intake channel or flume (including trash racks)
OF8 | U1 | 7110 | 2019-07-23 07:35 | 2019-07-23 13:19 | 12.58 | Intake channel or flume (including trash racks)
OF1 | U1 | 7110 | 2019-07-27 08:15 | 2019-07-27 13:55 | 12.58 | Intake channel or flume (including trash racks)
TC2 | U2 | 1060 | 2019-07-27 16:11 | 2019-07-30 19:28 | 549 | First reheater
OF1 | U1 | 9135 | 2019-07-28 14:23 | 2019-10-08 07:38 | 12.58 | Lack of water
PR13 | U1 | 4611 | 2019-07-28 15:04 | 2019-07-28 15:49 | 147 | Hydrogen coolers
OF2 | U1 | 9135 | 2019-07-28 16:17 | 2019-08-09 07:31 | 12.58 | Lack of water
OF3 | U1 | 9135 | 2019-07-29 17:22 | 2019-07-30 07:39 | 12.58 | Lack of water
TC6 | U1 | 5041 | 2019-07-30 21:40 | 2019-07-31 00:47 | 159 | Fuel piping and valves
TC2 | U1 | 380 | 2019-07-30 22:01 | 2019-07-31 02:33 | 549 | Light off (igniter) systems (including fuel supply)
TC2 | SF | 4308 | 2019-07-31 02:33 | 2019-07-31 06:33 | 549 | Automatic turbine control systems - digital control and monitoring
OF3 | U1 | 9135 | 2019-07-31 06:18 | 2019-08-01 10:16 | 12.58 | Lack of water
OF4 | U1 | 9135 | 2019-07-31 10:01 | 2019-08-01 09:21 | 12.58 | Lack of water
OF3 | U1 | 9135 | 2019-08-02 15:00 | 2019-08-09 07:00 | 12.58 | Lack of water
OF4 | U1 | 9135 | 2019-08-02 20:32 | 2019-08-08 06:53 | 12.58 | Lack of water
OF8 | U1 | 9135 | 2019-08-06 17:44 | 2019-08-08 07:45 | 12.58 | Lack of water
OF5 | U1 | 9135 | 2019-08-06 20:19 | 2019-08-08 09:33 | 12.58 | Lack of water
OF7 | U1 | 9135 | 2019-08-07 02:21 | 2019-08-08 07:28 | 12.58 | Lack of water
OF6 | U1 | 9135 | 2019-08-10 11:00 | 2019-08-14 06:57 | 12.58 | Lack of water
TC2 | U2 | 1000 | 2019-08-10 13:00 | 2019-08-12 16:49 | 549 | Waterwall (Furnace wall)
CR7 | U1 | 3350 | 2019-08-10 14:17 | 2019-08-10 17:17 | 662 | Condensate polishing and filtering systems
BR9 | SF | 3610 | 2019-08-10 14:25 | 2019-08-10 16:02 | 121 | Switchyard circuit breakers - external (not OMC)
OF2 | U1 | 9135 | 2019-08-11 09:31 | 2019-10-08 07:22 | 12.58 | Lack of water
BR6 | U1 | 5280 | 2019-08-11 10:04 | 2019-08-11 11:21 | 146 | Vibration (not engine) in unit not attributable to bearings or other components
OF5 | U1 | 9135 | 2019-08-11 12:40 | 2019-08-14 08:48 | 12.58 | Lack of water
BR9 | SF | 3610 | 2019-08-11 12:58 | 2019-08-11 14:36 | 121 | Switchyard circuit breakers - external (not OMC)
OF3 | U1 | 9135 | 2019-08-11 14:37 | 2019-08-14 10:24 | 12.58 | Lack of water
OF4 | U1 | 9135 | 2019-08-11 21:47 | 2019-08-14 09:07 | 12.58 | Lack of water
TC2 | SF | 4308 | 2019-08-12 16:49 | 2019-08-12 18:03 | 549 | Automatic turbine control systems - digital control and monitoring
TC6 | U1 | 5130 | 2019-08-13 15:16 | 2019-08-13 15:31 | 159 | Starting system (including motor)
TC5 | U1 | 5130 | 2019-08-13 15:16 | 2019-08-13 15:31 | 159 | Starting system (including motor)
OF3 | U1 | 9135 | 2019-08-15 12:20 | 2019-10-08 07:00 | 12.58 | Lack of water
OF4 | U1 | 9135 | 2019-08-15 17:10 | 2019-08-23 09:19 | 12.58 | Lack of water
OF5 | U1 | 9135 | 2019-08-17 22:49 | 2019-08-21 10:38 | 12.58 | Lack of water
OF6 | U1 | 9135 | 2019-08-18 22:35 | 2019-08-21 10:18 | 12.58 | Lack of water
OF7 | U1 | 9135 | 2019-08-20 06:17 | 2019-08-21 09:44 | 12.58 | Lack of water
BR6 | SF | 3610 | 2019-08-20 09:31 | 2019-08-20 10:40 | 146 | Switchyard circuit breakers - external (not OMC)
BR9 | SF | 5050 | 2019-08-20 12:35 | 2019-08-20 14:41 | 121 | Ignition system
BR9 | U1 | 5450 | 2019-08-20 15:54 | 2019-08-22 12:07 | 121 | Ignition system
OF8 | U1 | 9135 | 2019-08-21 06:56 | 2019-08-21 09:23 | 12.58 | Lack of water
OF5 | U1 | 9135 | 2019-08-22 17:50 | 2019-08-23 07:15 | 12.58 | Lack of water
OF4 | U1 | 9135 | 2019-08-23 20:09 | 2019-08-25 09:36 | 12.58 | Lack of water
OF5 | U1 | 9720 | 2019-08-24 21:48 | 2019-08-25 07:39 | 12.58 | Other safety problems
OF6 | U1 | 9720 | 2019-08-24 21:50 | 2019-08-25 07:22 | 12.58 | Other safety problems
OF7 | U1 | 9720 | 2019-08-24 21:52 | 2019-08-25 07:04 | 12.58 | Other safety problems
OF8 | U1 | 9720 | 2019-08-24 21:54 | 2019-08-25 06:49 | 12.58 | Other safety problems
OF6 | U1 | 9135 | 2019-08-26 08:46 | 2019-08-28 06:54 | 12.58 | Lack of water
OF5 | U1 | 9135 | 2019-08-26 11:05 | 2019-08-29 07:16 | 12.58 | Lack of water
OF7 | U1 | 9135 | 2019-08-26 14:09 | 2019-08-27 14:42 | 12.58 | Lack of water
OF4 | U1 | 9135 | 2019-08-28 06:54 | 2019-08-31 07:20 | 12.58 | Lack of water
BR3 | U1 | 385 | 2019-08-30 05:55 | 2019-08-30 06:23 | 412 | Igniters
BR3 | U1 | 385 | 2019-08-30 06:53 | 2019-08-30 09:55 | 412 | Igniters
OF5 | U1 | 9720 | 2019-08-30 09:41 | 2019-08-30 10:18 | 12.58 | Other safety problems
OF6 | U1 | 9720 | 2019-08-30 09:44 | 2019-08-30 10:04 | 12.58 | Other safety problems
BR3 | U1 | 385 | 2019-08-30 10:45 | 2019-08-30 13:14 | 412 | Igniters
OF5 | U1 | 9720 | 2019-08-30 15:32 | 2019-08-30 16:30 | 12.58 | Other safety problems
OF6 | U1 | 9720 | 2019-08-30 15:34 | 2019-08-30 16:21 | 12.58 | Other safety problems
OF4 | U1 | 9135 | 2019-08-31 20:44 | 2019-09-03 10:45 | 12.58 | Lack of water
OF5 | U1 | 9135 | 2019-08-31 21:46 | 2019-09-03 06:56 | 12.58 | Lack of water
BR3 | U1 | 4700 | 2019-09-03 12:32 | 2019-09-03 17:49 | 414 | Generator voltage control
TC10 | U1 | 3684 | 2019-09-04 17:47 | 2019-09-04 18:52 | 169 | Other voltage protection devices
OF4 | U1 | 9135 | 2019-09-05 11:03 | 2019-09-20 07:11 | 12.58 | Lack of water
TC10 | U1 | 5041 | 2019-09-05 12:58 | 2019-09-05 15:13 | 169 | Fuel piping and valves
OF5 | U1 | 9135 | 2019-09-06 07:29 | 2019-09-17 10:52 | 12.58 | Lack of water
OF6 | U1 | 9135 | 2019-09-06 10:25 | 2019-09-10 16:39 | 12.58 | Lack of water
OF8 | U1 | 9135 | 2019-09-06 12:15 | 2019-09-07 12:07 | 12.58 | Lack of water
OF7 | U1 | 9135 | 2019-09-06 14:43 | 2019-09-07 14:38 | 12.58 | Lack of water
MC2 | U1 | 1030 | 2019-09-08 17:15 | 2019-09-10 12:34 | 297 | "Boiler screen, wing wall, or slag screen (water tubes only)"
OF8 | U1 | 9135 | 2019-09-09 12:59 | 2019-09-10 16:09 | 12.58 | Lack of water
OF7 | U1 | 9135 | 2019-09-09 13:27 | 2019-09-10 16:31 | 12.58 | Lack of water
BR10 | SF | 5450 | 2019-09-10 11:33 | 2019-09-11 11:13 | 118 | Ignition system
PR12 | U1 | 3600 | 2019-09-11 05:55 | 2019-09-11 12:04 | 25.5 | Switchyard transformers and associated cooling systems - external (OMC)
OF7 | U1 | 9135 | 2019-09-11 21:58 | 2019-09-16 06:52 | 12.58 | Lack of water
OF8 | U1 | 9135 | 2019-09-12 04:15 | 2019-09-13 12:57 | 12.58 | Lack of water
OF6 | U1 | 9135 | 2019-09-12 08:22 | 2019-10-07 06:58 | 12.58 | Lack of water
BR10 | SF | 5041 | 2019-09-12 11:31 | 2019-09-12 12:03 | 118 | Fuel piping and valves
PR13 | SF | 3661 | 2019-09-13 11:29 | 2019-09-13 14:41 | 161 | 4000-7000 volt circuit breakers
TC9 | SF | 5041 | 2019-09-14 02:57 | 2019-09-14 10:45 | 169 | Fuel piping and valves
OF5 | U1 | 9135 | 2019-09-18 01:13 | 2019-09-19 15:23 | 12.58 | Lack of water
OF7 | U1 | 9135 | 2019-09-18 02:26 | 2019-09-19 13:33 | 12.58 | Lack of water
OF8 | U1 | 9135 | 2019-09-18 02:28 | 2019-09-18 10:59 | 12.58 | Lack of water
MC3 | U1 | 1471 | 2019-09-19 17:07 | 2019-09-19 23:19 | 392.5 | Induced draft fan motors - variable speed
MC1 | U1 | 3110 | 2019-09-19 17:09 | 2019-09-20 14:04 | 300 | Condenser tube leaks
OF7 | U1 | 9135 | 2019-09-20 06:34 | 2019-10-01 14:17 | 12.58 | Lack of water
OF4 | U1 | 9135 | 2019-09-20 09:58 | 2019-10-08 06:43 | 12.58 | Lack of water
OF5 | U1 | 9135 | 2019-09-20 11:58 | 2019-10-02 07:24 | 12.58 | Lack of water
OF8 | U1 | 9135 | 2019-09-20 15:58 | 2019-09-22 08:28 | 12.58 | Lack of water
OF8 | U1 | 9135 | 2019-09-23 09:15 | 2019-09-25 07:02 | 12.58 | Lack of water
OF8 | U1 | 9135 | 2019-09-26 06:50 | 2019-09-30 08:00 | 12.58 | Lack of water
OF8 | U1 | 9135 | 2019-09-30 16:05 | 2019-10-01 13:06 | 12.58 | Lack of water
BR6 | U1 | 3611 | 2019-10-01 07:16 | 2019-10-01 08:48 | 157 | Switchyard circuit breakers - external (OMC)
OF7 | U1 | 9135 | 2019-10-02 15:55 | 2019-10-07 07:15 | 12.58 | Lack of water
OF5 | U1 | 9135 | 2019-10-02 18:10 | 2019-10-08 06:34 | 12.58 | Lack of water
OF8 | U1 | 9135 | 2019-10-02 20:13 | 2019-10-04 07:34 | 12.58 | Lack of water
OF1 | U1 | 9135 | 2019-10-09 06:59 | 2019-10-30 07:18 | 12.58 | Lack of water
OF2 | U1 | 9135 | 2019-10-09 10:58 | 2019-10-29 06:28 | 12.58 | Lack of water
OF6 | U1 | 9135 | 2019-10-09 13:51 | 2019-10-21 12:42 | 12.58 | Lack of water
OF3 | U1 | 9135 | 2019-10-09 16:15 | 2019-10-11 08:52 | 12.58 | Lack of water
OF5 | U1 | 9135 | 2019-10-09 17:59 | 2019-10-11 06:48 | 12.58 | Lack of water
OF7 | U1 | 9135 | 2019-10-09 19:45 | 2019-10-14 07:40 | 12.58 | Lack of water
OF4 | U1 | 9135 | 2019-10-09 21:52 | 2019-10-11 06:55 | 12.58 | Lack of water
OF8 | U1 | 9135 | 2019-10-10 00:41 | 2019-10-14 07:21 | 12.58 | Lack of water
BR6 | SF | 5049 | 2019-10-10 10:09 | 2019-10-10 13:20 | 157 | Other fuel system problems
BR6 | U1 | 5640 | 2019-10-10 15:44 | 2019-10-11 09:06 | 157 | Fire detection and extinguishing system
OF3 | U1 | 9135 | 2019-10-11 22:02 | 2019-10-28 09:52 | 12.58 | Lack of water
OF4 | U1 | 9135 | 2019-10-12 01:53 | 2019-10-24 10:40 | 12.58 | Lack of water
OF5 | U1 | 9135 | 2019-10-12 01:55 | 2019-10-18 07:01 | 12.58 | Lack of water
OF7 | U1 | 9135 | 2019-10-15 00:34 | 2019-10-17 07:11 | 12.58 | Lack of water
OF8 | U1 | 9135 | 2019-10-15 02:58 | 2019-10-17 06:50 | 12.58 | Lack of water
TC2 | U1 | 1700 | 2019-10-16 23:00 | 2019-10-18 05:15 | 559.5 | "Feedwater controls (report local controls - feedwater pump, feedwater regulator valve, etc., - with component or system)"
BR6 | SF | 5048 | 2019-10-17 05:06 | 2019-10-17 13:36 | 157 | Gas fuel system including controls and instrumentation
OF5 | U1 | 9135 | 2019-10-18 22:13 | 2019-10-21 06:55 | 12.58 | Lack of water
MC2 | U1 | 4260 | 2019-10-19 03:16 | 2019-10-19 05:34 | 297 | Main stop valves
BR9 | SF | 3612 | 2019-10-21 09:08 | 2019-10-21 13:32 | 118 | Switchyard system protection devices - external (OMC)
BR8 | U1 | 3612 | 2019-10-21 09:08 | 2019-10-21 13:32 | 118 | Switchyard system protection devices - external (OMC)
OF6 | U1 | 9135 | 2019-10-22 06:01 | 2019-10-23 09:30 | 12.58 | Lack of water
OF5 | U1 | 9135 | 2019-10-22 09:26 | 2019-10-23 11:55 | 12.58 | Lack of water
OF7 | U1 | 9135 | 2019-10-22 11:57 | 2019-10-23 08:06 | 12.58 | Lack of water
OF8 | U1 | 9135 | 2019-10-22 13:53 | 2019-10-23 06:56 | 12.58 | Lack of water
TC5 | SF | 5041 | 2019-10-25 04:47 | 2019-10-25 07:31 | 169 | Fuel piping and valves
OF4 | U1 | 3999 | 2019-10-28 10:28 | 2019-10-28 11:01 | 12.58 | Other miscellaneous balance of plant problems
BR5 | SF | 5640 | 2019-11-04 06:26 | 2019-11-04 10:26 | 120 | Fire detection and extinguishing system
BR10 | U1 | 5201 | 2019-11-04 06:31 | 2019-11-04 09:02 | 118 | Load shaft and bearings
BR5 | U1 | 4810 | 2019-11-04 11:54 | 2019-11-04 14:29 | 120 | Generator output breaker
BR5 | SF | 3974 | 2019-11-06 05:25 | 2019-11-06 08:55 | 120 | DCS - logic problems
PR13 | SF | 5016 | 2019-11-08 04:28 | 2019-11-08 12:15 | 161 | High pressure compressor bleed valves
OF4 | U1 | 9135 | 2019-11-12 10:59 | 2019-11-13 14:15 | 12.58 | Lack of water
OF6 | U1 | 4750 | 2019-11-13 22:18 | 2019-11-14 08:04 | 12.58 | Other generator controls and metering problems
GH3 | U1 | 4630 | 2019-11-15 22:00 | 2019-11-16 13:34 | 478.5 | Liquid cooling system
BR8 | U1 | 5550 | 2019-11-16 12:52 | 2019-11-19 14:54 | 118 | Turning gear and motor
OF1 | U1 | 9135 | 2019-11-17 04:47 | 2019-11-23 10:13 | 12.58 | Lack of water
OF2 | U1 | 9135 | 2019-11-17 18:46 | 2019-11-20 13:51 | 12.58 | Lack of water
TC1 | U1 | 680 | 2019-11-17 21:29 | 2019-11-18 00:24 | 369.75 | Feedwater valves (not feedwater regulating valve)
TC10 | U1 | 4609 | 2019-11-17 23:56 | 2019-11-18 01:09 | 169 | Other exciter problems
OF8 | U1 | 9135 | 2019-11-18 09:22 | 2019-11-23 11:13 | 12.58 | Lack of water
OF7 | U1 | 9135 | 2019-11-18 14:19 | 2019-11-25 08:49 | 12.58 | Lack of water
GH2 | U1 | 3661 | 2019-11-19 15:42 | 2019-11-19 16:22 | 485.5 | 4000-7000 volt circuit breakers
OF6 | U1 | 9135 | 2019-11-21 13:40 | 2019-11-25 11:15 | 12.58 | Lack of water
TC1 | U1 | 1035 | 2019-11-24 10:03 | 2019-11-25 07:40 | 369.75 | Platen superheater
TC5 | SF | 5001 | 2019-12-02 05:52 | 2019-12-02 10:07 | 179 | Inlet air vanes/nozzles
TC6 | SF | 5001 | 2019-12-02 05:57 | 2019-12-02 14:19 | 179 | Inlet air vanes/nozzles
OF1 | U1 | 9000 | 2019-12-02 14:59 | 2019-12-06 10:57 | 12.58 | Flood
OF2 | U1 | 9000 | 2019-12-03 00:54 | 2019-12-06 10:04 | 12.58 | Flood
OF3 | U1 | 9000 | 2019-12-03 01:31 | 2019-12-06 09:53 | 12.58 | Flood
OF5 | U1 | 9000 | 2019-12-03 05:03 | 2019-12-05 14:18 | 12.58 | Flood
OF4 | U1 | 9000 | 2019-12-03 05:05 | 2019-12-05 14:24 | 12.58 | Flood
OF8 | U1 | 9000 | 2019-12-03 08:10 | 2019-12-05 11:09 | 12.58 | Flood
OF7 | U1 | 9000 | 2019-12-03 08:41 | 2019-12-05 11:22 | 12.58 | Flood
OF6 | U1 | 9000 | 2019-12-03 08:44 | 2019-12-05 13:57 | 12.58 | Flood
TC5 | U1 | 5248 | 2019-12-05 19:07 | 2019-12-07 17:06 | 179 | Gas Turbine Control System - logic problems
OF6 | U1 | 7110 | 2019-12-06 06:35 | 2019-12-06 13:18 | 12.58 | Intake channel or flume (including trash racks)
MC3 | U1 | 4420 | 2019-12-06 20:17 | 2019-12-07 09:50 | 394 | Vibration of the turbine generator unit that cannot be attributed to a specific cause such as bearings or blades (use this code for balance moves)
MC3 | U1 | 4420 | 2019-12-08 19:13 | 2019-12-09 07:22 | 394 | Vibration of the turbine generator unit that cannot be attributed to a specific cause such as bearings or blades (use this code for balance moves)
MC3 | U1 | 4420 | 2019-12-09 23:54 | 2019-12-10 09:21 | 394 | Vibration of the turbine generator unit that cannot be attributed to a specific cause such as bearings or blades (use this code for balance moves)
OF2 | U1 | 7141 | 2019-12-13 11:12 | 2019-12-13 11:35 | 12.58 | Wicket gate operating mechanism or positioner
OF1 | U1 | 9000 | 2019-12-13 22:22 | 2019-12-24 13:50 | 12.58 | Flood
OF2 | U1 | 9000 | 2019-12-14 11:54 | 2019-12-24 13:29 | 12.58 | Flood
OF3 | U1 | 9000 | 2019-12-14 12:02 | 2019-12-24 13:11 | 12.58 | Flood
OF4 | U1 | 9000 | 2019-12-14 12:25 | 2019-12-24 12:55 | 12.58 | Flood
OF5 | U1 | 9000 | 2019-12-14 12:59 | 2019-12-24 10:45 | 12.58 | Flood
OF6 | U1 | 7110 | 2019-12-14 13:11 | 2019-12-14 13:42 | 12.58 | Intake channel or flume (including trash racks)
OF7 | U1 | 9000 | 2019-12-14 13:18 | 2019-12-24 10:14 | 12.58 | Flood
OF8 | U1 | 9000 | 2019-12-14 13:20 | 2019-12-24 10:03 | 12.58 | Flood
OF6 | U2 | 7052 | 2019-12-14 14:32 | 2019-12-17 16:33 | 12.58 | "Other turbine control problems (Report specific wicket gate controls, etc., using the code for the appropriate equipment item.)"
BR3 | U1 | 1999 | 2019-12-16 21:14 | 2019-12-20 22:00 | 416 | "Boiler, miscellaneous"
OF6 | U1 | 9000 | 2019-12-17 16:33 | 2019-12-24 10:34 | 12.58 | Flood
BR10 | U1 | 5570 | 2019-12-18 06:08 | 2019-12-18 20:01 | 138 | Cooling water system
BR8 | U1 | 5449 | 2019-12-18 08:22 | 2019-12-18 11:40 | 128 | Other fuel system problems
TC1 | U1 | 4750 | 2019-12-18 12:36 | 2019-12-18 22:18 | 369.75 | Other generator controls and metering problems
MC2 | U1 | 1000 | 2019-12-18 21:54 | 2019-12-21 05:06 | 297 | Waterwall (Furnace wall)
TC1 | U1 | 9900 | 2019-12-18 22:27 | 2019-12-18 23:15 | 369.75 | Operator error
BR3 | U1 | 3344 | 2019-12-22 11:36 | 2019-12-22 18:30 | 416 | Deaerator (including level control)
BR3 | U1 | 4262 | 2019-12-22 18:30 | 2019-12-23 02:08 | 416 | Intercept valves
GH2 | U1 | 3631 | 2019-12-25 03:24 | 2019-12-25 05:30 | 486 | 400-700 volt circuit breakers
GH2 | U1 | 4535 | 2019-12-25 06:07 | 2019-12-25 09:55 | 486 | "Stator, General"
OF4 | U1 | 7141 | 2019-12-26 12:05 | 2019-12-26 16:08 | 12.58 | Wicket gate operating mechanism or positioner
PR12 | SF | 5530 | 2019-12-27 11:56 | 2019-12-27 16:04 | 28 | Starting system (including motor)
GH3 | U1 | 4609 | 2019-12-28 06:46 | 2019-12-28 15:10 | 476 | Other exciter problems
MC1 | U1 | 3273 | 2019-12-28 13:34 | 2019-12-28 18:00 | 300 | "Debris in circulating water from outside sources (leaves, mud, etc.)"
OF1 | U1 | 9000 | 2019-12-31 07:34 | 2019-12-31 23:59 | 12.58 | Flood
OF2 | U1 | 9000 | 2019-12-31 09:59 | 2019-12-31 23:59 | 12.58 | Flood
OF5 | U1 | 9000 | 2019-12-31 11:21 | 2019-12-31 23:59 | 12.58 | Flood
OF4 | U1 | 9000 | 2019-12-31 11:28 | 2019-12-31 23:59 | 12.58 | Flood
OF3 | U1 | 9000 | 2019-12-31 11:45 | 2019-12-31 23:59 | 12.58 | Flood
OF8 | U1 | 9000 | 2019-12-31 12:47 | 2019-12-31 23:59 | 12.58 | Flood
OF7 | U1 | 9000 | 2019-12-31 12:50 | 2019-12-31 23:59 | 12.58 | Flood
OF6 | U1 | 9000 | 2019-12-31 12:52 | 2019-12-31 23:59 | 12.58 | Flood
Note: The "MW on Outage" value is the Seasonal Net Unit Rating for Fossil Fuel units and the Generator Nameplate Rating for Hydro and Solar units.

## 2020
UnitName | EventType | CauseCode | EventStart | EventEnd | MW On Outage | Cause
OF6 | U1 | 9000 | 2020-01-01 | 2020-01-10 11:43 | 12.58 | Flood
OF5 | U1 | 9000 | 2020-01-01 | 2020-01-10 11:53 | 12.58 | Flood
OF3 | U1 | 9000 | 2020-01-01 | 2020-01-10 14:52 | 12.58 | Flood
OF2 | U1 | 9000 | 2020-01-01 | 2020-01-18 14:09 | 12.58 | Flood
OF1 | U1 | 9000 | 2020-01-01 | 2020-01-18 14:25 | 12.58 | Flood
OF7 | U1 | 9000 | 2020-01-01 | 2020-01-10 10:09 | 12.58 | Flood
OF4 | U1 | 9000 | 2020-01-01 | 2020-01-10 14:34 | 12.58 | Flood
OF8 | U1 | 9000 | 2020-01-01 | 2020-01-10 09:48 | 12.58 | Flood
OF3 | U1 | 9000 | 2020-01-14 09:56 | 2020-01-18 13:48 | 12.58 | Flood
OF5 | U1 | 9000 | 2020-01-14 09:58 | 2020-01-18 11:28 | 12.58 | Flood
OF4 | U1 | 9000 | 2020-01-14 10:06 | 2020-01-18 13:36 | 12.58 | Flood
OF6 | U1 | 9000 | 2020-01-15 14:45 | 2020-01-18 11:19 | 12.58 | Flood
OF7 | U1 | 9000 | 2020-01-16 08:30 | 2020-01-18 10:09 | 12.58 | Flood
OF8 | U1 | 9000 | 2020-01-17 09:55 | 2020-01-18 09:05 | 12.58 | Flood
BR3 | U1 | 4302 | 2020-01-20 05:59 | 2020-01-20 13:10 | 416 | Turbine trip devices (including instruments)
OF1 | U1 | 9000 | 2020-01-21 09:42 | 2020-01-24 10:58 | 12.58 | Flood
MC1 | U1 | 4270 | 2020-01-25 19:58 | 2020-01-26 02:52 | 300 | Crossover or under piping
OF1 | U1 | 9000 | 2020-01-27 06:52 | 2020-02-01 14:36 | 12.58 | Flood
OF2 | U1 | 9000 | 2020-01-27 07:35 | 2020-02-01 13:16 | 12.58 | Flood
OF3 | U1 | 9000 | 2020-01-27 18:41 | 2020-02-01 12:59 | 12.58 | Flood
OF4 | U1 | 9000 | 2020-01-27 18:49 | 2020-02-01 13:34 | 12.58 | Flood
OF5 | U1 | 9000 | 2020-01-27 18:53 | 2020-02-01 11:01 | 12.58 | Flood
OF6 | U1 | 9000 | 2020-01-28 15:13 | 2020-02-01 10:39 | 12.58 | Flood
TC2 | U2 | 1090 | 2020-01-29 01:14 | 2020-01-30 02:14 | 570 | Other boiler tube leaks
OF7 | U1 | 9000 | 2020-01-29 07:41 | 2020-02-01 10:21 | 12.58 | Flood
OF8 | U1 | 9000 | 2020-01-29 08:39 | 2020-02-01 10:08 | 12.58 | Flood
BR7 | SF | 4750 | 2020-01-30 06:00 | 2020-01-30 06:14 | 171 | Other generator controls and metering problems
OF1 | U1 | 9000 | 2020-02-07 22:04 | 2020-02-24 11:22 | 12.58 | Flood
OF2 | U1 | 9000 | 2020-02-08 09:19 | 2020-02-24 11:02 | 12.58 | Flood
OF5 | U1 | 9000 | 2020-02-08 12:15 | 2020-02-24 14:14 | 12.58 | Flood
OF3 | U1 | 9000 | 2020-02-08 12:28 | 2020-02-24 10:38 | 12.58 | Flood
OF4 | U1 | 9000 | 2020-02-08 12:30 | 2020-02-24 10:21 | 12.58 | Flood
OF6 | U1 | 9000 | 2020-02-08 22:23 | 2020-02-24 13:53 | 12.58 | Flood
OF7 | U1 | 9000 | 2020-02-09 08:42 | 2020-02-24 13:34 | 12.58 | Flood
OF8 | U1 | 9000 | 2020-02-09 08:44 | 2020-02-24 13:17 | 12.58 | Flood
BR10 | U1 | 5447 | 2020-02-14 04:30 | 2020-02-14 05:01 | 138 | Gas fuel system including controls and instrumentation
BR10 | U1 | 5120 | 2020-02-14 06:12 | 2020-02-14 09:23 | 138 | Hydraulic oil system
BR6 | SF | 5017 | 2020-02-14 07:20 | 2020-02-14 13:08 | 171 | Low pressure compressor bleed valves
BR7 | SF | 5102 | 2020-02-14 07:50 | 2020-02-14 13:20 | 171 | Vanes/nozzles
BR5 | SF | 5170 | 2020-02-14 08:13 | 2020-02-14 14:17 | 130 | Cooling water system
MC3 | U1 | 4420 | 2020-02-20 15:30 | 2020-02-20 19:27 | 394 | Vibration of the turbine generator unit that cannot be attributed to a specific cause such as bearings or blades (use this code for balance moves)
BR5 | SF | 5450 | 2020-02-27 06:00 | 2020-02-27 06:07 | 130 | Ignition system
OF1 | U1 | 7110 | 2020-03-02 06:59 | 2020-03-10 13:02 | 12.58 | Intake channel or flume (including trash racks)
GH4 | U1 | 1040 | 2020-03-02 09:34 | 2020-03-03 17:03 | 478 | First superheater
MC3 | U1 | 4420 | 2020-03-02 10:31 | 2020-03-02 12:30 | 392.5 | Vibration of the turbine generator unit that cannot be attributed to a specific cause such as bearings or blades (use this code for balance moves)
MC4 | U1 | 4302 | 2020-03-04 09:37 | 2020-03-04 13:57 | 481.5 | Turbine trip devices (including instruments)
OF2 | U1 | 7110 | 2020-03-05 14:18 | 2020-03-10 12:37 | 12.58 | Intake channel or flume (including trash racks)
OF5 | U1 | 7110 | 2020-03-05 15:05 | 2020-03-10 10:21 | 12.58 | Intake channel or flume (including trash racks)
OF4 | U1 | 7110 | 2020-03-05 15:07 | 2020-03-10 11:58 | 12.58 | Intake channel or flume (including trash racks)
OF3 | U1 | 7110 | 2020-03-05 15:09 | 2020-03-10 12:08 | 12.58 | Intake channel or flume (including trash racks)
OF6 | U1 | 9000 | 2020-03-05 21:30 | 2020-03-10 10:06 | 12.58 | Flood
OF7 | U1 | 9000 | 2020-03-06 06:48 | 2020-03-10 09:24 | 12.58 | Flood
OF8 | U1 | 9000 | 2020-03-06 06:50 | 2020-03-10 09:14 | 12.58 | Flood
BR5 | U1 | 5050 | 2020-03-10 17:58 | 2020-03-11 16:24 | 120 | Ignition system
OF6 | U1 | 3824 | 2020-03-10 22:41 | 2020-03-11 09:29 | 12.58 | Closed cooling water system fouling
OF1 | U1 | 9000 | 2020-03-13 19:11 | 2020-04-06 13:13 | 12.58 | Flood
OF2 | U1 | 9000 | 2020-03-14 18:41 | 2020-04-06 12:58 | 12.58 | Flood
OF3 | U1 | 9000 | 2020-03-15 10:05 | 2020-04-06 12:12 | 12.58 | Flood
OF4 | U1 | 9000 | 2020-03-15 10:11 | 2020-04-06 11:57 | 12.58 | Flood
OF5 | U1 | 9000 | 2020-03-15 10:17 | 2020-04-06 10:11 | 12.58 | Flood
OF6 | U1 | 9000 | 2020-03-15 10:23 | 2020-04-06 09:56 | 12.58 | Flood
OF7 | U1 | 9000 | 2020-03-15 10:31 | 2020-04-06 09:02 | 12.58 | Flood
OF8 | U1 | 9000 | 2020-03-15 10:35 | 2020-04-06 08:51 | 12.58 | Flood
BR6 | SF | 5246 | 2020-03-16 04:45 | 2020-03-16 06:01 | 157 | Gas Turbine Control System - hardware problems (including card failure)
BR7 | SF | 5246 | 2020-03-16 05:15 | 2020-03-16 06:17 | 157 | Gas Turbine Control System - hardware problems (including card failure)
BR6 | U1 | 5248 | 2020-03-16 06:04 | 2020-03-16 09:41 | 157 | Gas Turbine Control System - logic problems
MC1 | U1 | 741 | 2020-03-17 02:21 | 2020-03-17 16:29 | 300 | Boiler recirculation pumps - motors
BR6 | SF | 3681 | 2020-03-20 12:34 | 2020-03-20 17:11 | 157 | Other voltage circuit breakers
BR8 | U1 | 5150 | 2020-03-23 14:53 | 2020-03-23 18:27 | 118 | Turning gear and motor
BR9 | SF | 3611 | 2020-03-28 03:06 | 2020-03-28 09:26 | 118 | Switchyard circuit breakers - external (OMC)
GH3 | U1 | 3611 | 2020-03-31 02:29 | 2020-04-03 03:33 | 478.5 | Switchyard circuit breakers - external (OMC)
GH1 | U1 | 1000 | 2020-04-02 07:45 | 2020-04-04 08:00 | 477 | Waterwall (Furnace wall)
BR6 | U1 | 5550 | 2020-04-03 01:22 | 2020-04-08 20:30 | 157 | Turning gear and motor
CR7 | U1 | 5041 | 2020-04-03 16:06 | 2020-04-04 00:35 | 694 | Fuel piping and valves
OF7 | U1 | 3824 | 2020-04-07 05:57 | 2020-04-07 10:28 | 12.58 | Closed cooling water system fouling
OF7 | U1 | 3670 | 2020-04-08 17:50 | 2020-04-09 10:21 | 12.58 | 12-15kV transformers
OF8 | U1 | 3670 | 2020-04-08 17:50 | 2020-04-09 09:59 | 12.58 | 12-15kV transformers
OF6 | U1 | 3670 | 2020-04-08 17:50 | 2020-04-09 10:42 | 12.58 | 12-15kV transformers
OF5 | U1 | 3670 | 2020-04-08 17:50 | 2020-04-09 10:59 | 12.58 | 12-15kV transformers
OF1 | U1 | 9000 | 2020-04-10 14:54 | 2020-04-22 13:28 | 12.58 | Flood
Dix 3 | U1 | 7053 | 2020-04-13 07:40 | 2020-04-13 08:09 | 11.2 | Governor oil system
Dix 2 | U1 | 7053 | 2020-04-13 07:40 | 2020-04-13 08:09 | 11.2 | Governor oil system
Dix 1 | U1 | 7053 | 2020-04-13 07:40 | 2020-04-13 08:09 | 11.2 | Governor oil system
OF2 | U1 | 7110 | 2020-04-13 13:18 | 2020-04-22 13:11 | 12.58 | Intake channel or flume (including trash racks)
OF4 | U1 | 9000 | 2020-04-13 22:13 | 2020-04-22 09:51 | 12.58 | Flood
OF5 | U1 | 9000 | 2020-04-13 22:14 | 2020-04-21 13:22 | 12.58 | Flood
OF3 | U1 | 9000 | 2020-04-13 22:29 | 2020-04-22 10:06 | 12.58 | Flood
OF6 | U1 | 9000 | 2020-04-15 09:43 | 2020-04-21 13:10 | 12.58 | Flood
OF7 | U1 | 9000 | 2020-04-16 05:51 | 2020-04-21 09:12 | 12.58 | Flood
OF8 | U1 | 9000 | 2020-04-16 05:53 | 2020-04-21 09:02 | 12.58 | Flood
MC1 | U1 | 1475 | 2020-04-22 07:06 | 2020-04-22 12:56 | 300 | Induced draft fan controls
TC1 | U1 | 1799 | 2020-04-24 10:15 | 2020-04-24 11:51 | 369.75 | Other boiler instrumentation and control problems
OF1 | U1 | 9000 | 2020-04-26 10:59 | 2020-05-12 13:52 | 12.58 | Flood
Dix 1 | U1 | 7053 | 2020-04-27 00:19 | 2020-04-27 01:49 | 11.2 | Governor oil system
Dix 3 | U1 | 7053 | 2020-04-27 00:33 | 2020-04-27 00:42 | 11.2 | Governor oil system
OF2 | U1 | 9000 | 2020-04-28 07:28 | 2020-05-12 13:21 | 12.58 | Flood
OF5 | U1 | 9000 | 2020-04-28 14:08 | 2020-05-11 13:50 | 12.58 | Flood
OF4 | U1 | 9000 | 2020-04-28 14:10 | 2020-05-12 12:24 | 12.58 | Flood
OF3 | U1 | 9000 | 2020-04-28 14:12 | 2020-05-12 12:39 | 12.58 | Flood
OF6 | U1 | 9000 | 2020-04-29 10:20 | 2020-05-11 13:32 | 12.58 | Flood
OF7 | U1 | 9000 | 2020-04-29 10:23 | 2020-05-11 13:11 | 12.58 | Flood
OF8 | U1 | 9000 | 2020-04-29 10:25 | 2020-05-11 12:44 | 12.58 | Flood
CR7 | U1 | 3430 | 2020-05-04 23:05 | 2020-05-05 00:16 | 694 | Feedwater regulating (boiler level control) valve
MC1 | U1 | 370 | 2020-05-07 09:50 | 2020-05-07 11:36 | 300 | Burner instruments and controls (except light off)
HA2 | SF | 5120 | 2020-05-14 11:30 | 2020-05-21 13:55 | 12.8333 | Hydraulic oil system
HA1 | SF | 5520 | 2020-05-14 11:30 | 2020-05-14 12:33 | 12.8333 | Hydraulic oil system
GH4 | U1 | 1060 | 2020-05-14 23:24 | 2020-05-16 02:38 | 478 | First reheater
OF1 | U1 | 9000 | 2020-05-19 10:14 | 2020-05-30 10:31 | 12.58 | Flood
OF2 | U1 | 9000 | 2020-05-20 07:10 | 2020-05-30 09:10 | 12.58 | Flood
OF3 | U1 | 9000 | 2020-05-20 08:35 | 2020-05-30 07:45 | 12.58 | Flood
OF4 | U1 | 9000 | 2020-05-20 08:39 | 2020-05-30 07:25 | 12.58 | Flood
OF5 | U1 | 9000 | 2020-05-20 08:47 | 2020-05-30 08:49 | 12.58 | Flood
OF6 | U1 | 9000 | 2020-05-20 08:51 | 2020-05-29 13:45 | 12.58 | Flood
OF7 | U1 | 9000 | 2020-05-20 08:56 | 2020-05-29 13:06 | 12.58 | Flood
OF8 | U1 | 9000 | 2020-05-20 09:01 | 2020-05-29 12:34 | 12.58 | Flood
HA2 | SF | 5450 | 2020-05-21 13:55 | 2020-05-22 12:52 | 12.8333 | Ignition system
GH1 | U1 | 3653 | 2020-05-27 06:53 | 2020-05-27 13:22 | 477 | DC protection devices
BR5 | SF | 5130 | 2020-05-27 09:15 | 2020-06-04 18:18 | 120 | Starting system (including motor)
OF1 | U1 | 7110 | 2020-05-31 18:47 | 2020-06-03 07:51 | 12.58 | Intake channel or flume (including trash racks)
GH3 | U1 | 1480 | 2020-06-02 03:29 | 2020-06-02 07:03 | 481 | Other induced draft fan problems
OF8 | U1 | 3710 | 2020-06-03 13:41 | 2020-06-10 16:36 | 12.58 | Transmission line (connected to powerhouse switchyard to 1st Substation)
OF1 | U1 | 3710 | 2020-06-04 09:48 | 2020-06-04 12:57 | 12.58 | Transmission line (connected to powerhouse switchyard to 1st Substation)
OF2 | U1 | 3710 | 2020-06-04 12:59 | 2020-06-08 07:17 | 12.58 | Transmission line (connected to powerhouse switchyard to 1st Substation)
OF1 | U1 | 3710 | 2020-06-04 14:17 | 2020-06-17 12:51 | 12.58 | Transmission line (connected to powerhouse switchyard to 1st Substation)
TC1 | U1 | 260 | 2020-06-08 22:14 | 2020-06-09 00:58 | 369.75 | Primary air fan
BR7 | U1 | 5079 | 2020-06-09 11:29 | 2020-06-09 14:23 | 146 | Other combustor problems
OF2 | U1 | 7110 | 2020-06-10 09:42 | 2020-06-10 17:19 | 12.58 | Intake channel or flume (including trash racks)
OF3 | U1 | 7110 | 2020-06-10 09:46 | 2020-06-10 17:19 | 12.58 | Intake channel or flume (including trash racks)
OF4 | U1 | 7110 | 2020-06-10 09:49 | 2020-06-10 17:19 | 12.58 | Intake channel or flume (including trash racks)
OF5 | U1 | 7110 | 2020-06-10 09:52 | 2020-06-10 17:19 | 12.58 | Intake channel or flume (including trash racks)
OF6 | U1 | 7110 | 2020-06-10 09:54 | 2020-06-10 17:05 | 12.58 | Intake channel or flume (including trash racks)
OF7 | U1 | 7110 | 2020-06-10 10:00 | 2020-06-10 16:42 | 12.58 | Intake channel or flume (including trash racks)
OF4 | U1 | 3710 | 2020-06-10 17:19 | 2020-06-17 12:46 | 12.58 | Transmission line (connected to powerhouse switchyard to 1st Substation)
OF3 | U1 | 3710 | 2020-06-10 17:19 | 2020-06-17 12:45 | 12.58 | Transmission line (connected to powerhouse switchyard to 1st Substation)
OF2 | U1 | 3710 | 2020-06-10 17:19 | 2020-06-17 12:32 | 12.58 | Transmission line (connected to powerhouse switchyard to 1st Substation)
Dix 3 | U1 | 3720 | 2020-06-11 16:51 | 2020-06-12 11:15 | 11.2 | Transmission equipment at the 1st substation (see code 9300 if applicable)
Dix 1 | U1 | 3720 | 2020-06-11 20:10 | 2020-06-12 02:20 | 11.2 | Transmission equipment at the 1st substation (see code 9300 if applicable)
Dix 2 | U1 | 3720 | 2020-06-11 20:10 | 2020-06-12 02:20 | 11.2 | Transmission equipment at the 1st substation (see code 9300 if applicable)
Dix 2 | U1 | 4560 | 2020-06-15 15:02 | 2020-06-15 15:29 | 11.2 | Generator vibration (excluding vibration due to failed bearing and other components)
Dix 2 | U1 | 4560 | 2020-06-15 15:30 | 2020-06-15 16:36 | 11.2 | Generator vibration (excluding vibration due to failed bearing and other components)
OF5 | U1 | 3710 | 2020-06-16 12:14 | 2020-06-16 14:02 | 12.58 | Transmission line (connected to powerhouse switchyard to 1st Substation)
OF6 | U1 | 3710 | 2020-06-16 12:17 | 2020-06-16 13:51 | 12.58 | Transmission line (connected to powerhouse switchyard to 1st Substation)
OF7 | U1 | 3710 | 2020-06-16 12:21 | 2020-06-16 13:40 | 12.58 | Transmission line (connected to powerhouse switchyard to 1st Substation)
OF8 | U1 | 3710 | 2020-06-16 12:23 | 2020-06-16 13:31 | 12.58 | Transmission line (connected to powerhouse switchyard to 1st Substation)
OF5 | U1 | 3710 | 2020-06-17 08:58 | 2020-06-17 09:29 | 12.58 | Transmission line (connected to powerhouse switchyard to 1st Substation)
OF6 | U1 | 3710 | 2020-06-17 09:33 | 2020-06-17 09:56 | 12.58 | Transmission line (connected to powerhouse switchyard to 1st Substation)
OF7 | U1 | 3710 | 2020-06-17 10:03 | 2020-06-17 10:28 | 12.58 | Transmission line (connected to powerhouse switchyard to 1st Substation)
OF8 | U1 | 3710 | 2020-06-17 10:30 | 2020-06-17 11:04 | 12.58 | Transmission line (connected to powerhouse switchyard to 1st Substation)
TC5 | U2 | 4650 | 2020-06-18 18:00 | 2020-06-18 19:45 | 159 | Other cooling system problems
BR7 | U1 | 5479 | 2020-06-22 12:20 | 2020-06-22 14:15 | 146 | Other combustor problems
OF1 | U1 | 9350 | 2020-06-26 06:12 | 2020-06-26 12:50 | 12.58 | Public Safety (water hazard or river rescue)
OF2 | U1 | 9350 | 2020-06-26 06:14 | 2020-06-26 12:37 | 12.58 | Public Safety (water hazard or river rescue)
OF3 | U1 | 9350 | 2020-06-26 06:17 | 2020-06-26 12:23 | 12.58 | Public Safety (water hazard or river rescue)
OF5 | U1 | 9350 | 2020-06-26 06:21 | 2020-06-26 12:10 | 12.58 | Public Safety (water hazard or river rescue)
OF6 | U1 | 9350 | 2020-06-26 06:23 | 2020-06-26 10:56 | 12.58 | Public Safety (water hazard or river rescue)
OF7 | U1 | 9350 | 2020-06-26 06:26 | 2020-06-26 12:00 | 12.58 | Public Safety (water hazard or river rescue)
OF8 | U1 | 9350 | 2020-06-26 06:27 | 2020-06-26 10:20 | 12.58 | Public Safety (water hazard or river rescue)
BR8 | SF | 3619 | 2020-06-26 09:48 | 2020-06-26 09:54 | 121 | Other switchyard equipment - external (OMC)
OF6 | U1 | 4650 | 2020-06-26 14:16 | 2020-06-26 15:16 | 12.58 | Other cooling system problems
OF6 | U1 | 7050 | 2020-06-26 15:21 | 2020-06-26 15:35 | 12.58 | Turbine governor
OF6 | U1 | 9001 | 2020-06-28 01:35 | 2020-06-29 07:56 | 12.58 | Drought
OF4 | U1 | 9001 | 2020-06-28 07:12 | 2020-06-29 09:59 | 12.58 | Drought
OF1 | U1 | 9001 | 2020-06-28 09:25 | 2020-06-29 09:59 | 12.58 | Drought
OF2 | U1 | 9001 | 2020-06-28 12:17 | 2020-06-29 09:35 | 12.58 | Drought
TC1 | U1 | 1000 | 2020-06-29 00:56 | 2020-06-30 15:00 | 369.75 | Waterwall (Furnace wall)
OF6 | U1 | 9350 | 2020-06-30 08:00 | 2020-06-30 10:25 | 12.58 | Public Safety (water hazard or river rescue)
OF7 | U1 | 9350 | 2020-06-30 08:07 | 2020-06-30 10:15 | 12.58 | Public Safety (water hazard or river rescue)
OF8 | U1 | 9350 | 2020-06-30 08:12 | 2020-06-30 10:00 | 12.58 | Public Safety (water hazard or river rescue)
TC1 | U1 | 3499 | 2020-07-01 21:15 | 2020-07-03 09:14 | 369.75 | Other feedwater system problems
OF6 | U1 | 9135 | 2020-07-04 14:49 | 2020-07-20 13:22 | 12.58 | Lack of water
OF3 | U1 | 9135 | 2020-07-05 04:48 | 2020-07-31 07:21 | 12.58 | Lack of water
BR10 | U1 | 5550 | 2020-07-05 20:46 | 2020-07-06 00:46 | 121 | Turning gear and motor
OF1 | U1 | 9135 | 2020-07-06 10:17 | 2020-07-10 09:26 | 12.58 | Lack of water
BR7 | U1 | 3864 | 2020-07-06 14:51 | 2020-07-06 16:03 | 146 | Fire protection system instrumentation and controls
PR13 | SF | 3974 | 2020-07-08 10:55 | 2020-07-09 08:59 | 147 | DCS - logic problems
OF2 | U1 | 9135 | 2020-07-08 15:13 | 2020-07-10 10:42 | 12.58 | Lack of water
OF5 | U1 | 9135 | 2020-07-08 23:52 | 2020-07-10 06:53 | 12.58 | Lack of water
MC3 | U1 | 1799 | 2020-07-09 01:11 | 2020-07-09 03:54 | 391 | Other boiler instrumentation and control problems
MC1 | U1 | 782 | 2020-07-09 07:28 | 2020-07-10 23:05 | 300 | Headers and caps
OF7 | U1 | 9135 | 2020-07-09 07:34 | 2020-07-10 06:30 | 12.58 | Lack of water
OF1 | U1 | 9135 | 2020-07-11 09:39 | 2020-07-14 10:52 | 12.58 | Lack of water
OF2 | U1 | 9135 | 2020-07-11 10:27 | 2020-07-16 13:43 | 12.58 | Lack of water
GH1 | U1 | 3664 | 2020-07-11 12:34 | 2020-07-11 15:29 | 475 | 4000-7000 volt protection devices
OF1 | U1 | 9135 | 2020-07-16 03:43 | 2020-07-16 09:39 | 12.58 | Lack of water
TC1 | U1 | 3669 | 2020-07-16 08:41 | 2020-07-16 15:04 | 369.75 | Other 4000-7000 volt problems
OF5 | U1 | 9135 | 2020-07-16 09:44 | 2020-07-23 08:54 | 12.58 | Lack of water
OF7 | U1 | 9135 | 2020-07-16 13:47 | 2020-07-17 14:14 | 12.58 | Lack of water
OF1 | U1 | 9135 | 2020-07-16 14:50 | 2020-07-17 07:59 | 12.58 | Lack of water
BR6 | U1 | 3611 | 2020-07-17 07:40 | 2020-07-17 08:01 | 146 | Switchyard circuit breakers - external (OMC)
OF8 | U1 | 9135 | 2020-07-17 07:49 | 2020-07-17 14:04 | 12.58 | Lack of water
OF1 | U1 | 9135 | 2020-07-17 13:54 | 2020-07-20 11:58 | 12.58 | Lack of water
OF2 | U1 | 9135 | 2020-07-17 14:07 | 2020-07-20 13:40 | 12.58 | Lack of water
OF7 | U1 | 9135 | 2020-07-19 11:54 | 2020-07-20 07:08 | 12.58 | Lack of water
BR7 | SF | 5050 | 2020-07-20 07:59 | 2020-07-20 09:59 | 146 | Ignition system
OF6 | U1 | 9135 | 2020-07-20 13:27 | 2020-07-31 07:21 | 12.58 | Lack of water
OF1 | U1 | 9135 | 2020-07-21 05:52 | 2020-07-22 09:06 | 12.58 | Lack of water
OF2 | U1 | 9135 | 2020-07-21 08:58 | 2020-07-22 09:56 | 12.58 | Lack of water
OF7 | U1 | 9135 | 2020-07-21 12:05 | 2020-07-22 06:09 | 12.58 | Lack of water
OF8 | U1 | 9350 | 2020-07-22 09:32 | 2020-07-22 12:09 | 12.58 | Public Safety (water hazard or river rescue)
OF2 | U1 | 4730 | 2020-07-22 17:40 | 2020-07-22 20:06 | 12.58 | Generator current and potential transformers
OF1 | U1 | 9135 | 2020-07-23 06:14 | 2020-07-24 13:25 | 12.58 | Lack of water
OF2 | U1 | 9135 | 2020-07-23 08:39 | 2020-07-25 08:16 | 12.58 | Lack of water
BR6 | U1 | 3690 | 2020-07-23 12:30 | 2020-07-24 13:52 | 146 | "Station Service Power Distribution System, General"
OF2 | U1 | 4730 | 2020-07-25 15:48 | 2020-07-25 21:32 | 12.58 | Generator current and potential transformers
OF2 | U1 | 9135 | 2020-07-25 21:33 | 2020-07-31 07:21 | 12.58 | Lack of water
OF1 | U1 | 9135 | 2020-07-27 10:22 | 2020-07-31 07:21 | 12.58 | Lack of water
BR7 | SF | 5047 | 2020-07-28 11:00 | 2020-07-28 15:31 | 146 | Liquid fuel purge system
OF5 | U1 | 9135 | 2020-07-29 15:16 | 2020-07-30 11:58 | 12.58 | Lack of water
OF7 | U1 | 9135 | 2020-07-29 16:47 | 2020-07-31 06:55 | 12.58 | Lack of water
OF6 | U1 | 3710 | 2020-07-31 07:21 | 2020-08-04 19:34 | 12.58 | Transmission line (connected to powerhouse switchyard to 1st Substation)
OF2 | U1 | 3710 | 2020-07-31 07:21 | 2020-08-04 10:06 | 12.58 | Transmission line (connected to powerhouse switchyard to 1st Substation)
OF3 | U1 | 3710 | 2020-07-31 07:21 | 2020-08-04 19:34 | 12.58 | Transmission line (connected to powerhouse switchyard to 1st Substation)
OF1 | U1 | 7110 | 2020-08-04 07:08 | 2020-08-04 10:15 | 12.58 | Intake channel or flume (including trash racks)
OF5 | U1 | 7110 | 2020-08-04 07:12 | 2020-08-04 19:34 | 12.58 | Intake channel or flume (including trash racks)
OF7 | U1 | 7110 | 2020-08-04 07:16 | 2020-08-04 09:18 | 12.58 | Intake channel or flume (including trash racks)
OF8 | U1 | 7110 | 2020-08-04 07:44 | 2020-08-04 09:09 | 12.58 | Intake channel or flume (including trash racks)
OF5 | U1 | 9135 | 2020-08-04 19:34 | 2020-08-07 15:37 | 12.58 | Lack of water
OF6 | U1 | 9135 | 2020-08-04 19:34 | 2020-08-17 06:45 | 12.58 | Lack of water
OF3 | U1 | 9135 | 2020-08-04 19:34 | 2020-08-16 10:01 | 12.58 | Lack of water
OF1 | U1 | 9135 | 2020-08-04 19:34 | 2020-08-06 06:54 | 12.58 | Lack of water
OF1 | U1 | 9135 | 2020-08-07 14:40 | 2020-08-08 10:41 | 12.58 | Lack of water
MC1 | U1 | 3972 | 2020-08-09 05:47 | 2020-08-09 09:04 | 300 | DCS - hardware problems (including card failure)
OF1 | U1 | 9135 | 2020-08-10 06:38 | 2020-08-11 08:43 | 12.58 | Lack of water
OF2 | U1 | 9135 | 2020-08-10 08:22 | 2020-08-11 08:32 | 12.58 | Lack of water
OF5 | U1 | 9135 | 2020-08-10 10:42 | 2020-08-16 09:24 | 12.58 | Lack of water
OF7 | U1 | 9135 | 2020-08-11 08:35 | 2020-08-16 10:26 | 12.58 | Lack of water
OF8 | U1 | 9135 | 2020-08-11 08:46 | 2020-08-16 09:03 | 12.58 | Lack of water
OF6 | U1 | 9135 | 2020-08-20 05:53 | 2020-08-24 12:07 | 12.58 | Lack of water
OF1 | U1 | 9135 | 2020-08-20 08:11 | 2020-09-04 08:25 | 12.58 | Lack of water
OF5 | U1 | 9135 | 2020-08-21 07:40 | 2020-08-24 11:51 | 12.58 | Lack of water
OF7 | U1 | 9135 | 2020-08-24 11:55 | 2020-08-29 08:30 | 12.58 | Lack of water
OF8 | U1 | 9135 | 2020-08-24 12:11 | 2020-08-27 07:19 | 12.58 | Lack of water
OF2 | U1 | 9135 | 2020-08-24 13:23 | 2020-09-03 15:52 | 12.58 | Lack of water
BR6 | U1 | 3864 | 2020-08-26 17:14 | 2020-08-26 17:36 | 146 | Fire protection system instrumentation and controls
OF4 | U1 | 9135 | 2020-08-28 06:00 | 2020-09-03 11:16 | 12.58 | Lack of water
OF5 | U1 | 9135 | 2020-08-28 13:59 | 2020-08-29 08:51 | 12.58 | Lack of water
GH3 | U1 | 4308 | 2020-09-01 09:19 | 2020-09-01 10:23 | 478.5 | Automatic turbine control systems - digital control and monitoring
TC9 | U1 | 3864 | 2020-09-01 14:50 | 2020-09-01 15:26 | 169 | Fire protection system instrumentation and controls
TC2 | U3 | 1000 | 2020-09-02 15:51 | 2020-09-05 05:08 | 559.5 | Waterwall (Furnace wall)
OF2 | U1 | 9135 | 2020-09-08 05:07 | 2020-09-09 09:37 | 12.58 | Lack of water
OF1 | U1 | 9135 | 2020-09-08 08:15 | 2020-09-09 09:48 | 12.58 | Lack of water
GH4 | U1 | 400 | 2020-09-11 06:10 | 2020-09-14 04:26 | 478 | Burner wind box fires
OF4 | U1 | 9135 | 2020-09-11 07:00 | 2020-09-15 13:55 | 12.58 | Lack of water
OF1 | U1 | 9135 | 2020-09-12 18:26 | 2020-09-15 06:33 | 12.58 | Lack of water
OF8 | U1 | 9135 | 2020-09-12 21:16 | 2020-09-14 11:51 | 12.58 | Lack of water
OF2 | U1 | 9135 | 2020-09-13 16:20 | 2020-09-14 13:37 | 12.58 | Lack of water
OF5 | U1 | 4650 | 2020-09-15 07:32 | 2020-09-15 08:05 | 12.58 | Other cooling system problems
OF1 | U1 | 7110 | 2020-09-15 11:59 | 2020-09-15 15:21 | 12.58 | Intake channel or flume (including trash racks)
OF2 | U1 | 7110 | 2020-09-15 12:01 | 2020-09-15 15:08 | 12.58 | Intake channel or flume (including trash racks)
OF5 | U1 | 7110 | 2020-09-15 12:04 | 2020-09-15 14:45 | 12.58 | Intake channel or flume (including trash racks)
OF6 | U1 | 7110 | 2020-09-15 12:06 | 2020-09-15 14:31 | 12.58 | Intake channel or flume (including trash racks)
OF7 | U1 | 7110 | 2020-09-15 12:07 | 2020-09-15 14:16 | 12.58 | Intake channel or flume (including trash racks)
OF8 | U1 | 7110 | 2020-09-15 12:09 | 2020-09-15 14:05 | 12.58 | Intake channel or flume (including trash racks)
MC1 | U1 | 3972 | 2020-09-16 01:39 | 2020-09-16 02:34 | 300 | DCS - hardware problems (including card failure)
OF1 | U1 | 7110 | 2020-09-16 06:26 | 2020-10-03 09:05 | 12.58 | Intake channel or flume (including trash racks)
OF2 | U1 | 9135 | 2020-09-16 14:00 | 2020-10-29 12:21 | 12.58 | Lack of water
MC1 | U1 | 3972 | 2020-09-17 00:12 | 2020-09-17 01:26 | 300 | DCS - hardware problems (including card failure)
OF4 | U1 | 9135 | 2020-09-17 14:58 | 2020-09-19 09:33 | 12.58 | Lack of water
OF5 | U1 | 9135 | 2020-09-17 18:04 | 2020-09-18 06:42 | 12.58 | Lack of water
OF5 | U1 | 9135 | 2020-09-18 20:48 | 2020-09-19 08:40 | 12.58 | Lack of water
OF7 | U1 | 9135 | 2020-09-18 22:43 | 2020-09-29 06:51 | 12.58 | Lack of water
OF4 | U1 | 9135 | 2020-09-21 19:41 | 2020-10-03 08:38 | 12.58 | Lack of water
OF5 | U1 | 9135 | 2020-09-24 11:18 | 2020-10-03 08:13 | 12.58 | Lack of water
OF6 | U1 | 9135 | 2020-09-24 17:10 | 2020-09-29 10:36 | 12.58 | Lack of water
OF8 | U1 | 9135 | 2020-09-24 20:41 | 2020-09-29 06:36 | 12.58 | Lack of water
OF6 | U1 | 9135 | 2020-09-30 13:57 | 2020-10-03 08:02 | 12.58 | Lack of water
OF7 | U1 | 9135 | 2020-09-30 15:58 | 2020-10-03 07:53 | 12.58 | Lack of water
OF1 | U1 | 9135 | 2020-10-03 21:47 | 2020-10-29 12:21 | 12.58 | Lack of water
OF4 | U1 | 9135 | 2020-10-04 12:13 | 2020-10-29 10:02 | 12.58 | Lack of water
OF5 | U1 | 9135 | 2020-10-04 15:25 | 2020-10-23 07:35 | 12.58 | Lack of water
OF7 | U1 | 9135 | 2020-10-04 19:22 | 2020-10-13 09:31 | 12.58 | Lack of water
OF8 | U1 | 9135 | 2020-10-05 02:17 | 2020-10-08 10:16 | 12.58 | Lack of water
BR8 | SF | 5050 | 2020-10-09 10:53 | 2020-10-09 12:17 | 118 | Ignition system
OF8 | U1 | 9135 | 2020-10-09 16:59 | 2020-10-13 06:41 | 12.58 | Lack of water
GH1 | U1 | 4293 | 2020-10-11 05:39 | 2020-10-11 16:47 | 477 | Hydraulic system pipes and valves
OF6 | U1 | 9135 | 2020-10-16 07:23 | 2020-10-17 12:16 | 12.58 | Lack of water
OF7 | U1 | 9135 | 2020-10-16 09:09 | 2020-10-17 11:18 | 12.58 | Lack of water
OF8 | U1 | 9135 | 2020-10-16 12:23 | 2020-10-17 10:32 | 12.58 | Lack of water
OF3 | U1 | 9135 | 2020-10-23 10:00 | 2020-10-29 11:22 | 12.58 | Lack of water
MC1 | U1 | 740 | 2020-10-24 04:48 | 2020-10-24 05:36 | 300 | Boiler recirculation pumps
OF5 | U1 | 9135 | 2020-10-24 21:16 | 2020-10-27 06:50 | 12.58 | Lack of water
OF7 | U1 | 9135 | 2020-10-24 21:49 | 2020-10-26 07:08 | 12.58 | Lack of water
GH3 | SF | 4240 | 2020-10-29 12:30 | 2020-10-29 15:09 | 478.5 | Bearings
PR12 | U1 | 5206 | 2020-10-30 09:24 | 2020-11-03 10:43 | 25.5 | Clutch
TC2 | U1 | 3402 | 2020-10-30 20:04 | 2020-10-31 05:07 | 559.5 | Startup feedwater pump drives - all types
TC2 | U1 | 3621 | 2020-10-31 06:22 | 2020-10-31 10:45 | 559.5 | Unit auxiliaries transformer
OF1 | U1 | 7110 | 2020-11-01 05:30 | 2020-11-02 15:04 | 12.58 | Intake channel or flume (including trash racks)
MC3 | U1 | 3412 | 2020-11-01 21:18 | 2020-11-01 23:42 | 392.5 | Feedwater pump drive - steam turbine
MC3 | U1 | 800 | 2020-11-01 23:48 | 2020-11-02 00:39 | 392.5 | Drums and drum internals (single drum only)
OF3 | U1 | 3710 | 2020-11-02 08:27 | 2020-11-02 14:28 | 12.58 | Transmission line (connected to powerhouse switchyard to 1st Substation)
TC2 | U1 | 3431 | 2020-11-04 06:40 | 2020-11-04 10:06 | 559.5 | Other feedwater valves
OF1 | U1 | 3710 | 2020-11-05 12:53 | 2020-11-05 16:46 | 12.58 | Transmission line (connected to powerhouse switchyard to 1st Substation)
OF3 | U1 | 3710 | 2020-11-05 12:59 | 2020-11-05 16:08 | 12.58 | Transmission line (connected to powerhouse switchyard to 1st Substation)
MC2 | U1 | 4299 | 2020-11-05 19:02 | 2020-11-06 07:08 | 297 | Other hydraulic system problems
TC2 | U1 | 4290 | 2020-11-05 22:28 | 2020-11-06 03:48 | 559.5 | Hydraulic system pumps
TC2 | U1 | 4099 | 2020-11-06 03:57 | 2020-11-07 08:28 | 559.5 | Other high pressure turbine problems
OF8 | U1 | 9135 | 2020-11-08 19:00 | 2020-11-11 08:27 | 12.58 | Lack of water
OF5 | U1 | 9135 | 2020-11-08 23:00 | 2020-11-12 07:56 | 12.58 | Lack of water
OF6 | U1 | 9135 | 2020-11-09 13:10 | 2020-11-11 12:52 | 12.58 | Lack of water
OF4 | U1 | 9135 | 2020-11-09 13:10 | 2020-11-13 08:10 | 12.58 | Lack of water
OF1 | U1 | 9135 | 2020-11-11 08:15 | 2020-11-16 12:00 | 12.58 | Lack of water
CR7 | U3 | 6114 | 2020-11-12 23:20 | 2020-11-13 13:58 | 694 | HP steam isolation/boundary valves
TC8 | SF | 3610 | 2020-11-13 07:10 | 2020-11-13 11:32 | 169 | Switchyard circuit breakers - external (not OMC)
OF2 | U1 | 7110 | 2020-11-13 07:48 | 2020-11-16 12:00 | 12.58 | Intake channel or flume (including trash racks)
OF3 | U1 | 7110 | 2020-11-13 07:50 | 2020-11-13 08:39 | 12.58 | Intake channel or flume (including trash racks)
CR7 | U1 | 6114 | 2020-11-13 18:19 | 2020-11-15 17:36 | 694 | HP steam isolation/boundary valves
MC2 | U1 | 1470 | 2020-11-17 08:04 | 2020-11-17 09:18 | 297 | Induced draft fan motors and drives
BR10 | U1 | 3864 | 2020-11-19 10:08 | 2020-11-19 15:32 | 118 | Fire protection system instrumentation and controls
GH3 | U1 | 4302 | 2020-11-20 12:42 | 2020-11-20 13:32 | 478.5 | Turbine trip devices (including instruments)
TC9 | U1 | 5170 | 2020-11-24 08:47 | 2020-11-24 10:30 | 169 | Cooling water system
MC1 | U1 | 740 | 2020-12-01 06:53 | 2020-12-01 22:24 | 300 | Boiler recirculation pumps
PR13 | U1 | 4620 | 2020-12-01 12:15 | 2020-12-01 14:04 | 175 | Air cooling system
BR8 | SF | 3823 | 2020-12-02 05:57 | 2020-12-02 06:23 | 128 | Closed cooling water heat exchangers
BR7 | SF | 4700 | 2020-12-03 05:45 | 2020-12-03 06:21 | 171 | Generator voltage control
BR7 | U1 | 5041 | 2020-12-03 06:26 | 2020-12-03 14:54 | 171 | Fuel piping and valves
TC10 | U1 | 4630 | 2020-12-03 13:31 | 2020-12-03 13:57 | 179 | Liquid cooling system
MC4 | SF | 4720 | 2020-12-06 14:20 | 2020-12-07 06:43 | 486 | Generator synchronization equipment
MC4 | U1 | 4265 | 2020-12-07 08:02 | 2020-12-08 07:42 | 486 | Miscellaneous drain and vent valves
BR3 | U2 | 1060 | 2020-12-07 15:51 | 2020-12-10 05:22 | 416 | First reheater
MC4 | SF | 4265 | 2020-12-08 07:42 | 2020-12-09 04:30 | 486 | Miscellaneous drain and vent valves
MC4 | U1 | 4260 | 2020-12-09 11:48 | 2020-12-11 06:34 | 486 | Main stop valves
BR3 | U1 | 1350 | 2020-12-10 07:47 | 2020-12-11 01:02 | 416 | Other miscellaneous boiler tube problems
BR3 | U1 | 1350 | 2020-12-11 02:40 | 2020-12-11 14:16 | 416 | Other miscellaneous boiler tube problems
HA2 | SF | 5041 | 2020-12-11 11:28 | 2020-12-14 12:41 | 13.6667 | Fuel piping and valves
MC4 | U1 | 800 | 2020-12-13 09:06 | 2020-12-13 10:42 | 486 | Drums and drum internals (single drum only)
OF5 | U1 | 7050 | 2020-12-14 00:19 | 2020-12-14 08:01 | 12.58 | Turbine governor
GH2 | U1 | 1060 | 2020-12-14 11:21 | 2020-12-15 15:18 | 486 | First reheater
BR3 | U1 | 1350 | 2020-12-14 20:20 | 2020-12-16 07:59 | 416 | Other miscellaneous boiler tube problems
OF3 | U1 | 9350 | 2020-12-16 11:01 | 2020-12-16 17:00 | 12.58 | Public Safety (water hazard or river rescue)
OF4 | U1 | 9350 | 2020-12-16 11:03 | 2020-12-16 16:46 | 12.58 | Public Safety (water hazard or river rescue)
OF5 | U1 | 9350 | 2020-12-16 11:05 | 2020-12-16 16:38 | 12.58 | Public Safety (water hazard or river rescue)
OF6 | U1 | 9350 | 2020-12-16 11:07 | 2020-12-16 16:26 | 12.58 | Public Safety (water hazard or river rescue)
OF8 | U1 | 9350 | 2020-12-16 11:10 | 2020-12-16 16:16 | 12.58 | Public Safety (water hazard or river rescue)
OF2 | U1 | 4750 | 2020-12-19 16:33 | 2020-12-20 09:37 | 12.58 | Other generator controls and metering problems
PR13 | U1 | 4511 | 2020-12-20 18:07 | 2020-12-21 22:57 | 175 | "Rotor, General"
BR10 | SF | 3641 | 2020-12-26 04:29 | 2020-12-26 07:09 | 138 | AC Circuit breakers
BR11 | SF | 5130 | 2020-12-26 04:34 | 2020-12-26 13:16 | 128 | Starting system (including motor)
TC6 | U1 | 4555 | 2020-12-26 04:52 | 2020-12-26 08:21 | 179 | Bearing cooling system
BR9 | U1 | 5011 | 2020-12-26 09:29 | 2020-12-26 09:41 | 138 | High pressure bearings
OF8 | U1 | 4551 | 2020-12-27 02:43 | 2020-12-27 09:47 | 12.58 | Generator bearings
OF1 | U1 | 9000 | 2020-12-27 10:19 | 2021-01-01 | 12.58 | Flood
OF8 | U1 | 4551 | 2020-12-27 10:24 | 2020-12-27 11:58 | 12.58 | Generator bearings
OF8 | U1 | 9000 | 2020-12-27 12:12 | 2021-01-01 | 12.58 | Flood
OF7 | U1 | 9000 | 2020-12-27 20:33 | 2021-01-01 | 12.58 | Flood
OF6 | U1 | 9000 | 2020-12-27 20:56 | 2021-01-01 | 12.58 | Flood
OF5 | U1 | 9000 | 2020-12-27 20:57 | 2021-01-01 | 12.58 | Flood
OF4 | U1 | 9000 | 2020-12-27 21:04 | 2021-01-01 | 12.58 | Flood
OF3 | U1 | 9000 | 2020-12-27 21:09 | 2021-01-01 | 12.58 | Flood
OF2 | U1 | 9000 | 2020-12-27 22:36 | 2021-01-01 | 12.58 | Flood
Dix 1 | U1 | 4602 | 2020-12-29 11:57 | 2020-12-30 12:26 | 11.2 | Exciter commutator and brushes
Dix 1 | U1 | 4602 | 2020-12-30 12:34 | 2021-01-01 | 11.2 | Exciter commutator and brushes
Note: The "MW on Outage" value is the Seasonal Net Unit Rating for Fossil Fuel units and the Generator Nameplate Rating for Hydro and Solar units.

## 2021
UnitName | EventType | CauseCode | EventStart | EventEnd | MW On Outage | Cause
Dix 1 | U1 | 4602 | 2021-01-01 | 2021-01-18 14:10 | 11.2 | Exciter commutator and brushes
OF1 | U1 | 9000 | 2021-01-01 | 2021-01-11 12:04 | 12.58 | Flood
OF2 | U1 | 9000 | 2021-01-01 | 2021-01-11 12:01 | 12.58 | Flood
OF3 | U1 | 9000 | 2021-01-01 | 2021-01-11 11:50 | 12.58 | Flood
OF5 | U1 | 9000 | 2021-01-01 | 2021-01-11 10:43 | 12.58 | Flood
OF6 | U1 | 9000 | 2021-01-01 | 2021-01-11 10:39 | 12.58 | Flood
OF4 | U1 | 9000 | 2021-01-01 | 2021-01-11 11:44 | 12.58 | Flood
OF7 | U1 | 9000 | 2021-01-01 | 2021-01-11 10:25 | 12.58 | Flood
OF8 | U1 | 9000 | 2021-01-01 | 2021-01-11 12:05 | 12.58 | Flood
Dix 3 | U1 | 3644 | 2021-01-08 07:13 | 2021-01-08 13:30 | 11.2 | AC Protection devices
Dix 2 | U1 | 3644 | 2021-01-08 07:13 | 2021-01-08 12:02 | 11.2 | AC Protection devices
Dix 2 | U1 | 7199 | 2021-01-08 12:15 | 2021-01-08 13:09 | 11.2 | Other water supply/discharge problems (use for equipment related problems; use codes 9135 or 9320 for lack of water or discharge limit related problems)
OF7 | U1 | 4650 | 2021-01-11 21:47 | 2021-01-12 09:44 | 12.58 | Other cooling system problems
Dix 3 | U1 | 9910 | 2021-01-12 09:12 | 2021-01-12 09:47 | 11.2 | Maintenance personnel error
BR6 | SF | 4609 | 2021-01-18 06:41 | 2021-01-21 16:34 | 171 | Other exciter problems
BR7 | SF | 4609 | 2021-01-18 07:02 | 2021-01-18 11:37 | 171 | Other exciter problems
OF8 | U1 | 7141 | 2021-01-21 09:00 | 2022-01-01 | 12.58 | Wicket gate operating mechanism or positioner
BR6 | SF | 5050 | 2021-01-22 06:30 | 2021-01-22 11:28 | 171 | Ignition system
TC2 | U1 | 540 | 2021-01-25 18:30 | 2021-01-31 13:07 | 570 | Hot reheat steam piping up to turbine stop valves
MC2 | U1 | 9271 | 2021-01-25 21:03 | 2021-01-25 21:34 | 297 | Wet coal (not OMC)
TC8 | U1 | 5190 | 2021-01-26 06:05 | 2021-01-26 15:04 | 179 | Other auxiliary system problems
OF1 | U1 | 9000 | 2021-01-27 12:36 | 2021-02-05 11:31 | 12.58 | Flood
OF6 | U1 | 9000 | 2021-01-27 19:54 | 2021-02-05 10:32 | 12.58 | Flood
OF5 | U1 | 9000 | 2021-01-27 20:11 | 2021-02-05 10:42 | 12.58 | Flood
OF4 | U1 | 9000 | 2021-01-27 20:12 | 2021-02-05 10:54 | 12.58 | Flood
OF3 | U1 | 9000 | 2021-01-27 20:17 | 2021-02-05 11:01 | 12.58 | Flood
OF2 | U1 | 9000 | 2021-01-27 20:26 | 2021-02-05 11:15 | 12.58 | Flood
BR10 | U1 | 3611 | 2021-01-28 12:38 | 2021-01-28 15:03 | 138 | Switchyard circuit breakers - external (OMC)
PR13 | SF | 3644 | 2021-01-29 05:40 | 2021-01-29 15:14 | 175 | AC Protection devices
TC2 | U1 | 4499 | 2021-01-31 14:05 | 2021-01-31 15:29 | 570 | Other miscellaneous steam turbine problems
OF7 | U1 | 9000 | 2021-02-04 07:23 | 2021-02-05 10:24 | 12.58 | Flood
OF6 | U1 | 4650 | 2021-02-07 12:33 | 2021-02-07 15:41 | 12.58 | Other cooling system problems
OF7 | U1 | 4650 | 2021-02-07 13:26 | 2021-02-07 15:29 | 12.58 | Other cooling system problems
OF4 | U1 | 4550 | 2021-02-08 04:08 | 2021-02-11 14:56 | 12.58 | Generator bearings and lube oil system (including thrust bearings on hydro units)
BR10 | U1 | 3864 | 2021-02-09 15:33 | 2021-02-11 19:00 | 138 | Fire protection system instrumentation and controls
MC1 | U1 | 800 | 2021-02-10 18:21 | 2021-02-10 23:22 | 300 | Drums and drum internals (single drum only)
BR5 | SF | 4609 | 2021-02-15 08:17 | 2021-02-15 10:02 | 130 | Other exciter problems
BR8 | U1 | 5016 | 2021-02-17 03:48 | 2021-02-17 07:18 | 128 | High pressure compressor bleed valves
BR9 | SF | 3661 | 2021-02-17 04:57 | 2021-02-17 07:29 | 138 | 4000-7000 volt circuit breakers
OF1 | U1 | 9000 | 2021-02-22 13:09 | 2021-03-15 07:50 | 12.58 | Flood
CR7 | U1 | 3350 | 2021-02-23 10:32 | 2021-02-23 12:47 | 683 | Condensate polishing and filtering systems
OF2 | U1 | 9000 | 2021-02-24 07:29 | 2021-03-15 07:55 | 12.58 | Flood
OF3 | U1 | 9000 | 2021-02-24 19:21 | 2021-03-12 11:51 | 12.58 | Flood
OF5 | U1 | 9000 | 2021-02-24 21:02 | 2021-03-12 10:13 | 12.58 | Flood
OF4 | U1 | 9000 | 2021-02-24 21:07 | 2021-03-12 11:58 | 12.58 | Flood
OF7 | U1 | 9000 | 2021-02-24 21:08 | 2021-03-12 10:28 | 12.58 | Flood
OF6 | U1 | 9000 | 2021-02-24 21:08 | 2021-03-12 09:54 | 12.58 | Flood
TC10 | SF | 5130 | 2021-03-02 07:49 | 2021-03-02 17:30 | 169 | Starting system (including motor)
BR3 | U2 | 1060 | 2021-03-02 08:41 | 2021-03-04 10:00 | 414 | First reheater
MC3 | U1 | 1488 | 2021-03-05 23:50 | 2021-03-06 03:58 | 392.5 | Air heater (regenerative)
MC4 | U1 | 1430 | 2021-03-08 09:45 | 2021-03-08 12:20 | 481.5 | Air supply ducts from FD fan
MC4 | U1 | 3110 | 2021-03-08 22:16 | 2021-03-10 04:15 | 481.5 | Condenser tube leaks
MC3 | U1 | 3245 | 2021-03-09 20:34 | 2021-03-09 23:36 | 392.5 | Other cooling tower problems
BR8 | SF | 4511 | 2021-03-16 05:52 | 2021-03-16 07:59 | 118 | "Rotor, General"
OF1 | U1 | 9000 | 2021-03-17 04:50 | 2021-03-24 10:08 | 12.58 | Flood
OF2 | U1 | 9000 | 2021-03-20 00:59 | 2021-03-24 09:56 | 12.58 | Flood
OF3 | U1 | 9000 | 2021-03-20 06:04 | 2021-03-24 07:59 | 12.58 | Flood
OF4 | U1 | 9000 | 2021-03-20 07:01 | 2021-03-24 07:55 | 12.58 | Flood
OF7 | U1 | 9000 | 2021-03-20 08:07 | 2021-03-24 07:18 | 12.58 | Flood
OF5 | U1 | 9000 | 2021-03-20 08:25 | 2021-03-24 07:26 | 12.58 | Flood
OF6 | U1 | 9000 | 2021-03-20 08:26 | 2021-03-24 09:27 | 12.58 | Flood
BR10 | U1 | 5087 | 2021-03-22 12:47 | 2021-03-22 13:32 | 118 | Thrust bearing
OF5 | U1 | 7009 | 2021-03-25 04:19 | 2021-03-25 06:53 | 12.58 | Bearing oil system
TC1 | U1 | 4730 | 2021-03-25 16:00 | 2021-03-26 15:34 | 369.75 | Generator current and potential transformers
TC10 | U1 | 5130 | 2021-03-25 17:04 | 2021-03-25 17:14 | 169 | Starting system (including motor)
TC9 | U1 | 5130 | 2021-03-25 17:04 | 2021-03-25 17:14 | 169 | Starting system (including motor)
Dix 2 | U1 | 4609 | 2021-03-26 10:46 | 2021-04-09 14:16 | 11.2 | Other exciter problems
OF1 | U1 | 9000 | 2021-03-29 12:58 | 2021-04-06 07:11 | 12.58 | Flood
OF2 | U1 | 9000 | 2021-03-31 02:12 | 2021-04-05 13:04 | 12.58 | Flood
OF4 | U1 | 9000 | 2021-03-31 02:19 | 2021-04-05 09:09 | 12.58 | Flood
OF3 | U1 | 9000 | 2021-03-31 06:13 | 2021-04-05 09:26 | 12.58 | Flood
OF6 | U1 | 9000 | 2021-04-01 06:24 | 2021-04-05 12:56 | 12.58 | Flood
OF7 | U1 | 9000 | 2021-04-01 06:26 | 2021-04-05 08:23 | 12.58 | Flood
MC1 | U1 | 4261 | 2021-04-02 23:50 | 2021-04-03 01:18 | 300 | Control valves
MC1 | U1 | 800 | 2021-04-04 01:59 | 2021-04-04 03:01 | 300 | Drums and drum internals (single drum only)
MC1 | U1 | 4640 | 2021-04-04 04:51 | 2021-04-05 11:49 | 300 | Seal oil system and seals
OF1 | U1 | 3972 | 2021-04-07 07:33 | 2021-04-07 07:53 | 12.58 | DCS - hardware problems (including card failure)
OF1 | U1 | 3972 | 2021-04-07 07:54 | 2021-04-07 08:19 | 12.58 | DCS - hardware problems (including card failure)
BR9 | U1 | 5250 | 2021-04-12 07:44 | 2021-04-12 09:31 | 118 | Other controls and instrumentation problems
BR3 | U1 | 1488 | 2021-04-20 12:39 | 2021-04-22 16:58 | 414 | Air heater (regenerative)
MC2 | U1 | 4240 | 2021-04-23 19:12 | 2021-04-25 09:39 | 297 | Bearings
TC2 | U1 | 1035 | 2021-04-24 15:30 | 2021-04-28 13:15 | 559.5 | Platen superheater
MC2 | U1 | 4240 | 2021-04-25 10:18 | 2021-04-25 16:59 | 297 | Bearings
BR7 | SF | 5050 | 2021-05-11 10:33 | 2021-05-11 13:17 | 157 | Ignition system
BR11 | SF | 5050 | 2021-05-12 08:13 | 2021-05-12 09:35 | 118 | Ignition system
TC10 | U1 | 4609 | 2021-05-13 07:54 | 2021-05-13 12:35 | 169 | Other exciter problems
OF2 | U1 | 3979 | 2021-05-17 16:13 | 2021-05-18 07:19 | 12.58 | Other DCS problems
GH1 | U1 | 4302 | 2021-05-17 18:52 | 2021-05-17 20:06 | 477 | Turbine trip devices (including instruments)
BR3 | SF | 3122 | 2021-05-19 03:35 | 2021-05-19 12:19 | 414 | Gaskets and seals
TC10 | U1 | 5042 | 2021-05-20 21:07 | 2021-05-21 08:11 | 169 | Fuel nozzles/vanes
OF4 | U1 | 9135 | 2021-05-22 17:55 | 2021-05-25 06:40 | 12.58 | Lack of water
OF5 | U1 | 9135 | 2021-05-22 17:56 | 2021-05-25 07:03 | 12.58 | Lack of water
BR7 | SF | 5050 | 2021-05-25 09:46 | 2021-05-25 10:50 | 157 | Ignition system
OF6 | U1 | 9135 | 2021-05-27 14:10 | 2021-05-28 07:14 | 12.58 | Lack of water
OF7 | U1 | 9135 | 2021-05-27 14:10 | 2021-06-01 07:31 | 12.58 | Lack of water
OF1 | U1 | 9135 | 2021-05-27 23:20 | 2021-06-04 06:42 | 12.58 | Lack of water
MC4 | U1 | 8261 | 2021-05-28 17:55 | 2021-05-28 23:12 | 481.5 | Scrubber booster I.D. fan drive
TC10 | U1 | 3864 | 2021-05-30 19:56 | 2021-05-30 20:11 | 169 | Fire protection system instrumentation and controls
MC4 | U1 | 8262 | 2021-06-04 15:06 | 2021-06-04 19:45 | 477 | Scrubber booster I.D. fan vibration (fan specific to the scrubber)
OF6 | U1 | 9135 | 2021-06-06 15:01 | 2021-06-07 07:25 | 12.58 | Lack of water
OF1 | U1 | 9135 | 2021-06-06 16:14 | 2021-06-07 07:52 | 12.58 | Lack of water
TC8 | SF | 5130 | 2021-06-08 11:51 | 2021-06-08 12:13 | 159 | Starting system (including motor)
OF1 | U1 | 9135 | 2021-06-08 19:01 | 2021-06-10 07:12 | 12.58 | Lack of water
BR3 | U1 | 1100 | 2021-06-13 00:36 | 2021-06-13 21:50 | 412 | Waterwall (Furnace wall)
OF1 | U1 | 7110 | 2021-06-13 07:45 | 2021-06-15 13:51 | 12.58 | Intake channel or flume (including trash racks)
OF2 | U1 | 7110 | 2021-06-15 07:49 | 2021-06-15 13:39 | 12.58 | Intake channel or flume (including trash racks)
OF3 | U1 | 7110 | 2021-06-15 07:51 | 2021-06-15 13:27 | 12.58 | Intake channel or flume (including trash racks)
OF4 | U1 | 7110 | 2021-06-15 07:53 | 2021-06-15 13:18 | 12.58 | Intake channel or flume (including trash racks)
OF5 | U1 | 7110 | 2021-06-15 07:54 | 2021-06-15 13:09 | 12.58 | Intake channel or flume (including trash racks)
OF6 | U1 | 7110 | 2021-06-15 07:56 | 2021-06-15 12:59 | 12.58 | Intake channel or flume (including trash racks)
OF7 | U1 | 7110 | 2021-06-15 07:57 | 2021-06-15 12:49 | 12.58 | Intake channel or flume (including trash racks)
OF1 | U1 | 7110 | 2021-06-16 02:02 | 2021-06-21 09:23 | 12.58 | Intake channel or flume (including trash racks)
OF3 | U1 | 7053 | 2021-06-16 17:31 | 2021-06-17 07:29 | 12.58 | Governor oil system
MC2 | U1 | 250 | 2021-06-18 05:48 | 2021-06-18 07:56 | 297 | Pulverizer feeders
BR6 | U1 | 4560 | 2021-06-18 10:42 | 2021-06-18 11:56 | 146 | Generator vibration (excluding vibration due to failed bearing and other components)
OF2 | U1 | 7110 | 2021-06-19 19:36 | 2021-06-21 09:10 | 12.58 | Intake channel or flume (including trash racks)
OF7 | U1 | 7110 | 2021-06-19 23:37 | 2021-06-21 07:35 | 12.58 | Intake channel or flume (including trash racks)
OF6 | U1 | 7110 | 2021-06-20 02:45 | 2021-06-21 07:42 | 12.58 | Intake channel or flume (including trash racks)
OF5 | U1 | 7110 | 2021-06-20 02:48 | 2021-06-21 07:52 | 12.58 | Intake channel or flume (including trash racks)
OF4 | U1 | 7110 | 2021-06-20 02:49 | 2021-06-21 08:48 | 12.58 | Intake channel or flume (including trash racks)
OF3 | U1 | 7110 | 2021-06-20 02:50 | 2021-06-21 08:54 | 12.58 | Intake channel or flume (including trash racks)
BR7 | U1 | 5016 | 2021-06-20 14:38 | 2021-06-22 08:00 | 146 | High pressure compressor bleed valves
OF5 | U1 | 4650 | 2021-06-23 06:24 | 2021-06-23 06:53 | 12.58 | Other cooling system problems
OF1 | U1 | 7110 | 2021-06-23 06:43 | 2021-06-25 12:48 | 12.58 | Intake channel or flume (including trash racks)
TC8 | U1 | 5109 | 2021-06-24 14:18 | 2021-06-24 15:24 | 159 | Other exhaust problems (including high exhaust system temperature not attributable to a specific problem)
OF2 | U1 | 9135 | 2021-06-26 13:35 | 2021-06-28 09:39 | 12.58 | Lack of water
OF1 | U1 | 9135 | 2021-06-26 13:56 | 2021-06-28 09:19 | 12.58 | Lack of water
OF3 | U1 | 9135 | 2021-06-27 10:16 | 2021-06-28 09:39 | 12.58 | Lack of water
OF6 | U1 | 9135 | 2021-06-27 13:26 | 2021-06-28 09:39 | 12.58 | Lack of water
OF5 | U1 | 9135 | 2021-06-27 15:02 | 2021-06-28 07:22 | 12.58 | Lack of water
OF4 | U1 | 9135 | 2021-06-27 16:23 | 2021-06-28 07:33 | 12.58 | Lack of water
TC9 | U1 | 4640 | 2021-06-28 20:49 | 2021-06-30 08:14 | 159 | Seal oil system and seals
OF1 | U1 | 9135 | 2021-06-29 06:02 | 2021-07-01 07:35 | 12.58 | Lack of water
OF5 | U1 | 9135 | 2021-06-29 07:31 | 2021-07-01 07:35 | 12.58 | Lack of water
OF6 | U1 | 9135 | 2021-06-29 09:00 | 2021-07-01 07:35 | 12.58 | Lack of water
OF3 | U1 | 9135 | 2021-06-29 09:00 | 2021-07-01 07:35 | 12.58 | Lack of water
OF2 | U1 | 9135 | 2021-06-29 09:00 | 2021-07-01 07:35 | 12.58 | Lack of water
OF4 | U1 | 9135 | 2021-06-29 11:51 | 2021-07-01 07:35 | 12.58 | Lack of water
OF7 | U1 | 9135 | 2021-06-29 17:07 | 2021-06-30 13:51 | 12.58 | Lack of water
OF1 | U1 | 7110 | 2021-07-03 06:32 | 2021-07-06 06:41 | 12.58 | Intake channel or flume (including trash racks)
OF2 | U1 | 9135 | 2021-07-09 06:30 | 2021-07-13 09:57 | 12.58 | Lack of water
OF3 | U1 | 9135 | 2021-07-09 06:30 | 2021-07-13 09:37 | 12.58 | Lack of water
OF4 | U1 | 9135 | 2021-07-09 06:30 | 2021-07-13 09:48 | 12.58 | Lack of water
OF7 | U1 | 7110 | 2021-07-09 14:50 | 2021-07-13 09:02 | 12.58 | Intake channel or flume (including trash racks)
OF6 | U1 | 7110 | 2021-07-09 14:50 | 2021-07-13 08:54 | 12.58 | Intake channel or flume (including trash racks)
OF5 | U1 | 7110 | 2021-07-09 14:50 | 2021-07-13 09:23 | 12.58 | Intake channel or flume (including trash racks)
TC5 | SF | 5441 | 2021-07-10 15:33 | 2021-07-10 15:52 | 159 | Fuel piping and valves
BR10 | SF | 5122 | 2021-07-15 12:36 | 2021-07-15 14:17 | 121 | Hydraulic oil system piping/valves
MC2 | U1 | 9720 | 2021-07-15 13:14 | 2021-07-16 02:36 | 297 | Other safety problems
MC1 | U1 | 9720 | 2021-07-15 13:14 | 2021-07-16 01:44 | 300 | Other safety problems
MC3 | U1 | 9720 | 2021-07-15 13:16 | 2021-07-16 03:55 | 391 | Other safety problems
MC4 | U1 | 9720 | 2021-07-15 13:18 | 2021-07-16 01:44 | 477 | Other safety problems
HA1 | U1 | 4620 | 2021-07-15 14:35 | 2021-07-16 12:21 | 12 | Air cooling system
PR12 | U1 | 4570 | 2021-07-15 16:19 | 2021-07-16 05:00 | 23 | Generator casing
BR5 | U1 | 3974 | 2021-07-16 09:44 | 2021-07-20 10:30 | 130 | DCS - logic problems
PR12 | U1 | 4619 | 2021-07-19 12:00 | 2021-07-19 14:38 | 23 | Other hydrogen system problems
PR12 | U1 | 4570 | 2021-07-20 10:30 | 2021-07-26 07:03 | 23 | Generator casing
OF3 | U1 | 4609 | 2021-07-20 10:47 | 2021-07-20 11:08 | 12.58 | Other exciter problems
TC7 | U1 | 5016 | 2021-07-20 15:38 | 2021-07-20 18:45 | 159 | High pressure compressor bleed valves
BR5 | U2 | 4730 | 2021-07-20 18:07 | 2021-07-23 15:26 | 130 | Generator current and potential transformers
TC5 | SF | 4609 | 2021-07-22 13:32 | 2021-07-22 13:58 | 159 | Other exciter problems
TC7 | SF | 5109 | 2021-07-24 11:47 | 2021-07-24 12:33 | 159 | Other exhaust problems (including high exhaust system temperature not attributable to a specific problem)
TC1 | U1 | 1710 | 2021-07-27 15:57 | 2021-07-27 18:19 | 369.75 | "Combustion/steam condition controls (report local controls - burners, pulverizers, etc., - with component or system)"
TC1 | U1 | 3110 | 2021-07-30 01:37 | 2021-07-31 11:21 | 369.75 | Condenser tube leaks
OF2 | U1 | 9135 | 2021-07-30 07:51 | 2021-07-30 14:24 | 12.58 | Lack of water
OF2 | U1 | 9135 | 2021-08-04 05:55 | 2021-08-13 10:28 | 12.58 | Lack of water
GH1 | U1 | 4609 | 2021-08-04 06:40 | 2021-08-04 09:16 | 475 | Other exciter problems
OF3 | U1 | 9135 | 2021-08-04 08:26 | 2021-08-13 10:20 | 12.58 | Lack of water
OF4 | U1 | 9135 | 2021-08-04 10:52 | 2021-08-11 07:18 | 12.58 | Lack of water
BR3 | U1 | 830 | 2021-08-06 06:36 | 2021-08-07 01:48 | 412 | Doors
OF5 | U1 | 9135 | 2021-08-06 08:55 | 2021-08-11 07:04 | 12.58 | Lack of water
OF7 | U1 | 9135 | 2021-08-06 09:52 | 2021-08-07 07:52 | 12.58 | Lack of water
OF6 | U1 | 9135 | 2021-08-06 12:03 | 2021-08-07 07:45 | 12.58 | Lack of water
BR3 | U1 | 4293 | 2021-08-08 00:22 | 2021-08-08 19:12 | 412 | Hydraulic system pipes and valves
BR6 | U1 | 5088 | 2021-08-08 10:32 | 2021-08-08 11:23 | 146 | Gas turbine cooling system
OF6 | U1 | 9135 | 2021-08-09 22:17 | 2021-08-11 06:52 | 12.58 | Lack of water
OF7 | U1 | 9135 | 2021-08-10 06:30 | 2021-08-11 06:44 | 12.58 | Lack of water
GH1 | U1 | 4619 | 2021-08-11 20:22 | 2021-08-12 00:47 | 475 | Other hydrogen system problems
OF4 | U1 | 9135 | 2021-08-12 00:55 | 2021-08-13 13:02 | 12.58 | Lack of water
OF6 | U1 | 9135 | 2021-08-12 00:56 | 2021-08-17 06:40 | 12.58 | Lack of water
OF5 | U1 | 9135 | 2021-08-12 02:53 | 2021-08-13 07:01 | 12.58 | Lack of water
OF7 | U1 | 9135 | 2021-08-12 02:54 | 2021-08-13 06:46 | 12.58 | Lack of water
GH1 | U1 | 3431 | 2021-08-12 21:49 | 2021-08-13 12:13 | 475 | Other feedwater valves
TC10 | U1 | 5042 | 2021-08-13 19:18 | 2021-08-13 21:40 | 159 | Fuel nozzles/vanes
OF4 | U1 | 9135 | 2021-08-16 06:58 | 2021-08-17 09:39 | 12.58 | Lack of water
MC4 | U1 | 4611 | 2021-08-18 05:11 | 2021-08-18 06:52 | 477 | Hydrogen coolers
OF3 | U1 | 9135 | 2021-08-18 06:30 | 2021-08-18 07:53 | 12.58 | Lack of water
OF2 | U1 | 9135 | 2021-08-18 06:30 | 2021-08-18 07:53 | 12.58 | Lack of water
MC4 | U1 | 4630 | 2021-08-23 03:51 | 2021-08-23 06:05 | 477 | Liquid cooling system
TC9 | U1 | 5447 | 2021-08-23 12:42 | 2021-08-23 13:29 | 159 | Gas fuel system including controls and instrumentation
TC7 | U1 | 5160 | 2021-08-26 14:33 | 2021-08-26 21:30 | 159 | Cooling and seal air system
GH1 | U1 | 775 | 2021-08-28 23:57 | 2021-08-30 12:26 | 475 | Economizer piping
BR8 | SF | 3629 | 2021-08-29 16:44 | 2021-08-29 16:51 | 121 | Other switchyard or high voltage system problems - external
TC5 | U1 | 5240 | 2021-08-31 22:20 | 2021-09-01 | 159 | Fire detection and extinguishing system (including hazardous gas detection system)
TC5 | U1 | 5240 | 2021-09-01 | 2021-09-01 01:24 | 169 | Fire detection and extinguishing system (including hazardous gas detection system)
OF5 | U1 | 4650 | 2021-09-01 10:23 | 2021-09-01 10:43 | 12.58 | Other cooling system problems
OF7 | U1 | 9000 | 2021-09-03 01:24 | 2021-09-06 06:51 | 12.58 | Flood
OF6 | U1 | 9000 | 2021-09-03 10:35 | 2021-09-06 06:57 | 12.58 | Flood
OF5 | U1 | 9000 | 2021-09-03 10:38 | 2021-09-06 07:01 | 12.58 | Flood
OF4 | U1 | 9000 | 2021-09-03 10:39 | 2021-09-06 08:08 | 12.58 | Flood
OF3 | U1 | 9000 | 2021-09-03 10:40 | 2021-09-06 07:30 | 12.58 | Flood
OF2 | U1 | 9000 | 2021-09-03 10:41 | 2021-09-06 07:37 | 12.58 | Flood
OF5 | U1 | 9135 | 2021-09-11 07:09 | 2021-09-16 06:53 | 12.58 | Lack of water
OF4 | U1 | 9135 | 2021-09-11 13:14 | 2021-09-18 08:19 | 12.58 | Lack of water
OF3 | U1 | 9135 | 2021-09-14 18:05 | 2021-09-18 08:22 | 12.58 | Lack of water
TC8 | U1 | 4609 | 2021-09-14 19:20 | 2021-09-14 20:02 | 169 | Other exciter problems
TC10 | U1 | 4609 | 2021-09-14 19:20 | 2021-09-14 20:47 | 169 | Other exciter problems
OF5 | U1 | 9135 | 2021-09-16 19:00 | 2021-09-18 08:05 | 12.58 | Lack of water
GH4 | U1 | 1040 | 2021-09-18 01:30 | 2021-09-19 16:55 | 478 | First superheater
OF3 | U1 | 9135 | 2021-09-18 23:15 | 2021-09-24 13:26 | 12.58 | Lack of water
OF4 | U1 | 9135 | 2021-09-19 11:29 | 2021-09-22 12:01 | 12.58 | Lack of water
OF5 | U1 | 9135 | 2021-09-19 13:07 | 2021-09-21 06:42 | 12.58 | Lack of water
OF6 | U1 | 9135 | 2021-09-19 22:19 | 2021-09-21 06:47 | 12.58 | Lack of water
OF4 | U1 | 9135 | 2021-09-22 16:09 | 2021-09-24 13:32 | 12.58 | Lack of water
OF6 | U1 | 9135 | 2021-09-22 17:14 | 2021-09-24 13:45 | 12.58 | Lack of water
OF5 | U1 | 9135 | 2021-09-22 19:16 | 2021-09-24 13:35 | 12.58 | Lack of water
GH3 | U1 | 4281 | 2021-09-22 23:30 | 2021-09-23 00:32 | 478.5 | Lube oil coolers
GH2 | U1 | 1470 | 2021-09-26 04:12 | 2021-09-26 06:48 | 485.5 | Induced draft fan motors and drives
OF7 | U1 | 9135 | 2021-09-30 22:24 | 2021-10-04 08:40 | 12.58 | Lack of water
OF6 | U1 | 9135 | 2021-10-01 01:52 | 2021-10-02 09:18 | 12.58 | Lack of water
OF5 | U1 | 9135 | 2021-10-01 08:58 | 2021-10-04 07:45 | 12.58 | Lack of water
OF6 | U1 | 9135 | 2021-10-02 12:51 | 2021-10-04 08:47 | 12.58 | Lack of water
OF4 | U1 | 9135 | 2021-10-02 14:19 | 2021-10-04 07:11 | 12.58 | Lack of water
OF2 | U1 | 9135 | 2021-10-02 15:56 | 2021-10-04 07:40 | 12.58 | Lack of water
OF3 | U1 | 3979 | 2021-10-03 11:30 | 2021-10-04 06:48 | 12.58 | Other DCS problems
OF3 | U1 | 9900 | 2021-10-04 06:58 | 2021-10-04 07:06 | 12.58 | Operator error
OF4 | U1 | 9135 | 2021-10-05 06:03 | 2021-10-07 11:43 | 12.58 | Lack of water
OF2 | U1 | 9135 | 2021-10-05 10:01 | 2021-10-08 06:30 | 12.58 | Lack of water
GH2 | U1 | 4311 | 2021-10-06 23:20 | 2021-10-07 04:44 | 485.5 | Steam Turbine Control System - hardware problems (including card failure)
OF3 | U1 | 9135 | 2021-10-12 15:09 | 2021-10-14 07:07 | 12.58 | Lack of water
OF7 | U1 | 9135 | 2021-10-12 17:17 | 2021-10-14 07:12 | 12.58 | Lack of water
OF6 | U1 | 9135 | 2021-10-12 20:45 | 2021-10-17 07:28 | 12.58 | Lack of water
MC4 | U1 | 1400 | 2021-10-13 15:53 | 2021-10-15 09:40 | 481.5 | Forced draft fans
OF5 | U1 | 9135 | 2021-10-14 16:51 | 2021-10-25 09:35 | 12.58 | Lack of water
OF4 | U1 | 9135 | 2021-10-14 17:48 | 2021-10-18 08:00 | 12.58 | Lack of water
OF7 | U1 | 9135 | 2021-10-21 19:52 | 2021-10-25 09:44 | 12.58 | Lack of water
OF6 | U1 | 9135 | 2021-10-22 14:56 | 2021-10-25 09:39 | 12.58 | Lack of water
TC1 | U1 | 3620 | 2021-10-31 16:35 | 2021-11-02 19:46 | 369.75 | Main transformer
OF2 | U1 | 4551 | 2021-11-01 23:18 | 2021-11-02 07:03 | 12.58 | Generator bearings
TC10 | SF | 5130 | 2021-11-02 05:32 | 2021-11-02 06:43 | 169 | Starting system (including motor)
BR8 | SF | 5050 | 2021-11-02 05:36 | 2021-11-02 19:06 | 118 | Ignition system
GH3 | U1 | 1060 | 2021-11-02 05:47 | 2021-11-03 10:01 | 478.5 | First reheater
BR6 | SF | 5001 | 2021-11-02 06:00 | 2021-11-02 06:21 | 157 | Inlet air vanes/nozzles
TC1 | U1 | 3610 | 2021-11-02 21:49 | 2021-11-02 23:59 | 369.75 | Switchyard circuit breakers - external (not OMC)
HA1 | SF | 5050 | 2021-11-03 06:00 | 2021-11-03 07:55 | 12.8333 | Ignition system
HA2 | SF | 5450 | 2021-11-03 06:00 | 2021-11-03 08:10 | 12.8333 | Ignition system
PR13 | U1 | 5016 | 2021-11-03 13:34 | 2021-11-03 14:15 | 161 | High pressure compressor bleed valves
BR5 | U1 | 5041 | 2021-11-04 06:38 | 2021-11-04 07:13 | 120 | Fuel piping and valves
Dix 2 | U1 | 7121 | 2021-11-12 12:48 | 2021-11-12 13:31 | 11.2 | Shutoff valves
MC1 | U1 | 1080 | 2021-11-17 21:20 | 2021-11-20 02:24 | 300 | Economizer
Dix 2 | U1 | 7121 | 2021-11-19 06:04 | 2021-11-19 06:38 | 11.2 | Shutoff valves
Dix 2 | U1 | 7121 | 2021-11-19 06:53 | 2021-11-19 07:38 | 11.2 | Shutoff valves
Dix 2 | U1 | 7121 | 2021-11-19 07:51 | 2021-11-19 09:33 | 11.2 | Shutoff valves
MC3 | SF | 1488 | 2021-11-29 14:32 | 2021-11-30 11:45 | 392.5 | Air heater (regenerative)
PR13 | U1 | 3644 | 2021-12-05 13:23 | 2021-12-12 13:30 | 175 | AC Protection devices
OF6 | U1 | 7110 | 2021-12-06 14:51 | 2021-12-07 14:43 | 12.58 | Intake channel or flume (including trash racks)
OF7 | U1 | 7110 | 2021-12-07 07:43 | 2021-12-07 14:18 | 12.58 | Intake channel or flume (including trash racks)
OF2 | U1 | 9000 | 2021-12-07 15:18 | 2021-12-10 10:59 | 12.58 | Flood
OF1 | U1 | 9000 | 2021-12-08 07:01 | 2021-12-10 11:10 | 12.58 | Flood
Dix 2 | U1 | 7052 | 2021-12-08 15:58 | 2021-12-08 16:44 | 11.2 | "Other turbine control problems (Report specific wicket gate controls, etc., using the code for the appropriate equipment item.)"
TC6 | U1 | 5450 | 2021-12-08 16:44 | 2021-12-08 18:24 | 179 | Ignition system
Dix 2 | U1 | 7052 | 2021-12-08 16:45 | 2021-12-08 17:31 | 11.2 | "Other turbine control problems (Report specific wicket gate controls, etc., using the code for the appropriate equipment item.)"
Dix 2 | U1 | 7052 | 2021-12-08 17:32 | 2021-12-08 19:26 | 11.2 | "Other turbine control problems (Report specific wicket gate controls, etc., using the code for the appropriate equipment item.)"
OF7 | U1 | 9000 | 2021-12-09 07:04 | 2021-12-10 07:50 | 12.58 | Flood
OF7 | U1 | 7003 | 2021-12-10 07:50 | 2021-12-10 15:02 | 12.58 | Lube oil system (use code 7007 to report bearing failures due to lube oil problems)
MC4 | U1 | 1407 | 2021-12-10 08:29 | 2021-12-10 10:34 | 486 | Forced draft fan lubrication system
OF1 | U1 | 4609 | 2021-12-11 01:36 | 2021-12-15 08:23 | 12.58 | Other exciter problems
OF2 | U1 | 9000 | 2021-12-12 20:55 | 2021-12-15 08:31 | 12.58 | Flood
OF6 | U1 | 9000 | 2021-12-12 20:57 | 2021-12-15 08:15 | 12.58 | Flood
OF5 | U1 | 9000 | 2021-12-12 21:00 | 2021-12-15 08:15 | 12.58 | Flood
OF7 | U1 | 9000 | 2021-12-13 04:18 | 2021-12-15 09:06 | 12.58 | Flood
OF3 | U1 | 9000 | 2021-12-13 04:19 | 2021-12-15 08:53 | 12.58 | Flood
BR7 | U1 | 3974 | 2021-12-13 17:43 | 2021-12-13 19:00 | 171 | DCS - logic problems
OF7 | U1 | 7053 | 2021-12-22 14:45 | 2021-12-22 15:17 | 12.58 | Governor oil system
OF7 | U1 | 7053 | 2021-12-23 04:05 | 2021-12-23 11:07 | 12.58 | Governor oil system
OF7 | U1 | 7053 | 2021-12-23 15:58 | 2021-12-30 14:19 | 12.58 | Governor oil system
Dix 1 | U1 | 7009 | 2021-12-28 08:40 | 2021-12-28 09:18 | 11.2 | Bearing oil system
Dix 1 | U1 | 7009 | 2021-12-28 09:19 | 2021-12-28 09:57 | 11.2 | Bearing oil system
TC2 | U1 | 256 | 2021-12-30 03:55 | 2021-12-30 09:17 | 570 | Seal air system (air to pulverizers)
OF5 | U1 | 9000 | 2021-12-31 07:21 | 2022-01-01 | 12.58 | Flood
OF4 | U1 | 9000 | 2021-12-31 08:38 | 2022-01-01 | 12.58 | Flood
OF3 | U1 | 9000 | 2021-12-31 08:39 | 2022-01-01 | 12.58 | Flood
OF2 | U1 | 9000 | 2021-12-31 08:42 | 2022-01-01 | 12.58 | Flood
OF1 | U1 | 9000 | 2021-12-31 09:45 | 2022-01-01 | 12.58 | Flood
Note: The "MW on Outage" value is the Seasonal Net Unit Rating for Fossil Fuel units and the Generator Nameplate Rating for Hydro and Solar units.

## 2022
UnitName | EventType | CauseCode | EventStart | EventEnd | MW On Outage | Cause
OF1 | U1 | 9000 | 2022-01-01 | 2022-01-16 11:32 | 12.58 | Flood
OF2 | U1 | 9000 | 2022-01-01 | 2022-01-16 11:45 | 12.58 | Flood
OF3 | U1 | 9000 | 2022-01-01 | 2022-01-16 13:01 | 12.58 | Flood
OF5 | U1 | 9000 | 2022-01-01 | 2022-01-16 13:58 | 12.58 | Flood
OF4 | U1 | 9000 | 2022-01-01 | 2022-01-16 13:57 | 12.58 | Flood
OF8 | U1 | 7141 | 2022-01-01 | 2022-01-31 15:56 | 12.58 | Wicket gate operating mechanism or positioner
OF6 | U1 | 9000 | 2022-01-01 18:10 | 2022-01-16 12:55 | 12.58 | Flood
OF7 | U1 | 9000 | 2022-01-01 18:54 | 2022-01-16 13:58 | 12.58 | Flood
GH2 | U1 | 3499 | 2022-01-02 13:50 | 2022-01-02 15:41 | 486 | Other feedwater system problems
GH3 | U1 | 1488 | 2022-01-02 18:31 | 2022-01-02 20:30 | 476 | Air heater (regenerative)
MC2 | U1 | 1530 | 2022-01-03 07:38 | 2022-01-03 09:41 | 297 | Other flue gas problems
TC9 | U1 | 5247 | 2022-01-03 10:20 | 2022-01-03 12:02 | 179 | Gas Turbine Control System - internal and termination wiring
MC1 | SF | 4499 | 2022-01-03 14:30 | 2022-01-03 18:58 | 300 | Other miscellaneous steam turbine problems
GH3 | U1 | 4308 | 2022-01-06 02:09 | 2022-01-06 03:07 | 476 | Automatic turbine control systems - digital control and monitoring
MC2 | U1 | 250 | 2022-01-10 08:19 | 2022-01-10 09:25 | 297 | Pulverizer feeders
TC5 | U1 | 5050 | 2022-01-10 16:17 | 2022-01-10 16:36 | 179 | Ignition system
OF7 | U1 | 7053 | 2022-01-16 14:03 | 2022-01-16 14:11 | 12.58 | Governor oil system
OF7 | U1 | 7053 | 2022-01-16 21:46 | 2022-01-17 08:11 | 12.58 | Governor oil system
PR13 | U1 | 3842 | 2022-01-17 06:57 | 2022-01-17 14:08 | 175 | Service air valves
OF1 | U1 | 4551 | 2022-01-17 13:39 | 2022-01-17 14:56 | 12.58 | Generator bearings
BR6 | U1 | 4740 | 2022-01-17 20:33 | 2022-01-18 14:20 | 171 | Emergency generator trip devices
OF7 | U1 | 7053 | 2022-01-18 01:08 | 2022-01-18 08:24 | 12.58 | Governor oil system
BR6 | U1 | 3974 | 2022-01-21 07:57 | 2022-01-21 07:59 | 171 | DCS - logic problems
BR7 | U1 | 5048 | 2022-01-21 08:26 | 2022-01-21 15:24 | 171 | Gas fuel system including controls and instrumentation
BR10 | SF | 4603 | 2022-01-27 03:46 | 2022-01-27 12:08 | 138 | Solid state exciter element
BR11 | U1 | 4603 | 2022-01-27 03:46 | 2022-01-27 12:08 | 128 | Solid state exciter element
OF3 | U1 | 7110 | 2022-01-31 09:49 | 2022-02-01 10:52 | 12.58 | Intake channel or flume (including trash racks)
OF6 | U1 | 9000 | 2022-02-02 14:47 | 2022-02-03 10:46 | 12.58 | Flood
OF5 | U1 | 9000 | 2022-02-03 19:14 | 2022-02-14 11:34 | 12.58 | Flood
BR3 | U1 | 3621 | 2022-02-03 21:24 | 2022-02-04 15:03 | 416 | Unit auxiliaries transformer
OF1 | U1 | 9000 | 2022-02-04 05:35 | 2022-02-14 15:08 | 12.58 | Flood
OF4 | U1 | 9000 | 2022-02-04 05:40 | 2022-02-14 10:51 | 12.58 | Flood
OF2 | U1 | 9000 | 2022-02-04 05:43 | 2022-02-14 14:04 | 12.58 | Flood
OF6 | U1 | 9000 | 2022-02-04 07:15 | 2022-02-14 15:08 | 12.58 | Flood
OF7 | U1 | 9000 | 2022-02-04 10:31 | 2022-02-14 15:08 | 12.58 | Flood
OF8 | U1 | 9000 | 2022-02-04 11:51 | 2022-02-14 15:08 | 12.58 | Flood
OF3 | U1 | 9000 | 2022-02-04 11:51 | 2022-02-14 13:58 | 12.58 | Flood
TC2 | U1 | 1000 | 2022-02-14 16:26 | 2022-02-17 10:01 | 570 | Waterwall (Furnace wall)
OF5 | U1 | 9000 | 2022-02-15 13:54 | 2022-03-21 07:33 | 12.58 | Flood
Dix 1 | U1 | 7160 | 2022-02-15 15:34 | 2022-03-03 15:38 | 11.2 | Pressure regulating valve
OF4 | U1 | 9000 | 2022-02-15 20:39 | 2022-03-21 07:34 | 12.58 | Flood
OF3 | U1 | 9000 | 2022-02-16 08:06 | 2022-03-21 07:22 | 12.58 | Flood
OF2 | U1 | 9000 | 2022-02-17 07:14 | 2022-03-21 07:16 | 12.58 | Flood
TC1 | U1 | 3210 | 2022-02-17 14:09 | 2022-02-17 16:29 | 369.75 | Circulating water pumps
OF1 | U1 | 9000 | 2022-02-17 20:07 | 2022-03-21 07:09 | 12.58 | Flood
OF6 | U1 | 9000 | 2022-02-18 07:25 | 2022-03-21 07:08 | 12.58 | Flood
OF7 | U1 | 9000 | 2022-02-18 07:25 | 2022-03-21 07:08 | 12.58 | Flood
OF8 | U1 | 9000 | 2022-02-18 07:25 | 2022-03-21 07:08 | 12.58 | Flood
MC2 | U1 | 3999 | 2022-02-19 13:52 | 2022-02-26 14:35 | 297 | Other miscellaneous balance of plant problems
GH1 | U1 | 3110 | 2022-02-20 11:30 | 2022-02-21 04:00 | 479 | Condenser tube leaks
MC3 | SF | 730 | 2022-02-20 21:00 | 2022-02-21 13:01 | 394 | Other blowdown system problems
TC9 | U1 | 4740 | 2022-02-20 23:29 | 2022-02-21 11:16 | 179 | Emergency generator trip devices
TC2 | U1 | 3431 | 2022-02-25 23:32 | 2022-02-25 23:33 | 570 | Other feedwater valves
MC2 | SF | 710 | 2022-02-26 14:35 | 2022-02-27 21:39 | 297 | Blowdown system piping
BR6 | U1 | 3864 | 2022-03-05 18:59 | 2022-03-06 01:32 | 157 | Fire protection system instrumentation and controls
BR9 | SF | 4609 | 2022-03-23 06:51 | 2022-03-23 08:05 | 118 | Other exciter problems
OF1 | U1 | 9135 | 2022-03-31 10:42 | 2022-03-31 11:54 | 12.58 | Lack of water
TC2 | U1 | 3430 | 2022-04-03 19:44 | 2022-04-03 19:45 | 559.5 | Feedwater regulating (boiler level control) valve
BR9 | U1 | 3611 | 2022-04-06 21:53 | 2022-04-07 00:46 | 118 | Switchyard circuit breakers - external (OMC)
OF1 | U1 | 9000 | 2022-04-09 04:23 | 2022-04-18 07:51 | 12.58 | Flood
OF2 | U1 | 9000 | 2022-04-10 05:29 | 2022-04-18 07:44 | 12.58 | Flood
OF3 | U1 | 9000 | 2022-04-10 06:34 | 2022-04-18 07:35 | 12.58 | Flood
OF4 | U1 | 9000 | 2022-04-10 07:01 | 2022-04-18 07:29 | 12.58 | Flood
OF5 | U1 | 9000 | 2022-04-10 07:43 | 2022-04-18 07:22 | 12.58 | Flood
OF6 | U1 | 9000 | 2022-04-10 20:38 | 2022-04-18 07:16 | 12.58 | Flood
PR13 | U1 | 3641 | 2022-04-13 22:45 | 2022-04-16 19:49 | 161 | AC Circuit breakers
OF7 | U1 | 9000 | 2022-04-15 01:57 | 2022-04-18 07:10 | 12.58 | Flood
OF8 | U1 | 9000 | 2022-04-15 11:48 | 2022-04-18 07:05 | 12.58 | Flood
PR13 | U1 | 5150 | 2022-04-18 06:28 | 2022-04-18 09:40 | 161 | Turning gear and motor
TC6 | U1 | 5079 | 2022-04-18 09:41 | 2022-04-18 10:18 | 169 | Other combustor problems
GH3 | U1 | 4740 | 2022-04-20 00:01 | 2022-04-20 09:46 | 478.5 | Emergency generator trip devices
PR13 | SF | 3979 | 2022-04-20 06:51 | 2022-04-20 08:12 | 161 | Other DCS problems
MC3 | U1 | 1080 | 2022-04-20 08:40 | 2022-04-21 16:05 | 392.5 | Economizer
OF1 | U1 | 9000 | 2022-04-22 04:28 | 2022-04-25 07:09 | 12.58 | Flood
GH4 | U1 | 1040 | 2022-04-30 11:16 | 2022-05-02 16:50 | 478 | First superheater
BR8 | U1 | 4604 | 2022-04-30 18:15 | 2022-04-30 20:15 | 118 | Exciter drive - shaft
CR7 | SF | 5041 | 2022-05-01 13:47 | 2022-05-01 14:52 | 694 | Fuel piping and valves
CR7 | U1 | 3407 | 2022-05-01 15:39 | 2022-05-01 19:25 | 694 | Feedwater pump suction screens
CR7 | U1 | 6122 | 2022-05-01 20:16 | 2022-05-01 21:46 | 694 | Other IP steam valves (including vent and drain valves but not including the turbine stop valves)
CR7 | U1 | 6122 | 2022-05-01 22:43 | 2022-05-01 23:54 | 694 | Other IP steam valves (including vent and drain valves but not including the turbine stop valves)
CR7 | SF | 5050 | 2022-05-01 23:54 | 2022-05-02 00:20 | 694 | Ignition system
CR7 | SF | 5050 | 2022-05-02 00:20 | 2022-05-02 01:16 | 694 | Ignition system
PR13 | U1 | 5150 | 2022-05-02 05:38 | 2022-05-02 08:21 | 161 | Turning gear and motor
BR3 | U1 | 741 | 2022-05-02 14:14 | 2022-05-04 13:59 | 414 | Boiler recirculation pumps - motors
GH4 | U1 | 4240 | 2022-05-02 22:52 | 2022-05-18 08:15 | 478 | Bearings
OF1 | U1 | 9000 | 2022-05-07 08:06 | 2022-05-16 09:52 | 12.58 | Flood
OF3 | U1 | 9000 | 2022-05-07 13:48 | 2022-05-16 09:36 | 12.58 | Flood
OF2 | U1 | 9000 | 2022-05-07 13:48 | 2022-05-16 09:45 | 12.58 | Flood
OF4 | U1 | 9000 | 2022-05-07 16:32 | 2022-05-16 09:30 | 12.58 | Flood
OF5 | U1 | 9000 | 2022-05-07 16:37 | 2022-05-16 09:21 | 12.58 | Flood
OF6 | U1 | 9000 | 2022-05-07 21:24 | 2022-05-16 09:14 | 12.58 | Flood
OF7 | U1 | 9000 | 2022-05-08 17:02 | 2022-05-16 09:00 | 12.58 | Flood
OF8 | U1 | 9010 | 2022-05-08 17:04 | 2022-05-16 08:54 | 12.58 | "Fire including wildfires, not related to a specific component"
BR7 | SF | 5108 | 2022-05-11 12:00 | 2022-05-11 15:06 | 157 | High engine exhaust temperature
BR5 | U1 | 3972 | 2022-05-11 17:50 | 2022-05-11 22:38 | 120 | DCS - hardware problems (including card failure)
GH2 | U1 | 3110 | 2022-05-11 21:19 | 2022-05-13 01:06 | 485.5 | Condenser tube leaks
HA2 | U1 | 4620 | 2022-05-12 13:25 | 2022-05-12 16:01 | 12.8333 | Air cooling system
PR13 | U1 | 3671 | 2022-05-17 05:42 | 2022-05-17 09:50 | 161 | 12-15kV circuit breakers
PR12 | U1 | 3671 | 2022-05-17 05:42 | 2022-05-17 07:15 | 25.5 | 12-15kV circuit breakers
TC10 | U1 | 3670 | 2022-05-20 02:12 | 2022-05-20 05:14 | 169 | 12-15kV transformers
TC9 | U1 | 3670 | 2022-05-20 02:12 | 2022-05-20 05:14 | 169 | 12-15kV transformers
OF2 | U1 | 7053 | 2022-05-23 10:10 | 2022-05-23 10:30 | 12.58 | Governor oil system
OF1 | U1 | 7110 | 2022-05-25 07:04 | 2022-05-25 13:29 | 12.58 | Intake channel or flume (including trash racks)
MC2 | SF | 3235 | 2022-05-27 05:49 | 2022-06-05 03:30 | 297 | Cooling tower booster pump
OF1 | U1 | 7110 | 2022-05-29 14:13 | 2022-06-01 09:38 | 12.58 | Intake channel or flume (including trash racks)
OF3 | U1 | 9000 | 2022-05-30 07:09 | 2022-06-01 07:45 | 12.58 | Flood
OF2 | U1 | 9000 | 2022-05-30 07:58 | 2022-06-01 09:33 | 12.58 | Flood
OF4 | U1 | 9000 | 2022-05-30 08:55 | 2022-06-01 07:37 | 12.58 | Flood
OF5 | U1 | 9000 | 2022-05-30 10:18 | 2022-06-01 07:23 | 12.58 | Flood
OF6 | U1 | 9000 | 2022-05-30 20:19 | 2022-06-01 07:18 | 12.58 | Flood
CR7 | U1 | 4800 | 2022-05-31 05:30 | 2022-06-01 07:40 | 694 | Generator main leads
OF8 | U1 | 7110 | 2022-05-31 07:04 | 2022-06-01 06:55 | 12.58 | Intake channel or flume (including trash racks)
OF7 | U1 | 7110 | 2022-05-31 07:09 | 2022-06-01 07:01 | 12.58 | Intake channel or flume (including trash racks)
MC1 | U1 | 4264 | 2022-06-02 15:49 | 2022-06-02 19:01 | 300 | Combined intercept valves
OF2 | U1 | 4609 | 2022-06-03 06:43 | 2022-06-03 09:28 | 12.58 | Other exciter problems
BR9 | U1 | 5121 | 2022-06-07 09:40 | 2022-06-07 13:37 | 121 | Hydraulic oil system pumps
OF1 | U1 | 7110 | 2022-06-08 05:24 | 2022-06-09 06:56 | 12.58 | Intake channel or flume (including trash racks)
CR7 | SF | 5050 | 2022-06-10 09:07 | 2022-06-10 09:49 | 662 | Ignition system
OF1 | U1 | 4740 | 2022-06-13 14:52 | 2022-06-13 17:16 | 12.58 | Emergency generator trip devices
OF8 | U1 | 7053 | 2022-06-13 20:16 | 2022-06-14 07:41 | 12.58 | Governor oil system
BR7 | U1 | 3972 | 2022-06-15 08:02 | 2022-06-15 13:56 | 146 | DCS - hardware problems (including card failure)
BR3 | U1 | 3619 | 2022-06-16 02:23 | 2022-06-16 10:10 | 412 | Other switchyard equipment - external (OMC)
TC9 | U1 | 3972 | 2022-06-18 21:56 | 2022-06-19 05:29 | 159 | DCS - hardware problems (including card failure)
TC9 | SF | 5016 | 2022-06-19 11:39 | 2022-06-19 13:29 | 159 | High pressure compressor bleed valves
PR13 | SF | 3661 | 2022-06-20 07:22 | 2022-06-20 07:37 | 147 | 4000-7000 volt circuit breakers
GH1 | U1 | 1000 | 2022-06-21 01:11 | 2022-06-21 08:31 | 475 | Waterwall (Furnace wall)
BR11 | SF | 5130 | 2022-06-22 10:03 | 2022-06-22 10:18 | 121 | Starting system (including motor)
OF1 | U1 | 9135 | 2022-06-22 14:15 | 2022-06-24 09:31 | 12.58 | Lack of water
MC1 | U1 | 1455 | 2022-06-22 15:40 | 2022-06-22 16:56 | 300 | Induced draft fans
OF3 | U1 | 9135 | 2022-06-22 17:30 | 2022-06-24 06:56 | 12.58 | Lack of water
OF3 | U1 | 9135 | 2022-06-25 03:56 | 2022-06-28 07:24 | 12.58 | Lack of water
OF4 | U1 | 9135 | 2022-06-25 06:44 | 2022-06-27 07:04 | 12.58 | Lack of water
OF1 | U1 | 9135 | 2022-06-25 09:28 | 2022-06-28 08:47 | 12.58 | Lack of water
OF2 | U1 | 9135 | 2022-06-25 13:55 | 2022-06-28 08:40 | 12.58 | Lack of water
OF5 | U1 | 9135 | 2022-06-25 14:54 | 2022-06-27 06:58 | 12.58 | Lack of water
OF6 | U1 | 9135 | 2022-06-25 16:21 | 2022-06-28 07:39 | 12.58 | Lack of water
OF1 | U1 | 9135 | 2022-06-30 06:38 | 2022-07-07 08:41 | 12.58 | Lack of water
OF7 | U1 | 9135 | 2022-06-30 13:16 | 2022-07-05 12:16 | 12.58 | Lack of water
OF4 | U1 | 9135 | 2022-06-30 20:08 | 2022-07-05 12:35 | 12.58 | Lack of water
OF2 | U1 | 9135 | 2022-07-01 01:15 | 2022-07-07 07:38 | 12.58 | Lack of water
OF5 | U1 | 9135 | 2022-07-01 04:15 | 2022-07-05 12:29 | 12.58 | Lack of water
OF3 | U1 | 9135 | 2022-07-01 05:31 | 2022-07-05 12:49 | 12.58 | Lack of water
OF6 | U1 | 9900 | 2022-07-01 06:17 | 2022-07-01 06:40 | 12.58 | Operator error
OF6 | U1 | 7008 | 2022-07-06 00:44 | 2022-07-06 07:09 | 12.58 | Bearing cooling system
OF6 | U1 | 9135 | 2022-07-06 07:09 | 2022-07-07 06:45 | 12.58 | Lack of water
BR8 | SF | 5530 | 2022-07-06 08:54 | 2022-07-06 11:49 | 121 | Starting system (including motor)
BR9 | SF | 3618 | 2022-07-06 09:16 | 2022-07-06 12:04 | 121 | Other switchyard equipment - external (not OMC)
OF3 | U1 | 9135 | 2022-07-06 10:48 | 2022-07-07 07:34 | 12.58 | Lack of water
OF4 | U1 | 9135 | 2022-07-06 13:52 | 2022-07-07 06:49 | 12.58 | Lack of water
BR5 | U1 | 4750 | 2022-07-11 17:01 | 2022-07-13 12:52 | 130 | Other generator controls and metering problems
OF1 | U1 | 9135 | 2022-07-13 12:04 | 2022-07-19 07:19 | 12.58 | Lack of water
OF2 | U1 | 9135 | 2022-07-13 12:40 | 2022-07-19 07:34 | 12.58 | Lack of water
OF3 | U1 | 9135 | 2022-07-16 13:59 | 2022-07-19 06:54 | 12.58 | Lack of water
OF4 | U1 | 9135 | 2022-07-16 15:43 | 2022-07-18 10:43 | 12.58 | Lack of water
OF5 | U1 | 3979 | 2022-07-16 22:42 | 2022-07-17 08:38 | 12.58 | Other DCS problems
OF6 | U1 | 3979 | 2022-07-16 22:44 | 2022-07-17 08:35 | 12.58 | Other DCS problems
OF7 | U1 | 3979 | 2022-07-16 22:48 | 2022-07-17 08:28 | 12.58 | Other DCS problems
OF8 | U1 | 3979 | 2022-07-16 22:49 | 2022-07-17 08:25 | 12.58 | Other DCS problems
OF5 | U1 | 9135 | 2022-07-17 14:45 | 2022-07-18 07:38 | 12.58 | Lack of water
BR11 | U1 | 4511 | 2022-07-20 11:19 | 2022-07-20 15:59 | 121 | "Rotor, General"
BR7 | SF | 8656 | 2022-07-21 10:54 | 2022-07-21 16:00 | 146 | Controls and instrumentation
OF1 | U1 | 9135 | 2022-07-22 13:58 | 2022-07-25 06:49 | 12.58 | Lack of water
OF2 | U1 | 9135 | 2022-07-22 16:13 | 2022-07-25 06:49 | 12.58 | Lack of water
TC1 | U1 | 890 | 2022-07-24 01:30 | 2022-07-26 21:29 | 369.75 | Bottom ash systems (wet or dry)
TC1 | U1 | 1475 | 2022-07-31 08:04 | 2022-07-31 10:27 | 369.75 | Induced draft fan controls
OF8 | U1 | 7110 | 2022-08-02 03:21 | 2022-08-02 13:10 | 12.58 | Intake channel or flume (including trash racks)
OF4 | U1 | 7110 | 2022-08-02 06:05 | 2022-08-02 13:32 | 12.58 | Intake channel or flume (including trash racks)
OF7 | U1 | 7110 | 2022-08-02 06:45 | 2022-08-02 13:14 | 12.58 | Intake channel or flume (including trash racks)
OF6 | U1 | 7110 | 2022-08-02 06:46 | 2022-08-02 13:20 | 12.58 | Intake channel or flume (including trash racks)
OF5 | U1 | 7110 | 2022-08-02 06:48 | 2022-08-02 13:23 | 12.58 | Intake channel or flume (including trash racks)
OF3 | U1 | 7110 | 2022-08-02 06:49 | 2022-08-02 13:42 | 12.58 | Intake channel or flume (including trash racks)
OF2 | U1 | 7110 | 2022-08-02 06:51 | 2022-08-02 13:49 | 12.58 | Intake channel or flume (including trash racks)
OF1 | U1 | 7110 | 2022-08-02 06:52 | 2022-08-02 13:55 | 12.58 | Intake channel or flume (including trash racks)
MC2 | U1 | 1799 | 2022-08-02 21:41 | 2022-08-03 10:38 | 297 | Other boiler instrumentation and control problems
MC2 | U1 | 1710 | 2022-08-05 03:16 | 2022-08-05 05:17 | 297 | "Combustion/steam condition controls (report local controls - burners, pulverizers, etc., - with component or system)"
MC2 | U1 | 800 | 2022-08-05 06:10 | 2022-08-05 08:15 | 297 | Drums and drum internals (single drum only)
Dix 3 | U1 | 7009 | 2022-08-13 06:25 | 2022-08-13 10:43 | 11.2 | Bearing oil system
Dix 2 | U1 | 4550 | 2022-08-14 11:26 | 2022-08-14 13:49 | 11.2 | Generator bearings and lube oil system (including thrust bearings on hydro units)
Dix 2 | U1 | 4550 | 2022-08-14 13:51 | 2022-08-14 17:52 | 11.2 | Generator bearings and lube oil system (including thrust bearings on hydro units)
TC5 | U1 | 5091 | 2022-08-15 11:16 | 2022-08-15 12:08 | 159 | Low pressure bearings
OF4 | U1 | 7110 | 2022-08-17 06:59 | 2022-08-22 09:13 | 12.58 | Intake channel or flume (including trash racks)
BR5 | SF | 5130 | 2022-08-19 11:47 | 2022-08-19 16:20 | 130 | Starting system (including motor)
OF3 | U1 | 7053 | 2022-08-19 14:17 | 2022-08-23 07:32 | 12.58 | Governor oil system
OF5 | U1 | 9135 | 2022-08-20 15:01 | 2022-08-22 12:24 | 12.58 | Lack of water
OF6 | U1 | 9135 | 2022-08-20 17:03 | 2022-08-22 12:30 | 12.58 | Lack of water
OF8 | U1 | 7110 | 2022-08-23 10:33 | 2022-08-23 13:36 | 12.58 | Intake channel or flume (including trash racks)
OF7 | U1 | 7110 | 2022-08-23 10:35 | 2022-08-23 13:37 | 12.58 | Intake channel or flume (including trash racks)
OF6 | U1 | 7110 | 2022-08-23 10:52 | 2022-08-23 13:47 | 12.58 | Intake channel or flume (including trash racks)
OF5 | U1 | 7110 | 2022-08-23 10:53 | 2022-08-23 13:41 | 12.58 | Intake channel or flume (including trash racks)
OF3 | U1 | 7110 | 2022-08-23 10:57 | 2022-08-23 13:51 | 12.58 | Intake channel or flume (including trash racks)
OF4 | U1 | 7110 | 2022-08-23 10:57 | 2022-08-23 13:48 | 12.58 | Intake channel or flume (including trash racks)
OF2 | U1 | 7110 | 2022-08-23 11:00 | 2022-08-23 13:53 | 12.58 | Intake channel or flume (including trash racks)
OF1 | U1 | 7110 | 2022-08-23 11:00 | 2022-08-23 14:18 | 12.58 | Intake channel or flume (including trash racks)
OF4 | U1 | 9135 | 2022-08-26 06:02 | 2022-08-29 12:39 | 12.58 | Lack of water
OF3 | U1 | 9135 | 2022-08-26 22:15 | 2022-08-29 14:17 | 12.58 | Lack of water
OF2 | U1 | 9135 | 2022-08-28 08:02 | 2022-08-29 16:40 | 12.58 | Lack of water
OF1 | U1 | 9135 | 2022-08-28 13:06 | 2022-08-29 16:40 | 12.58 | Lack of water
OF5 | U1 | 9135 | 2022-08-28 17:01 | 2022-08-29 10:55 | 12.58 | Lack of water
OF6 | U1 | 9135 | 2022-08-28 22:15 | 2022-08-29 08:02 | 12.58 | Lack of water
BR7 | U1 | 4619 | 2022-08-29 09:56 | 2022-08-29 11:09 | 146 | Other hydrogen system problems
OF1 | U1 | 3672 | 2022-08-29 16:40 | 2022-08-30 12:56 | 12.58 | 12-15kV conductors and buses
OF2 | U1 | 3672 | 2022-08-29 16:40 | 2022-08-30 12:56 | 12.58 | 12-15kV conductors and buses
OF3 | U1 | 3672 | 2022-08-29 16:40 | 2022-08-30 12:56 | 12.58 | 12-15kV conductors and buses
OF4 | U1 | 3672 | 2022-08-29 16:40 | 2022-08-30 12:46 | 12.58 | 12-15kV conductors and buses
OF2 | U1 | 9135 | 2022-08-30 12:56 | 2022-09-04 08:24 | 12.58 | Lack of water
OF1 | U1 | 9135 | 2022-08-30 12:56 | 2022-09-04 08:34 | 12.58 | Lack of water
GH1 | U1 | 3812 | 2022-08-31 00:46 | 2022-08-31 07:24 | 475 | Service water valves
BR8 | SF | 5650 | 2022-08-31 09:58 | 2022-08-31 10:18 | 121 | Other controls and instrumentation problems
TC1 | U1 | 1475 | 2022-08-31 10:55 | 2022-08-31 11:35 | 369.75 | Induced draft fan controls
GH1 | U1 | 3972 | 2022-09-01 14:32 | 2022-09-01 18:32 | 477 | DCS - hardware problems (including card failure)
GH1 | U1 | 400 | 2022-09-01 21:40 | 2022-09-02 12:52 | 477 | Burner wind box fires
OF3 | U1 | 9135 | 2022-09-02 06:22 | 2022-09-04 08:09 | 12.58 | Lack of water
OF1 | U1 | 9135 | 2022-09-04 16:00 | 2022-09-06 09:26 | 12.58 | Lack of water
OF2 | U1 | 9135 | 2022-09-04 17:52 | 2022-09-06 09:20 | 12.58 | Lack of water
OF3 | U1 | 9135 | 2022-09-04 17:53 | 2022-09-06 09:15 | 12.58 | Lack of water
OF5 | U1 | 7110 | 2022-09-06 07:17 | 2022-09-06 09:00 | 12.58 | Intake channel or flume (including trash racks)
OF4 | U1 | 7110 | 2022-09-06 07:17 | 2022-09-06 09:11 | 12.58 | Intake channel or flume (including trash racks)
OF6 | U1 | 7110 | 2022-09-06 07:18 | 2022-09-06 08:56 | 12.58 | Intake channel or flume (including trash racks)
OF7 | U1 | 7110 | 2022-09-06 07:20 | 2022-09-06 08:51 | 12.58 | Intake channel or flume (including trash racks)
OF8 | U1 | 7110 | 2022-09-06 07:21 | 2022-09-06 08:47 | 12.58 | Intake channel or flume (including trash racks)
OF5 | U1 | 7110 | 2022-09-06 12:49 | 2022-09-07 07:10 | 12.58 | Intake channel or flume (including trash racks)
OF6 | U1 | 7110 | 2022-09-06 12:54 | 2022-09-07 06:54 | 12.58 | Intake channel or flume (including trash racks)
OF7 | U1 | 7110 | 2022-09-06 12:56 | 2022-09-07 06:43 | 12.58 | Intake channel or flume (including trash racks)
OF4 | U1 | 7110 | 2022-09-06 12:57 | 2022-09-07 07:01 | 12.58 | Intake channel or flume (including trash racks)
OF8 | U1 | 7110 | 2022-09-06 12:59 | 2022-09-07 06:38 | 12.58 | Intake channel or flume (including trash racks)
OF3 | U1 | 7110 | 2022-09-06 13:01 | 2022-09-07 07:16 | 12.58 | Intake channel or flume (including trash racks)
OF2 | U1 | 7110 | 2022-09-06 13:09 | 2022-09-07 07:20 | 12.58 | Intake channel or flume (including trash racks)
OF1 | U1 | 7110 | 2022-09-06 14:14 | 2022-09-07 07:27 | 12.58 | Intake channel or flume (including trash racks)
OF8 | U1 | 9900 | 2022-09-08 12:17 | 2022-09-08 12:25 | 12.58 | Operator error
OF8 | U1 | 7110 | 2022-09-11 06:06 | 2022-09-15 14:00 | 12.58 | Intake channel or flume (including trash racks)
OF7 | U1 | 9135 | 2022-09-12 02:02 | 2022-09-13 13:21 | 12.58 | Lack of water
OF6 | U1 | 7110 | 2022-09-13 03:30 | 2022-09-13 14:06 | 12.58 | Intake channel or flume (including trash racks)
OF5 | U1 | 7110 | 2022-09-13 04:13 | 2022-09-13 14:04 | 12.58 | Intake channel or flume (including trash racks)
OF4 | U1 | 7110 | 2022-09-13 04:19 | 2022-09-13 14:22 | 12.58 | Intake channel or flume (including trash racks)
OF3 | U1 | 7110 | 2022-09-13 05:02 | 2022-09-13 14:19 | 12.58 | Intake channel or flume (including trash racks)
OF2 | U1 | 7110 | 2022-09-13 06:19 | 2022-09-14 06:52 | 12.58 | Intake channel or flume (including trash racks)
OF1 | U1 | 7110 | 2022-09-13 07:16 | 2022-09-14 10:05 | 12.58 | Intake channel or flume (including trash racks)
GH1 | U1 | 3972 | 2022-09-13 08:07 | 2022-09-13 08:55 | 477 | DCS - hardware problems (including card failure)
OF5 | U1 | 9135 | 2022-09-14 09:55 | 2022-09-23 10:40 | 12.58 | Lack of water
OF8 | U1 | 7007 | 2022-09-15 14:00 | 2022-09-23 13:18 | 12.58 | Bearings
OF1 | U1 | 9135 | 2022-09-16 10:58 | 2022-09-28 08:00 | 12.58 | Lack of water
OF4 | U1 | 9135 | 2022-09-16 13:51 | 2022-09-23 10:14 | 12.58 | Lack of water
OF3 | U1 | 9135 | 2022-09-18 08:01 | 2022-09-23 10:48 | 12.58 | Lack of water
OF2 | U1 | 9135 | 2022-09-18 15:56 | 2022-09-28 07:57 | 12.58 | Lack of water
OF6 | U1 | 9135 | 2022-09-21 18:10 | 2022-10-01 06:28 | 12.58 | Lack of water
OF8 | U1 | 9135 | 2022-09-23 13:18 | 2022-10-03 09:22 | 12.58 | Lack of water
OF7 | U1 | 9135 | 2022-09-25 07:31 | 2022-09-28 06:54 | 12.58 | Lack of water
OF3 | U1 | 9135 | 2022-09-25 10:30 | 2022-09-28 06:58 | 12.58 | Lack of water
OF4 | U1 | 9135 | 2022-09-25 13:47 | 2022-09-30 14:02 | 12.58 | Lack of water
OF5 | U1 | 9135 | 2022-09-25 15:44 | 2022-10-02 10:00 | 12.58 | Lack of water
BR3 | U1 | 1000 | 2022-09-26 10:50 | 2022-09-28 18:32 | 414 | Waterwall (Furnace wall)
OF7 | U1 | 9135 | 2022-09-28 18:32 | 2022-10-01 06:22 | 12.58 | Lack of water
OF2 | U1 | 9135 | 2022-09-28 18:52 | 2022-09-30 10:11 | 12.58 | Lack of water
OF3 | U1 | 9135 | 2022-09-28 18:53 | 2022-09-30 12:47 | 12.58 | Lack of water
OF1 | U1 | 9135 | 2022-09-29 01:08 | 2022-09-30 08:46 | 12.58 | Lack of water
OF5 | U1 | 7008 | 2022-10-06 01:51 | 2022-10-06 06:53 | 12.58 | Bearing cooling system
OF7 | U1 | 9135 | 2022-10-07 04:57 | 2022-11-01 06:33 | 12.58 | Lack of water
MC1 | SF | 4280 | 2022-10-07 09:15 | 2022-10-08 20:40 | 300 | Lube oil pumps
OF1 | U1 | 9135 | 2022-10-07 17:56 | 2022-11-12 14:21 | 12.58 | Lack of water
OF2 | U1 | 9135 | 2022-10-07 23:08 | 2022-11-12 14:16 | 12.58 | Lack of water
OF3 | U1 | 9135 | 2022-10-08 04:53 | 2022-10-12 07:01 | 12.58 | Lack of water
OF4 | U1 | 9135 | 2022-10-11 12:56 | 2022-10-14 09:03 | 12.58 | Lack of water
OF3 | U1 | 9135 | 2022-10-12 16:54 | 2022-11-12 14:13 | 12.58 | Lack of water
OF5 | U1 | 9135 | 2022-10-12 18:21 | 2022-10-14 09:00 | 12.58 | Lack of water
OF6 | U1 | 9135 | 2022-10-12 21:50 | 2022-10-14 06:44 | 12.58 | Lack of water
TC5 | U1 | 3610 | 2022-10-13 14:25 | 2022-10-13 15:13 | 169 | Switchyard circuit breakers - external (not OMC)
TC6 | U1 | 3610 | 2022-10-13 14:25 | 2022-10-13 15:13 | 169 | Switchyard circuit breakers - external (not OMC)
OF4 | U1 | 9135 | 2022-10-14 13:09 | 2022-11-09 07:43 | 12.58 | Lack of water
OF5 | U1 | 9135 | 2022-10-14 14:46 | 2022-10-22 06:21 | 12.58 | Lack of water
OF6 | U1 | 9135 | 2022-10-15 01:08 | 2022-10-16 06:49 | 12.58 | Lack of water
OF8 | U1 | 9135 | 2022-10-15 10:19 | 2022-10-16 06:51 | 12.58 | Lack of water
OF6 | U1 | 9135 | 2022-10-17 23:56 | 2022-10-22 06:16 | 12.58 | Lack of water
BR7 | SF | 5001 | 2022-10-18 06:00 | 2022-10-21 11:58 | 157 | Inlet air vanes/nozzles
TC2 | U1 | 1000 | 2022-10-20 22:46 | 2022-10-23 20:20 | 559.5 | Waterwall (Furnace wall)
TC1 | SF | 4293 | 2022-10-22 02:19 | 2022-10-22 13:06 | 369.75 | Hydraulic system pipes and valves
OF8 | U1 | 9135 | 2022-10-23 08:11 | 2022-10-28 10:51 | 12.58 | Lack of water
OF6 | U1 | 9135 | 2022-10-23 15:12 | 2022-10-25 09:11 | 12.58 | Lack of water
BR7 | U1 | 5048 | 2022-10-24 11:07 | 2022-10-24 11:30 | 157 | Gas fuel system including controls and instrumentation
OF5 | U1 | 9135 | 2022-10-29 09:58 | 2022-11-06 08:29 | 12.58 | Lack of water
OF6 | U1 | 9135 | 2022-10-29 10:31 | 2022-11-01 06:36 | 12.58 | Lack of water
OF8 | U1 | 9135 | 2022-10-29 11:00 | 2022-10-31 11:44 | 12.58 | Lack of water
OF6 | U1 | 9135 | 2022-11-02 08:50 | 2022-11-06 08:20 | 12.58 | Lack of water
OF8 | U1 | 9135 | 2022-11-02 14:38 | 2022-11-06 08:26 | 12.58 | Lack of water
OF5 | U1 | 9135 | 2022-11-07 09:51 | 2022-11-09 07:35 | 12.58 | Lack of water
OF6 | U1 | 9135 | 2022-11-07 12:52 | 2022-11-09 07:31 | 12.58 | Lack of water
OF7 | U1 | 9135 | 2022-11-07 20:08 | 2022-11-09 07:27 | 12.58 | Lack of water
OF4 | U1 | 9135 | 2022-11-10 00:50 | 2022-11-12 14:08 | 12.58 | Lack of water
OF5 | U1 | 9135 | 2022-11-10 09:01 | 2022-11-12 14:05 | 12.58 | Lack of water
TC7 | U1 | 5122 | 2022-11-12 15:15 | 2022-11-14 13:30 | 169 | Hydraulic oil system piping/valves
TC6 | U1 | 5017 | 2022-11-14 22:19 | 2022-11-15 16:04 | 169 | Low pressure compressor bleed valves
GH2 | U1 | 3499 | 2022-11-19 18:22 | 2022-11-19 20:11 | 485.5 | Other feedwater system problems
TC10 | U1 | 5017 | 2022-11-20 07:30 | 2022-11-20 08:12 | 169 | Low pressure compressor bleed valves
OF1 | U1 | 9135 | 2022-11-26 01:00 | 2022-11-28 07:40 | 12.58 | Lack of water
OF6 | U1 | 9135 | 2022-11-27 00:21 | 2022-11-28 07:54 | 12.58 | Lack of water
OF2 | U1 | 9135 | 2022-11-27 09:46 | 2022-11-28 07:46 | 12.58 | Lack of water
OF3 | U1 | 9135 | 2022-11-27 11:57 | 2022-11-28 07:50 | 12.58 | Lack of water
MC3 | U1 | 1421 | 2022-12-01 14:40 | 2022-12-01 15:45 | 394 | Secondary air fans/blowers
OF4 | U1 | 7110 | 2022-12-02 11:50 | 2022-12-12 14:21 | 12.58 | Intake channel or flume (including trash racks)
PR13 | U1 | 5150 | 2022-12-03 03:06 | 2022-12-03 15:54 | 175 | Turning gear and motor
BR10 | U1 | 5109 | 2022-12-03 18:26 | 2023-01-01 | 138 | Other exhaust problems (including high exhaust system temperature not attributable to a specific problem)
OF1 | U1 | 7110 | 2022-12-11 08:08 | 2022-12-12 14:58 | 12.58 | Intake channel or flume (including trash racks)
OF2 | U1 | 7110 | 2022-12-11 08:10 | 2022-12-12 08:20 | 12.58 | Intake channel or flume (including trash racks)
OF3 | U1 | 7110 | 2022-12-11 08:13 | 2022-12-12 08:27 | 12.58 | Intake channel or flume (including trash racks)
OF5 | U1 | 7110 | 2022-12-11 08:15 | 2022-12-12 14:53 | 12.58 | Intake channel or flume (including trash racks)
OF6 | U1 | 7110 | 2022-12-11 08:19 | 2022-12-12 11:59 | 12.58 | Intake channel or flume (including trash racks)
OF7 | U1 | 7110 | 2022-12-11 08:22 | 2022-12-12 09:46 | 12.58 | Intake channel or flume (including trash racks)
OF8 | U1 | 7110 | 2022-12-11 08:28 | 2022-12-12 09:41 | 12.58 | Intake channel or flume (including trash racks)
CR7 | U1 | 3330 | 2022-12-13 09:18 | 2022-12-13 11:05 | 683 | Condensate valves
CR7 | U1 | 5041 | 2022-12-13 13:35 | 2022-12-13 14:24 | 683 | Fuel piping and valves
CR7 | SF | 801 | 2022-12-13 14:24 | 2022-12-13 15:34 | 683 | HP Drum (including drum level trips not attributable to other causes)
Dix 3 | U1 | 3653 | 2022-12-14 12:52 | 2022-12-14 14:24 | 11.2 | DC protection devices
TC1 | U1 | 897 | 2022-12-22 15:35 | 2022-12-30 02:19 | 369.75 | Bottom ash rotary (drag chain type) conveyor and motor
BR5 | U1 | 5041 | 2022-12-23 01:28 | 2022-12-23 17:22 | 130 | Fuel piping and valves
BR9 | U1 | 5041 | 2022-12-23 01:30 | 2022-12-23 03:50 | 138 | Fuel piping and valves
BR8 | U1 | 5041 | 2022-12-23 01:30 | 2022-12-23 03:36 | 128 | Fuel piping and valves
BR11 | U1 | 5041 | 2022-12-23 01:30 | 2022-12-23 03:50 | 128 | Fuel piping and valves
BR8 | U1 | 5111 | 2022-12-23 03:36 | 2022-12-23 06:26 | 128 | Lube oil pumps
OF1 | U1 | 9036 | 2022-12-23 04:32 | 2022-12-27 14:40 | 12.58 | "Storms (ice, snow, etc)"
PR13 | U1 | 3822 | 2022-12-23 06:36 | 2022-12-23 07:13 | 175 | Closed cooling water valves
HA2 | U1 | 3700 | 2022-12-23 10:33 | 2022-12-24 14:57 | 13.6667 | Power Station switchyard (non generating unit equipment)
HA1 | U1 | 3700 | 2022-12-23 10:33 | 2022-12-24 14:57 | 13.6667 | Power Station switchyard (non generating unit equipment)
TC5 | U1 | 5048 | 2022-12-23 13:08 | 2022-12-23 13:48 | 179 | Gas fuel system including controls and instrumentation, Interstate pipeline gas pressure issue
TC5 | U1 | 9130 | 2022-12-23 13:48 | 2022-12-25 11:47 | 179 | "Lack of fuel (water from rivers or lakes, coal mines, gas lines, etc) where the operator is not in control of contracts, supply lines, or delivery of fuels", Interstate pipeline gas pressure issue
OF4 | U1 | 9036 | 2022-12-23 15:20 | 2022-12-27 10:39 | 12.58 | "Storms (ice, snow, etc)"
BR11 | U1 | 5073 | 2022-12-23 15:39 | 2022-12-23 17:03 | 128 | Flame scanners
OF3 | U1 | 9036 | 2022-12-23 16:49 | 2022-12-27 13:39 | 12.58 | "Storms (ice, snow, etc)"
HA2 | U1 | 5110 | 2022-12-24 14:57 | 2022-12-28 10:30 | 13.6667 | Lube oil system - general
TC9 | U1 | 9130 | 2022-12-25 08:39 | 2022-12-25 11:47 | 179 | "Lack of fuel (water from rivers or lakes, coal mines, gas lines, etc) where the operator is not in control of contracts, supply lines, or delivery of fuels", Interstate pipeline gas pressure issue
BR3 | U1 | 920 | 2022-12-25 21:15 | 2023-01-01 | 416 | Other slag and ash removal problems
OF1 | U1 | 9135 | 2022-12-27 15:57 | 2022-12-29 14:34 | 12.58 | Lack of water
OF2 | U1 | 9135 | 2022-12-28 14:31 | 2022-12-29 13:46 | 12.58 | Lack of water
OF3 | U1 | 7053 | 2022-12-29 15:10 | 2022-12-29 16:20 | 12.58 | Governor oil system
PR12 | U1 | 3872 | 2022-12-29 21:55 | 2022-12-30 11:38 | 28 | Fuel Gas Compressor Valves
OF1 | U1 | 7110 | 2022-12-30 07:14 | 2023-01-01 | 12.58 | Intake channel or flume (including trash racks)
Note: The "MW on Outage" value is the Seasonal Net Unit Rating for Fossil Fuel units and the Generator Nameplate Rating for Hydro and Solar units.

## Unit Abbreviations Key
BR | E.W. Brown
CR | Cane Run
Dix | Dix Dam
GH | Ghent
HF | Haefling
MC | Mill Creek
OF | Ohio Falls
PR | Paddys Run
TC | Trimble County