## Daily MWh Lost by Type (4.1.a.)
Date | Forced Daily | Maintenance Daily | Combined
2014-01-01 | 2160.9909 | 497.6757 | 2658.6666
2014-01-02 | 1233.0229 | 4246.2193 | 5479.2423
2014-01-03 | 12068.2672 | 7342.4912 | 19410.7584
2014-01-04 | 5655.8617 | 3543.15 | 9199.0117
2014-01-05 | 3705.2664 | 0 | 3705.2664
2014-01-06 | 6029.535 | 0 | 6029.535
2014-01-07 | 4654.7992 | 0 | 4654.7992
2014-01-08 | 10065.1837 | 238.1374 | 10303.3211
2014-01-09 | 8443.0889 | 3308.8641 | 11751.953
2014-01-10 | 5628.3203 | 14254.7802 | 19883.1005
2014-01-11 | 10640.312 | 23224.9378 | 33865.2498
2014-01-12 | 9320.9658 | 19487.2 | 28808.1658
2014-01-13 | 10775.5054 | 9333.6318 | 20109.1372
2014-01-14 | 11923.3917 | 7802.7445 | 19726.1362
2014-01-15 | 9595.3379 | 7462.398 | 17057.7359
2014-01-16 | 8744.7444 | 7168.8031 | 15913.5475
2014-01-17 | 1640.331 | 1632.3757 | 3272.7068
2014-01-18 | 2010.2443 | 538.7882 | 2549.0326
2014-01-19 | 683.4465 | 157.5254 | 840.9719
2014-01-20 | 1546.3803 | 1409.7248 | 2956.1052
2014-01-21 | 611.4816 | 441.7655 | 1053.247
2014-01-22 | 1631.2101 | 0 | 1631.2101
2014-01-23 | 1359.629 | 0 | 1359.629
2014-01-24 | 1428.8249 | 103.0276 | 1531.8526
2014-01-25 | 10690.3975 | 1428.7549 | 12119.1524
2014-01-26 | 17588.2221 | 1550.4333 | 19138.6555
2014-01-27 | 3861.7021 | 10845 | 14706.7021
2014-01-28 | 583.6459 | 0 | 583.6459
2014-01-29 | 854.011 | 0 | 854.011
2014-01-30 | 13181.8901 | 4715.5667 | 17897.4568
2014-01-31 | 11891.3085 | 11568 | 23459.3085
2014-02-01 | 7449.9101 | 8843.8 | 16293.7101
2014-02-02 | 4505.2182 | 11856.2688 | 16361.4871
2014-02-03 | 882.471 | 1981.509 | 2863.98
2014-02-04 | 156.5031 | 1995.4022 | 2151.9053
2014-02-05 | 2485.1666 | 895.8116 | 3380.9782
2014-02-06 | 155.52 | 310.3558 | 465.8758
2014-02-07 | 5708.5812 | 64.2872 | 5772.8685
2014-02-08 | 7923.146 | 215.1573 | 8138.3033
2014-02-09 | 8889.2498 | 71.7191 | 8960.9689
2014-02-10 | 1524.5304 | 848.631 | 2373.1614
2014-02-11 | 1617.7396 | 0 | 1617.7396
2014-02-12 | 473.3395 | 0 | 473.3395
2014-02-13 | 432.8764 | 211.1922 | 644.0686
2014-02-14 | 1354.091 | 415.5151 | 1769.606
2014-02-15 | 1988.9665 | 7614.6889 | 9603.6555
2014-02-16 | 1559.7385 | 13021.4499 | 14581.1884
2014-02-17 | 3699.8166 | 13522.5536 | 17222.3702
2014-02-18 | 6669.6237 | 7873.3509 | 14542.9745
2014-02-19 | 2927.3474 | 16890.7053 | 19818.0527
2014-02-20 | 2674.2607 | 15114.6803 | 17788.9409
2014-02-21 | 4972.2135 | 13493.7504 | 18465.9639
2014-02-22 | 10705.5559 | 14209.1833 | 24914.7392
2014-02-23 | 2350.2097 | 11154.65 | 13504.8597
2014-02-24 | 2845.5629 | 4600.5735 | 7446.1364
2014-02-25 | 3246.2609 | 9151.7494 | 12398.0103
2014-02-26 | 2796.8156 | 2092.3753 | 4889.1909
2014-02-27 | 1017.2977 | 1147.8324 | 2165.13
2014-02-28 | 861.3948 | 5389.3246 | 6250.7194
2014-03-01 | 1053.78 | 8675.4525 | 9729.2325
2014-03-02 | 1794.7147 | 4986.2 | 6780.9147
2014-03-03 | 5650.8206 | 0 | 5650.8206
2014-03-04 | 6812.7342 | 0 | 6812.7342
2014-03-05 | 18674.5542 | 29.8006 | 18704.3548
2014-03-06 | 8683.4834 | 2711.2198 | 11394.7032
2014-03-07 | 490.6872 | 5198.1852 | 5688.8724
2014-03-08 | 1560.8196 | 1246.3803 | 2807.2
2014-03-09 | 720.8777 | 1913.8039 | 2634.6816
2014-03-10 | 2434.3354 | 0 | 2434.3354
2014-03-11 | 7519.6904 | 206.5909 | 7726.2813
2014-03-12 | 4920.0588 | 303 | 5223.0588
2014-03-13 | 3027.1284 | 0 | 3027.1284
2014-03-14 | 3949.8987 | 0 | 3949.8987
2014-03-15 | 638.4143 | 0 | 638.4143
2014-03-16 | 715.7333 | 0 | 715.7333
2014-03-17 | 738.0408 | 0 | 738.0408
2014-03-18 | 421.1848 | 2365.3756 | 2786.5604
2014-03-19 | 2058.8518 | 2961.3756 | 5020.2274
2014-03-20 | 10141.6387 | 91.7 | 10233.3387
2014-03-21 | 4006.4483 | 2456.2762 | 6462.7246
2014-03-22 | 1839.5724 | 3838.0668 | 5677.6392
2014-03-23 | 1008.5732 | 1102.0668 | 2110.64
2014-03-24 | 1516.2788 | 1700.2789 | 3216.5577
2014-03-25 | 1943.036 | 4209.4729 | 6152.5088
2014-03-26 | 1084.0605 | 1178.8941 | 2262.9546
2014-03-27 | 1288.8851 | 575.6122 | 1864.4973
2014-03-28 | 1059.1585 | 0 | 1059.1585
2014-03-29 | 2170.4339 | 0 | 2170.4339
2014-03-30 | 528.7797 | 0 | 528.7797
2014-03-31 | 2334.1407 | 344.303 | 2678.4437
2014-04-01 | 7727.8048 | 861.2443 | 8589.0491
2014-04-02 | 8304.4603 | 2190.0481 | 10494.5084
2014-04-03 | 10059.5319 | 253.7234 | 10313.2553
2014-04-04 | 7561.0588 | 294.3191 | 7855.378
2014-04-05 | 4255.404 | 9394.5327 | 13649.9367
2014-04-06 | 2479.2909 | 6924.1167 | 9403.4076
2014-04-07 | 2206.5194 | 580.6114 | 2787.1308
2014-04-08 | 4396.8382 | 321.0754 | 4717.9137
2014-04-09 | 4693.3667 | 443.8007 | 5137.1674
2014-04-10 | 2563.7524 | 3830.3433 | 6394.0957
2014-04-11 | 5844.0739 | 2385.7696 | 8229.8435
2014-04-12 | 11124.3228 | 2530.545 | 13654.8678
2014-04-13 | 7359.5171 | 708.5803 | 8068.0973
2014-04-14 | 3244.9764 | 694.8488 | 3939.8252
2014-04-15 | 1763.0438 | 1158.268 | 2921.3118
2014-04-16 | 1180.8836 | 0 | 1180.8836
2014-04-17 | 5086.1183 | 444.4377 | 5530.556
2014-04-18 | 8096.1909 | 447.5019 | 8543.6928
2014-04-19 | 7635.2654 | 11972.2122 | 19607.4777
2014-04-20 | 6302.3055 | 2694.5969 | 8996.9023
2014-04-21 | 7884.2981 | 149.3595 | 8033.6577
2014-04-22 | 6840.2803 | 5852.1139 | 12692.3941
2014-04-23 | 7546.8574 | 9705.0754 | 17251.9329
2014-04-24 | 9900.0089 | 1383.8894 | 11283.8982
2014-04-25 | 11001.4313 | 3079.4318 | 14080.8631
2014-04-26 | 7189.279 | 2391.6333 | 9580.9123
2014-04-27 | 6797.0713 | 165.2727 | 6962.3441
2014-04-28 | 15224.1374 | 553.1983 | 15777.3357
2014-04-29 | 17413.9177 | 1981.2425 | 19395.1602
2014-04-30 | 16798.2625 | 1203.8737 | 18002.1362
2014-05-01 | 8702.8217 | 322.1258 | 9024.9475
2014-05-02 | 11552.7311 | 12079.2 | 23631.9311
2014-05-03 | 9430.4174 | 11256 | 20686.4174
2014-05-04 | 1900.8204 | 11437.1386 | 13337.9591
2014-05-05 | 1325.3537 | 15361.72 | 16687.0736
2014-05-06 | 2661.6639 | 8163.0898 | 10824.7536
2014-05-07 | 2498.3272 | 2102.4971 | 4600.8243
2014-05-08 | 3700.8621 | 2812.2329 | 6513.0949
2014-05-09 | 1835.3242 | 17413.142 | 19248.4662
2014-05-10 | 1560.5142 | 21336 | 22896.5142
2014-05-11 | 1357.8947 | 13231.9488 | 14589.8435
2014-05-12 | 3177.9842 | 4508.082 | 7686.0661
2014-05-13 | 2757.9251 | 1174.848 | 3932.7731
2014-05-14 | 2980.9707 | 1306.4047 | 4287.3754
2014-05-15 | 1773.5796 | 14889.5876 | 16663.1672
2014-05-16 | 1815.6617 | 4885.095 | 6700.7567
2014-05-17 | 2731.8059 | 24832.9833 | 27564.7892
2014-05-18 | 2620.366 | 7089.073 | 9709.439
2014-05-19 | 1059.1839 | 7860.0886 | 8919.2726
2014-05-20 | 11606.7415 | 7926.5842 | 19533.3257
2014-05-21 | 18484.0875 | 3073.7388 | 21557.8264
2014-05-22 | 21455.5873 | 221.6455 | 21677.2328
2014-05-23 | 10558.254 | 877.7333 | 11435.9873
2014-05-24 | 3633.8101 | 10380.95 | 14014.7601
2014-05-25 | 4119.7706 | 3720 | 7839.7706
2014-05-26 | 4445.0465 | 3884.1818 | 8329.2284
2014-05-27 | 4764.577 | 5398.9641 | 10163.5411
2014-05-28 | 10298.8249 | 3455.8758 | 13754.7007
2014-05-29 | 7591.148 | 1114.929 | 8706.077
2014-05-30 | 2888.3774 | 8277.9285 | 11166.3058
2014-05-31 | 2215.9482 | 29005.8084 | 31221.7566
2014-06-01 | 8632.1191 | 25442.2631 | 34074.3822
2014-06-02 | 13230.7143 | 4864.2011 | 18094.9153
2014-06-03 | 2694.3166 | 4280.8609 | 6975.1775
2014-06-04 | 4908.3303 | 4602.011 | 9510.3413
2014-06-05 | 9113.0836 | 7671.2164 | 16784.3001
2014-06-06 | 15939.0539 | 7095.7333 | 23034.7872
2014-06-07 | 13719.3085 | 14387.95 | 28107.2585
2014-06-08 | 19688.8554 | 13608 | 33296.8554
2014-06-09 | 11036.3212 | 19383.7914 | 30420.1126
2014-06-10 | 5244.7689 | 24088.7237 | 29333.4926
2014-06-11 | 8865.0755 | 12663.8172 | 21528.8927
2014-06-12 | 3523.776 | 11954.8143 | 15478.5902
2014-06-13 | 2636.5539 | 14906.9593 | 17543.5132
2014-06-14 | 4254.9357 | 3010.1333 | 7265.069
2014-06-15 | 11699.495 | 675.7931 | 12375.2881
2014-06-16 | 5445.2893 | 1876.5277 | 7321.817
2014-06-17 | 4314.8021 | 126.4004 | 4441.2025
2014-06-18 | 13252.987 | 600.599 | 13853.586
2014-06-19 | 5837.1722 | 1122.6241 | 6959.7964
2014-06-20 | 3675.8173 | 1407.3636 | 5083.181
2014-06-21 | 3063.4948 | 1088.6621 | 4152.157
2014-06-22 | 6484.0834 | 83.0368 | 6567.1201
2014-06-23 | 9930.0554 | 272.9289 | 10202.9843
2014-06-24 | 8558.7201 | 1107.2447 | 9665.9648
2014-06-25 | 6502.0697 | 1571.7538 | 8073.8235
2014-06-26 | 6912.9262 | 1821.9265 | 8734.8527
2014-06-27 | 6556.6284 | 654.7213 | 7211.3497
2014-06-28 | 4082.8223 | 2312.5843 | 6395.4066
2014-06-29 | 19579.1628 | 184.6215 | 19763.7843
2014-06-30 | 15915.314 | 133.869 | 16049.1831
2014-07-01 | 14853.4586 | 588.1774 | 15441.636
2014-07-02 | 16258.6797 | 892.9579 | 17151.6376
2014-07-03 | 21555.8901 | 1071.0524 | 22626.9426
2014-07-04 | 17780.1295 | 10992 | 28772.1295
2014-07-05 | 15397.7568 | 10992 | 26389.7568
2014-07-06 | 13970.3027 | 8800.688 | 22770.9907
2014-07-07 | 14837.5541 | 7466.136 | 22303.6901
2014-07-08 | 19923.4722 | 2249.2123 | 22172.6845
2014-07-09 | 15755.2791 | 644.7251 | 16400.0042
2014-07-10 | 19166.8914 | 1859.1936 | 21026.085
2014-07-11 | 19841.3684 | 376.4533 | 20217.8217
2014-07-12 | 18304.6799 | 83.7893 | 18388.4692
2014-07-13 | 7248.8537 | 4031.5787 | 11280.4324
2014-07-14 | 10790.6408 | 847.7184 | 11638.3593
2014-07-15 | 9470.7688 | 16023.2 | 25493.9688
2014-07-16 | 7534.1524 | 20301.3167 | 27835.4691
2014-07-17 | 10597.6189 | 10949.6156 | 21547.2345
2014-07-18 | 13074.3745 | 1950.6667 | 15025.0411
2014-07-19 | 11043.1742 | 21173.4087 | 32216.5829
2014-07-20 | 11022.3322 | 20083.8945 | 31106.2267
2014-07-21 | 11479.0233 | 3231.0801 | 14710.1034
2014-07-22 | 10336.0969 | 22.0325 | 10358.1294
2014-07-23 | 14766.2298 | 344.0787 | 15110.3085
2014-07-24 | 16359.7742 | 1169.6138 | 17529.388
2014-07-25 | 19166.6812 | 573.0088 | 19739.69
2014-07-26 | 13145.204 | 2747.4055 | 15892.6096
2014-07-27 | 11868.3465 | 1581.6133 | 13449.9598
2014-07-28 | 2255.0729 | 8775.5133 | 11030.5862
2014-07-29 | 12243.6682 | 9467.7347 | 21711.4029
2014-07-30 | 13168.2261 | 3035.3745 | 16203.6005
2014-07-31 | 6656.1954 | 2455.8367 | 9112.0321
2014-08-01 | 2325.0238 | 9790.9705 | 12115.9943
2014-08-02 | 13811.4821 | 11509.6192 | 25321.1013
2014-08-03 | 5103.2755 | 9051.5667 | 14154.8422
2014-08-04 | 3602.0051 | 157.4127 | 3759.4178
2014-08-05 | 2795.3283 | 1126.4203 | 3921.7486
2014-08-06 | 5396.744 | 378.0284 | 5774.7725
2014-08-07 | 3421.885 | 3975.4333 | 7397.3183
2014-08-08 | 1171.6894 | 14203.4862 | 15375.1756
2014-08-09 | 1429.0126 | 12641.5639 | 14070.5765
2014-08-10 | 2950.7441 | 3801 | 6751.7441
2014-08-11 | 15041.2928 | 654.1879 | 15695.4807
2014-08-12 | 9457.0714 | 1552.194 | 11009.2654
2014-08-13 | 1457.2931 | 5261.9893 | 6719.2824
2014-08-14 | 1475.036 | 4669.4498 | 6144.4859
2014-08-15 | 7885.2024 | 4056 | 11941.2024
2014-08-16 | 1903.8725 | 6557.25 | 8461.1225
2014-08-17 | 3739.9288 | 336 | 4075.9288
2014-08-18 | 5615.1059 | 754.8743 | 6369.9802
2014-08-19 | 2352.5267 | 997.4126 | 3349.9393
2014-08-20 | 2537.7455 | 576.1335 | 3113.8791
2014-08-21 | 4500.2795 | 498 | 4998.2795
2014-08-22 | 6029.766 | 640.85 | 6670.616
2014-08-23 | 8972.4844 | 11719.5 | 20691.9844
2014-08-24 | 6009.4 | 11737.8409 | 17747.2409
2014-08-25 | 10527.8915 | 1114.3109 | 11642.2023
2014-08-26 | 9801.1479 | 1791.563 | 11592.7109
2014-08-27 | 10556.3743 | 1490.1518 | 12046.5262
2014-08-28 | 14690.1937 | 953.2686 | 15643.4623
2014-08-29 | 13337.2434 | 909.9647 | 14247.208
2014-08-30 | 2928.3696 | 2880 | 5808.3696
2014-08-31 | 2521.7291 | 4289.9 | 6811.6291
2014-09-01 | 4352.3312 | 559.4167 | 4911.7479
2014-09-02 | 8406.6163 | 959.6037 | 9366.22
2014-09-03 | 4046.8156 | 1716.3028 | 5763.1184
2014-09-04 | 6176.4858 | 529.8 | 6706.2858
2014-09-05 | 11075.6384 | 4188.6503 | 15264.2887
2014-09-06 | 1937.5002 | 16809.1726 | 18746.6728
2014-09-07 | 3567.1755 | 8689.1451 | 12256.3206
2014-09-08 | 4845.8412 | 1360.5094 | 6206.3506
2014-09-09 | 4306.3247 | 561.75 | 4868.0747
2014-09-10 | 3908.9085 | 1575.9592 | 5484.8677
2014-09-11 | 4213.945 | 3923.3555 | 8137.3005
2014-09-12 | 1500.9332 | 10762.7604 | 12263.6936
2014-09-13 | 1763.7445 | 450.8649 | 2214.6094
2014-09-14 | 7162.645 | 0 | 7162.645
2014-09-15 | 14747.645 | 3949.6667 | 18697.3117
2014-09-16 | 14740.4008 | 1174.8333 | 15915.2342
2014-09-17 | 20683.5694 | 1985.3333 | 22668.9027
2014-09-18 | 29529.2392 | 2023.5619 | 31552.8011
2014-09-19 | 28651.7074 | 1746.8346 | 30398.542
2014-09-20 | 20040.2137 | 4127.8755 | 24168.0892
2014-09-21 | 13681.9487 | 4177.9394 | 17859.8881
2014-09-22 | 24460.506 | 1435.8222 | 25896.3282
2014-09-23 | 9413.8188 | 2883.9101 | 12297.729
2014-09-24 | 3141.8426 | 8397.3706 | 11539.2131
2014-09-25 | 5881.3254 | 14118.0736 | 19999.399
2014-09-26 | 995.0392 | 13739.1682 | 14734.2074
2014-09-27 | 750.1392 | 16072.4867 | 16822.6259
2014-09-28 | 1920.4919 | 6836.7551 | 8757.2469
2014-09-29 | 1627.3763 | 9244.9486 | 10872.3249
2014-09-30 | 3958.7597 | 8454.4311 | 12413.1908
2014-10-01 | 2565.5833 | 11941.1941 | 14506.7774
2014-10-02 | 4977.0262 | 9134.1781 | 14111.2043
2014-10-03 | 3829.3682 | 9309.3517 | 13138.7199
2014-10-04 | 2349.8222 | 32328.1335 | 34677.9556
2014-10-05 | 2471.8384 | 34102.8668 | 36574.7052
2014-10-06 | 4470.9113 | 27667.0668 | 32137.9781
2014-10-07 | 9662.07 | 3875.812 | 13537.882
2014-10-08 | 14472.4371 | 1330.355 | 15802.7921
2014-10-09 | 11801.4724 | 2103.0486 | 13904.521
2014-10-10 | 8210.2131 | 11504.7513 | 19714.9644
2014-10-11 | 3553.2954 | 9767.8299 | 13321.1253
2014-10-12 | 2453.8947 | 1618.5829 | 4072.4776
2014-10-13 | 8350.6638 | 1060.3919 | 9411.0558
2014-10-14 | 8106.0152 | 838.6557 | 8944.6709
2014-10-15 | 1760.8781 | 603.035 | 2363.9131
2014-10-16 | 2112.6532 | 332.0178 | 2444.671
2014-10-17 | 1596.0747 | 1989.3 | 3585.3747
2014-10-18 | 1662.6579 | 0 | 1662.6579
2014-10-19 | 3495.0833 | 336.4805 | 3831.5638
2014-10-20 | 1605.657 | 5259.6404 | 6865.2974
2014-10-21 | 1934.4302 | 5967.7566 | 7902.1868
2014-10-22 | 2941.7405 | 6827.9306 | 9769.6711
2014-10-23 | 2170.4193 | 10012.6041 | 12183.0234
2014-10-24 | 2425.292 | 7573.3947 | 9998.6867
2014-10-25 | 1737.6597 | 15970.7667 | 17708.4264
2014-10-26 | 1739.3111 | 15686.2048 | 17425.5159
2014-10-27 | 2258.0403 | 8467.2333 | 10725.2736
2014-10-28 | 4269.4688 | 526.9818 | 4796.4507
2014-10-29 | 4038.9836 | 2950.8358 | 6989.8193
2014-10-30 | 2545.0044 | 1129.1581 | 3674.1625
2014-10-31 | 5988.4535 | 415.5292 | 6403.9827
2014-11-01 | 8832.1165 | 1166.824 | 9998.9405
2014-11-02 | 6994.3894 | 1017.624 | 8012.0134
2014-11-03 | 1912.7114 | 449.885 | 2362.5964
2014-11-04 | 1817.6066 | 406.7116 | 2224.3182
2014-11-05 | 2068.265 | 704.2814 | 2772.5465
2014-11-06 | 3470.1287 | 1242.6696 | 4712.7984
2014-11-07 | 1596.0747 | 407.85 | 2003.9247
2014-11-08 | 2823.7173 | 11832 | 14655.7173
2014-11-09 | 2169.0248 | 4931.4 | 7100.4248
2014-11-10 | 1639.5899 | 2431.9194 | 4071.5093
2014-11-11 | 1674.0095 | 5146.651 | 6820.6605
2014-11-12 | 5585.3858 | 4412.8269 | 9998.2127
2014-11-13 | 13317.6963 | 2570.4 | 15888.0963
2014-11-14 | 14479.8655 | 1002.7501 | 15482.6156
2014-11-15 | 16200.1875 | 914.2721 | 17114.4596
2014-11-16 | 17740.2821 | 0 | 17740.2821
2014-11-17 | 14494.6888 | 0 | 14494.6888
2014-11-18 | 6901.6388 | 0 | 6901.6388
2014-11-19 | 8105.3976 | 922.7576 | 9028.1552
2014-11-20 | 7454.0123 | 583.8986 | 8037.9109
2014-11-21 | 12623.5031 | 258.7965 | 12882.2996
2014-11-22 | 13730.6815 | 4212.2382 | 17942.9197
2014-11-23 | 11441.6991 | 13190.6667 | 24632.3658
2014-11-24 | 8000.2342 | 13166.15 | 21166.3842
2014-11-25 | 5291.2254 | 11979.0909 | 17270.3163
2014-11-26 | 2868.8175 | 8368.0606 | 11236.8781
2014-11-27 | 7721.7569 | 12662.3667 | 20384.1236
2014-11-28 | 4620.6728 | 17078.8333 | 21699.5061
2014-11-29 | 6156.2946 | 4320.0833 | 10476.378
2014-11-30 | 3649.4676 | 5872.2298 | 9521.6974
2014-12-01 | 5525.2087 | 8809.3667 | 14334.5753
2014-12-02 | 1596.0747 | 13660.4968 | 15256.5716
2014-12-03 | 1962.0246 | 18815.8944 | 20777.919
2014-12-04 | 2203.4247 | 22121.942 | 24325.3668
2014-12-05 | 13224.9247 | 16716.1513 | 29941.0761
2014-12-06 | 21789.0693 | 21559.5096 | 43348.579
2014-12-07 | 29236.4746 | 15576 | 44812.4746
2014-12-08 | 14218.1273 | 15576 | 29794.1273
2014-12-09 | 10993.4226 | 9681.5333 | 20674.9559
2014-12-10 | 27214.6975 | 4032 | 31246.6975
2014-12-11 | 23697.8831 | 523.6 | 24221.4831
2014-12-12 | 20879.9738 | 178.5 | 21058.4738
2014-12-13 | 21633.378 | 11571.939 | 33205.317
2014-12-14 | 8375.9588 | 21980.7848 | 30356.7435
2014-12-15 | 7788.3011 | 20305.5357 | 28093.8368
2014-12-16 | 13165.7058 | 10309.3286 | 23475.0344
2014-12-17 | 21290.5336 | 10002.2667 | 31292.8002
2014-12-18 | 21861.7798 | 9936 | 31797.7798
2014-12-19 | 20482.4751 | 9936 | 30418.4751
2014-12-20 | 15907.2766 | 2158.65 | 18065.9266
2014-12-21 | 4309.8679 | 14794.8987 | 19104.7666
2014-12-22 | 3219.6851 | 15582.5188 | 18802.2039
2014-12-23 | 10183.9987 | 9310.0384 | 19494.0371
2014-12-24 | 9166.6923 | 11784 | 20950.6923
2014-12-25 | 11507.3747 | 11784 | 23291.3747
2014-12-26 | 10017.3965 | 9525.4 | 19542.7965
2014-12-27 | 8821.4462 | 0 | 8821.4462
2014-12-28 | 8960.8721 | 2030.2142 | 10991.0863
2014-12-29 | 8861.7543 | 88.5714 | 8950.3257
2014-12-30 | 8845.2257 | 137.2857 | 8982.5115
2014-12-31 | 9359.7327 | 0 | 9359.7327
2015-01-01 | 8776.8506 | 353.4 | 9130.2506
2015-01-02 | 9664.0507 | 3720 | 13384.0507
2015-01-03 | 8772.0747 | 2474.0762 | 11246.1509
2015-01-04 | 11190.0747 | 97.2 | 11287.2747
2015-01-05 | 11666.8215 | 420.9322 | 12087.7536
2015-01-06 | 6636.1173 | 169.6313 | 6805.7486
2015-01-07 | 9164.7808 | 0 | 9164.7808
2015-01-08 | 10945.0729 | 0 | 10945.0729
2015-01-09 | 7772.2935 | 0 | 7772.2935
2015-01-10 | 8512.4081 | 204.0833 | 8716.4914
2015-01-11 | 2438.1186 | 3720 | 6158.1186
2015-01-12 | 3522.6242 | 332.9271 | 3855.5513
2015-01-13 | 2414.3441 | 1216.0079 | 3630.3521
2015-01-14 | 3054.4545 | 172.251 | 3226.7055
2015-01-15 | 4744.0074 | 10820.0212 | 15564.0286
2015-01-16 | 5043.8518 | 14065.4035 | 19109.2553
2015-01-17 | 3847.9309 | 22623.65 | 26471.5809
2015-01-18 | 4372.5425 | 27645.6429 | 32018.1854
2015-01-19 | 7709.3782 | 17816.3667 | 25525.7449
2015-01-20 | 7944.4824 | 10486.756 | 18431.2384
2015-01-21 | 2923.236 | 11498.8333 | 14422.0693
2015-01-22 | 6150.5207 | 8917.2957 | 15067.8164
2015-01-23 | 4300.9163 | 5974.7779 | 10275.6943
2015-01-24 | 2981.7395 | 9782.5775 | 12764.317
2015-01-25 | 10383.8672 | 8838 | 19221.8672
2015-01-26 | 31577.6317 | 0 | 31577.6317
2015-01-27 | 2872.665 | 0 | 2872.665
2015-01-28 | 2766.6317 | 8316.6 | 11083.2317
2015-01-29 | 2794.0079 | 16866 | 19660.0079
2015-01-30 | 2285.079 | 18813.2 | 21098.279
2015-01-31 | 3953.665 | 12045.8334 | 15999.4984
2015-02-01 | 2245.4593 | 3120 | 5365.4593
2015-02-02 | 2227.3943 | 301.0986 | 2528.4929
2015-02-03 | 3268.4651 | 2237.4972 | 5505.9622
2015-02-04 | 8030.4372 | 3660.4537 | 11690.891
2015-02-05 | 9887.1643 | 2953.6568 | 12840.8211
2015-02-06 | 10713.8742 | 2849.2887 | 13563.1628
2015-02-07 | 4288.065 | 10594.6733 | 14882.7384
2015-02-08 | 3184.7687 | 8275.5902 | 11460.3588
2015-02-09 | 4451.5279 | 3871.2188 | 8322.7467
2015-02-10 | 10593.1305 | 4429.6127 | 15022.7432
2015-02-11 | 8955.9694 | 5847.96 | 14803.9294
2015-02-12 | 3546.2788 | 3605.0059 | 7151.2847
2015-02-13 | 7615.8289 | 45.9298 | 7661.7587
2015-02-14 | 6759.7289 | 42.9333 | 6802.6623
2015-02-15 | 15966.6122 | 0 | 15966.6122
2015-02-16 | 8350.1675 | 0 | 8350.1675
2015-02-17 | 10352.7951 | 266.9333 | 10619.7285
2015-02-18 | 8397.3695 | 0 | 8397.3695
2015-02-19 | 11529.3246 | 0 | 11529.3246
2015-02-20 | 11118.5072 | 9.4667 | 11127.9738
2015-02-21 | 7890.9041 | 2668.2822 | 10559.1863
2015-02-22 | 7698.4741 | 2730 | 10428.4741
2015-02-23 | 19619.6515 | 0 | 19619.6515
2015-02-24 | 13077.0402 | 3317.8201 | 16394.8603
2015-02-25 | 12042.1253 | 8531.0106 | 20573.1359
2015-02-26 | 12067.0028 | 3597.0995 | 15664.1023
2015-02-27 | 16403.0686 | 0 | 16403.0686
2015-02-28 | 11683.4262 | 5529.1286 | 17212.5548
2015-03-01 | 3072.2537 | 11861 | 14933.2537
2015-03-02 | 3494.1167 | 14543.6601 | 18037.7768
2015-03-03 | 4624.4757 | 10212.2537 | 14836.7295
2015-03-04 | 4658.3008 | 8872.9081 | 13531.2089
2015-03-05 | 8826.2552 | 1478.4667 | 10304.7219
2015-03-06 | 18374.0955 | 0 | 18374.0955
2015-03-07 | 6476.3974 | 452 | 6928.3974
2015-03-08 | 5008.1728 | 7720.3527 | 12728.5255
2015-03-09 | 3155.1506 | 8988.9833 | 12144.134
2015-03-10 | 2711.6654 | 6575.3393 | 9287.0047
2015-03-11 | 3368.3867 | 6600.559 | 9968.9457
2015-03-12 | 4434.6897 | 6033.8333 | 10468.523
2015-03-13 | 3090.0959 | 20245.3333 | 23335.4292
2015-03-14 | 3773.6234 | 21816.0333 | 25589.6568
2015-03-15 | 3340.9085 | 21840.4889 | 25181.3974
2015-03-16 | 3983.6866 | 17743.6376 | 21727.3242
2015-03-17 | 7845.1655 | 10187.8276 | 18032.9931
2015-03-18 | 8188.1656 | 9984 | 18172.1656
2015-03-19 | 7504.1174 | 18990.8833 | 26495.0007
2015-03-20 | 7496.7805 | 22630.0667 | 30126.8471
2015-03-21 | 7496.7805 | 29727.0638 | 37223.8442
2015-03-22 | 7979.4032 | 29477.8513 | 37457.2546
2015-03-23 | 15293.3311 | 10652.65 | 25945.9811
2015-03-24 | 9859.1177 | 5760 | 15619.1177
2015-03-25 | 5572.8251 | 7141.6 | 12714.4251
2015-03-26 | 3394.2302 | 5760 | 9154.2302
2015-03-27 | 2684.3557 | 5760 | 8444.3557
2015-03-28 | 3063.0533 | 5760 | 8823.0533
2015-03-29 | 2182.6559 | 6948.6659 | 9131.3217
2015-03-30 | 3198.0984 | 6391.7407 | 9589.8392
2015-03-31 | 2720.0237 | 6772.9561 | 9492.9798
2015-04-01 | 1994.382 | 660.289 | 2654.671
2015-04-02 | 868.5279 | 313.6 | 1182.1279
2015-04-03 | 5929.3055 | 26.6948 | 5956.0003
2015-04-04 | 5213.4363 | 2769.3333 | 7982.7697
2015-04-05 | 2879.347 | 3317 | 6196.347
2015-04-06 | 5729.4361 | 0 | 5729.4361
2015-04-07 | 2703.3217 | 933.5021 | 3636.8238
2015-04-08 | 2494.8794 | 381.9691 | 2876.8485
2015-04-09 | 3838.6284 | 0 | 3838.6284
2015-04-10 | 1535.9539 | 136.85 | 1672.8039
2015-04-11 | 817.3114 | 10507.1333 | 11324.4447
2015-04-12 | 964.6232 | 3719.1438 | 4683.7669
2015-04-13 | 5697.5892 | 604.9367 | 6302.5259
2015-04-14 | 3947.8345 | 0 | 3947.8345
2015-04-15 | 1223.1466 | 0 | 1223.1466
2015-04-16 | 525.9466 | 75.1823 | 601.1289
2015-04-17 | 1877.8722 | 216.2692 | 2094.1414
2015-04-18 | 7573.0257 | 4763.0333 | 12336.059
2015-04-19 | 11840.0412 | 366.8333 | 12206.8745
2015-04-20 | 9020.6598 | 0 | 9020.6598
2015-04-21 | 10253.6258 | 1229.9 | 11483.5258
2015-04-22 | 8129.7248 | 162.381 | 8292.1057
2015-04-23 | 8100.9192 | 244.4325 | 8345.3518
2015-04-24 | 8705.8044 | 1093.1498 | 9798.9542
2015-04-25 | 8262.6932 | 11343.1062 | 19605.7994
2015-04-26 | 8100.9192 | 11256 | 19356.9192
2015-04-27 | 8100.9192 | 11256 | 19356.9192
2015-04-28 | 8100.9192 | 11560.3 | 19661.2192
2015-04-29 | 13088.2859 | 11335.3452 | 24423.6311
2015-04-30 | 8100.9192 | 12658.9451 | 20759.8644
2015-05-01 | 8801.9246 | 12698.1667 | 21500.0913
2015-05-02 | 9382.1632 | 9384 | 18766.1632
2015-05-03 | 16544.7781 | 9384 | 25928.7781
2015-05-04 | 13548.1621 | 9344.0106 | 22892.1727
2015-05-05 | 6745.3911 | 8589.9089 | 15335.3
2015-05-06 | 12199.1974 | 4483.8951 | 16683.0925
2015-05-07 | 17119.6161 | 2104.2048 | 19223.8209
2015-05-08 | 16947.1027 | 1185.4333 | 18132.5361
2015-05-09 | 9217.8544 | 1747.2333 | 10965.0877
2015-05-10 | 2708.171 | 0 | 2708.171
2015-05-11 | 3751.9373 | 8776.8 | 12528.7373
2015-05-12 | 4199.6596 | 15889.243 | 20088.9026
2015-05-13 | 5282.2896 | 22107.9007 | 27390.1903
2015-05-14 | 13507.4639 | 23764.3422 | 37271.8061
2015-05-15 | 11202.5302 | 32459.6333 | 43662.1635
2015-05-16 | 6695.1557 | 28988.0833 | 35683.239
2015-05-17 | 15217.5115 | 15456 | 30673.5115
2015-05-18 | 13677.1483 | 16271.2227 | 29948.371
2015-05-19 | 12201.3394 | 7273.6863 | 19475.0257
2015-05-20 | 12974.1632 | 9347.5667 | 22321.7298
2015-05-21 | 13073.3596 | 21553.0333 | 34626.3929
2015-05-22 | 13108.4374 | 29692.41 | 42800.8474
2015-05-23 | 6513.862 | 17456.1 | 23969.962
2015-05-24 | 6256.6351 | 3785.3333 | 10041.9684
2015-05-25 | 1593.6742 | 3532.5 | 5126.1742
2015-05-26 | 2583.2864 | 8500.8779 | 11084.1643
2015-05-27 | 5006.2918 | 10479.9207 | 15486.2125
2015-05-28 | 4779.6523 | 5523.9076 | 10303.5599
2015-05-29 | 1786.6364 | 1839.298 | 3625.9343
2015-05-30 | 3516.253 | 2565.2823 | 6081.5353
2015-05-31 | 5769.4697 | 6045.5576 | 11815.0273
2015-06-01 | 7523.1783 | 576.0682 | 8099.2465
2015-06-02 | 6029.8733 | 7452.7833 | 13482.6567
2015-06-03 | 6637.8491 | 1600.85 | 8238.6991
2015-06-04 | 2220.9415 | 3611 | 5831.9415
2015-06-05 | 1320.1314 | 7246.8451 | 8566.9765
2015-06-06 | 1894.7906 | 11107.323 | 13002.1135
2015-06-07 | 2048.303 | 16145.2167 | 18193.5197
2015-06-08 | 3884.1998 | 1288.6533 | 5172.8531
2015-06-09 | 3232.3393 | 661.0006 | 3893.3399
2015-06-10 | 3027.7763 | 590.2653 | 3618.0416
2015-06-11 | 14429.2357 | 506.1974 | 14935.4331
2015-06-12 | 5816.46 | 1082.9205 | 6899.3804
2015-06-13 | 9173.0898 | 9904.7167 | 19077.8065
2015-06-14 | 17694.8721 | 9834.0667 | 27528.9387
2015-06-15 | 10907.6688 | 3066.4045 | 13974.0733
2015-06-16 | 8011.6116 | 3715.8394 | 11727.451
2015-06-17 | 4531.6364 | 6226.4112 | 10758.0476
2015-06-18 | 4531.6364 | 10601.8013 | 15133.4377
2015-06-19 | 7019.8399 | 22551.0064 | 29570.8463
2015-06-20 | 920.603 | 29069.3262 | 29989.9292
2015-06-21 | 1940.803 | 22786.1887 | 24726.9917
2015-06-22 | 2120.8776 | 8818.9665 | 10939.8441
2015-06-23 | 956.4009 | 8432.1685 | 9388.5694
2015-06-24 | 2961.0697 | 8644.9839 | 11606.0536
2015-06-25 | 9696.4364 | 8810.6248 | 18507.0612
2015-06-26 | 12113.5517 | 9305.3512 | 21418.9029
2015-06-27 | 8627.0864 | 23069.65 | 31696.7364
2015-06-28 | 5021.8212 | 17223.3407 | 22245.1619
2015-06-29 | 1510.3033 | 18200.5989 | 19710.9022
2015-06-30 | 7027.3917 | 11451.8361 | 18479.2277
2015-07-01 | 5274.703 | 10341.7069 | 15616.4098
2015-07-02 | 11411.5296 | 12915.4241 | 24326.9536
2015-07-03 | 8741.5948 | 19224 | 27965.5948
2015-07-04 | 2104.613 | 16798.1667 | 18902.7796
2015-07-05 | 1788.3643 | 9384 | 11172.3643
2015-07-06 | 2763.3974 | 2293.8667 | 5057.2641
2015-07-07 | 3546.0297 | 1081.0613 | 4627.091
2015-07-08 | 1858.5602 | 8461.9659 | 10320.5261
2015-07-09 | 1766.2768 | 8117.8333 | 9884.1102
2015-07-10 | 2137.9136 | 1574.1 | 3712.0136
2015-07-11 | 1766.2768 | 2544 | 4310.2768
2015-07-12 | 1766.2768 | 2544 | 4310.2768
2015-07-13 | 5893.3987 | 2827.1706 | 8720.5694
2015-07-14 | 4381.9514 | 2770.1255 | 7152.0769
2015-07-15 | 9681.3279 | 3207.3154 | 12888.6433
2015-07-16 | 4304.9997 | 2544 | 6848.9997
2015-07-17 | 2114.7194 | 2450.3667 | 4565.0861
2015-07-18 | 6308.6365 | 0 | 6308.6365
2015-07-19 | 5838.0753 | 72.7273 | 5910.8025
2015-07-20 | 5822.8356 | 84.8485 | 5907.6841
2015-07-21 | 8981.9669 | 26.6 | 9008.5669
2015-07-22 | 12747.5038 | 640.3387 | 13387.8425
2015-07-23 | 5086.6686 | 15087 | 20173.6686
2015-07-24 | 4315.5879 | 0 | 4315.5879
2015-07-25 | 5911.1501 | 11867.55 | 17778.7001
2015-07-26 | 16341.557 | 3797.25 | 20138.807
2015-07-27 | 19485.8479 | 0 | 19485.8479
2015-07-28 | 11550.4729 | 0 | 11550.4729
2015-07-29 | 3825.7442 | 127.5 | 3953.2442
2015-07-30 | 3511.3177 | 175.3125 | 3686.6302
2015-07-31 | 2830.2541 | 0 | 2830.2541
2015-08-01 | 2568.2724 | 0 | 2568.2724
2015-08-02 | 9022.8081 | 0 | 9022.8081
2015-08-03 | 5172.2984 | 0 | 5172.2984
2015-08-04 | 16926.2866 | 0 | 16926.2866
2015-08-05 | 9420.488 | 551.6833 | 9972.1713
2015-08-06 | 4009.168 | 12389.65 | 16398.818
2015-08-07 | 2550.6452 | 26568 | 29118.6452
2015-08-08 | 5225.0906 | 9510.85 | 14735.9406
2015-08-09 | 1168.2921 | 3863.7 | 5031.9921
2015-08-10 | 2968.3668 | 864.7 | 3833.0668
2015-08-11 | 3266.0643 | 2794.85 | 6060.9143
2015-08-12 | 2251.9088 | 13543.8 | 15795.7088
2015-08-13 | 13571.4588 | 13541.7016 | 27113.1603
2015-08-14 | 23748.698 | 12762.0022 | 36510.7002
2015-08-15 | 24410.1254 | 7682.0159 | 32092.1413
2015-08-16 | 2132.4046 | 292.3003 | 2424.7049
2015-08-17 | 4756.1217 | 849.6033 | 5605.725
2015-08-18 | 2532.2633 | 8159.85 | 10692.1133
2015-08-19 | 2211.3206 | 10939.1276 | 13150.4482
2015-08-20 | 10608.4588 | 17273.3773 | 27881.836
2015-08-21 | 3279.9798 | 16577.5333 | 19857.5131
2015-08-22 | 8421.8546 | 7613.9699 | 16035.8245
2015-08-23 | 11139.5421 | 6120.3844 | 17259.9265
2015-08-24 | 15603.5771 | 2800.085 | 18403.6622
2015-08-25 | 1480.2921 | 3701.0698 | 5181.3619
2015-08-26 | 4941.2421 | 3148.8763 | 8090.1184
2015-08-27 | 17001.169 | 3644.606 | 20645.775
2015-08-28 | 16718.0468 | 2958 | 19676.0468
2015-08-29 | 12968.8784 | 2957.2012 | 15926.0796
2015-08-30 | 19507.7491 | 3084.0535 | 22591.8026
2015-08-31 | 26184.0158 | 2930.7424 | 29114.7583
2015-09-01 | 28287.8071 | 1141.5 | 29429.3071
2015-09-02 | 13026.7561 | 102.2802 | 13129.0363
2015-09-03 | 3133.5588 | 457.9409 | 3591.4997
2015-09-04 | 1480.2921 | 777.14 | 2257.4321
2015-09-05 | 1601.6825 | 2365.2 | 3966.8825
2015-09-06 | 2428.8722 | 11461.95 | 13890.8222
2015-09-07 | 2114.6821 | 9007.35 | 11122.0321
2015-09-08 | 8476.3937 | 0 | 8476.3937
2015-09-09 | 13335.8521 | 3209.0167 | 16544.8688
2015-09-10 | 9274.8988 | 3934.8333 | 13209.7321
2015-09-11 | 2802.0325 | 7261.3833 | 10063.4158
2015-09-12 | 1548.6657 | 19176 | 20724.6657
2015-09-13 | 1480.2921 | 19176 | 20656.2921
2015-09-14 | 10006.1076 | 16577.7 | 26583.8076
2015-09-15 | 9138.1086 | 5296.55 | 14434.6586
2015-09-16 | 10939.9107 | 6700.0204 | 17639.9312
2015-09-17 | 8169.8597 | 5703.5597 | 13873.4195
2015-09-18 | 3235.2921 | 5778.9167 | 9014.2088
2015-09-19 | 3476.0421 | 14747.4 | 18223.4421
2015-09-20 | 3235.2921 | 13006.9 | 16242.1921
2015-09-21 | 13099.0176 | 15918.35 | 29017.3676
2015-09-22 | 16411.2921 | 13751.5667 | 30162.8588
2015-09-23 | 19053.3649 | 8546.7 | 27600.0649
2015-09-24 | 12188.0111 | 4109.95 | 16297.9611
2015-09-25 | 4032.4503 | 5351.75 | 9384.2003
2015-09-26 | 3313.3878 | 3864 | 7177.3878
2015-09-27 | 4361.9878 | 3864 | 8225.9878
2015-09-28 | 4953.3878 | 3864 | 8817.3878
2015-09-29 | 3475.8109 | 4749.3167 | 8225.1276
2015-09-30 | 3313.3878 | 8467.2219 | 11780.6098
2015-10-01 | 2819.7971 | 9362.6667 | 12182.4638
2015-10-02 | 4912.6838 | 8863.0167 | 13775.7005
2015-10-03 | 2933.131 | 646.25 | 3579.381
2015-10-04 | 2933.131 | 2329.65 | 5262.781
2015-10-05 | 3094.8294 | 735.096 | 3829.9253
2015-10-06 | 2982.8417 | 601.8397 | 3584.6814
2015-10-07 | 2933.131 | 1463.544 | 4396.675
2015-10-08 | 4763.2921 | 852.6864 | 5615.9785
2015-10-09 | 5256.3478 | 261.3333 | 5517.6811
2015-10-10 | 2933.131 | 0 | 2933.131
2015-10-11 | 2933.131 | 0 | 2933.131
2015-10-12 | 5968.131 | 0 | 5968.131
2015-10-13 | 10133.131 | 1960.8 | 12093.931
2015-10-14 | 8923.285 | 0 | 8923.285
2015-10-15 | 3145.7702 | 71.5152 | 3217.2854
2015-10-16 | 2621.131 | 269.3737 | 2890.5047
2015-10-17 | 3543.0694 | 885.5 | 4428.5694
2015-10-18 | 16562.181 | 0 | 16562.181
2015-10-19 | 12726.9997 | 0 | 12726.9997
2015-10-20 | 3860.6843 | 245.8333 | 4106.5177
2015-10-21 | 4658.1523 | 4110.3333 | 8768.4856
2015-10-22 | 3357.2677 | 1672.503 | 5029.7708
2015-10-23 | 3088.0628 | 1062.8086 | 4150.8714
2015-10-24 | 3366.1982 | 0 | 3366.1982
2015-10-25 | 3158.1387 | 122.5 | 3280.6387
2015-10-26 | 4882.6889 | 0 | 4882.6889
2015-10-27 | 7423.0422 | 5315.3333 | 12738.3755
2015-10-28 | 3977.722 | 11424 | 15401.722
2015-10-29 | 4657.3053 | 11293.1152 | 15950.4205
2015-10-30 | 3171.9387 | 1028.7 | 4200.6387
2015-10-31 | 3709.3887 | 9112.5 | 12821.8887
2015-11-01 | 3158.1387 | 0 | 3158.1387
2015-11-02 | 3247.5553 | 68.5354 | 3316.0907
2015-11-03 | 3284.8432 | 1411.202 | 4696.0452
2015-11-04 | 3224.2315 | 709.9374 | 3934.1689
2015-11-05 | 9029.6868 | 346.5137 | 9376.2006
2015-11-06 | 17586.2097 | 1553.9692 | 19140.1789
2015-11-07 | 16853.0311 | 2127.5167 | 18980.5477
2015-11-08 | 18006.7404 | 242.0833 | 18248.8238
2015-11-09 | 15713.1557 | 1190.9639 | 16904.1196
2015-11-10 | 6960.5703 | 2559.4337 | 9520.004
2015-11-11 | 6153.2366 | 11582.8109 | 17736.0474
2015-11-12 | 7358.1387 | 12043.3624 | 19401.5011
2015-11-13 | 12087.1535 | 7893.6667 | 19980.8201
2015-11-14 | 19034.1657 | 0 | 19034.1657
2015-11-15 | 18782.1387 | 0 | 18782.1387
2015-11-16 | 15153.9053 | 0 | 15153.9053
2015-11-17 | 14891.6539 | 0 | 14891.6539
2015-11-18 | 9438.4616 | 166.4 | 9604.8616
2015-11-19 | 9099.2048 | 0 | 9099.2048
2015-11-20 | 8060.9495 | 0 | 8060.9495
2015-11-21 | 13047.3993 | 0 | 13047.3993
2015-11-22 | 13264.1947 | 0 | 13264.1947
2015-11-23 | 17070.2758 | 0 | 17070.2758
2015-11-24 | 13832.3384 | 0 | 13832.3384
2015-11-25 | 12356.3991 | 6046.7 | 18403.0991
2015-11-26 | 13769.9158 | 650.7515 | 14420.6674
2015-11-27 | 6760.2 | 14073.3333 | 20833.5333
2015-11-28 | 6721.2481 | 23352 | 30073.2481
2015-11-29 | 6769.6931 | 21452.7 | 28222.3931
2015-11-30 | 19075.6668 | 11807.4773 | 30883.144
2015-12-01 | 10154.0337 | 12082.3636 | 22236.3974
2015-12-02 | 6925.461 | 11664 | 18589.461
2015-12-03 | 6936.978 | 11728.9432 | 18665.9212
2015-12-04 | 7703.4842 | 12286.0983 | 19989.5825
2015-12-05 | 4447.4591 | 15573.1801 | 20020.6392
2015-12-06 | 4196.4758 | 4621.1247 | 8817.6005
2015-12-07 | 4113.3149 | 944.6182 | 5057.9331
2015-12-08 | 4113.3149 | 343.1982 | 4456.5132
2015-12-09 | 13899.1316 | 1180.8 | 15079.9316
2015-12-10 | 3775.3247 | 0 | 3775.3247
2015-12-11 | 3404.7442 | 690.8437 | 4095.5879
2015-12-12 | 2933.8134 | 12897.4473 | 15831.2607
2015-12-13 | 7534.4375 | 8934.9439 | 16469.3814
2015-12-14 | 12125.8134 | 18738.8426 | 30864.656
2015-12-15 | 12125.8134 | 18247.1913 | 30373.0047
2015-12-16 | 12125.8134 | 13845.9471 | 25971.7605
2015-12-17 | 13033.7189 | 13474.7333 | 26508.4523
2015-12-18 | 14810.9285 | 12888 | 27698.9285
2015-12-19 | 6728.7901 | 13150.0025 | 19878.7927
2015-12-20 | 5279.5932 | 14280 | 19559.5932
2015-12-21 | 4889.5387 | 14280 | 19169.5387
2015-12-22 | 5725.2883 | 15052.1674 | 20777.4557
2015-12-23 | 7785.8042 | 9829.2738 | 17615.0781
2015-12-24 | 15625.5136 | 778.1071 | 16403.6207
2015-12-25 | 3457.0944 | 0 | 3457.0944
2015-12-26 | 3326.6856 | 0 | 3326.6856
2015-12-27 | 3252.5577 | 103.8545 | 3356.4123
2015-12-28 | 3904.7775 | 2053.1241 | 5957.9016
2015-12-29 | 5618.1232 | 170.3608 | 5788.484
2015-12-30 | 3782.8996 | 811.2473 | 4594.1469
2015-12-31 | 2685.3777 | 1032.2274 | 3717.6052
2016-01-01 | 3195.0442 | 0 | 3195.0442
2016-01-02 | 2980.8562 | 0 | 2980.8562
2016-01-03 | 2923.4569 | 173.2482 | 3096.7051
2016-01-04 | 3423.3419 | 514.9387 | 3938.2806
2016-01-05 | 7840.3914 | 219.5455 | 8059.9368
2016-01-06 | 8934.0902 | 1508.0029 | 10442.0931
2016-01-07 | 10384.8685 | 5525.2113 | 15910.0797
2016-01-08 | 10408.6199 | 11548.116 | 21956.7359
2016-01-09 | 10274.3365 | 20587.4333 | 30861.7698
2016-01-10 | 17407.4316 | 7603.8 | 25011.2316
2016-01-11 | 29513.295 | 0 | 29513.295
2016-01-12 | 28614.3027 | 250.4383 | 28864.741
2016-01-13 | 14217.1703 | 763.2838 | 14980.4541
2016-01-14 | 4461.4754 | 16449.3 | 20910.7754
2016-01-15 | 3235.1943 | 16824.2113 | 20059.4056
2016-01-16 | 3732.0255 | 7992.1333 | 11724.1588
2016-01-17 | 4836.5969 | 976.05 | 5812.6469
2016-01-18 | 8549.389 | 0 | 8549.389
2016-01-19 | 8504.3873 | 0 | 8504.3873
2016-01-20 | 6113.2338 | 81.8182 | 6195.052
2016-01-21 | 4358.0943 | 587.7273 | 4945.8215
2016-01-22 | 3416.7556 | 379.0909 | 3795.8465
2016-01-23 | 3235.1943 | 0 | 3235.1943
2016-01-24 | 8727.3579 | 0 | 8727.3579
2016-01-25 | 3235.1943 | 0 | 3235.1943
2016-01-26 | 2903.7527 | 4733.4 | 7637.1527
2016-01-27 | 8512.9043 | 10017.9669 | 18530.8712
2016-01-28 | 11859.1402 | 11180.9577 | 23040.0979
2016-01-29 | 2561.7569 | 14812.8 | 17374.5569
2016-01-30 | 2227.4569 | 25779.05 | 28006.5069
2016-01-31 | 2227.4569 | 13570.6667 | 15798.1235
2016-02-01 | 3434.7296 | 11157.4 | 14592.1296
2016-02-02 | 4044.8781 | 8741.8494 | 12786.7274
2016-02-03 | 2382.7915 | 7651.3155 | 10034.107
2016-02-04 | 11155.9627 | 3514.2045 | 14670.1672
2016-02-05 | 13858.4569 | 2943.4949 | 16801.9518
2016-02-06 | 20025.9569 | 11496 | 31521.9569
2016-02-07 | 21263.4569 | 6730.5167 | 27993.9735
2016-02-08 | 15907.4569 | 80.4545 | 15987.9114
2016-02-09 | 7894.139 | 510.8864 | 8405.0254
2016-02-10 | 7555.9856 | 0 | 7555.9856
2016-02-11 | 5899.4569 | 0 | 5899.4569
2016-02-12 | 2698.7707 | 0 | 2698.7707
2016-02-13 | 8210.3867 | 0 | 8210.3867
2016-02-14 | 8113.6866 | 0 | 8113.6866
2016-02-15 | 4434.2569 | 2260.1867 | 6694.4436
2016-02-16 | 7647.6999 | 1631.2284 | 9278.9284
2016-02-17 | 10457.0262 | 11284.1586 | 21741.1848
2016-02-18 | 13184.0402 | 11152.8248 | 24336.865
2016-02-19 | 2227.4569 | 9639.4167 | 11866.8735
2016-02-20 | 3454.1711 | 16560 | 20014.1711
2016-02-21 | 3102.9872 | 12788 | 15890.9872
2016-02-22 | 3263.6616 | 4475 | 7738.6616
2016-02-23 | 3010.3569 | 6248.8 | 9259.1569
2016-02-24 | 2272.3588 | 0 | 2272.3588
2016-02-25 | 3127.196 | 2693.25 | 5820.446
2016-02-26 | 2587.4569 | 931.5 | 3518.9569
2016-02-27 | 5654.5564 | 0 | 5654.5564
2016-02-28 | 8848.2643 | 850.75 | 9699.0143
2016-02-29 | 8221.2474 | 600.8418 | 8822.0892
2016-03-01 | 1550.824 | 1323.1523 | 2873.9762
2016-03-02 | 987.4906 | 882.9043 | 1870.3949
2016-03-03 | 1250.343 | 703.2754 | 1953.6184
2016-03-04 | 1153.8543 | 720 | 1873.8543
2016-03-05 | 987.4906 | 69.0017 | 1056.4923
2016-03-06 | 1541.9074 | 0 | 1541.9074
2016-03-07 | 3342.1924 | 81.8182 | 3424.0106
2016-03-08 | 2332.4426 | 9998.097 | 12330.5396
2016-03-09 | 3499.271 | 12514.397 | 16013.6679
2016-03-10 | 4612.8543 | 7139.9015 | 11752.7558
2016-03-11 | 8928.0294 | 9801.5455 | 18729.5749
2016-03-12 | 19161.939 | 5953.7342 | 25115.6733
2016-03-13 | 11853.8621 | 8112 | 19965.8621
2016-03-14 | 18894.4935 | 8112 | 27006.4935
2016-03-15 | 27820.7903 | 8144.8859 | 35965.6762
2016-03-16 | 36391.8265 | 6816.3333 | 43208.1599
2016-03-17 | 38195.0069 | 0 | 38195.0069
2016-03-18 | 38637.1411 | 0 | 38637.1411
2016-03-19 | 38307.5911 | 0 | 38307.5911
2016-03-20 | 26033.885 | 0 | 26033.885
2016-03-21 | 13895.1182 | 3641.95 | 17537.0682
2016-03-22 | 15652.0585 | 4056 | 19708.0585
2016-03-23 | 13679.8017 | 5092.5333 | 18772.335
2016-03-24 | 19873.7183 | 4219.2333 | 24092.9517
2016-03-25 | 14297.8517 | 4056 | 18353.8517
2016-03-26 | 16296.252 | 4056 | 20352.252
2016-03-27 | 15585.4387 | 4056 | 19641.4387
2016-03-28 | 8368.1385 | 4246.2751 | 12614.4136
2016-03-29 | 8238.544 | 6325.4217 | 14563.9657
2016-03-30 | 6544.4825 | 9821.4525 | 16365.935
2016-03-31 | 6544.4825 | 15951.749 | 22496.2315
2016-04-01 | 5291.6471 | 24716.449 | 30008.0961
2016-04-02 | 4661.0424 | 20758.7667 | 25419.8091
2016-04-03 | 6854.6835 | 8398.5271 | 15253.2106
2016-04-04 | 5765.2969 | 4101.2075 | 9866.5044
2016-04-05 | 4820.7021 | 4943.4138 | 9764.116
2016-04-06 | 5651.1432 | 4096.7754 | 9747.9186
2016-04-07 | 6057.9728 | 4056 | 10113.9728
2016-04-08 | 4590.1907 | 4056 | 8646.1907
2016-04-09 | 5149.1689 | 4056 | 9205.1689
2016-04-10 | 4247.8017 | 5257.7341 | 9505.5358
2016-04-11 | 4637.5018 | 4056 | 8693.5018
2016-04-12 | 4447.4098 | 4239.1869 | 8686.5967
2016-04-13 | 4400.1853 | 4320.7743 | 8720.9596
2016-04-14 | 6530.7517 | 4056 | 10586.7517
2016-04-15 | 4964.611 | 4302.0427 | 9266.6537
2016-04-16 | 8221.9477 | 12491.749 | 20713.6966
2016-04-17 | 16507.1942 | 12491.749 | 28998.9431
2016-04-18 | 15200.2782 | 12491.749 | 27692.0271
2016-04-19 | 9190.3907 | 12491.749 | 21682.1396
2016-04-20 | 8029.6563 | 12491.749 | 20521.4053
2016-04-21 | 3304.7258 | 12799.849 | 16104.5747
2016-04-22 | 1225.1424 | 10430.8607 | 11656.0031
2016-04-23 | 2805.7435 | 6853.25 | 9658.9935
2016-04-24 | 575.8017 | 4056 | 4631.8017
2016-04-25 | 616.8942 | 5905.3364 | 6522.2306
2016-04-26 | 1428.571 | 4461 | 5889.571
2016-04-27 | 1070.7933 | 4994.8377 | 6065.631
2016-04-28 | 6703.2429 | 5139.7783 | 11843.0212
2016-04-29 | 11896.8004 | 5063.225 | 16960.0254
2016-04-30 | 11591.8017 | 19031.3333 | 30623.135
2016-05-01 | 11326.7017 | 17496 | 28822.7017
2016-05-02 | 23.8017 | 18563.4944 | 18587.2961
2016-05-03 | 23.8017 | 29440.2439 | 29464.0456
2016-05-04 | 23.8017 | 30319.1772 | 30342.9789
2016-05-05 | 23.8017 | 26398.9879 | 26422.7895
2016-05-06 | 23.8017 | 31885.1742 | 31908.9759
2016-05-07 | 23.8017 | 25594.1333 | 25617.935
2016-05-08 | 23.8017 | 23886.303 | 23910.1047
2016-05-09 | 4314.3794 | 4797.0642 | 9111.4436
2016-05-10 | 4356.8471 | 8907.5671 | 13264.4142
2016-05-11 | 15721.6732 | 8877.2294 | 24598.9027
2016-05-12 | 20199.3441 | 8851.658 | 29051.0021
2016-05-13 | 9903.3293 | 5812.4142 | 15715.7436
2016-05-14 | 3935.0397 | 8585.7833 | 12520.823
2016-05-15 | 1825.885 | 6287.5833 | 8113.4683
2016-05-16 | 7223.8017 | 14665.9333 | 21889.735
2016-05-17 | 6474.2454 | 23328 | 29802.2454
2016-05-18 | 6502.8513 | 8574.6667 | 15077.518
2016-05-19 | 12379.563 | 298.5239 | 12678.0869
2016-05-20 | 13855.4583 | 7307.7376 | 21163.1958
2016-05-21 | 13463.8017 | 11568 | 25031.8017
2016-05-22 | 13463.8017 | 11568 | 25031.8017
2016-05-23 | 13463.8017 | 11568 | 25031.8017
2016-05-24 | 15505.885 | 11568 | 27073.885
2016-05-25 | 17110.0595 | 11568 | 28678.0595
2016-05-26 | 13533.3899 | 11568 | 25101.3899
2016-05-27 | 13803.5303 | 11568 | 25371.5303
2016-05-28 | 13463.8017 | 11568 | 25031.8017
2016-05-29 | 13584.5232 | 11804.6 | 25389.1232
2016-05-30 | 14466.1311 | 8438.3 | 22904.4311
2016-05-31 | 13788.3761 | 0 | 13788.3761
2016-06-01 | 13688.063 | 0 | 13688.063
2016-06-02 | 15270.4548 | 0 | 15270.4548
2016-06-03 | 16359.513 | 0 | 16359.513
2016-06-04 | 20754.7325 | 0 | 20754.7325
2016-06-05 | 14185.7107 | 0 | 14185.7107
2016-06-06 | 14442.0634 | 81 | 14523.0634
2016-06-07 | 14806.3583 | 2557.9983 | 17364.3566
2016-06-08 | 14066.8448 | 2798.0421 | 16864.8869
2016-06-09 | 19746.5425 | 3271.45 | 23017.9925
2016-06-10 | 13902.2925 | 4872.2667 | 18774.5592
2016-06-11 | 16971.5065 | 0 | 16971.5065
2016-06-12 | 25771.7925 | 0 | 25771.7925
2016-06-13 | 25890.8909 | 0 | 25890.8909
2016-06-14 | 26660.7258 | 0 | 26660.7258
2016-06-15 | 22862.5853 | 153.4335 | 23016.0188
2016-06-16 | 14210.7745 | 320.0185 | 14530.793
2016-06-17 | 14210.8367 | 9513.6833 | 23724.52
2016-06-18 | 14014.338 | 8656.5667 | 22670.9046
2016-06-19 | 14200.838 | 0 | 14200.838
2016-06-20 | 21793.5352 | 305.0833 | 22098.6185
2016-06-21 | 25130.3282 | 263.6667 | 25393.9949
2016-06-22 | 16945.3522 | 0 | 16945.3522
2016-06-23 | 16005.2356 | 170.7912 | 16176.0269
2016-06-24 | 19364.6808 | 299.8719 | 19664.5527
2016-06-25 | 18587.3991 | 309.5819 | 18896.981
2016-06-26 | 20674.6546 | 382.2183 | 21056.8729
2016-06-27 | 20943.3755 | 319.3602 | 21262.7357
2016-06-28 | 20856.6336 | 127.9504 | 20984.584
2016-06-29 | 20742.8286 | 1048.2497 | 21791.0782
2016-06-30 | 20742.8286 | 2089.7411 | 22832.5696
2016-07-01 | 23376.1376 | 7602.5518 | 30978.6893
2016-07-02 | 37354.713 | 8288.3245 | 45643.0374
2016-07-03 | 28119.4357 | 15070.1 | 43189.5357
2016-07-04 | 23853.9242 | 0 | 23853.9242
2016-07-05 | 22069.9812 | 25.5725 | 22095.5537
2016-07-06 | 24487.3345 | 36.691 | 24524.0255
2016-07-07 | 18388.2958 | 134.966 | 18523.2619
2016-07-08 | 19201.1214 | 71.4197 | 19272.541
2016-07-09 | 26105.8383 | 428.4135 | 26534.2518
2016-07-10 | 19622.4626 | 75.9763 | 19698.4389
2016-07-11 | 13902.2925 | 158.284 | 14060.5765
2016-07-12 | 13876.2675 | 37.8104 | 13914.0779
2016-07-13 | 14953.6925 | 198.5046 | 15152.1971
2016-07-14 | 14238.2925 | 185.9012 | 14424.1937
2016-07-15 | 10092.1238 | 195 | 10287.1238
2016-07-16 | 1844.0352 | 7687.3667 | 9531.4018
2016-07-17 | 2445.7468 | 7516.6167 | 9962.3635
2016-07-18 | 6980.4175 | 1945 | 8925.4175
2016-07-19 | 16789.9891 | 0 | 16789.9891
2016-07-20 | 9729.5663 | 9.0053 | 9738.5716
2016-07-21 | 1147.8683 | 0 | 1147.8683
2016-07-22 | 666.6675 | 0 | 666.6675
2016-07-23 | 4895.7925 | 125.0333 | 5020.8258
2016-07-24 | 11886.2925 | 0 | 11886.2925
2016-07-25 | 12863.6588 | 0 | 12863.6588
2016-07-26 | 12000.3852 | 70.2 | 12070.5852
2016-07-27 | 13140.4687 | 321.3 | 13461.7687
2016-07-28 | 13043.5318 | 2003.4333 | 15046.9651
2016-07-29 | 12054.3387 | 820.5 | 12874.8387
2016-07-30 | 10711.0856 | 2940.6898 | 13651.7754
2016-07-31 | 10318.2454 | 6428.1671 | 16746.4125
2016-08-01 | 2505.0774 | 0 | 2505.0774
2016-08-02 | 753.4746 | 0 | 753.4746
2016-08-03 | 863.9092 | 64.3639 | 928.2731
2016-08-04 | 5478.2467 | 0 | 5478.2467
2016-08-05 | 1897.7191 | 142.2 | 2039.9191
2016-08-06 | 823.1875 | 9727.3333 | 10550.5208
2016-08-07 | 666.6675 | 679.169 | 1345.8365
2016-08-08 | 726.2925 | 491.2451 | 1217.5376
2016-08-09 | 3056.0703 | 518.9976 | 3575.0679
2016-08-10 | 2318.9425 | 235.5339 | 2554.4764
2016-08-11 | 1178.9865 | 1538.1458 | 2717.1323
2016-08-12 | 12293.2013 | 695.7495 | 12988.9508
2016-08-13 | 2404.5842 | 1547.3833 | 3951.9675
2016-08-14 | 666.6675 | 12547.3852 | 13214.0527
2016-08-15 | 761.444 | 9888.7273 | 10650.1713
2016-08-16 | 666.6675 | 10927.4545 | 11594.122
2016-08-17 | 1755.066 | 3281.8344 | 5036.9004
2016-08-18 | 10204.5978 | 1066.6536 | 11271.2514
2016-08-19 | 1094.2967 | 715.9667 | 1810.2634
2016-08-20 | 725.1508 | 0 | 725.1508
2016-08-21 | 876.4307 | 934.0495 | 1810.4802
2016-08-22 | 3129.6978 | 9189.05 | 12318.7478
2016-08-23 | 666.6675 | 1876.5455 | 2543.213
2016-08-24 | 923.7535 | 1987.1682 | 2910.9217
2016-08-25 | 5714.8624 | 390.6963 | 6105.5587
2016-08-26 | 8776.4219 | 1011.5349 | 9787.9568
2016-08-27 | 8816.8654 | 2411.4778 | 11228.3432
2016-08-28 | 8802.6398 | 0 | 8802.6398
2016-08-29 | 13261.1563 | 0 | 13261.1563
2016-08-30 | 15051.8276 | 0 | 15051.8276
2016-08-31 | 7985.8675 | 904.4 | 8890.2675
2016-09-01 | 529.1267 | 13544.0159 | 14073.1425
2016-09-02 | 3064.0571 | 17026.7793 | 20090.8365
2016-09-03 | 3182.3446 | 6026.7349 | 9209.0795
2016-09-04 | 23.8017 | 1710.0671 | 1733.8688
2016-09-05 | 91.4017 | 0 | 91.4017
2016-09-06 | 499.8449 | 90.785 | 590.6298
2016-09-07 | 2043.8393 | 453.9544 | 2497.7937
2016-09-08 | 23.8017 | 368.9225 | 392.7242
2016-09-09 | 282.9282 | 799.6333 | 1082.5615
2016-09-10 | 48.3101 | 7971.6718 | 8019.9819
2016-09-11 | 7602.1451 | 4223.4479 | 11825.593
2016-09-12 | 1253.2295 | 0 | 1253.2295
2016-09-13 | 179.3065 | 674.5667 | 853.8731
2016-09-14 | 677.0267 | 989.3273 | 1666.3539
2016-09-15 | 23.8017 | 567.0841 | 590.8857
2016-09-16 | 2624.014 | 2744.7473 | 5368.7613
2016-09-17 | 11423.8017 | 8201.6667 | 19625.4683
2016-09-18 | 11423.8017 | 7272.6545 | 18696.4562
2016-09-19 | 11425.7683 | 2452.5742 | 13878.3426
2016-09-20 | 18364.6017 | 420.077 | 18784.6786
2016-09-21 | 26591.454 | 591.8691 | 27183.3232
2016-09-22 | 37179.1882 | 391.6993 | 37570.8875
2016-09-23 | 25234.4076 | 0 | 25234.4076
2016-09-24 | 6244.4947 | 756.1112 | 7000.606
2016-09-25 | 498.8017 | 4235.1662 | 4733.9678
2016-09-26 | 23.8017 | 2401.8385 | 2425.6402
2016-09-27 | 4779.4802 | 6869.6691 | 11649.1493
2016-09-28 | 23.8017 | 12233.2018 | 12257.0034
2016-09-29 | 23.8017 | 10352.7145 | 10376.5162
2016-09-30 | 23.8017 | 2007.9802 | 2031.7818
2016-10-01 | 23.8017 | 0 | 23.8017
2016-10-02 | 23.8017 | 2316.7338 | 2340.5354
2016-10-03 | 23.8017 | 7991.75 | 8015.5517
2016-10-04 | 23.8017 | 11312.75 | 11336.5517
2016-10-05 | 8675.8829 | 9864 | 18539.8829
2016-10-06 | 2700.8471 | 9864 | 12564.8471
2016-10-07 | 2219.1047 | 10092.2333 | 12311.338
2016-10-08 | 23.8017 | 17572.3098 | 17596.1115
2016-10-09 | 2540.3251 | 16977.4497 | 19517.7748
2016-10-10 | 1652.8906 | 16521.8182 | 18174.7088
2016-10-11 | 305.6808 | 13581.9364 | 13887.6172
2016-10-12 | 305.6808 | 10721.0182 | 11026.699
2016-10-13 | 750.7142 | 21552.5455 | 22303.2596
2016-10-14 | 305.6808 | 21288 | 21593.6808
2016-10-15 | 305.6808 | 13910 | 14215.6808
2016-10-16 | 363.0349 | 4524.4672 | 4887.5021
2016-10-17 | 675.4142 | 0 | 675.4142
2016-10-18 | 3463.462 | 0 | 3463.462
2016-10-19 | 1213.8899 | 0 | 1213.8899
2016-10-20 | 436.5899 | 1732.2333 | 2168.8233
2016-10-21 | 395.5872 | 1609.25 | 2004.8372
2016-10-22 | 7054.6975 | 252 | 7306.6975
2016-10-23 | 10117.8 | 2186.443 | 12304.2429
2016-10-24 | 11203.4699 | 1586.8167 | 12790.2866
2016-10-25 | 3928.6953 | 2832 | 6760.6953
2016-10-26 | 11295.4995 | 7429.8833 | 18725.3829
2016-10-27 | 10956.6698 | 16591.85 | 27548.5198
2016-10-28 | 5646.6829 | 11616 | 17262.6829
2016-10-29 | 1835.5543 | 1072.8667 | 2908.421
2016-10-30 | 12074.0698 | 2141.6555 | 14215.7253
2016-10-31 | 5237.8522 | 0 | 5237.8522
2016-11-01 | 7546.5594 | 0 | 7546.5594
2016-11-02 | 10108.9696 | 0 | 10108.9696
2016-11-03 | 15570.435 | 0 | 15570.435
2016-11-04 | 10059.6683 | 1691.3333 | 11751.0017
2016-11-05 | 9959.8017 | 2320.8054 | 12280.607
2016-11-06 | 9959.8017 | 0 | 9959.8017
2016-11-07 | 10641.435 | 129.9362 | 10771.3712
2016-11-08 | 9982.7067 | 556.8071 | 10539.5138
2016-11-09 | 10319.3834 | 350.4545 | 10669.8379
2016-11-10 | 9759.7017 | 0 | 9759.7017
2016-11-11 | 4884.1805 | 0 | 4884.1805
2016-11-12 | 1991.6105 | 393.3333 | 2384.9438
2016-11-13 | 56.0017 | 2653.172 | 2709.1737
2016-11-14 | 956.2683 | 0 | 956.2683
2016-11-15 | 1969.3517 | 105.2625 | 2074.6142
2016-11-16 | 510.885 | 4271.9048 | 4782.7898
2016-11-17 | 298.0204 | 3091.0521 | 3389.0725
2016-11-18 | 23.8017 | 4551.2612 | 4575.0629
2016-11-19 | 1057.3578 | 17869.9301 | 18927.2879
2016-11-20 | 23.8017 | 13792.846 | 13816.6477
2016-11-21 | 234.587 | 8305.0303 | 8539.6173
2016-11-22 | 319.1688 | 118.9871 | 438.156
2016-11-23 | 1036.9835 | 0 | 1036.9835
2016-11-24 | 23.8017 | 0 | 23.8017
2016-11-25 | 984.3523 | 0 | 984.3523
2016-11-26 | 3863.2489 | 2531.9221 | 6395.171
2016-11-27 | 259.4907 | 201.5141 | 461.0048
2016-11-28 | 1826.1605 | 409.4524 | 2235.6128
2016-11-29 | 10553.362 | 360.7273 | 10914.0893
2016-11-30 | 1782.5517 | 2950.2303 | 4732.782
2016-12-01 | 1572.2167 | 3241.5606 | 4813.7773
2016-12-02 | 2062.4911 | 428.1818 | 2490.6729
2016-12-03 | 2036.6732 | 0 | 2036.6732
2016-12-04 | 1783.4811 | 2417.57 | 4201.0511
2016-12-05 | 1387.2619 | 122.7273 | 1509.9892
2016-12-06 | 1392.1849 | 342.2727 | 1734.4576
2016-12-07 | 1545.0182 | 1377.6741 | 2922.6924
2016-12-08 | 3334.0216 | 297.4095 | 3631.4311
2016-12-09 | 8892.3545 | 565.3008 | 9457.6552
2016-12-10 | 1986.3525 | 6029.8748 | 8016.2273
2016-12-11 | 4059.6547 | 6188.0176 | 10247.6723
2016-12-12 | 2120.5664 | 8871.4217 | 10991.9882
2016-12-13 | 1811.4993 | 10029.1877 | 11840.687
2016-12-14 | 2196.7805 | 3636.7413 | 5833.5218
2016-12-15 | 2108.4213 | 0 | 2108.4213
2016-12-16 | 1878.7866 | 0 | 1878.7866
2016-12-17 | 1231.7901 | 507.5535 | 1739.3437
2016-12-18 | 2684.0273 | 1903.3258 | 4587.3531
2016-12-19 | 3426.0224 | 54.5455 | 3480.5678
2016-12-20 | 3615.0798 | 351.9185 | 3966.9982
2016-12-21 | 2361.4577 | 2116.7407 | 4478.1984
2016-12-22 | 3227.402 | 0 | 3227.402
2016-12-23 | 3579.8231 | 2410.8793 | 5990.7024
2016-12-24 | 2622.1731 | 0 | 2622.1731
2016-12-25 | 1318.4564 | 0 | 1318.4564
2016-12-26 | 2255.6933 | 0 | 2255.6933
2016-12-27 | 2274.2675 | 0 | 2274.2675
2016-12-28 | 3173.0019 | 650.6667 | 3823.6686
2016-12-29 | 4486.9065 | 0 | 4486.9065
2016-12-30 | 3473.419 | 5961.2714 | 9434.6904
2016-12-31 | 3173.0019 | 1112.7677 | 4285.7696
2017-01-01 | 3173.0019 | 0 | 3173.0019
2017-01-02 | 3374.47 | 0 | 3374.47
2017-01-03 | 6922.9429 | 1721.4 | 8644.3429
2017-01-04 | 7368.7553 | 996.4333 | 8365.1886
2017-01-05 | 7046.7673 | 0 | 7046.7673
2017-01-06 | 6821.1469 | 0 | 6821.1469
2017-01-07 | 2475.6766 | 0 | 2475.6766
2017-01-08 | 2922.3615 | 0 | 2922.3615
2017-01-09 | 2409.9948 | 4509.4946 | 6919.4894
2017-01-10 | 3995.1909 | 22091.3132 | 26086.5041
2017-01-11 | 12378.3791 | 10689.4667 | 23067.8458
2017-01-12 | 9467.4779 | 16850.9167 | 26318.3945
2017-01-13 | 7773.2205 | 14271.9333 | 22045.1538
2017-01-14 | 1811.7962 | 30072 | 31883.7962
2017-01-15 | 1559.2205 | 20907.7667 | 22466.9872
2017-01-16 | 1559.2205 | 29102.0045 | 30661.225
2017-01-17 | 2361.3992 | 28260.1773 | 30621.5765
2017-01-18 | 4962.6205 | 17771.3167 | 22733.9372
2017-01-19 | 12983.2205 | 23413 | 36396.2205
2017-01-20 | 13663.3594 | 24755.1848 | 38418.5442
2017-01-21 | 12983.2205 | 27672 | 40655.2205
2017-01-22 | 1590.9538 | 29405.2733 | 30996.2271
2017-01-23 | 1559.2205 | 19242.3207 | 20801.5412
2017-01-24 | 1559.2205 | 21405.6709 | 22964.8914
2017-01-25 | 1559.2205 | 27691.2727 | 29250.4932
2017-01-26 | 3617.0785 | 19672.947 | 23290.0255
2017-01-27 | 1974.9175 | 21831.3818 | 23806.2993
2017-01-28 | 2323.3872 | 28323.5535 | 30646.9407
2017-01-29 | 1559.2205 | 23682.0591 | 25241.2796
2017-01-30 | 1578.0245 | 16473.8182 | 18051.8427
2017-01-31 | 1668.5532 | 16842 | 18510.5532
2017-02-01 | 1775.4004 | 17431.1453 | 19206.5457
2017-02-02 | 3161.2705 | 21962.4194 | 25123.6899
2017-02-03 | 2197.4363 | 20689.4941 | 22886.9304
2017-02-04 | 1559.2205 | 18129.5535 | 19688.774
2017-02-05 | 1559.2205 | 18889.5034 | 20448.7239
2017-02-06 | 3460.2372 | 6162.1578 | 9622.395
2017-02-07 | 13006.3775 | 0 | 13006.3775
2017-02-08 | 17734.8038 | 0 | 17734.8038
2017-02-09 | 8994.7858 | 0 | 8994.7858
2017-02-10 | 1559.2205 | 0 | 1559.2205
2017-02-11 | 1559.2205 | 5276.175 | 6835.3955
2017-02-12 | 13604.6893 | 2959.6667 | 16564.356
2017-02-13 | 12832.0846 | 0 | 12832.0846
2017-02-14 | 25800.4122 | 0 | 25800.4122
2017-02-15 | 21044.7205 | 10586.5 | 31631.2205
2017-02-16 | 15329.6675 | 16392 | 31721.6675
2017-02-17 | 3623.5205 | 16430.6692 | 20054.1897
2017-02-18 | 1559.2205 | 22436.0232 | 23995.2437
2017-02-19 | 1651.7942 | 18450.3333 | 20102.1275
2017-02-20 | 1597.2519 | 19248 | 20845.2519
2017-02-21 | 3574.7372 | 18055.2 | 21629.9372
2017-02-22 | 16936.1205 | 16439.7273 | 33375.8478
2017-02-23 | 15552.1427 | 17738.3864 | 33290.5291
2017-02-24 | 15754.5235 | 17540.5212 | 33295.0447
2017-02-25 | 20256.9028 | 16392 | 36648.9028
2017-02-26 | 14105.9902 | 16392 | 30497.9902
2017-02-27 | 6058.576 | 16392 | 22450.576
2017-02-28 | 6793.1968 | 17092 | 23885.1968
2017-03-01 | 796.5206 | 23592 | 24388.5206
2017-03-02 | 1908.0415 | 23592 | 25500.0415
2017-03-03 | 1896.2415 | 22272 | 24168.2415
2017-03-04 | 922.7415 | 22758.6 | 23681.3415
2017-03-05 | 456.6415 | 21576.7216 | 22033.3632
2017-03-06 | 1040.5688 | 16534.567 | 17575.1358
2017-03-07 | 536.4751 | 16503.3667 | 17039.8418
2017-03-08 | 6744.5987 | 16392 | 23136.5987
2017-03-09 | 3429.632 | 11075.2072 | 14504.8392
2017-03-10 | 565.8987 | 0 | 565.8987
2017-03-11 | 1067.9508 | 0 | 1067.9508
2017-03-12 | 565.8987 | 0 | 565.8987
2017-03-13 | 565.8987 | 174.9233 | 740.822
2017-03-14 | 703.9153 | 1204.5857 | 1908.501
2017-03-15 | 565.8987 | 0 | 565.8987
2017-03-16 | 650.7316 | 4783.7901 | 5434.5217
2017-03-17 | 623.6531 | 18400.854 | 19024.5071
2017-03-18 | 1525.4077 | 24493 | 26018.4077
2017-03-19 | 1524.1546 | 13128.4833 | 14652.638
2017-03-20 | 3258.2085 | 0 | 3258.2085
2017-03-21 | 631.2675 | 1296.2333 | 1927.5008
2017-03-22 | 682.89 | 1093.7667 | 1776.6566
2017-03-23 | 891.8431 | 293.1818 | 1185.0249
2017-03-24 | 4258.3125 | 455.4545 | 4713.767
2017-03-25 | 825.56 | 7974.3333 | 8799.8933
2017-03-26 | 664.4274 | 11568 | 12232.4274
2017-03-27 | 565.8987 | 2949.8667 | 3515.7653
2017-03-28 | 565.8987 | 216.8833 | 782.782
2017-03-29 | 692.15 | 71.5 | 763.65
2017-03-30 | 5219.2273 | 0 | 5219.2273
2017-03-31 | 12367.241 | 0 | 12367.241
2017-04-01 | 12133.8987 | 0 | 12133.8987
2017-04-02 | 5695.0509 | 0 | 5695.0509
2017-04-03 | 565.8987 | 914.3616 | 1480.2603
2017-04-04 | 565.8987 | 11344.9167 | 11910.8153
2017-04-05 | 565.8987 | 96.7381 | 662.6368
2017-04-06 | 565.8987 | 7.739 | 573.6377
2017-04-07 | 4239.8376 | 1001.9318 | 5241.7694
2017-04-08 | 3250.192 | 8339.7793 | 11589.9713
2017-04-09 | 1888.193 | 8339.7793 | 10227.9723
2017-04-10 | 754.0546 | 8385.6447 | 9139.6993
2017-04-11 | 925.0935 | 8800.7781 | 9725.8716
2017-04-12 | 598.5956 | 6780.4505 | 7379.046
2017-04-13 | 8734.647 | 0 | 8734.647
2017-04-14 | 3323.847 | 0 | 3323.847
2017-04-15 | 5692.547 | 0 | 5692.547
2017-04-16 | 14633.4804 | 192 | 14825.4804
2017-04-17 | 22453.7137 | 384 | 22837.7137
2017-04-18 | 18305.9225 | 384 | 18689.9225
2017-04-19 | 5819.0926 | 384 | 6203.0926
2017-04-20 | 3029.3282 | 297.8709 | 3327.1992
2017-04-21 | 2052.147 | 4192.3362 | 6244.4832
2017-04-22 | 880.5926 | 4108.2953 | 4988.8879
2017-04-23 | 238.1272 | 6149.062 | 6387.1892
2017-04-24 | 238.1272 | 2479.6447 | 2717.7719
2017-04-25 | 866.8133 | 0 | 866.8133
2017-04-26 | 3636.7757 | 0 | 3636.7757
2017-04-27 | 16006.4439 | 0 | 16006.4439
2017-04-28 | 22558.1272 | 36.6923 | 22594.8195
2017-04-29 | 25494.9421 | 136.0673 | 25631.0094
2017-04-30 | 18297.8975 | 77.1135 | 18375.0109
2017-05-01 | 14762.1921 | 1116.9054 | 15879.0976
2017-05-02 | 14179.4151 | 1146.6258 | 15326.0409
2017-05-03 | 20584.8106 | 7831.5667 | 28416.3772
2017-05-04 | 10344.6729 | 564.1324 | 10908.8053
2017-05-05 | 672.0666 | 3719.0689 | 4391.1356
2017-05-06 | 238.1272 | 15674.446 | 15912.5733
2017-05-07 | 238.1272 | 8514.4127 | 8752.5399
2017-05-08 | 856.6939 | 12144.746 | 13001.4399
2017-05-09 | 422.9872 | 13441.6999 | 13864.6871
2017-05-10 | 1180.8601 | 15532.148 | 16713.0081
2017-05-11 | 791.1251 | 14188.312 | 14979.4371
2017-05-12 | 1027.3179 | 17550.657 | 18577.9749
2017-05-13 | 238.1272 | 26511.567 | 26749.6942
2017-05-14 | 805.556 | 9588.3899 | 10393.9459
2017-05-15 | 297.8223 | 8804.4853 | 9102.3076
2017-05-16 | 576.3939 | 8339.7793 | 8916.1733
2017-05-17 | 262.012 | 8339.7793 | 8601.7914
2017-05-18 | 374.5714 | 6658.1627 | 7032.7341
2017-05-19 | 4209.4794 | 705.5667 | 4915.0461
2017-05-20 | 7380.6486 | 3706.7 | 11087.3486
2017-05-21 | 8479.4509 | 20139.953 | 28619.4039
2017-05-22 | 7586.7454 | 11537.1333 | 19123.8788
2017-05-23 | 489.7044 | 17069.65 | 17559.3544
2017-05-24 | 238.1272 | 16712.2437 | 16950.371
2017-05-25 | 960.2772 | 16658.8122 | 17619.0894
2017-05-26 | 238.1272 | 16656 | 16894.1272
2017-05-27 | 2473.2088 | 6165.0333 | 8638.2421
2017-05-28 | 238.1272 | 2442.953 | 2681.0803
2017-05-29 | 238.1272 | 0 | 238.1272
2017-05-30 | 778.7782 | 0 | 778.7782
2017-05-31 | 9453.8714 | 3767.9426 | 13221.814
2017-06-01 | 14686.8518 | 2721.6968 | 17408.5486
2017-06-02 | 16531.4707 | 0 | 16531.4707
2017-06-03 | 16453.4208 | 0 | 16453.4208
2017-06-04 | 7567.2208 | 67.1538 | 7634.3746
2017-06-05 | 14504.6158 | 188.0308 | 14692.6466
2017-06-06 | 14021.5708 | 1575.4602 | 15597.031
2017-06-07 | 14155.9708 | 8031.5862 | 22187.557
2017-06-08 | 12529.6833 | 665.9144 | 13195.5977
2017-06-09 | 1694.845 | 5124.5 | 6819.345
2017-06-10 | 1642.0201 | 18178.5333 | 19820.5535
2017-06-11 | 1821.2918 | 11739.5 | 13560.7918
2017-06-12 | 3505.0116 | 0 | 3505.0116
2017-06-13 | 3602.5732 | 75.6 | 3678.1732
2017-06-14 | 10774.2909 | 472.0584 | 11246.3493
2017-06-15 | 20743.6575 | 72.7273 | 20816.3848
2017-06-16 | 20476.6159 | 666.6276 | 21143.2434
2017-06-17 | 19996.5212 | 1459.1405 | 21455.6617
2017-06-18 | 8981.3684 | 2335.1237 | 11316.4921
2017-06-19 | 4354.7275 | 11115.9348 | 15470.6623
2017-06-20 | 1387.8887 | 16669.8091 | 18057.6977
2017-06-21 | 2313.3746 | 16308 | 18621.3746
2017-06-22 | 3228.2737 | 11144.0696 | 14372.3432
2017-06-23 | 8484.5257 | 644.538 | 9129.0637
2017-06-24 | 1451.3911 | 3203.85 | 4655.2411
2017-06-25 | 2287.461 | 6800.6237 | 9088.0847
2017-06-26 | 1505.4286 | 9301.2 | 10806.6286
2017-06-27 | 7076.3801 | 8875.6333 | 15952.0135
2017-06-28 | 8722.3964 | 831.7167 | 9554.113
2017-06-29 | 5190.0167 | 475.9333 | 5665.95
2017-06-30 | 2462.9668 | 0 | 2462.9668
2017-07-01 | 975.6773 | 0 | 975.6773
2017-07-02 | 5092.3381 | 1654.046 | 6746.384
2017-07-03 | 3192.0252 | 969.9 | 4161.9252
2017-07-04 | 2080.7852 | 0 | 2080.7852
2017-07-05 | 2168.1047 | 107.1 | 2275.2047
2017-07-06 | 1237.5141 | 157.7945 | 1395.3086
2017-07-07 | 1485.259 | 1406.6725 | 2891.9315
2017-07-08 | 1464.9043 | 11400 | 12864.9043
2017-07-09 | 1316.6622 | 13735.1237 | 15051.7859
2017-07-10 | 1552.21 | 4116.6667 | 5668.8767
2017-07-11 | 2561.8953 | 85.2417 | 2647.137
2017-07-12 | 2591.4174 | 510.7708 | 3102.1882
2017-07-13 | 9097.5669 | 269.3453 | 9366.9122
2017-07-14 | 9490.2969 | 139.3297 | 9629.6266
2017-07-15 | 5671.0923 | 132.3632 | 5803.4555
2017-07-16 | 13000.0437 | 2401.8346 | 15401.8784
2017-07-17 | 11111.9437 | 500.3318 | 11612.2755
2017-07-18 | 1375.6437 | 276.8502 | 1652.494
2017-07-19 | 1290.3937 | 106.8 | 1397.1937
2017-07-20 | 2460.0771 | 0 | 2460.0771
2017-07-21 | 1374.5037 | 0 | 1374.5037
2017-07-22 | 1416.9549 | 233.5124 | 1650.4673
2017-07-23 | 1327.1683 | 2839.8895 | 4167.0578
2017-07-24 | 2693.7245 | 572.8514 | 3266.5759
2017-07-25 | 11616.0687 | 572.0577 | 12188.1264
2017-07-26 | 9530.9371 | 546.5683 | 10077.5054
2017-07-27 | 1271.1755 | 684.1792 | 1955.3547
2017-07-28 | 2047.0437 | 8985.981 | 11033.0248
2017-07-29 | 1234.2687 | 6237.1146 | 7471.3834
2017-07-30 | 13911.2937 | 144 | 14055.2937
2017-07-31 | 14357.1387 | 662.9 | 15020.0387
2017-08-01 | 14066.5887 | 528.3667 | 14594.9554
2017-08-02 | 14104.0437 | 0 | 14104.0437
2017-08-03 | 11470.6794 | 0 | 11470.6794
2017-08-04 | 2219.9738 | 2522.3431 | 4742.3168
2017-08-05 | 928.0437 | 12666.1363 | 13594.1801
2017-08-06 | 928.0437 | 9816 | 10744.0437
2017-08-07 | 928.0437 | 8184.5181 | 9112.5619
2017-08-08 | 1067.7687 | 815.0702 | 1882.839
2017-08-09 | 2704.682 | 2250.3162 | 4954.9982
2017-08-10 | 1198.0181 | 747.0646 | 1945.0827
2017-08-11 | 928.0437 | 327.2727 | 1255.3165
2017-08-12 | 928.0437 | 0 | 928.0437
2017-08-13 | 928.0437 | 2429.6308 | 3357.6746
2017-08-14 | 3729.6937 | 235.6249 | 3965.3186
2017-08-15 | 1386.9059 | 644.3745 | 2031.2804
2017-08-16 | 1115.3034 | 565.4367 | 1680.74
2017-08-17 | 1544.6415 | 354.5743 | 1899.2158
2017-08-18 | 3505.3109 | 391.7233 | 3897.0343
2017-08-19 | 1475.4109 | 0 | 1475.4109
2017-08-20 | 1681.6293 | 2335.1237 | 4016.7531
2017-08-21 | 3197.4525 | 0 | 3197.4525
2017-08-22 | 5153.4597 | 179.141 | 5332.6007
2017-08-23 | 1030.5144 | 258.3419 | 1288.8564
2017-08-24 | 1017.1494 | 925.7895 | 1942.9389
2017-08-25 | 1018.6344 | 372.0021 | 1390.6365
2017-08-26 | 1036.9494 | 4227.5833 | 5264.5327
2017-08-27 | 1036.9494 | 2498.7601 | 3535.7095
2017-08-28 | 1383.3994 | 369.5455 | 1752.9449
2017-08-29 | 2446.4677 | 4919.9052 | 7366.3729
2017-08-30 | 1025.5644 | 4257.5156 | 5283.08
2017-08-31 | 993.3894 | 4956.8222 | 5950.2116
2017-09-01 | 892.335 | 12176.2835 | 13068.6184
2017-09-02 | 826.4017 | 4056 | 4882.4017
2017-09-03 | 261.4017 | 6498.953 | 6760.3547
2017-09-04 | 261.4017 | 1475.9333 | 1737.335
2017-09-05 | 5289.2167 | 1926 | 7215.2167
2017-09-06 | 10124.6017 | 1299.6197 | 11424.2213
2017-09-07 | 6932.3635 | 560.5792 | 7492.9426
2017-09-08 | 9039.2973 | 0 | 9039.2973
2017-09-09 | 260.6017 | 4006.8 | 4267.4017
2017-09-10 | 342.4249 | 2430.2215 | 2772.6464
2017-09-11 | 260.6017 | 0 | 260.6017
2017-09-12 | 865.6676 | 2665.0592 | 3530.7268
2017-09-13 | 283.378 | 3817.1213 | 4100.4994
2017-09-14 | 1239.0183 | 1507.2 | 2746.2183
2017-09-15 | 613.4374 | 1597.8667 | 2211.304
2017-09-16 | 239.0744 | 0 | 239.0744
2017-09-17 | 239.0744 | 2442.953 | 2682.0274
2017-09-18 | 248.6198 | 411.9504 | 660.5702
2017-09-19 | 586.421 | 75 | 661.421
2017-09-20 | 477.7392 | 0 | 477.7392
2017-09-21 | 891.5039 | 0 | 891.5039
2017-09-22 | 431.2425 | 114.3975 | 545.64
2017-09-23 | 7883.0744 | 0 | 7883.0744
2017-09-24 | 1053.0148 | 182.0993 | 1235.1141
2017-09-25 | 2354.7908 | 1156.8067 | 3511.5975
2017-09-26 | 785.9077 | 1378.6746 | 2164.5823
2017-09-27 | 6914.0177 | 14.0654 | 6928.0831
2017-09-28 | 11903.0744 | 0 | 11903.0744
2017-09-29 | 895.1744 | 6369.7279 | 7264.9023
2017-09-30 | 239.0744 | 9134.6985 | 9373.7729
2017-10-01 | 259.4212 | 2896.5754 | 3155.9965
2017-10-02 | 239.0744 | 0 | 239.0744
2017-10-03 | 1696.9513 | 0 | 1696.9513
2017-10-04 | 239.0744 | 0 | 239.0744
2017-10-05 | 239.0744 | 0 | 239.0744
2017-10-06 | 239.0744 | 0 | 239.0744
2017-10-07 | 239.0744 | 684.45 | 923.5244
2017-10-08 | 239.0744 | 2534.5638 | 2773.6381
2017-10-09 | 1069.8726 | 150.4043 | 1220.2768
2017-10-10 | 1032.693 | 1048.0898 | 2080.7828
2017-10-11 | 7563.2182 | 1227.7496 | 8790.9678
2017-10-12 | 1774.8616 | 2913.1021 | 4687.9637
2017-10-13 | 239.0744 | 384 | 623.0744
2017-10-14 | 624.879 | 384 | 1008.879
2017-10-15 | 239.0744 | 2918.5638 | 3157.6381
2017-10-16 | 239.0744 | 887.634 | 1126.7084
2017-10-17 | 1002.391 | 1585.228 | 2587.619
2017-10-18 | 763.7744 | 959.7576 | 1723.532
2017-10-19 | 14741.3744 | 811.8788 | 15553.2532
2017-10-20 | 4295.0744 | 2134.553 | 6429.6274
2017-10-21 | 4295.0744 | 384 | 4679.0744
2017-10-22 | 4409.1297 | 2804.5084 | 7213.6381
2017-10-23 | 4508.6874 | 511.8182 | 5020.5055
2017-10-24 | 4261.2885 | 688.0727 | 4949.3612
2017-10-25 | 7346.0244 | 384 | 7730.0244
2017-10-26 | 4999.3846 | 384 | 5383.3846
2017-10-27 | 152.9653 | 2252.3 | 2405.2653
2017-10-28 | 152.9653 | 384 | 536.9653
2017-10-29 | 704.9954 | 2897.4424 | 3602.4378
2017-10-30 | 1063.9538 | 384 | 1447.9538
2017-10-31 | 152.9653 | 384 | 536.9653
2017-11-01 | 865.9569 | 384 | 1249.9569
2017-11-02 | 152.9653 | 384 | 536.9653
2017-11-03 | 214.932 | 5931.5 | 6146.432
2017-11-04 | 152.9653 | 20158.953 | 20311.9183
2017-11-05 | 171.5468 | 17937.5439 | 18109.0908
2017-11-06 | 1592.2039 | 17371.0606 | 18963.2645
2017-11-07 | 1140.932 | 16796 | 17936.932
2017-11-08 | 152.9653 | 16656 | 16808.9653
2017-11-09 | 152.9653 | 16656 | 16808.9653
2017-11-10 | 344.7997 | 16656 | 17000.7997
2017-11-11 | 1651.4653 | 17144.5906 | 18796.0559
2017-11-12 | 12121.1678 | 18219.4899 | 30340.6577
2017-11-13 | 1468.5922 | 16656 | 18124.5922
2017-11-14 | 670.5793 | 16656 | 17326.5793
2017-11-15 | 12017.6598 | 16656 | 28673.6598
2017-11-16 | 919.7076 | 18557.25 | 19476.9576
2017-11-17 | 441.1636 | 12398.7141 | 12839.8777
2017-11-18 | 3532.2303 | 4782.3974 | 8314.6277
2017-11-19 | 19501.9993 | 0 | 19501.9993
2017-11-20 | 28620.7666 | 0 | 28620.7666
2017-11-21 | 18458.2673 | 91.0496 | 18549.3169
2017-11-22 | 13915.0911 | 1397.2816 | 15312.3727
2017-11-23 | 587.2773 | 6765 | 7352.2773
2017-11-24 | 441.1636 | 7200 | 7641.1636
2017-11-25 | 5908.4136 | 7200 | 13108.4136
2017-11-26 | 433.8435 | 9103.6197 | 9537.4632
2017-11-27 | 2156.7608 | 0 | 2156.7608
2017-11-28 | 3306.5309 | 4499.7667 | 7806.2976
2017-11-29 | 18271.597 | 3428.1667 | 21699.7636
2017-11-30 | 11598.8636 | 1326.65 | 12925.5136
2017-12-01 | 12926.9407 | 543.6523 | 13470.593
2017-12-02 | 9890.0979 | 998.3552 | 10888.4531
2017-12-03 | 8386.2342 | 6943.0967 | 15329.3309
2017-12-04 | 976.7539 | 4731.7599 | 5708.5139
2017-12-05 | 1409.1007 | 3718.0682 | 5127.1689
2017-12-06 | 2430.0956 | 564.9697 | 2995.0653
2017-12-07 | 3684.7228 | 664.8141 | 4349.5369
2017-12-08 | 1302.8873 | 221.6717 | 1524.559
2017-12-09 | 1191.8498 | 3548.4911 | 4740.3409
2017-12-10 | 14659.1876 | 0 | 14659.1876
2017-12-11 | 14918.8706 | 0 | 14918.8706
2017-12-12 | 16239.9833 | 0 | 16239.9833
2017-12-13 | 9200.3824 | 259.0909 | 9459.4733
2017-12-14 | 1942.4124 | 809.3515 | 2751.764
2017-12-15 | 2057.2106 | 1109.5424 | 3166.7531
2017-12-16 | 1827.6143 | 3159.7491 | 4987.3634
2017-12-17 | 2468.6611 | 0 | 2468.6611
2017-12-18 | 2025.5328 | 336.8846 | 2362.4174
2017-12-19 | 1471.7881 | 433.1309 | 1904.919
2017-12-20 | 1186.7353 | 10998.6688 | 12185.4041
2017-12-21 | 1287.429 | 13923.5255 | 15210.9545
2017-12-22 | 1138.8251 | 8181.0169 | 9319.8421
2017-12-23 | 1138.8251 | 0 | 1138.8251
2017-12-24 | 1138.8251 | 0 | 1138.8251
2017-12-25 | 2735.8101 | 0 | 2735.8101
2017-12-26 | 6423.357 | 0 | 6423.357
2017-12-27 | 20700.3918 | 435.5667 | 21135.9585
2017-12-28 | 18538.0085 | 0 | 18538.0085
2017-12-29 | 16250.7862 | 0 | 16250.7862
2017-12-30 | 17929.6407 | 0 | 17929.6407
2017-12-31 | 20445.9193 | 0 | 20445.9193
2018-01-01 | 13002.3184 | 0 | 13002.3184
2018-01-02 | 8397.8085 | 0 | 8397.8085
2018-01-03 | 9717.4018 | 86.6241 | 9804.0259
2018-01-04 | 11175.3873 | 228.1102 | 11403.4975
2018-01-05 | 9579.9155 | 2565.7846 | 12145.7002
2018-01-06 | 3242.6851 | 2164.2095 | 5406.8946
2018-01-07 | 3242.6851 | 4034.3832 | 7277.0683
2018-01-08 | 3567.6851 | 2938.0594 | 6505.7445
2018-01-09 | 3329.3092 | 10474.1878 | 13803.497
2018-01-10 | 3595.1317 | 10421.2144 | 14016.3461
2018-01-11 | 6407.6789 | 6659.698 | 13067.3769
2018-01-12 | 12569.8751 | 384.0336 | 12953.9087
2018-01-13 | 16682.2918 | 2537.7677 | 19220.0595
2018-01-14 | 13319.4251 | 0 | 13319.4251
2018-01-15 | 9502.5421 | 0 | 9502.5421
2018-01-16 | 3668.1237 | 0 | 3668.1237
2018-01-17 | 1920.8185 | 0 | 1920.8185
2018-01-18 | 5754.8002 | 0 | 5754.8002
2018-01-19 | 11917.2251 | 2183.1 | 14100.3251
2018-01-20 | 4707.9659 | 23377.3937 | 28085.3596
2018-01-21 | 4594.8251 | 27461.6014 | 32056.4266
2018-01-22 | 4869.4678 | 20880.7451 | 25750.2129
2018-01-23 | 5048.6405 | 6850.7994 | 11899.4399
2018-01-24 | 4676.1605 | 14285.1256 | 18961.2861
2018-01-25 | 6298.3258 | 6724.5057 | 13022.8315
2018-01-26 | 5016.3001 | 8699.1035 | 13715.4036
2018-01-27 | 6057.5091 | 0 | 6057.5091
2018-01-28 | 4782.5758 | 1906.3736 | 6688.9494
2018-01-29 | 4917.2267 | 594.7256 | 5511.9523
2018-01-30 | 4408.8732 | 608.1776 | 5017.0508
2018-01-31 | 4788.6102 | 5735.2073 | 10523.8175
2018-02-01 | 5140.7085 | 9912 | 15052.7085
2018-02-02 | 5505.4028 | 998.0833 | 6503.4862
2018-02-03 | 1138.8251 | 3613.6667 | 4752.4918
2018-02-04 | 1138.8251 | 2537.7677 | 3676.5928
2018-02-05 | 1196.9471 | 551.6 | 1748.5471
2018-02-06 | 1174.2741 | 9972.6883 | 11146.9624
2018-02-07 | 4932.0728 | 923.3608 | 5855.4336
2018-02-08 | 3191.2808 | 356.4 | 3547.6808
2018-02-09 | 3876.5168 | 11664 | 15540.5168
2018-02-10 | 8099.7335 | 12425.3303 | 20525.0638
2018-02-11 | 1138.8251 | 10815.9677 | 11954.7928
2018-02-12 | 1136.1433 | 707.4136 | 1843.557
2018-02-13 | 1099.8494 | 499.2515 | 1599.1009
2018-02-14 | 1489.7085 | 0 | 1489.7085
2018-02-15 | 1931.5418 | 672.6005 | 2604.1423
2018-02-16 | 1522.8251 | 9215.7576 | 10738.5828
2018-02-17 | 1522.8251 | 9387.5535 | 10910.3787
2018-02-18 | 1711.6174 | 8880 | 10591.6174
2018-02-19 | 6295.5271 | 7199 | 13494.5271
2018-02-20 | 15536.4649 | 1449.9 | 16986.3649
2018-02-21 | 12278.3812 | 2924.1 | 15202.4812
2018-02-22 | 6206.8882 | 442.8854 | 6649.7736
2018-02-23 | 2193.7388 | 0 | 2193.7388
2018-02-24 | 13769.4349 | 8882.4833 | 22651.9183
2018-02-25 | 15918.2626 | 6169.7667 | 22088.0293
2018-02-26 | 15209.4923 | 0 | 15209.4923
2018-02-27 | 4670.9578 | 5783.4 | 10454.3578
2018-02-28 | 5432.4401 | 0 | 5432.4401
2018-03-01 | 3001.4528 | 164.5487 | 3166.0015
2018-03-02 | 4407.7087 | 581.4475 | 4989.1561
2018-03-03 | 8408.2757 | 11568 | 19976.2757
2018-03-04 | 2662.7182 | 11568 | 14230.7182
2018-03-05 | 4500.2667 | 11568 | 16068.2667
2018-03-06 | 3522.3273 | 11777.9508 | 15300.2781
2018-03-07 | 10569.4273 | 1429.3 | 11998.7273
2018-03-08 | 3522.3273 | 0 | 3522.3273
2018-03-09 | 5171.9042 | 0 | 5171.9042
2018-03-10 | 5502.2682 | 0 | 5502.2682
2018-03-11 | 5448 | 0 | 5448
2018-03-12 | 16559.1833 | 0 | 16559.1833
2018-03-13 | 10415.0038 | 0 | 10415.0038
2018-03-14 | 6240.6912 | 0 | 6240.6912
2018-03-15 | 4632.1579 | 0 | 4632.1579
2018-03-16 | 4963.3614 | 0 | 4963.3614
2018-03-17 | 4632.1579 | 0 | 4632.1579
2018-03-18 | 4632.1579 | 0 | 4632.1579
2018-03-19 | 4730.2925 | 98.163 | 4828.4555
2018-03-20 | 4632.1579 | 0 | 4632.1579
2018-03-21 | 4632.1579 | 0 | 4632.1579
2018-03-22 | 4632.1579 | 0 | 4632.1579
2018-03-23 | 3585.4579 | 0 | 3585.4579
2018-03-24 | 1752.1579 | 0 | 1752.1579
2018-03-25 | 1788.4359 | 0 | 1788.4359
2018-03-26 | 3448.8768 | 0 | 3448.8768
2018-03-27 | 1752.1579 | 641.1333 | 2393.2912
2018-03-28 | 3556.3818 | 0 | 3556.3818
2018-03-29 | 1752.1579 | 0 | 1752.1579
2018-03-30 | 1775.5233 | 0 | 1775.5233
2018-03-31 | 2050.6331 | 0 | 2050.6331
2018-04-01 | 1752.1579 | 0 | 1752.1579
2018-04-02 | 2000.6427 | 104.2424 | 2104.8852
2018-04-03 | 1752.1579 | 113.9394 | 1866.0973
2018-04-04 | 1752.1579 | 0 | 1752.1579
2018-04-05 | 2708.7644 | 0 | 2708.7644
2018-04-06 | 1752.1579 | 0 | 1752.1579
2018-04-07 | 1752.1579 | 0 | 1752.1579
2018-04-08 | 1752.1579 | 0 | 1752.1579
2018-04-09 | 1752.1579 | 0 | 1752.1579
2018-04-10 | 1960.9079 | 0 | 1960.9079
2018-04-11 | 3115.1579 | 218.1818 | 3333.3397
2018-04-12 | 4390.2841 | 367.2727 | 4757.5568
2018-04-13 | 1912.1579 | 200 | 2112.1579
2018-04-14 | 93.6918 | 360 | 453.6918
2018-04-15 | 0 | 360 | 360
2018-04-16 | 0 | 360 | 360
2018-04-17 | 326.7333 | 590.5333 | 917.2667
2018-04-18 | 0 | 360 | 360
2018-04-19 | 213.0923 | 415.0385 | 628.1308
2018-04-20 | 109.35 | 855.2973 | 964.6473
2018-04-21 | 0 | 2689.6321 | 2689.6321
2018-04-22 | 328.9846 | 2539.0667 | 2868.0513
2018-04-23 | 1501.9667 | 3192 | 4693.9667
2018-04-24 | 0 | 3190.0333 | 3190.0333
2018-04-25 | 215.8 | 3190.0333 | 3405.8333
2018-04-26 | 312 | 3401.6661 | 3713.6661
2018-04-27 | 312 | 3745.3502 | 4057.3502
2018-04-28 | 312 | 3014.7273 | 3326.7273
2018-04-29 | 1931.41 | 2552.0121 | 4483.4221
2018-04-30 | 312 | 79.0909 | 391.0909
2018-05-01 | 2592.7764 | 56.0769 | 2648.8533
2018-05-02 | 9487.5254 | 210.2885 | 9697.8139
2018-05-03 | 13713.3804 | 0 | 13713.3804
2018-05-04 | 2969.1892 | 8725.8333 | 11695.0225
2018-05-05 | 312 | 9395 | 9707
2018-05-06 | 4918.7353 | 6578.6667 | 11497.4019
2018-05-07 | 1450.3933 | 2774.6167 | 4225.0099
2018-05-08 | 2091.4595 | 4275.3833 | 6366.8429
2018-05-09 | 2600.0014 | 9097.7 | 11697.7014
2018-05-10 | 2807.106 | 2832 | 5639.106
2018-05-11 | 2563.0683 | 3512 | 6075.0683
2018-05-12 | 2424.1579 | 10032 | 12456.1579
2018-05-13 | 5933.4912 | 12284 | 18217.4912
2018-05-14 | 3951.1482 | 16272 | 20223.1482
2018-05-15 | 6868.2699 | 16272 | 23140.2699
2018-05-16 | 2112.1579 | 17011.0667 | 19123.2246
2018-05-17 | 3810.6496 | 27840 | 31650.6496
2018-05-18 | 4839.5429 | 27840 | 32679.5429
2018-05-19 | 4839.5429 | 21759.6861 | 26599.2289
2018-05-20 | 2669.4976 | 27840 | 30509.4976
2018-05-21 | 4060.7771 | 16595.9162 | 20656.6932
2018-05-22 | 389.8544 | 17025.6081 | 17415.4625
2018-05-23 | 2259.7 | 16948.0439 | 19207.7439
2018-05-24 | 466.205 | 13831.0724 | 14297.2774
2018-05-25 | 1399.0443 | 1864.3567 | 3263.401
2018-05-26 | 7738.331 | 0 | 7738.331
2018-05-27 | 7481.9237 | 0 | 7481.9237
2018-05-28 | 6264.9617 | 0 | 6264.9617
2018-05-29 | 2793.2074 | 0 | 2793.2074
2018-05-30 | 4565.5228 | 0 | 4565.5228
2018-05-31 | 489.7895 | 971.1 | 1460.8895
2018-06-01 | 903.3593 | 1960.1432 | 2863.5025
2018-06-02 | 809.8489 | 8503.8114 | 9313.6603
2018-06-03 | 1179.3321 | 9590.8469 | 10770.179
2018-06-04 | 3581.6292 | 8119.4053 | 11701.0345
2018-06-05 | 3575.2187 | 8666.1538 | 12241.3725
2018-06-06 | 3303.906 | 10347.7781 | 13651.6841
2018-06-07 | 3230.6028 | 9353.7817 | 12584.3845
2018-06-08 | 1523.6816 | 8251.678 | 9775.3596
2018-06-09 | 1807.0331 | 10865.4689 | 12672.502
2018-06-10 | 3681.2391 | 9874.4622 | 13555.7014
2018-06-11 | 3894.2042 | 8507.7689 | 12401.9731
2018-06-12 | 3341.7066 | 13508.574 | 16850.2806
2018-06-13 | 7890.6037 | 8643.0595 | 16533.6632
2018-06-14 | 12609.4573 | 8663.0963 | 21272.5536
2018-06-15 | 2618.8155 | 8290.9689 | 10909.7844
2018-06-16 | 2208.83 | 7955.7689 | 10164.5989
2018-06-17 | 5775.0727 | 8117.7689 | 13892.8416
2018-06-18 | 4111.8689 | 7050.8826 | 11162.7515
2018-06-19 | 3625.0747 | 414.45 | 4039.5247
2018-06-20 | 3125.4482 | 445.0196 | 3570.4678
2018-06-21 | 1993.2325 | 12969.2099 | 14962.4424
2018-06-22 | 1601.7925 | 23220.3504 | 24822.1429
2018-06-23 | 1591.1258 | 31848 | 33439.1258
2018-06-24 | 1591.1258 | 30836.2333 | 32427.3591
2018-06-25 | 1591.1258 | 5738.1072 | 7329.233
2018-06-26 | 1591.1258 | 538.6819 | 2129.8077
2018-06-27 | 1591.1258 | 8119.4053 | 9710.531
2018-06-28 | 1777.944 | 8313.5871 | 10091.531
2018-06-29 | 2314.5758 | 8221.7189 | 10536.2947
2018-06-30 | 3716.3138 | 7955.7689 | 11672.0827
2018-07-01 | 3806.684 | 10288.5505 | 14095.2344
2018-07-02 | 3804.4448 | 7955.7689 | 11760.2137
2018-07-03 | 3982.3013 | 7955.7689 | 11938.0702
2018-07-04 | 3940.2293 | 7955.7689 | 11895.9982
2018-07-05 | 4128.7447 | 7955.7689 | 12084.5135
2018-07-06 | 2620.7276 | 15376.0951 | 17996.8227
2018-07-07 | 1788.0485 | 9572.6675 | 11360.716
2018-07-08 | 2716.5798 | 10385.6314 | 13102.2112
2018-07-09 | 1756.6638 | 3643.2266 | 5399.8905
2018-07-10 | 2240.4878 | 1093.1865 | 3333.6743
2018-07-11 | 2844.5271 | 2243.0848 | 5087.612
2018-07-12 | 8015.2393 | 162 | 8177.2393
2018-07-13 | 4755.7816 | 324 | 5079.7816
2018-07-14 | 1529.058 | 591.8095 | 2120.8675
2018-07-15 | 1308.5954 | 2825.6159 | 4134.2113
2018-07-16 | 1713.9278 | 2875.3906 | 4589.3185
2018-07-17 | 1348.3762 | 5106.4951 | 6454.8713
2018-07-18 | 1181.2109 | 4372.7983 | 5554.0092
2018-07-19 | 1046.0148 | 3840.565 | 4886.5797
2018-07-20 | 4062.5686 | 148.4 | 4210.9686
2018-07-21 | 10747.2577 | 4483.9777 | 15231.2354
2018-07-22 | 10747.2577 | 4172.0359 | 14919.2935
2018-07-23 | 10747.2577 | 452.7273 | 11199.9849
2018-07-24 | 11017.2577 | 357.2727 | 11374.5304
2018-07-25 | 10747.2577 | 522.2727 | 11269.5304
2018-07-26 | 10747.2577 | 2284.0386 | 13031.2963
2018-07-27 | 10747.2577 | 2593.3846 | 13340.6423
2018-07-28 | 11422.4748 | 2016.5664 | 13439.0412
2018-07-29 | 10747.2577 | 2770.4136 | 13517.6712
2018-07-30 | 10747.2577 | 798.2727 | 11545.5304
2018-07-31 | 10747.2577 | 1569.9091 | 12317.1668
2018-08-01 | 10999.2225 | 818.4545 | 11817.6771
2018-08-02 | 10747.2577 | 650.2 | 11397.4577
2018-08-03 | 10747.2577 | 355.05 | 11102.3077
2018-08-04 | 10747.2577 | 0 | 10747.2577
2018-08-05 | 6221.2906 | 2495.7772 | 8717.0678
2018-08-06 | 3576.1644 | 453.6 | 4029.7644
2018-08-07 | 3259.9407 | 355.95 | 3615.8907
2018-08-08 | 1902.9698 | 749.2321 | 2652.2018
2018-08-09 | 1145.4958 | 461.3346 | 1606.8304
2018-08-10 | 1183.3682 | 869.2588 | 2052.627
2018-08-11 | 1254.5777 | 7955.7689 | 9210.3466
2018-08-12 | 1039.1258 | 10289.5461 | 11328.6719
2018-08-13 | 2876.7963 | 3764.1954 | 6640.9916
2018-08-14 | 1091.8467 | 476.8364 | 1568.683
2018-08-15 | 1268.6373 | 1997.5394 | 3266.1767
2018-08-16 | 1039.1258 | 1044.9818 | 2084.1076
2018-08-17 | 1909.4094 | 7523.4545 | 9432.864
2018-08-18 | 1039.1258 | 7128 | 8167.1258
2018-08-19 | 1039.1258 | 9543.5954 | 10582.7212
2018-08-20 | 2100.1194 | 5517.8455 | 7617.9649
2018-08-21 | 2554.1304 | 652.9091 | 3207.0395
2018-08-22 | 1405.1285 | 1790.7212 | 3195.8497
2018-08-23 | 2149.3486 | 10428.7736 | 12578.1222
2018-08-24 | 5406.5901 | 13710.6458 | 19117.236
2018-08-25 | 5928.6392 | 8874 | 14802.6392
2018-08-26 | 13773.5987 | 6120.9636 | 19894.5623
2018-08-27 | 1663.1258 | 580.6364 | 2243.7622
2018-08-28 | 1525.9258 | 520.0636 | 2045.9894
2018-08-29 | 1375.1258 | 439.0909 | 1814.2167
2018-08-30 | 1398.781 | 897.5305 | 2296.3115
2018-08-31 | 2824.4278 | 2525.5259 | 5349.9537
2018-09-01 | 1719.0481 | 9380.4167 | 11099.4648
2018-09-02 | 1273.5591 | 3093.7591 | 4367.3182
2018-09-03 | 1059.1722 | 4916.4925 | 5975.6647
2018-09-04 | 1792.3441 | 156.9044 | 1949.2486
2018-09-05 | 1080.9074 | 583.2627 | 1664.1701
2018-09-06 | 1213.2268 | 429.6532 | 1642.88
2018-09-07 | 5517.1763 | 717.776 | 6234.9523
2018-09-08 | 17062.9849 | 618.1799 | 17681.1648
2018-09-09 | 17713.0593 | 2754.7275 | 20467.7869
2018-09-10 | 14389.542 | 362.6102 | 14752.1522
2018-09-11 | 9600.8862 | 1492.8833 | 11093.7695
2018-09-12 | 2539.0159 | 8825.7207 | 11364.7366
2018-09-13 | 9829.5789 | 1000 | 10829.5789
2018-09-14 | 6890.0664 | 0 | 6890.0664
2018-09-15 | 937.3724 | 691.85 | 1629.2224
2018-09-16 | 1726.911 | 11652.2887 | 13379.1997
2018-09-17 | 696 | 10658.5333 | 11354.5333
2018-09-18 | 1051.3649 | 10016.8955 | 11068.2603
2018-09-19 | 10378.6789 | 682.1831 | 11060.8621
2018-09-20 | 1919.5789 | 724.0067 | 2643.5856
2018-09-21 | 955.5789 | 6086.7895 | 7042.3685
2018-09-22 | 955.5789 | 6904.5446 | 7860.1235
2018-09-23 | 955.5789 | 6816.7142 | 7772.2931
2018-09-24 | 1511.963 | 3581.7457 | 5093.7088
2018-09-25 | 2813.4526 | 6293.2943 | 9106.7469
2018-09-26 | 3809.8853 | 90.5019 | 3900.3872
2018-09-27 | 1070.0038 | 1338.5774 | 2408.5812
2018-09-28 | 955.5789 | 12237.4833 | 13193.0623
2018-09-29 | 955.5789 | 0 | 955.5789
2018-09-30 | 1103.6357 | 2534.3473 | 3637.9831
2018-10-01 | 2247.0864 | 219.7 | 2466.7864
2018-10-02 | 1876.0289 | 2378.5462 | 4254.5751
2018-10-03 | 1940.4969 | 250.0096 | 2190.5065
2018-10-04 | 1871.2094 | 609.5048 | 2480.7142
2018-10-05 | 5402.11 | 360.5019 | 5762.6119
2018-10-06 | 3483.6522 | 978.1472 | 4461.7994
2018-10-07 | 5750.1505 | 2125.2943 | 7875.4448
2018-10-08 | 990.8148 | 0 | 990.8148
2018-10-09 | 1259.0204 | 0 | 1259.0204
2018-10-10 | 955.5789 | 602.2083 | 1557.7873
2018-10-11 | 955.5789 | 4423.3763 | 5378.9552
2018-10-12 | 955.5789 | 18404.0733 | 19359.6522
2018-10-13 | 1099.2549 | 354.1203 | 1453.3752
2018-10-14 | 933.7671 | 2785.1443 | 3718.9114
2018-10-15 | 1294.7401 | 10320.3 | 11615.0401
2018-10-16 | 1392.5777 | 11610.3333 | 13002.911
2018-10-17 | 734.5269 | 9948.5 | 10683.0269
2018-10-18 | 1826.0864 | 10061.1667 | 11887.2531
2018-10-19 | 1823.7969 | 10280.9333 | 12104.7302
2018-10-20 | 1569.2514 | 14335.8114 | 15905.0628
2018-10-21 | 1569.2514 | 12400.9811 | 13970.2325
2018-10-22 | 1703.0067 | 3301.7 | 5004.7067
2018-10-23 | 3917.4101 | 889.7752 | 4807.1853
2018-10-24 | 3850.9484 | 549.2209 | 4400.1693
2018-10-25 | 1446.9356 | 818.1818 | 2265.1174
2018-10-26 | 1581.2458 | 727.0815 | 2308.3273
2018-10-27 | 2996.9681 | 0 | 2996.9681
2018-10-28 | 1276.0514 | 2700.6175 | 3976.6689
2018-10-29 | 3537.8881 | 413.2259 | 3951.114
2018-10-30 | 1458.6637 | 493.6364 | 1952.3001
2018-10-31 | 1657.5322 | 1219.0172 | 2876.5494
2018-11-01 | 11627.8793 | 314.9948 | 11942.874
2018-11-02 | 14722.2437 | 708.8636 | 15431.1073
2018-11-03 | 4851.6325 | 1100.1197 | 5951.7522
2018-11-04 | 1241.5072 | 1128.0273 | 2369.5344
2018-11-05 | 2262.3834 | 80.7273 | 2343.1106
2018-11-06 | 3837.2451 | 232.7636 | 4070.0088
2018-11-07 | 2794.3232 | 262.3636 | 3056.6868
2018-11-08 | 2334.5319 | 643.7686 | 2978.3005
2018-11-09 | 2937.2777 | 501.9092 | 3439.1869
2018-11-10 | 3398.9558 | 0 | 3398.9558
2018-11-11 | 3322.3997 | 1014.7925 | 4337.1922
2018-11-12 | 3391.1978 | 1344.733 | 4735.9308
2018-11-13 | 6946.4282 | 329.1131 | 7275.5413
2018-11-14 | 8635.0122 | 115.9091 | 8750.9213
2018-11-15 | 3288.9067 | 941.7455 | 4230.6521
2018-11-16 | 3540.853 | 3492.6667 | 7033.5197
2018-11-17 | 3686.4654 | 4830.5833 | 8517.0488
2018-11-18 | 3649.6724 | 9620.8978 | 13270.5702
2018-11-19 | 3570.5215 | 7280.1709 | 10850.6924
2018-11-20 | 14426.0031 | 4684.2358 | 19110.2389
2018-11-21 | 14626.327 | 4135.7333 | 18762.0603
2018-11-22 | 13176.2781 | 10801 | 23977.2781
2018-11-23 | 13131.5414 | 11256 | 24387.5414
2018-11-24 | 13135.745 | 12934.6358 | 26070.3809
2018-11-25 | 13907.8877 | 14193.6127 | 28101.5005
2018-11-26 | 26112.8581 | 7369.4937 | 33482.3518
2018-11-27 | 21535.5825 | 6311.9136 | 27847.4961
2018-11-28 | 18608.062 | 3380 | 21988.062
2018-11-29 | 21168.6188 | 3151.5 | 24320.1188
2018-11-30 | 11956.5673 | 10716.5333 | 22673.1007
2018-12-01 | 10864.8833 | 9504.6649 | 20369.5481
2018-12-02 | 14641.4071 | 9451.5946 | 24093.0016
2018-12-03 | 21360.7738 | 295 | 21655.7738
2018-12-04 | 10591.204 | 0 | 10591.204
2018-12-05 | 3442.6226 | 786.45 | 4229.0726
2018-12-06 | 3459.7738 | 580.0177 | 4039.7914
2018-12-07 | 3455.2087 | 6147.1667 | 9602.3754
2018-12-08 | 2950.3145 | 12286.5315 | 15236.8461
2018-12-09 | 3233.913 | 13867.5946 | 17101.5075
2018-12-10 | 2603.4661 | 8534.1833 | 11137.6494
2018-12-11 | 2427.2994 | 0 | 2427.2994
2018-12-12 | 3147.6661 | 9306.7195 | 12454.3855
2018-12-13 | 2333.3461 | 13183.6879 | 15517.0339
2018-12-14 | 2267.4661 | 11878.0667 | 14145.5327
2018-12-15 | 1663.4792 | 3072.5315 | 4736.0107
2018-12-16 | 2267.045 | 5198.6779 | 7465.7229
2018-12-17 | 14846.0027 | 7080 | 21926.0027
2018-12-18 | 10731.545 | 11935.5769 | 22667.1219
2018-12-19 | 3342.712 | 20223.4923 | 23566.2043
2018-12-20 | 7284.6601 | 6719.2744 | 14003.9344
2018-12-21 | 5683.045 | 11065.8911 | 16748.9361
2018-12-22 | 5683.045 | 9519.8667 | 15202.9117
2018-12-23 | 3356.045 | 9456 | 12812.045
2018-12-24 | 1387.045 | 8976.6333 | 10363.6783
2018-12-25 | 1387.045 | 0 | 1387.045
2018-12-26 | 1387.045 | 1603.8167 | 2990.8617
2018-12-27 | 2531.0142 | 1675.5 | 4206.5142
2018-12-28 | 3330.1104 | 359.8 | 3689.9104
2018-12-29 | 3181.1783 | 0 | 3181.1783
2018-12-30 | 1387.045 | 760.9394 | 2147.9844
2018-12-31 | 1873.6612 | 1775.5253 | 3649.1865
2019-01-01 | 3155.1919 | 0 | 3155.1919
2019-01-02 | 3317.8268 | 0 | 3317.8268
2019-01-03 | 1708.7533 | 651.1449 | 2359.8982
2019-01-04 | 1580.693 | 18104.4333 | 19685.1264
2019-01-05 | 1539.2329 | 16392 | 17931.2329
2019-01-06 | 2412.0469 | 12173.1706 | 14585.2175
2019-01-07 | 2824.375 | 8401.8931 | 11226.2681
2019-01-08 | 2824.375 | 4348.2194 | 7172.5944
2019-01-09 | 11921.359 | 1637.1838 | 13558.5427
2019-01-10 | 3211.2959 | 0 | 3211.2959
2019-01-11 | 1725.2403 | 0 | 1725.2403
2019-01-12 | 1725.2403 | 0 | 1725.2403
2019-01-13 | 1725.2403 | 0 | 1725.2403
2019-01-14 | 5682.2841 | 521.3241 | 6203.6082
2019-01-15 | 8893.5345 | 368.1525 | 9261.687
2019-01-16 | 8840.6915 | 0 | 8840.6915
2019-01-17 | 9218.207 | 0 | 9218.207
2019-01-18 | 6728.568 | 4034.0981 | 10762.6661
2019-01-19 | 6085.9885 | 0 | 6085.9885
2019-01-20 | 2040.912 | 0 | 2040.912
2019-01-21 | 1640.6915 | 86.6241 | 1727.3156
2019-01-22 | 1916.3709 | 1177.645 | 3094.016
2019-01-23 | 1698.1081 | 180.0692 | 1878.1774
2019-01-24 | 2132.9415 | 86.6241 | 2219.5656
2019-01-25 | 1882.9947 | 4029.5792 | 5912.5739
2019-01-26 | 1594.1896 | 4792.9394 | 6387.1291
2019-01-27 | 10299.0394 | 1519.8477 | 11818.8872
2019-01-28 | 9958.6921 | 86.6241 | 10045.3162
2019-01-29 | 2941.4503 | 401.3584 | 3342.8087
2019-01-30 | 2978.1552 | 0 | 2978.1552
2019-01-31 | 2853.4457 | 0 | 2853.4457
2019-02-01 | 2599.7992 | 8.1 | 2607.8992
2019-02-02 | 2904.9125 | 20427.6939 | 23332.6065
2019-02-03 | 7321.9111 | 29319.4883 | 36641.3994
2019-02-04 | 2603.5841 | 23039.5322 | 25643.1162
2019-02-05 | 2599.7992 | 18045.5499 | 20645.3491
2019-02-06 | 2770.8712 | 10405.6959 | 13176.5671
2019-02-07 | 2501.1589 | 9185.8971 | 11687.056
2019-02-08 | 2599.7992 | 6083.1391 | 8682.9383
2019-02-09 | 2599.7992 | 0 | 2599.7992
2019-02-10 | 2599.7992 | 0 | 2599.7992
2019-02-11 | 2635.7325 | 527.8511 | 3163.5836
2019-02-12 | 6741.7038 | 1829.9512 | 8571.6551
2019-02-13 | 15039.8091 | 203.6222 | 15243.4314
2019-02-14 | 10483.594 | 1292.0667 | 11775.6607
2019-02-15 | 4407.6834 | 12565.7212 | 16973.4045
2019-02-16 | 2642.0736 | 8422.1321 | 11064.2057
2019-02-17 | 2599.7992 | 5007.845 | 7607.6442
2019-02-18 | 6631.7326 | 5473.5332 | 12105.2658
2019-02-19 | 4975.4701 | 4812.9949 | 9788.465
2019-02-20 | 2994.0764 | 4623.1556 | 7617.2319
2019-02-21 | 2941.98 | 4862.6667 | 7804.6467
2019-02-22 | 2599.7992 | 5679.8 | 8279.5992
2019-02-23 | 2599.7992 | 7194.334 | 9794.1332
2019-02-24 | 2599.7992 | 7691.3872 | 10291.1864
2019-02-25 | 2599.7992 | 1790.6234 | 4390.4226
2019-02-26 | 2924.1492 | 2733.7924 | 5657.9416
2019-02-27 | 2665.031 | 1387.2348 | 4052.2658
2019-02-28 | 2633.6188 | 1298.2823 | 3931.9011
2019-03-01 | 1675.8101 | 8629.0258 | 10304.8358
2019-03-02 | 1701.2046 | 488.4189 | 2189.6234
2019-03-03 | 2482.4519 | 1322.8011 | 3805.253
2019-03-04 | 2443.6681 | 95.695 | 2539.3631
2019-03-05 | 1792.6951 | 822.9348 | 2615.6299
2019-03-06 | 1708.2423 | 594.5455 | 2302.7878
2019-03-07 | 1708.2423 | 484.8085 | 2193.0508
2019-03-08 | 1456.7307 | 6588.9259 | 8045.6566
2019-03-09 | 847.9434 | 12138.1791 | 12986.1225
2019-03-10 | 2099.0526 | 8559.4086 | 10658.4612
2019-03-11 | 1488.7374 | 312 | 1800.7374
2019-03-12 | 902.8377 | 312 | 1214.8377
2019-03-13 | 949.2164 | 312 | 1261.2164
2019-03-14 | 1157.9501 | 1049.9213 | 2207.8714
2019-03-15 | 974.1769 | 312 | 1286.1769
2019-03-16 | 672 | 1199.25 | 1871.25
2019-03-17 | 672 | 1506.2667 | 2178.2667
2019-03-18 | 672 | 312 | 984
2019-03-19 | 788.2307 | 360.7667 | 1148.9973
2019-03-20 | 800.2667 | 468.2167 | 1268.4833
2019-03-21 | 984 | 312 | 1296
2019-03-22 | 808.9333 | 127.1833 | 936.1167
2019-03-23 | 672 | 5921.1 | 6593.1
2019-03-24 | 672 | 11926.858 | 12598.858
2019-03-25 | 672 | 2397.2333 | 3069.2333
2019-03-26 | 779.775 | 0 | 779.775
2019-03-27 | 672 | 0 | 672
2019-03-28 | 672 | 1454.3667 | 2126.3667
2019-03-29 | 862.9588 | 0 | 862.9588
2019-03-30 | 1883.3684 | 0 | 1883.3684
2019-03-31 | 1883.3684 | 0 | 1883.3684
2019-04-01 | 3458.6018 | 0 | 3458.6018
2019-04-02 | 7557.9662 | 238.1167 | 7796.0829
2019-04-03 | 4571.4342 | 0 | 4571.4342
2019-04-04 | 1160.3667 | 345.617 | 1505.9837
2019-04-05 | 672 | 432.5097 | 1104.5097
2019-04-06 | 672 | 0 | 672
2019-04-07 | 672 | 172.8085 | 844.8085
2019-04-08 | 672 | 211.6904 | 883.6904
2019-04-09 | 672 | 0 | 672
2019-04-10 | 672 | 309.1067 | 981.1067
2019-04-11 | 838.0198 | 0 | 838.0198
2019-04-12 | 774.7251 | 340.9855 | 1115.7106
2019-04-13 | 672 | 0 | 672
2019-04-14 | 1025.5577 | 233.2121 | 1258.7698
2019-04-15 | 741.5882 | 375.0828 | 1116.6711
2019-04-16 | 672 | 0 | 672
2019-04-17 | 756.9971 | 0 | 756.9971
2019-04-18 | 759.3756 | 0 | 759.3756
2019-04-19 | 672 | 0 | 672
2019-04-20 | 12770.45 | 0 | 12770.45
2019-04-21 | 22223.9297 | 0 | 22223.9297
2019-04-22 | 21042.9391 | 0 | 21042.9391
2019-04-23 | 10177.0676 | 0 | 10177.0676
2019-04-24 | 8951.3313 | 161.4545 | 9112.7858
2019-04-25 | 4272.0382 | 403.6364 | 4675.6746
2019-04-26 | 17659.7706 | 340.5212 | 18000.2918
2019-04-27 | 7850.8 | 8339.7793 | 16190.5793
2019-04-28 | 672 | 8351.8884 | 9023.8884
2019-04-29 | 896.3801 | 8501.2339 | 9397.6139
2019-04-30 | 746.2275 | 8388.2157 | 9134.4432
2019-05-01 | 10222.1794 | 1129.3451 | 11351.5246
2019-05-02 | 994.8287 | 8339.7793 | 9334.6081
2019-05-03 | 1291.6676 | 10888.4011 | 12180.0687
2019-05-04 | 990.6667 | 8339.7793 | 9330.446
2019-05-05 | 672 | 8339.7793 | 9011.7793
2019-05-06 | 24338.3627 | 187.2092 | 24525.5719
2019-05-07 | 26411.6505 | 324.016 | 26735.6664
2019-05-08 | 17648.9625 | 1755 | 19403.9625
2019-05-09 | 14163.1527 | 437.6667 | 14600.8193
2019-05-10 | 21917.7 | 352.3046 | 22270.0046
2019-05-11 | 24656.5731 | 0 | 24656.5731
2019-05-12 | 25548 | 0 | 25548
2019-05-13 | 24961.0167 | 2063.5 | 27024.5167
2019-05-14 | 20901.55 | 10888.1167 | 31789.6667
2019-05-15 | 14100 | 141.127 | 14241.127
2019-05-16 | 10082.8 | 316.8156 | 10399.6156
2019-05-17 | 14431.1304 | 144.1587 | 14575.2891
2019-05-18 | 6757.6066 | 11.5327 | 6769.1393
2019-05-19 | 1570.8948 | 0 | 1570.8948
2019-05-20 | 1401.9429 | 2722.9248 | 4124.8677
2019-05-21 | 2789.3795 | 2859.9126 | 5649.2921
2019-05-22 | 954.2916 | 9714.7381 | 10669.0298
2019-05-23 | 433.0676 | 13706.7879 | 14139.8555
2019-05-24 | 1075.2676 | 13452.4833 | 14527.751
2019-05-25 | 2607.325 | 9651.375 | 12258.7
2019-05-26 | 621.8038 | 0 | 621.8038
2019-05-27 | 360 | 3864 | 4224
2019-05-28 | 1730.1186 | 2737 | 4467.1186
2019-05-29 | 4264.1151 | 1219.526 | 5483.6411
2019-05-30 | 4868.2263 | 3717.0615 | 8585.2879
2019-05-31 | 5286.7415 | 1360 | 6646.7415
2019-06-01 | 4528.9744 | 3924.2823 | 8453.2567
2019-06-02 | 4363.1068 | 11949.8717 | 16312.9784
2019-06-03 | 7314.7401 | 9460.35 | 16775.0901
2019-06-04 | 6765.3046 | 10969.8503 | 17735.1549
2019-06-05 | 5079.3255 | 11163.5372 | 16242.8628
2019-06-06 | 5137.568 | 1820.853 | 6958.4211
2019-06-07 | 4404.4734 | 7543.6212 | 11948.0947
2019-06-08 | 9180.6651 | 20547.2823 | 29727.9474
2019-06-09 | 13894.1807 | 21951.7663 | 35845.9471
2019-06-10 | 14963.7434 | 19673.5365 | 34637.2799
2019-06-11 | 10228.4125 | 6557.9834 | 16786.3959
2019-06-12 | 2591.3734 | 4604.4307 | 7195.8041
2019-06-13 | 2632.6593 | 4360.3501 | 6993.0094
2019-06-14 | 2189.1824 | 13059.1117 | 15248.2941
2019-06-15 | 1165.4353 | 19986.5981 | 21152.0335
2019-06-16 | 764.5401 | 15061.7695 | 15826.3096
2019-06-17 | 764.5401 | 3983.5866 | 4748.1267
2019-06-18 | 819.9568 | 5214.6061 | 6034.5628
2019-06-19 | 764.5401 | 4842.4704 | 5607.0105
2019-06-20 | 853.1459 | 4444.8682 | 5298.0141
2019-06-21 | 2000.5229 | 5682.0167 | 7682.5396
2019-06-22 | 2561.835 | 9548.2823 | 12110.1173
2019-06-23 | 1379.7522 | 13552.9362 | 14932.6884
2019-06-24 | 1023.452 | 4013.8288 | 5037.2808
2019-06-25 | 764.5401 | 5582.8875 | 6347.4277
2019-06-26 | 4994.0061 | 3967.8955 | 8961.9016
2019-06-27 | 1178.4795 | 4190.4343 | 5368.9139
2019-06-28 | 1394.6176 | 4010.2074 | 5404.825
2019-06-29 | 8171.8585 | 3504 | 11675.8585
2019-06-30 | 3150.0188 | 3654.8067 | 6804.8254
2019-07-01 | 11683.3484 | 143.4135 | 11826.7619
2019-07-02 | 14144.1651 | 334.3365 | 14478.5016
2019-07-03 | 8380.8437 | 644.7339 | 9025.5775
2019-07-04 | 4268.5401 | 4055.7692 | 8324.3093
2019-07-05 | 4268.5401 | 678.778 | 4947.3182
2019-07-06 | 4268.5401 | 468.1613 | 4736.7014
2019-07-07 | 4268.5401 | 1872.6453 | 6141.1854
2019-07-08 | 7449.0188 | 719.3479 | 8168.3668
2019-07-09 | 10611.9772 | 383.1667 | 10995.1439
2019-07-10 | 8626.9486 | 149.8077 | 8776.7563
2019-07-11 | 4671.9369 | 260.6813 | 4932.6182
2019-07-12 | 4726.9679 | 2275.5407 | 7002.5086
2019-07-13 | 9414.4494 | 2196.3944 | 11610.8437
2019-07-14 | 5876.2646 | 171.8182 | 6048.0828
2019-07-15 | 5410.2124 | 587.9446 | 5998.157
2019-07-16 | 4484.1492 | 1159.2047 | 5643.3539
2019-07-17 | 4419.5555 | 455.4545 | 4875.01
2019-07-18 | 5197.5281 | 279.5455 | 5477.0735
2019-07-19 | 10244.7674 | 0 | 10244.7674
2019-07-20 | 5535.9779 | 112.7852 | 5648.763
2019-07-21 | 4630.9657 | 99.5455 | 4730.5112
2019-07-22 | 4419.5555 | 1870.2768 | 6289.8323
2019-07-23 | 4542.9888 | 2991.094 | 7534.0829
2019-07-24 | 4755.5555 | 1134.2 | 5889.7555
2019-07-25 | 4821.143 | 7899.5 | 12720.643
2019-07-26 | 4755.5555 | 8880 | 13635.5555
2019-07-27 | 9106.5305 | 8880 | 17986.5305
2019-07-28 | 18101.4305 | 3268.3333 | 21369.7638
2019-07-29 | 18074.501 | 0 | 18074.501
2019-07-30 | 18158.3441 | 320.4834 | 18478.8275
2019-07-31 | 8814.0499 | 419.8917 | 9233.9415
2019-08-01 | 4976.9888 | 482.3182 | 5459.307
2019-08-02 | 5046.6434 | 276.75 | 5323.3934
2019-08-03 | 4922.4126 | 8533.5109 | 13455.9235
2019-08-04 | 4519.9353 | 13500.3995 | 18020.3348
2019-08-05 | 1418.4126 | 3253.75 | 4672.1626
2019-08-06 | 1418.4126 | 201.6 | 1620.0126
2019-08-07 | 1616.8626 | 414 | 2030.8626
2019-08-08 | 1418.4126 | 467.7673 | 1886.1799
2019-08-09 | 1478.0376 | 165.75 | 1643.7876
2019-08-10 | 11589.4214 | 0 | 11589.4214
2019-08-11 | 22935.1815 | 0 | 22935.1815
2019-08-12 | 15059.3924 | 0 | 15059.3924
2019-08-13 | 1497.9126 | 83.081 | 1580.9936
2019-08-14 | 1493.5564 | 552.5667 | 2046.1231
2019-08-15 | 1232.9126 | 465.85 | 1698.7626
2019-08-16 | 1168.278 | 0 | 1168.278
2019-08-17 | 1082.4126 | 2333.7772 | 3416.1898
2019-08-18 | 1082.4126 | 0 | 1082.4126
2019-08-19 | 1148.9939 | 183.9231 | 1332.917
2019-08-20 | 2550.1001 | 336.8179 | 2886.9181
2019-08-21 | 4046.0376 | 743.0167 | 4789.0543
2019-08-22 | 2548.5293 | 9979.6364 | 12528.1657
2019-08-23 | 1082.4126 | 4694.0136 | 5776.4263
2019-08-24 | 1221.5957 | 0 | 1221.5957
2019-08-25 | 1082.4126 | 2678.2202 | 3760.6329
2019-08-26 | 1082.4126 | 0 | 1082.4126
2019-08-27 | 1229.6854 | 0 | 1229.6854
2019-08-28 | 1247.7157 | 0 | 1247.7157
2019-08-29 | 1323.593 | 156.6 | 1480.193
2019-08-30 | 3529.596 | 272.7 | 3802.296
2019-08-31 | 1082.4126 | 535.644 | 1618.0567
2019-09-01 | 509.0526 | 1389.9528 | 1899.0055
2019-09-02 | 509.0526 | 0 | 509.0526
2019-09-03 | 2762.8487 | 0 | 2762.8487
2019-09-04 | 761.7242 | 532.65 | 1294.3742
2019-09-05 | 889.3026 | 11676.7273 | 12566.0299
2019-09-06 | 509.0526 | 1601.9864 | 2111.039
2019-09-07 | 509.0526 | 513.7547 | 1022.8073
2019-09-08 | 2507.0526 | 1816.8236 | 4323.8762
2019-09-09 | 7682.6409 | 347.3387 | 8029.9795
2019-09-10 | 6326.9664 | 0 | 6326.9664
2019-09-11 | 3085.7742 | 0 | 3085.7742
2019-09-12 | 4491.5538 | 0 | 4491.5538
2019-09-13 | 2789.0249 | 96.8167 | 2885.8416
2019-09-14 | 1862.0102 | 8236.5881 | 10098.5983
2019-09-15 | 995.5021 | 8953.517 | 9949.019
2019-09-16 | 578.6409 | 321.503 | 900.1439
2019-09-17 | 509.0526 | 987.384 | 1496.4366
2019-09-18 | 509.0526 | 8880 | 9389.0526
2019-09-19 | 5154.3659 | 4964.1667 | 10118.5326
2019-09-20 | 4821.7799 | 0 | 4821.7799
2019-09-21 | 1992.689 | 616.5057 | 2609.1947
2019-09-22 | 1353.5812 | 1746.766 | 3100.3473
2019-09-23 | 634.8102 | 387.4333 | 1022.2435
2019-09-24 | 584.4399 | 526.8085 | 1111.2484
2019-09-25 | 509.0526 | 786.4213 | 1295.4739
2019-09-26 | 580.9605 | 1974.2817 | 2555.2422
2019-09-27 | 579.8007 | 0 | 579.8007
2019-09-28 | 578.6409 | 513.7547 | 1092.3956
2019-09-29 | 509.0526 | 1335.7623 | 1844.8149
2019-09-30 | 585.5997 | 163.6364 | 749.2361
2019-10-01 | 828.6526 | 294.5455 | 1123.1981
2019-10-02 | 1057.531 | 0 | 1057.531
2019-10-03 | 459.5997 | 0 | 459.5997
2019-10-04 | 176.2291 | 0 | 176.2291
2019-10-05 | 0 | 513.7547 | 513.7547
2019-10-06 | 392.7273 | 1233.0113 | 1625.7386
2019-10-07 | 0 | 0 | 0
2019-10-08 | 0 | 744.6359 | 744.6359
2019-10-09 | 55.9091 | 237.021 | 292.9301
2019-10-10 | 1863.7588 | 324.5329 | 2188.2917
2019-10-11 | 1428.7 | 0 | 1428.7
2019-10-12 | 0 | 513.7547 | 513.7547
2019-10-13 | 342.4615 | 1233.0113 | 1575.4729
2019-10-14 | 9.7846 | 688.1833 | 697.9679
2019-10-15 | 0 | 380.3474 | 380.3474
2019-10-16 | 823.5575 | 0 | 823.5575
2019-10-17 | 14762.5 | 0 | 14762.5
2019-10-18 | 3059.6827 | 0 | 3059.6827
2019-10-19 | 1132.6715 | 0 | 1132.6715
2019-10-20 | 94.4412 | 0 | 94.4412
2019-10-21 | 1107.9882 | 1829.8182 | 2937.8064
2019-10-22 | 0 | 67.3475 | 67.3475
2019-10-23 | 0 | 0 | 0
2019-10-24 | 1369.8418 | 310.9091 | 1680.7509
2019-10-25 | 533.8412 | 903.2803 | 1437.1215
2019-10-26 | 346.9173 | 4295.9333 | 4642.8506
2019-10-27 | 119.1702 | 4669.6 | 4788.7702
2019-10-28 | 0 | 4110.5455 | 4110.5455
2019-10-29 | 200.8904 | 2318.4826 | 2519.373
2019-10-30 | 15.1356 | 1218.837 | 1233.9726
2019-10-31 | 96.2637 | 1304.3276 | 1400.5913
2019-11-01 | 0 | 0 | 0
2019-11-02 | 0 | 0 | 0
2019-11-03 | 68.7981 | 103.6364 | 172.4344
2019-11-04 | 1164.6735 | 342.2727 | 1506.9463
2019-11-05 | 247.3824 | 347.5091 | 594.8915
2019-11-06 | 568.0053 | 1457.711 | 2025.7163
2019-11-07 | 97.9111 | 903.9646 | 1001.8757
2019-11-08 | 1468.8042 | 0 | 1468.8042
2019-11-09 | 0 | 0 | 0
2019-11-10 | 0 | 732.6283 | 732.6283
2019-11-11 | 68.4284 | 1465.2566 | 1533.685
2019-11-12 | 2542.6008 | 0 | 2542.6008
2019-11-13 | 291.4824 | 0 | 291.4824
2019-11-14 | 768.0783 | 0 | 768.0783
2019-11-15 | 958 | 0 | 958
2019-11-16 | 8145.8337 | 610.5236 | 8756.3573
2019-11-17 | 4286.0143 | 1465.2566 | 5751.2709
2019-11-18 | 4987.8622 | 0 | 4987.8622
2019-11-19 | 4835.4202 | 0 | 4835.4202
2019-11-20 | 3652.7869 | 1966.8545 | 5619.6415
2019-11-21 | 1672.4372 | 7210.4364 | 8882.8735
2019-11-22 | 0 | 9792.5333 | 9792.5333
2019-11-23 | 0 | 9199.4616 | 9199.4616
2019-11-24 | 5161.5 | 1790.1933 | 6951.6933
2019-11-25 | 2836.6667 | 8686.9697 | 11523.6364
2019-11-26 | 254.4729 | 14711 | 14965.4729
2019-11-27 | 1840.4479 | 7628.7333 | 9469.1812
2019-11-28 | 2822.4121 | 7200 | 10022.4121
2019-11-29 | 2822.4121 | 7182.4071 | 10004.8191
2019-11-30 | 2822.4121 | 10651.3038 | 13473.7159
2019-12-01 | 3467.195 | 8860.4574 | 12327.6524
2019-12-02 | 5166.0054 | 3761.25 | 8927.2554
2019-12-03 | 2839.8846 | 4878.8895 | 7718.7742
2019-12-04 | 2910.3493 | 16416.4767 | 19326.826
2019-12-05 | 3650.8296 | 16555.3763 | 20206.2059
2019-12-06 | 8537.0796 | 7298.05 | 15835.1296
2019-12-07 | 12021.1189 | 634.1162 | 12655.235
2019-12-08 | 3833.3201 | 1788.2077 | 5621.5278
2019-12-09 | 3608.9117 | 219.7571 | 3828.6687
2019-12-10 | 4386.1737 | 0 | 4386.1737
2019-12-11 | 3712.7514 | 62.7877 | 3775.5391
2019-12-12 | 3022.8017 | 2540.5293 | 5563.3311
2019-12-13 | 667.045 | 9456 | 10123.045
2019-12-14 | 667.045 | 13198.942 | 13865.987
2019-12-15 | 667.045 | 9473.7577 | 10140.8027
2019-12-16 | 2646.4507 | 13664.3436 | 16310.7943
2019-12-17 | 10579.045 | 12434.5856 | 23013.6306
2019-12-18 | 17419.22 | 9456 | 26875.22
2019-12-19 | 20188.7188 | 9456 | 29644.7188
2019-12-20 | 17525.1054 | 17066 | 34591.1054
2019-12-21 | 2171.545 | 31792.9394 | 33964.4844
2019-12-22 | 7620.9617 | 23965.8253 | 31586.787
2019-12-23 | 2257.4264 | 21078.8333 | 23336.2597
2019-12-24 | 667.045 | 13647.95 | 14314.995
2019-12-25 | 3534.445 | 9456 | 12990.445
2019-12-26 | 667.045 | 17674.9333 | 18341.9783
2019-12-27 | 782.7783 | 21319.4667 | 22102.245
2019-12-28 | 6231.5056 | 15871.6061 | 22103.1117
2019-12-29 | 667.045 | 26374.292 | 27041.337
2019-12-30 | 843.1728 | 10737.5152 | 11580.688
2019-12-31 | 667.045 | 9547.7778 | 10214.8228
2020-01-01 | 667.045 | 9536.4545 | 10203.4996
2020-01-02 | 667.045 | 11114.1848 | 11781.2299
2020-01-03 | 667.045 | 9456 | 10123.045
2020-01-04 | 667.045 | 10216.9394 | 10883.9844
2020-01-05 | 1050.5663 | 3195.585 | 4246.1512
2020-01-06 | 1923.0947 | 2429.6667 | 4352.7613
2020-01-07 | 667.045 | 9456 | 10123.045
2020-01-08 | 843.845 | 1890.4818 | 2734.3268
2020-01-09 | 3326.7106 | 345.6566 | 3672.3672
2020-01-10 | 4235.862 | 1290.2644 | 5526.1265
2020-01-11 | 5106.3842 | 13898.5516 | 19004.9359
2020-01-12 | 3800.662 | 16867.2 | 20667.862
2020-01-13 | 3950.6242 | 23088 | 27038.6242
2020-01-14 | 2129.9033 | 25805.3212 | 27935.2245
2020-01-15 | 1051.045 | 14027.5273 | 15078.5723
2020-01-16 | 1051.045 | 9813.5758 | 10864.6208
2020-01-17 | 917.1783 | 11442.4773 | 12359.6556
2020-01-18 | 1258.9783 | 17484.5719 | 18743.5502
2020-01-19 | 1051.977 | 9508.1212 | 10560.0982
2020-01-20 | 3655.3117 | 9797.0606 | 13452.3723
2020-01-21 | 4796.1202 | 9812.6818 | 14608.802
2020-01-22 | 667.045 | 9894.4773 | 10561.5223
2020-01-23 | 667.045 | 9887.9318 | 10554.9768
2020-01-24 | 667.045 | 9913.5 | 10580.545
2020-01-25 | 1907.811 | 10450.2728 | 12358.0838
2020-01-26 | 1527.045 | 11231.5253 | 12758.5703
2020-01-27 | 667.045 | 9456 | 10123.045
2020-01-28 | 667.045 | 836.6667 | 1503.7117
2020-01-29 | 14921.8787 | 252.6439 | 15174.5226
2020-01-30 | 3924.7961 | 13452.7576 | 17377.5536
2020-01-31 | 1134.9176 | 13680 | 14814.9176
2020-02-01 | 667.045 | 8103.5 | 8770.545
2020-02-02 | 1427.9844 | 0 | 1427.9844
2020-02-03 | 2494.1774 | 4374.8348 | 6869.0122
2020-02-04 | 667.045 | 4651.9091 | 5318.9541
2020-02-05 | 667.045 | 3698.5045 | 4365.5496
2020-02-06 | 738.8126 | 297.2727 | 1036.0853
2020-02-07 | 740.0416 | 260.4545 | 1000.4961
2020-02-08 | 667.045 | 760.9394 | 1427.9844
2020-02-09 | 667.045 | 2282.8183 | 2949.8633
2020-02-10 | 1744.0625 | 850.4545 | 2594.517
2020-02-11 | 1197.7244 | 10481.4924 | 11679.2168
2020-02-12 | 691.5787 | 11929.1136 | 12620.6924
2020-02-13 | 2021.1977 | 12685.5118 | 14706.7095
2020-02-14 | 7991.295 | 3636.7309 | 11628.0259
2020-02-15 | 667.045 | 760.9394 | 1427.9844
2020-02-16 | 746.427 | 2113.7206 | 2860.1476
2020-02-17 | 667.045 | 4786.6917 | 5453.7367
2020-02-18 | 667.045 | 8649.6 | 9316.645
2020-02-19 | 798.8258 | 8967.12 | 9765.9458
2020-02-20 | 2434.1303 | 8289.7032 | 10723.8335
2020-02-21 | 1625.8425 | 8279.8397 | 9905.6822
2020-02-22 | 667.045 | 11116.8728 | 11783.9178
2020-02-23 | 931.4723 | 10661.3809 | 11592.8532
2020-02-24 | 1022.0564 | 8712.6141 | 9734.6705
2020-02-25 | 667.045 | 9165.4959 | 9832.541
2020-02-26 | 667.045 | 9035.7273 | 9702.7723
2020-02-27 | 682.3283 | 8606.0909 | 9288.4192
2020-02-28 | 1177.972 | 8444.1818 | 9622.1539
2020-02-29 | 974.4209 | 14052.3 | 15026.7209
2020-03-01 | 0 | 20688.3051 | 20688.3051
2020-03-02 | 7858.7205 | 15775.2453 | 23633.9658
2020-03-03 | 8275.7833 | 18048.8154 | 26324.5987
2020-03-04 | 2516.3335 | 22378.5 | 24894.8335
2020-03-05 | 312 | 29088 | 29400
2020-03-06 | 312 | 16071.125 | 16383.125
2020-03-07 | 312 | 8928.6283 | 9240.6283
2020-03-08 | 312 | 16680.9193 | 16992.9193
2020-03-09 | 183.9548 | 8554.0097 | 8737.9645
2020-03-10 | 724 | 8678.8771 | 9402.8771
2020-03-11 | 1968 | 8788.5544 | 10756.5544
2020-03-12 | 0 | 9007.187 | 9007.187
2020-03-13 | 0 | 8960.195 | 8960.195
2020-03-14 | 0 | 8683.0113 | 8683.0113
2020-03-15 | 772.1508 | 9803.1374 | 10575.2881
2020-03-16 | 2308.3633 | 8196 | 10504.3633
2020-03-17 | 4240 | 8219.3413 | 12459.3413
2020-03-18 | 548.6728 | 8196 | 8744.6728
2020-03-19 | 0 | 8359.6364 | 8359.6364
2020-03-20 | 1027.7712 | 9978.0828 | 11005.8541
2020-03-21 | 455.5021 | 9905.466 | 10360.9681
2020-03-22 | 520.2231 | 8359.6364 | 8879.8594
2020-03-23 | 1424.3042 | 8624.1818 | 10048.486
2020-03-24 | 360 | 9818.3667 | 10178.3667
2020-03-25 | 431.6559 | 14865.2727 | 15296.9286
2020-03-26 | 360 | 17329.2333 | 17689.2333
2020-03-27 | 360 | 15535.1144 | 15895.1144
2020-03-28 | 1107.3333 | 16126.517 | 17233.8503
2020-03-29 | 360 | 17100.5396 | 17460.5396
2020-03-30 | 620.7481 | 7297.8002 | 7918.5483
2020-03-31 | 10655.725 | 2900.4716 | 13556.1966
2020-04-01 | 11844 | 8746.8009 | 20590.8009
2020-04-02 | 19595.25 | 8460.5914 | 28055.8414
2020-04-03 | 22827.8146 | 6087.9353 | 28915.7499
2020-04-04 | 8348.8333 | 28067.3047 | 36416.138
2020-04-05 | 5052.7984 | 17384.1468 | 22436.9452
2020-04-06 | 11522.493 | 11145.6037 | 22668.0967
2020-04-07 | 5691.7086 | 6033.3534 | 11725.0621
2020-04-08 | 3578.5 | 4464.4598 | 8042.9598
2020-04-09 | 360 | 5069.6507 | 5429.6507
2020-04-10 | 1269.1216 | 4056 | 5325.1216
2020-04-11 | 360 | 1239.6283 | 1599.6283
2020-04-12 | 360 | 1709.466 | 2069.466
2020-04-13 | 360 | 11410.4167 | 11770.4167
2020-04-14 | 568.6219 | 15499.6364 | 16068.2583
2020-04-15 | 360 | 15882.225 | 16242.225
2020-04-16 | 1049.1901 | 14670.3129 | 15719.503
2020-04-17 | 360 | 3237 | 3597
2020-04-18 | 360 | 732.6283 | 1092.6283
2020-04-19 | 360 | 1873.1024 | 2233.1024
2020-04-20 | 360 | 10268.0144 | 10628.0144
2020-04-21 | 568 | 23695.8189 | 24263.8189
2020-04-22 | 2422 | 24733.8717 | 27155.8717
2020-04-23 | 551.1 | 25766.5136 | 26317.6136
2020-04-24 | 951.6 | 16020.3818 | 16971.9818
2020-04-25 | 1163.395 | 28872.6283 | 30036.0233
2020-04-26 | 360 | 29849.466 | 30209.466
2020-04-27 | 360 | 28140 | 28500
2020-04-28 | 360 | 28140 | 28500
2020-04-29 | 360 | 27365.0333 | 27725.0333
2020-04-30 | 360 | 11538.1212 | 11898.1212
2020-05-01 | 1721.7909 | 8372.9077 | 10094.6986
2020-05-02 | 1587.8008 | 4500.6283 | 6088.4292
2020-05-03 | 480.3453 | 5477.466 | 5957.8113
2020-05-04 | 1296.8915 | 3768 | 5064.8915
2020-05-05 | 3244.7792 | 16136.311 | 19381.0901
2020-05-06 | 386.0396 | 3768 | 4154.0396
2020-05-07 | 1177.7875 | 3768 | 4945.7875
2020-05-08 | 360 | 9209.4667 | 9569.4667
2020-05-09 | 360 | 11604.6283 | 11964.6283
2020-05-10 | 360 | 12581.466 | 12941.466
2020-05-11 | 360 | 8545.7833 | 8905.7833
2020-05-12 | 360 | 7104 | 7464
2020-05-13 | 624.1846 | 7374.8667 | 7999.0513
2020-05-14 | 822.95 | 13171.5 | 13994.45
2020-05-15 | 12144 | 7538.6333 | 19682.6333
2020-05-16 | 1930.7333 | 7836.6283 | 9767.3616
2020-05-17 | 1361.2912 | 8813.466 | 10174.7572
2020-05-18 | 1039.6048 | 7104 | 8143.6048
2020-05-19 | 672 | 7195.7308 | 7867.7308
2020-05-20 | 672 | 7242.5135 | 7914.5135
2020-05-21 | 672 | 7104 | 7776
2020-05-22 | 527.2667 | 7652.55 | 8179.8167
2020-05-23 | 1616.3826 | 7836.6283 | 9453.0109
2020-05-24 | 808.5931 | 9215.9037 | 10024.4967
2020-05-25 | 577.5413 | 7104 | 7681.5413
2020-05-26 | 360 | 129.5455 | 489.5455
2020-05-27 | 5280.0248 | 309.5455 | 5589.5703
2020-05-28 | 3240 | 125.4545 | 3365.4545
2020-05-29 | 3240 | 0 | 3240
2020-05-30 | 3240 | 1875.123 | 5115.123
2020-05-31 | 3468.7452 | 1709.466 | 5178.2112
2020-06-01 | 4207.9526 | 7960.55 | 12168.5026
2020-06-02 | 5552.5002 | 0 | 5552.5002
2020-06-03 | 3836.9336 | 0 | 3836.9336
2020-06-04 | 3095.9336 | 0 | 3095.9336
2020-06-05 | 716.9336 | 0 | 716.9336
2020-06-06 | 716.9336 | 821.3951 | 1538.3286
2020-06-07 | 716.9336 | 2803.2551 | 3520.1887
2020-06-08 | 1494.3893 | 0 | 1494.3893
2020-06-09 | 4924.1667 | 0 | 4924.1667
2020-06-10 | 1246.4944 | 0 | 1246.4944
2020-06-11 | 912.7989 | 5675.9 | 6588.6989
2020-06-12 | 940.7797 | 10128 | 11068.7797
2020-06-13 | 940.7797 | 7750.0451 | 8690.8248
2020-06-14 | 983.6847 | 1639.5051 | 2623.1898
2020-06-15 | 1048.5177 | 6532.95 | 7581.4677
2020-06-16 | 940.7797 | 448.2391 | 1389.0188
2020-06-17 | 940.7797 | 809.3269 | 1750.1066
2020-06-18 | 1219.0297 | 9167.2417 | 10386.2714
2020-06-19 | 940.7797 | 11756.139 | 12696.9187
2020-06-20 | 940.7797 | 3219.7087 | 4160.4884
2020-06-21 | 1068.6423 | 1723.8064 | 2792.4486
2020-06-22 | 2070.1887 | 7687.3528 | 9757.5415
2020-06-23 | 1010.3938 | 13156.2599 | 14166.6536
2020-06-24 | 940.7797 | 13637.3897 | 14578.1694
2020-06-25 | 940.7797 | 10314.2085 | 11254.9882
2020-06-26 | 1013.4985 | 6948.357 | 7961.8555
2020-06-27 | 940.7797 | 700.1332 | 1640.9129
2020-06-28 | 940.7797 | 1633.644 | 2574.4238
2020-06-29 | 9469.6797 | 85.2417 | 9554.9214
2020-06-30 | 6406.5073 | 586.6451 | 6993.1524
2020-07-01 | 3720.2802 | 1110.9836 | 4831.2638
2020-07-02 | 9590.9336 | 127.2 | 9718.1336
2020-07-03 | 4653.9853 | 95.4 | 4749.3853
2020-07-04 | 716.9336 | 700.1332 | 1417.0667
2020-07-05 | 1108.1669 | 1764.348 | 2872.5149
2020-07-06 | 984.9002 | 211.94 | 1196.8402
2020-07-07 | 716.9336 | 220.9091 | 937.8426
2020-07-08 | 2804.3374 | 85.2417 | 2889.5791
2020-07-09 | 8526.1358 | 100.8694 | 8627.0052
2020-07-10 | 7641.9336 | 700.1332 | 8342.0667
2020-07-11 | 2432.1766 | 2259.0107 | 4691.1873
2020-07-12 | 1624.3868 | 0 | 1624.3868
2020-07-13 | 716.9336 | 1128.1515 | 1845.0851
2020-07-14 | 805.4138 | 467.1231 | 1272.5369
2020-07-15 | 716.9336 | 489.5455 | 1206.479
2020-07-16 | 3123.8466 | 315.3539 | 3439.2005
2020-07-17 | 3634.6899 | 778.5867 | 4413.2766
2020-07-18 | 716.9336 | 4056 | 4772.9336
2020-07-19 | 716.9336 | 3979.95 | 4696.8836
2020-07-20 | 1008.9336 | 0 | 1008.9336
2020-07-21 | 716.9336 | 382.5901 | 1099.5236
2020-07-22 | 766.6656 | 434.1696 | 1200.8352
2020-07-23 | 2395.9336 | 1720.4821 | 4116.4156
2020-07-24 | 2741.4669 | 1241.4968 | 3982.9637
2020-07-25 | 716.9336 | 1633.644 | 2350.5776
2020-07-26 | 716.9336 | 0 | 716.9336
2020-07-27 | 757.5057 | 0 | 757.5057
2020-07-28 | 1507.2467 | 599.7417 | 2106.9884
2020-07-29 | 716.9336 | 170.4834 | 887.417
2020-07-30 | 716.9336 | 2031.5 | 2748.4336
2020-07-31 | 716.9336 | 12172.1332 | 12889.0667
2020-08-01 | 716.9336 | 13696.4476 | 14413.3811
2020-08-02 | 716.9336 | 3616.8667 | 4333.8002
2020-08-03 | 874.5093 | 265.8173 | 1140.3266
2020-08-04 | 716.9336 | 288.1346 | 1005.0682
2020-08-05 | 716.9336 | 629.9513 | 1346.8848
2020-08-06 | 716.9336 | 255.9065 | 972.8401
2020-08-07 | 716.9336 | 1353.4897 | 2070.4232
2020-08-08 | 716.9336 | 1633.644 | 2350.5776
2020-08-09 | 1701.9336 | 0 | 1701.9336
2020-08-10 | 716.9336 | 0 | 716.9336
2020-08-11 | 716.9336 | 0 | 716.9336
2020-08-12 | 716.9336 | 0 | 716.9336
2020-08-13 | 876.9336 | 0 | 876.9336
2020-08-14 | 1004.9336 | 0 | 1004.9336
2020-08-15 | 1004.9336 | 700.1332 | 1705.0667
2020-08-16 | 1004.9336 | 1633.644 | 2638.5776
2020-08-17 | 1004.9336 | 85.2417 | 1090.1753
2020-08-18 | 1004.9336 | 1789.2814 | 2794.215
2020-08-19 | 2285.9064 | 996.5197 | 3282.4261
2020-08-20 | 2551.483 | 2901.3937 | 5452.8767
2020-08-21 | 2455.483 | 0 | 2455.483
2020-08-22 | 2455.483 | 8970.2082 | 11425.6912
2020-08-23 | 2489.2811 | 10507.644 | 12996.9251
2020-08-24 | 2455.483 | 4745.125 | 7200.608
2020-08-25 | 2455.483 | 0 | 2455.483
2020-08-26 | 2509.0163 | 0 | 2509.0163
2020-08-27 | 3131.4445 | 0 | 3131.4445
2020-08-28 | 2825.4349 | 0 | 2825.4349
2020-08-29 | 2455.483 | 1545.0851 | 4000.5681
2020-08-30 | 2455.483 | 5286.6992 | 7742.1822
2020-08-31 | 2748.9702 | 3750.9833 | 6499.9535
2020-09-01 | 3006.2883 | 165.1154 | 3171.4036
2020-09-02 | 6729.8694 | 128.4231 | 6858.2925
2020-09-03 | 15717.9444 | 167.6182 | 15885.5626
2020-09-04 | 15597.9444 | 2167.9405 | 17765.8849
2020-09-05 | 5042.0444 | 0 | 5042.0444
2020-09-06 | 2678.2702 | 0 | 2678.2702
2020-09-07 | 431.395 | 0 | 431.395
2020-09-08 | 431.395 | 0 | 431.395
2020-09-09 | 721.4501 | 672.7487 | 1394.1988
2020-09-10 | 431.395 | 3693.9346 | 4125.3296
2020-09-11 | 8955.7283 | 2884.2667 | 11839.995
2020-09-12 | 11903.395 | 1600.867 | 13504.2619
2020-09-13 | 11903.395 | 2634.0396 | 14537.4346
2020-09-14 | 2550.5283 | 113.2833 | 2663.8116
2020-09-15 | 431.395 | 0 | 431.395
2020-09-16 | 706.395 | 0 | 706.395
2020-09-17 | 801.395 | 1205 | 2006.395
2020-09-18 | 431.395 | 7200 | 7631.395
2020-09-19 | 431.395 | 7362.3635 | 7793.7584
2020-09-20 | 431.395 | 7200 | 7631.395
2020-09-21 | 431.395 | 2102.061 | 2533.456
2020-09-22 | 910.6882 | 696.1187 | 1606.8069
2020-09-23 | 431.395 | 472.2977 | 903.6926
2020-09-24 | 504.1222 | 402.7069 | 906.8291
2020-09-25 | 561.0919 | 386.7111 | 947.8031
2020-09-26 | 431.395 | 0 | 431.395
2020-09-27 | 431.395 | 0 | 431.395
2020-09-28 | 463.7616 | 0 | 463.7616
2020-09-29 | 431.395 | 0 | 431.395
2020-09-30 | 431.395 | 0 | 431.395
2020-10-01 | 421.4596 | 2392.6667 | 2814.1263
2020-10-02 | 360 | 0 | 360
2020-10-03 | 360 | 0 | 360
2020-10-04 | 360 | 0 | 360
2020-10-05 | 360 | 0 | 360
2020-10-06 | 105 | 1822.3636 | 1927.3636
2020-10-07 | 0 | 358.6364 | 358.6364
2020-10-08 | 0 | 370.9091 | 370.9091
2020-10-09 | 165.2 | 872.7647 | 1037.9647
2020-10-10 | 0 | 0 | 0
2020-10-11 | 5310.6 | 0 | 5310.6
2020-10-12 | 0 | 1527.8253 | 1527.8253
2020-10-13 | 0 | 11073.3527 | 11073.3527
2020-10-14 | 0 | 11302.7308 | 11302.7308
2020-10-15 | 0 | 10930.203 | 10930.203
2020-10-16 | 1256.7584 | 2980.3636 | 4237.1221
2020-10-17 | 0 | 0 | 0
2020-10-18 | 0 | 0 | 0
2020-10-19 | 0 | 0 | 0
2020-10-20 | 147.9486 | 375.6818 | 523.6304
2020-10-21 | 393.5606 | 245.2912 | 638.8518
2020-10-22 | 0 | 479.5998 | 479.5998
2020-10-23 | 0 | 286.3636 | 286.3636
2020-10-24 | 750.5748 | 3400.9038 | 4151.4786
2020-10-25 | 0 | 4844.6667 | 4844.6667
2020-10-26 | 0 | 3185.65 | 3185.65
2020-10-27 | 0 | 81.8182 | 81.8182
2020-10-28 | 209.1385 | 540.5091 | 749.6476
2020-10-29 | 1268.025 | 289.1 | 1557.125
2020-10-30 | 2875.4438 | 0 | 2875.4438
2020-10-31 | 6421.2187 | 4466.675 | 10887.8937
2020-11-01 | 1644.5 | 13428 | 15072.5
2020-11-02 | 2134.8466 | 13428 | 15562.8466
2020-11-03 | 278.6333 | 13514.2943 | 13792.9277
2020-11-04 | 1920.95 | 3198.8047 | 5119.7547
2020-11-05 | 3154.3903 | 256.4333 | 3410.8236
2020-11-06 | 15462.675 | 3537.7333 | 19000.4083
2020-11-07 | 4889.4423 | 3694.5333 | 8583.9756
2020-11-08 | 0 | 0 | 0
2020-11-09 | 0 | 3229.8485 | 3229.8485
2020-11-10 | 161.85 | 11405.7477 | 11567.5977
2020-11-11 | 312 | 11497.2667 | 11809.2667
2020-11-12 | 774.6667 | 7898.4038 | 8673.0704
2020-11-13 | 14687.0667 | 348.9544 | 15036.0211
2020-11-14 | 17322.2192 | 414.5226 | 17736.7419
2020-11-15 | 12526.4 | 967.2195 | 13493.6195
2020-11-16 | 312 | 0 | 312
2020-11-17 | 678.3 | 451.2948 | 1129.5948
2020-11-18 | 312 | 643.9528 | 955.9528
2020-11-19 | 1209.7154 | 0 | 1209.7154
2020-11-20 | 711.1667 | 143.1 | 854.2667
2020-11-21 | 312 | 730.517 | 1042.517
2020-11-22 | 312 | 974.0226 | 1286.0226
2020-11-23 | 312 | 196.6667 | 508.6667
2020-11-24 | 1476.6352 | 0 | 1476.6352
2020-11-25 | 796.4257 | 100.9038 | 897.3296
2020-11-26 | 1922.1716 | 196.9115 | 2119.0831
2020-11-27 | 407.8054 | 8595.9335 | 9003.7388
2020-11-28 | 312 | 7858.517 | 8170.517
2020-11-29 | 312 | 8832.5396 | 9144.5396
2020-11-30 | 312 | 2117.9667 | 2429.9667
2020-12-01 | 5951.9617 | 220.9091 | 6172.8708
2020-12-02 | 1854.1694 | 6.5423 | 1860.7117
2020-12-03 | 3542.5617 | 86.6241 | 3629.1858
2020-12-04 | 1185.595 | 2732.4863 | 3918.0813
2020-12-05 | 1317.3758 | 5104.6728 | 6422.0485
2020-12-06 | 5677.045 | 5439.0587 | 11116.1037
2020-12-07 | 15393.545 | 0 | 15393.545
2020-12-08 | 22638.713 | 525.0667 | 23163.7796
2020-12-09 | 19079.245 | 824.0667 | 19903.3117
2020-12-10 | 21878.2553 | 2002.3019 | 23880.5572
2020-12-11 | 9597.2423 | 1022.9346 | 10620.177
2020-12-12 | 1376.455 | 12424.9394 | 13801.3945
2020-12-13 | 2084.725 | 5793.1253 | 7877.8503
2020-12-14 | 8825.6595 | 50.5307 | 8876.1902
2020-12-15 | 18886.6739 | 490.87 | 19377.5438
2020-12-16 | 4631.7271 | 538.5132 | 5170.2403
2020-12-17 | 1455.2815 | 446.1142 | 1901.3957
2020-12-18 | 1496.8102 | 7519.7096 | 9016.5199
2020-12-19 | 979.045 | 23920.9394 | 24899.9844
2020-12-20 | 2008.6283 | 24376.6253 | 26385.2537
2020-12-21 | 4995.295 | 1312.1324 | 6307.4275
2020-12-22 | 979.045 | 6341.9141 | 7320.9591
2020-12-23 | 979.045 | 493.7849 | 1472.8299
2020-12-24 | 979.045 | 0 | 979.045
2020-12-25 | 979.045 | 0 | 979.045
2020-12-26 | 3911.8049 | 0 | 3911.8049
2020-12-27 | 2529.1068 | 0 | 2529.1068
2020-12-28 | 2601.17 | 0 | 2601.17
2020-12-29 | 979.045 | 173.2482 | 1152.2932
2020-12-30 | 979.045 | 519.7447 | 1498.7897
2020-12-31 | 1796.3666 | 4437.4865 | 6233.8531
2021-01-01 | 979.045 | 16332.2894 | 17311.3344
2021-01-02 | 979.045 | 16216.2878 | 17195.3328
2021-01-03 | 3063.4465 | 9984 | 13047.4465
2021-01-04 | 3590.954 | 10970 | 14560.954
2021-01-05 | 1803.895 | 18858 | 20661.895
2021-01-06 | 1100.1905 | 14316.5866 | 15416.7771
2021-01-07 | 1430.4191 | 10404.2778 | 11834.6968
2021-01-08 | 979.045 | 8218.6 | 9197.645
2021-01-09 | 979.045 | 760.9394 | 1739.9844
2021-01-10 | 1025.88 | 8311.6935 | 9337.5735
2021-01-11 | 979.045 | 450 | 1429.045
2021-01-12 | 844.9283 | 437.0787 | 1282.007
2021-01-13 | 667.045 | 424.4582 | 1091.5032
2021-01-14 | 1115.92 | 4117.4717 | 5233.3917
2021-01-15 | 667.045 | 8672.8705 | 9339.9155
2021-01-16 | 667.045 | 6628.6894 | 7295.7344
2021-01-17 | 667.045 | 3340.2587 | 4007.3037
2021-01-18 | 4479.9883 | 81.8182 | 4561.8065
2021-01-19 | 4771.045 | 865.9621 | 5637.0071
2021-01-20 | 4771.045 | 591.1579 | 5362.2029
2021-01-21 | 5789.2028 | 2309.875 | 8099.0778
2021-01-22 | 1516.345 | 219.2675 | 1735.6125
2021-01-23 | 667.045 | 4661.1951 | 5328.2401
2021-01-24 | 667.045 | 10772.2526 | 11439.2976
2021-01-25 | 3955.495 | 6168.0864 | 10123.5814
2021-01-26 | 15955.0617 | 801.7682 | 16756.8299
2021-01-27 | 14347.045 | 390.5455 | 14737.5905
2021-01-28 | 14680.545 | 378 | 15058.545
2021-01-29 | 16021.2117 | 307.8 | 16329.0117
2021-01-30 | 14347.045 | 0 | 14347.045
2021-01-31 | 8941.545 | 112.6113 | 9054.1564
2021-02-01 | 667.045 | 1166.6798 | 1833.7248
2021-02-02 | 667.045 | 81 | 748.045
2021-02-03 | 667.045 | 2302.9333 | 2969.9783
2021-02-04 | 667.045 | 16738.3194 | 17405.3644
2021-02-05 | 667.045 | 19756.919 | 20423.964
2021-02-06 | 742.5796 | 5056.9394 | 5799.5191
2021-02-07 | 1069.195 | 6218.6753 | 7287.8703
2021-02-08 | 1179.445 | 602.6333 | 1782.0783
2021-02-09 | 1891.5672 | 0 | 1891.5672
2021-02-10 | 5843.6404 | 0 | 5843.6404
2021-02-11 | 3430.4238 | 0 | 3430.4238
2021-02-12 | 756.4325 | 760.9394 | 1517.3719
2021-02-13 | 994.3177 | 1775.5253 | 2769.8431
2021-02-14 | 994.3177 | 0 | 994.3177
2021-02-15 | 978.4086 | 0 | 978.4086
2021-02-16 | 742.8026 | 0 | 742.8026
2021-02-17 | 2747.4313 | 0 | 2747.4313
2021-02-18 | 1081.5905 | 0 | 1081.5905
2021-02-19 | 1065.9389 | 0 | 1065.9389
2021-02-20 | 885.2268 | 760.9394 | 1646.1663
2021-02-21 | 797.6511 | 1775.5253 | 2573.1764
2021-02-22 | 667.045 | 0 | 667.045
2021-02-23 | 2203.795 | 385.4773 | 2589.2723
2021-02-24 | 709.4181 | 2915.3138 | 3624.7319
2021-02-25 | 667.045 | 808.6667 | 1475.7117
2021-02-26 | 667.045 | 288 | 955.045
2021-02-27 | 667.045 | 1141.4091 | 1808.4542
2021-02-28 | 666.5818 | 2663.288 | 3329.8698
2021-03-01 | 0 | 2957.5 | 2957.5
2021-03-02 | 7977.5833 | 2951.8667 | 10929.45
2021-03-03 | 9936 | 0 | 9936
2021-03-04 | 4140 | 0 | 4140
2021-03-05 | 656.3953 | 0 | 656.3953
2021-03-06 | 1690.1035 | 732.6283 | 2422.7318
2021-03-07 | 0 | 1738.1157 | 1738.1157
2021-03-08 | 2227.9772 | 116.5088 | 2344.486
2021-03-09 | 12746.5833 | 0 | 12746.5833
2021-03-10 | 2880.174 | 0 | 2880.174
2021-03-11 | 1730.0729 | 1571.7 | 3301.7729
2021-03-12 | 1915.0742 | 732.6283 | 2647.7025
2021-03-13 | 1081.2956 | 1709.466 | 2790.7616
2021-03-14 | 0 | 346.6232 | 346.6232
2021-03-15 | 0 | 210.3397 | 210.3397
2021-03-16 | 249.7667 | 535.4103 | 785.1769
2021-03-17 | 0 | 57.2994 | 57.2994
2021-03-18 | 0 | 144.2036 | 144.2036
2021-03-19 | 0 | 85.9491 | 85.9491
2021-03-20 | 0 | 730.517 | 730.517
2021-03-21 | 527.5762 | 1716.9545 | 2244.5307
2021-03-22 | 88.5 | 179.2775 | 267.7775
2021-03-23 | 0 | 217.1988 | 217.1988
2021-03-24 | 0 | 223.2453 | 223.2453
2021-03-25 | 3014.3333 | 83.717 | 3098.0503
2021-03-26 | 5755.775 | 0 | 5755.775
2021-03-27 | 0 | 0 | 0
2021-03-28 | 0 | 173.7219 | 173.7219
2021-03-29 | 0 | 246.106 | 246.106
2021-03-30 | 676 | 722.8552 | 1398.8552
2021-03-31 | 0 | 655.9917 | 655.9917
2021-04-01 | 28.3333 | 2001.9124 | 2030.2458
2021-04-02 | 50 | 0 | 50
2021-04-03 | 516.3636 | 4225 | 4741.3636
2021-04-04 | 6055 | 330 | 6385
2021-04-05 | 3545 | 139.5283 | 3684.5283
2021-04-06 | 60 | 909.7605 | 969.7605
2021-04-07 | 428.6186 | 105.0489 | 533.6676
2021-04-08 | 0 | 85.9491 | 85.9491
2021-04-09 | 0 | 113.1664 | 113.1664
2021-04-10 | 179.1069 | 0 | 179.1069
2021-04-11 | 0 | 71.6243 | 71.6243
2021-04-12 | 500.8879 | 198.1605 | 699.0484
2021-04-13 | 170.5274 | 134.6536 | 305.181
2021-04-14 | 0 | 1119.8819 | 1119.8819
2021-04-15 | 0 | 1535.1756 | 1535.1756
2021-04-16 | 140.4 | 5738.1061 | 5878.5061
2021-04-17 | 0 | 3298.3167 | 3298.3167
2021-04-18 | 0 | 4316.5828 | 4316.5828
2021-04-19 | 0 | 4458.9916 | 4458.9916
2021-04-20 | 5914.1463 | 4179.6713 | 10093.8176
2021-04-21 | 10204.9389 | 4264.6654 | 14469.6043
2021-04-22 | 7024.2 | 7141.6083 | 14165.8083
2021-04-23 | 1425.6 | 14092.274 | 15517.874
2021-04-24 | 12689.7467 | 13992 | 26681.7467
2021-04-25 | 20237.8027 | 5886.7611 | 26124.5638
2021-04-26 | 16851.6 | 4056 | 20907.6
2021-04-27 | 16560 | 4056 | 20616
2021-04-28 | 10545.375 | 4056 | 14601.375
2021-04-29 | 3132 | 6120.8167 | 9252.8167
2021-04-30 | 3132 | 16386.4333 | 19518.4333
2021-05-01 | 3132 | 15612 | 18744
2021-05-02 | 3132 | 13629.825 | 16761.825
2021-05-03 | 3447.3861 | 4056 | 7503.3861
2021-05-04 | 2971.05 | 4520.475 | 7491.525
2021-05-05 | 0 | 11184 | 11184
2021-05-06 | 1458.6024 | 6713.2167 | 8171.819
2021-05-07 | 138.4683 | 20712 | 20850.4683
2021-05-08 | 17.6673 | 21442.517 | 21460.1843
2021-05-09 | 0 | 22473.839 | 22473.839
2021-05-10 | 0 | 18869.6973 | 18869.6973
2021-05-11 | 3459.1852 | 21290.5625 | 24749.7477
2021-05-12 | 4984.609 | 23556.0221 | 28540.6311
2021-05-13 | 5906.6092 | 25857.9289 | 31764.5381
2021-05-14 | 4733.3077 | 13436.1174 | 18169.4251
2021-05-15 | 4733.3077 | 16258.517 | 20991.8247
2021-05-16 | 4733.3077 | 17232.5396 | 21965.8473
2021-05-17 | 5321.6077 | 15528 | 20849.6077
2021-05-18 | 4733.3077 | 15528 | 20261.3077
2021-05-19 | 8348.9077 | 15528 | 23876.9077
2021-05-20 | 5504.0712 | 15528 | 21032.0712
2021-05-21 | 1391.9227 | 15528 | 16919.9227
2021-05-22 | 0 | 16258.517 | 16258.517
2021-05-23 | 0 | 17232.5396 | 17232.5396
2021-05-24 | 0 | 20874 | 20874
2021-05-25 | 167.4667 | 18931.6167 | 19099.0833
2021-05-26 | 0 | 8798.1 | 8798.1
2021-05-27 | 235.4423 | 3727.4 | 3962.8423
2021-05-28 | 2543.925 | 12684.5167 | 15228.4417
2021-05-29 | 752.286 | 4840.667 | 5592.953
2021-05-30 | 1262.1732 | 1704.5396 | 2966.7128
2021-05-31 | 1219.9232 | 0 | 1219.9232
2021-06-01 | 887.5759 | 6561.4 | 7448.9759
2021-06-02 | 404.7368 | 12958.2 | 13362.9368
2021-06-03 | 404.7368 | 5441 | 5845.7368
2021-06-04 | 2901.6689 | 1368.9558 | 4270.6247
2021-06-05 | 1211.2524 | 700.1332 | 1911.3856
2021-06-06 | 854.1122 | 2506.5687 | 3360.6809
2021-06-07 | 404.7368 | 0 | 404.7368
2021-06-08 | 861.2134 | 5700 | 6561.2134
2021-06-09 | 404.7368 | 15149.4115 | 15554.1483
2021-06-10 | 404.7368 | 16381.3334 | 16786.0702
2021-06-11 | 505.2176 | 16430.5273 | 16935.7449
2021-06-12 | 404.7368 | 12959.5457 | 13364.2825
2021-06-13 | 9152.8702 | 8833.644 | 17986.5142
2021-06-14 | 920.8118 | 7200 | 8120.8118
2021-06-15 | 404.7368 | 7200 | 7604.7368
2021-06-16 | 404.7368 | 7362 | 7766.7368
2021-06-17 | 1594.7464 | 7564.5 | 9159.2464
2021-06-18 | 3750.9823 | 7200 | 10950.9823
2021-06-19 | 2630.8966 | 7456.5749 | 10087.4715
2021-06-20 | 3676.7352 | 8995.644 | 12672.3792
2021-06-21 | 5813.2019 | 4735.9463 | 10549.1481
2021-06-22 | 4161.2019 | 6182.3855 | 10343.5873
2021-06-23 | 3222.548 | 7689.9316 | 10912.4796
2021-06-24 | 2484.1019 | 5764.704 | 8248.8058
2021-06-25 | 2309.2019 | 3631.5682 | 5940.77
2021-06-26 | 2309.2019 | 4081.9513 | 6391.1532
2021-06-27 | 2309.2019 | 5015.4622 | 7324.6641
2021-06-28 | 2815.3519 | 2957.1508 | 5772.5026
2021-06-29 | 6996.4615 | 3267.2086 | 10263.6701
2021-06-30 | 3746.7667 | 2857.5857 | 6604.3524
2021-07-01 | 3112.3242 | 2842.9629 | 5955.2871
2021-07-02 | 2309.2019 | 1963.6364 | 4272.8382
2021-07-03 | 2309.2019 | 2663.7695 | 4972.9714
2021-07-04 | 2309.2019 | 3597.2804 | 5906.4823
2021-07-05 | 2309.2019 | 1963.6364 | 4272.8382
2021-07-06 | 2309.2019 | 2493.1997 | 4802.4016
2021-07-07 | 2309.2019 | 1963.6364 | 4272.8382
2021-07-08 | 2309.2019 | 1963.6364 | 4272.8382
2021-07-09 | 2309.2019 | 3186.3364 | 5495.5382
2021-07-10 | 2934.0903 | 10084.1332 | 13018.2235
2021-07-11 | 2737.6769 | 11799.394 | 14537.0709
2021-07-12 | 2695.6019 | 3186.65 | 5882.2519
2021-07-13 | 2309.2019 | 213.1043 | 2522.3061
2021-07-14 | 2309.2019 | 527.6013 | 2836.8031
2021-07-15 | 19368.5889 | 24.75 | 19393.3389
2021-07-16 | 8077.4852 | 0 | 8077.4852
2021-07-17 | 5429.2019 | 8951.7207 | 14380.9225
2021-07-18 | 5633.8172 | 7481.8565 | 13115.6738
2021-07-19 | 5489.7685 | 0 | 5489.7685
2021-07-20 | 5245.0852 | 0 | 5245.0852
2021-07-21 | 5981.2019 | 0 | 5981.2019
2021-07-22 | 6050.1019 | 170.4834 | 6220.5853
2021-07-23 | 4867.5352 | 426.2085 | 5293.7437
2021-07-24 | 2983.1019 | 700.1332 | 3683.235
2021-07-25 | 2861.2019 | 1633.644 | 4494.8459
2021-07-26 | 2471.3519 | 136.3636 | 2607.7155
2021-07-27 | 3717.7982 | 381.8182 | 4099.6164
2021-07-28 | 10429.8392 | 285 | 10714.8392
2021-07-29 | 10468.1659 | 0 | 10468.1659
2021-07-30 | 11130.1927 | 0 | 11130.1927
2021-07-31 | 7356.8947 | 7422.9327 | 14779.8274
2021-08-01 | 2309.2019 | 7655.4693 | 9964.6712
2021-08-02 | 2309.2019 | 5659.6364 | 7968.8382
2021-08-03 | 2309.2019 | 10630.631 | 12939.8328
2021-08-04 | 3646.739 | 7755.9234 | 11402.6624
2021-08-05 | 2309.2019 | 7177.7243 | 9486.9262
2021-08-06 | 9478.0019 | 8442.55 | 17920.5519
2021-08-07 | 3050.8019 | 8280.7723 | 11331.5742
2021-08-08 | 10192.6352 | 8761.644 | 18954.2792
2021-08-09 | 2309.2019 | 7862.8667 | 10172.0685
2021-08-10 | 2309.2019 | 5677.65 | 7986.8519
2021-08-11 | 4254.356 | 0 | 4254.356
2021-08-12 | 3876.4031 | 0 | 3876.4031
2021-08-13 | 8910.8077 | 0 | 8910.8077
2021-08-14 | 2969.6345 | 700.1332 | 3669.7677
2021-08-15 | 2538.2928 | 1804.1275 | 4342.4202
2021-08-16 | 2309.2019 | 223.0491 | 2532.251
2021-08-17 | 2461.2162 | 4427.2142 | 6888.4304
2021-08-18 | 3335.0365 | 519.3585 | 3854.395
2021-08-19 | 2565.3492 | 0 | 2565.3492
2021-08-20 | 2309.2019 | 0 | 2309.2019
2021-08-21 | 2362.1321 | 700.1332 | 3062.2653
2021-08-22 | 2976.3837 | 1633.644 | 4610.0277
2021-08-23 | 3941.0557 | 1377 | 5318.0557
2021-08-24 | 2523.9543 | 1944 | 4467.9543
2021-08-25 | 2488.9783 | 1944 | 4432.9783
2021-08-26 | 3654.8372 | 1944 | 5598.8372
2021-08-27 | 2420.3477 | 1053 | 3473.3477
2021-08-28 | 2451.8701 | 700.1332 | 3152.0033
2021-08-29 | 13853.8954 | 1633.644 | 15487.5395
2021-08-30 | 8237.5752 | 0 | 8237.5752
2021-08-31 | 3905.7662 | 0 | 3905.7662
2021-09-01 | 1016.5386 | 4307.3561 | 5323.8947
2021-09-02 | 71.395 | 231.8182 | 303.2131
2021-09-03 | 71.395 | 4338.252 | 4409.647
2021-09-04 | 71.395 | 1197.2759 | 1268.6709
2021-09-05 | 71.395 | 1714.3925 | 1785.7874
2021-09-06 | 71.395 | 0 | 71.395
2021-09-07 | 71.395 | 0 | 71.395
2021-09-08 | 71.395 | 0 | 71.395
2021-09-09 | 71.395 | 2339.5788 | 2410.9737
2021-09-10 | 71.395 | 300 | 371.395
2021-09-11 | 71.395 | 730.517 | 801.9119
2021-09-12 | 181.0663 | 1704.5396 | 1885.606
2021-09-13 | 82.2876 | 947.9333 | 1030.2209
2021-09-14 | 2867.7696 | 979.803 | 3847.5726
2021-09-15 | 180.6325 | 1069.8826 | 1250.5151
2021-09-16 | 130.2152 | 1720.0364 | 1850.2515
2021-09-17 | 71.395 | 2117.2221 | 2188.6171
2021-09-18 | 10826.395 | 2191.5509 | 13017.9459
2021-09-19 | 8505.0054 | 0 | 8505.0054
2021-09-20 | 71.395 | 0 | 71.395
2021-09-21 | 71.395 | 359.7917 | 431.1866
2021-09-22 | 859.195 | 9420 | 10279.195
2021-09-23 | 1349.6271 | 9420 | 10769.6271
2021-09-24 | 8495.4395 | 4108.1667 | 12603.6061
2021-09-25 | 71.395 | 730.517 | 801.9119
2021-09-26 | 1333.695 | 1704.5396 | 3038.2346
2021-09-27 | 71.395 | 81.8182 | 153.2131
2021-09-28 | 71.395 | 185.4545 | 256.8495
2021-09-29 | 322.7586 | 0 | 322.7586
2021-09-30 | 196.7999 | 0 | 196.7999
2021-10-01 | 23.8532 | 0 | 23.8532
2021-10-02 | 620.1827 | 730.517 | 1350.6997
2021-10-03 | 0 | 1704.5396 | 1704.5396
2021-10-04 | 0 | 0 | 0
2021-10-05 | 0 | 0 | 0
2021-10-06 | 323.6667 | 0 | 323.6667
2021-10-07 | 2619.2121 | 283.2 | 2902.4121
2021-10-08 | 116.7067 | 243.5057 | 360.2124
2021-10-09 | 0 | 2325.914 | 2325.914
2021-10-10 | 579.6484 | 1876.3578 | 2456.0062
2021-10-11 | 1137.1163 | 0 | 1137.1163
2021-10-12 | 0 | 0 | 0
2021-10-13 | 5151.6261 | 0 | 5151.6261
2021-10-14 | 15966.2455 | 0 | 15966.2455
2021-10-15 | 9118.9773 | 0 | 9118.9773
2021-10-16 | 2.55 | 730.517 | 733.067
2021-10-17 | 0 | 1704.5396 | 1704.5396
2021-10-18 | 0 | 3812.7167 | 3812.7167
2021-10-19 | 582.75 | 12573.3667 | 13156.1167
2021-10-20 | 0 | 4068.3 | 4068.3
2021-10-21 | 0 | 3768 | 3768
2021-10-22 | 0 | 9168 | 9168
2021-10-23 | 0 | 7930.517 | 7930.517
2021-10-24 | 0 | 3103.9146 | 3103.9146
2021-10-25 | 0 | 0 | 0
2021-10-26 | 0 | 663.2617 | 663.2617
2021-10-27 | 0 | 1060.047 | 1060.047
2021-10-28 | 0 | 0 | 0
2021-10-29 | 0 | 0 | 0
2021-10-30 | 0 | 730.517 | 730.517
2021-10-31 | 2742.3125 | 2191.5509 | 4933.8634
2021-11-01 | 8874 | 0 | 8874
2021-11-02 | 18674.4583 | 0 | 18674.4583
2021-11-03 | 5876.2308 | 0 | 5876.2308
2021-11-04 | 3316.2387 | 0 | 3316.2387
2021-11-05 | 4299.6967 | 732.6283 | 5032.325
2021-11-06 | 5161.4986 | 1709.466 | 6870.9646
2021-11-07 | 5327.4972 | 0 | 5327.4972
2021-11-08 | 5187.0967 | 163.6364 | 5350.733
2021-11-09 | 1120.3002 | 3373.9091 | 4494.2093
2021-11-10 | 925.4038 | 4315.3636 | 5240.7674
2021-11-11 | 887.4 | 4202.1818 | 5089.5818
2021-11-12 | 887.4 | 3864 | 4751.4
2021-11-13 | 887.4 | 1687.8167 | 2575.2167
2021-11-14 | 887.4 | 321.0577 | 1208.4577
2021-11-15 | 909.553 | 0 | 909.553
2021-11-16 | 887.4 | 0 | 887.4
2021-11-17 | 1687.4 | 766.3783 | 2453.7783
2021-11-18 | 8182.4094 | 1465.2566 | 9647.666
2021-11-19 | 8087.4 | 0 | 8087.4
2021-11-20 | 1640.4774 | 0 | 1640.4774
2021-11-21 | 887.4 | 4267.2656 | 5154.6656
2021-11-22 | 887.4 | 12561.4982 | 13448.8982
2021-11-23 | 1861.6061 | 7252.2182 | 9113.8244
2021-11-24 | 5025.2152 | 334.8 | 5360.0152
2021-11-25 | 64.7062 | 8226.9375 | 8291.6438
2021-11-26 | 1135.1366 | 8874 | 10009.1366
2021-11-27 | 0 | 9606.6283 | 9606.6283
2021-11-28 | 0 | 3693.791 | 3693.791
2021-11-29 | 3890.2599 | 0 | 3890.2599
2021-11-30 | 7437.0018 | 6544.1274 | 13981.1292
2021-12-01 | 4157.3365 | 3002.1333 | 7159.4698
2021-12-02 | 0 | 1100.7667 | 1100.7667
2021-12-03 | 0 | 1684.8 | 1684.8
2021-12-04 | 3675.8423 | 8877.1394 | 12552.9817
2021-12-05 | 2446.4018 | 1775.5253 | 4221.9271
2021-12-06 | 4585.5618 | 11028.0676 | 15613.6294
2021-12-07 | 5064.3864 | 10807.2877 | 15871.6741
2021-12-08 | 4498.3333 | 3670.7686 | 8169.1019
2021-12-09 | 4252.843 | 7555.1333 | 11807.9763
2021-12-10 | 8488.7571 | 11938 | 20426.7571
2021-12-11 | 10309.7143 | 12497.1394 | 22806.8537
2021-12-12 | 8472.2143 | 11759.5253 | 20231.7396
2021-12-13 | 6357.3472 | 17104 | 23461.3472
2021-12-14 | 6130.8515 | 23637.7909 | 29768.6424
2021-12-15 | 6109.7143 | 19382.6697 | 25492.384
2021-12-16 | 6109.7143 | 11423.3455 | 17533.0597
2021-12-17 | 6214.8506 | 17409.3955 | 23624.2461
2021-12-18 | 3203.3571 | 12111.5144 | 15314.8716
2021-12-19 | 159.6212 | 12266.8183 | 12426.4395
2021-12-20 | 1408.6304 | 9984 | 11392.6304
2021-12-21 | 854.7459 | 5435.7333 | 6290.4793
2021-12-22 | 327.2727 | 453.15 | 780.4227
2021-12-23 | 302.9545 | 535 | 837.9545
2021-12-24 | 0 | 4305 | 4305
2021-12-25 | 0 | 760.9394 | 760.9394
2021-12-26 | 0 | 1775.5253 | 1775.5253
2021-12-27 | 0 | 86.6241 | 86.6241
2021-12-28 | 0 | 542.8444 | 542.8444
2021-12-29 | 0 | 1371.6324 | 1371.6324
2021-12-30 | 3059 | 3616.0394 | 6675.0394
2021-12-31 | 0 | 8196 | 8196
2022-01-01 | 0 | 3517.45 | 3517.45
2022-01-02 | 3497.0778 | 1666 | 5163.0778
2022-01-03 | 8741.7385 | 11464.5 | 20206.2385
2022-01-04 | 5984 | 12800.8589 | 18784.8589
2022-01-05 | 5103.0222 | 12094.0165 | 17197.0388
2022-01-06 | 567.3863 | 737.8 | 1305.1863
2022-01-07 | 22.1537 | 0 | 22.1537
2022-01-08 | 0 | 760.9394 | 760.9394
2022-01-09 | 294.12 | 1775.5253 | 2069.6453
2022-01-10 | 4845.4961 | 0 | 4845.4961
2022-01-11 | 224.3077 | 0 | 224.3077
2022-01-12 | 0 | 3471.9167 | 3471.9167
2022-01-13 | 436.8186 | 8196 | 8632.8186
2022-01-14 | 3915.8667 | 4462.2667 | 8378.1333
2022-01-15 | 0 | 17482.5228 | 17482.5228
2022-01-16 | 0 | 18167.5253 | 18167.5253
2022-01-17 | 1890.6833 | 7467.4667 | 9358.15
2022-01-18 | 2451 | 6698 | 9149
2022-01-19 | 0 | 7392.9314 | 7392.9314
2022-01-20 | 1402.6885 | 0 | 1402.6885
2022-01-21 | 1252.4265 | 0 | 1252.4265
2022-01-22 | 0 | 0 | 0
2022-01-23 | 97.9357 | 0 | 97.9357
2022-01-24 | 0 | 81.8182 | 81.8182
2022-01-25 | 0 | 486.8182 | 486.8182
2022-01-26 | 165 | 529.0909 | 694.0909
2022-01-27 | 2225.5333 | 252.2727 | 2477.8061
2022-01-28 | 0 | 0 | 0
2022-01-29 | 254.2385 | 1014.5859 | 1268.8244
2022-01-30 | 0 | 2449.1853 | 2449.1853
2022-01-31 | 182.25 | 422.7273 | 604.9773
2022-02-01 | 977.4 | 469.6364 | 1447.0364
2022-02-02 | 95.85 | 454.95 | 550.8
2022-02-03 | 1081.6 | 643.95 | 1725.55
2022-02-04 | 6356.6094 | 363.15 | 6719.7594
2022-02-05 | 0 | 760.9394 | 760.9394
2022-02-06 | 0 | 2110.99 | 2110.99
2022-02-07 | 0 | 431.4545 | 431.4545
2022-02-08 | 0 | 603.45 | 603.45
2022-02-09 | 0 | 941.625 | 941.625
2022-02-10 | 478.1 | 0 | 478.1
2022-02-11 | 0 | 1130.824 | 1130.824
2022-02-12 | 0 | 1218.9122 | 1218.9122
2022-02-13 | 0 | 1775.5253 | 1775.5253
2022-02-14 | 4664.1125 | 0 | 4664.1125
2022-02-15 | 13680 | 4183.375 | 17863.375
2022-02-16 | 13680 | 9280.3333 | 22960.3333
2022-02-17 | 6572.25 | 7955.6333 | 14527.8833
2022-02-18 | 0 | 332.8 | 332.8
2022-02-19 | 3434.91 | 7067.3147 | 10502.2247
2022-02-20 | 14714.2295 | 317.0581 | 15031.2876
2022-02-21 | 16189.3 | 0 | 16189.3
2022-02-22 | 7128 | 4959.25 | 12087.25
2022-02-23 | 7247.4429 | 1015 | 8262.4429
2022-02-24 | 7570.1538 | 0 | 7570.1538
2022-02-25 | 7306.9923 | 0 | 7306.9923
2022-02-26 | 7803.3006 | 0 | 7803.3006
2022-02-27 | 6513.5679 | 0 | 6513.5679
2022-02-28 | 0 | 0 | 0
2022-03-01 | 0 | 0 | 0
2022-03-02 | 0 | 81 | 81
2022-03-03 | 0 | 403.65 | 403.65
2022-03-04 | 215.9578 | 0 | 215.9578
2022-03-05 | 1018.4667 | 395.4545 | 1413.9212
2022-03-06 | 240.7333 | 0 | 240.7333
2022-03-07 | 0 | 0 | 0
2022-03-08 | 0 | 0 | 0
2022-03-09 | 0 | 496.3333 | 496.3333
2022-03-10 | 0 | 2025.3417 | 2025.3417
2022-03-11 | 0 | 0 | 0
2022-03-12 | 0 | 0 | 0
2022-03-13 | 0 | 0 | 0
2022-03-14 | 0 | 0 | 0
2022-03-15 | 361.9206 | 1295.6667 | 1657.5873
2022-03-16 | 0 | 372.7364 | 372.7364
2022-03-17 | 129.2381 | 482.8712 | 612.1093
2022-03-18 | 967.5358 | 1275 | 2242.5358
2022-03-19 | 28.4091 | 5530 | 5558.4091
2022-03-20 | 1424.2424 | 0 | 1424.2424
2022-03-21 | 0 | 0 | 0
2022-03-22 | 0 | 0 | 0
2022-03-23 | 145.5333 | 66.8667 | 212.4
2022-03-24 | 0 | 270 | 270
2022-03-25 | 0 | 866.91 | 866.91
2022-03-26 | 0 | 0 | 0
2022-03-27 | 0 | 0 | 0
2022-03-28 | 0 | 0 | 0
2022-03-29 | 0 | 7898.9673 | 7898.9673
2022-03-30 | 0 | 10471.6425 | 10471.6425
2022-03-31 | 0 | 10261.7286 | 10261.7286
2022-04-01 | 440.5477 | 9749.7 | 10190.2477
2022-04-02 | 0 | 0 | 0
2022-04-03 | 9.325 | 2377.875 | 2387.2
2022-04-04 | 0 | 13428 | 13428
2022-04-05 | 0 | 14299.5062 | 14299.5062
2022-04-06 | 249.7667 | 13891.2584 | 14141.025
2022-04-07 | 90.4667 | 11153.3314 | 11243.798
2022-04-08 | 896.7709 | 2767.0867 | 3663.8577
2022-04-09 | 0 | 4056 | 4056
2022-04-10 | 2015.4983 | 2078.7 | 4094.1983
2022-04-11 | 3816.8164 | 0 | 3816.8164
2022-04-12 | 347.445 | 0 | 347.445
2022-04-13 | 654.85 | 481.8333 | 1136.6833
2022-04-14 | 4317.6 | 971.7219 | 5289.3219
2022-04-15 | 4603.8 | 424.171 | 5027.971
2022-04-16 | 4032.0583 | 730.517 | 4762.5753
2022-04-17 | 626.4 | 1447.2002 | 2073.6002
2022-04-18 | 1245.8167 | 354.6822 | 1600.4989
2022-04-19 | 626.4 | 173.7219 | 800.1219
2022-04-20 | 11611.2462 | 86.8609 | 11698.1072
2022-04-21 | 6966.6841 | 3107.2917 | 10073.9758
2022-04-22 | 1340.0264 | 9420 | 10760.0264
2022-04-23 | 1125.4909 | 1735.2336 | 2860.7246
2022-04-24 | 1437.7636 | 13260.5396 | 14698.3033
2022-04-25 | 2067.599 | 12629.8 | 14697.399
2022-04-26 | 2733.2957 | 14388 | 17121.2957
2022-04-27 | 626.4 | 11960.725 | 12587.125
2022-04-28 | 626.4 | 1408.1333 | 2034.5333
2022-04-29 | 626.4 | 0 | 626.4
2022-04-30 | 6766.2333 | 0 | 6766.2333
2022-05-01 | 16769.5333 | 0 | 16769.5333
2022-05-02 | 14332.7359 | 8015.4546 | 22348.1905
2022-05-03 | 21408 | 9296.6619 | 30704.6619
2022-05-04 | 17261.1 | 10152.618 | 27413.718
2022-05-05 | 11790.9356 | 9751.3163 | 21542.2519
2022-05-06 | 11472 | 10350.92 | 21822.92
2022-05-07 | 11472 | 16656 | 28128
2022-05-08 | 11472 | 18770.9393 | 30242.9393
2022-05-09 | 11472 | 12597.492 | 24069.492
2022-05-10 | 11472 | 8339.7793 | 19811.7793
2022-05-11 | 16295.4577 | 8339.7793 | 24635.237
2022-05-12 | 23157.358 | 8339.7793 | 31497.1373
2022-05-13 | 12092.5686 | 8649.4397 | 20742.0083
2022-05-14 | 11472 | 10065.7841 | 21537.7841
2022-05-15 | 11472 | 8339.7793 | 19811.7793
2022-05-16 | 11472 | 9040.8018 | 20512.8018
2022-05-17 | 12176.9917 | 8413.164 | 20590.1556
2022-05-18 | 3943.5 | 8635.1066 | 12578.6066
2022-05-19 | 0 | 8568.8703 | 8568.8703
2022-05-20 | 1025.2667 | 8109.1495 | 9134.4162
2022-05-21 | 3127.4173 | 5933.4074 | 9060.8246
2022-05-22 | 4204.6388 | 1709.466 | 5914.1048
2022-05-23 | 3937.4438 | 2695.1667 | 6632.6105
2022-05-24 | 5018.101 | 13207.9667 | 18226.0677
2022-05-25 | 0 | 23564.5833 | 23564.5833
2022-05-26 | 0 | 20421.3833 | 20421.3833
2022-05-27 | 5400.45 | 19264.8167 | 24665.2667
2022-05-28 | 7128 | 16656 | 23784
2022-05-29 | 7128 | 16656 | 23784
2022-05-30 | 7128 | 16656 | 23784
2022-05-31 | 19955.4333 | 3828.5667 | 23784
2022-06-01 | 17569.6198 | 0 | 17569.6198
2022-06-02 | 10215.9556 | 11916 | 22131.9556
2022-06-03 | 7128 | 15888 | 23016
2022-06-04 | 7128 | 16548.0653 | 23676.0653
2022-06-05 | 1039.5 | 17428.1524 | 18467.6524
2022-06-06 | 12.285 | 15973.2417 | 15985.5267
2022-06-07 | 0 | 16207.6564 | 16207.6564
2022-06-08 | 954.3638 | 14369.9126 | 15324.2764
2022-06-09 | 7885.1556 | 1585.7377 | 9470.8933
2022-06-10 | 8118.5719 | 0 | 8118.5719
2022-06-11 | 7885.1556 | 0 | 7885.1556
2022-06-12 | 7885.1556 | 0 | 7885.1556
2022-06-13 | 7885.1556 | 0 | 7885.1556
2022-06-14 | 7885.1556 | 0 | 7885.1556
2022-06-15 | 7885.1556 | 0 | 7885.1556
2022-06-16 | 7885.1556 | 0 | 7885.1556
2022-06-17 | 7885.1556 | 845.0153 | 8730.1709
2022-06-18 | 7885.1556 | 1540.1524 | 9425.3079
2022-06-19 | 7885.1556 | 3388.3333 | 11273.4889
2022-06-20 | 7885.1556 | 11400 | 19285.1556
2022-06-21 | 11368.4889 | 643.0833 | 12011.5722
2022-06-22 | 9048.3688 | 241.65 | 9290.0188
2022-06-23 | 7102.1158 | 1703.7667 | 8805.8825
2022-06-24 | 0 | 16455 | 16455
2022-06-25 | 0 | 15888 | 15888
2022-06-26 | 0 | 15888 | 15888
2022-06-27 | 0 | 15973.2417 | 15973.2417
2022-06-28 | 0 | 16310.1683 | 16310.1683
2022-06-29 | 0 | 15888 | 15888
2022-06-30 | 0 | 15973.2417 | 15973.2417
2022-07-01 | 3666.3663 | 16192.0288 | 19858.395
2022-07-02 | 5265.3155 | 6807.5667 | 12072.8821
2022-07-03 | 3480.2552 | 0 | 3480.2552
2022-07-04 | 3480.2552 | 0 | 3480.2552
2022-07-05 | 3480.2552 | 85.2417 | 3565.4969
2022-07-06 | 4171.9719 | 637.8051 | 4809.7769
2022-07-07 | 3480.2552 | 2476.3501 | 5956.6053
2022-07-08 | 3979.9917 | 46.8829 | 4026.8746
2022-07-09 | 4293.7797 | 0 | 4293.7797
2022-07-10 | 3480.2552 | 0 | 3480.2552
2022-07-11 | 4388.0885 | 269.7609 | 4657.8495
2022-07-12 | 6600.2552 | 1899.1629 | 8499.4181
2022-07-13 | 5152.9219 | 9888 | 15040.9219
2022-07-14 | 3480.2552 | 7876.0667 | 11356.3219
2022-07-15 | 3480.2552 | 292.9167 | 3773.1719
2022-07-16 | 3480.2552 | 8850.8333 | 12331.0885
2022-07-17 | 3839.0116 | 0 | 3839.0116
2022-07-18 | 3480.2552 | 1228.15 | 4708.4052
2022-07-19 | 1666.1957 | 0 | 1666.1957
2022-07-20 | 791.8532 | 508.2 | 1300.0532
2022-07-21 | 1911.5066 | 195.5868 | 2107.0934
2022-07-22 | 47.6066 | 0 | 47.6066
2022-07-23 | 47.6066 | 0 | 47.6066
2022-07-24 | 8366.9816 | 0 | 8366.9816
2022-07-25 | 11540.3805 | 0 | 11540.3805
2022-07-26 | 8200.7927 | 205.1923 | 8405.985
2022-07-27 | 2556.3254 | 0 | 2556.3254
2022-07-28 | 843.383 | 0 | 843.383
2022-07-29 | 265.4066 | 2817.3333 | 3082.7399
2022-07-30 | 393.5205 | 1026.7665 | 1420.287
2022-07-31 | 3576.4094 | 1633.644 | 5210.0535
2022-08-01 | 1262.2954 | 95.9135 | 1358.2089
2022-08-02 | 1950.3454 | 910 | 2860.3454
2022-08-03 | 4420.3954 | 0 | 4420.3954
2022-08-04 | 1262.2954 | 712.2532 | 1974.5486
2022-08-05 | 2328.1593 | 929.9962 | 3258.1555
2022-08-06 | 1292.7681 | 3163.6974 | 4456.4655
2022-08-07 | 47.6066 | 0 | 47.6066
2022-08-08 | 1496.6389 | 0 | 1496.6389
2022-08-09 | 1648.6938 | 0 | 1648.6938
2022-08-10 | 47.6066 | 462.3333 | 509.9399
2022-08-11 | 47.6066 | 2139.6048 | 2187.2113
2022-08-12 | 47.6066 | 3619.9 | 3667.5066
2022-08-13 | 47.6066 | 7690.5766 | 7738.1831
2022-08-14 | 47.6066 | 7955.7689 | 8003.3754
2022-08-15 | 185.4066 | 5976.0038 | 6161.4103
2022-08-16 | 47.6066 | 307.8 | 355.4066
2022-08-17 | 47.6066 | 929.5333 | 977.1399
2022-08-18 | 47.6066 | 1743.8167 | 1791.4232
2022-08-19 | 639.1066 | 290.4 | 929.5066
2022-08-20 | 47.6066 | 12279.3 | 12326.9066
2022-08-21 | 47.6066 | 13176 | 13223.6066
2022-08-22 | 47.6066 | 9250.65 | 9298.2566
2022-08-23 | 47.6066 | 6373.8675 | 6421.474
2022-08-24 | 865.7895 | 2334.7885 | 3200.578
2022-08-25 | 7198.3508 | 2381.3207 | 9579.6715
2022-08-26 | 8003.3754 | 2281.8721 | 10285.2475
2022-08-27 | 8003.3754 | 1963.6364 | 9967.0118
2022-08-28 | 8003.3754 | 2044.6364 | 10048.0118
2022-08-29 | 8181.0088 | 353.7 | 8534.7088
2022-08-30 | 8003.3754 | 271.35 | 8274.7254
2022-08-31 | 11441.0421 | 522.9551 | 11963.9972
2022-09-01 | 8397.8288 | 0 | 8397.8288
2022-09-02 | 10980.7846 | 0 | 10980.7846
2022-09-03 | 4843.3846 | 0 | 4843.3846
2022-09-04 | 4843.3846 | 0 | 4843.3846
2022-09-05 | 2973.3 | 0 | 2973.3
2022-09-06 | 0 | 0 | 0
2022-09-07 | 0 | 0 | 0
2022-09-08 | 0 | 2863.5 | 2863.5
2022-09-09 | 0 | 201.4963 | 201.4963
2022-09-10 | 0 | 8421.4034 | 8421.4034
2022-09-11 | 0 | 8339.7793 | 8339.7793
2022-09-12 | 3027.6791 | 4928.5037 | 7956.1829
2022-09-13 | 381.6 | 3435.8229 | 3817.4229
2022-09-14 | 0 | 5506.5833 | 5506.5833
2022-09-15 | 0 | 4894.6497 | 4894.6497
2022-09-16 | 0 | 1239.3333 | 1239.3333
2022-09-17 | 0 | 0 | 0
2022-09-18 | 0 | 0 | 0
2022-09-19 | 4395.7587 | 0 | 4395.7587
2022-09-20 | 8339.7793 | 0 | 8339.7793
2022-09-21 | 8339.7793 | 0 | 8339.7793
2022-09-22 | 4882.2458 | 3599.7162 | 8481.962
2022-09-23 | 271.575 | 9719.1054 | 9990.6804
2022-09-24 | 0 | 1472.7273 | 1472.7273
2022-09-25 | 0 | 0 | 0
2022-09-26 | 5451 | 0 | 5451
2022-09-27 | 10022.4 | 0 | 10022.4
2022-09-28 | 7672.8 | 0 | 7672.8
2022-09-29 | 0 | 1118.2167 | 1118.2167
2022-09-30 | 0 | 0 | 0
2022-10-01 | 0 | 0 | 0
2022-10-02 | 0 | 0 | 0
2022-10-03 | 118.7618 | 0 | 118.7618
2022-10-04 | 0 | 0 | 0
2022-10-05 | 0 | 1991.3833 | 1991.3833
2022-10-06 | 0 | 0 | 0
2022-10-07 | 4425 | 5826 | 10251
2022-10-08 | 6200 | 12652 | 18852
2022-10-09 | 0 | 14968 | 14968
2022-10-10 | 0 | 1940 | 1940
2022-10-11 | 232.9545 | 0 | 232.9545
2022-10-12 | 0 | 783.5792 | 783.5792
2022-10-13 | 270.4 | 114.0667 | 384.4667
2022-10-14 | 1523.0216 | 0 | 1523.0216
2022-10-15 | 2301.3128 | 1300.5 | 3601.8128
2022-10-16 | 2432.6925 | 1836 | 4268.6925
2022-10-17 | 2301.3128 | 1889.2038 | 4190.5167
2022-10-18 | 5127.3128 | 1836 | 6963.3128
2022-10-19 | 6069.3128 | 1836 | 7905.3128
2022-10-20 | 6759.3628 | 1926.8135 | 8686.1763
2022-10-21 | 17698.7904 | 1836 | 19534.7904
2022-10-22 | 19716.4503 | 1836 | 21552.4503
2022-10-23 | 15920.1489 | 1836 | 17756.1489
2022-10-24 | 5542.7415 | 1836 | 7378.7415
2022-10-25 | 5482.5581 | 1836 | 7318.5581
2022-10-26 | 5482.5581 | 2184.3679 | 7666.9261
2022-10-27 | 5157.806 | 5807.5 | 10965.306
2022-10-28 | 2301.3128 | 178.5 | 2479.8128
2022-10-29 | 2301.3128 | 3056.3167 | 5357.6295
2022-10-30 | 2301.3128 | 3864 | 6165.3128
2022-10-31 | 2301.3128 | 3864 | 6165.3128
2022-11-01 | 2330.5628 | 117.6 | 2448.1628
2022-11-02 | 2301.3128 | 92.4 | 2393.7128
2022-11-03 | 2301.3128 | 0 | 2301.3128
2022-11-04 | 2301.3128 | 0 | 2301.3128
2022-11-05 | 2301.3128 | 2526.5006 | 4827.8135
2022-11-06 | 862.9923 | 3834.4833 | 4697.4756
2022-11-07 | 0 | 3945 | 3945
2022-11-08 | 0 | 4052.9308 | 4052.9308
2022-11-09 | 0 | 3156.2833 | 3156.2833
2022-11-10 | 124.875 | 94.4827 | 219.3577
2022-11-11 | 0 | 730.517 | 730.517
2022-11-12 | 1478.75 | 1704.5396 | 3183.2896
2022-11-13 | 4164 | 0 | 4164
2022-11-14 | 2565.9833 | 305.8191 | 2871.8024
2022-11-15 | 3502.063 | 286.3636 | 3788.4266
2022-11-16 | 0 | 0 | 0
2022-11-17 | 0 | 0 | 0
2022-11-18 | 0 | 0 | 0
2022-11-19 | 1560.4175 | 0 | 1560.4175
2022-11-20 | 155.8758 | 0 | 155.8758
2022-11-21 | 3620.925 | 0 | 3620.925
2022-11-22 | 4694.8455 | 1506.4394 | 6201.2849
2022-11-23 | 3887.8437 | 730.517 | 4618.3606
2022-11-24 | 0 | 1704.5396 | 1704.5396
2022-11-25 | 0 | 0 | 0
2022-11-26 | 342.4909 | 0 | 342.4909
2022-11-27 | 0 | 0 | 0
2022-11-28 | 0 | 11837.108 | 11837.108
2022-11-29 | 0 | 14240.6443 | 14240.6443
2022-11-30 | 0 | 17296.0658 | 17296.0658
2022-12-01 | 716.1844 | 13094.9333 | 13811.1178
2022-12-02 | 119.4533 | 14369.0063 | 14488.4596
2022-12-03 | 3008.2 | 17419.6146 | 20427.8146
2022-12-04 | 3312 | 11472 | 14784
2022-12-05 | 3388.9373 | 848.7697 | 4237.707
2022-12-06 | 3644.5365 | 8644.5826 | 12289.1191
2022-12-07 | 3312 | 28389.9697 | 31701.9697
2022-12-08 | 3312 | 15629.4221 | 18941.4221
2022-12-09 | 3312 | 5984.4182 | 9296.4182
2022-12-10 | 3312 | 1396.5 | 4708.5
2022-12-11 | 3312 | 0 | 3312
2022-12-12 | 3312 | 4860.05 | 8172.05
2022-12-13 | 5884.6333 | 7895.8091 | 13780.4424
2022-12-14 | 3312 | 8464.3726 | 11776.3726
2022-12-15 | 3312 | 8312.5 | 11624.5
2022-12-16 | 3312 | 7571.7333 | 10883.7333
2022-12-17 | 3312 | 5963.3563 | 9275.3563
2022-12-18 | 3312 | 1613.7479 | 4925.7479
2022-12-19 | 3312 | 29.8769 | 3341.8769
2022-12-20 | 3312 | 3566.2604 | 6878.2604
2022-12-21 | 4581.2417 | 4281.684 | 8862.9257
2022-12-22 | 6888.4127 | 426.9888 | 7315.4014
2022-12-23 | 27074.652 | 0 | 27074.652
2022-12-24 | 31890.5164 | 92.4317 | 31982.9481
2022-12-25 | 23989.7828 | 0 | 23989.7828
2022-12-26 | 23274.8879 | 0 | 23274.8879
2022-12-27 | 22603.8386 | 0 | 22603.8386
2022-12-28 | 22170 | 86.2604 | 22256.2604
2022-12-29 | 22228.3333 | 484.4957 | 22712.829
2022-12-30 | 14478.3208 | 445.6785 | 14923.9993
2022-12-31 | 13343.2652 | 733.8633 | 14077.1285

## Top 10 Days by Year (4.1.b.)
Total MWh Lost |  |  | Forced/Unplanned Outages/Derates
Rank | Date | MWh Lost | Rank | Date | Forced MWh Lost
2014 |  |  | 2014
1 | 2014-12-07 | 44812.4746 | 1 | 2014-09-18 | 29529.2392
2 | 2014-12-06 | 43348.579 | 2 | 2014-12-07 | 29236.4746
3 | 2014-10-05 | 36574.7052 | 3 | 2014-09-19 | 28651.7074
4 | 2014-10-04 | 34677.9556 | 4 | 2014-12-10 | 27214.6975
5 | 2014-06-01 | 34074.3822 | 5 | 2014-09-22 | 24460.506
6 | 2014-01-11 | 33865.2498 | 6 | 2014-12-11 | 23697.8831
7 | 2014-06-08 | 33296.8554 | 7 | 2014-12-18 | 21861.7798
8 | 2014-12-13 | 33205.317 | 8 | 2014-12-06 | 21789.0693
9 | 2014-07-19 | 32216.5829 | 9 | 2014-12-13 | 21633.378
10 | 2014-10-06 | 32137.9781 | 10 | 2014-07-03 | 21555.8901
2015 |  |  | 2015
1 | 2015-05-15 | 43662.1635 | 1 | 2015-01-26 | 31577.6317
2 | 2015-05-22 | 42800.8474 | 2 | 2015-09-01 | 28287.8071
3 | 2015-03-22 | 37457.2546 | 3 | 2015-08-31 | 26184.0158
4 | 2015-05-14 | 37271.8061 | 4 | 2015-08-15 | 24410.1254
5 | 2015-03-21 | 37223.8442 | 5 | 2015-08-14 | 23748.698
6 | 2015-08-14 | 36510.7002 | 6 | 2015-02-23 | 19619.6515
7 | 2015-05-16 | 35683.239 | 7 | 2015-08-30 | 19507.7491
8 | 2015-05-21 | 34626.3929 | 8 | 2015-07-27 | 19485.8479
9 | 2015-08-15 | 32092.1413 | 9 | 2015-11-30 | 19075.6668
10 | 2015-01-18 | 32018.1854 | 10 | 2015-09-23 | 19053.3649
2016 |  |  | 2016
1 | 2016-07-02 | 45643.0374 | 1 | 2016-03-18 | 38637.1411
2 | 2016-03-16 | 43208.1599 | 2 | 2016-03-19 | 38307.5911
3 | 2016-07-03 | 43189.5357 | 3 | 2016-03-17 | 38195.0069
4 | 2016-03-18 | 38637.1411 | 4 | 2016-07-02 | 37354.713
5 | 2016-03-19 | 38307.5911 | 5 | 2016-09-22 | 37179.1882
6 | 2016-03-17 | 38195.0069 | 6 | 2016-03-16 | 36391.8265
7 | 2016-09-22 | 37570.8875 | 7 | 2016-01-11 | 29513.295
8 | 2016-03-15 | 35965.6762 | 8 | 2016-01-12 | 28614.3027
9 | 2016-05-06 | 31908.9759 | 9 | 2016-07-03 | 28119.4357
10 | 2016-02-06 | 31521.9569 | 10 | 2016-03-15 | 27820.7903
2017 |  |  | 2017
1 | 2017-01-21 | 40655.2205 | 1 | 2017-11-20 | 28620.7666
2 | 2017-01-20 | 38418.5442 | 2 | 2017-02-14 | 25800.4122
3 | 2017-02-25 | 36648.9028 | 3 | 2017-04-29 | 25494.9421
4 | 2017-01-19 | 36396.2205 | 4 | 2017-04-28 | 22558.1272
5 | 2017-02-22 | 33375.8478 | 5 | 2017-04-17 | 22453.7137
6 | 2017-02-24 | 33295.0447 | 6 | 2017-02-15 | 21044.7205
7 | 2017-02-23 | 33290.5291 | 7 | 2017-06-15 | 20743.6575
8 | 2017-01-14 | 31883.7962 | 8 | 2017-12-27 | 20700.3918
9 | 2017-02-16 | 31721.6675 | 9 | 2017-05-03 | 20584.8106
10 | 2017-02-15 | 31631.2205 | 10 | 2017-06-16 | 20476.6159
2018 |  |  | 2018
1 | 2018-11-26 | 33482.3518 | 1 | 2018-11-26 | 26112.8581
2 | 2018-06-23 | 33439.1258 | 2 | 2018-11-27 | 21535.5825
3 | 2018-05-18 | 32679.5429 | 3 | 2018-12-03 | 21360.7738
4 | 2018-06-24 | 32427.3591 | 4 | 2018-11-29 | 21168.6188
5 | 2018-01-21 | 32056.4266 | 5 | 2018-11-28 | 18608.062
6 | 2018-05-17 | 31650.6496 | 6 | 2018-09-09 | 17713.0593
7 | 2018-05-20 | 30509.4976 | 7 | 2018-09-08 | 17062.9849
8 | 2018-11-25 | 28101.5005 | 8 | 2018-01-13 | 16682.2918
9 | 2018-01-20 | 28085.3596 | 9 | 2018-03-12 | 16559.1833
10 | 2018-11-27 | 27847.4961 | 10 | 2018-02-25 | 15918.2626
2019 |  |  | 2019
1 | 2019-02-03 | 36641.3994 | 1 | 2019-05-07 | 26411.6505
2 | 2019-06-09 | 35845.9471 | 2 | 2019-05-12 | 25548
3 | 2019-06-10 | 34637.2799 | 3 | 2019-05-13 | 24961.0167
4 | 2019-12-20 | 34591.1054 | 4 | 2019-05-11 | 24656.5731
5 | 2019-12-21 | 33964.4844 | 5 | 2019-05-06 | 24338.3627
6 | 2019-05-14 | 31789.6667 | 6 | 2019-08-11 | 22935.1815
7 | 2019-12-22 | 31586.787 | 7 | 2019-04-21 | 22223.9297
8 | 2019-06-08 | 29727.9474 | 8 | 2019-05-10 | 21917.7
9 | 2019-12-19 | 29644.7188 | 9 | 2019-04-22 | 21042.9391
10 | 2019-12-29 | 27041.337 | 10 | 2019-05-14 | 20901.55
2020 |  |  | 2020
1 | 2020-04-04 | 36416.138 | 1 | 2020-04-03 | 22827.8146
2 | 2020-04-26 | 30209.466 | 2 | 2020-12-08 | 22638.713
3 | 2020-04-25 | 30036.0233 | 3 | 2020-12-10 | 21878.2553
4 | 2020-03-05 | 29400 | 4 | 2020-04-02 | 19595.25
5 | 2020-04-03 | 28915.7499 | 5 | 2020-12-09 | 19079.245
6 | 2020-04-27 | 28500 | 6 | 2020-12-15 | 18886.6739
7 | 2020-04-28 | 28500 | 7 | 2020-11-14 | 17322.2192
8 | 2020-04-02 | 28055.8414 | 8 | 2020-09-03 | 15717.9444
9 | 2020-01-14 | 27935.2245 | 9 | 2020-09-04 | 15597.9444
10 | 2020-04-29 | 27725.0333 | 10 | 2020-11-06 | 15462.675
2021 |  |  | 2021
1 | 2021-05-13 | 31764.5381 | 1 | 2021-04-25 | 20237.8027
2 | 2021-12-14 | 29768.6424 | 2 | 2021-07-15 | 19368.5889
3 | 2021-05-12 | 28540.6311 | 3 | 2021-11-02 | 18674.4583
4 | 2021-04-24 | 26681.7467 | 4 | 2021-04-26 | 16851.6
5 | 2021-04-25 | 26124.5638 | 5 | 2021-04-27 | 16560
6 | 2021-12-15 | 25492.384 | 6 | 2021-01-29 | 16021.2117
7 | 2021-05-11 | 24749.7477 | 7 | 2021-10-14 | 15966.2455
8 | 2021-05-19 | 23876.9077 | 8 | 2021-01-26 | 15955.0617
9 | 2021-12-17 | 23624.2461 | 9 | 2021-01-28 | 14680.545
10 | 2021-12-13 | 23461.3472 | 10 | 2021-01-27 | 14347.045
2022 |  |  | 2022
1 | 2022-12-24 | 31982.9481 | 1 | 2022-12-24 | 31890.5164
2 | 2022-12-07 | 31701.9697 | 2 | 2022-12-23 | 27074.652
3 | 2022-05-12 | 31497.1373 | 3 | 2022-12-25 | 23989.7828
4 | 2022-05-03 | 30704.6619 | 4 | 2022-12-26 | 23274.8879
5 | 2022-05-08 | 30242.9393 | 5 | 2022-05-12 | 23157.358
6 | 2022-05-07 | 28128 | 6 | 2022-12-27 | 22603.8386
7 | 2022-05-04 | 27413.718 | 7 | 2022-12-29 | 22228.3333
8 | 2022-12-23 | 27074.652 | 8 | 2022-12-28 | 22170
9 | 2022-05-27 | 24665.2667 | 9 | 2022-05-03 | 21408
10 | 2022-05-11 | 24635.237 | 10 | 2022-05-31 | 19955.4333

## 2014 - Total MWh Lost Detail
Unit | Event Type | Daily Net MWh Lost | Cause | Description | Forced Category
2014-12-07 | 44812.4746
Brown 1 | Forced Derate | 88.8225 | Pulverizer Mills | 1-4 mill broken spring bolt | Mechanical Issue
Brown 10 CT | Forced Derate | 452.7194 | Other Gas Turbine Low Pressure Problems | Blade design issues has unit limited to 120MWs. | Mechanical Issue
Brown 11 CT | Forced Derate | 214.3256 | Other Gas Turbine Low Pressure Problems | Blade design issues has unit limited to 120MWs. | Mechanical Issue
Brown 2 | Maintenance Outage | 4032 | Hydrogen System Problems | Investigate and repair hydrogen leak and eccentricity issues | N/A
Brown 5 CT | Forced Derate | 261.9847 | Other Gas Turbine Low Pressure Problems | Blade design issues has unit limited to 120MWs. | Mechanical Issue
Brown 8 CT | Forced Derate | 214.3256 | Other Gas Turbine Low Pressure Problems | Blade design issues has unit limited to 120MWs. | Mechanical Issue
Brown 9 CT | Forced Derate | 452.7194 | Other Gas Turbine Low Pressure Problems | Blade design issues has unit limited to 120MWs. | Mechanical Issue
Ghent 1 | Maintenance Outage | 11544 | Furnace Wall Leaks | Unit 1 had been running with two water wall tube leaks. | N/A
Ghent 4 | Forced Derate | 1308.3219 | Boiler Water Condition | High boiler drum silica on start up after Fall Outage. | Mechanical Issue
Ghent 4 | Forced Outage | 4271.7 | Feedwater Valves | Packing blew out on the flue economizer inlet valve | Mechanical Issue
Green River 3 | Forced Outage | 1704 | Condenser Tube Leaks | GR3 taken out of service in an orderly manner due to boiler chemistry indication | Mechanical Issue
Mill Creek 2 | Forced Outage | 4913.5667 | Condenser Tube Leaks | Condenser Tube Leak | Mechanical Issue
Mill Creek 4 | Forced Derate | 1743.8143 | Boiler Water Condition | High Silica | Mechanical Issue
Trimble County 1 | Forced Derate | 53.6745 | Main Steam Shortage | Unit 2 using Unit 1 steam during Unit 2 start-up. | Mechanical Issue
Trimble County 2 | Forced Outage | 9642.5 | High Pressure Heater Problems | While attempting to isolate the 8A heater for repair, the 8A heater bypass valve | Mechanical Issue
Trimble County 2 | Forced Outage | 218.5 | Pulverizer Feeders | 2E Coal Mill clean out conveyor issues. | Mechanical Issue
Trimble County 2 | Forced Outage | 3695.5 | Feedwater System Problems | Feedwater flow limit during mill swap. | Mechanical Issue
2014-12-06 | 43348.579
Brown 1 | Forced Derate | 15.4243 | Wet Coal | Wet coal | Mechanical Issue
Brown 1 | Forced Derate | 45.2091 | Pulverizer Mills | 1-4 mill broken spring bolt | Mechanical Issue
Brown 10 CT | Forced Derate | 452.7194 | Other Gas Turbine Low Pressure Problems | Blade design issues has unit limited to 120MWs. | Mechanical Issue
Brown 11 CT | Forced Derate | 214.3256 | Other Gas Turbine Low Pressure Problems | Blade design issues has unit limited to 120MWs. | Mechanical Issue
Brown 2 | Maintenance Outage | 4032 | Hydrogen System Problems | Investigate and repair hydrogen leak and eccentricity issues | N/A
Brown 5 CT | Forced Derate | 261.9847 | Other Gas Turbine Low Pressure Problems | Blade design issues has unit limited to 120MWs. | Mechanical Issue
Brown 8 CT | Forced Derate | 214.3256 | Other Gas Turbine Low Pressure Problems | Blade design issues has unit limited to 120MWs. | Mechanical Issue
Brown 9 CT | Forced Derate | 452.7194 | Other Gas Turbine Low Pressure Problems | Blade design issues has unit limited to 120MWs. | Mechanical Issue
Ghent 1 | Maintenance Outage | 11544 | Furnace Wall Leaks | Unit 1 had been running with two water wall tube leaks. | N/A
Ghent 4 | Forced Derate | 846.5612 | Boiler Water Condition | High boiler drum silica on start up after Fall Outage. | Mechanical Issue
Green River 3 | Forced Outage | 463.8667 | Condenser Tube Leaks | GR3 taken out of service in an orderly manner due to boiler chemistry indication | Mechanical Issue
Green River 4 | Forced Derate | 42.7 | Opacity - Fossil Steam Units | GR4 load reduction due to opacity. Blowing soot and cleaning boiler. | Mechanical Issue
Mill Creek 2 | Forced Outage | 7176 | Condenser Tube Leaks | Condenser Tube Leak | Mechanical Issue
Mill Creek 4 | Maintenance Outage | 5775.3 | Generator Vibration | Generator - Balance Shot | N/A
Mill Creek 4 | Forced Outage | 299.7 | Boiler Drums And Drum Internals | Low Drum Level Trip - Operator Error | Mechanical Issue
Trimble County 2 | Maintenance Derate | 208.2096 | High Pressure Heater Head Leaks | Planned derate to repair head leak on 8A FW heater. | N/A
Trimble County 2 | Forced Outage | 10887 | High Pressure Heater Problems | While attempting to isolate the 8A heater for repair, the 8A heater bypass valve | Mechanical Issue
Trimble County 5 CT | Forced Outage | 416.5333 | Gas Turbine - High Engine Exhaust Temperature | Exhaust thermocouple #1 failed high before reaching mode 6, | Mechanical Issue
2014-10-05 | 36574.7052
Brown 10 CT | Forced Derate | 452.7194 | Other Gas Turbine Low Pressure Problems | Blade design issues has unit limited to 120MWs. | Mechanical Issue
Brown 11 CT | Forced Derate | 214.3256 | Other Gas Turbine Low Pressure Problems | Blade design issues has unit limited to 120MWs. | Mechanical Issue
Brown 5 CT | Forced Derate | 261.9847 | Other Gas Turbine Low Pressure Problems | Blade design issues has unit limited to 120MWs. | Mechanical Issue
Brown 8 CT | Forced Derate | 214.3256 | Other Gas Turbine Low Pressure Problems | Blade design issues has unit limited to 120MWs. | Mechanical Issue
Brown 9 CT | Forced Derate | 452.7194 | Other Gas Turbine Low Pressure Problems | Blade design issues has unit limited to 120MWs. | Mechanical Issue
Ghent 1 | Forced Derate | 77.4531 | Other Pulverizer Problems | 1-2 Mill pyrite scraper broke off. | Mechanical Issue
Ghent 2 | Maintenance Derate | 1102.0668 | Pulverizer Overhaul | Planned overhaul on 2-6 Mill. | N/A
Ghent 3 | Maintenance Outage | 11568 | Air Heater Fouling | Unit 3 was running with leaks in the 3-2 Air Preheating Coil. | N/A
Ghent 4 | Forced Derate | 507.5506 | Other Miscellaneous Steam Turbine Problems | Turbine degradation due to copper deposits. | Mechanical Issue
Green River 3 | Forced Derate | 68.16 | Condenser Tube Sheet Fouling | GR3 Condenser plugged with debris from the river due to recent rain storm. | Mechanical Issue
Green River 4 | Forced Derate | 29.7111 | Condenser Tube Sheet Fouling | GR4 Condenser plugged with debris from he river due to recent rain storm. | Mechanical Issue
Green River 4 | Forced Derate | 30.8 | Condenser Tube Sheet Fouling | GR4 Condenser plugged with debris from he river due to recent rain storm. | Mechanical Issue
Green River 4 | Forced Derate | 77.1556 | Condenser Tube Sheet Fouling | GR4 Condenser plugged with debris from the river due to recent rain storm. | Mechanical Issue
Green River 4 | Forced Derate | 57.8667 | Condenser Tube Sheet Fouling | Backwashing GR4 Condenser due to river debris clogging tube sheet. | Mechanical Issue
Green River 4 | Forced Derate | 27.0667 | Condenser Tube Sheet Fouling | Backwashing GR4 Condenser due to river debris clogging tube sheet. | Mechanical Issue
Trimble County 10 CT | Maintenance Outage | 4015.7333 | General Gas Turbine Unit Inspection | Ultrasonic inspection of R0 and R1 compressor blades. | N/A
Trimble County 2 | Maintenance Outage | 13680 | Economizer Piping | TC2 was taken offline for a maintenance outage to repair a leak in the economizer | N/A
Trimble County 9 CT | Maintenance Outage | 3737.0667 | General Gas Turbine Unit Inspection | Ultrasonic inspection of R0 and R1 compressor blades. | N/A
2014-10-04 | 34677.9556
Brown 10 CT | Forced Derate | 452.7194 | Other Gas Turbine Low Pressure Problems | Blade design issues has unit limited to 120MWs. | Mechanical Issue
Brown 11 CT | Forced Derate | 214.3256 | Other Gas Turbine Low Pressure Problems | Blade design issues has unit limited to 120MWs. | Mechanical Issue
Brown 5 CT | Forced Derate | 261.9847 | Other Gas Turbine Low Pressure Problems | Blade design issues has unit limited to 120MWs. | Mechanical Issue
Brown 8 CT | Forced Derate | 214.3256 | Other Gas Turbine Low Pressure Problems | Blade design issues has unit limited to 120MWs. | Mechanical Issue
Brown 9 CT | Forced Derate | 452.7194 | Other Gas Turbine Low Pressure Problems | Blade design issues has unit limited to 120MWs. | Mechanical Issue
Ghent 1 | Forced Derate | 59.5435 | Pulverizer Feeders | 1-1 Feeder tripped and wouldn't restart. | Mechanical Issue
Ghent 2 | Maintenance Derate | 1102.0668 | Pulverizer Overhaul | Planned overhaul on 2-6 Mill. | N/A
Ghent 3 | Maintenance Outage | 11568 | Air Heater Fouling | Unit 3 was running with leaks in the 3-2 Air Preheating Coil. | N/A
Ghent 4 | Forced Derate | 507.5506 | Other Miscellaneous Steam Turbine Problems | Turbine degradation due to copper deposits. | Mechanical Issue
Green River 3 | Forced Derate | 48.1222 | Condenser Tube Sheet Fouling | GR3 Condenser plugged with debris from river due to recent rain storm. | Mechanical Issue
Green River 3 | Forced Derate | 39.2867 | Condenser Tube Sheet Fouling | GR3 Condenser plugged with debris from the river due to recent rain storm. | Mechanical Issue
Green River 4 | Forced Derate | 9.0222 | Condenser Tube Sheet Fouling | GR4 Condenser plugged with debris from he river due to recent rain storm. | Mechanical Issue
Green River 4 | Forced Derate | 19.1333 | Condenser Tube Sheet Fouling | GR4 Condenser plugged with debris from he river due to recent rain storm. | Mechanical Issue
Green River 4 | Forced Derate | 71.0889 | Condenser Tube Sheet Fouling | GR4 Condenser plugged with debris from he river due to recent rain storm. | Mechanical Issue
Trimble County 2 | Maintenance Outage | 11609 | Economizer Piping | TC2 was taken offline for a maintenance outage to repair a leak in the economizer | N/A
Trimble County 7 CT | Maintenance Outage | 4200.5333 | General Gas Turbine Unit Inspection | Inspection of R0 and R1 compressor blades. | N/A
Trimble County 8 CT | Maintenance Outage | 3848.5333 | General Gas Turbine Unit Inspection | Ultrasonic inspection of R0 and R1 compressor blades. | N/A
2014-06-01 | 34074.3822
Brown 1 | Maintenance Derate | 181.5914 | Pulverizer Mills | 1-3 mill race replacement | N/A
Brown 10 CT | Forced Derate | 59.7073 | Gas Turbine - Blading Design Issue | Reduction in IAC capability. | Mechanical Issue
Brown 11 CT | Forced Derate | 59.7073 | Gas Turbine - Blading Design Issue | Reduction in IAC capability. | Mechanical Issue
Brown 5 CT | Forced Derate | 225.7099 | Gas Turbine - Blading Design Issue | Reduction in IAC capability. | Mechanical Issue
Brown 8 CT | Forced Derate | 59.7073 | Gas Turbine - Blading Design Issue | Reduction in IAC capability. | Mechanical Issue
Brown 9 CT | Forced Derate | 59.7073 | Gas Turbine - Blading Design Issue | Reduction in IAC capability. | Mechanical Issue
Cane Run 6 | Forced Derate | 1566.8966 | Feedwater Pump/Drive Lube Oil System | Lost of 62 Boiler Feed Pump - fluid drive oil pump | Mechanical Issue
Ghent 4 | Maintenance Outage | 10138.2167 | Induced Draft Fans | Unit 4 was running with 4-2 ID Fan hydraulic leak on the blade pitch | N/A
Mill Creek 2 | Maintenance Derate | 263.6364 | Feedwater Pump | 2B Boiler Feed Pump - Injection Water Line Leak Repair | N/A
Mill Creek 4 | Maintenance Outage | 6034.05 | Condenser Tube and Water Box Cleaning | Condenser - Clean Water Box Tubesheets | N/A
Mill Creek 4 | Maintenance Outage | 5413.95 | First Superheater Leaks | Boiler Tube Leak - First Superheater | N/A
Trimble County 2 | Maintenance Derate | 3410.8186 | Burners | TC2 is being held at 430MW for combustion testing and tuning following the install | N/A
Trimble County 2 | Forced Outage | 5590.65 | Instrument Air Dryers | TC2 tripped offline when the instrument air dryer de-pressurized. | Mechanical Issue
Trimble County 6 CT | Forced Outage | 1010.0333 | Other Gas Turbine Combustor Problems | Start up failure due to failure to ignite. Spark rod not operating properly. | Mechanical Issue
2014-01-11 | 33865.2498
Brown 2 | Forced Derate | 105 | Pulverizer Mills | Repair 2-2 mill broken spring bolt | Mechanical Issue
Brown 3 | Maintenance Outage | 5540.7 | 3-1 Boiler Recirculation Pump Replacement | Replace 3-1 BCWP | N/A
Cane Run 5 | Forced Outage | 456.4 | Induced Draft Fan Motors and Drives | 5A induced draft fan tripped due to bad thyrister card causing unit to trip. | Mechanical Issue
Cane Run 6 | Maintenance Outage | 5760 | Reheater Tube Leaks | Boiler Leak Repair - A tube within the RH Pendants was discovered to be cracked, | N/A
Ghent 3 | Maintenance Outage | 11568 | 3-2 Induced Draft Fan Trip | Unit derated to minimum load due to 3-2 ID Fan tripping on | N/A
Green River 4 | Maintenance Derate | 36.8667 | Pulverizer Overhaul | Maint discovered a broken lower race on 5-3 Pulv during inspection. | N/A
Green River 4 | Maintenance Derate | 16.0533 | Pulverizer Overhaul | Maint discovered a broken lower race on 5-3 Pulv during inspection. | N/A
Green River 4 | Maintenance Derate | 16.1778 | Pulverizer Overhaul | Maint discovered a broken lower race on 5-3 Pulv during inspection. | N/A
Green River 4 | Maintenance Derate | 250.4289 | Pulverizer Overhaul | Maint discovered a broken lower race on 5-3 Pulv during inspection. | N/A
Green River 4 | Maintenance Derate | 36.7111 | Pulverizer Overhaul | Maint discovered a broken lower race on 5-3 Pulv during inspection. | N/A
Green River 4 | Forced Derate | 49.9333 | Electrostatic Precipitator Field Out Of Service | Broken wire in B5 Precip causing loss of two half cabinets. | Mechanical Issue
Haefling 1 CT | Forced Outage | 336 | Gas Turbine - Cooling And Seal Air System | Busted glycol line on radiator. Failed to ignite on start up. | Mechanical Issue
Trimble County 1 | Forced Derate | 925.9259 | Chemical Feed Storage; Mill Feeders And Conveyors | Reactant supply C Limestone conveyor belt broke and issues with running backup | Mechanical Issue
Trimble County 1 | Forced Derate | 362.0751 | Chemical Feed Storage; Mill Feeders And Conveyors | Reactant supply C Limestone conveyor belt broke and issues with running backup | Mechanical Issue
Trimble County 1 | Forced Outage | 1129.85 | Operator Error | During load drop, operator error in valve closing caused the TDBFP main extraction | Mechanical Issue
Trimble County 2 | Forced Derate | 1926.1993 | Chemical Feed Storage; Mill Feeders And Conveyors | Reactant supply C Limestone conveyor belt broke and issues with running backup | Mechanical Issue
Trimble County 2 | Forced Derate | 1124.9283 | Chemical Feed Storage; Mill Feeders And Conveyors | Reactant supply C Limestone conveyor belt broke and issues with running backup | Mechanical Issue
Trimble County 8 CT | Forced Outage | 4224 | Other Fire Protection System Problems | Forced outage due to issue with Fire Protection System. | Mechanical Issue
2014-06-08 | 33296.8554
Brown 10 CT | Forced Derate | 59.7073 | Gas Turbine - Blading Design Issue | Reduction in IAC capability. | Mechanical Issue
Brown 11 CT | Forced Derate | 59.7073 | Gas Turbine - Blading Design Issue | Reduction in IAC capability. | Mechanical Issue
Brown 3 | Maintenance Outage | 9840 | High Pressure Heater Tube Leaks | Repair 3-F2 HP heater tube leak | N/A
Brown 5 CT | Forced Derate | 225.7099 | Gas Turbine - Blading Design Issue | Reduction in IAC capability. | Mechanical Issue
Brown 8 CT | Forced Derate | 59.7073 | Gas Turbine - Blading Design Issue | Reduction in IAC capability. | Mechanical Issue
Brown 9 CT | Forced Derate | 59.7073 | Gas Turbine - Blading Design Issue | Reduction in IAC capability. | Mechanical Issue
Mill Creek 3 | Forced Outage | 9384 | Economizer Leaks | Boiler Tube Leak - Economizer | Mechanical Issue
Mill Creek 4 | Forced Derate | 22.0662 | Combustion/Steam Condition Controls | Max Steam Flow Issue | Mechanical Issue
Mill Creek 4 | Forced Outage | 9818.25 | First Reheater Leaks | Boiler Tube Leak - First Reheater | Mechanical Issue
Trimble County 7 CT | Maintenance Outage | 3768 | Other Gas Turbine Problems | Planned maintenance outage to conduct a generator balance shot. | N/A
2014-12-13 | 33205.317
Brown 10 CT | Forced Derate | 452.7194 | Other Gas Turbine Low Pressure Problems | Blade design issues has unit limited to 120MWs. | Mechanical Issue
Brown 11 CT | Forced Derate | 214.3256 | Other Gas Turbine Low Pressure Problems | Blade design issues has unit limited to 120MWs. | Mechanical Issue
Brown 3 | Maintenance Outage | 9039 | SCR NOx Plugging | Clean and inspect SCR | N/A
Brown 5 CT | Forced Derate | 261.9847 | Other Gas Turbine Low Pressure Problems | Blade design issues has unit limited to 120MWs. | Mechanical Issue
Brown 8 CT | Forced Derate | 214.3256 | Other Gas Turbine Low Pressure Problems | Blade design issues has unit limited to 120MWs. | Mechanical Issue
Brown 9 CT | Forced Derate | 452.7194 | Other Gas Turbine Low Pressure Problems | Blade design issues has unit limited to 120MWs. | Mechanical Issue
Ghent 4 | Forced Outage | 2078.5667 | Induced Draft Fans | U4 Boiler tripped on "Low Furnace Pressure" ... 4-2A and 4-2B ID fan. | Mechanical Issue
Mill Creek 1 | Forced Derate | 2203.6364 | Boiler Water Condition | High Silica | Mechanical Issue
Mill Creek 2 | Forced Derate | 1522.1818 | Boiler Water Condition | High Silica | Mechanical Issue
Mill Creek 3 | Forced Derate | 2190.7518 | Boiler Water Condition | High Silica | Mechanical Issue
Mill Creek 4 | Forced Outage | 10716.3 | Condenser Tube Leaks | Condenser Tube Leaks | Mechanical Issue
Trimble County 2 | Maintenance Derate | 4.4057 | Tube Slagging or Fouling | Unit derate to conduct boiler OEM recommended unit deslag. Unit was available | N/A
Trimble County 8 CT | Maintenance Outage | 504.5333 | Switchyard Circuit Breakers | Maintenance outage on generator main line breaker for compliance testing. | N/A
Trimble County 8 CT | Forced Outage | 1325.8667 | Switchyard Circuit Breakers | Generator line breaker failed to operate due to springs not charging. | Mechanical Issue
Trimble County 9 CT | Maintenance Outage | 2024 | Switchyard Circuit Breakers | Maintenance outage on generator mail line breaker due to compliance to regulation. | N/A
2014-07-19 | 32216.5829
Brown 10 CT | Forced Derate | 59.7073 | Gas Turbine - Blading Design Issue | Reduction in IAC capability. | Mechanical Issue
Brown 11 CT | Forced Derate | 59.7073 | Gas Turbine - Blading Design Issue | Reduction in IAC capability. | Mechanical Issue
Brown 3 | Forced Outage | 9840 | Other Cooling Tower Problems | 3-2 Cooloing tower cell damage | Mechanical Issue
Brown 5 CT | Forced Derate | 225.7099 | Gas Turbine - Blading Design Issue | Reduction in IAC capability. | Mechanical Issue
Brown 8 CT | Forced Derate | 59.7073 | Gas Turbine - Blading Design Issue | Reduction in IAC capability. | Mechanical Issue
Brown 9 CT | Forced Derate | 59.7073 | Gas Turbine - Blading Design Issue | Reduction in IAC capability. | Mechanical Issue
Cane Run 5 | Forced Derate | 356.4199 | Feedwater Pump Motor High Stator Temp | 52 boiler feed pump stator high temperature. Unit derated 16 MW. | Mechanical Issue
Ghent 3 | Maintenance Derate | 782.0337 | Induced Draft Fan Motors and Drives | 3-2A ID Fan OOS for VFD coolant system repairs and to check motor | N/A
Ghent 4 | Maintenance Outage | 11256 | Wet Scrubber Mist Eliminators/demisters & Washdown | FGD Absorber Tower Mist Eliminators showing high differential. | N/A
Mill Creek 4 | Forced Derate | 237.8234 | Combustion/Steam Condition Controls | Max Steam Flow Issues | Mechanical Issue
Mill Creek 4 | Forced Derate | 144.3917 | Combustion/Steam Condition Controls | Max Steam Flow Issue | Mechanical Issue
Trimble County 1 | Maintenance Outage | 9135.375 | Other Boiler Tube Leaks | Maintenance outage to inspect for an expected boiler tube leak in the penthouse. | N/A
2014-10-06 | 32137.9781
Brown 10 CT | Forced Derate | 452.7194 | Other Gas Turbine Low Pressure Problems | Blade design issues has unit limited to 120MWs. | Mechanical Issue
Brown 11 CT | Forced Derate | 214.3256 | Other Gas Turbine Low Pressure Problems | Blade design issues has unit limited to 120MWs. | Mechanical Issue
Brown 5 CT | Forced Derate | 261.9847 | Other Gas Turbine Low Pressure Problems | Blade design issues has unit limited to 120MWs. | Mechanical Issue
Brown 7 CT | Forced Outage | 954.75 | Gas Turbine - Ignition System | Unit trip at Flame on. | Mechanical Issue
Brown 8 CT | Forced Derate | 214.3256 | Other Gas Turbine Low Pressure Problems | Blade design issues has unit limited to 120MWs. | Mechanical Issue
Brown 9 CT | Forced Derate | 452.7194 | Other Gas Turbine Low Pressure Problems | Blade design issues has unit limited to 120MWs. | Mechanical Issue
Ghent 2 | Maintenance Derate | 1102.0668 | Pulverizer Overhaul | Planned overhaul on 2-6 Mill. | N/A
Ghent 2 | Forced Derate | 636.1093 | Pulverizer Inspection | 2-4 Mill off to inspect grinding section due to mill dumping coal | Mechanical Issue
Ghent 3 | Maintenance Outage | 11568 | Air Heater Fouling | Unit 3 was running with leaks in the 3-2 Air Preheating Coil. | N/A
Ghent 4 | Forced Derate | 507.5506 | Other Miscellaneous Steam Turbine Problems | Turbine degradation due to copper deposits. | Mechanical Issue
Green River 3 | Forced Derate | 68.16 | Condenser Tube Sheet Fouling | GR3 Condenser plugged with debris from the river due to recent rain storm. | Mechanical Issue
Green River 4 | Forced Derate | 112 | Condenser Tube Sheet Fouling | GR4 Condenser plugged with debris from the river due to recent rain storm. | Mechanical Issue
Green River 4 | Forced Derate | 44.8 | Condenser Tube Sheet Fouling | Backwashing GR4 Condenser due to river debris clogging tube sheet. | Mechanical Issue
Trimble County 10 CT | Maintenance Outage | 4224 | General Gas Turbine Unit Inspection | Ultrasonic inspection of R0 and R1 compressor blades. | N/A
Trimble County 2 | Maintenance Outage | 10773 | Economizer Piping | TC2 was taken offline for a maintenance outage to repair a leak in the economizer | N/A
Trimble County 9 CT | Forced Outage | 551.4667 | Gas Turbine - Starting System (including Motor) | LCI had low water level. Added demin water and unit made available. | Mechanical Issue

## 2014 - Forced MWh Lost Detail
Unit | Event Type | Daily Net Forced MWh Lost | Cause | Description | Forced Category
2014-09-18 | 29529.2392
Brown 10 CT | Forced Derate | 59.7073 | Gas Turbine - Blading Design Issue | Reduction in IAC capability. | Mechanical Issue
Brown 10 CT | Forced Derate | 142.8 | Gas Turbine - IAC Cooler Issue | Reduction in IAC capability. | Mechanical Issue
Brown 11 CT | Forced Derate | 59.7073 | Gas Turbine - Blading Design Issue | Reduction in IAC capability. | Mechanical Issue
Brown 3 | Forced Outage | 9840 | Turbine Lube Oil Coolers | 3-1 Turbine Oil cooler leak. | Mechanical Issue
Brown 5 CT | Forced Derate | 225.7099 | Gas Turbine - Blading Design Issue | Reduction in IAC capability. | Mechanical Issue
Brown 8 CT | Forced Derate | 59.7073 | Gas Turbine - Blading Design Issue | Reduction in IAC capability. | Mechanical Issue
Brown 8 CT | Forced Derate | 102 | Gas Turbine - IAC Cooler Issue | Reduction in IAC capability. | Mechanical Issue
Brown 9 CT | Forced Derate | 59.7073 | Gas Turbine - Blading Design Issue | Reduction in IAC capability. | Mechanical Issue
Brown 9 CT | Forced Derate | 40.8 | Gas Turbine - IAC Cooler Issue | Reduction in IAC capability. | Mechanical Issue
Ghent 2 | Forced Derate | 75.75 | Primary Air Flow Instrumentation | Unit 2 was derated due to changing out primary air control | Mechanical Issue
Ghent 3 | Forced Derate | 42.3067 | Low Grindability | The unit was derated due to mill grinding and air flow issues | Mechanical Issue
Mill Creek 1 | Forced Derate | 130.8409 | Pulverizer Mills | 1C Coal Mill - Inspection | Mechanical Issue
Mill Creek 4 | Forced Derate | 255.1074 | Other Feedwater System Problems | Feedwater Flow Maxed Out | Mechanical Issue
Mill Creek 4 | Forced Derate | 393.6783 | Other Reheat Steam Valves (not Incl Turbine Stop.. | Reheat Spray Issue - High Temperature, Block Valve Closed | Mechanical Issue
Mill Creek 4 | Forced Outage | 4529.4167 | Other Ac Instrument Power Problems | Electrical Wiring - Burnt Wiring in Wire Tray | Mechanical Issue
Trimble County 2 | Forced Outage | 13176 | Boiler Screen; Wing Wall; Or Slag Screen Leaks... | Unit on forced outage due to tube leak. Waiting for unit to cool enough for access | Mechanical Issue
Zorn 1 CT | Forced Outage | 336 | Lack Of Fuel (OMC) | Gas line repairs due to explosion on main gas line on 9/17/14 near Goshen Kentucky | Fuel Supply Disruption
2014-12-07 | 29236.4746
Brown 1 | Forced Derate | 88.8225 | Pulverizer Mills | 1-4 mill broken spring bolt | Mechanical Issue
Brown 10 CT | Forced Derate | 452.7194 | Other Gas Turbine Low Pressure Problems | Blade design issues has unit limited to 120MWs. | Mechanical Issue
Brown 11 CT | Forced Derate | 214.3256 | Other Gas Turbine Low Pressure Problems | Blade design issues has unit limited to 120MWs. | Mechanical Issue
Brown 5 CT | Forced Derate | 261.9847 | Other Gas Turbine Low Pressure Problems | Blade design issues has unit limited to 120MWs. | Mechanical Issue
Brown 8 CT | Forced Derate | 214.3256 | Other Gas Turbine Low Pressure Problems | Blade design issues has unit limited to 120MWs. | Mechanical Issue
Brown 9 CT | Forced Derate | 452.7194 | Other Gas Turbine Low Pressure Problems | Blade design issues has unit limited to 120MWs. | Mechanical Issue
Ghent 4 | Forced Derate | 1308.3219 | Boiler Water Condition | High boiler drum silica on start up after Fall Outage. | Mechanical Issue
Ghent 4 | Forced Outage | 4271.7 | Feedwater Valves | Packing blew out on the flue economizer inlet valve | Mechanical Issue
Green River 3 | Forced Outage | 1704 | Condenser Tube Leaks | GR3 taken out of service in an orderly manner due to boiler chemistry indication | Mechanical Issue
Mill Creek 2 | Forced Outage | 4913.5667 | Condenser Tube Leaks | Condenser Tube Leak | Mechanical Issue
Mill Creek 4 | Forced Derate | 1743.8143 | Boiler Water Condition | High Silica | Mechanical Issue
Trimble County 1 | Forced Derate | 53.6745 | Main Steam Shortage | Unit 2 using Unit 1 steam during Unit 2 start-up. | Mechanical Issue
Trimble County 2 | Forced Outage | 9642.5 | High Pressure Heater Problems | While attempting to isolate the 8A heater for repair, the 8A heater bypass valve | Mechanical Issue
Trimble County 2 | Forced Outage | 218.5 | Pulverizer Feeders | 2E Coal Mill clean out conveyor issues. | Mechanical Issue
Trimble County 2 | Forced Outage | 3695.5 | Feedwater System Problems | Feedwater flow limit during mill swap. | Mechanical Issue
2014-09-19 | 28651.7074
Brown 10 CT | Forced Derate | 59.7073 | Gas Turbine - Blading Design Issue | Reduction in IAC capability. | Mechanical Issue
Brown 10 CT | Forced Derate | 142.8 | Gas Turbine - IAC Cooler Issue | Reduction in IAC capability. | Mechanical Issue
Brown 11 CT | Forced Derate | 59.7073 | Gas Turbine - Blading Design Issue | Reduction in IAC capability. | Mechanical Issue
Brown 3 | Forced Outage | 9840 | Turbine Lube Oil Coolers | 3-1 Turbine Oil cooler leak. | Mechanical Issue
Brown 5 CT | Forced Derate | 225.7099 | Gas Turbine - Blading Design Issue | Reduction in IAC capability. | Mechanical Issue
Brown 8 CT | Forced Derate | 59.7073 | Gas Turbine - Blading Design Issue | Reduction in IAC capability. | Mechanical Issue
Brown 8 CT | Forced Derate | 102 | Gas Turbine - IAC Cooler Issue | Reduction in IAC capability. | Mechanical Issue
Brown 9 CT | Forced Derate | 59.7073 | Gas Turbine - Blading Design Issue | Reduction in IAC capability. | Mechanical Issue
Brown 9 CT | Forced Derate | 40.8 | Gas Turbine - IAC Cooler Issue | Reduction in IAC capability. | Mechanical Issue
Mill Creek 1 | Forced Derate | 159.7636 | Pulverizer Mills | 1C Coal Mill - Inspection | Mechanical Issue
Mill Creek 2 | Forced Derate | 229.8545 | Pulverizer Mills | 2B Coal Mill - Inspection | Mechanical Issue
Mill Creek 4 | Forced Outage | 11544 | Other Ac Instrument Power Problems | Electrical Wiring - Burnt Wiring in Wire Tray | Mechanical Issue
Trimble County 2 | Forced Outage | 5791.95 | Boiler Screen; Wing Wall; Or Slag Screen Leaks... | Unit on forced outage due to tube leak. Waiting for unit to cool enough for access | Mechanical Issue
Zorn 1 CT | Forced Outage | 336 | Lack Of Fuel (OMC) | Gas line repairs due to explosion on main gas line on 9/17/14 near Goshen Kentucky | Fuel Supply Disruption
2014-12-10 | 27214.6975
Brown 10 CT | Forced Derate | 452.7194 | Other Gas Turbine Low Pressure Problems | Blade design issues has unit limited to 120MWs. | Mechanical Issue
Brown 11 CT | Forced Derate | 214.3256 | Other Gas Turbine Low Pressure Problems | Blade design issues has unit limited to 120MWs. | Mechanical Issue
Brown 5 CT | Forced Derate | 261.9847 | Other Gas Turbine Low Pressure Problems | Blade design issues has unit limited to 120MWs. | Mechanical Issue
Brown 8 CT | Forced Derate | 214.3256 | Other Gas Turbine Low Pressure Problems | Blade design issues has unit limited to 120MWs. | Mechanical Issue
Brown 9 CT | Forced Derate | 452.7194 | Other Gas Turbine Low Pressure Problems | Blade design issues has unit limited to 120MWs. | Mechanical Issue
Ghent 1 | Forced Outage | 11544 | First Reheater Leaks | Reheat pendant tube ruptured a few feet out from the east side of the boi | Mechanical Issue
Ghent 4 | Forced Derate | 299.5958 | Induced Draft Fans | 4-2 FD fan inlet vane control card failed. 4-2 FD fan inlet | Mechanical Issue
Ghent 4 | Forced Outage | 1481.1833 | Induced Draft Fan Motors and Drives | U4 Boiler tripped on low furnace pressure while working on 4-2 FD fan | Mechanical Issue
Ghent 4 | Forced Derate | 186.6536 | Boiler Water Condition | High boiler drum silica on start up after Fall Outage. | Mechanical Issue
Green River 4 | Forced Outage | 2352 | Second Superheater Leaks | GR4 taken out of service in an orderly manner due to Sec SH Section tube leak. | Mechanical Issue
Mill Creek 1 | Forced Derate | 935.0152 | Boiler Water Condition | High Silica | Mechanical Issue
Mill Creek 1 | Forced Derate | 313.5897 | Boiler Water Condition | High Silica | Mechanical Issue
Mill Creek 2 | Forced Derate | 1660.8091 | Boiler Water Condition | High Silica | Mechanical Issue
Mill Creek 2 | Forced Derate | 385.9818 | Boiler Water Condition | High Silica | Mechanical Issue
Mill Creek 2 | Forced Derate | 7.8525 | Boiler Water Condition | High Silica | Mechanical Issue
Mill Creek 3 | Forced Derate | 174.9559 | Boiler Water Condition | High Silica | Mechanical Issue
Mill Creek 3 | Forced Derate | 70.417 | Boiler Water Condition | High Silica | Mechanical Issue
Mill Creek 3 | Forced Derate | 208.4257 | Boiler Water Condition | High Silica | Mechanical Issue
Mill Creek 3 | Forced Derate | 113.015 | Wet Scrubber - Reagent Feed Piping | FGD Reactive Feed Return Line - Broken | Mechanical Issue
Mill Creek 4 | Forced Outage | 1044.9 | Induced Draft Fans | 4A Induced Draft Fan - Trip | Mechanical Issue
Mill Creek 4 | Forced Derate | 316.9029 | Feedwater Pump Drive - Steam Turbine | Turbine Driven Boiler Feed Pump - Control Issue | Mechanical Issue
Mill Creek 4 | Forced Derate | 836.892 | Feedwater Pump Drive - Steam Turbine | Turbine Driven Boiler Feed Pump - Control Issue | Mechanical Issue
Mill Creek 4 | Forced Outage | 972 | Boiler Drums And Drum Internals | Low Drum Level Trip - Operator Error | Mechanical Issue
Mill Creek 4 | Forced Outage | 2227.5 | Condenser Tube Leaks | Condenser Tube Leaks | Mechanical Issue
Trimble County 10 CT | Forced Outage | 234.6667 | Dc Protection Devices | Loss of DC voltage supply to TC9 BOP Fuel Gas Valves, needed the fuel gas heater | Mechanical Issue
Trimble County 9 CT | Forced Outage | 252.2667 | Dc Protection Devices | Unit tripped due to loss of DC voltage to the BOP Fuel Gas Valves. Problem corrected | Mechanical Issue
2014-09-22 | 24460.506
Brown 10 CT | Forced Derate | 59.7073 | Gas Turbine - Blading Design Issue | Reduction in IAC capability. | Mechanical Issue
Brown 10 CT | Forced Derate | 142.8 | Gas Turbine - IAC Cooler Issue | Reduction in IAC capability. | Mechanical Issue
Brown 11 CT | Forced Derate | 59.7073 | Gas Turbine - Blading Design Issue | Reduction in IAC capability. | Mechanical Issue
Brown 5 CT | Forced Derate | 225.7099 | Gas Turbine - Blading Design Issue | Reduction in IAC capability. | Mechanical Issue
Brown 8 CT | Forced Derate | 59.7073 | Gas Turbine - Blading Design Issue | Reduction in IAC capability. | Mechanical Issue
Brown 8 CT | Forced Derate | 102 | Gas Turbine - IAC Cooler Issue | Reduction in IAC capability. | Mechanical Issue
Brown 9 CT | Forced Derate | 59.7073 | Gas Turbine - Blading Design Issue | Reduction in IAC capability. | Mechanical Issue
Brown 9 CT | Forced Derate | 40.8 | Gas Turbine - IAC Cooler Issue | Reduction in IAC capability. | Mechanical Issue
Ghent 2 | Forced Derate | 1424.75 | Other Stack Or Exhaust Emissions -fossil Stm Unit | Unit is limited due to H2SO4 emission being high. | Mechanical Issue
Mill Creek 1 | Forced Derate | 39.9409 | Pulverizer Mills | 1C Coal Mill - Inspection | Mechanical Issue
Mill Creek 1 | Forced Derate | 214.2424 | Pulverizer Mills | 1C Coal Mill - Adjusted Rollers | Mechanical Issue
Mill Creek 3 | Forced Derate | 58.5523 | Wet Scrubber - Recycle (liquid) Pumps | FGD 3A1 Recycle Pump - Remove Blank | Mechanical Issue
Mill Creek 4 | Forced Outage | 11544 | Other Ac Instrument Power Problems | Electrical Wiring - Burnt Wiring in Wire Tray | Mechanical Issue
Trimble County 2 | Forced Derate | 2426.2145 | Other Feedwater Valves | Derate on the unit due to a packing leak on a feedwater bypass valve. | Mechanical Issue
Trimble County 2 | Forced Outage | 7777.5 | Other Feedwater Valves | Packing leak on feedwater start-up bypass valve required unit to be taken off | Mechanical Issue
Zorn 1 CT | Forced Outage | 225.1667 | Lack Of Fuel (OMC) | Gas line repairs due to explosion on main gas line on 9/17/14 near Goshen Kentucky | Fuel Supply Disruption
2014-12-11 | 23697.8831
Brown 10 CT | Forced Derate | 452.7194 | Other Gas Turbine Low Pressure Problems | Blade design issues has unit limited to 120MWs. | Mechanical Issue
Brown 11 CT | Forced Derate | 214.3256 | Other Gas Turbine Low Pressure Problems | Blade design issues has unit limited to 120MWs. | Mechanical Issue
Brown 5 CT | Forced Derate | 261.9847 | Other Gas Turbine Low Pressure Problems | Blade design issues has unit limited to 120MWs. | Mechanical Issue
Brown 8 CT | Forced Derate | 214.3256 | Other Gas Turbine Low Pressure Problems | Blade design issues has unit limited to 120MWs. | Mechanical Issue
Brown 9 CT | Forced Derate | 452.7194 | Other Gas Turbine Low Pressure Problems | Blade design issues has unit limited to 120MWs. | Mechanical Issue
Ghent 1 | Forced Outage | 1499.1167 | First Reheater Leaks | Reheat pendant tube ruptured a few feet out from the east side of the boi | Mechanical Issue
Ghent 1 | Forced Derate | 578.5335 | Boiler Water Condition | High boiler drum silica after start up. | Mechanical Issue
Ghent 4 | Forced Derate | 267.1077 | Boiler Water Condition | High boiler drum silica on start up after Fall Outage. | Mechanical Issue
Ghent 4 | Forced Derate | 166.7316 | Induced Draft Fan Controls | FD fan master was indicating 100%. | Mechanical Issue
Ghent 4 | Forced Derate | 248.4883 | High Pressure Heater Problems | HP Heaters are out of service for level control investigation. | Mechanical Issue
Green River 4 | Forced Outage | 731.7333 | Second Superheater Leaks | GR4 taken out of service in an orderly manner due to Sec SH Section tube leak. | Mechanical Issue
Mill Creek 1 | Forced Derate | 2071.4182 | Boiler Water Condition | High Silica | Mechanical Issue
Mill Creek 2 | Forced Derate | 2261.5273 | Boiler Water Condition | High Silica | Mechanical Issue
Mill Creek 3 | Forced Derate | 2190.7518 | Boiler Water Condition | High Silica | Mechanical Issue
Mill Creek 4 | Forced Outage | 11664 | Condenser Tube Leaks | Condenser Tube Leaks | Mechanical Issue
Trimble County 7 CT | Forced Outage | 211.2 | Gas Turbine - Starting System (including Motor) | Static Start 89SS switch failed to engage on TC8. Adjustments made to limit switch | Mechanical Issue
Trimble County 8 CT | Forced Outage | 211.2 | Gas Turbine - Starting System (including Motor) | Static start 89SS switch failed to engage. Adjustments made to limit switches | Mechanical Issue
2014-12-18 | 21861.7798
Brown 10 CT | Forced Derate | 452.7194 | Other Gas Turbine Low Pressure Problems | Blade design issues has unit limited to 120MWs. | Mechanical Issue
Brown 11 CT | Forced Derate | 214.3256 | Other Gas Turbine Low Pressure Problems | Blade design issues has unit limited to 120MWs. | Mechanical Issue
Brown 5 CT | Forced Derate | 261.9847 | Other Gas Turbine Low Pressure Problems | Blade design issues has unit limited to 120MWs. | Mechanical Issue
Brown 8 CT | Forced Derate | 214.3256 | Other Gas Turbine Low Pressure Problems | Blade design issues has unit limited to 120MWs. | Mechanical Issue
Brown 9 CT | Forced Derate | 452.7194 | Other Gas Turbine Low Pressure Problems | Blade design issues has unit limited to 120MWs. | Mechanical Issue
Green River 3 | Forced Derate | 56.3267 | Opacity (fossil) | GR3 load reduction due to B4 combustion issues resulting in high opacity. | Mechanical Issue
Green River 3 | Forced Derate | 73.3667 | Opacity (fossil) | GR3 load reduction due to B4 combustion issues. Derate reduction from Event #86. | Mechanical Issue
Mill Creek 1 | Forced Derate | 283.8712 | Boiler Water Condition | High Silica | Mechanical Issue
Mill Creek 1 | Forced Derate | 6.8864 | Boiler water condition (not feedwater water quality) | High Silica | Mechanical Issue
Mill Creek 2 | Forced Derate | 160.0707 | Boiler Water Condition | High Silica | Mechanical Issue
Mill Creek 2 | Forced Derate | 137.4192 | Boiler Water Condition | High Silica | Mechanical Issue
Mill Creek 4 | Forced Outage | 5742.9 | Condenser Tube Leaks | High Silica | Mechanical Issue
Trimble County 1 | Forced Derate | 64.2226 | Pulverizer motors and drives | Coal Pulverizer motor current increased above the high limit, forcing a derate. | Mechanical Issue
Trimble County 1 | Forced Derate | 60.6417 | Pulverizer motors and drives | Coal pulverizer motor current increased above the high limit, forcing a derate. | Mechanical Issue
Trimble County 2 | Forced Outage | 13680 | Boiler Tube Leak(s) | Boiler Tube Leak(s) | Mechanical Issue
2014-12-06 | 21789.0693
Brown 1 | Forced Derate | 15.4243 | Wet Coal | Wet coal | Mechanical Issue
Brown 1 | Forced Derate | 45.2091 | Pulverizer Mills | 1-4 mill broken spring bolt | Mechanical Issue
Brown 10 CT | Forced Derate | 452.7194 | Other Gas Turbine Low Pressure Problems | Blade design issues has unit limited to 120MWs. | Mechanical Issue
Brown 11 CT | Forced Derate | 214.3256 | Other Gas Turbine Low Pressure Problems | Blade design issues has unit limited to 120MWs. | Mechanical Issue
Brown 5 CT | Forced Derate | 261.9847 | Other Gas Turbine Low Pressure Problems | Blade design issues has unit limited to 120MWs. | Mechanical Issue
Brown 8 CT | Forced Derate | 214.3256 | Other Gas Turbine Low Pressure Problems | Blade design issues has unit limited to 120MWs. | Mechanical Issue
Brown 9 CT | Forced Derate | 452.7194 | Other Gas Turbine Low Pressure Problems | Blade design issues has unit limited to 120MWs. | Mechanical Issue
Ghent 4 | Forced Derate | 846.5612 | Boiler Water Condition | High boiler drum silica on start up after Fall Outage. | Mechanical Issue
Green River 3 | Forced Outage | 463.8667 | Condenser Tube Leaks | GR3 taken out of service in an orderly manner due to boiler chemistry indication | Mechanical Issue
Green River 4 | Forced Derate | 42.7 | Opacity - Fossil Steam Units | GR4 load reduction due to opacity. Blowing soot and cleaning boiler. | Mechanical Issue
Mill Creek 2 | Forced Outage | 7176 | Condenser Tube Leaks | Condenser Tube Leak | Mechanical Issue
Mill Creek 4 | Forced Outage | 299.7 | Boiler Drums And Drum Internals | Low Drum Level Trip - Operator Error | Mechanical Issue
Trimble County 2 | Forced Outage | 10887 | High Pressure Heater Problems | While attempting to isolate the 8A heater for repair, the 8A heater bypass valve | Mechanical Issue
Trimble County 5 CT | Forced Outage | 416.5333 | Gas Turbine - High Engine Exhaust Temperature | Exhaust thermocouple #1 failed high before reaching mode 6, | Mechanical Issue
2014-12-13 | 21633.378
Brown 10 CT | Forced Derate | 452.7194 | Other Gas Turbine Low Pressure Problems | Blade design issues has unit limited to 120MWs. | Mechanical Issue
Brown 11 CT | Forced Derate | 214.3256 | Other Gas Turbine Low Pressure Problems | Blade design issues has unit limited to 120MWs. | Mechanical Issue
Brown 5 CT | Forced Derate | 261.9847 | Other Gas Turbine Low Pressure Problems | Blade design issues has unit limited to 120MWs. | Mechanical Issue
Brown 8 CT | Forced Derate | 214.3256 | Other Gas Turbine Low Pressure Problems | Blade design issues has unit limited to 120MWs. | Mechanical Issue
Brown 9 CT | Forced Derate | 452.7194 | Other Gas Turbine Low Pressure Problems | Blade design issues has unit limited to 120MWs. | Mechanical Issue
Ghent 4 | Forced Outage | 2078.5667 | Induced Draft Fans | U4 Boiler tripped on "Low Furnace Pressure" ... 4-2A and 4-2B ID fan. | Mechanical Issue
Mill Creek 1 | Forced Derate | 2203.6364 | Boiler Water Condition | High Silica | Mechanical Issue
Mill Creek 2 | Forced Derate | 1522.1818 | Boiler Water Condition | High Silica | Mechanical Issue
Mill Creek 3 | Forced Derate | 2190.7518 | Boiler Water Condition | High Silica | Mechanical Issue
Mill Creek 4 | Forced Outage | 10716.3 | Condenser Tube Leaks | Condenser Tube Leaks | Mechanical Issue
Trimble County 8 CT | Forced Outage | 1325.8667 | Switchyard Circuit Breakers | Generator line breaker failed to operate due to springs not charging. | Mechanical Issue
2014-07-03 | 21555.8901
Brown 10 CT | Forced Derate | 59.7073 | Gas Turbine - Blading Design Issue | Reduction in IAC capability. | Mechanical Issue
Brown 11 CT | Forced Derate | 59.7073 | Gas Turbine - Blading Design Issue | Reduction in IAC capability. | Mechanical Issue
Brown 5 CT | Forced Derate | 225.7099 | Gas Turbine - Blading Design Issue | Reduction in IAC capability. | Mechanical Issue
Brown 8 CT | Forced Derate | 59.7073 | Gas Turbine - Blading Design Issue | Reduction in IAC capability. | Mechanical Issue
Brown 9 CT | Forced Derate | 59.7073 | Gas Turbine - Blading Design Issue | Reduction in IAC capability. | Mechanical Issue
Mill Creek 3 | Forced Outage | 3323.5 | Boiler - Master Fuel Trip | Master Fuel Trip | Mechanical Issue
Mill Creek 3 | Forced Outage | 1159.9667 | Feedwater Recirc Valves - Low Drum Level | Low Drum Level - TDBFP Recirc Valve Issues | Mechanical Issue
Mill Creek 4 | Forced Derate | 265.7176 | Combustion/Steam Controls - Max Steam Flow | Max Steam Flow Issue | Mechanical Issue
Trimble County 2 | Forced Outage | 13176 | Turbine - EHC System Problems | The unit was taken offline due to EHC system and turbine valve issues. | Mechanical Issue
Trimble County 7 CT | Forced Outage | 52.3333 | Gas Turbine - Fuel Issues (Gas above set point) | Fuel gas P2 transmitters drifted beyond set point and caused unit to be "not ready | Mechanical Issue
Trimble County 9 CT | Forced Outage | 3113.8333 | Gas Turbine - Battery System Ground | Event 125 was the start to this event, chasing DC grounds in the unit | Mechanical Issue

## 2015 - Total MWh Lost Detail
Unit | Event Type | Daily Net MWh Lost | Cause | Description | Forced Category
2015-05-15 | 43662.1635
Brown 1 | Forced Outage | 2544 | Platen superheater tube leak | SH tube leak | Mechanical Issue
Brown 10 CT | Forced Outage | 831.3 | Load shaft and bearings B | Outage to adjust bearing tilt on #1 exhaust end bearing. | Mechanical Issue
Brown 10 CT | Forced Outage | 334.9 | Load shaft and bearings B | Outage to adjust tilt on exhaust end bearing. | Mechanical Issue
Brown 10 CT | Forced Outage | 1154.3 | Load shaft and bearings B | Outage to adjust bearing tilt on exhaust end bearing. | Mechanical Issue
Cane Run 4 | Maintenance Outage | 3720 | #7 and #8 Control valves won't open completely | #7 & #8 turbine valve maintenance. | N/A
Ghent 1 | Forced Derate | 2.0766 | Induced draft fans near trip point | Operations suspected ID Fan Inlet pressure was near trip point. | Mechanical Issue
Ghent 3 | Maintenance Outage | 11736 | Air heater (seals leaking) | Air heater seals are leaking badly causing large swings in furnace an | N/A
Mill Creek 4 | Forced Derate | 462.2379 | Boiler water condition (silica) | High silica | Mechanical Issue
Mill Creek 4 | Forced Derate | 413.7998 | Boiler water condition (silica) | High silica | Mechanical Issue
Mill Creek 4 | Forced Derate | 152.5108 | Boiler water condition (silica) | High Silica | Mechanical Issue
Mill Creek 4 | Forced Derate | 223.7687 | Air heater (high differential) | 4A Air heater pressure differential | Mechanical Issue
Paddy's Run 11 CT | Forced Outage | 141.2 | Starting system (including motor) A | Starting diesel water pump seals and bearing failed. | Mechanical Issue
Paddy's Run 12 CT | Forced Outage | 15.3333 | Other combustor problems B | Combustor temperature went high due to loading of the turbine. | Mechanical Issue
Paddy's Run 12 CT | Forced Outage | 232.6833 | Ccombustor temperature problems | Flamewout due to spike in the combustor temperature. Upon investigation found | Mechanical Issue
Paddy's Run 13 CT | Forced Derate | 763.6364 | Main transformer load limitation | To keep from exceeding 175 MVA limit on GSU. Unit derated 4 MW. | Mechanical Issue
Trimble County 10 CT | Forced Outage | 225.0333 | High pressure compressor bleed valves | Compressor bleed valve limit switches did not disengage, causing a "not ready to s | Mechanical Issue
Trimble County 2 | Forced Outage | 3705.75 | 2A control valve hydraulic system bolt failure issue | A bolt sheared on the 2A control valve hydraulic manifold which resulted in unit t | Mechanical Issue
Trimble County 2 | Maintenance Outage | 9470.25 | Primary air duct expansion joint failure | Maintenance outage to replace a primary air duct expansion joint which had failed, | N/A
Trimble County 5 CT | Maintenance Outage | 3765.3833 | Fire protection system instrumentation and controls | Maintenance outage to prepare for summer run. | N/A
Trimble County 6 CT | Maintenance Outage | 3768 | Fire protection system instrumentation and controls | Maintenance outage to prepare for summer run. | N/A
2015-05-22 | 42800.8474
Brown 1 | Maintenance Outage | 2544 | Flue gas expansion joint leak | Replace Unit 1 & 2 combined duct expansion joint | N/A
Brown 2 | Maintenance Outage | 3984 | Flue gas expansion joint leak | Replace Unit 1 & 2 combined duct expansion joint | N/A
Cane Run 4 | Forced Outage | 2234.5833 | Stator hydrogen meter issue | Calibration of hydrogen purity meter. | Mechanical Issue
Cane Run 5 | Forced Outage | 2153.2 | Waterwall tube leaks | 2 boiler leaks on waterwall @ south ashpit area. | Mechanical Issue
Ghent 1 | Maintenance Outage | 11496 | Intercept valves fine mesh screen removal | The unit was running with fine mesh screens in the Turbine | N/A
Green River 4 | Maintenance Derate | 220.41 | Desuperheater/attemperator control issue | I&E making adjustments to Attemperator calibration due to temperature swinging | N/A
Mill Creek 1 | Forced Outage | 7272 | Air heater (basket issue) | Air pre-heater baskets | Mechanical Issue
Mill Creek 2 | Forced Derate | 6.8409 | FGD Clearwell pump failure | Loss of clearwell pumps | Mechanical Issue
Mill Creek 2 | Forced Derate | 126.1768 | 2B Pulverizer feeder issue | 2B Feeder issues | Mechanical Issue
Mill Creek 4 | Maintenance Outage | 11448 | Air heater (wash) | Air heater wash | N/A
Paddy's Run 12 CT | Forced Outage | 552 | Combustor temperature problems | Flamewout due to spike in the combustor temperature. Upon investigation found | Mechanical Issue
Paddy's Run 13 CT | Forced Derate | 763.6364 | Main transformer load limitation | To keep from exceeding 175 MVA limit on GSU. Unit derated 4 MW. | Mechanical Issue
2015-03-22 | 37457.2546
Brown 10 CT | Forced Derate | 452.7194 | Other low pressure problems B | Blade desing issues has unit limited to 120MWs. | Mechanical Issue
Brown 11 CT | Forced Derate | 214.3256 | Other low pressure problems B | Blade design issues has unit limited to 120MWs. | Mechanical Issue
Brown 5 CT | Forced Derate | 261.9847 | Other low pressure problems B | Blade design issues has unit limited to 120MWs. | Mechanical Issue
Brown 8 CT | Forced Derate | 214.3256 | Other low pressure problems B | Blade design issues has unit limited to 120MWs. | Mechanical Issue
Brown 9 CT | Forced Derate | 452.7194 | Other low pressure problems B | Blade desing issues has unit limited to 120MWs. | Mechanical Issue
Cane Run 5 | Forced Outage | 4032 | Drum relief/safety valves | Following an internal inspection of the steam drum safety | Mechanical Issue
Cane Run 6 | Maintenance Outage | 5760 | Transmission System Switch Form CR6 To CR7. | Transmission system project for Cane Run 7. | N/A
Ghent 2 | Forced Derate | 482.6228 | Boiler water condition (not feedwater water quality) | Boiler chemistry was out of range after unit start up. Silica | Mechanical Issue
Ghent 4 | Maintenance Derate | 1266.118 | Waterwall (Furnace wall) B | Boiler deslag. | N/A
Mill Creek 1 | Forced Derate | 1322.1818 | Scrubber recycle (liquid) pumps | FGD 1B3 Recycle Pump - Bearing Issue | Mechanical Issue
Mill Creek 3 | Maintenance Outage | 9035.7333 | Miscellaneous mechanical failures | Cleaned chevrons | N/A
Trimble County 1 | Maintenance Outage | 9192 | Air heater fouling | Unit was taken out of service to conduct air heater wash on the unit. Other addit | N/A
Trimble County 2 | Forced Derate | 174.584 | Reheat steam relief/safety valves | Unit is derated due to reheat safety valve that will not lift, which was discovere | Mechanical Issue
Trimble County 2 | Forced Derate | 371.9399 | Reheat steam relief/safety valves | Unit is derated due to reheat safety valve that will not lift, which was discovere | Mechanical Issue
Trimble County 6 CT | Maintenance Outage | 4224 | Fuel piping and valves A | Rebuild Fuel Gas Control Valves PM2 and PM3 due to erractic behavior. | N/A
2015-05-14 | 37271.8061
Brown 1 | Maintenance Outage | 505.2667 | Hydrogen system leak | Investigate and repair generator H2 leak | N/A
Brown 1 | Forced Outage | 84.8 | Platen superheater tube leak | SH tube leak | Mechanical Issue
Brown 10 CT | Forced Outage | 929.9 | Load shaft and bearings B | Outage to adjust bearing tilt on #1 bearing exhaust end | Mechanical Issue
Brown 10 CT | Forced Outage | 1419.5 | Load shaft and bearings B | Outage to adjust bearing tilt on #1 exhaust end bearing. | Mechanical Issue
Brown 8 CT | Forced Outage | 164.9 | Switchyard circuit breakers - (not omc) | Hydraulic leak on Substation generator circuit breaker would not allow breaker to | Mechanical Issue
Cane Run 4 | Maintenance Outage | 3720 | #7 and #8 Control valves won't open completely | #7 & #8 turbine valve maintenance. | N/A
Ghent 3 | Maintenance Outage | 11736 | Air heater (seals leaking) | Air heater seals are leaking badly causing large swings in furnace an | N/A
Ghent 4 | Maintenance Derate | 345.1089 | SO3 mitigation (SAM test) | Low-load SAM test. | N/A
Mill Creek 4 | Forced Derate | 167.3037 | Air heater (high differential) | 4A air heater pressure differential | Mechanical Issue
Mill Creek 4 | Forced Outage | 946.05 | Induced draft fan suction pressure trip | ID fan sunction pressure trip | Mechanical Issue
Mill Creek 4 | Forced Outage | 222.6 | Drums and drum internals (high drum level trip) | High drum level trip | Mechanical Issue
Mill Creek 4 | Forced Derate | 590.6373 | Boiler water condition (silica) | High silica | Mechanical Issue
Paddy's Run 13 CT | Forced Derate | 763.6364 | Main transformer load limitation | To keep from exceeding 175 MVA limit on GSU. Unit derated 4 MW. | Mechanical Issue
Trimble County 2 | Forced Derate | 422.3365 | 6A High pressure heater tube leaks | The 6A HP Feedwater heater had tube leaks and unit required derate while heater is | Mechanical Issue
Trimble County 2 | Forced Outage | 7795.8 | 2A control valve hydraulic system bolt failure issue | A bolt sheared on the 2A control valve hydraulic manifold which resulted in unit t | Mechanical Issue
Trimble County 5 CT | Maintenance Outage | 3768 | Fire protection system instrumentation and controls | Maintenance outage to prepare for summer run. | N/A
Trimble County 6 CT | Maintenance Outage | 3652.8667 | Fire protection system instrumentation and controls | Maintenance outage to prepare for summer run. | N/A
Zorn 1 CT | Maintenance Outage | 37.1 | Starting system (including motor) A | Yearly servicing of the starting diesel engine. | N/A
2015-03-21 | 37223.8442
Brown 10 CT | Forced Derate | 452.7194 | Other low pressure problems B | Blade desing issues has unit limited to 120MWs. | Mechanical Issue
Brown 11 CT | Forced Derate | 214.3256 | Other low pressure problems B | Blade design issues has unit limited to 120MWs. | Mechanical Issue
Brown 5 CT | Forced Derate | 261.9847 | Other low pressure problems B | Blade design issues has unit limited to 120MWs. | Mechanical Issue
Brown 8 CT | Forced Derate | 214.3256 | Other low pressure problems B | Blade design issues has unit limited to 120MWs. | Mechanical Issue
Brown 9 CT | Forced Derate | 452.7194 | Other low pressure problems B | Blade desing issues has unit limited to 120MWs. | Mechanical Issue
Cane Run 5 | Forced Outage | 4032 | Drum relief/safety valves | Following an internal inspection of the steam drum safety | Mechanical Issue
Cane Run 6 | Maintenance Outage | 5760 | Transmission System Switch Form CR6 To CR7. | Transmission system project for Cane Run 7. | N/A
Ghent 3 | Maintenance Derate | 1095.0638 | Waterwall (Furnace wall) B | Boiler deslag. | N/A
Mill Creek 1 | Forced Derate | 1322.1818 | Scrubber recycle (liquid) pumps | FGD 1B3 Recycle Pump - Bearing Issue | Mechanical Issue
Mill Creek 3 | Maintenance Outage | 9456 | Miscellaneous mechanical failures | Cleaned chevrons | N/A
Trimble County 1 | Maintenance Outage | 9192 | Air heater fouling | Unit was taken out of service to conduct air heater wash on the unit. Other addit | N/A
Trimble County 2 | Forced Derate | 546.5239 | Reheat steam relief/safety valves | Unit is derated due to reheat safety valve that will not lift, which was discovere | Mechanical Issue
Trimble County 6 CT | Maintenance Outage | 4224 | Fuel piping and valves A | Rebuild Fuel Gas Control Valves PM2 and PM3 due to erractic behavior. | N/A
2015-08-14 | 36510.7002
Brown 10 CT | Forced Derate | 95.2131 | Gas turbine problems | Unit derated to 113MW due to chilled air inlet coil freeze damage | Mechanical Issue
Brown 11 CT | Forced Derate | 47.6066 | Gas turbine problems | Unit derated to 120 MWs for row 3 blade design issues. | Mechanical Issue
Brown 2 | Forced Derate | 68.3226 | 2-4 coal mill noise & vibration | Excessive noise and vibration in 2-4 mill | Mechanical Issue
Brown 8 CT | Forced Derate | 166.623 | Gas turbine problems | Unit derated to 120 MWs for row 3 blade design issues, and to 115 MWs for chilled | Mechanical Issue
Brown 9 CT | Forced Derate | 95.2131 | Gas turbine problems | Unit derated to 120 MWs for row 3 blade design issues, and to 118 MWs for chilled | Mechanical Issue
Ghent 1 | Forced Outage | 11376 | Other Main Steam Valves | A leak developed in the Main Steam line drain S9. Removed the unit from | Mechanical Issue
Ghent 3 | Forced Outage | 10508.3333 | First superheater BTF | Primary Superheater developed a tube leak that required the unit to be removed | Mechanical Issue
Ghent 4 | Forced Outage | 627.75 | Feedwater regulating (boiler level control) valve | Adjustments were being made to HP heater level controls and the HP heater | Mechanical Issue
Mill Creek 1 | Maintenance Outage | 7200 | Reheat stop valves | Turbine Reheat Stop Valves - Remove Screens/Baskets | N/A
Mill Creek 3 | Maintenance Derate | 1162.2212 | Cooling tower fan bus issue | Cooling Tower Fan H - Breaker Issue | N/A
Paddy's Run 13 CT | Forced Derate | 763.6364 | Main transformer load limitation | To keep from exceeding 175 MVA limit on GSU. Unit derated 4 MW. | Mechanical Issue
Trimble County 2 | Maintenance Derate | 583.7809 | high pressure heater problems | Repairs were being done on the 8A and 8B FWH safeties due to the earlier TC2 FW | N/A
Trimble County 9 CT | Maintenance Outage | 3816 | Lube oil pumps replacement issue | Maintenance outage to replace 88QA-1 Aux. Lube Oil pump. No borescopes performed d | N/A
2015-05-16 | 35683.239
Brown 1 | Forced Outage | 256.1667 | Platen superheater tube leak | SH tube leak | Mechanical Issue
Brown 10 CT | Forced Outage | 884 | Load shaft and bearings B | Outage to adjust bearing tilt on exhaust end bearing. | Mechanical Issue
Brown 10 CT | Forced Outage | 1353.2 | Load shaft and bearings B | Outage to adjust bearing tilt on exhaust end bearing. | Mechanical Issue
Cane Run 4 | Maintenance Outage | 3720 | #7 and #8 Control valves won't open completely | #7 & #8 turbine valve maintenance. | N/A
Ghent 3 | Maintenance Outage | 11736 | Air heater (seals leaking) | Air heater seals are leaking badly causing large swings in furnace an | N/A
Green River 4 | Forced Outage | 1920.45 | 480-volt circuit breakers flooded (ash line failure) | Broken ash discharge piping flooded 5-1 BRMCC causing loss of critical equipment. | Mechanical Issue
Mill Creek 4 | Forced Derate | 376.4333 | Air heater (high differential) | 4A Air heater pressure differential | Mechanical Issue
Paddy's Run 11 CT | Forced Outage | 288 | Starting system (including motor) A | Starting diesel water pump seals and bearing failed. | Mechanical Issue
Paddy's Run 12 CT | Forced Outage | 552 | Ccombustor temperature problems | Flamewout due to spike in the combustor temperature. Upon investigation found | Mechanical Issue
Paddy's Run 13 CT | Forced Derate | 763.6364 | Main transformer load limitation | To keep from exceeding 175 MVA limit on GSU. Unit derated 4 MW. | Mechanical Issue
Paddy's Run 13 CT | Forced Outage | 58.8 | Other fuel quality problems | High gas pressure. | Fuel Supply Issue
Trimble County 1 | Forced Derate | 9.4193 | 1A Pulverizer mill runback | 1A coal mill ran back to minimum and was removed from service, S/M inspected the m | Mechanical Issue
Trimble County 1 | Forced Derate | 233.0501 | 1A, 1C, 1D Pulverizer mill issues | Unit had issues with 1A, 1C, and 1D mills that required derate to inspect issues. | Mechanical Issue
Trimble County 2 | Maintenance Outage | 10065 | Primary air duct expansion joint failure | Maintenance outage to replace a primary air duct expansion joint which had failed, | N/A
Trimble County 6 CT | Maintenance Outage | 3467.0833 | Fire protection system instrumentation and controls | Maintenance outage to prepare for summer run. | N/A
2015-05-21 | 34626.3929
Brown 1 | Maintenance Outage | 415.1667 | Flue gas expansion joint leak | Replace Unit 1 & 2 combined duct expansion joint | N/A
Brown 11 CT | Maintenance Outage | 686.8 | DCS - hardware problems (including card failure) | Outage to replace DCS IO card. | N/A
Brown 2 | Maintenance Outage | 907.4667 | Flue gas expansion joint leak | Replace Unit 1 & 2 combined duct expansion joint | N/A
Cane Run 4 | Forced Outage | 1454.4167 | Stator windings inspection | Open generator for inspection. | Mechanical Issue
Cane Run 4 | Forced Outage | 198.9167 | LP steam turbine vibration / back pressure loss | Loss of unit back pressure while trying to control LP bearing vibration. | Mechanical Issue
Cane Run 4 | Forced Outage | 126.5833 | LP steam turbine vibration / back pressure loss | Loss of unit back pressure while trying to control LP bearing vibration. | Mechanical Issue
Cane Run 4 | Forced Outage | 860.25 | Generator stator noise and temp issues | Generator noise & heating issues. | Mechanical Issue
Cane Run 4 | Forced Outage | 353.9167 | Stator hydrogen meter issue | Calibration of hydrogen purity meter. | Mechanical Issue
Ghent 1 | Maintenance Outage | 11496 | Intercept valves fine mesh screen removal | The unit was running with fine mesh screens in the Turbine | N/A
Ghent 2 | Forced Derate | 382.5 | 2-6c burner temp issue | Operations took 2-6 Mill out of service after attempts to stop t | Mechanical Issue
Green River 4 | Maintenance Derate | 55.8 | Desuperheater/attemperator control issue | I&E making adjustments to Attemperator calibration due to temperature swinging | N/A
Mill Creek 1 | Forced Outage | 7272 | Air heater (basket issue) | Air pre-heater baskets | Mechanical Issue
Mill Creek 2 | Maintenance Outage | 2392.95 | WFGD Inspection | WFGD Inspection | N/A
Mill Creek 2 | Forced Derate | 183.9444 | Boiler water condition (silica) | High silica | Mechanical Issue
Mill Creek 2 | Forced Derate | 559.4343 | Boiler water condition (silica) | High Silica | Mechanical Issue
Mill Creek 4 | Forced Derate | 207.5611 | Air heater (high differential) | 4A Air heater pressure differential | Mechanical Issue
Mill Creek 4 | Maintenance Outage | 5135.7 | Air heater (wash) | Air heater wash | N/A
Paddy's Run 11 CT | Forced Outage | 158.2 | Starting system (including motor) A | Starting diesel water pump seals and bearing failed. | Mechanical Issue
Paddy's Run 12 CT | Forced Outage | 552 | Ccombustor temperature problems | Flamewout due to spike in the combustor temperature. Upon investigation found | Mechanical Issue
Paddy's Run 13 CT | Forced Derate | 763.6364 | Main transformer load limitation | To keep from exceeding 175 MVA limit on GSU. Unit derated 4 MW. | Mechanical Issue
Trimble County 5 CT | Maintenance Outage | 463.15 | Expansion joints A | Exhaust duct expansion joint inspection to determine repair procedure. | N/A
2015-08-15 | 32092.1413
Ghent 1 | Forced Outage | 11376 | Other Main Steam Valves | A leak developed in the Main Steam line drain S9. Removed the unit from | Mechanical Issue
Mill Creek 1 | Maintenance Outage | 3825 | Reheat stop valves | Turbine Reheat Stop Valves - Remove Screens/Baskets | N/A
Ghent 3 | Forced Outage | 10265.8333 | First superheater BTF | Primary Superheater developed a tube leak that required the unit to be removed | Mechanical Issue
Trimble County 2 | Maintenance Derate | 1868.099 | high pressure heater problems | Repairs were being done on the 8A and 8B FWH safeties due to the earlier TC2 FW | N/A
Mill Creek 1 | Forced Outage | 1145 | AC Protection devices | Generator Lockout - Protective Relays | Mechanical Issue
Trimble County 2 | Maintenance Derate | 194.8669 | high pressure heater problems | The deslag was finished and repairs continued on the 8A and 8B FWH safeties. | N/A
Mill Creek 1 | Forced Outage | 265 | Drums and drum internals (single drum only) | High Drum Level Trip | Mechanical Issue
Mill Creek 1 | Forced Outage | 190 | Drums and drum internals (single drum only) | High Drum Level Trip | Mechanical Issue
Paddy's Run 13 CT | Forced Derate | 763.6364 | Main transformer load limitation | To keep from exceeding 175 MVA limit on GSU. Unit derated 4 MW. | Mechanical Issue
Brown 8 CT | Forced Derate | 166.623 | Gas turbine problems | Unit derated to 120 MWs for row 3 blade design issues, and to 115 MWs for chilled | Mechanical Issue
Trimble County 9 CT | Maintenance Outage | 1794.05 | Lube oil pumps replacement issue | Maintenance outage to replace 88QA-1 Aux. Lube Oil pump. No borescopes performed d | N/A
Brown 9 CT | Forced Derate | 95.2131 | Gas turbine problems | Unit derated to 120 MWs for row 3 blade design issues, and to 118 MWs for chilled | Mechanical Issue
Brown 10 CT | Forced Derate | 95.2131 | Gas turbine problems | Unit derated to 113MW due to chilled air inlet coil freeze damage | Mechanical Issue
Brown 11 CT | Forced Derate | 47.6066 | Gas turbine problems | Unit derated to 120 MWs for row 3 blade design issues. | Mechanical Issue
2015-01-18 | 32018.1854
Brown 10 CT | Forced Derate | 452.7194 | Other low pressure problems B | Blade desing issues has unit limited to 120MWs. | Mechanical Issue
Brown 11 CT | Forced Derate | 214.3256 | Other low pressure problems B | Blade design issues has unit limited to 120MWs. | Mechanical Issue
Brown 5 CT | Forced Derate | 261.9847 | Other low pressure problems B | Blade design issues has unit limited to 120MWs. | Mechanical Issue
Brown 8 CT | Forced Derate | 214.3256 | Other low pressure problems B | Blade design issues has unit limited to 120MWs. | Mechanical Issue
Brown 9 CT | Forced Derate | 452.7194 | Other low pressure problems B | Blade desing issues has unit limited to 120MWs. | Mechanical Issue
Cane Run 11 CT | Forced Derate | 240 | Exhaust Temperature At Limit | High Exhaust Temperature Issues. | Mechanical Issue
Cane Run 6 | Maintenance Outage | 5760 | Turbine bearing damage | CR6 - #4 turbine bearing wiped. | N/A
Ghent 1 | Forced Derate | 315.2085 | Pulverizer grinding section noise | 1-3 Mill off to inspect noise in the grinding section. | Mechanical Issue
Ghent 3 | Maintenance Outage | 11568 | Air heater seal leaks | Unit 1 was running with leaking on the Air Heater seals | N/A
Green River 4 | Forced Derate | 38.9667 | Opacity issues | GR4 load reduction for boiler cleaning due to opacity issues. | Mechanical Issue
Green River 4 | Forced Outage | 1154.7667 | Waterwall tube leak | GR4 removed from service in an orderly manner due to waterwall tube leak. | Mechanical Issue
Mill Creek 2 | Maintenance Outage | 7176 | Hydrogen leak in bushing box | Generator Bushing Box - Hydrogen Leak Repair | N/A
Mill Creek 4 | Maintenance Derate | 3141.6429 | FGD emissions testing | FGD Performance Testing | N/A
Mill Creek 4 | Forced Outage | 623.7 | Reheat/intercept valve testing | Turbine Reheat/Intercept Valve Check - Trip | Mechanical Issue
Trimble County 1 | Forced Derate | 60.1357 | Pulverizer fires | The 1D coal mill had a temperature spike which brought the mill offline | Mechanical Issue
Trimble County 2 | Forced Derate | 343.6903 | Other turbine valves | Unit was derated 20MW due to HP turbine bypass valve leak through. This required | Mechanical Issue

## 2015 - Forced MWh Lost Detail
Unit | Event Type | Daily Net Forced MWh Lost | Cause | Description | Forced Category
2015-01-26 | 31577.6317
Brown 10 CT | Forced Derate | 452.7194 | Other low pressure problems B | Blade desing issues has unit limited to 120MWs. | Mechanical Issue
Brown 11 CT | Forced Derate | 214.3256 | Other low pressure problems B | Blade design issues has unit limited to 120MWs. | Mechanical Issue
Brown 3 | Forced Outage | 7590 | Main Steam Piping leak before Turbine Stop Valves | Pin hole leak in main steam drain line prior to isolation valve. | Mechanical Issue
Brown 5 CT | Forced Derate | 261.9847 | Other low pressure problems B | Blade design issues has unit limited to 120MWs. | Mechanical Issue
Brown 6 CT | Forced Outage | 22.8 | Compressor valve problems | Blow off valve not staying closed while unit is online | Mechanical Issue
Brown 6 CT | Forced Outage | 478.8 | Compressor valve problems | Compressor blow off valve not staying closed while unit online | Mechanical Issue
Brown 8 CT | Forced Derate | 214.3256 | Other low pressure problems B | Blade design issues has unit limited to 120MWs. | Mechanical Issue
Brown 8 CT | Forced Outage | 285.8667 | Starting system (including motor) B | Power oil valve on trip block not showing fully closed in controls. | Mechanical Issue
Brown 9 CT | Forced Derate | 452.7194 | Other low pressure problems B | Blade desing issues has unit limited to 120MWs. | Mechanical Issue
Ghent 2 | Forced Outage | 9476.4 | Steam turbine overspeed control problems | During the previous event of the UAT-2 differential, the Main Turbine went into overspeed | Mechanical Issue
Ghent 4 | Forced Outage | 11784 | Water side cleaning (acid cleaning) | While filling the boiler for startup from the previous Maintenance event, | Mechanical Issue
Trimble County 2 | Forced Derate | 343.6903 | Other turbine valves | Unit was derated 20MW due to HP turbine bypass valve leak through. This required | Mechanical Issue
2015-09-01 | 28287.8071
Brown 10 CT | Forced Derate | 95.2131 | Gas turbine problems | Unit derated to 113MW due to chilled air inlet coil freeze damage | Mechanical Issue
Brown 11 CT | Forced Derate | 47.6066 | Gas turbine problems | Unit derated to 120 MWs for row 3 blade design issues. | Mechanical Issue
Brown 2 | Forced Derate | 459.7512 | Feedwater pump | Repair 2-1 BFP balance line leak | Mechanical Issue
Brown 3 | Forced Derate | 177.6667 | Pulverized fuel and air piping | 3-4 mill burner line fire | Mechanical Issue
Brown 3 | Forced Derate | 74.1905 | Pulverizer mills | Inspect 3-2 mill motor coupling | Mechanical Issue
Brown 3 | Forced Derate | 804.2308 | Pulverizer mills | Replace 3-2 mill motor to mill coupling | Mechanical Issue
Brown 8 CT | Forced Derate | 166.623 | Gas turbine problems | Unit derated to 120 MWs for row 3 blade design issues, and to 115 MWs for chilled | Mechanical Issue
Brown 9 CT | Forced Derate | 95.2131 | Gas turbine problems | Unit derated to 120 MWs for row 3 blade design issues, and to 118 MWs for chilled | Mechanical Issue
Cane Run 7 | Forced Derate | 2156.05 | Cooling and seal air system | CT 2 - Leaking flange on compressor stage 11 bleed line. Gasket replaced | Mechanical Issue
Ghent 1 | Forced Outage | 10317.4 | First superheater BTF | Unit 1 developed what appeared to be a leak in the Primary Superheater | Mechanical Issue
Ghent 3 | Forced Outage | 11640 | Economizer BTF | Unit 3 developed a tube leak in the Economizer section of the Boiler. | Mechanical Issue
Green River 4 | Forced Derate | 10.664 | high pressure turbine performance issues | Excessive steam flow due to HP Turbine efficiency. | Mechanical Issue
Paddy's Run 11 CT | Forced Outage | 312 | Ignition system water damage | Compartment that houses the ignition transformers was filled with water and shorted | Mechanical Issue
Paddy's Run 13 CT | Forced Derate | 763.6364 | Main transformer load limitation | To keep from exceeding 175 MVA limit on GSU. Unit derated 4 MW. | Mechanical Issue
Trimble County 2 | Forced Derate | 1167.5619 | feedwater valve packing issue | Load was dropped so a contractor could safely work on a feedwater valve packing | Mechanical Issue
2015-08-31 | 26184.0158
Brown 10 CT | Forced Derate | 95.2131 | Gas turbine problems | Unit derated to 113MW due to chilled air inlet coil freeze damage | Mechanical Issue
Brown 11 CT | Forced Derate | 47.6066 | Gas turbine problems | Unit derated to 120 MWs for row 3 blade design issues. | Mechanical Issue
Brown 2 | Forced Derate | 157.0904 | Feedwater pump | Repair 2-1 BFP balance line leak | Mechanical Issue
Brown 8 CT | Forced Derate | 166.623 | Gas turbine problems | Unit derated to 120 MWs for row 3 blade design issues, and to 115 MWs for chilled | Mechanical Issue
Brown 9 CT | Forced Derate | 95.2131 | Gas turbine problems | Unit derated to 120 MWs for row 3 blade design issues, and to 118 MWs for chilled | Mechanical Issue
Cane Run 7 | Forced Derate | 989.75 | Cooling and seal air system | CT 2 - Leaking flange on compressor stage 11 bleed line. Gasket replaced | Mechanical Issue
Ghent 1 | Forced Outage | 11376 | First superheater BTF | Unit 1 developed what appeared to be a leak in the Primary Superheater | Mechanical Issue
Ghent 3 | Forced Outage | 11640 | Economizer BTF | Unit 3 developed a tube leak in the Economizer section of the Boiler. | Mechanical Issue
Mill Creek 3 | Forced Outage | 540.8833 | Feedwater pump drive - steam turbine trip | Boiler Feed Pump Turbine Driven - Tripped, HMI Failure | Mechanical Issue
Paddy's Run 11 CT | Forced Outage | 312 | Ignition system water damage | Compartment that houses the ignition transformers was filled with water and shorted | Mechanical Issue
Paddy's Run 13 CT | Forced Derate | 763.6364 | Main transformer load limitation | To keep from exceeding 175 MVA limit on GSU. Unit derated 4 MW. | Mechanical Issue
2015-08-15 | 24410.1254
Brown 10 CT | Forced Derate | 95.2131 | Gas turbine problems | Unit derated to 113MW due to chilled air inlet coil freeze damage | Mechanical Issue
Brown 11 CT | Forced Derate | 47.6066 | Gas turbine problems | Unit derated to 120 MWs for row 3 blade design issues. | Mechanical Issue
Brown 8 CT | Forced Derate | 166.623 | Gas turbine problems | Unit derated to 120 MWs for row 3 blade design issues, and to 115 MWs for chilled | Mechanical Issue
Brown 9 CT | Forced Derate | 95.2131 | Gas turbine problems | Unit derated to 120 MWs for row 3 blade design issues, and to 118 MWs for chilled | Mechanical Issue
Ghent 1 | Forced Outage | 11376 | Other Main Steam Valves | A leak developed in the Main Steam line drain S9. Removed the unit from | Mechanical Issue
Ghent 3 | Forced Outage | 10265.8333 | First superheater BTF | Primary Superheater developed a tube leak that required the unit to be removed | Mechanical Issue
Mill Creek 1 | Forced Outage | 265 | Drums and drum internals (single drum only) | High Drum Level Trip | Mechanical Issue
Mill Creek 1 | Forced Outage | 190 | Drums and drum internals (single drum only) | High Drum Level Trip | Mechanical Issue
Mill Creek 1 | Forced Outage | 1145 | AC Protection devices | Generator Lockout - Protective Relays | Mechanical Issue
Paddy's Run 13 CT | Forced Derate | 763.6364 | Main transformer load limitation | To keep from exceeding 175 MVA limit on GSU. Unit derated 4 MW. | Mechanical Issue
2015-08-14 | 23748.698
Brown 10 CT | Forced Derate | 95.2131 | Gas turbine problems | Unit derated to 113MW due to chilled air inlet coil freeze damage | Mechanical Issue
Brown 11 CT | Forced Derate | 47.6066 | Gas turbine problems | Unit derated to 120 MWs for row 3 blade design issues. | Mechanical Issue
Brown 2 | Forced Derate | 68.3226 | 2-4 coal mill noise & vibration | Excessive noise and vibration in 2-4 mill | Mechanical Issue
Brown 8 CT | Forced Derate | 166.623 | Gas turbine problems | Unit derated to 120 MWs for row 3 blade design issues, and to 115 MWs for chilled | Mechanical Issue
Brown 9 CT | Forced Derate | 95.2131 | Gas turbine problems | Unit derated to 120 MWs for row 3 blade design issues, and to 118 MWs for chilled | Mechanical Issue
Ghent 1 | Forced Outage | 11376 | Other Main Steam Valves | A leak developed in the Main Steam line drain S9. Removed the unit from | Mechanical Issue
Ghent 3 | Forced Outage | 10508.3333 | First superheater BTF | Primary Superheater developed a tube leak that required the unit to be removed | Mechanical Issue
Ghent 4 | Forced Outage | 627.75 | Feedwater regulating (boiler level control) valve | Adjustments were being made to HP heater level controls and the HP heater | Mechanical Issue
Paddy's Run 13 CT | Forced Derate | 763.6364 | Main transformer load limitation | To keep from exceeding 175 MVA limit on GSU. Unit derated 4 MW. | Mechanical Issue
2015-02-23 | 19619.6515
Brown 10 CT | Forced Derate | 452.7194 | Other low pressure problems B | Blade desing issues has unit limited to 120MWs. | Mechanical Issue
Brown 10 CT | Forced Outage | 342.7 | Other switchyard equipment - external | F410Failure of MOS limit switches kept unit's GCB from being able to close. | Mechanical Issue
Brown 11 CT | Forced Derate | 214.3256 | Other low pressure problems B | Blade design issues has unit limited to 120MWs. | Mechanical Issue
Brown 3 | Forced Derate | 79.0858 | Other pulverizer problems | 3-5 Mill CO issues | Mechanical Issue
Brown 5 CT | Forced Derate | 261.9847 | Other low pressure problems B | Blade design issues has unit limited to 120MWs. | Mechanical Issue
Brown 6 CT | Forced Outage | 4104 | Starting system (including motor) A | Controls processor failed on static starting device. | Mechanical Issue
Brown 7 CT | Forced Outage | 4104 | Starting system (including motor) A | Control processor on static starting device failed. | Mechanical Issue
Brown 8 CT | Forced Derate | 214.3256 | Other low pressure problems B | Blade design issues has unit limited to 120MWs. | Mechanical Issue
Brown 9 CT | Forced Derate | 452.7194 | Other low pressure problems B | Blade desing issues has unit limited to 120MWs. | Mechanical Issue
Cane Run 11 CT | Forced Outage | 336 | Turning gear and motor C | Turning gear motor failure. | Mechanical Issue
Cane Run 4 | Forced Derate | 19.1443 | 12kV circuit breakers | Load limit placed on CR4 as a precautionary measure until root cause found | Mechanical Issue
Cane Run 5 | Forced Derate | 16.4751 | 12kV circuit breakers | Load limit placed on CR5 as a precautionary measure until root cause found | Mechanical Issue
Cane Run 6 | Forced Outage | 3500 | 12kV circuit breakers | Lost air pressure to the 2A bus tie and the bus tie reacton A breakers | Mechanical Issue
Ghent 2 | Forced Derate | 163.2171 | Feedwater pump | 2-2 BFP inboard oil seal started slinging oil. Found oil pressure | Mechanical Issue
Mill Creek 3 | Forced Derate | 3.198 | Pulverizer feeders | 3A Coal Feeder - Feeder kept tripping | Mechanical Issue
Paddy's Run 11 CT | Forced Outage | 312 | Other fuel quality problems | Gas pressure problems. | Fuel Supply Disruption
Paddy's Run 12 CT | Forced Outage | 672 | Other fuel quality problems | Gas pressure problems. | Fuel Supply Disruption
Trimble County 1 | Forced Derate | 280.2439 | Air heater fouling | Differential pressure across the AH increased and required a derate in order to ke | Mechanical Issue
Trimble County 2 | Forced Derate | 343.6903 | Other turbine valves | Unit was derated 20MW due to HP turbine bypass valve leak through. This required | Mechanical Issue
Trimble County 5 CT | Forced Outage | 442.9333 | Other combustor problems B | Manual shut down signal initiated due high NOx readings | Mechanical Issue
Trimble County 5 CT | Forced Derate | 447.8222 | Other combustor problems B | Load limit set because NOx and dynamics were too high at higher loads. | Mechanical Issue
Trimble County 6 CT | Forced Outage | 1765.8667 | Other combustor problems B | NOx readings while machine was running were too high, machine taken off line manually | Mechanical Issue
Trimble County 6 CT | Forced Outage | 1091.2 | Other combustor problems B | Machine taken off line due to high NOx and dynamics. Machine was running with Auto | Mechanical Issue
2015-08-30 | 19507.7491
Brown 10 CT | Forced Derate | 95.2131 | Gas turbine problems | Unit derated to 113MW due to chilled air inlet coil freeze damage | Mechanical Issue
Brown 11 CT | Forced Derate | 47.6066 | Gas turbine problems | Unit derated to 120 MWs for row 3 blade design issues. | Mechanical Issue
Brown 8 CT | Forced Derate | 166.623 | Gas turbine problems | Unit derated to 120 MWs for row 3 blade design issues, and to 115 MWs for chilled | Mechanical Issue
Brown 8 CT | Forced Outage | 153.2667 | Switchyard circuit breakers - external | Start up failure due to failure to synchronize. | Mechanical Issue
Brown 9 CT | Forced Derate | 95.2131 | Gas turbine problems | Unit derated to 120 MWs for row 3 blade design issues, and to 118 MWs for chilled | Mechanical Issue
Ghent 1 | Forced Outage | 11376 | First superheater BTF | Unit 1 developed what appeared to be a leak in the Primary Superheater | Mechanical Issue
Ghent 3 | Forced Outage | 6369.6667 | Economizer BTF | Unit 3 developed a tube leak in the Economizer section of the Boiler. | Mechanical Issue
Mill Creek 4 | Forced Derate | 49.7298 | Light-off (igniter) system issue | 4C & 4E Coal Mills - Lighter Issues | Mechanical Issue
Paddy's Run 11 CT | Forced Outage | 312 | Ignition system water damage | Compartment that houses the ignition transformers was filled with water and shorted | Mechanical Issue
Paddy's Run 13 CT | Forced Derate | 763.6364 | Main transformer load limitation | To keep from exceeding 175 MVA limit on GSU. Unit derated 4 MW. | Mechanical Issue
Trimble County 2 | Forced Derate | 78.7938 | Pulverizer mill fire issue | 2D Mill began spitting fireflies and smoke out of the pyrite chute. | Mechanical Issue
2015-07-27 | 19485.8479
Brown 10 CT | Forced Derate | 95.2131 | Gas turbine problems | Unit derated to 113MW due to chilled air inlet coil freeze damage | Mechanical Issue
Brown 11 CT | Forced Derate | 47.6066 | Gas turbine problems | Unit derated to 120 MWs for row 3 blade design issues. | Mechanical Issue
Brown 5 CT | Forced Derate | 261.9847 | Gas turbine problems | Unit derated due to Row 3 blade design issues. | Mechanical Issue
Brown 8 CT | Forced Derate | 166.623 | Gas turbine problems | Unit derated to 120 MWs for row 3 blade design issues, and to 115 MWs for chilled | Mechanical Issue
Brown 9 CT | Forced Derate | 95.2131 | Gas turbine problems | Unit derated to 120 MWs for row 3 blade design issues, and to 118 MWs for chilled | Mechanical Issue
Green River 3 | Forced Derate | 126.5556 | Other flue gas problems | There is a restriction in the flue gas path. | Mechanical Issue
Green River 3 | Forced Derate | 243.7926 | Burner instruments and controls | 4-6 Burner (4-1 Pulv) Register door controller will not operate. | Mechanical Issue
Green River 3 | Forced Derate | 27.3889 | flue gas path problems | There is a restriction in the flue gas path. Derate reduced from Event #48. | Mechanical Issue
Green River 4 | Forced Outage | 438.65 | Second superheater B | GR4/B5 removed from service in an orderly manner due to Sec SH Section tube leak. | Mechanical Issue
Green River 4 | Forced Derate | 8.6025 | Other pulverizer problems | 5-2 Pulverizer breaker would not close. I&E replaced the breaker with A spare brea | Mechanical Issue
Mill Creek 1 | Forced Derate | 27.8788 | Pulverizer feeders | 1B Coal Feeder - Replaced Action Pack Relay | Mechanical Issue
Paddy's Run 13 CT | Forced Derate | 763.6364 | Main transformer load limitation | To keep from exceeding 175 MVA limit on GSU. Unit derated 4 MW. | Mechanical Issue
Paddy's Run 13 CT | Forced Derate | 190.7027 | gas turbine load issues | Unit unable to reach full rated Load. | Mechanical Issue
Trimble County 2 | Forced Outage | 13176 | Other high pressure heater problems (see condensate system for LP and IP heater codes) | Low feedwater flow caused by heater 8A and 6A's safeties lifting and not reseating | Mechanical Issue
Trimble County 5 CT | Forced Outage | 3816 | Switchyard circuit breakers - (not outside management control) | The main breaker on TC5 was found with low air pressure in the breaker actuator. | Mechanical Issue
2015-11-30 | 19075.6668
Brown 11 CT | Forced Derate | 214.3256 | Blade Design Issue Limitation | Derate due to R3 turbine blade operational limit set to 120MWs. | Mechanical Issue
Brown 3 | Forced Derate | 2869.9168 | 3-2 Boiler Feedwater Pump Damage Inspection | Inspect 3-2 BFP for damage due to excessive balance line pressure | Mechanical Issue
Brown 5 CT | Forced Derate | 261.9847 | Blade Design Issue Limitation | Derate due to R3 turbine blade operational limit set to 120MWs. | Mechanical Issue
Brown 8 CT | Forced Derate | 214.3256 | Blade Design Issue Limitation | Derate due to R3 turbine blade operational limit set to 120MWs. | Mechanical Issue
Brown 9 CT | Forced Derate | 452.7194 | Blade Design Issue Limitation | Derate due to R3 turbine blade operational limit set to 120MWs. | Mechanical Issue
Ghent 2 | Forced Derate | 107.7233 | 4160-volt circuit breaker failure | U2 FGDA 4KV reserve breaker failed. Dropped load until FGD 4KV | Mechanical Issue
Ghent 4 | Forced Derate | 415.8652 | Steam turbine cooper deposit issues | Load reduced due to turbine copper deposition. | Mechanical Issue
Paddy's Run 11 CT | Forced Outage | 312 | Turning gear and motor solenoid failure | rathcet turning gear failed to engage. Ratchet soleniod has failed. | Mechanical Issue
Paddy's Run 13 CT | Forced Derate | 763.6364 | Main transformer load limitation | To keep from exceeding 175 MVA limit on GSU. Unit derated 4 MW. | Mechanical Issue
Paddy's Run 13 CT | Forced Derate | 405.6818 | Other compressor problems | Unit needs a compressor wash. | Mechanical Issue
Trimble County 10 CT | Forced Derate | 71.6 | Transmission line (connected to powerhouse switchyard to 1st Substation) | F530Outside management control (OMC), inadequate transmission (NITS). | Mechanical Issue
Trimble County 2 | Forced Derate | 36.388 | Feedwater Booster Pump Drive - Steam Turbine | Continued problems with the 2A TDBFP. | Mechanical Issue
Trimble County 2 | Forced Outage | 12207.5 | 2A Forced draft fan vibration MFT | 2A Forced Draft fan vibration caused unit to MFT. | Mechanical Issue
Trimble County 5 CT | Forced Derate | 71.6 | Transmission line (connected to powerhouse switchyard to 1st Substation) | F530Outside management control (OMC), inadequate transmission (NITS). | Mechanical Issue
Trimble County 6 CT | Forced Derate | 71.6 | Transmission line (connected to powerhouse switchyard to 1st Substation) | F530Outside management control (OMC), inadequate transmission (NITS). | Mechanical Issue
Trimble County 7 CT | Forced Derate | 71.6 | Outside management control (OMC), inadequate transmission (NITS). | Outside management control (OMC), inadequate transmission (NITS). | Mechanical Issue
Trimble County 8 CT | Forced Derate | 71.6 | Outside management control (OMC), inadequate transmission (NITS). | Outside management control (OMC), inadequate transmission (NITS). | Mechanical Issue
Trimble County 9 CT | Forced Derate | 71.6 | Transmission line (connected to powerhouse switchyard to 1st Substation) | F530Outside management control (OMC), inadequate transmission (NITS). | Mechanical Issue
Zorn 1 CT | Forced Outage | 384 | Battery and charger system | Battery charge had alarms during startup and shut the unit down. Found a dead short | Mechanical Issue
2015-09-23 | 19053.3649
Brown 10 CT | Forced Derate | 95.2131 | Gas turbine problems | Unit derated to 113MW due to chilled air inlet coil freeze damage | Mechanical Issue
Brown 11 CT | Forced Derate | 47.6066 | Gas turbine problems | Unit derated to 120 MWs for row 3 blade design issues. | Mechanical Issue
Brown 3 | Forced Derate | 231.2821 | 3-5 coal coal mill bunker empty | 3-5 mill coal bunker empty | Mechanical Issue
Brown 8 CT | Forced Derate | 166.623 | Gas turbine problems | Unit derated to 120 MWs for row 3 blade design issues, and to 115 MWs for chilled | Mechanical Issue
Brown 9 CT | Forced Derate | 95.2131 | Gas turbine problems | Unit derated to 120 MWs for row 3 blade design issues, and to 118 MWs for chilled | Mechanical Issue
Ghent 2 | Forced Derate | 1755 | 2-5 pulverizer shaft problems | 2-5 Mill vertical shaft broke. | Mechanical Issue
Paddy's Run 11 CT | Forced Outage | 312 | Ignition system water damage | Compartment that houses the ignition transformers was filled with water and shorted | Mechanical Issue
Paddy's Run 13 CT | Forced Derate | 763.6364 | Main transformer load limitation | To keep from exceeding 175 MVA limit on GSU. Unit derated 4 MW. | Mechanical Issue
Trimble County 2 | Forced Outage | 4373.7 | Main Steam Valve packing leak | Forced outage due to the packing leak in the Non-Return Main Steam MOV. | Mechanical Issue
Trimble County 2 | Forced Derate | 4899.5908 | DCS - MDBFP transfer problems | Due to low load of unit while ramping, there was problem transferring from MDBFP | Mechanical Issue
Trimble County 2 | Forced Outage | 3586.8 | DCS - mill logic problems | While ramping and placing three mills in service, a logic problem caused the mills | Mechanical Issue
Trimble County 2 | Forced Outage | 2507.1 | Light-off (igniter) system failure | As unit was firing, oil guns were lost on the A Mill. This caused a trip on the A | Mechanical Issue
Trimble County 2 | Forced Outage | 219.6 | DCS - feedwater logic problems | Despite the Feedwater Storage Vessel being at high level, the unit was calling for more | Mechanical Issue

## 2016 - Total MWh Lost Detail
Unit | Event Type | Daily Net MWh Lost | Cause | Description | Forced Category
2016-07-02 | 45643.0374
Brown 10 CT | Forced Derate | 166.623 | Inlet air chillers out | Unit derated to 115 MWs due to inet air cooling coils. | Mechanical Issue
Brown 11 CT | Forced Derate | 47.6066 | Row 3 turbine Blade 120 mw limit | Unit derated to 120 MWs due to R3 blade design. | Mechanical Issue
Brown 3 | Forced Outage | 9816 | First reheater BTF | Reheat tube leak | Mechanical Issue
Brown 5 CT | Forced Derate | 309.6183 | Row 3 turbine Blade 120 mw limit & Inlet air chillers out | Unit derated to 120 MWs due to R3 blade design issue, and to 118 MWs due to Inlet | Mechanical Issue
Brown 8 CT | Forced Derate | 95.2131 | Row 3 turbine Blade 120 mw limit & Inlet air chillers out | Unit derated to 120 MWs due to R3 blade design, and to 118MWs due to inet air cool | Mechanical Issue
Brown 9 CT | Forced Derate | 47.6066 | Row 3 turbine Blade 120 mw limit | Unit derated to 120 MWs due to R3 blade design. | Mechanical Issue
Cane Run 7 | Maintenance Outage | 959.9 | Headers between tube bundles | HRSG 2 HPSH vent line leak. Investigated to identify source | N/A
Ghent 1 | Maintenance Derate | 128.4245 | 1-1 pulverizer journal failure | 1-1 Mill was removed from service to replace a journal. | N/A
Ghent 2 | Forced Derate | 112.0455 | Steam turbine copper deposit problems | Turbine performance. Turbine copper deposition. | Mechanical Issue
Ghent 3 | Forced Outage | 11640 | First superheater BTF | Unit 3 was removed from service due to a boiler superheat tube leak. | Mechanical Issue
Mill Creek 1 | Maintenance Outage | 7200 | First reheater BTF | Boiler and condenser tube leaks (Boiler Tube Repair Time) | N/A
Mill Creek 2 | Forced Derate | 1944 | Feedwater pump drive - motor failure | 2A MDBFP - motor | Mechanical Issue
Trimble County 2 | Forced Outage | 13176 | Generator rotor winding and vibration issues. | Unit continued to have problems with bearing #9 vibration and tripped on low steam | Mechanical Issue
2016-03-16 | 43208.1599
Brown 5 CT | Forced Derate | 23.8017 | Row 3 Turbine Blade Design Isuue … 120mw load limit | Derate due to R3 blade design issues. | Mechanical Issue
Cane Run 7 | Forced Derate | 3444.5975 | CT 2 - Lube oil valve/piping leak | Leaking CT2 generator TE bearing oil supply line. Replaced pipe spool | Mechanical Issue
Cane Run 7 | Forced Derate | 199.1774 | CT 2 - Exciter blower problems | CT2 generator collector blower failed to start causing startup trip | Mechanical Issue
Ghent 4 | Forced Outage | 11424 | Economizer BTF | Unit came off line due to a leak in the economizer. | Mechanical Issue
Mill Creek 3 | Forced Outage | 9432 | Main transformer failure/fire | "A" Phase main transformer fire | Mechanical Issue
Paddy's Run 13 CT | Forced Outage | 3864 | Hydraulic oil system A | Hydarulic System Pressure Switch Failure. | Mechanical Issue
Trimble County 10 CT | Forced Outage | 225.3333 | Exciter problems | Unit was made unavailable due to generator exciter problems. | Mechanical Issue
Trimble County 2 | Forced Outage | 6813.3333 | Waterwall (Furnace wall) BTF | Forced outage due to a boiler tube leak. | Mechanical Issue
Trimble County 7 CT | Maintenance Outage | 3129.3167 | Generator current and potential transformers | Maintenance Outage - multiple maintenance items, but largest project is the Genera | N/A
Trimble County 7 CT | Forced Outage | 349.2667 | Lack of fuel | The gas supply valve closed while unit was coming offline. | Mechanical Issue
Trimble County 8 CT | Maintenance Outage | 3501.1167 | Generator current and potential transformers | Maintenance Outage - multiple maintenance items, but largest project is the Genera | N/A
Trimble County 8 CT | Maintenance Derate | 185.9 | Total unit performance testing (use appropriate codes for individual component testing) | Non-curtailing derate for online unit testing while coming back from outage. | N/A
Trimble County 8 CT | Forced Outage | 256.3167 | Lack of fuel | Unit outage due to gas valve closure while unit was coming offline. | Mechanical Issue
Zorn 1 CT | Forced Outage | 360 | Lube oil pumps B | DC Lube Oil Pump Motor Failure. | Mechanical Issue
2016-07-03 | 43189.5357
Brown 10 CT | Forced Derate | 166.623 | Inlet air chillers out | Unit derated to 115 MWs due to inet air cooling coils. | Mechanical Issue
Brown 11 CT | Forced Derate | 47.6066 | Row 3 turbine Blade 120 mw limit | Unit derated to 120 MWs due to R3 blade design. | Mechanical Issue
Brown 3 | Forced Outage | 9816 | First reheater BTF | Reheat tube leak | Mechanical Issue
Brown 5 CT | Forced Derate | 309.6183 | Row 3 turbine Blade 120 mw limit & Inlet air chillers out | Unit derated to 120 MWs due to R3 blade design issue, and to 118 MWs due to Inlet | Mechanical Issue
Brown 8 CT | Forced Derate | 95.2131 | Row 3 turbine Blade 120 mw limit & Inlet air chillers out | Unit derated to 120 MWs due to R3 blade design, and to 118MWs due to inet air cool | Mechanical Issue
Brown 9 CT | Forced Derate | 47.6066 | Row 3 turbine Blade 120 mw limit | Unit derated to 120 MWs due to R3 blade design. | Mechanical Issue
Cane Run 7 | Maintenance Outage | 12280.1 | Headers between tube bundles | HRSG 2 HPSH vent line leak. Investigated to identify source | N/A
Ghent 2 | Forced Derate | 112.0455 | Steam turbine copper deposit problems | Turbine performance. Turbine copper deposition. | Mechanical Issue
Ghent 3 | Forced Outage | 2473.5 | First superheater BTF | Unit 3 was removed from service due to a boiler superheat tube leak. | Mechanical Issue
Mill Creek 1 | Maintenance Outage | 2790 | First reheater BTF | Boiler and condenser tube leaks (Boiler Tube Repair Time) | N/A
Mill Creek 1 | Forced Derate | 43.2727 | Boiler water condition (silica) | High Silica | Mechanical Issue
Mill Creek 2 | Forced Derate | 1831.95 | Feedwater pump drive - motor failure | 2A MDBFP - motor | Mechanical Issue
Trimble County 2 | Forced Outage | 13176 | Generator rotor winding and vibration issues. | Unit continued to have problems with bearing #9 vibration and tripped on low steam | Mechanical Issue
2016-03-18 | 38637.1411
Brown 5 CT | Forced Derate | 23.8017 | Row 3 Turbine Blade Design Isuue … 120mw load limit | Derate due to R3 blade design issues. | Mechanical Issue
Ghent 4 | Forced Derate | 11187.7895 | Economizer BTF | Load reduced due to Turbine copper deposition. Derate started aft | Mechanical Issue
Mill Creek 3 | Forced Outage | 9432 | Main transformer failure/fire | "A" Phase main transformer fire | Mechanical Issue
Paddy's Run 13 CT | Forced Outage | 3864 | Hydraulic oil system A | Hydarulic System Pressure Switch Failure. | Mechanical Issue
Trimble County 10 CT | Forced Outage | 329.55 | Controls and instrumentation issues | Unit made unavailable due to hazgas monitor problems. | Mechanical Issue
Trimble County 2 | Forced Outage | 8652 | Waterwall (Furnace wall) BTF | Forced outage due to a boiler tube leak. | Mechanical Issue
Trimble County 2 | Forced Outage | 4788 | Waterwall (Furnace wall) BTF | As the boiler was coming back online from an outage due to a tube leak when anothe | Mechanical Issue
Zorn 1 CT | Forced Outage | 360 | Lube oil pumps B | DC Lube Oil Pump Motor Failure. | Mechanical Issue
2016-03-19 | 38307.5911
Brown 5 CT | Forced Derate | 23.8017 | Row 3 Turbine Blade Design Isuue … 120mw load limit | Derate due to R3 blade design issues. | Mechanical Issue
Ghent 4 | Forced Derate | 11187.7895 | Economizer BTF | Load reduced due to Turbine copper deposition. Derate started aft | Mechanical Issue
Mill Creek 3 | Forced Outage | 9432 | Main transformer failure/fire | "A" Phase main transformer fire | Mechanical Issue
Paddy's Run 13 CT | Forced Outage | 3864 | Hydraulic oil system A | Hydarulic System Pressure Switch Failure. | Mechanical Issue
Trimble County 2 | Forced Outage | 13440 | Waterwall (Furnace wall) BTF | As the boiler was coming back online from an outage due to a tube leak when anothe | Mechanical Issue
Zorn 1 CT | Forced Outage | 360 | Lube oil pumps B | DC Lube Oil Pump Motor Failure. | Mechanical Issue
2016-03-17 | 38195.0069
Brown 3 | Forced Derate | 234.9123 | Operator error | Error in managing feedwater system during unit startup | Mechanical Issue
Brown 3 | Forced Outage | 1002.5333 | Operator error | Error in managing feedwater system during unit startup | Mechanical Issue
Brown 5 CT | Forced Derate | 23.8017 | Row 3 Turbine Blade Design Isuue … 120mw load limit | Derate due to R3 blade design issues. | Mechanical Issue
Ghent 4 | Forced Outage | 6338.7333 | Economizer BTF | Unit came off line due to a leak in the economizer. | Mechanical Issue
Ghent 4 | Forced Derate | 1406.243 | Economizer BTF | Load reduced due to Turbine copper deposition. Derate started aft | Mechanical Issue
Mill Creek 3 | Forced Outage | 9432 | Main transformer failure/fire | "A" Phase main transformer fire | Mechanical Issue
Paddy's Run 13 CT | Forced Outage | 3864 | Hydraulic oil system A | Hydarulic System Pressure Switch Failure. | Mechanical Issue
Trimble County 10 CT | Forced Outage | 808.3833 | Exciter problems | Unit was made unavailable due to generator exciter problems. | Mechanical Issue
Trimble County 2 | Forced Outage | 13440 | Waterwall (Furnace wall) BTF | Forced outage due to a boiler tube leak. | Mechanical Issue
Trimble County 7 CT | Forced Outage | 594.3167 | Lack of fuel | The gas supply valve closed while unit was coming offline. | Mechanical Issue
Trimble County 8 CT | Forced Outage | 690.0833 | Lack of fuel | Unit outage due to gas valve closure while unit was coming offline. | Mechanical Issue
Zorn 1 CT | Forced Outage | 360 | Lube oil pumps B | DC Lube Oil Pump Motor Failure. | Mechanical Issue
2016-09-22 | 37570.8875
Brown 5 CT | Forced Derate | 23.8017 | Row 3 low pressure blades/buckets design issue | One MW derate due to R3 blade design. | Mechanical Issue
Brown 9 CT | Forced Outage | 47.2 | Switchyard circuit breakers | Unit tripped when U11's motor operated switch went open. Controls tripped due to | Mechanical Issue
Cane Run 7 | Forced Derate | 167.9539 | Condensate makeup and return system | CT1 shut down to save demineralized water | Mechanical Issue
Cane Run 7 | Forced Derate | 1511.5686 | BOP DCS communication problems | BOP DCS heartbeat communication error caused ST trip | Mechanical Issue
Cane Run 7 | Forced Derate | 1175.6772 | Low pressure compressor bleed valves | CT1 LP bleed valve position error. Limit switchbox re-attached | Mechanical Issue
Ghent 1 | Forced Outage | 11400 | First superheater BTF | Unit 1 came off line due to a Primary Superheat tube leak. | Mechanical Issue
Ghent 3 | Forced Outage | 10314.8 | First reheater BTF | U3 came off line with a Reheat tube leak. | Mechanical Issue
Mill Creek 3 | Maintenance Derate | 391.6993 | 3A coal Pulverizer mills | 3A Mill Maintenance | N/A
Mill Creek 4 | Forced Outage | 11568 | First superheater BTF | Boiler tube leak - superheater | Mechanical Issue
Trimble County 1 | Forced Derate | 970.1868 | 1A Primary air fan drives | The 1A PA Fan inlet vane damper drive had a faulty circuit board, which resulted i | Mechanical Issue
2016-03-15 | 35965.6762
Brown 5 CT | Forced Derate | 23.8017 | Row 3 Turbine Blade Design Isuue … 120mw load limit | Derate due to R3 blade design issues. | Mechanical Issue
Brown 9 CT | Forced Outage | 188.8 | Starting system (including motor) brush lift off issue | Brush lift off device for the SFC did not engage. Unit would not roll up past 20M | Mechanical Issue
Cane Run 7 | Forced Derate | 4739.2506 | CT 2 - Lube oil valve/piping leak | Leaking CT2 generator TE bearing oil supply line. Replaced pipe spool | Mechanical Issue
Cane Run 7 | Forced Derate | 1957.8 | Distributive Control System (DCS) - process computer | Primary and backup controllers failed during load operation. Re-booted | Mechanical Issue
Cane Run 7 | Forced Derate | 2226.1004 | CT 2 - Lube oil valve/piping leak | Leaking CT2 generator TE bearing oil supply line. Replaced pipe spool | Mechanical Issue
Ghent 4 | Forced Outage | 11424 | Economizer BTF | Unit came off line due to a leak in the economizer. | Mechanical Issue
Mill Creek 3 | Forced Derate | 441.3121 | Boiler water condition (silica) | High silica | Mechanical Issue
Mill Creek 3 | Forced Derate | 241.839 | Boiler water condition (silica) | High silica | Mechanical Issue
Mill Creek 3 | Forced Derate | 3.6234 | Boiler water condition (silica) | High silica | Mechanical Issue
Mill Creek 3 | Forced Outage | 2312.15 | Main transformer failure/fire | "A" Phase main transformer fire | Mechanical Issue
Paddy's Run 13 CT | Forced Outage | 3864 | Hydraulic oil system A | Hydarulic System Pressure Switch Failure. | Mechanical Issue
Trimble County 1 | Forced Derate | 38.1132 | Wet coal | Derate for operating with wet fuel. | Mechanical Issue
Trimble County 2 | Maintenance Derate | 32.8859 | Air heater (air flow issues) | Planned derate to swap mills. Due to airflow issues with the air heater, load must | N/A
Trimble County 7 CT | Maintenance Outage | 4056 | Generator current and potential transformers | Maintenance Outage - multiple maintenance items, but largest project is the Genera | N/A
Trimble County 8 CT | Maintenance Outage | 4056 | Generator current and potential transformers | Maintenance Outage - multiple maintenance items, but largest project is the Genera | N/A
Zorn 1 CT | Forced Outage | 360 | Lube oil pumps B | DC Lube Oil Pump Motor Failure. | Mechanical Issue
2016-05-06 | 31908.9759
Brown 5 CT | Forced Derate | 23.8017 | Row 3 Turbine Blade Design Isuue … 120mw load limit | Derate due to R3 blade design issues. | Mechanical Issue
Brown 6 CT | Maintenance Outage | 2854.7833 | Lube oil system - general | Outage to replace rotor barring pump motor. Motor was going wearing DC brushes ve | N/A
Ghent 3 | Maintenance Outage | 11568 | Flue gas expansion joint leaks | off line to repair expansion joint damage. | N/A
Mill Creek 1 | Maintenance Derate | 242.4242 | 1A Boiler recirculation pump issue | 1A BCP troublehsoot isolation problems | N/A
Trimble County 2 | Maintenance Outage | 13440 | Bearings Temperature Issue. | Unit was taken offline for high LP turbine bearing temperature. | N/A
Trimble County 9 CT | Maintenance Outage | 3779.9667 | generator controls and metering problems | Maintenance Outage - main scope is for generator maintenance. | N/A
2016-02-06 | 31521.9569
Brown 11 CT | Forced Derate | 214.3256 | Row 3 Blade Design Limitations/Issues | Derate due to row 3 turbine blades | Mechanical Issue
Brown 5 CT | Forced Derate | 261.9847 | Row 3 Blade Design Limitations/Issues | Derate due to R3 turbine blade operational limit set to 120MWs. | Mechanical Issue
Brown 8 CT | Forced Derate | 214.3256 | Row 3 Blade Design Limitations/Issues | Derate to 120MWs due to Row 3 turbine blade design. | Mechanical Issue
Brown 9 CT | Forced Derate | 452.7194 | Row 3 Blade Design Limitations/Issues | Unit derate due to Row 3 Blades design. | Mechanical Issue
Ghent 1 | Forced Outage | 9440.6667 | First reheater BTF | Unit removed from service due to reheat tube leak at the IK #6 | Mechanical Issue
Ghent 1 | Forced Outage | 1983.3333 | Circulating water piping issue | GH1 Forced Outage was changed from a Reheat tube leak, once repairs were | Mechanical Issue
Ghent 4 | Forced Derate | 415.8652 | Copper deposits on steam turbine blades | Unit 4 is limited due to copper build up on the turbine blades. | Mechanical Issue
Mill Creek 1 | Maintenance Outage | 7200 | Condenser tube leaks | Condenser tube leak | N/A
Paddy's Run 13 CT | Forced Derate | 238.6364 | Compressor problems - needs washing | Unit needs a compressor wash. | Mechanical Issue
Trimble County 10 CT | Forced Derate | 71.6 | Insufficient Transmission line access | Outside Management Control (OMC), inadequate transmission (NITS). Continuation from last year | Transmission
Trimble County 2 | Forced Outage | 6374.5 | Waterwall (Furnace wall) BTF | Unit was manually taken offline for a boiler tuble leak. | Mechanical Issue
Trimble County 5 CT | Forced Derate | 71.6 | Insufficient Transmission line access | Outside Management Control (OMC), inadequate transmission (NITS). Continuation from last year | Transmission
Trimble County 6 CT | Forced Derate | 71.6 | Insufficient Transmission line access | Outside Management Control (OMC), inadequate transmission (NITS). Continuation from last year | Transmission
Trimble County 7 CT | Forced Derate | 71.6 | Insufficient Transmission line access | Outside Management Control (OMC), inadequate transmission (NITS). Continuation from last year | Transmission
Trimble County 8 CT | Forced Derate | 71.6 | Insufficient Transmission line access | Outside Management Control (OMC), inadequate transmission (NITS). Continuation from last year | Transmission
Trimble County 9 CT | Forced Derate | 71.6 | Insufficient Transmission line access | Outside Management Control (OMC), inadequate transmission (NITS). Continuation from last year | Transmission
Trimble County 9 CT | Maintenance Outage | 4296 | Rotor windings (thermal sensitivity testing prep) | Outage to install termporary flux probe on generator. | N/A

## 2016 - Forced MWh Lost Detail
Unit | Event Type | Daily Net Forced MWh Lost | Cause | Description | Forced Category
2016-03-18 | 38637.1411
Brown 5 CT | Forced Derate | 23.8017 | Row 3 Turbine Blade Design Isuue … 120mw load limit | Derate due to R3 blade design issues. | Mechanical Issue
Ghent 4 | Forced Derate | 11187.7895 | Economizer BTF | Load reduced due to Turbine copper deposition. Derate started aft | Mechanical Issue
Mill Creek 3 | Forced Outage | 9432 | Main transformer failure/fire | "A" Phase main transformer fire | Mechanical Issue
Paddy's Run 13 CT | Forced Outage | 3864 | Hydraulic oil system A | Hydarulic System Pressure Switch Failure. | Mechanical Issue
Trimble County 10 CT | Forced Outage | 329.55 | Controls and instrumentation issues | Unit made unavailable due to hazgas monitor problems. | Mechanical Issue
Trimble County 2 | Forced Outage | 8652 | Waterwall (Furnace wall) BTF | Forced outage due to a boiler tube leak. | Mechanical Issue
Trimble County 2 | Forced Outage | 4788 | Waterwall (Furnace wall) BTF | As the boiler was coming back online from an outage due to a tube leak when anothe | Mechanical Issue
Zorn 1 CT | Forced Outage | 360 | Lube oil pumps B | DC Lube Oil Pump Motor Failure. | Mechanical Issue
2016-03-19 | 38307.5911
Brown 5 CT | Forced Derate | 23.8017 | Row 3 Turbine Blade Design Isuue … 120mw load limit | Derate due to R3 blade design issues. | Mechanical Issue
Ghent 4 | Forced Derate | 11187.7895 | Economizer BTF | Load reduced due to Turbine copper deposition. Derate started aft | Mechanical Issue
Mill Creek 3 | Forced Outage | 9432 | Main transformer failure/fire | "A" Phase main transformer fire | Mechanical Issue
Paddy's Run 13 CT | Forced Outage | 3864 | Hydraulic oil system A | Hydarulic System Pressure Switch Failure. | Mechanical Issue
Trimble County 2 | Forced Outage | 13440 | Waterwall (Furnace wall) BTF | As the boiler was coming back online from an outage due to a tube leak when anothe | Mechanical Issue
Zorn 1 CT | Forced Outage | 360 | Lube oil pumps B | DC Lube Oil Pump Motor Failure. | Mechanical Issue
2016-03-17 | 38195.0069
Brown 3 | Forced Derate | 0 | Operator error | Error in managing feedwater system during unit startup | Mechanical Issue
Brown 3 | Forced Outage | 0 | Operator error | Error in managing feedwater system during unit startup | Mechanical Issue
Brown 5 CT | Forced Derate | 0 | Row 3 Turbine Blade Design Isuue … 120mw load limit | Derate due to R3 blade design issues. | Mechanical Issue
Ghent 4 | Forced Outage | 0 | Economizer BTF | Unit came off line due to a leak in the economizer. | Mechanical Issue
Ghent 4 | Forced Derate | 0 | Economizer BTF | Load reduced due to Turbine copper deposition. Derate started aft | Mechanical Issue
Mill Creek 3 | Forced Outage | 0 | Main transformer failure/fire | "A" Phase main transformer fire | Mechanical Issue
Paddy's Run 13 CT | Forced Outage | 0 | Hydraulic oil system A | Hydarulic System Pressure Switch Failure. | Mechanical Issue
Trimble County 10 CT | Forced Outage | 0 | Exciter problems | Unit was made unavailable due to generator exciter problems. | Mechanical Issue
Trimble County 2 | Forced Outage | 0 | Waterwall (Furnace wall) BTF | Forced outage due to a boiler tube leak. | Mechanical Issue
Trimble County 7 CT | Forced Outage | 0 | Lack of fuel | The gas supply valve closed while unit was coming offline. | Mechanical Issue
Trimble County 8 CT | Forced Outage | 0 | Lack of fuel | Unit outage due to gas valve closure while unit was coming offline. | Mechanical Issue
Zorn 1 CT | Forced Outage | 0 | Lube oil pumps B | DC Lube Oil Pump Motor Failure. | Mechanical Issue
2016-07-02 | 37354.713
Brown 10 CT | Forced Derate | 166.623 | Inlet air chillers out | Unit derated to 115 MWs due to inet air cooling coils. | Mechanical Issue
Brown 11 CT | Forced Derate | 47.6066 | Row 3 turbine Blade 120 mw limit | Unit derated to 120 MWs due to R3 blade design. | Mechanical Issue
Brown 3 | Forced Outage | 9816 | First reheater BTF | Reheat tube leak | Mechanical Issue
Brown 5 CT | Forced Derate | 309.6183 | Row 3 turbine Blade 120 mw limit & Inlet air chillers out | Unit derated to 120 MWs due to R3 blade design issue, and to 118 MWs due to Inlet | Mechanical Issue
Brown 8 CT | Forced Derate | 95.2131 | Row 3 turbine Blade 120 mw limit & Inlet air chillers out | Unit derated to 120 MWs due to R3 blade design, and to 118MWs due to inet air cool | Mechanical Issue
Brown 9 CT | Forced Derate | 47.6066 | Row 3 turbine Blade 120 mw limit | Unit derated to 120 MWs due to R3 blade design. | Mechanical Issue
Ghent 2 | Forced Derate | 112.0455 | Steam turbine copper deposit problems | Turbine performance. Turbine copper deposition. | Mechanical Issue
Ghent 3 | Forced Outage | 11640 | First superheater BTF | Unit 3 was removed from service due to a boiler superheat tube leak. | Mechanical Issue
Mill Creek 2 | Forced Derate | 1944 | Feedwater pump drive - motor failure | 2A MDBFP - motor | Mechanical Issue
Trimble County 2 | Forced Outage | 13176 | Generator rotor winding and vibration issues. | Unit continued to have problems with bearing #9 vibration and tripped on low steam | Mechanical Issue
2016-09-22 | 37179.1882
Brown 5 CT | Forced Derate | 23.8017 | Row 3 low pressure blades/buckets design issue | One MW derate due to R3 blade design. | Mechanical Issue
Brown 9 CT | Forced Outage | 47.2 | Switchyard circuit breakers | Unit tripped when U11's motor operated switch went open. Controls tripped due to | Mechanical Issue
Cane Run 7 | Forced Derate | 167.9539 | Condensate makeup and return system | CT1 shut down to save demineralized water | Mechanical Issue
Cane Run 7 | Forced Derate | 1511.5686 | BOP DCS communication problems | BOP DCS heartbeat communication error caused ST trip | Mechanical Issue
Cane Run 7 | Forced Derate | 1175.6772 | Low pressure compressor bleed valves | CT1 LP bleed valve position error. Limit switchbox re-attached | Mechanical Issue
Ghent 1 | Forced Outage | 11400 | First superheater BTF | Unit 1 came off line due to a Primary Superheat tube leak. | Mechanical Issue
Ghent 3 | Forced Outage | 10314.8 | First reheater BTF | U3 came off line with a Reheat tube leak. | Mechanical Issue
Mill Creek 4 | Forced Outage | 11568 | First superheater BTF | Boiler tube leak - superheater | Mechanical Issue
Trimble County 1 | Forced Derate | 970.1868 | 1A Primary air fan drives | The 1A PA Fan inlet vane damper drive had a faulty circuit board, which resulted i | Mechanical Issue
2016-03-16 | 36391.8265
Brown 5 CT | Forced Derate | 23.8017 | Row 3 Turbine Blade Design Isuue … 120mw load limit | Derate due to R3 blade design issues. | Mechanical Issue
Cane Run 7 | Forced Derate | 3444.5975 | CT 2 - Lube oil valve/piping leak | Leaking CT2 generator TE bearing oil supply line. Replaced pipe spool | Mechanical Issue
Cane Run 7 | Forced Derate | 199.1774 | CT 2 - Exciter blower problems | CT2 generator collector blower failed to start causing startup trip | Mechanical Issue
Ghent 4 | Forced Outage | 11424 | Economizer BTF | Unit came off line due to a leak in the economizer. | Mechanical Issue
Mill Creek 3 | Forced Outage | 9432 | Main transformer failure/fire | "A" Phase main transformer fire | Mechanical Issue
Paddy's Run 13 CT | Forced Outage | 3864 | Hydraulic oil system A | Hydarulic System Pressure Switch Failure. | Mechanical Issue
Trimble County 10 CT | Forced Outage | 225.3333 | Exciter problems | Unit was made unavailable due to generator exciter problems. | Mechanical Issue
Trimble County 2 | Forced Outage | 6813.3333 | Waterwall (Furnace wall) BTF | Forced outage due to a boiler tube leak. | Mechanical Issue
Trimble County 7 CT | Forced Outage | 349.2667 | Lack of fuel | The gas supply valve closed while unit was coming offline. | Mechanical Issue
Trimble County 8 CT | Forced Outage | 256.3167 | Lack of fuel | Unit outage due to gas valve closure while unit was coming offline. | Mechanical Issue
Zorn 1 CT | Forced Outage | 360 | Lube oil pumps B | DC Lube Oil Pump Motor Failure. | Mechanical Issue
2016-01-11 | 29513.295
Brown 11 CT | Forced Derate | 214.3256 | Row 3 Blade Design Limitations/Issues | Derate due to R3 turbine blade operational limit set to 120MWs. | Mechanical Issue
Brown 3 | Forced Derate | 695.7374 | 3-1D Induced draft fan vibration | 3-1 ID Fan high vibration | Mechanical Issue
Brown 5 CT | Forced Derate | 261.9847 | Row 3 Blade Design Limitations/Issues | Derate due to R3 turbine blade operational limit set to 120MWs. | Mechanical Issue
Brown 5 CT | Forced Outage | 522.1667 | Cooling water system trip | Cooling water pump tripping 480V breaker | Mechanical Issue
Brown 7 CT | Forced Outage | 4104 | Hot end inspection | Inspection needed due to water ingress from failure of NOx water pump. | Mechanical Issue
Brown 8 CT | Forced Derate | 214.3256 | Row 3 Blade Design Limitations/Issues | Derate due to R3 turbine blade operational limit set to 120MWs. | Mechanical Issue
Brown 9 CT | Forced Derate | 452.7194 | Row 3 Blade Design Limitations/Issues | Derate due to R3 turbine blade operational limit set to 120MWs. | Mechanical Issue
Cane Run 7 | Forced Derate | 4688.2861 | HRSG-2 HP steam system problems | HRSG-2 HP steam final attemp. outlet pressure Xmitters failed. Replaced | Mechanical Issue
Cane Run 7 | Forced Derate | 34.5 | CT 2/HRSG-2 Condensate makeup water issue | Waiting on demineralized water quantity before restarting CT2/HRSG2 | Mechanical Issue
Cane Run 7 | Forced Outage | 7061 | HRSG-1 Economizer piping relief valve issue | HRSG-1 IP Economizer Inlet Relief Valve lifting. Valve rebuilt | Mechanical Issue
Ghent 3 | Forced Outage | 5815.6667 | Generator main leads overheating | Unit 3 was removed from service due to generator bus duct overheating. | Mechanical Issue
Ghent 4 | Forced Derate | 415.8652 | Copper deposits on steam turbine blades | Unit 4 is limited due to copper build up on the turbine blades. | Mechanical Issue
Paddy's Run 11 CT | Forced Outage | 312 | Turning gear and motor failure to engage | rathcet turning gear failed to engage. Ratchet soleniod has failed. | Mechanical Issue
Paddy's Run 12 CT | Forced Outage | 373.3333 | Lack of fuel | Lack of fuel supply from gas department. | Fuel Supply Disruption
Paddy's Run 13 CT | Forced Derate | 238.6364 | Compressor problems - needs washing | Unit needs a compressor wash. | Mechanical Issue
Paddy's Run 13 CT | Forced Outage | 2333.3333 | Lack of fuel | Lack of Gas Pressure from Gas department. | Fuel Supply Disruption
Trimble County 10 CT | Forced Derate | 71.6 | Insufficient Transmission line access | Outside Management Control (OMC), inadequate transmission (NITS). Continuation from last year | Transmission
Trimble County 2 | Forced Derate | 283.7479 | fuel quality problems | Low fuel quality caused a unit derate. | Mechanical Issue
Trimble County 5 CT | Forced Derate | 71.6 | Insufficient Transmission line access | Outside Management Control (OMC), inadequate transmission (NITS). Continuation from last year | Transmission
Trimble County 6 CT | Forced Derate | 71.6 | Insufficient Transmission line access | Outside Management Control (OMC), inadequate transmission (NITS). Continuation from last year | Transmission
Trimble County 6 CT | Forced Outage | 1062.0667 | Starting system issues | The 89ND switch did not engage causing starting sequence to not complete | Mechanical Issue
Trimble County 7 CT | Forced Derate | 71.6 | Insufficient Transmission line access | Outside Management Control (OMC), inadequate transmission (NITS). Continuation from last year | Transmission
Trimble County 8 CT | Forced Derate | 71.6 | Insufficient Transmission line access | Outside Management Control (OMC), inadequate transmission (NITS). Continuation from last year | Transmission
Trimble County 9 CT | Forced Derate | 71.6 | Insufficient Transmission line access | Outside Management Control (OMC), inadequate transmission (NITS). Continuation from last year | Transmission
2016-01-12 | 28614.3027
Brown 11 CT | Forced Derate | 214.3256 | Row 3 Blade Design Limitations/Issues | Derate due to R3 turbine blade operational limit set to 120MWs. | Mechanical Issue
Brown 3 | Forced Derate | 297.1379 | 3-1D Induced draft fan vibration | 3-1 ID Fan high vibration | Mechanical Issue
Brown 3 | Forced Derate | 315.9807 | 3-1D Induced draft fan vibration | 3-1 ID Fan vibration | Mechanical Issue
Brown 5 CT | Forced Derate | 261.9847 | Row 3 Blade Design Limitations/Issues | Derate due to R3 turbine blade operational limit set to 120MWs. | Mechanical Issue
Brown 5 CT | Forced Outage | 108.3333 | Inlet air vanes/noozles control card issue | Unit tripped due to Atos card on R3 guide vanes. | Mechanical Issue
Brown 5 CT | Forced Outage | 398.6667 | Inlet air vanes/noozles control card issue | Unit tripped due to failure of R3 Atos card on inlet guide vanes. | Mechanical Issue
Brown 7 CT | Forced Outage | 2359.8 | Hot end inspection | Inspection needed due to water ingress from failure of NOx water pump. | Mechanical Issue
Brown 8 CT | Forced Derate | 214.3256 | Row 3 Blade Design Limitations/Issues | Derate due to R3 turbine blade operational limit set to 120MWs. | Mechanical Issue
Brown 9 CT | Forced Derate | 452.7194 | Row 3 Blade Design Limitations/Issues | Derate due to R3 turbine blade operational limit set to 120MWs. | Mechanical Issue
Cane Run 7 | Forced Outage | 4427.5 | HRSG-1 Economizer piping relief valve issue | HRSG-1 IP Economizer Inlet Relief Valve lifting. Valve rebuilt | Mechanical Issue
Cane Run 7 | Forced Derate | 5451 | HRSG-1 Economizer piping relief valve issue | HRSG-1 IP Economizer Inlet Relief Valve lifting. Valve rebuilt | Mechanical Issue
Ghent 2 | Forced Derate | 32.1436 | 2-2 coal mill D burner fire | 2-2 Mill "D" burner caught fire. Blanked burner line off. | Mechanical Issue
Ghent 3 | Forced Outage | 11472 | Generator main leads overheating | Unit 3 was removed from service due to generator bus duct overheating. | Mechanical Issue
Ghent 4 | Forced Derate | 415.8652 | Copper deposits on steam turbine blades | Unit 4 is limited due to copper build up on the turbine blades. | Mechanical Issue
Paddy's Run 11 CT | Forced Outage | 312 | Turning gear and motor failure to engage | rathcet turning gear failed to engage. Ratchet soleniod has failed. | Mechanical Issue
Paddy's Run 13 CT | Forced Derate | 238.6364 | Compressor problems - needs washing | Unit needs a compressor wash. | Mechanical Issue
Trimble County 1 | Forced Derate | 80.9593 | 1F Pulverizer fire | 1F Mill caught on fire and 1B Mill was put in service. 1B was taken out of service | Mechanical Issue
Trimble County 1 | Forced Derate | 230.2282 | 1B and 1F Pulverizer motors and drive issue | Continued problems with the F and B Mills, combined with the loss of control power | Mechanical Issue
Trimble County 10 CT | Forced Derate | 71.6 | Insufficient Transmission line access | Outside Management Control (OMC), inadequate transmission (NITS). Continuation from last year | Transmission
Trimble County 2 | Forced Derate | 34.7446 | fuel quality problems | Low fuel quality caused a unit derate. | Mechanical Issue
Trimble County 2 | Forced Derate | 254.4811 | 2D and 2C coal Pulverizer mill issue | Problems with the 2D and 2C coal mills contributed to a derate while swapping mill | Mechanical Issue
Trimble County 2 | Forced Derate | 121.6063 | fuel quality problems | Problems with fuel quality. | Mechanical Issue
Trimble County 2 | Forced Derate | 320.2142 | fuel quality problems | Problems with fuel quality. | Mechanical Issue
Trimble County 5 CT | Forced Derate | 71.6 | Insufficient Transmission line access | Outside Management Control (OMC), inadequate transmission (NITS). Continuation from last year | Transmission
Trimble County 6 CT | Forced Derate | 71.6 | Insufficient Transmission line access | Outside Management Control (OMC), inadequate transmission (NITS). Continuation from last year | Transmission
Trimble County 6 CT | Forced Outage | 170.05 | Exhaust thermocouple trip | First reported as an exciter trip, later reported as a thermocouple trip. | Mechanical Issue
Trimble County 7 CT | Forced Derate | 71.6 | Insufficient Transmission line access | Outside Management Control (OMC), inadequate transmission (NITS). Continuation from last year | Transmission
Trimble County 8 CT | Forced Derate | 71.6 | Insufficient Transmission line access | Outside Management Control (OMC), inadequate transmission (NITS). Continuation from last year | Transmission
Trimble County 9 CT | Forced Derate | 71.6 | Insufficient Transmission line access | Outside Management Control (OMC), inadequate transmission (NITS). Continuation from last year | Transmission
2016-07-03 | 28119.4357
Brown 10 CT | Forced Derate | 166.623 | Inlet air chillers out | Unit derated to 115 MWs due to inet air cooling coils. | Mechanical Issue
Brown 11 CT | Forced Derate | 47.6066 | Row 3 turbine Blade 120 mw limit | Unit derated to 120 MWs due to R3 blade design. | Mechanical Issue
Brown 3 | Forced Outage | 9816 | First reheater BTF | Reheat tube leak | Mechanical Issue
Brown 5 CT | Forced Derate | 309.6183 | Row 3 turbine Blade 120 mw limit & Inlet air chillers out | Unit derated to 120 MWs due to R3 blade design issue, and to 118 MWs due to Inlet | Mechanical Issue
Brown 8 CT | Forced Derate | 95.2131 | Row 3 turbine Blade 120 mw limit & Inlet air chillers out | Unit derated to 120 MWs due to R3 blade design, and to 118MWs due to inet air cool | Mechanical Issue
Brown 9 CT | Forced Derate | 47.6066 | Row 3 turbine Blade 120 mw limit | Unit derated to 120 MWs due to R3 blade design. | Mechanical Issue
Ghent 2 | Forced Derate | 112.0455 | Steam turbine copper deposit problems | Turbine performance. Turbine copper deposition. | Mechanical Issue
Ghent 3 | Forced Outage | 2473.5 | First superheater BTF | Unit 3 was removed from service due to a boiler superheat tube leak. | Mechanical Issue
Mill Creek 1 | Forced Derate | 43.2727 | Boiler water condition (silica) | High Silica | Mechanical Issue
Mill Creek 2 | Forced Derate | 1831.95 | Feedwater pump drive - motor failure | 2A MDBFP - motor | Mechanical Issue
Trimble County 2 | Forced Outage | 13176 | Generator rotor winding and vibration issues. | Unit continued to have problems with bearing #9 vibration and tripped on low steam | Mechanical Issue
2016-03-15 | 27820.7903
Brown 5 CT | Forced Derate | 23.8017 | Row 3 Turbine Blade Design Isuue … 120mw load limit | Derate due to R3 blade design issues. | Mechanical Issue
Brown 9 CT | Forced Outage | 188.8 | Starting system (including motor) brush lift off issue | Brush lift off device for the SFC did not engage. Unit would not roll up past 20M | Mechanical Issue
Cane Run 7 | Forced Derate | 4739.2506 | CT 2 - Lube oil valve/piping leak | Leaking CT2 generator TE bearing oil supply line. Replaced pipe spool | Mechanical Issue
Cane Run 7 | Forced Derate | 1957.8 | Distributive Control System (DCS) - process computer | Primary and backup controllers failed during load operation. Re-booted | Mechanical Issue
Cane Run 7 | Forced Derate | 2226.1004 | CT 2 - Lube oil valve/piping leak | Leaking CT2 generator TE bearing oil supply line. Replaced pipe spool | Mechanical Issue
Ghent 4 | Forced Outage | 11424 | Economizer BTF | Unit came off line due to a leak in the economizer. | Mechanical Issue
Mill Creek 3 | Forced Derate | 441.3121 | Boiler water condition (silica) | High silica | Mechanical Issue
Mill Creek 3 | Forced Derate | 241.839 | Boiler water condition (silica) | High silica | Mechanical Issue
Mill Creek 3 | Forced Derate | 3.6234 | Boiler water condition (silica) | High silica | Mechanical Issue
Mill Creek 3 | Forced Outage | 2312.15 | Main transformer failure/fire | "A" Phase main transformer fire | Mechanical Issue
Paddy's Run 13 CT | Forced Outage | 3864 | Hydraulic oil system A | Hydarulic System Pressure Switch Failure. | Mechanical Issue
Trimble County 1 | Forced Derate | 38.1132 | Wet coal | Derate for operating with wet fuel. | Mechanical Issue
Zorn 1 CT | Forced Outage | 360 | Lube oil pumps B | DC Lube Oil Pump Motor Failure. | Mechanical Issue

## 2017 - Total MWh Lost Detail
Unit | Event Type | Daily Net MWh Lost | Cause | Description | Forced Category
2017-01-21 | 40655.2205
Brown 11 CT | Forced Derate | 214.3256 | Row 3 turbine blade design issues. | Derate due to row 3 turbine blade design issues. | Mechanical Issue
Brown 5 CT | Forced Derate | 261.9847 | Row 3 turbine blade design issues. | Derate due to row 3 turbine blade design issues. | Mechanical Issue
Brown 8 CT | Forced Derate | 214.3256 | Row 3 turbine blade design issues. | Derate due to row 3 turbine blade design issues. | Mechanical Issue
Brown 9 CT | Forced Derate | 452.7194 | Row 3 turbine blade design issues. | Derate due to row 3 turbine blade design issues. | Mechanical Issue
Cane Run 7 | Maintenance Outage | 16392 | IP Startup bypass valve mtce. | Block outage for valve repairs | N/A
Ghent 1 | Forced Outage | 11424 | First superheater B - BTF | Outage #3 Unit 1 off line for a tube leak in the Low Temp SH section of the boiler. | Mechanical Issue
Ghent 4 | Forced Derate | 415.8652 | Steam turbine unable to make rating (CT issues) | Not able to make winter MW high (534). Several CT's out of service. | Mechanical Issue
Mill Creek 2 | Maintenance Outage | 7080 | Control valves | #4 Control Valve Stuck Closed (and WW repair) | N/A
Paddy's Run 13 CT | Maintenance Outage | 4200 | Other switchyard equipment - external | Transmission carding for new pole installation. | N/A
2017-01-20 | 38418.5442
Brown 11 CT | Forced Derate | 214.3256 | Row 3 turbine blade design issues. | Derate due to row 3 turbine blade design issues. | Mechanical Issue
Brown 3 | Maintenance Outage | 4880.2833 | 3-1 Induced draft fan vibration | Balance 3-1 ID Fan due to vibration | N/A
Brown 5 CT | Forced Derate | 261.9847 | Row 3 turbine blade design issues. | Derate due to row 3 turbine blade design issues. | Mechanical Issue
Brown 8 CT | Forced Derate | 214.3256 | Row 3 turbine blade design issues. | Derate due to row 3 turbine blade design issues. | Mechanical Issue
Brown 9 CT | Forced Derate | 452.7194 | Row 3 turbine blade design issues. | Derate due to row 3 turbine blade design issues. | Mechanical Issue
Cane Run 7 | Maintenance Outage | 16392 | IP Startup bypass valve mtce. | Block outage for valve repairs | N/A
Ghent 1 | Forced Outage | 11424 | First superheater B - BTF | Outage #3 Unit 1 off line for a tube leak in the Low Temp SH section of the boiler. | Mechanical Issue
Ghent 4 | Forced Derate | 415.8652 | Steam turbine unable to make rating (CT issues) | Not able to make winter MW high (534). Several CT's out of service. | Mechanical Issue
Mill Creek 2 | Maintenance Derate | 469.3182 | Pulverizer mills | 2C Mill Maintenance | N/A
Mill Creek 2 | Forced Derate | 680.1389 | Control valves | #4 Control Valve Stuck Closed | Mechanical Issue
Mill Creek 2 | Maintenance Outage | 231.0833 | Control valves | #4 Control Valve Stuck Closed (and WW repair) | N/A
Paddy's Run 13 CT | Maintenance Outage | 2782.5 | Other switchyard equipment - external | Transmission carding for new pole installation. | N/A
2017-02-25 | 36648.9028
Brown 11 CT | Forced Derate | 214.3256 | Row 3 turbine blade design issues. | Derate due to row 3 turbine blade design issues. | Mechanical Issue
Brown 5 CT | Forced Derate | 261.9847 | Row 3 turbine blade design issues. | Derate due to row 3 turbine blade design issues. | Mechanical Issue
Brown 8 CT | Forced Derate | 214.3256 | Row 3 turbine blade design issues. | Derate due to row 3 turbine blade design issues. | Mechanical Issue
Brown 8 CT | Forced Outage | 324.2667 | Other exciter problems | Loose connection in the generator voltage regulator cabinet. | Mechanical Issue
Brown 9 CT | Forced Derate | 452.7194 | Row 3 turbine blade design issues. | Derate due to row 3 turbine blade design issues. | Mechanical Issue
Cane Run 7 | Maintenance Outage | 16392 | IP steam isolation/boundary valves | HRSG 1 HRH steam isolation valve seat delamination. Replaced seats | N/A
Ghent 4 | Forced Derate | 415.8652 | Other miscellaneous steam turbine problems | Not able to make full load due to turbine performance issues. | Mechanical Issue
Mill Creek 1 | Forced Derate | 1963.6364 | Air heater fouling (regenerative) | High Air Heater Differential (A Side) (OPEN) | Mechanical Issue
Mill Creek 4 | Forced Outage | 2916 | Burner instruments and controls (except light-off) | Master Fuel Trip (Lost Flame Scanner) | Mechanical Issue
Trimble County 1 | Forced Derate | 79.7793 | 1C Coal Pulverizer mills | 1C Mill Feeder tripped due to the tachometer speed switch not operating correctly | Mechanical Issue
Trimble County 2 | Forced Outage | 13414 | Exciter transformer | A water leak from the roof of the turbine building ran onto the TC2 Exciter Transformer | Mechanical Issue
2017-01-19 | 36396.2205
Brown 11 CT | Forced Derate | 214.3256 | Row 3 turbine blade design issues. | Derate due to row 3 turbine blade design issues. | Mechanical Issue
Brown 3 | Maintenance Outage | 7021 | 3-1 Induced draft fan vibration | Balance 3-1 ID Fan due to vibration | N/A
Brown 5 CT | Forced Derate | 261.9847 | Row 3 turbine blade design issues. | Derate due to row 3 turbine blade design issues. | Mechanical Issue
Brown 8 CT | Forced Derate | 214.3256 | Row 3 turbine blade design issues. | Derate due to row 3 turbine blade design issues. | Mechanical Issue
Brown 9 CT | Forced Derate | 452.7194 | Row 3 turbine blade design issues. | Derate due to row 3 turbine blade design issues. | Mechanical Issue
Cane Run 7 | Maintenance Outage | 16392 | IP Startup bypass valve mtce. | Block outage for valve repairs | N/A
Ghent 1 | Forced Outage | 11424 | First superheater B - BTF | Outage #3 Unit 1 off line for a tube leak in the Low Temp SH section of the boiler. | Mechanical Issue
Ghent 4 | Forced Derate | 415.8652 | Steam turbine unable to make rating (CT issues) | Not able to make winter MW high (534). Several CT's out of service. | Mechanical Issue
2017-02-22 | 33375.8478
Brown 11 CT | Forced Derate | 214.3256 | Row 3 turbine blade design issues. | Derate due to row 3 turbine blade design issues. | Mechanical Issue
Brown 5 CT | Forced Derate | 261.9847 | Row 3 turbine blade design issues. | Derate due to row 3 turbine blade design issues. | Mechanical Issue
Brown 8 CT | Forced Derate | 214.3256 | Row 3 turbine blade design issues. | Derate due to row 3 turbine blade design issues. | Mechanical Issue
Brown 9 CT | Forced Derate | 452.7194 | Row 3 turbine blade design issues. | Derate due to row 3 turbine blade design issues. | Mechanical Issue
Cane Run 7 | Maintenance Outage | 16392 | IP steam isolation/boundary valves | HRSG 1 HRH steam isolation valve seat delamination. Replaced seats | N/A
Ghent 3 | Forced Outage | 1696.9 | Generator exciter field ground detection issues | Generator exciter field ground detection issues resulted in a startup failure | Mechanical Issue
Ghent 4 | Forced Derate | 415.8652 | Other miscellaneous steam turbine problems | Not able to make full load due to turbine performance issues. | Mechanical Issue
Mill Creek 1 | Maintenance Derate | 47.7273 | Pulverizer mills | 1A Mill Maintenance | N/A
Trimble County 2 | Forced Outage | 13680 | Exciter transformer | A water leak from the roof of the turbine building ran onto the TC2 Exciter Transformer | Mechanical Issue
2017-02-24 | 33295.0447
Brown 10 CT | Maintenance Outage | 234.6 | Lube oil system - general | Maintenance outage to check DC brushes on emergency lube oil equipment. | N/A
Brown 11 CT | Forced Derate | 214.3256 | Row 3 turbine blade design issues. | Derate due to row 3 turbine blade design issues. | Mechanical Issue
Brown 11 CT | Maintenance Outage | 168.5333 | Lube oil system - general | Maintenance outage to replace DC brushes as needed on emergency lube oil equipment | N/A
Brown 5 CT | Forced Derate | 261.9847 | Row 3 turbine blade design issues. | Derate due to row 3 turbine blade design issues. | Mechanical Issue
Brown 8 CT | Forced Derate | 214.3256 | Row 3 turbine blade design issues. | Derate due to row 3 turbine blade design issues. | Mechanical Issue
Brown 8 CT | Maintenance Outage | 200.5333 | Lube oil system - general | Maintenance outage to check DC brushes on emergency lube oil equipment. | N/A
Brown 9 CT | Forced Derate | 452.7194 | Row 3 turbine blade design issues. | Derate due to row 3 turbine blade design issues. | Mechanical Issue
Brown 9 CT | Maintenance Outage | 179.4 | Lube oil system - general | Maintenance outage to check DC brushes on emergency lube oil equipment | N/A
Cane Run 7 | Maintenance Outage | 16392 | IP steam isolation/boundary valves | HRSG 1 HRH steam isolation valve seat delamination. Replaced seats | N/A
Ghent 4 | Forced Derate | 415.8652 | Other miscellaneous steam turbine problems | Not able to make full load due to turbine performance issues. | Mechanical Issue
Mill Creek 1 | Maintenance Derate | 365.4545 | Pulverizer mills | 1D Mill Maintenance | N/A
Mill Creek 1 | Forced Derate | 426.6667 | Air heater fouling (regenerative) | High Air Heater Differential (A Side) | Mechanical Issue
Mill Creek 1 | Forced Derate | 88.6364 | Air heater fouling (regenerative) | High Air Heater Differential (A Side) (OPEN) | Mechanical Issue
Trimble County 2 | Forced Outage | 13680 | Exciter transformer | A water leak from the roof of the turbine building ran onto the TC2 Exciter Transformer | Mechanical Issue
2017-02-23 | 33290.5291
Brown 11 CT | Forced Derate | 214.3256 | Row 3 turbine blade design issues. | Derate due to row 3 turbine blade design issues. | Mechanical Issue
Brown 5 CT | Forced Derate | 261.9847 | Row 3 turbine blade design issues. | Derate due to row 3 turbine blade design issues. | Mechanical Issue
Brown 6 CT | Maintenance Outage | 897.75 | Generator heaters | Maintenance outage to replace generator stand still heater. | N/A
Brown 8 CT | Forced Derate | 214.3256 | Row 3 turbine blade design issues. | Derate due to row 3 turbine blade design issues. | Mechanical Issue
Brown 9 CT | Forced Derate | 452.7194 | Row 3 turbine blade design issues. | Derate due to row 3 turbine blade design issues. | Mechanical Issue
Cane Run 7 | Maintenance Outage | 16392 | IP steam isolation/boundary valves | HRSG 1 HRH steam isolation valve seat delamination. Replaced seats | N/A
Ghent 3 | Forced Derate | 312.9222 | Boiler water condition (not feedwater water quality) | Load was reduced due to high silica levels following start up | Mechanical Issue
Ghent 4 | Forced Derate | 415.8652 | Other miscellaneous steam turbine problems | Not able to make full load due to turbine performance issues. | Mechanical Issue
Mill Creek 1 | Maintenance Derate | 366.8182 | Pulverizer mills | 1A Mill Maintenance | N/A
Mill Creek 1 | Maintenance Derate | 81.8182 | Pulverizer mills | 1D Mill Maintenance | N/A
Trimble County 2 | Forced Outage | 13680 | Exciter transformer | A water leak from the roof of the turbine building ran onto the TC2 Exciter Transformer | Mechanical Issue
2017-01-14 | 31883.7962
Brown 11 CT | Forced Derate | 214.3256 | Row 3 turbine blade design issues. | Derate due to row 3 turbine blade design issues. | Mechanical Issue
Brown 5 CT | Forced Derate | 261.9847 | Row 3 turbine blade design issues. | Derate due to row 3 turbine blade design issues. | Mechanical Issue
Brown 8 CT | Forced Derate | 214.3256 | Row 3 turbine blade design issues. | Derate due to row 3 turbine blade design issues. | Mechanical Issue
Brown 9 CT | Forced Derate | 452.7194 | Row 3 turbine blade design issues. | Derate due to row 3 turbine blade design issues. | Mechanical Issue
Cane Run 7 | Maintenance Outage | 16392 | IP Startup bypass valve mtce. | Block outage for valve repairs | N/A
Ghent 4 | Forced Derate | 415.8652 | Steam turbine unable to make rating (CT issues) | Not able to make winter MW high (534). Several CT's out of service. | Mechanical Issue
Mill Creek 1 | Forced Derate | 20.9091 | Boiler water condition (silica) | High silica | Mechanical Issue
Mill Creek 1 | Forced Derate | 231.6667 | Boiler water condition (silica) | High silica | Mechanical Issue
Trimble County 2 | Maintenance Outage | 13680 | Air heater (2A FD at its stall point) | Air Heater washing - high DP issues and various other minor maintenance items. | N/A
2017-02-16 | 31721.6675
Brown 11 CT | Forced Derate | 214.3256 | Row 3 turbine blade design issues. | Derate due to row 3 turbine blade design issues. | Mechanical Issue
Brown 5 CT | Forced Derate | 261.9847 | Row 3 turbine blade design issues. | Derate due to row 3 turbine blade design issues. | Mechanical Issue
Brown 8 CT | Forced Derate | 214.3256 | Row 3 turbine blade design issues. | Derate due to row 3 turbine blade design issues. | Mechanical Issue
Brown 9 CT | Forced Derate | 452.7194 | Row 3 turbine blade design issues. | Derate due to row 3 turbine blade design issues. | Mechanical Issue
Cane Run 7 | Maintenance Outage | 16392 | IP Startup bypass system valves | HRSG 2 HRH bypass valve stuck closed. Replaced trim | N/A
Ghent 4 | Forced Derate | 415.8652 | Other miscellaneous steam turbine problems | Not able to make full load due to turbine performance issues. | Mechanical Issue
Trimble County 1 | Forced Derate | 90.447 | 1F Coal Pulverizer fires | The unit was placed on a derate when the 1F Mill had a fire in the seal ring heade | Mechanical Issue
Trimble County 2 | Forced Outage | 13680 | Bottom ash systems (wet or dry) | The unit was placed on a Forced Outage due to the previous event involving the Sub | Mechanical Issue
2017-02-15 | 31631.2205
Brown 11 CT | Forced Derate | 214.3256 | Row 3 turbine blade design issues. | Derate due to row 3 turbine blade design issues. | Mechanical Issue
Brown 5 CT | Forced Derate | 261.9847 | Row 3 turbine blade design issues. | Derate due to row 3 turbine blade design issues. | Mechanical Issue
Brown 8 CT | Forced Derate | 214.3256 | Row 3 turbine blade design issues. | Derate due to row 3 turbine blade design issues. | Mechanical Issue
Brown 9 CT | Forced Derate | 452.7194 | Row 3 turbine blade design issues. | Derate due to row 3 turbine blade design issues. | Mechanical Issue
Cane Run 7 | Forced Outage | 5805.5 | IP Startup bypass system valves | HRSG 1 HRH bypass valve spray nozzle leaking. Replaced soft goods | Mechanical Issue
Cane Run 7 | Maintenance Outage | 10586.5 | IP Startup bypass system valves | HRSG 2 HRH bypass valve stuck closed. Replaced trim | N/A
Ghent 4 | Forced Derate | 415.8652 | Other miscellaneous steam turbine problems | Not able to make full load due to turbine performance issues. | Mechanical Issue
Trimble County 2 | Forced Outage | 13680 | Bottom ash systems (wet or dry) | The unit was placed on a Forced Outage due to the previous event involving the Sub | Mechanical Issue

## 2017 - Forced MWh Lost Detail
Unit | Event Type | Daily Net Forced MWh Lost | Cause | Description | Forced Category
2017-11-20 | 28620.7666
Brown 5 CT | Forced Outage | 564 | Enclosure Fan Control System Issue | Issue with enclosure fan control system. | Mechanical Issue
Brown 6 CT | Forced Outage | 2912.35 | Generator AVR Fault During Syncronization | AVR fault while trying to sync. | Mechanical Issue
Cane Run 7 | Forced Derate | 965.9066 | High HRSG Exhaust Gas Duct Pressure | High exhaust gas pressure in both HRSGs | Mechanical Issue
Ghent 1 | Forced Derate | 224.7404 | 1-3 Coal feeder plugged | 1-3 Coal feeder plugged. | Mechanical Issue
Ghent 1 | Forced Derate | 108.2423 | 1-3 Coal Feeder Plugged | 1-3 coal feeder plugged | Mechanical Issue
Ghent 3 | Forced Outage | 11496 | Superheater Tube Leak | Unit 3 was forced off-line due to superheat tube leak. | Mechanical Issue
Ghent 4 | Forced Outage | 11472 | Circulating Water Line Leak | GH4 was Forced off line due to Circulating water line leak. | Mechanical Issue
Mill Creek 1 | Forced Derate | 436.3636 | 1A Air Heater High DP | 1A Air Heater High DP | Mechanical Issue
Mill Creek 2 | Forced Derate | 129.1636 | High Pressure Turbine Restriction Issues | HP Turbine Restriction | Mechanical Issue
Paddy's Run 11 CT | Forced Outage | 312 | Starting System Failure - Broke Into Pieces | Starting Diesel Starter Failed. Broke into pieces. | Mechanical Issue
2017-02-14 | 25800.4122
Brown 11 CT | Forced Derate | 214.3256 | Row 3 turbine blade design issues. | Derate due to row 3 turbine blade design issues. | Mechanical Issue
Brown 5 CT | Forced Derate | 261.9847 | Row 3 turbine blade design issues. | Derate due to row 3 turbine blade design issues. | Mechanical Issue
Brown 8 CT | Forced Derate | 214.3256 | Row 3 turbine blade design issues. | Derate due to row 3 turbine blade design issues. | Mechanical Issue
Brown 9 CT | Forced Derate | 452.7194 | Row 3 turbine blade design issues. | Derate due to row 3 turbine blade design issues. | Mechanical Issue
Cane Run 7 | Forced Outage | 16392 | IP Startup bypass system valves | HRSG 1 HRH bypass valve spray nozzle leaking. Replaced soft goods | Mechanical Issue
Ghent 4 | Forced Derate | 415.8652 | Other miscellaneous steam turbine problems | Not able to make full load due to turbine performance issues. | Mechanical Issue
Mill Creek 2 | Forced Derate | 75.0909 | 2B Coal Mill Burner Temperature | 2B Coal Mill Burner Temperature | Mechanical Issue
Mill Creek 4 | Forced Outage | 955.8 | Reheat/intercept valve testing | Trip During Valve Testing (Under Investigation) | Mechanical Issue
Mill Creek 4 | Forced Derate | 176.58 | Boiler water condition (not feedwater water quality) | Boiler Chemistry - High Silica After Startup | Mechanical Issue
Trimble County 2 | Forced Derate | 1302.7208 | Bottom ash systems (wet or dry) | The unit was placed on a derate due to faulty controls in the Submerged Scraper Co | Mechanical Issue
Trimble County 2 | Forced Outage | 5339 | Bottom ash systems (wet or dry) | The unit was placed on a Forced Outage due to the previous event involving the Sub | Mechanical Issue
2017-04-29 | 25494.9421
Brown 10 CT | Forced Outage | 153.4 | Gas Turbine Control System - logic problems | Switch over unit logic prevented gas turbine from starting. | Mechanical Issue
Brown 11 CT | Forced Derate | 214.3256 | Row 3 turbine blade design issues. | Derate due to row 3 turbine blade design issues. | Mechanical Issue
Brown 11 CT | Forced Outage | 153.4 | Gas Turbine Control System - logic problems | Switchover unit logic prevented units from being able to start. | Mechanical Issue
Brown 5 CT | Forced Derate | 23.8017 | Row 3 Turbine blade design issues. | Derate due to Row 3 Turbine blade design issues. | Mechanical Issue
Brown 8 CT | Forced Outage | 153.4 | Gas Turbine Control System - logic problems | Switchover unit logic prevented units from being able to start. | Mechanical Issue
Brown 9 CT | Forced Outage | 153.4 | Gas Turbine Control System - logic problems | Switch over unit logic prevent units from being able to start. | Mechanical Issue
Ghent 1 | Forced Derate | 191.1058 | 1-1 Coal Feeder Wet coal | 1-1 Feeder plugged with wet coal. | Mechanical Issue
Mill Creek 2 | Forced Outage | 1406 | Drums and drum internals (trip) | Drum Level Trip | Mechanical Issue
Mill Creek 2 | Forced Derate | 399.3758 | Boiler water condition (silica) | High Silica - Startup | Mechanical Issue
Trimble County 1 | Forced Outage | 8880 | Waterwall (Furnace wall) Boiler Tube leaks. | The unit was placed on a Forced Outage for repairs to an identified tube leak. | Mechanical Issue
Trimble County 2 | Forced Outage | 13440 | Other boiler tube leaks | The unit was placed on a Forced Outage for repairs to identified tube leaks. | Mechanical Issue
Trimble County 7 CT | Forced Outage | 326.7333 | Gas fuel system B | The unit failed to start when a fuel gas valve controller failed. The controller f | Mechanical Issue
2017-04-28 | 22558.1272
Brown 11 CT | Forced Derate | 214.3256 | Row 3 turbine blade design issues. | Derate due to row 3 turbine blade design issues. | Mechanical Issue
Brown 5 CT | Forced Derate | 23.8017 | Row 3 Turbine blade design issues. | Derate due to Row 3 Turbine blade design issues. | Mechanical Issue
Trimble County 1 | Forced Outage | 8880 | Waterwall (Furnace wall) Boiler Tube leaks. | The unit was placed on a Forced Outage for repairs to an identified tube leak. | Mechanical Issue
Trimble County 2 | Forced Outage | 13440 | Other boiler tube leaks | The unit was placed on a Forced Outage for repairs to identified tube leaks. | Mechanical Issue
2017-04-17 | 22453.7137
Brown 10 CT | Forced Outage | 1.9667 | Low pressure compressor bleed valves | Limit on Blow off valve did not make forcing unit offline. | Mechanical Issue
Brown 10 CT | Forced Outage | 23.6 | Low pressure compressor bleed valves | Limit switch on compressor blow off valve did not make forcing unit offline | Mechanical Issue
Brown 11 CT | Forced Derate | 214.3256 | Row 3 turbine blade design issues. | Derate due to row 3 turbine blade design issues. | Mechanical Issue
Brown 5 CT | Forced Derate | 23.8017 | Row 3 Turbine blade design issues. | Derate due to Row 3 Turbine blade design issues. | Mechanical Issue
Cane Run 7 | Forced Derate | 1814.0198 | HRSG-1 IP Startup bypass valve stuck open. | HRSG 1 HRH bypass valve stuck partially open | Mechanical Issue
Ghent 3 | Forced Outage | 11496 | Economizer Tube Leak | Unit 3 was forced off line due to a tube leak in the upper economizer | Mechanical Issue
Trimble County 1 | Forced Outage | 8880 | Waterwall (Furnace wall) Tube Leak. | The unit was taken offline and placed on a Forced Outage for repairs on a leaking | Mechanical Issue
2017-02-15 | 21044.7205
Brown 11 CT | Forced Derate | 214.3256 | Row 3 turbine blade design issues. | Derate due to row 3 turbine blade design issues. | Mechanical Issue
Brown 5 CT | Forced Derate | 261.9847 | Row 3 turbine blade design issues. | Derate due to row 3 turbine blade design issues. | Mechanical Issue
Brown 8 CT | Forced Derate | 214.3256 | Row 3 turbine blade design issues. | Derate due to row 3 turbine blade design issues. | Mechanical Issue
Brown 9 CT | Forced Derate | 452.7194 | Row 3 turbine blade design issues. | Derate due to row 3 turbine blade design issues. | Mechanical Issue
Cane Run 7 | Forced Outage | 5805.5 | IP Startup bypass system valves | HRSG 1 HRH bypass valve spray nozzle leaking. Replaced soft goods | Mechanical Issue
Ghent 4 | Forced Derate | 415.8652 | Other miscellaneous steam turbine problems | Not able to make full load due to turbine performance issues. | Mechanical Issue
Trimble County 2 | Forced Outage | 13680 | Bottom ash systems (wet or dry) | The unit was placed on a Forced Outage due to the previous event involving the Sub | Mechanical Issue
2017-06-15 | 20743.6575
Brown 10 CT | Forced Derate | 190.4262 | Inlet air chillers out of service … with leaks | Chilled inlet air system has coil banks out of service due to leaks. | Mechanical Issue
Brown 11 CT | Forced Derate | 47.6066 | Row 3 turbine blade design issues | Derate due to issues with the Row 3 turbine blade design. | Mechanical Issue
Brown 5 CT | Forced Derate | 309.6183 | Inlet Air Chillers Problems - Coils Out Of Service | Chilled inlet air system has coil banks out of service due to leaks. | Mechanical Issue
Brown 8 CT | Forced Derate | 142.8197 | Inlet air chillers out of service … with leaks | Chilled inlet air system has coil banks out of service due to leaks. | Mechanical Issue
Brown 9 CT | Forced Derate | 47.6066 | Inlet air chillers out of service … with leaks | Chilled inlet air system has coil banks out of service due to leaks. | Mechanical Issue
Cane Run 7 | Forced Derate | 7955.7689 | Boiler Feedwater pump 201 thrust bearing failure | BFP 201 thrust bearing failure. Cause under investigation. Pump swapped with spare | Mechanical Issue
Ghent 1 | Forced Outage | 11400 | Boiler water cooled spacer tube leaks | Boiler leak in a water cooled spacer tube. | Mechanical Issue
Ghent 3 | Forced Derate | 217.8113 | Turbine copper deposits | Load was reduced due to turbine copper depostion. | Mechanical Issue
Mill Creek 2 | Forced Derate | 432 | HP turbine restriction issues | HP Turbine Restriction | Mechanical Issue
2017-12-27 | 20700.3918
Brown 11 CT | Forced Derate | 214.3256 | Row 3 Blade Design. | Unit derated to 120 MWs for R3 blade design. | Mechanical Issue
Brown 3 | Forced Outage | 9216.7833 | Economizer tube leak | Economizer tube leak | Mechanical Issue
Brown 5 CT | Forced Outage | 864.5 | Cooling water system A | F660Low cooling water pressure prevented system from starting. | Mechanical Issue
Brown 6 CT | Forced Outage | 4104 | Ignition system B - SFC During Brown 7 Startup | SFC during Brown 7 Startup. | Mechanical Issue
Brown 7 CT | Forced Outage | 3437.1 | DCS - Logic Issues; Unit will not sync and trips due to reverse power flows. | Unit will not sync online. Goes online and then trips back off due to reverse pow | Mechanical Issue
Brown 8 CT | Forced Derate | 214.3256 | Row 3 Blade Design. | Unit derated to 120 MWs for R3 blade design. | Mechanical Issue
Brown 8 CT | Forced Outage | 1555.2 | Starting system - Bad Three Position ISO Limit Switch. | Found bad limit switch on three position ISO switch. | Mechanical Issue
Brown 9 CT | Forced Derate | 452.7194 | R3 blade design | R3 blade design | Mechanical Issue
Brown 9 CT | Forced Outage | 351.9 | Starting system (including motor) A | F410Start up failure on U8 tied up SFC preventing unit 9 from starting. | Mechanical Issue
Mill Creek 2 | Forced Derate | 257.4545 | HP Turbine Restriction | HP Turbine Restriction | Mechanical Issue
Paddy's Run 13 CT | Forced Outage | 32.0833 | Generator casing | F660Generator Hydrogen Pressure dropped below limits on startup. | Mechanical Issue
2017-05-03 | 20584.8106
Brown 11 CT | Forced Derate | 214.3256 | Row 3 turbine blade design issues. | Derate due to row 3 turbine blade design issues. | Mechanical Issue
Brown 5 CT | Forced Derate | 23.8017 | Row 3 Turbine blade design issues. | Derate due to Row 3 Turbine blade design issues. | Mechanical Issue
Ghent 4 | Forced Outage | 10539.9 | First superheater BTF | GH4 was removed from service due to a tube leak in the PSH area of the bo | Mechanical Issue
Trimble County 10 CT | Forced Outage | 277.45 | Low Fuel Pressure - Start Failure. | TC10 failed on startup after gas pressure dropped when the monitor valve closed. T | Mechanical Issue
Trimble County 2 | Forced Outage | 9529.3333 | Other boiler tube leaks | The unit was placed on a Forced Outage for repairs to identified tube leaks. | Mechanical Issue
2017-06-16 | 20476.6159
Brown 10 CT | Forced Derate | 190.4262 | Inlet air chillers out of service … with leaks | Chilled inlet air system has coil banks out of service due to leaks. | Mechanical Issue
Brown 11 CT | Forced Derate | 47.6066 | Row 3 turbine blade design issues | Derate due to issues with the Row 3 turbine blade design. | Mechanical Issue
Brown 5 CT | Forced Derate | 309.6183 | Inlet Air Chillers Problems - Coils Out Of Service | Chilled inlet air system has coil banks out of service due to leaks. | Mechanical Issue
Brown 8 CT | Forced Derate | 142.8197 | Inlet air chillers out of service … with leaks | Chilled inlet air system has coil banks out of service due to leaks. | Mechanical Issue
Brown 9 CT | Forced Derate | 47.6066 | Inlet air chillers out of service … with leaks | Chilled inlet air system has coil banks out of service due to leaks. | Mechanical Issue
Cane Run 7 | Forced Derate | 7552.4556 | Boiler Feedwater pump 201 thrust bearing failure | BFP 201 thrust bearing failure. Cause under investigation. Pump swapped with spare | Mechanical Issue
Cane Run 7 | Forced Derate | 11.0497 | HRSG-2 IP Startup bypass system valve stuck closed | HRSG2 HRH bypass valve stuck closed causing CT2 trip | Mechanical Issue
Ghent 1 | Forced Outage | 11400 | Boiler water cooled spacer tube leaks | Boiler leak in a water cooled spacer tube. | Mechanical Issue
Ghent 3 | Forced Derate | 217.8113 | Turbine copper deposits | Load was reduced due to turbine copper depostion. | Mechanical Issue
Mill Creek 2 | Forced Derate | 432 | HP turbine restriction issues | HP Turbine Restriction | Mechanical Issue
Mill Creek 3 | Forced Derate | 125.2219 | 3A Induced draft fan damper linkage | 3A ID Fan Beck Drive Linkage | Mechanical Issue

## 2018 - Total MWh Lost Detail
Unit | Event Type | Daily Net MWh Lost | Cause | Description | Forced Category
2018-11-26 | 33482.3518
Brown 1 | Forced Derate | 1139.55 | 1-1 FD Fan Coupling Bad and Bearings Wiped | 1-1 FD Fan coupling bad and bearings wiped | Mechanical Issue
Brown 1 | Forced Derate | 62.8547 | Boiler MFT Due to Flame Instability | Boiler MFT due to flame instability | Mechanical Issue
Brown 1 | Forced Derate | 42.2368 | 1-1 FD Fan Coupling Bad and Bearings Wiped | 1-1 FD Fan coupling bad and bearings wiped | Mechanical Issue
Cane Run 7 | Maintenance Derate | 174.727 | Boiler Safety Valve Test | Post-outage safety/relief valve testing | N/A
Ghent 1 | Forced Derate | 125.6712 | AH Flue Gas Outlet Duct Pressure | AH outlet duct pressure | Mechanical Issue
Ghent 3 | Forced Outage | 11496 | First Superheater BTF | Multiple tube leaks in 3rd division panel. | Mechanical Issue
Mill Creek 1 | Maintenance Outage | 815 | Air Heater Wash and Boiler Deslag - Extension | Air Heater Wash and Boiler Deslag - Extension | N/A
Mill Creek 2 | Forced Derate | 1318.5455 | Air Heater High Differential - Variable | Air Heater High Differential - Variable | Mechanical Issue
Mill Creek 4 | Forced Outage | 11568 | TDBFP Bearing Oil Leak/Fire | TDBFP Bearing Oil Leak/Fire | Mechanical Issue
Paddy's Run 13 CT | Maintenance Outage | 2323.7667 | Other switchyard equipment - external | 138kv bus Maint. | N/A
Trimble County 9 CT | Maintenance Outage | 4056 | Exhaust Stack | The unit was placed on a Maintenance Outage for repairs to the exhaust stack lining. | N/A
Zorn 1 CT | Forced Outage | 360 | Distributive Control System (DCS) - process computer | PLC Controller card failure. | Mechanical Issue
2018-06-23 | 33439.1258
Brown 10 CT | Forced Derate | 47.6066 | Other inlet air problems A | Two MW derate due to inlet air cooling system. | Mechanical Issue
Brown 11 CT | Forced Derate | 47.6066 | Blades | Derate due to row 3 turbine blade design. | Mechanical Issue
Brown 3 | Forced Derate | 107.8681 | HP Turbine Steam Flow Restriction - Fouling | HP Turbine fouling restricting steam flow | Mechanical Issue
Brown 5 CT | Forced Derate | 309.6183 | Inlet air filters A | 118 MWs max due to inlet air coils out of service. | Mechanical Issue
Brown 8 CT | Forced Derate | 142.8197 | Inlet air chillers A | Derate due to inlet coils being out of service due to leaks | Mechanical Issue
Brown 9 CT | Forced Derate | 47.6066 | Blades | Derate due to R3 Turbine blades. | Mechanical Issue
Ghent 4 | Maintenance Outage | 11472 | Replacement of the condensate to feedwater stop/check valve. | Unit 4 was removed from service for replacement of the condensate to feedwater stop/check valve. | N/A
Mill Creek 1 | Maintenance Outage | 7200 | Air Pre-Heater Wash | Air Pre-Heater Wash | N/A
Paddy's Run 12 CT | Forced Outage | 552 | Generator output breaker | Generator circuit breaker coil malfunction prevented synchronization | Mechanical Issue
Trimble County 2 | Maintenance Outage | 13176 | Replace Main Stop turbine valve screens | TC2 was brought offline for a Maintenance Outage with the purpose of replacing the Main Stop turbine valve screens. | N/A
Zorn 1 CT | Forced Outage | 336 | PLC Controller Card Failure | PLC Controller card failure. | Mechanical Issue
2018-05-18 | 32679.5429
Brown 9 CT | Maintenance Outage | 2832 | Vanes/nozzles B | Replace R2 vanes on unit. | N/A
Ghent 4 | Forced Derate | 4479.5429 | 4-1 BFP Outboard Bearing Exceeding Temp Limits | 4-1 BFP outboard bearing temperature exceeding temperature limits | Mechanical Issue
Mill Creek 4 | Maintenance Outage | 11568 | Air Pre-Heater Wash | Air Pre-Heater Wash | N/A
Trimble County 2 | Maintenance Outage | 13440 | LP Turbine Bearing #8 High Temps - Bearing Tilt | During turbine checkouts of the 2018 Spring Planned Outage, high temperatures were noted on the LP Turbine Bearing #8. The unit was taken offline on a MO basis to address the tilt of the bearing. | N/A
Zorn 1 CT | Forced Outage | 360 | Distributive Control System (DCS) - process computer | PLC Controller card failure. | Mechanical Issue
2018-06-24 | 32427.3591
Brown 10 CT | Forced Derate | 47.6066 | Other inlet air problems A | Two MW derate due to inlet air cooling system. | Mechanical Issue
Brown 11 CT | Forced Derate | 47.6066 | Blades | Derate due to row 3 turbine blade design. | Mechanical Issue
Brown 3 | Forced Derate | 107.8681 | HP Turbine Steam Flow Restriction - Fouling | HP Turbine fouling restricting steam flow | Mechanical Issue
Brown 5 CT | Forced Derate | 309.6183 | Inlet air filters A | 118 MWs max due to inlet air coils out of service. | Mechanical Issue
Brown 8 CT | Forced Derate | 142.8197 | Inlet air chillers A | Derate due to inlet coils being out of service due to leaks | Mechanical Issue
Brown 9 CT | Forced Derate | 47.6066 | Blades | Derate due to R3 Turbine blades. | Mechanical Issue
Ghent 4 | Maintenance Outage | 5736 | Replacement of the condensate to feedwater stop/check valve. | Unit 4 was removed from service for replacement of the condensate to feedwater stop/check valve. | N/A
Ghent 4 | Maintenance Outage | 4724.2333 | Maintenance Extension | Maintenance Extension | N/A
Mill Creek 1 | Maintenance Outage | 7195 | Air Pre-Heater Wash | Air Pre-Heater Wash | N/A
Mill Creek 1 | Maintenance Outage | 5 | Air Pre-Heater Wash (Extension) | Air Pre-Heater Wash (Extension) | N/A
Paddy's Run 12 CT | Forced Outage | 552 | Generator output breaker | Generator circuit breaker coil malfunction prevented synchronization | Mechanical Issue
Trimble County 2 | Maintenance Outage | 13176 | Replace Main Stop turbine valve screens | TC2 was brought offline for a Maintenance Outage with the purpose of replacing the Main Stop turbine valve screens. | N/A
Zorn 1 CT | Forced Outage | 336 | PLC Controller Card Failure | PLC Controller card failure. | Mechanical Issue
2018-01-21 | 32056.4266
Brown 11 CT | Forced Derate | 214.3256 | Row 3 Blade Design. | Unit derated to 120 MWs for R3 blade design. | Mechanical Issue
Brown 11 CT | Forced Outage | 3072 | TAT Spread Exhaust Temps | Unit could not meet TAT spread exhaust temperature limits. | Mechanical Issue
Brown 2 | Maintenance Outage | 39.2 | Aux Transformer 2B Main Feed Breaker Inspection | 2B main feed brekaer inspection | N/A
Brown 6 CT | Maintenance Outage | 4104 | Ignition System A - Replaced Propane Ignition Torch | Maintenance outage to replace ignition torch on unit. | N/A
Brown 8 CT | Forced Derate | 214.3256 | Row 3 Blade Design. | Unit derated to 120 MWs for R3 blade design. | Mechanical Issue
Brown 9 CT | Forced Derate | 452.7194 | Row 3 Blade Design. | Unit derated to 120 MWs for R3 blade design. | Mechanical Issue
Mill Creek 2 | Forced Derate | 257.4545 | HP Turbine Restriction | HP Turbine Restriction | Mechanical Issue
Mill Creek 3 | Maintenance Derate | 173.2482 | 3D Coal Mill Maintenance | 3D Coal Mill Maintenance | N/A
Mill Creek 4 | Maintenance Outage | 11664 | Air Heater Fouling, Pre-Heater Wash | Air Pre-Heater Wash | N/A
Trimble County 1 | Maintenance Outage | 8880 | Generator Bearing vibration | Bearing vibrations in the T | N/A
Trimble County 2 | Maintenance Derate | 2601.1532 | Boiler deslagging | Maintenance Derate for routine boiler deslagging. | N/A
Zorn 1 CT | Forced Outage | 384 | Low gas line pressure due to transmission line leak. | Gas Supply pressure lost due to leak out on line in the transmission system. | Fuel Supply Disruption
2018-05-17 | 31650.6496
Brown 3 | Forced Derate | 1028.176 | 3-1 ID Fan Ground Fault | GROUND FAULT ON 3-1 ID FAN | Mechanical Issue
Brown 9 CT | Maintenance Outage | 2832 | Vanes/nozzles B | Replace R2 vanes on unit. | N/A
Ghent 4 | Forced Derate | 1608.2803 | 4-1 BFP Outboard Bearing Exceeding Temp Limits | 4-1 BFP outboard bearing temperature exceeding temperature limits. | Mechanical Issue
Ghent 4 | Forced Derate | 235.5857 | 4-2 BFP Turbine Inboard Bearing Leaking Oil | 4-2 BFP turbine inboard bearing leaking oil. | Mechanical Issue
Ghent 4 | Forced Derate | 578.6076 | 4-1 BFP Outboard Bearing Exceeding Temp Limits | 4-1 BFP outboard bearing temperature exceeding temperature limits | Mechanical Issue
Mill Creek 4 | Maintenance Outage | 11568 | Air Pre-Heater Wash | Air Pre-Heater Wash | N/A
Trimble County 2 | Maintenance Outage | 13440 | LP Turbine Bearing #8 High Temps - Bearing Tilt | During turbine checkouts of the 2018 Spring Planned Outage, high temperatures were noted on the LP Turbine Bearing #8. The unit was taken offline on a MO basis to address the tilt of the bearing. | N/A
Zorn 1 CT | Forced Outage | 360 | Distributive Control System (DCS) - process computer | PLC Controller card failure. | Mechanical Issue
2018-05-20 | 30509.4976
Brown 5 CT | Forced Outage | 82 | DCS - hardware problems (including card failure) | Failure of siesmic vibration probe. Unhooked probe. | Mechanical Issue
Brown 9 CT | Maintenance Outage | 2832 | Vanes/nozzles B | Replace R2 vanes on unit. | N/A
Cane Run 7 | Forced Derate | 1505.7935 | Inlet Air Vanes / Nozzles - CT2 VGV2 Rotary Position Transmitter Deviation (Bent Linkage) | CT2 VGV2 rotarty position transmitter deviation due to bent linkage | Mechanical Issue
Ghent 4 | Forced Derate | 721.7041 | 4-1 BFP Outboard Bearing Exceeding Temp Limits | 4-1 BFP outboard bearing temperature exceeding temperature limits | Mechanical Issue
Mill Creek 4 | Maintenance Outage | 11568 | Air Pre-Heater Wash | Air Pre-Heater Wash | N/A
Trimble County 2 | Maintenance Outage | 13440 | Turbine Valve Screens Plugged | Due to boiler tube work during the outage, screens before the main stop valves were installed to protect the turbine. The differential across these screrens are monitored during startup, and were found to be experiencing a high pressure drop. A Maintenance Outage was taken to correct the issue and replace the screens. | N/A
Zorn 1 CT | Forced Outage | 360 | Distributive Control System (DCS) - process computer | PLC Controller card failure. | Mechanical Issue
2018-11-25 | 28101.5005
Brown 1 | Forced Derate | 1216.4211 | 1-1 FD Fan Coupling Bad and Bearings Wiped | 1-1 FD Fan coupling bad and bearings wiped | Mechanical Issue
Ghent 3 | Forced Outage | 11496 | First Superheater BTF | Multiple tube leaks in 3rd division panel. | Mechanical Issue
Mill Creek 1 | Maintenance Outage | 7200 | Air Heater Wash and Boiler Deslag | Air Heater Wash and Boiler Deslag | N/A
Mill Creek 4 | Forced Outage | 835.4667 | TDBFP Bearing Oil Leak/Fir | TDBFP Bearing Oil Leak/Fire | Mechanical Issue
Trimble County 2 | Maintenance Derate | 2378.0675 | Routine Boiler Deslagging and 2B TDBFP Maintenance | The unit was placed on a Planned Derate for routine boiler deslagging and maintenance work on the 2B TDBFP. | N/A
Trimble County 2 | Maintenance Derate | 559.5453 | Routine Boiler Deslagging and 2B TDBFP Maintenance - Extension | The unit was placed on a Planned Derate Extension for completion of the deslag and 2B TDBFP work. | N/A
Trimble County 9 CT | Maintenance Outage | 4056 | Exhaust Stack | The unit was placed on a Maintenance Outage for repairs to the exhaust stack lining. | N/A
Zorn 1 CT | Forced Outage | 360 | Distributive Control System (DCS) - process computer | PLC Controller card failure. | Mechanical Issue
2018-01-20 | 28085.3596
Brown 11 CT | Forced Derate | 214.3256 | Row 3 Blade Design. | Unit derated to 120 MWs for R3 blade design. | Mechanical Issue
Brown 11 CT | Forced Outage | 3072 | TAT Spread Exhaust Temps | Unit could not meet TAT spread exhaust temperature limits. | Mechanical Issue
Brown 3 | Maintenance Derate | 265.6937 | 3-2 BFP Circulating Water Piping fouling | Clean 3-2 BFP CW lines | N/A
Brown 6 CT | Maintenance Outage | 4104 | Ignition System A - Replaced Propane Ignition Torch | Maintenance outage to replace ignition torch on unit. | N/A
Brown 8 CT | Forced Derate | 214.3256 | Row 3 Blade Design. | Unit derated to 120 MWs for R3 blade design. | Mechanical Issue
Brown 9 CT | Forced Derate | 452.7194 | Row 3 Blade Design. | Unit derated to 120 MWs for R3 blade design. | Mechanical Issue
Ghent 1 | Forced Derate | 83.5179 | Deslagging Boiler - Wet Ash Pit | Slagging of the boiler in the wet ash pit | Mechanical Issue
Mill Creek 2 | Forced Derate | 257.4545 | HP Turbine Restriction | HP Turbine Restriction | Mechanical Issue
Mill Creek 4 | Forced Derate | 29.6229 | Induced Draft Fan suction pressure | ID Fan Suction Pressure | Mechanical Issue
Mill Creek 4 | Maintenance Outage | 10627.2 | Air Heater Fouling, Pre-Heater Wash | Air Pre-Heater Wash (OPEN) | N/A
Trimble County 1 | Maintenance Outage | 8380.5 | Generator Bearing vibration | Bearing vibrations in the T | N/A
Zorn 1 CT | Forced Outage | 384 | Low gas line pressure due to transmission line leak. | Gas Supply pressure lost due to leak out on line in the transmission system. | Fuel Supply Disruption
2018-11-27 | 27847.4961
Brown 1 | Forced Derate | 1216.4211 | 1-1 FD Fan Coupling Bad and Bearings Wiped | 1-1 FD Fan coupling bad and bearings wiped | Mechanical Issue
Cane Run 7 | Maintenance Derate | 7.2803 | Boiler Safety Valve Test | Post-outage safety/relief valve testing | N/A
Ghent 1 | Forced Derate | 220.1538 | AH Flue Gas Outlet Duct Pressure | AH outlet duct pressure | Mechanical Issue
Ghent 3 | Forced Outage | 2842.0667 | First Superheater BTF | Multiple tube leaks in 3rd division panel. | Mechanical Issue
Ghent 3 | Forced Outage | 3520.65 | Removed Debris From SH Division Panel Inlet Header | Removed tube 20 and 21 from the 3rd SH division panel, capped tubes at the header. Removed debris from SH division panel inlet header. | Mechanical Issue
Mill Creek 2 | Forced Derate | 1808.2909 | Air Heater High Differential - Variable | Air Heater High Differential - Variable | Mechanical Issue
Mill Creek 4 | Forced Outage | 11568 | TDBFP Bearing Oil Leak/Fire | TDBFP Bearing Oil Leak/Fire | Mechanical Issue
Paddy's Run 13 CT | Maintenance Outage | 2248.6333 | Other switchyard equipment - external | 138kv bus Maint. | N/A
Trimble County 9 CT | Maintenance Outage | 4056 | Exhaust Stack | The unit was placed on a Maintenance Outage for repairs to the exhaust stack lining. | N/A
Zorn 1 CT | Forced Outage | 360 | Distributive Control System (DCS) - process computer | PLC Controller card failure. | Mechanical Issue

## 2018 - Forced MWh Lost Detail
Unit | Event Type | Daily Net Forced MWh Lost | Cause | Description | Forced Category
2018-11-26 | 26112.8581
Brown 1 | Forced Derate | 1139.55 | 1-1 FD Fan Coupling Bad and Bearings Wiped | 1-1 FD Fan coupling bad and bearings wiped | Mechanical Issue
Brown 1 | Forced Derate | 62.8547 | Boiler MFT Due to Flame Instability | Boiler MFT due to flame instability | Mechanical Issue
Brown 1 | Forced Derate | 42.2368 | 1-1 FD Fan Coupling Bad and Bearings Wiped | 1-1 FD Fan coupling bad and bearings wiped | Mechanical Issue
Ghent 1 | Forced Derate | 125.6712 | AH Flue Gas Outlet Duct Pressure | AH outlet duct pressure | Mechanical Issue
Ghent 3 | Forced Outage | 11496 | First Superheater BTF | Multiple tube leaks in 3rd division panel. | Mechanical Issue
Mill Creek 2 | Forced Derate | 1318.5455 | Air Heater High Differential - Variable | Air Heater High Differential - Variable | Mechanical Issue
Mill Creek 4 | Forced Outage | 11568 | TDBFP Bearing Oil Leak/Fire | TDBFP Bearing Oil Leak/Fire | Mechanical Issue
Zorn 1 CT | Forced Outage | 360 | Distributive Control System (DCS) - process computer | PLC Controller card failure. | Mechanical Issue
2018-11-27 | 21535.5825
Brown 1 | Forced Derate | 1216.4211 | 1-1 FD Fan Coupling Bad and Bearings Wiped | 1-1 FD Fan coupling bad and bearings wiped | Mechanical Issue
Ghent 1 | Forced Derate | 220.1538 | AH Flue Gas Outlet Duct Pressure | AH outlet duct pressure | Mechanical Issue
Ghent 3 | Forced Outage | 2842.0667 | First Superheater BTF | Multiple tube leaks in 3rd division panel. | Mechanical Issue
Ghent 3 | Forced Outage | 3520.65 | Removed Debris From SH Division Panel Inlet Header | Removed tube 20 and 21 from the 3rd SH division panel, capped tubes at the header. Removed debris from SH division panel inlet header. | Mechanical Issue
Mill Creek 2 | Forced Derate | 1808.2909 | Air Heater High Differential - Variable | Air Heater High Differential - Variable | Mechanical Issue
Mill Creek 4 | Forced Outage | 11568 | TDBFP Bearing Oil Leak/Fire | TDBFP Bearing Oil Leak/Fire | Mechanical Issue
Zorn 1 CT | Forced Outage | 360 | Distributive Control System (DCS) - process computer | PLC Controller card failure. | Mechanical Issue
2018-12-03 | 21360.7738
Brown 1 | Forced Derate | 1216.4211 | 1-1 FD Fan Coupling Bad and Bearings Wiped | 1-1 FD Fan coupling bad and bearings wiped | Mechanical Issue
Brown 8 CT | Forced Derate | 214.3256 | Blades | Derate due to row 3 blade design. Blades will be changed out at next scheduled overhaul. | Mechanical Issue
Brown 9 CT | Forced Derate | 452.7194 | Blades | 19MW derate due to row 3 blade design. Blades will be changed at the next overhaul. | Mechanical Issue
Ghent 1 | Forced Derate | 884.3077 | Air Heater Flue Gas Duct Pressure | AH outlet duct pressure. | Mechanical Issue
Ghent 3 | Forced Outage | 11424 | Primary Superheater Tube Leak | Tube leak primary superheater panel 95. Removed debris from superheat division panel header. | Mechanical Issue
Mill Creek 2 | Forced Outage | 6785 | 2A ID Fan VFD Fault | 2A ID Fan VFD Fault | Mechanical Issue
Zorn 1 CT | Forced Outage | 384 | Distributive Control System (DCS) - process computer | PLC Controller card failure. | Mechanical Issue
2018-11-29 | 21168.6188
Brown 1 | Forced Derate | 1216.4211 | 1-1 FD Fan Coupling Bad and Bearings Wiped | 1-1 FD Fan coupling bad and bearings wiped | Mechanical Issue
Ghent 1 | Forced Derate | 220.1538 | AH Flue Gas Outlet Duct Pressure | AH outlet duct pressure | Mechanical Issue
Ghent 3 | Forced Outage | 11496 | Removed Debris From SH Division Panel Inlet Header | Removed tube 20 and 21 from the 3rd SH division panel, capped tubes at the header. Removed debris from SH division panel inlet header. | Mechanical Issue
Mill Creek 2 | Forced Derate | 1676.4364 | Air Heater High Differential - Variable | Air Heater High Differential - Variable | Mechanical Issue
Mill Creek 3 | Forced Derate | 929.2174 | 3C Coal Mill - Lube Oil Pump | 3C Coal Mill - Lube Oil Pump | Mechanical Issue
Mill Creek 4 | Forced Derate | 503.1858 | High Silica - Startup - Variable | High Silica - Startup - Variable | Mechanical Issue
Mill Creek 4 | Forced Derate | 711.2044 | High Silica - Startup | High Silica - Startup | Mechanical Issue
Trimble County 9 CT | Forced Outage | 4056 | Hydraulic oil system piping/valves | The unit was forced on outage after the hydraulic lift oil pressure was not sufficient to allow the rotor to turn. The hydraulic oil hoses were replaced to correct the issue. | Mechanical Issue
Zorn 1 CT | Forced Outage | 360 | Distributive Control System (DCS) - process computer | PLC Controller card failure. | Mechanical Issue
2018-11-28 | 18608.062
Brown 1 | Forced Derate | 1216.4211 | 1-1 FD Fan Coupling Bad and Bearings Wiped | 1-1 FD Fan coupling bad and bearings wiped | Mechanical Issue
Ghent 1 | Forced Derate | 220.1538 | AH Flue Gas Outlet Duct Pressure | AH outlet duct pressure | Mechanical Issue
Ghent 2 | Forced Derate | 414.3462 | SO2 Monitor | High SO2 dropped load, equipment failure. | Mechanical Issue
Ghent 3 | Forced Outage | 11496 | Removed Debris From SH Division Panel Inlet Header | Removed tube 20 and 21 from the 3rd SH division panel, capped tubes at the header. Removed debris from SH division panel inlet header. | Mechanical Issue
Mill Creek 2 | Forced Derate | 1808.2909 | Air Heater High Differential - Variable | Air Heater High Differential - Variable | Mechanical Issue
Mill Creek 4 | Forced Outage | 1952.1 | TDBFP Bearing Oil Leak/Fire | TDBFP Bearing Oil Leak/Fire | Mechanical Issue
Trimble County 7 CT | Forced Outage | 464.75 | Fuel piping and valves A | TC7 was forced onto outage due to the gas supply valve closing. The valve closed due to gas pressure swinging, and the controller was replaced, resolving the issue. | Mechanical Issue
Trimble County 9 CT | Forced Outage | 676 | Hydraulic oil system piping/valves | The unit was forced on outage after the hydraulic lift oil pressure was not sufficient to allow the rotor to turn. The hydraulic oil hoses were replaced to correct the issue. | Mechanical Issue
Zorn 1 CT | Forced Outage | 360 | Distributive Control System (DCS) - process computer | PLC Controller card failure. | Mechanical Issue
2018-09-09 | 17713.0593
Brown 3 | Forced Derate | 389.3684 | HP Turbine Fouling Restricting Steam Flow | HP turbine fouling restricting steam flow | Mechanical Issue
Cane Run 11 CT | Forced Outage | 336 | Starting system (including motor) A | Starting Diesel Radiator sprung a leak. | Mechanical Issue
Cane Run 7 | Forced Derate | 677.6071 | CT1 RAC Bypass Valve Malfunction Caused High RAC Temp Trip | CT1 RAC bypass valve malfunction caused high RAC temp trip. Valve closed manually | Mechanical Issue
Cane Run 7 | Forced Derate | 46.3321 | HRSG 1 BOP Unload/Trip | HRSG 1 BOP unload/trip - exact cause unknown, under investgation | Mechanical Issue
Cane Run 7 | Forced Derate | 3886.1055 | CT1 RAC Bypass Valve Malfunction Caused High RAC Temp Trip | CT1 RAC bypass valve malfunction caused high RAC temp trip. Positioner Replaced | Mechanical Issue
Ghent 2 | Forced Outage | 11664 | First Superheater BTF | Boiler tube leak. SH leak repaired and then found a WW leak 9/11/@ 0500 | Mechanical Issue
Trimble County 2 | Forced Derate | 353.6462 | 2C Pulverizer Mill Tripped Due to Low Primary Air Flow | Unit load was dropped when the 2C Mill tripped due to low Primary Air flow. | Mechanical Issue
Zorn 1 CT | Forced Outage | 360 | Distributive Control System (DCS) - process computer | PLC Controller card failure. | Mechanical Issue
2018-09-08 | 17062.9849
Brown 3 | Forced Derate | 389.3684 | HP Turbine Fouling Restricting Steam Flow | HP turbine fouling restricting steam flow | Mechanical Issue
Cane Run 11 CT | Forced Outage | 336 | Starting system (including motor) A | Starting Diesel Radiator sprung a leak. | Mechanical Issue
Cane Run 7 | Forced Derate | 631.275 | CT1 RAC Bypass Valve Malfunction Caused High RAC Temp Trip | CT1 RAC bypass valve malfunction caused high RAC temp trip. Valve closed manually | Mechanical Issue
Ghent 2 | Forced Outage | 11664 | First Superheater BTF | Boiler tube leak. SH leak repaired and then found a WW leak 9/11/@ 0500 | Mechanical Issue
Trimble County 10 CT | Forced Outage | 3506.75 | Fuel piping and valves A | The TC10 safety relief valve was leaking through, and a forced outage was taken to | Mechanical Issue
Trimble County 2 | Forced Derate | 60.1726 | Pulverizer Mill Swap - High Airflow | Unit load was dropped while performing a coal mill swap due to high airflow demands when bringing the sixth mill in service. | Mechanical Issue
Trimble County 2 | Forced Derate | 75.3038 | Pulverizer Mill Swap - High Airflow | Unit load was dropped while performing a coal mill swap due to high airflow demands when bringing the sixth mill in service. | Mechanical Issue
Trimble County 2 | Forced Derate | 40.1151 | Pulverizer Mill Swap - High Airflow | Unit load was dropped while performing a coal mill swap due to high airflow demands when bringing the sixth mill in service. | Mechanical Issue
Zorn 1 CT | Forced Outage | 360 | Distributive Control System (DCS) - process computer | PLC Controller card failure. | Mechanical Issue
2018-01-13 | 16682.2918
Brown 11 CT | Forced Derate | 214.3256 | Row 3 Blade Design. | Unit derated to 120 MWs for R3 blade design. | Mechanical Issue
Brown 3 | Forced Outage | 9912 | Reheat Section BTF | Various leak repairs in reheat section of boiler | Mechanical Issue
Brown 6 CT | Forced Outage | 4104 | Ignition System A - Propane Ignitor issues | Propane ignitor would not light off. | Mechanical Issue
Brown 8 CT | Forced Derate | 214.3256 | Row 3 Blade Design. | Unit derated to 120 MWs for R3 blade design. | Mechanical Issue
Brown 9 CT | Forced Derate | 452.7194 | Row 3 Blade Design. | Unit derated to 120 MWs for R3 blade design. | Mechanical Issue
Mill Creek 2 | Forced Derate | 257.4545 | HP Turbine Restriction | HP Turbine Restriction | Mechanical Issue
Trimble County 6 CT | Forced Outage | 137.2333 | Turbine thrust bearing high temp alarm. Faulty thermocouple. | TC6 was removed from service when an alarm came in for high temperature on turbine | Mechanical Issue
Trimble County 7 CT | Forced Outage | 880.0833 | Exhaust Fan alarm. Frozen switch. | TC7 tripped when alarm came in that neither exhaust fans were running. The switch | Mechanical Issue
Trimble County 9 CT | Forced Outage | 510.15 | Exhaust pressure alarm. Frozen switch. | TC9 tripped when an alarm came in for exhaust pressure. The switch was frozen beca | Mechanical Issue
2018-03-12 | 16559.1833
Brown 1 | Forced Outage | 2568 | Loss of drum level. Boiler leak at mud drum. | Boiler leak at mud drum header. Loss of drum level (Dry). | Mechanical Issue
Brown 2 | Forced Outage | 1917.7167 | Lost power to scrubber | Lost power to scrubber facility | Mechanical Issue
Brown 3 | Forced Outage | 9165.3 | Generator lockout due to loss of ground neutral | Generator lockout due to 60 fl vt fuse loss grnd neut. overcurrent 86u 3-1 86u 3-2 | Mechanical Issue
Brown 5 CT | Forced Outage | 2880 | Starting system (including motor) B | Failure of PSR2 controls on SFC. | Mechanical Issue
Trimble County 5 CT | Forced Outage | 28.1667 | Ignition system A | An igniter issue and an ignition exciter issue caused the unit to fail to start. | Mechanical Issue
2018-02-25 | 15918.2626
Brown 11 CT | Forced Derate | 214.3256 | Row 3 Blade Design. | Unit derated to 120 MWs for R3 blade design. | Mechanical Issue
Brown 8 CT | Forced Derate | 214.3256 | Row 3 Blade Design. | Unit derated to 120 MWs for R3 blade design. | Mechanical Issue
Brown 9 CT | Forced Derate | 452.7194 | Row 3 Blade Design. | Unit derated to 120 MWs for R3 blade design. | Mechanical Issue
Cane Run 7 | Forced Outage | 1252.1667 | CT1 Stage A Fuel Gas Valve solenoid wiring short, causing erratic operation | CT1 Stage A Fuel Gas Valve solenoid wiring short, causing erratic operation | Mechanical Issue
Ghent 1 | Forced Outage | 11496 | Waterwall (Furnace wall) A - 7th Floor | Water wall leak on 7th floor. | Mechanical Issue
Ghent 2 | Forced Derate | 212.1577 | 2-3 mill issues. | 2-3 mill issues. | Mechanical Issue
Ghent 2 | Forced Derate | 70.0962 | 2-3 mill issues. | 2-3 mill issues. | Mechanical Issue
Ghent 2 | Forced Derate | 9.9692 | Wet coal keeping 5 mills from getting to 460 mw and 2-3 mill | Wet coal keeping 5 mills from getting to 460 mw and 2-3 mill | Mechanical Issue
Mill Creek 1 | Forced Derate | 158.4091 | 1D Coal Feeder Plugged - Wet Coal | 1D Coal Feeder Plugged - Wet Coal | Mechanical Issue
Mill Creek 1 | Forced Derate | 126.2121 | 1B Coal Feeder Plugged - Wet Coal | 1B Coal Feeder Plugged - Wet Coal | Mechanical Issue
Mill Creek 2 | Forced Derate | 257.4545 | HP Turbine Restriction | HP Turbine Restriction | Mechanical Issue
Mill Creek 4 | Forced Outage | 972 | Low Level Drum Level Trip | Low Level Drum Level Trip | Mechanical Issue
Trimble County 1 | Forced Derate | 98.4265 | 1F coal feeder plugged due to wet coal | Wet coal caused an issue with pluggage on the 1F Coal Feeder. | Mechanical Issue
Zorn 1 CT | Forced Outage | 384 | DC lube oil pump failure. | DC lube oil pump failure. | Mechanical Issue

## 2019 - Total MWh Lost Detail
Unit | Event Type | Daily Net MWh Lost | Cause | Description | Forced Category
2019-02-03 | 36641.3994
Brown 3 | Maintenance Outage | 9912 | 3-1 Hot Water Recirc Pump Strainer Cleaning | 3-1 HWRP stainer cleaning | N/A
Brown 8 CT | Forced Derate | 214.3256 | Blades | Derate due to row 3 blade design. Blades will be changed out at next scheduled overhaul. | Mechanical Issue
Brown 9 CT | Forced Derate | 452.7194 | Blades | 19MW derate due to row 3 blade design. Blades will be changed at the next overhaul. | Mechanical Issue
Cane Run 7 | Forced Outage | 478.1 | CWP B Tripped During CWP A Motor Startup for Rotation Check | CWP B tripped when CWP A motor was started for rotation check | Mechanical Issue
Cane Run 7 | Maintenance Derate | 996.4996 | CWP A Motor Replacement Due to Bearing Failure | CWP A motor replacement due to failing bearing | N/A
Cane Run 7 | Forced Derate | 404.1083 | BFP 101/CT1 Trip Due to High Oil Temperature | BFP101/CT1 tripped due to high oil temeprature. Cooling water valve left in manual | Mechanical Issue
Cane Run 7 | Maintenance Derate | 171.6659 | CWP A Motor Replacement Due to Bearing Failure | CWP A motor replacement due to failing bearing | N/A
Cane Run 7 | Forced Derate | 4894.8333 | CT1 Offline to Replenish Demineralized Water Supply | CT1 taken offline to replinish demineralized water supply | Mechanical Issue
Cane Run 7 | Maintenance Derate | 787.151 | CWP A Motor Replacement Due to Bearing Failure | CWP A motor replacement due to failing bearing | N/A
Haefling 1 CT | Forced Outage | 336 | Liquid fuel oil transfer/forwarding pump A | Replace fuel oil piping going to unit from forwarding skid. | Mechanical Issue
Mill Creek 4 | Maintenance Outage | 11664 | Turbine Fine Mesh Screen Removal & Air Heater Wash | Turbine Fine Mesh Screen Removal & Air Heater Wash | N/A
Trimble County 2 | Maintenance Derate | 2029.1718 | Routine Boiler Deslagging | The unit was placed on a Maintenance Derate for routine boiler deslagging. | N/A
Trimble County 2 | Forced Derate | 157.8245 | 6A HPH Tube Leak | The unit load was derated when the 6A heater was taken out of service due to a suspected tube leak. | Mechanical Issue
Trimble County 8 CT | Maintenance Outage | 3759 | Exhaust Stack | The unit was placed on a Maintenance Outage for repairs to the exhaust stack lining. | N/A
Zorn 1 CT | Forced Outage | 384 | Distributive Control System (DCS) - process computer | PLC Controller card failure. | Mechanical Issue
2019-06-09 | 35845.9471
Brown 10 CT | Forced Derate | 47.6066 | Inlet air chillers B | Derate due to inlet air cooling. | Mechanical Issue
Brown 11 CT | Forced Derate | 47.6066 | Inlet air chillers B | Derate due to inlet air cooling. | Mechanical Issue
Brown 5 CT | Forced Derate | 142.9008 | Inlet air chillers B | Derate due to air permit and inlet cooling. | Mechanical Issue
Brown 7 CT | Maintenance Outage | 3504 | Stator; General | Maintenance outage to perform stator phase lug connection modification. Rotor is pulled, and electrical testing performed. | N/A
Brown 8 CT | Forced Derate | 142.8197 | Air cooling system | Derate due to inlet cooling and R3 Blades | Mechanical Issue
Brown 9 CT | Forced Derate | 47.6066 | Inlet air chillers B | Derate due to R3 Blade | Mechanical Issue
Cane Run 11 CT | Maintenance Outage | 336 | Other miscellaneous external problems | CR coal plant demolition outage | N/A
Cane Run 7 | Maintenance Outage | 15888 | Gas Turbine Exhaust Expansion Joint Repairs | Both gas turbine exhaust expansion joints leaking. Replaced | N/A
Ghent 1 | Forced Derate | 128.7981 | 1-3 Pulverizer Pyrite Section Noise | 1-3 mill noise in pyrite section. | Mechanical Issue
Mill Creek 1 | Forced Derate | 43.6364 | 1C Coal Mill - Wet Coal Issues | 1C Coal Mill - Wet Coal Issues | Mechanical Issue
Mill Creek 2 | Forced Derate | 387.6 | 2A & 2C Coal Feeders - Wet Coal Issues | 2A & 2C Coal Feeders - Wet Coal Issues | Mechanical Issue
Mill Creek 3 | Forced Derate | 101.9812 | 3C and 3D Coal Feeders - Wet Coal Issues - Variable | 3C and 3D Coal Feeders - Wet Coal Issues - Variable | Mechanical Issue
Paddy's Run 13 CT | Forced Outage | 3528 | Generator bearings | During Reassembly of the unit we had to roll out bearings for troubleshooting purposes and found them to have excessive wear. Sent out to be repoured. | Mechanical Issue
Trimble County 1 | Forced Outage | 8880 | Platen Superheater BTF | The unit was taken offline for repairs to tubes in the superheat vertical platens, 13th assembly. | Mechanical Issue
Trimble County 2 | Maintenance Derate | 2223.7663 | Routine Boiler Deslagging | The unit was placed on a Maintenance Derate for routine boiler deslagging. | N/A
Trimble County 7 CT | Forced Derate | 59.625 | High pressure bearings D | The unit was placed on a limited load for one hour as a hold point for #1 turbine bearing to warm and eliminate vibrations for the rest of operation. | Mechanical Issue
Zorn 1 CT | Forced Outage | 336 | Distributive Control System (DCS) - process computer | PLC Controller card failure. | Mechanical Issue
2019-06-10 | 34637.2799
Brown 10 CT | Forced Derate | 47.6066 | Inlet air chillers B | Derate due to inlet air cooling. | Mechanical Issue
Brown 11 CT | Forced Derate | 47.6066 | Inlet air chillers B | Derate due to inlet air cooling. | Mechanical Issue
Brown 5 CT | Forced Derate | 142.9008 | Inlet air chillers B | Derate due to air permit and inlet cooling. | Mechanical Issue
Brown 7 CT | Maintenance Outage | 3504 | Stator; General | Maintenance outage to perform stator phase lug connection modification. Rotor is pulled, and electrical testing performed. | N/A
Brown 8 CT | Forced Derate | 142.8197 | Air cooling system | Derate due to inlet cooling and R3 Blades | Mechanical Issue
Brown 9 CT | Forced Derate | 47.6066 | Inlet air chillers B | Derate due to R3 Blade | Mechanical Issue
Cane Run 11 CT | Maintenance Outage | 109.2 | Other miscellaneous external problems | CR coal plant demolition outage | N/A
Cane Run 7 | Maintenance Outage | 15888 | Gas Turbine Exhaust Expansion Joint Repairs | Both gas turbine exhaust expansion joints leaking. Replaced | N/A
Mill Creek 1 | Forced Derate | 23.1818 | 1C Coal Mill - Wet Coal Issues | 1C Coal Mill - Wet Coal Issues | Mechanical Issue
Mill Creek 1 | Forced Derate | 1355.1515 | 1A, 1B and 1C Coal Mills - Wet Coal Issues | 1A, 1B and 1C Coal Mills - Wet Coal Issues | Mechanical Issue
Mill Creek 2 | Forced Derate | 176.85 | 2C Coal Feeder Plugged - Wet Coal Issues | 2C Coal Feeder Plugged - Wet Coal Issues | Mechanical Issue
Mill Creek 2 | Forced Derate | 274.5 | 2A Coal Feeder Plugged - Wet Coal Issues | 2A Coal Feeder Plugged - Wet Coal Issues | Mechanical Issue
Mill Creek 3 | Forced Derate | 421.653 | 3C and 3D Coal Feeders - Wet Coal Issues - Variable | 3C and 3D Coal Feeders - Wet Coal Issues - Variable | Mechanical Issue
Mill Creek 3 | Maintenance Derate | 172.3365 | 3D PA Fan Maintenance | 3D PA Fan Maintenance | N/A
Mill Creek 4 | Forced Derate | 1331.6327 | 4A, 4D and 4E Coal Feeders - Wet Coal Issues - Variable | 4A, 4D and 4E Coal Feeders - Wet Coal Issues - Variable | Mechanical Issue
Mill Creek 4 | Forced Derate | 628.8342 | 4A and 4E Coal Mills - Wet Coal Issues | 4A and 4E Coal Mills - Wet Coal Issues | Mechanical Issue
Paddy's Run 13 CT | Forced Outage | 1107.4 | Generator bearings | During Reassembly of the unit we had to roll out bearings for troubleshooting purposes and found them to have excessive wear. Sent out to be repoured. | Mechanical Issue
Trimble County 1 | Forced Outage | 8880 | Platen Superheater BTF | The unit was taken offline for repairs to tubes in the superheat vertical platens, 13th assembly. | Mechanical Issue
Zorn 1 CT | Forced Outage | 336 | Distributive Control System (DCS) - process computer | PLC Controller card failure. | Mechanical Issue
2019-12-20 | 34591.1054
Brown 10 CT | Maintenance Outage | 798.1 | Switchyard circuit breakers - external | F590Substation Circuit breaker maintenance. Gas flow meter calibration and orifice check. | N/A
Brown 3 | Forced Outage | 9086 | MFT - 3E Heater Extraction Piping Leak at DA Heater | F540MFT due to BCWP east diff press sensing line leak. 3e heater extraction piping leak at DA heater. | Mechanical Issue
Brown 3 | Maintenance Outage | 826 | Generator Air Test | F790conducting air test on generator for leaks | N/A
Brown 8 CT | Forced Derate | 214.3256 | Blades | F600Derate due to R3 blades. | Mechanical Issue
Brown 9 CT | Forced Derate | 452.7194 | Blades | F600Derate due to R3 blades. | Mechanical Issue
Ghent 2 | Maintenance Outage | 5985.9 | Pull Turbine Fine Mesh Screens | F590Outage # 8U2 came off line for a maintenance outage to pull turbine fine mesh screens. | N/A
Mill Creek 2 | Forced Outage | 7080 | Boiler Tube Leak - Waterwall | F820Boiler Tube Leak - Waterwall | Mechanical Issue
Mill Creek 3 | Maintenance Outage | 9456 | Maintenance Outage - Turbine Vibration | F850Maintenance Outage - Turbine Vibration | N/A
Trimble County 1 | Forced Derate | 692.0604 | High Silica | FA00The unit was placed on an immediate derate due to silica level restrictions in the condensate/feedwater. | Mechanical Issue
2019-12-21 | 33964.4844
Brown 3 | Maintenance Outage | 9912 | Generator Air Test | F790conducting air test on generator for leaks | N/A
Brown 8 CT | Forced Derate | 214.3256 | Blades | F600Derate due to R3 blades. | Mechanical Issue
Brown 9 CT | Forced Derate | 452.7194 | Blades | F600Derate due to R3 blades. | Mechanical Issue
Ghent 2 | Maintenance Outage | 11664 | Pull Turbine Fine Mesh Screens | F590Outage # 8U2 came off line for a maintenance outage to pull turbine fine mesh screens. | N/A
Mill Creek 2 | Forced Outage | 1504.5 | Boiler Tube Leak - Waterwall | F820Boiler Tube Leak - Waterwall | Mechanical Issue
Mill Creek 3 | Maintenance Outage | 9456 | Maintenance Outage - Turbine Vibration | F850Maintenance Outage - Turbine Vibration | N/A
Trimble County 2 | Maintenance Derate | 760.9394 | Routine Boiler Deslagging | FS00The unit was placed on a maintenace derate for routine boiler deslagging. | N/A
2019-05-14 | 31789.6667
Brown 10 CT | Maintenance Outage | 100.3 | Lube oil system - general | Outage to check and change as needed brushes for DC lube oil motors. | N/A
Brown 11 CT | Maintenance Outage | 165.2 | Lube oil system - general | Outage to check and change as needed brushes for DC lube oil motors. | N/A
Brown 8 CT | Maintenance Outage | 273.3667 | Lube oil system - general | Outage to check and change as needed brushes for DC lube oil motors. | N/A
Brown 9 CT | Forced Outage | 1852.6 | Turning gear and motor C | Outage to replace pump and motor for rotor barring system. Motor was changed first and then existing pump would not prime itself. | Mechanical Issue
Ghent 1 | Forced Outage | 5676.3 | Generator Vibration (Excluding Failed Bearing) | Turbine vibration | Mechanical Issue
Ghent 2 | Maintenance Outage | 8650.8 | Waterwall (Furnace wall) | Maintenance Outage | N/A
Paddy's Run 11 CT | Forced Outage | 312 | Starting system (including motor) A | When Servicing Diesel we found Antifreeze in the Oil. Believe that the head gasket is leaking. Will disassembly the motor to know for sure. | Mechanical Issue
Trimble County 2 | Forced Outage | 2508.425 | Generator Bearing #11 Vibration | The unit tripped offline due to vibration levels in Generator Bearing #11. | Mechanical Issue
Trimble County 2 | Forced Outage | 5044.825 | D2 Burner Flame Scanning Equipment Issues | The unit tripped due to issues with the flame scanning equipment on D2 burner. | Mechanical Issue
Trimble County 2 | Forced Outage | 1296.175 | D1 Burner Flame Scanning Equipment Issues | The unit tripped due to issues with the flame scanning equipment on the D1 burner. | Mechanical Issue
Trimble County 2 | Forced Outage | 3851.225 | SF due to MDBFP Voith Drive Scoop Tube Issues | The unit failed to start when the Motor Driven Boiler Feed Pump experienced issues with the Voith Drive scoop tube. | Mechanical Issue
Trimble County 7 CT | Maintenance Outage | 1698.45 | High pressure bearings D | The unit was placed on a Maintenance Outage for investigation into the turbine bearing vibration. | N/A
Zorn 1 CT | Forced Outage | 360 | Distributive Control System (DCS) - process computer | PLC Controller card failure. | Mechanical Issue
2019-12-22 | 31586.787
Brown 3 | Maintenance Outage | 3310.8833 | Generator Air Test | F790conducting air test on generator for leaks | N/A
Brown 3 | Forced Outage | 2849.7 | Deaerator Storage Tank Manway Door Gasket Leaking | F540DA storage tank manway door gasket leaking | Mechanical Issue
Brown 3 | Forced Outage | 2271.5 | RS Intercept Valve EH Leak | F540RS intercept valve EH leak - seal blownalso DA tank man door damage | Mechanical Issue
Brown 8 CT | Forced Derate | 214.3256 | Blades | F600Derate due to R3 blades. | Mechanical Issue
Brown 9 CT | Forced Derate | 452.7194 | Blades | F600Derate due to R3 blades. | Mechanical Issue
Cane Run 7 | Forced Derate | 1832.7167 | CT1 Trip on High Blade Path Spread - 5 T/C Failure | F520CT1 tripped on high blade path spread when combustor 5 T/C failed. Replaced T/C | Mechanical Issue
Ghent 1 | Maintenance Outage | 5883.7167 | Condenser Tube Leak | F590Outage # 8U1 came offline to repair a condenser tube leak. | N/A
Ghent 2 | Maintenance Outage | 3539.7 | Pull Turbine Fine Mesh Screens | F590Outage # 8U2 came off line for a maintenance outage to pull turbine fine mesh screens. | N/A
Mill Creek 3 | Maintenance Outage | 9456 | Maintenance Outage - Turbine Vibration | F850Maintenance Outage - Turbine Vibration | N/A
Trimble County 2 | Maintenance Derate | 1775.5253 | Routine Boiler Deslagging | FS00The unit was placed on a maintenace derate for routine boiler deslagging. | N/A
2019-06-08 | 29727.9474
Brown 10 CT | Forced Derate | 47.6066 | Inlet air chillers B | Derate due to inlet air cooling. | Mechanical Issue
Brown 11 CT | Forced Derate | 47.6066 | Inlet air chillers B | Derate due to inlet air cooling. | Mechanical Issue
Brown 5 CT | Forced Derate | 142.9008 | Inlet air chillers B | Derate due to air permit and inlet cooling. | Mechanical Issue
Brown 7 CT | Maintenance Outage | 3504 | Stator; General | Maintenance outage to perform stator phase lug connection modification. Rotor is pulled, and electrical testing performed. | N/A
Brown 8 CT | Forced Derate | 142.8197 | Air cooling system | Derate due to inlet cooling and R3 Blades | Mechanical Issue
Brown 9 CT | Forced Derate | 47.6066 | Inlet air chillers B | Derate due to R3 Blade | Mechanical Issue
Cane Run 11 CT | Maintenance Outage | 336 | Other miscellaneous external problems | CR coal plant demolition outage | N/A
Cane Run 7 | Maintenance Outage | 15888 | Gas Turbine Exhaust Expansion Joint Repairs | Both gas turbine exhaust expansion joints leaking. Replaced | N/A
Paddy's Run 13 CT | Forced Outage | 3528 | Generator bearings | During Reassembly of the unit we had to roll out bearings for troubleshooting purposes and found them to have excessive wear. Sent out to be repoured. | Mechanical Issue
Trimble County 1 | Forced Outage | 4828.5 | Platen Superheater BTF | The unit was taken offline for repairs to tubes in the superheat vertical platens, 13th assembly. | Mechanical Issue
Trimble County 2 | Maintenance Derate | 819.2823 | Routine Boiler Deslagging | The unit was placed on a Maintenance Derate for routine boiler deslagging. | N/A
Trimble County 7 CT | Forced Derate | 59.625 | High pressure bearings D | The unit was placed on a limited load for one hour as a hold point for #1 turbine bearing to warm and eliminate vibrations for the rest of operation. | Mechanical Issue
Zorn 1 CT | Forced Outage | 336 | Distributive Control System (DCS) - process computer | PLC Controller card failure. | Mechanical Issue
2019-12-19 | 29644.7188
Brown 3 | Forced Outage | 9912 | MFT - 3E Heater Extraction Piping Leak at DA Heater | F540MFT due to BCWP east diff press sensing line leak. 3e heater extraction piping leak at DA heater. | Mechanical Issue
Brown 8 CT | Forced Derate | 214.3256 | Blades | F600Derate due to R3 blades. | Mechanical Issue
Brown 9 CT | Forced Derate | 452.7194 | Blades | F600Derate due to R3 blades. | Mechanical Issue
Cane Run 7 | Forced Derate | 1070.0333 | CT1 BFP 101 Tripped Manually - Frozen PT | F480CT1, BFP 101 tripped manually due to frozen PT. Reset heat trace | Cold Weather
Mill Creek 2 | Forced Outage | 7080 | Boiler Tube Leak - Waterwall | F820Boiler Tube Leak - Waterwall | Mechanical Issue
Mill Creek 3 | Maintenance Outage | 9456 | Maintenance Outage - Turbine Vibration | F850Maintenance Outage - Turbine Vibration | N/A
Trimble County 1 | Forced Derate | 767.5801 | High Silica | FA00The unit was placed on an immediate derate due to silica level restrictions in the condensate/feedwater. | Mechanical Issue
Trimble County 1 | Forced Derate | 692.0604 | High Silica | FA00The unit was placed on an immediate derate due to silica level restrictions in the condensate/feedwater. | Mechanical Issue
2019-12-29 | 27041.337
Brown 8 CT | Forced Derate | 214.3256 | Blades | F600Derate due to R3 blades. | Mechanical Issue
Brown 9 CT | Forced Derate | 452.7194 | Blades | F600Derate due to R3 blades. | Mechanical Issue
Ghent 4 | Maintenance Outage | 7942.7667 | Condenser Tube Leak | F590Outage #5Repair condenser leak. Switched to reserve at 12/29-16:37 hours. | N/A
Mill Creek 1 | Maintenance Outage | 7200 | Condenser Clean | F180Condenser Clean | N/A
Mill Creek 3 | Maintenance Outage | 9456 | Maintenance Outage - Turbine Vibration | F850Maintenance Outage - Turbine Vibration | N/A
Trimble County 2 | Maintenance Derate | 1775.5253 | Routine Boiler Deslagging | FS00The unit was placed on a maintenace derate for routine boiler deslagging. | N/A

## 2019 - Forced MWh Lost Detail
Unit | Event Type | Daily Net Forced MWh Lost | Cause | Description | Forced Category
2019-05-07 | 26411.6505
Cane Run 7 | Forced Derate | 4766.4156 | CT1 Turning Gear (Speed Sensor) | CT1 turning gear shear pins broke starting high-speed turning gear. Replaced | Mechanical Issue
Ghent 4 | Forced Derate | 275.6467 | 4-4 Pulverizer Tripped Due to 4 kV Breaker DC Fault Detection | 4-4 Pulverizer tripped with coal due to 4KV breaker DC fault detection. | Mechanical Issue
Mill Creek 1 | Forced Outage | 7200 | Emergency Seal Oil Pump | Emergency Seal Oil Pump | Mechanical Issue
Paddy's Run 11 CT | Forced Outage | 312 | Starting system (including motor) A | When Servicing Diesel we found Antifreeze in the Oil. Believe that the head gasket is leaking. Will disassembly the motor to know for sure. | Mechanical Issue
Trimble County 2 | Forced Outage | 13428 | Generator Bearing #11 Vibration (Tail Shaft) | The unit was placed on a forced outage for repairs to Generator Bearing #11, which sustained damage during start-up from a lack of oil flow to the bearing due to an install issue by GE. | Mechanical Issue
Trimble County 7 CT | Forced Derate | 69.5882 | High pressure bearings D | The unit was placed on a limited load for one hour as a hold point for #1 turbine bearing to warm and eliminate vibrations for the rest of operation. | Mechanical Issue
Zorn 1 CT | Forced Outage | 360 | Distributive Control System (DCS) - process computer | PLC Controller card failure. | Mechanical Issue
2019-05-12 | 25548
Ghent 1 | Forced Outage | 11448 | Generator Vibration (Excluding Failed Bearing) | Turbine vibration | Mechanical Issue
Paddy's Run 11 CT | Forced Outage | 312 | Starting system (including motor) A | When Servicing Diesel we found Antifreeze in the Oil. Believe that the head gasket is leaking. Will disassembly the motor to know for sure. | Mechanical Issue
Trimble County 2 | Forced Outage | 3254.425 | Turbine Bearing #7 Vibration | The unit failed to complete startup due to high vibration levels on Turbine Bearing #7. | Mechanical Issue
Trimble County 2 | Forced Outage | 10173.575 | Generator Bearing #9 Vibration | The unit failed to complete startup due to high vibration levels on Generator Bearing #9. | Mechanical Issue
Zorn 1 CT | Forced Outage | 360 | Distributive Control System (DCS) - process computer | PLC Controller card failure. | Mechanical Issue
2019-05-13 | 24961.0167
Brown 9 CT | Forced Outage | 550.6667 | Turning gear and motor C | Outage to replace pump and motor for rotor barring system. Motor was changed first and then existing pump would not prime itself. | Mechanical Issue
Ghent 1 | Forced Outage | 11448 | Generator Vibration (Excluding Failed Bearing) | Turbine vibration | Mechanical Issue
Paddy's Run 11 CT | Forced Outage | 312 | Starting system (including motor) A | When Servicing Diesel we found Antifreeze in the Oil. Believe that the head gasket is leaking. Will disassembly the motor to know for sure. | Mechanical Issue
Trimble County 2 | Forced Outage | 6732.65 | Generator Bearing #9 Vibration | The unit failed to complete startup due to high vibration levels on Generator Bearing #9. | Mechanical Issue
Trimble County 2 | Forced Outage | 5557.7 | Generator Bearing #11 Vibration | The unit tripped offline due to vibration levels in Generator Bearing #11. | Mechanical Issue
Zorn 1 CT | Forced Outage | 360 | Distributive Control System (DCS) - process computer | PLC Controller card failure. | Mechanical Issue
2019-05-11 | 24656.5731
Ghent 1 | Forced Outage | 7568.4 | Hydrogen Seals | Hydrogen leak | Mechanical Issue
Ghent 1 | Forced Outage | 2862 | Generator Vibration (Excluding Failed Bearing) | Turbine vibration | Mechanical Issue
Ghent 2 | Forced Derate | 126.1731 | 2-5 Pulverizer Mill Overheated | 2-5 Mill got hot. Maintenance inspected, nothing found. | Mechanical Issue
Paddy's Run 11 CT | Forced Outage | 312 | Starting system (including motor) A | When Servicing Diesel we found Antifreeze in the Oil. Believe that the head gasket is leaking. Will disassembly the motor to know for sure. | Mechanical Issue
Trimble County 2 | Forced Outage | 13428 | Turbine Bearing #7 Vibration | The unit failed to complete startup due to high vibration levels on Turbine Bearing #7. | Mechanical Issue
Zorn 1 CT | Forced Outage | 360 | Distributive Control System (DCS) - process computer | PLC Controller card failure. | Mechanical Issue
2019-05-06 | 24338.3627
Cane Run 7 | Forced Derate | 8339.7793 | CT1 Turning Gear (Speed Sensor) | CT1 turning gear shear pins broke starting high-speed turning gear. Replaced | Mechanical Issue
Mill Creek 1 | Forced Outage | 1800 | Emergency Seal Oil Pump | Emergency Seal Oil Pump | Mechanical Issue
Paddy's Run 11 CT | Forced Outage | 312 | Starting system (including motor) A | When Servicing Diesel we found Antifreeze in the Oil. Believe that the head gasket is leaking. Will disassembly the motor to know for sure. | Mechanical Issue
Trimble County 2 | Forced Outage | 13428 | Generator Bearing #11 Vibration (Tail Shaft) | The unit was placed on a forced outage for repairs to Generator Bearing #11, which sustained damage during start-up from a lack of oil flow to the bearing due to an install issue by GE. | Mechanical Issue
Trimble County 7 CT | Forced Derate | 98.5833 | High pressure bearings D | The unit was placed on a limited load for one hour as a hold point for #1 turbine bearing to warm and eliminate vibrations for the rest of operation. | Mechanical Issue
Zorn 1 CT | Forced Outage | 360 | Distributive Control System (DCS) - process computer | PLC Controller card failure. | Mechanical Issue
2019-08-11 | 22935.1815
Brown 10 CT | Forced Derate | 47.6066 | Inlet air chillers B | Derate due to inlet air cooling. | Mechanical Issue
Brown 11 CT | Forced Derate | 47.6066 | Inlet air chillers B | Derate due to inlet air cooling. | Mechanical Issue
Brown 3 | Forced Derate | 151.0154 | Turbine Blade Fouling | Turbine perfomance due to blade fouling. | Mechanical Issue
Brown 5 CT | Forced Derate | 142.9008 | Inlet air chillers B | Derate due to air permit and inlet cooling. | Mechanical Issue
Brown 6 CT | Forced Derate | 166.8571 | Gas Turbine Control System - logic problems | Derate due to tuning conditions above 140MWs. Limited operation to below this until OEM can give recommendation. | Mechanical Issue
Brown 6 CT | Forced Outage | 187.3667 | Vibration (not engine) in unit not attributable to bearings or other components B | Erratic seismic probe on number 2 bearing. Repaired connection. | Mechanical Issue
Brown 8 CT | Forced Derate | 142.8197 | Air cooling system | Derate due to inlet cooling and R3 Blades | Mechanical Issue
Brown 9 CT | Forced Derate | 47.6066 | Inlet air chillers B | Derate due to R3 Blade | Mechanical Issue
Brown 9 CT | Forced Outage | 197.6333 | Switchyard circuit breakers - (not outside management control) | Limit switch in MOS tripped substation breaker upon closure. Will adjust limit switch at future opportunity. | Mechanical Issue
Cane Run 11 CT | Forced Outage | 336 | Turning gear and motor C | Turning Gear Gear Box Failure. | Mechanical Issue
Cane Run 7 | Forced Derate | 7955.7689 | HRSG 1 HPSH Drain Line Leak | HRSG 1 HPSH drain line leak. Replaced failed piping and fittings | Mechanical Issue
Trimble County 2 | Forced Outage | 13176 | Waterwall BTF | The unit was brought offline for waterwall tube leak repairs, located on the left waterwall below the middle burner elevation. | Mechanical Issue
Zorn 1 CT | Forced Outage | 336 | Distributive Control System (DCS) - process computer | PLC Controller card failure. | Mechanical Issue
2019-04-21 | 22223.9297
Ghent 2 | Forced Outage | 11664 | Burner Fire at B Corner Windbox | Forced Outage Burner fire @ B corner windbox. | Mechanical Issue
Mill Creek 2 | Forced Derate | 455.9297 | High Silica - Startup - Variable | High Silica - Startup - Variable | Mechanical Issue
Mill Creek 3 | Forced Outage | 9432 | Condenser Waterbox Leaks | Condenser Waterbox Leaks | Mechanical Issue
Paddy's Run 11 CT | Forced Outage | 312 | Starting system (including motor) A | When Servicing Diesel we found Antifreeze in the Oil. Believe that the head gasket is leaking. Will disassembly the motor to know for sure. | Mechanical Issue
Zorn 1 CT | Forced Outage | 360 | Distributive Control System (DCS) - process computer | PLC Controller card failure. | Mechanical Issue
2019-05-10 | 21917.7
Ghent 1 | Forced Outage | 4817.7 | Hydrogen Seals | Hydrogen leak | Mechanical Issue
Mill Creek 1 | Forced Outage | 3000 | High Turbine Vibration | High Turbine Vibration | Mechanical Issue
Paddy's Run 11 CT | Forced Outage | 312 | Starting system (including motor) A | When Servicing Diesel we found Antifreeze in the Oil. Believe that the head gasket is leaking. Will disassembly the motor to know for sure. | Mechanical Issue
Trimble County 2 | Forced Outage | 6396.95 | Generator Bearing #11 Vibration (Tail Shaft) | The unit was placed on a forced outage for repairs to Generator Bearing #11, which sustained damage during start-up from a lack of oil flow to the bearing due to an install issue by GE. | Mechanical Issue
Trimble County 2 | Forced Outage | 4671.825 | Turbine Bearing #7 Vibration | The unit failed to complete startup due to high vibration levels on Turbine Bearing #7. | Mechanical Issue
Trimble County 2 | Forced Outage | 2359.225 | Turbine Bearing #7 Vibration | The unit failed to complete startup due to high vibration levels on Turbine Bearing #7. | Mechanical Issue
Zorn 1 CT | Forced Outage | 360 | Distributive Control System (DCS) - process computer | PLC Controller card failure. | Mechanical Issue
2019-04-22 | 21042.9391
Ghent 2 | Forced Outage | 178.2 | Burner Fire at B Corner Windbox | Forced Outage Burner fire @ B corner windbox. | Mechanical Issue
Ghent 2 | Forced Derate | 191.9077 | LP heater - 3 Heaters Out of Service (Extractions) | Having trouble getting extractions open, had 3 heaters out of service. | Mechanical Issue
Ghent 3 | Forced Outage | 10498.0833 | Exciter Cooler Leak Caused Generator Ground Fault | Exiter cooler leaked causing a generator ground detection. | Mechanical Issue
Mill Creek 3 | Forced Outage | 9432 | Condenser Waterbox Leaks | Condenser Waterbox Leaks | Mechanical Issue
Paddy's Run 11 CT | Forced Outage | 312 | Starting system (including motor) A | When Servicing Diesel we found Antifreeze in the Oil. Believe that the head gasket is leaking. Will disassembly the motor to know for sure. | Mechanical Issue
Trimble County 7 CT | Forced Derate | 70.748 | High pressure bearings D | The unit was placed on a limited load for one hour as a hold point for turbine bearing #1 to warm and eliminate vibrations for the rest of operation. | Mechanical Issue
Zorn 1 CT | Forced Outage | 360 | Distributive Control System (DCS) - process computer | PLC Controller card failure. | Mechanical Issue
2019-05-14 | 20901.55
Brown 9 CT | Forced Outage | 1852.6 | Turning gear and motor C | Outage to replace pump and motor for rotor barring system. Motor was changed first and then existing pump would not prime itself. | Mechanical Issue
Ghent 1 | Forced Outage | 5676.3 | Generator Vibration (Excluding Failed Bearing) | Turbine vibration | Mechanical Issue
Paddy's Run 11 CT | Forced Outage | 312 | Starting system (including motor) A | When Servicing Diesel we found Antifreeze in the Oil. Believe that the head gasket is leaking. Will disassembly the motor to know for sure. | Mechanical Issue
Trimble County 2 | Forced Outage | 2508.425 | Generator Bearing #11 Vibration | The unit tripped offline due to vibration levels in Generator Bearing #11. | Mechanical Issue
Trimble County 2 | Forced Outage | 5044.825 | D2 Burner Flame Scanning Equipment Issues | The unit tripped due to issues with the flame scanning equipment on D2 burner. | Mechanical Issue
Trimble County 2 | Forced Outage | 1296.175 | D1 Burner Flame Scanning Equipment Issues | The unit tripped due to issues with the flame scanning equipment on the D1 burner. | Mechanical Issue
Trimble County 2 | Forced Outage | 3851.225 | SF due to MDBFP Voith Drive Scoop Tube Issues | The unit failed to start when the Motor Driven Boiler Feed Pump experienced issues with the Voith Drive scoop tube. | Mechanical Issue
Zorn 1 CT | Forced Outage | 360 | Distributive Control System (DCS) - process computer | PLC Controller card failure. | Mechanical Issue

## 2020 - Total MWh Lost Detail
Unit | Event Type | Daily Net MWh Lost | Cause | Description | Forced Category
2020-04-04 | 36416.138
Brown 6 CT | Forced Outage | 3768 | Turning gear and motor B | F690Unit would not go on rotor barring. | Mechanical Issue
Cane Run 7 | Forced Outage | 404.8333 | CT2 Trip on Blade Path Spread Due to Clogged Fuel Strainer | F120CT2 trip on blade path spread due to clogged fuel strainer. Cleaned strainer and restarted | Mechanical Issue
Cane Run 7 | Maintenance Derate | 8137.0764 | 2020 Planned Spring Outage - Hot End Inspection B - CT1 Extension | F5302020 planned spring outage - CT1 extension | N/A
Ghent 1 | Forced Outage | 3816 | Waterwall BTF | F540Outage #6GH1 was forced off-line due to a water wall tube leak on "D" corner 6th elevation. | Mechanical Issue
Ghent 1 | Maintenance Outage | 7632 | Turbine Valve Screen Change Out | F590Outage #7Maintenance outage for turbine valve screen change out. | N/A
Mill Creek 2 | Maintenance Outage | 7104 | Air Heater Wash | F320Maintenance Outage - Air Heater Wash | N/A
Trimble County 10 CT | Maintenance Outage | 743.6 | Gas fuel system B | F590The unit was placed on a Maintenance Outage for the fuel gas supplier technicians to perform routine inspection and cleaning on non-owner gas supply meters. | N/A
Trimble County 2 | Maintenance Derate | 732.6283 | Routine Boiler Deslagging | FS00The unit was placed on a minatenance derate for routine boiler deslagging. | N/A
Trimble County 5 CT | Maintenance Outage | 743.6 | Gas fuel system B | F590The unit was placed on a Maintenance Outage for the fuel gas supplier technicians to perform routine inspection and cleaning on non-owner gas supply meters. | N/A
Trimble County 6 CT | Maintenance Outage | 743.6 | Gas fuel system B | F590The unit was placed on a Maintenance Outage for the fuel gas supplier technicians to perform routine inspection and cleaning on non-owner gas supply meters. | N/A
Trimble County 7 CT | Maintenance Outage | 743.6 | Gas fuel system B | F590The unit was placed on a Maintenance Outage for the fuel gas supplier technicians to perform routine inspection and cleaning on non-owner gas supply meters. | N/A
Trimble County 8 CT | Maintenance Outage | 743.6 | Gas fuel system B | F590The unit was placed on a Maintenance Outage for the fuel gas supplier technicians to perform routine inspection and cleaning on non-owner gas supply meters. | N/A
Trimble County 9 CT | Maintenance Outage | 743.6 | Gas fuel system B | F590The unit was placed on a Maintenance Outage for the fuel gas supplier technicians to perform routine inspection and cleaning on non-owner gas supply meters. | N/A
Zorn 1 CT | Forced Outage | 360 | Stator; General | F820Generator lockout, troubleshooting pending. | Mechanical Issue
2020-04-26 | 30209.466
Cane Run 7 | Maintenance Outage | 16656 | IP Startup Bypass System Valve Maintenance and Instrumentation Problems | F540Block maintenance outage for valve maintenace and instrumentation problems | N/A
Ghent 3 | Maintenance Outage | 7.975 | Air Heater Inspection and Wash | F530Outage #4Maintenance Outage. | N/A
Ghent 3 | Maintenance Outage | 11476.025 | Air Heater Inspection and Wash - Extension | F590Outage #5Maintenance Extension. Air heater wash. | N/A
Trimble County 2 | Maintenance Derate | 1709.466 | Routine Boiler Deslagging | FS00The unit was placed on a Maintenance Derate for routine boiler deslagging. | N/A
Zorn 1 CT | Forced Outage | 360 | Stator; General | F820Generator lockout, troubleshooting pending. | Mechanical Issue
2020-04-25 | 30036.0233
Cane Run 7 | Maintenance Outage | 16656 | IP Startup Bypass System Valve Maintenance and Instrumentation Problems | F540Block maintenance outage for valve maintenace and instrumentation problems | N/A
Ghent 3 | Maintenance Outage | 11484 | Air Heater Inspection and Wash | F530Outage #4Maintenance Outage. | N/A
Mill Creek 4 | Forced Derate | 803.395 | High Silica - Startup | F170High Silica - Startup | Mechanical Issue
Trimble County 2 | Maintenance Derate | 732.6283 | Routine Boiler Deslagging | FS00The unit was placed on a Maintenance Derate for routine boiler deslagging. | N/A
Zorn 1 CT | Forced Outage | 360 | Stator; General | F820Generator lockout, troubleshooting pending. | Mechanical Issue
2020-03-05 | 29400
Cane Run 7 | Maintenance Derate | 8196 | 2020 Spring Outage - Hot End Inspection B - CT2 off early | F5302020 planned spring outage - CT2 off early | N/A
Ghent 4 | Maintenance Outage | 11472 | Superheater - Washing Backpass | F590Outage #3Maintenance Outage. Washing the backpass. | N/A
Mill Creek 3 | Maintenance Outage | 9420 | Turbine Coupling Alignment | F040Turbine Coupling Alignment | N/A
Paddy's Run 11 CT | Forced Outage | 312 | Other DC power problems | F870Multiple Battery low voltage, unable to restore. Repeat equalizing charges successful. Two consecutive Diesel test starts done satisfactorily. | Mechanical Issue
2020-04-03 | 28915.7499
Brown 6 CT | Forced Outage | 3553.4333 | Turning gear and motor B | F690Unit would not go on rotor barring. | Mechanical Issue
Cane Run 7 | Maintenance Derate | 5594.602 | 2020 Planned Spring Outage - Hot End Inspection B - CT1 Extension | F5302020 planned spring outage - CT1 extension | N/A
Cane Run 7 | Forced Outage | 5482.6 | CT2 Trip on Blade Path Spread Due to Clogged Fuel Strainer | F120CT2 trip on blade path spread due to clogged fuel strainer. Cleaned strainer and restarted | Mechanical Issue
Ghent 1 | Forced Outage | 11448 | Waterwall BTF | F540Outage #6GH1 was forced off-line due to a water wall tube leak on "D" corner 6th elevation. | Mechanical Issue
Ghent 3 | Forced Outage | 1698.675 | Substation Circuit Breaker Failure | F700Outage #3Electrical component went to ground. | Mechanical Issue
Ghent 3 | Forced Derate | 285.1063 | High Silica | FA00Load Reduction #4Load restriction after start-up due to elevated silica level and reduced drum pressure. | Mechanical Issue
Mill Creek 2 | Maintenance Outage | 493.3333 | Air Heater Wash | F320Maintenance Outage - Air Heater Wash | N/A
Zorn 1 CT | Forced Outage | 360 | Stator; General | F820Generator lockout, troubleshooting pending. | Mechanical Issue
2020-04-27 | 28500
Cane Run 7 | Maintenance Outage | 16656 | IP Startup Bypass System Valve Maintenance and Instrumentation Problems | F540Block maintenance outage for valve maintenace and instrumentation problems | N/A
Ghent 3 | Maintenance Outage | 11484 | Air Heater Inspection and Wash - Extension | F590Outage #5Maintenance Extension. Air heater wash. | N/A
Zorn 1 CT | Forced Outage | 360 | Stator; General | F820Generator lockout, troubleshooting pending. | Mechanical Issue
2020-04-28 | 28500
Cane Run 7 | Maintenance Outage | 16656 | IP Startup Bypass System Valve Maintenance and Instrumentation Problems | F540Block maintenance outage for valve maintenace and instrumentation problems | N/A
Ghent 3 | Maintenance Outage | 11484 | Air Heater Inspection and Wash - Extension | F590Outage #5Maintenance Extension. Air heater wash. | N/A
Zorn 1 CT | Forced Outage | 360 | Stator; General | F820Generator lockout, troubleshooting pending. | Mechanical Issue
2020-04-02 | 28055.8414
Cane Run 7 | Maintenance Derate | 8339.7793 | 2020 Planned Spring Outage - Hot End Inspection B - CT1 Extension | F5302020 planned spring outage - CT1 extension | N/A
Ghent 1 | Forced Outage | 7751.25 | Waterwall BTF | F540Outage #6GH1 was forced off-line due to a water wall tube leak on "D" corner 6th elevation. | Mechanical Issue
Ghent 3 | Forced Outage | 11484 | Substation Circuit Breaker Failure | F700Outage #3Electrical component went to ground. | Mechanical Issue
Mill Creek 3 | Maintenance Derate | 120.8121 | 3D Mill Maintenance | F5903D Mill Maintenance | N/A
Zorn 1 CT | Forced Outage | 360 | Stator; General | F820Generator lockout, troubleshooting pending. | Mechanical Issue
2020-01-14 | 27935.2245
Brown 8 CT | Forced Derate | 214.3256 | Blades | F600Derate due to R3 blades. | Mechanical Issue
Brown 9 CT | Forced Derate | 452.7194 | Blades | F600Derate due to R3 blades. | Mechanical Issue
Ghent 2 | Maintenance Outage | 7905.6 | Other exciter problems | F590Outage #2Maintenance outage. | N/A
Ghent 3 | Maintenance Outage | 11424 | Air Heater Wash | F590Outage #1 | N/A
Mill Creek 1 | Maintenance Derate | 145.4545 | 1A Mill Maintenance - Inspection | F5901A Mill Maintenance - Inspection | N/A
Mill Creek 3 | Forced Derate | 1078.8583 | High Turbine Vibration - #3 Bearing - Variable | F850High Turbine Vibration - #3 Bearing - Variable | Mechanical Issue
Mill Creek 3 | Maintenance Outage | 6330.2667 | Maintenance Outage - Turbine Vibration | F850Maintenance Outage - Turbine Vibration | N/A
Zorn 1 CT | Forced Outage | 384 | 480-volt protection devices | F030Burnt OL Assembly on 480 VAC breaker for Lube Oil tank heater caused loss of oil temperature permissive. | Mechanical Issue
2020-04-29 | 27725.0333
Cane Run 7 | Maintenance Outage | 15881.0333 | IP Startup Bypass System Valve Maintenance and Instrumentation Problems | F540Block maintenance outage for valve maintenace and instrumentation problems | N/A
Ghent 3 | Maintenance Outage | 11484 | Air Heater Inspection and Wash - Extension | F590Outage #5Maintenance Extension. Air heater wash. | N/A
Zorn 1 CT | Forced Outage | 360 | Stator; General | F820Generator lockout, troubleshooting pending. | Mechanical Issue

## 2020 - Forced MWh Lost Detail
Unit | Event Type | Daily Net Forced MWh Lost | Cause | Description | Forced Category
2020-04-03 | 22827.8146
Brown 6 CT | Forced Outage | 3553.4333 | Turning gear and motor B | F690Unit would not go on rotor barring. | Mechanical Issue
Cane Run 7 | Forced Outage | 5482.6 | CT2 Trip on Blade Path Spread Due to Clogged Fuel Strainer | F120CT2 trip on blade path spread due to clogged fuel strainer. Cleaned strainer and restarted | Mechanical Issue
Ghent 1 | Forced Outage | 11448 | Waterwall BTF | F540Outage #6GH1 was forced off-line due to a water wall tube leak on "D" corner 6th elevation. | Mechanical Issue
Ghent 3 | Forced Outage | 1698.675 | Substation Circuit Breaker Failure | F700Outage #3Electrical component went to ground. | Mechanical Issue
Ghent 3 | Forced Derate | 285.1063 | High Silica | FA00Load Reduction #4Load restriction after start-up due to elevated silica level and reduced drum pressure. | Mechanical Issue
Zorn 1 CT | Forced Outage | 360 | Stator; General | F820Generator lockout, troubleshooting pending. | Mechanical Issue
2020-12-08 | 22638.713
Brown 3 | Forced Outage | 9984 | First Reheater BTF | F540Reheat tube leak | Mechanical Issue
Brown 8 CT | Forced Derate | 214.3256 | Blades | F600Derate due to R3 blades. | Mechanical Issue
Brown 9 CT | Forced Derate | 452.7194 | Blades | F600Derate due to R3 blades. | Mechanical Issue
Ghent 1 | Forced Derate | 11.6679 | Air Heater Fouling | F320Load Reduction #68Air heater duct pressure limit. Air heater fouling. | Mechanical Issue
Mill Creek 4 | Forced Outage | 3742.2 | MSV Seat Drain Steam Leak | F830MSV Seat Drain Steam Leak | Mechanical Issue
Mill Creek 4 | Forced Outage | 7921.8 | MSV Seat Drain Steam Leak | F830MSV Seat Drain Steam Leak | Mechanical Issue
Paddy's Run 11 CT | Forced Outage | 312 | Rotor; General | F510Unit will not rotate | Mechanical Issue
2020-12-10 | 21878.2553
Brown 3 | Forced Outage | 2440.5333 | First Reheater BTF | F540Reheat tube leak | Mechanical Issue
Brown 3 | Forced Outage | 6746.1333 | Mud Drum Door Gasket Leak | F540mud drum door gasket leak | Mechanical Issue
Brown 8 CT | Forced Derate | 214.3256 | Blades | F600Derate due to R3 blades. | Mechanical Issue
Brown 9 CT | Forced Derate | 452.7194 | Blades | F600Derate due to R3 blades. | Mechanical Issue
Mill Creek 3 | Forced Derate | 48.5437 | 3A 4KV Breaker Overload | F5203A 4KV Breaker Overload | Mechanical Issue
Mill Creek 4 | Forced Outage | 11664 | MSV Screen Differential | F830MSV Screen Differential | Mechanical Issue
Paddy's Run 11 CT | Forced Outage | 312 | Rotor; General | F510Unit will not rotate | Mechanical Issue
2020-04-02 | 19595.25
Ghent 1 | Forced Outage | 7751.25 | Waterwall BTF | F540Outage #6GH1 was forced off-line due to a water wall tube leak on "D" corner 6th elevation. | Mechanical Issue
Ghent 3 | Forced Outage | 11484 | Substation Circuit Breaker Failure | F700Outage #3Electrical component went to ground. | Mechanical Issue
Zorn 1 CT | Forced Outage | 360 | Stator; General | F820Generator lockout, troubleshooting pending. | Mechanical Issue
2020-12-09 | 19079.245
Brown 3 | Forced Outage | 9984 | First Reheater BTF | F540Reheat tube leak | Mechanical Issue
Brown 8 CT | Forced Derate | 214.3256 | Blades | F600Derate due to R3 blades. | Mechanical Issue
Brown 9 CT | Forced Derate | 452.7194 | Blades | F600Derate due to R3 blades. | Mechanical Issue
Mill Creek 4 | Forced Outage | 2187 | MSV Seat Drain Steam Leak | F830MSV Seat Drain Steam Leak | Mechanical Issue
Mill Creek 4 | Forced Outage | 5929.2 | MSV Screen Differential | F830MSV Screen Differential | Mechanical Issue
Paddy's Run 11 CT | Forced Outage | 312 | Rotor; General | F510Unit will not rotate | Mechanical Issue
2020-12-15 | 18886.6739
Brown 3 | Forced Outage | 9984 | Mud Drum Access Door Repair | F540mud drum access door repair | Mechanical Issue
Brown 8 CT | Forced Derate | 214.3256 | Blades | F600Derate due to R3 blades. | Mechanical Issue
Brown 9 CT | Forced Derate | 452.7194 | Blades | F600Derate due to R3 blades. | Mechanical Issue
Ghent 1 | Forced Derate | 229.8279 | Air Heater Differential | F400Load Reduction #70Air Heater Differential. | Mechanical Issue
Ghent 2 | Forced Outage | 7435.8 | First Reheater BTF | F830Outage #10Forced offline due to a tube leak in the RH section of the boiler | Mechanical Issue
Mill Creek 3 | Forced Derate | 20.7867 | 3A Mill Maintenance | F5903A Mill Maintenance | Mechanical Issue
Mill Creek 4 | Forced Derate | 237.2143 | SH Temp High | F060SH Temperature High | Mechanical Issue
Paddy's Run 11 CT | Forced Outage | 312 | Rotor; General | F510Unit will not rotate | Mechanical Issue
2020-11-14 | 17322.2192
Cane Run 7 | Forced Outage | 16656 | HRSG 1 Main Steam Header Isolation Valve Bonnet Leak | F540HRSG 1 main steam header isolation valve bonnet leak. Rebuilt valve with new pressure seal | Mechanical Issue
Ghent 2 | Forced Derate | 168.2308 | 2-3 Pulverizer Mill Fire | FR00Load Reduction #282-3 Mill got hot and maintenance needed to vacuum out the mill and do an inspection. | Mechanical Issue
Ghent 2 | Forced Derate | 185.9885 | 2-3 Pulverizer Mill Fire | FR00Load Reduction #292-3 Mill got hot and maintenance needed to vacuum out the mill and do an inspection. | Mechanical Issue
Paddy's Run 11 CT | Forced Outage | 312 | Rotor; General | F510Unit will not rotate | Mechanical Issue
2020-09-03 | 15717.9444
Brown 3 | Forced Derate | 1738.5495 | 3-3 Pulverizer Mill Broken Vertical Shaft | F0603-3 mill has a broken vertical shaft | Mechanical Issue
Brown 8 CT | Forced Derate | 71.395 | Inlet air chillers B | F600Derate due to R3 Turbine blades and inlet air cooling. | Mechanical Issue
Mill Creek 1 | Forced Derate | 120 | 1B Feeder Inspection | F6201B Feeder Inspection | Mechanical Issue
Trimble County 2 | Forced Outage | 13428 | Waterwall BTF | F540The unit was placed on a Forced Outage due to the discovery of a waterwall leak on the left wall. | Mechanical Issue
Zorn 1 CT | Forced Outage | 360 | Exciter commutator and brushes | F820Generator lockout, troubleshooting ongoing. | Mechanical Issue
2020-09-04 | 15597.9444
Brown 3 | Forced Derate | 1738.5495 | 3-3 Pulverizer Mill Broken Vertical Shaft | F0603-3 mill has a broken vertical shaft | Mechanical Issue
Brown 8 CT | Forced Derate | 71.395 | Inlet air chillers B | F600Derate due to R3 Turbine blades and inlet air cooling. | Mechanical Issue
Trimble County 2 | Forced Outage | 13428 | Waterwall BTF | F540The unit was placed on a Forced Outage due to the discovery of a waterwall leak on the left wall. | Mechanical Issue
Zorn 1 CT | Forced Outage | 360 | Exciter commutator and brushes | F820Generator lockout, troubleshooting ongoing. | Mechanical Issue
2020-11-06 | 15462.675
Mill Creek 2 | Forced Outage | 2118.6 | EHC Leak - CV#1 | F830EHC Leak - CV#1 | Mechanical Issue
Trimble County 2 | Forced Outage | 2126.1 | EHC Pump Failure - Plugged Controller | F340The unit experienced a Forced Outage when the EHC pressure fell due to the one EHC pump in service failed due to a plugged controller. | Mechanical Issue
Trimble County 2 | Forced Outage | 11217.975 | High HP Turbine Exhaust Temps | F780The unit experienced a forced outage when the HP Turbine Exhaust temperature exceeded its normal limits. | Mechanical Issue

## 2021 - Total MWh Lost Detail
Unit | Event Type | Daily Net MWh Lost | Cause | Description | Forced Category
2021-05-13 | 31764.5381
Brown 3 | Maintenance Outage | 9936 | Boiler and Expansion Joint Inspection | F590General outage maint inspections: boiler and expansion joints | N/A
Ghent 1 | Forced Derate | 4733.3077 | 1-2 FD Fan Motor Rewind | F490Load Reduction #151-2 FD Fan Motor was out for a rewind. | Mechanical Issue
Ghent 2 | Maintenance Outage | 11652 | Condenser Tube and Waterbox Cleaning | F590General maintenance | N/A
Mill Creek 1 | Forced Derate | 381.8182 | 1D Feeder Plugged | F1801D Feeder Plugged | Mechanical Issue
Mill Creek 1 | Maintenance Derate | 122.7273 | 1A Mill Maintenance | F5901A Mill Maintenance | N/A
Mill Creek 4 | Maintenance Derate | 91.2016 | 4C Mill Maintenance | F5904C Mill Maintenance | N/A
Trimble County 10 CT | Forced Outage | 791.4833 | Other exciter problems | F520The unit was made unavailable after an exciter alarm was triggered. Investigation showed the problem was due to a malfunctioning piece of controls hardware. | Mechanical Issue
Trimble County 5 CT | Maintenance Outage | 4056 | Major overhaul (use for non-specific overhaul only; see page B-1) A | F790The unit was placed on a Maintenance Outage Extension for testing following the TC5 2020-2021 Planned Outage. | N/A
2021-12-14 | 29768.6424
Brown 3 | Maintenance Outage | 9984 | Clean Absorber Vessel - Slagging Sulfites | F590Remove protective screens from turbine reheat line. Clean absorber vessel due to slagging of sulfites. | N/A
Brown 5 CT | Maintenance Outage | 262 | DC protection devices | F590Gen compliance on site to perform PRC-005 checks | N/A
Brown 6 CT | Maintenance Outage | 433.2 | DC protection devices | F590Gen compliance on site to perfrom PRC-005 checks. | N/A
Brown 7 CT | Maintenance Outage | 4104 | Combustion Inspection (CI) | F590Continued commissioning activites by GE | N/A
Mill Creek 1 | Maintenance Derate | 181.5909 | 1D Mill Maintenance | F5901D Mill Maintenance | N/A
Mill Creek 2 | Maintenance Derate | 81 | 2C Mill Maintenance | F5902C Mill Maintenance | N/A
Mill Creek 4 | Forced Derate | 6109.7143 | 4B FD Fan Out of Service | F7804B FD Fan Out of Service | Mechanical Issue
Trimble County 2 | Forced Derate | 21.1372 | 6B HP Heater Head Leaks | F540Derate due to low deaerator level caused by 6B heater head leak and heater being bypassed which has additional flow going through the condensate system. | Mechanical Issue
Trimble County 5 CT | Maintenance Outage | 4296 | Miscellaneous CEMS problems | F590The unit was placed on a maintenance outage to replace the CEM shelter as well as other maintenance issues. | N/A
Trimble County 6 CT | Maintenance Outage | 4296 | Miscellaneous CEMS problems | F590The unit was placed on a maintenance outage to replace the CEM shelter as well as other maintenance issu | N/A
2021-05-12 | 28540.6311
Brown 11 CT | Forced Outage | 161.2667 | Ignition system A | F460Unit failed to light on oil. | Mechanical Issue
Brown 3 | Maintenance Outage | 9936 | Boiler and Expansion Joint Inspection | F590General outage maint inspections: boiler and expansion joints | N/A
Cane Run 7 | Maintenance Outage | 10514.1 | Block - HRH Isolation Valve Repair -Extension | F540Block outage for HRH isolation valve repair | N/A
Ghent 1 | Forced Derate | 614.2904 | 1-2 FD Fan Motor Rewind | F4901-2 FD fan motor is out for a rewind. | Mechanical Issue
Ghent 1 | Forced Derate | 4089.0519 | 1-2 FD Fan Motor Rewind | F490Load Reduction #151-2 FD Fan Motor was out for a rewind. | Mechanical Issue
Ghent 2 | Maintenance Outage | 509.775 | Condenser Tube and Waterbox Cleaning | F590General maintenance | N/A
Mill Creek 1 | Forced Derate | 120 | 1D Feeder Plugged | F1801D Feeder Plugged | Mechanical Issue
Mill Creek 4 | Maintenance Derate | 106.4814 | 4B Mill Maintenance | F5904B Mill Maintenance | N/A
Mill Creek 4 | Maintenance Derate | 95.499 | 4C Mill Maintenance | F5904C Mill Maintenance | N/A
Trimble County 5 CT | Maintenance Outage | 1267.5 | Major overhaul (use for non-specific overhaul only; see page B-1) A | F790The unit was placed on a Maintenance Outage Extension for testing following the TC5 2020-2021 Planned Outage. | N/A
Trimble County 5 CT | Maintenance Outage | 1126.6667 | Major overhaul (use for non-specific overhaul only; see page B-1) A | F790The unit was placed on a Maintenance Outage Extension for testing following the TC5 2020-2021 Planned Outage. | N/A
2021-04-24 | 26681.7467
Brown 3 | Maintenance Outage | 9936 | Boiler Ash Hopper Ring Header Plugged | F590Ring header on boiler ash hopper plugged. | N/A
Mill Creek 2 | Forced Outage | 7128 | High Turbine Vibration | F820High Turbine Vibration | Mechanical Issue
Trimble County 2 | Forced Derate | 210.6042 | Superheater BTF | F540The unit load was derated due to a tube leak in an outlet stub tube on the rear platen superheat assemblies. | Mechanical Issue
Trimble County 2 | Forced Derate | 595.3925 | E Pulverizer Mill Fire | FR00Unit load was further derated due to a fire in the E Mill, taking it out of service. | Mechanical Issue
Trimble County 2 | Forced Outage | 4755.75 | Superheater BTF | F540The unit load was taken offline for repairs to a leak in an outlet stub tube on the rear platen superheat assemblies. | Mechanical Issue
Trimble County 5 CT | Maintenance Outage | 4056 | Major overhaul (use for non-specific overhaul only; see page B-1) A | F790The unit was placed on a Maintenance Outage for testing following the TC5 2020-2021 Planned Outage. | N/A
2021-04-25 | 26124.5638
Brown 3 | Maintenance Outage | 1276.5 | Boiler Ash Hopper Ring Header Plugged | F590Ring header on boiler ash hopper plugged. | N/A
Brown 3 | Forced Derate | 575.5377 | 3-4 Feeder - Broken Roller & Belt Replacement | F0603-4 Feeder had broken roller and belt was replaced. | Mechanical Issue
Mill Creek 2 | Forced Outage | 2866.05 | High Turbine Vibration | F820High Turbine Vibration | Mechanical Issue
Mill Creek 2 | Forced Derate | 46.8 | 2C Mill Unavailable - Puff | F4402C Mill Unavailable | Mechanical Issue
Mill Creek 2 | Forced Outage | 1984.95 | High Turbine Vibration | F820High Turbine Vibration | Mechanical Issue
Mill Creek 2 | Forced Derate | 332.4 | 2C Mill Unavailable - Puff | F4402C Mill Unavailable | Mechanical Issue
Mill Creek 2 | Forced Derate | 388.8 | 2C and 2D Mills Unavailable - Puff | F4402C and 2D Mills Unavailable | Mechanical Issue
Mill Creek 3 | Maintenance Derate | 554.2611 | Cooling Tower Breaker Maintenance | F700Cooling Tower Breaker Maintenance | N/A
Mill Creek 3 | Forced Derate | 615.265 | 3D Feeder Belt | F0603D Feeder Belt | Mechanical Issue
Trimble County 2 | Forced Outage | 13428 | Superheater BTF | F540The unit load was taken offline for repairs to a leak in an outlet stub tube on the rear platen superheat assemblies. | Mechanical Issue
Trimble County 5 CT | Maintenance Outage | 4056 | Major overhaul (use for non-specific overhaul only; see page B-1) A | F790The unit was placed on a Maintenance Outage for testing following the TC5 2020-2021 Planned Outage. | N/A
2021-12-15 | 25492.384
Brown 3 | Maintenance Outage | 9984 | Clean Absorber Vessel - Slagging Sulfites | F590Remove protective screens from turbine reheat line. Clean absorber vessel due to slagging of sulfites. | N/A
Brown 7 CT | Maintenance Outage | 1744.2 | Combustion Inspection (CI) | F590Continued commissioning activites by GE | N/A
Mill Creek 1 | Maintenance Derate | 163.6364 | 1D Feeder Maintenance | F5901D Feeder Maintenance | N/A
Mill Creek 2 | Maintenance Derate | 372.6 | 2C Mill Maintenance | F5902C Mill Maintenance | N/A
Mill Creek 4 | Forced Derate | 6109.7143 | 4B FD Fan Out of Service | F7804B FD Fan Out of Service | Mechanical Issue
Trimble County 5 CT | Maintenance Outage | 3559.1167 | Miscellaneous CEMS problems | F590The unit was placed on a maintenance outage to replace the CEM shelter as well as other maintenance issues. | N/A
Trimble County 6 CT | Maintenance Outage | 3559.1167 | Miscellaneous CEMS problems | F590The unit was placed on a maintenance outage to replace the CEM shelter as well as other maintenance issu | N/A
2021-05-11 | 24749.7477
Brown 3 | Maintenance Outage | 724.5 | Boiler and Expansion Joint Inspection | F590General outage maint inspections: boiler and expansion joints | N/A
Brown 6 CT | Maintenance Outage | 408.2 | Ignition system A | F590Replaced faulty ignition switch. | N/A
Brown 7 CT | Forced Outage | 429.1333 | Ignition system A | F060Replaced bad ignition torch. | Mechanical Issue
Cane Run 7 | Maintenance Outage | 11.5667 | Block - HRH Isolation Valve Repair | F540Block outage for HRH isolation valve repair | N/A
Cane Run 7 | Maintenance Outage | 16644.4333 | Block - HRH Isolation Valve Repair -Extension | F540Block outage for HRH isolation valve repair | N/A
Ghent 1 | Forced Derate | 524.7 | 1-2 FD Fan Motor Rewind | F4901-2 FD fan motor is out for a rewind. Unit was removed from service at 10:16 to repair turbine trip solenoid and repair turbine oil leak. | Mechanical Issue
Ghent 1 | Maintenance Outage | 747.3 | Turbine Trip Solenoid and Turbine Oil Leak Repairs | F540leaks; Unit was removed from service at 10:16 to repair turbine trip solenoid and repair turbine oil leak. | N/A
Ghent 1 | Forced Derate | 2354.4231 | 1-2 FD Fan Motor Rewind | F4901-2 FD fan motor is out for a rewind. | Mechanical Issue
Ghent 1 | Forced Derate | 94.024 | 1-2 FD Fan Motor Rewind | F4901-2 FD fan motor is out for a rewind. | Mechanical Issue
Ghent 4 | Forced Derate | 56.9048 | U4 Gas Path Ducts - Airflow/Pressure Issues | F660U4 gas path ducts, airflow/pressure issues. | Mechanical Issue
Haefling 1 CT | Maintenance Outage | 73.3867 | Other switchyard equipment - external | F590Substation performing work at Haefling | N/A
Haefling 2 CT | Maintenance Outage | 73.3867 | Other switchyard equipment - external | F590Substation work at Haefling. | N/A
Mill Creek 4 | Maintenance Derate | 102.6615 | 4A Mill Maintenance | F5904A Mill Maintenance | N/A
Mill Creek 4 | Maintenance Derate | 65.8943 | 4B Mill Maintenance | F5904B Mill Maintenance | N/A
Trimble County 5 CT | Maintenance Outage | 811.2 | Major overhaul (use for non-specific overhaul only; see page B-1) A | F790The unit was placed on a Maintenance Outage Extension for testing following the TC5 2020-2021 Planned Outage. | N/A
Trimble County 5 CT | Maintenance Outage | 1628.0333 | Major overhaul (use for non-specific overhaul only; see page B-1) A | F790The unit was placed on a Maintenance Outage Extension for testing following the TC5 2020-2021 Planned Outage. | N/A
2021-05-19 | 23876.9077
Brown 3 | Forced Outage | 3615.6 | Condenser CW Waterbox Door Gasket Leak | F540condenser cw waterbox door gasket leaking badly | Mechanical Issue
Ghent 1 | Forced Derate | 4733.3077 | 1-2 FD Fan Motor Rewind | F490Load Reduction #151-2 FD Fan Motor was out for a rewind. | Mechanical Issue
Ghent 4 | Maintenance Outage | 11472 | 4-1 Air Heater Restricted Air Flow - Extension | F590Outage #3Maintenacne Outage Extension, 4-1 Air Heater restricted air flow. | N/A
Trimble County 5 CT | Maintenance Outage | 4056 | Major overhaul (use for non-specific overhaul only; see page B-1) A | F790The unit was placed on a Maintenance Outage Extension for testing following the TC5 2020-2021 Planned Outage. | N/A
2021-12-17 | 23624.2461
Brown 3 | Maintenance Outage | 9984 | Clean Absorber Vessel - Slagging Sulfites | F590Remove protective screens from turbine reheat line. Clean absorber vessel due to slagging of sulfites. | N/A
Brown 6 CT | Maintenance Outage | 2881.35 | Distributive Control System (DCS) - process computer | F590DCS controllers needed reloaded from HMI upgrade. | N/A
Brown 7 CT | Maintenance Outage | 4104 | Combustion Inspection (CI) | F590Demobilization of GE commissioning team | N/A
Mill Creek 1 | Maintenance Derate | 354.5455 | 1A Feeder Maintenance | F5901A Feeder Maintenance | N/A
Mill Creek 1 | Forced Derate | 105.1364 | Elevated Backpressure | F660Elevated Backpressure | Mechanical Issue
Mill Creek 2 | Maintenance Derate | 85.5 | Feeder Maintenance | F590Feeder Maintenance | N/A
Mill Creek 4 | Forced Derate | 6109.7143 | 4B FD Fan Out of Service | F7804B FD Fan Out of Service | Mechanical Issue
2021-12-13 | 23461.3472
Brown 3 | Maintenance Outage | 9984 | Clean Absorber Vessel - Slagging Sulfites | F590Remove protective screens from turbine reheat line. Clean absorber vessel due to slagging of sulfites. | N/A
Brown 7 CT | Forced Outage | 219.45 | DCS - logic problems | FP00Online tuning revision by GE commissioning engineer caused a unit trip. | Mechanical Issue
Brown 7 CT | Maintenance Outage | 855 | Combustion Inspection (CI) | F590Continued commissioning activites by GE | N/A
Mill Creek 4 | Forced Derate | 6109.7143 | 4B FD Fan Out of Service | F7804B FD Fan Out of Service | Mechanical Issue
Trimble County 2 | Forced Derate | 28.1829 | 6B HP Heater Head Leaks | F540Derate due to low deaerator level caused by 6B heater head leak and heater being bypassed which has additional flow going through the condensate system. | Mechanical Issue
Trimble County 5 CT | Maintenance Outage | 3132.5 | Miscellaneous CEMS problems | F590The unit was placed on a maintenance outage to replace the CEM shelter as well as other maintenance issues. | N/A
Trimble County 6 CT | Maintenance Outage | 3132.5 | Miscellaneous CEMS problems | F590The unit was placed on a maintenance outage to replace the CEM shelter as well as other maintenance issu | N/A

## 2021 - Forced MWh Lost Detail
Unit | Event Type | Daily Net Forced MWh Lost | Cause | Description | Forced Category
2021-04-25 | 20237.8027
Brown 3 | Forced Derate | 575.5377 | 3-4 Feeder - Broken Roller & Belt Replacement | F0603-4 Feeder had broken roller and belt was replaced. | Mechanical Issue
Mill Creek 2 | Forced Outage | 2866.05 | High Turbine Vibration | F820High Turbine Vibration | Mechanical Issue
Mill Creek 2 | Forced Derate | 46.8 | 2C Mill Unavailable - Puff | F4402C Mill Unavailable | Mechanical Issue
Mill Creek 2 | Forced Outage | 1984.95 | High Turbine Vibration | F820High Turbine Vibration | Mechanical Issue
Mill Creek 2 | Forced Derate | 332.4 | 2C Mill Unavailable - Puff | F4402C Mill Unavailable | Mechanical Issue
Mill Creek 2 | Forced Derate | 388.8 | 2C and 2D Mills Unavailable - Puff | F4402C and 2D Mills Unavailable | Mechanical Issue
Mill Creek 3 | Forced Derate | 615.265 | 3D Feeder Belt | F0603D Feeder Belt | Mechanical Issue
Trimble County 2 | Forced Outage | 13428 | Superheater BTF | F540The unit load was taken offline for repairs to a leak in an outlet stub tube on the rear platen superheat assemblies. | Mechanical Issue
2021-07-15 | 19368.5889
Brown 10 CT | Forced Derate | 452.2623 | Inlet air chillers | F540inlet cooling unavailable | Mechanical Issue
Brown 10 CT | Forced Outage | 203.6833 | Hydraulic oil system piping/valves | F690Staging valve stuck casuing flame trip. | Mechanical Issue
Brown 11 CT | Forced Derate | 452.2623 | Inlet air chillers | F540inlet cooling unavailable. | Mechanical Issue
Brown 5 CT | Forced Derate | 500.1527 | Inlet air chillers | F540Inlet cooling not available. | Mechanical Issue
Brown 8 CT | Forced Derate | 452.2623 | Inlet air chillers | F540Inlet cooling not available. | Mechanical Issue
Brown 9 CT | Forced Derate | 452.2623 | Inlet air chillers | F540inlet cooling unavailable | Mechanical Issue
Haefling 1 CT | Forced Outage | 113 | Air cooling system | F820Shear pin on fan failed. | Mechanical Issue
Mill Creek 1 | Forced Outage | 3230 | Station Service Water Out of Service | F830Station Service Water Out of Service | Diver Incident
Mill Creek 2 | Forced Derate | 239.85 | LSSWPs Out of Service | F190LSSWPs Out of Service | Diver Incident
Mill Creek 2 | Forced Outage | 3197.7 | Station Service Water Out of Service | F830Station Service Water Out of Service | Diver Incident
Mill Creek 3 | Forced Derate | 298.9637 | LSSWPs Out of Service | F190LSSWPs Out of Service | Diver Incident
Mill Creek 3 | Forced Outage | 4196.7333 | Station Service Water Out of Service | F830Station Service Water Out of Service | Diver Incident
Mill Creek 4 | Forced Derate | 298.84 | LSSWPs Out of Service | F190LSSWPs Out of Service | Diver Incident
Mill Creek 4 | Forced Outage | 5103.9 | Station Service Water Out of Service | F830Station Service Water Out of Service | Diver Incident
Paddy's Run 12 CT | Forced Outage | 176.7167 | Generator casing | F500Generator cooling issues. | Mechanical Issue
2021-11-02 | 18674.4583
Brown 6 CT | Forced Outage | 54.95 | Inlet air vanes/nozzles | F400Inlet vanes were not at light off position. | Mechanical Issue
Brown 8 CT | Forced Outage | 1593 | Ignition system | F060Spark plug faulty | Mechanical Issue
Ghent 3 | Forced Outage | 8716.675 | Reheater BTF | F830Outage #4Boiler Trip - Tube Leak. Unit was removed from service due to tube leak in the reheat section. | Mechanical Issue
Trimble County 1 | Forced Outage | 7308.725 | GSU Transformer Oil Leak | F540The unit was taken offline due to a GSU Transformer oil leak. | Mechanical Issue
Trimble County 1 | Forced Outage | 801.125 | Switchyard Circuit Breakers - 4511 Tie Breaker Relay (not OMC) | F630A relay issue on the 4511 tie breaker caused the breaker to open, causing a unit trip. | Mechanical Issue
Trimble County 10 CT | Forced Outage | 199.9833 | Other controls and instrumentation problems | F840TC currently investigating. | Mechanical Issue
2021-04-26 | 16851.6
Mill Creek 2 | Forced Derate | 729 | 2C and 2D Mills Unavailable - Puff | F4402C and 2D Mills Unavailable | Mechanical Issue
Mill Creek 2 | Forced Derate | 391.275 | 2A, 2C, and 2D Mills Unavailable - Puff | F4402A, 2C, and 2D Mills Unavailable | Mechanical Issue
Mill Creek 2 | Forced Derate | 2303.325 | 2C and 2D Mills Unavailable - Variable - Puff | F4402C and 2D Mills Unavailable - Variable | Mechanical Issue
Trimble County 2 | Forced Outage | 13428 | Superheater BTF | F540The unit load was taken offline for repairs to a leak in an outlet stub tube on the rear platen superheat assemblies. | Mechanical Issue
2021-04-27 | 16560
Mill Creek 2 | Forced Derate | 3132 | 2C and 2D Mills Unavailable - Variable - Puff | F4402C and 2D Mills Unavailable - Variable | Mechanical Issue
Trimble County 2 | Forced Outage | 13428 | Superheater BTF | F540The unit load was taken offline for repairs to a leak in an outlet stub tube on the rear platen superheat assemblies. | Mechanical Issue
2021-01-29 | 16021.2117
Brown 8 CT | Forced Derate | 214.3256 | Blades | F600Derate due to R3 blades. | Mechanical Issue
Brown 9 CT | Forced Derate | 452.7194 | Blades | F600Derate due to R3 blades. | Mechanical Issue
Paddy's Run 13 CT | Forced Outage | 1674.1667 | AC Protection devices | F840Trouble with Pilot Gas control valve | Mechanical Issue
Trimble County 2 | Forced Outage | 13680 | HRH Steam Leak | F540The unit was removed from service for repairs to a HRH steam leak. | Mechanical Issue
2021-10-14 | 15966.2455
Mill Creek 1 | Forced Derate | 1767.2727 | NOx Mitigation | FE00NOx Mitigation | Mechanical Issue
Mill Creek 1 | Forced Derate | 327.2727 | NOx Mitigation | FE00NOx Mitigation | Mechanical Issue
Mill Creek 2 | Forced Derate | 2000.7 | NOx Mitigation | FE00NOx Mitigation | Mechanical Issue
Mill Creek 2 | Forced Derate | 315 | NOx Mitigation | FE00NOx Mitigation | Mechanical Issue
Mill Creek 4 | Forced Outage | 11556 | FD Fan Bearing Vibration | F830FD Fan Bearing Vibration | Mechanical Issue
2021-01-26 | 15955.0617
Brown 8 CT | Forced Derate | 214.3256 | Blades | F600Derate due to R3 blades. | Mechanical Issue
Brown 9 CT | Forced Derate | 452.7194 | Blades | F600Derate due to R3 blades. | Mechanical Issue
Trimble County 2 | Forced Outage | 13680 | HRH Steam Leak | F540The unit was removed from service for repairs to a HRH steam leak. | Mechanical Issue
Trimble County 8 CT | Forced Outage | 1608.0167 | Other auxiliary system problems A | F340The unit was made unavailable when a purge credit nitrogen valve failed to operate properly. | Mechanical Issue
2021-01-28 | 14680.545
Brown 10 CT | Forced Outage | 333.5 | Switchyard circuit breakers - external | F590Hydraulic hose on substation breaker blown out. | Mechanical Issue
Brown 8 CT | Forced Derate | 214.3256 | Blades | F600Derate due to R3 blades. | Mechanical Issue
Brown 9 CT | Forced Derate | 452.7194 | Blades | F600Derate due to R3 blades. | Mechanical Issue
Trimble County 2 | Forced Outage | 13680 | HRH Steam Leak | F540The unit was removed from service for repairs to a HRH steam leak. | Mechanical Issue
2021-01-27 | 14347.045
Brown 8 CT | Forced Derate | 214.3256 | Blades | F600Derate due to R3 blades. | Mechanical Issue
Brown 9 CT | Forced Derate | 452.7194 | Blades | F600Derate due to R3 blades. | Mechanical Issue
Trimble County 2 | Forced Outage | 13680 | HRH Steam Leak | F540The unit was removed from service for repairs to a HRH steam leak. | Mechanical Issue

## 2022 - Total MWh Lost Detail
Unit | Event Type | Daily Net MWh Lost | Cause | Description | Forced Category
2022-12-24 | 31982.9481
Brown 10 CT | Forced Outage | 3312 | Exhaust Diffuser Issues | F060Exhaust diffuser sections have separated. Bolts need to be replaced and exhaust diffusers realigned. | Mechanical Issue
Brown 3 | Forced Derate | 1654.8672 | Ash disposal problem | FS00Baghouse issues | Mechanical Issue
Cane Run 7 | Forced Derate | 2190.3103 | Low Gas Pipeline Pressure | FX00Block derate due to low fuel gas pipeline pressure | Fuel Supply Disruption
Ghent 2 | Maintenance Derate | 92.4317 | Load Reduction #252-3 Pulverizer Mills | F590Load Reduction #252-3 Pulverizer Mill was hold carded out of service for getting hot. Mill wrights were called in for inspection of the mill. | N/A
Haefling 1 CT | Forced Outage | 209.3 | Power Station switchyard (non generating unit equipment) | F820Substation breaker will not remain closed. | Mechanical Issue
Haefling 2 CT | Forced Outage | 209.3 | Substation breaker will not remain closed. | F820Substation breaker will not remain closed. | Mechanical Issue
Trimble County 1 | Forced Outage | 8874 | Primary Submerged Chain Conveyor freezing | F340The unit was placed on a forced outage due to issues with the primary submerged chain conveyor. Outage duration was prolonged due to freezing issues around plant caused by unit offline. | Mechanical Issue
Trimble County 10 CT | Forced Derate | 2195.7333 | Lack of Fuel | Lack of Fuel | Fuel Supply Disruption
Trimble County 2 | Forced Derate | 539.2619 | Maintain Deaerator Tank Levels- Cold Weather | F780In order to slow demand to the water coil air heaters from the deaerator, the unit was placed on a derate to maintain deaerator tank level. | Cold Weather
Trimble County 2 | Forced Derate | 261.0505 | Leaking Closed cooling water valves | F540The unit was placed on derate in order to address a leaking closed cooling water valve used to maintain the level of the SSC. This was in addition to the deaerator level issues. | Mechanical Issue
Trimble County 2 | Forced Derate | 59.1598 | Maintain Deaerator tank level | F780In order to slow demand to the water coil air heaters from the deaerator, the unit was placed on a derate to maintain deaerator tank level. | Cold Weather
Trimble County 5 CT | Forced Outage | 4296 | Lack of Fuel | Lack of Fuel | Fuel Supply Disruption
Trimble County 6 CT | Forced Derate | 1933.2 | Lack of Fuel | Lack of Fuel | Fuel Supply Disruption
Trimble County 7 CT | Forced Derate | 2243.4667 | Lack of Fuel | Lack of Fuel | Fuel Supply Disruption
Trimble County 8 CT | Forced Derate | 2100.2667 | Lack of Fuel | Lack of Fuel | Fuel Supply Disruption
Trimble County 9 CT | Forced Derate | 1812.6 | Lack of Fuel | Lack of Fuel | Fuel Supply Disruption
2022-12-07 | 31701.9697
Brown 10 CT | Forced Outage | 3312 | Exhaust Diffuser Issues | F060Exhaust diffuser sections have separated. Bolts need to be replaced and exhaust diffusers realigned. | Mechanical Issue
Brown 7 CT | Maintenance Outage | 4104 | Boroscope inspection | F590Annual borescope inspection | N/A
Brown 8 CT | Maintenance Outage | 2069.3333 | Unit Inspection | F590Unit plane readings | N/A
Ghent 2 | Maintenance Outage | 11652 | Waterwall BTF | F540Outage #12Maintenance Outage, to repair water wall tube leak in the furnace. | N/A
Mill Creek 1 | Maintenance Derate | 358.6364 | 1A Mill Maintenance | F5901A Mill Maintenance | N/A
Mill Creek 2 | Maintenance Derate | 162 | Mill Maintenance | F5902C Mill Maintenance | N/A
Mill Creek 4 | Maintenance Outage | 10044 | Balance Shot | F850Balance Shot | N/A
2022-05-12 | 31497.1373
Cane Run 7 | Maintenance Derate | 8339.7793 | 2022 Spring Outage - Combustion Inspection (CI) - CT1 Extension | F5302022 planned spring outage (CT1 extension) | N/A
Ghent 2 | Forced Outage | 11652 | Condenser Tube Leak | F540Outage #5Condenser tube leaks. | Mechanical Issue
Ghent 4 | Forced Outage | 11472 | #3 Turbine Bearing Overheated During Rollup | F820Outage #3Ghent 4 Divsion panel #3 Tube14 tube leaks were repaired at 16:50 hours on 5-2-2022. The unit was unable to be placed in service due to overheating of the #3 turbine bearing during initial roll up after tube leak repair. | Mechanical Issue
Haefling 2 CT | Forced Outage | 33.358 | Air cooling system | F760Broken shear pin on cooling fan caused excessive oil temps | Mechanical Issue
2022-05-03 | 30704.6619
Brown 3 | Forced Outage | 9936 | 3-4 BCWP Replacement | F780Replace 3-4 BCWP, Unable to run on two Bcwp's. | Mechanical Issue
Cane Run 7 | Maintenance Derate | 8339.7793 | 2022 Spring Outage - Combustion Inspection (CI) - CT1 Extension | F5302022 planned spring outage (CT1 extension) | N/A
Ghent 4 | Forced Outage | 11472 | #3 Turbine Bearing Overheated During Rollup | F820Outage #3Ghent 4 Divsion panel #3 Tube14 tube leaks were repaired at 16:50 hours on 5-2-2022. The unit was unable to be placed in service due to overheating of the #3 turbine bearing during initial roll up after tube leak repair. | Mechanical Issue
Trimble County 1 | Maintenance Derate | 268.592 | Boiler Performance Testing | F790Unit placed on planned derate for boiler performance testing. | N/A
Trimble County 2 | Maintenance Derate | 688.2906 | SCR Tuning | F790Unit placed on planned derate for SCR tuning at minimum load. | N/A
2022-05-08 | 30242.9393
Cane Run 7 | Maintenance Outage | 3701.3333 | CT2/ST - BFP 201 Oil Change - Extension | F590CT2/ST shut down for BFP 201 oil change (extension) | N/A
Cane Run 7 | Maintenance Derate | 6486.495 | 2022 Spring Outage - Combustion Inspection (CI) - CT1 Extension | F5302022 planned spring outage (CT1 extension) | N/A
Ghent 2 | Maintenance Outage | 8496.25 | 2-2 Main Condenser Tube Leak | F540Outage # 42-2 Main Condenser Tube Leaks. | N/A
Ghent 4 | Forced Outage | 11472 | #3 Turbine Bearing Overheated During Rollup | F820Outage #3Ghent 4 Divsion panel #3 Tube14 tube leaks were repaired at 16:50 hours on 5-2-2022. The unit was unable to be placed in service due to overheating of the #3 turbine bearing during initial roll up after tube leak repair. | Mechanical Issue
Mill Creek 3 | Maintenance Derate | 86.8609 | 3C Mill Maintenance - Hot Air Damper Inspection | F5903C Mill Maintenance - Hot Air Damper Inspection | N/A
2022-05-07 | 28128
Cane Run 7 | Maintenance Outage | 8339.5667 | CT2/ST - BFP 201 Oil Change | F590CT2/ST shut down for BFP 201 oil change | N/A
Cane Run 7 | Maintenance Outage | 8316.4333 | CT2/ST - BFP 201 Oil Change - Extension | F590CT2/ST shut down for BFP 201 oil change (extension) | N/A
Ghent 4 | Forced Outage | 11472 | #3 Turbine Bearing Overheated During Rollup | F820Outage #3Ghent 4 Divsion panel #3 Tube14 tube leaks were repaired at 16:50 hours on 5-2-2022. The unit was unable to be placed in service due to overheating of the #3 turbine bearing during initial roll up after tube leak repair. | Mechanical Issue
2022-05-04 | 27413.718
Brown 3 | Forced Outage | 5789.1 | 3-4 BCWP Replacement | F780Replace 3-4 BCWP, Unable to run on two Bcwp's. | Mechanical Issue
Brown 3 | Maintenance Outage | 96.6 | SCR NOx Ammonia Injection Skid Controller Rebuild | F060Ammonia injection skid controller rebuild | N/A
Cane Run 7 | Maintenance Derate | 8339.7793 | 2022 Spring Outage - Combustion Inspection (CI) - CT1 Extension | F5302022 planned spring outage (CT1 extension) | N/A
Ghent 4 | Forced Outage | 11472 | #3 Turbine Bearing Overheated During Rollup | F820Outage #3Ghent 4 Divsion panel #3 Tube14 tube leaks were repaired at 16:50 hours on 5-2-2022. The unit was unable to be placed in service due to overheating of the #3 turbine bearing during initial roll up after tube leak repair. | Mechanical Issue
Trimble County 1 | Maintenance Derate | 110.2274 | Boiler Performance Testing | F790Unit placed on planned derate for boiler performance testing. | N/A
Trimble County 2 | Maintenance Derate | 1606.0113 | SCR Tuning | F790Unit placed on planned derate for SCR tuning at minimum load. | N/A
2022-12-23 | 27074.652
Brown 10 CT | Forced Outage | 3312 | Exhaust Diffuser Issues | F060Exhaust diffuser sections have separated. Bolts need to be replaced and exhaust diffusers realigned. | Mechanical Issue
Brown 11 CT | Forced Outage | 298.6667 | Fuel piping and valves Frozen | F480Frozen fuel valves due to valves heaters to the 11N2 units kept going out. | Cold Weather
Brown 11 CT | Forced Outage | 179.2 | Flame trip | F820Flame trip | Mechanical Issue
Brown 3 | Forced Derate | 61.6694 | Pulverizer Mills high Tonage | FS00Mills on high tonage. | Mechanical Issue
Brown 3 | Forced Derate | 309.0699 | Baghouse Pluggage from Boiler Slagging | FS00Baghouse plugging up due to boiler slagging. | Mechanical Issue
Brown 3 | Forced Derate | 712.5123 | Ash disposal problem | FS00Baghouse issues | Mechanical Issue
Brown 5 CT | Forced Outage | 2067 | Fuel piping and valves Frozen | F480Fuel valves froze after valve heaters to 11N2 units were blown out. | Cold Weather
Brown 5 CT | Forced Derate | 92.2901 | Pressure Switch Fail | F570Pressure switch on U5 lube oil pump failed. | Mechanical Issue
Brown 8 CT | Forced Outage | 268.8 | Fuel piping and valves Frozen | F480Fuel valves froze because valves heaters to the 11N2 units kept going out. | Cold Weather
Brown 8 CT | Forced Outage | 362.6667 | Lube oil pumps Malfunction | F570Malfunctioning lube oil pump | Mechanical Issue
Brown 8 CT | Forced Derate | 133.8047 | Other miscellaneous pollution control equipment problems | FE00Generation limited due to high input temperature alarm. | Mechanical Issue
Brown 9 CT | Forced Outage | 322 | Fuel piping and valves Frozen | F480Frozen fuel valves due to valves heaters to the 11N2 units kept going out. | Cold Weather
Cane Run 7 | Forced Derate | 1443.7207 | Low Gas Pipeline Pressure | FX00Block derate due to low fuel gas pipeline pressure | Fuel Supply Disruption
Haefling 1 CT | Forced Outage | 188.3 | Power Station switchyard (non generating unit equipment) | F820Substation breaker will not remain closed. | Mechanical Issue
Haefling 2 CT | Forced Outage | 188.3 | Power Station switchyard (non generating unit equipment) | F820Substation breaker will not remain closed. | Mechanical Issue
Mill Creek 4 | Forced Derate | 242.6914 | Coal Silo Tripper - Cold Weather | F480Coal Silo Tripper Issues - Cold Weather | Cold Weather
Paddy's Run 13 CT | Forced Outage | 107.9167 | Closed cooling water valves | F820Gen cold gas temp got too low. | Cold Weather
Trimble County 1 | Forced Outage | 8874 | Primary Submerged Chain Conveyor freezing | F340The unit was placed on a forced outage due to issues with the primary submerged chain conveyor. Outage duration was prolonged due to freezing issues around plant caused by unit offline. | Mechanical Issue
Trimble County 10 CT | Forced Derate | 933.1867 | Lack of Fuel | Lack of Fuel | Fuel Supply Disruption
Trimble County 2 | Forced Derate | 349.9662 | Maintain Deaerator Tank Levels- Cold Weather | F780In order to slow demand to the water coil air heaters from the deaerator, the unit was placed on a derate to maintain deaerator tank level. | Cold Weather
Trimble County 2 | Forced Derate | 524.3703 | Loss of B TDBFP | F480The unit was placed on derate due to frozen transmitter that caused the loss of the B TDBFP. | Cold Weather
Trimble County 2 | Forced Derate | 666.702 | Maintain Deaerator Tank Levels- Cold Weather | F480The unit was placed on a variable derate due to various cold weather issues encountered while trying to start-up the B TDBFP. | Cold Weather
Trimble County 2 | Forced Derate | 52.6334 | Maintain Deaerator Tank Levels- Cold Weather | F780In order to slow demand to the water coil air heaters from the deaerator, the unit was placed on a derate to maintain deaerator tank level. | Cold Weather
Trimble County 5 CT | Forced Outage | 119.3333 | Gas fuel system including controls and instrumentation | F820Lean Blow Out (LBO), and low fuel gas supply pressure. | Fuel Supply Disruption
Trimble County 5 CT | Forced Outage | 1825.8 | Lack of Fuel | Lack of Fuel | Fuel Supply Disruption
Trimble County 6 CT | Forced Derate | 821.61 | Lack of Fuel | Lack of Fuel | Fuel Supply Disruption
Trimble County 7 CT | Forced Derate | 953.4733 | Lack of Fuel | Lack of Fuel | Fuel Supply Disruption
Trimble County 8 CT | Forced Derate | 892.6133 | Lack of Fuel | Lack of Fuel | Fuel Supply Disruption
Trimble County 9 CT | Forced Derate | 770.355 | Lack of Fuel | Lack of Fuel | Fuel Supply Disruption
2022-05-27 | 24665.2667
Brown 7 CT | Maintenance Outage | 2608.8167 | Switchyard circuit breakers - external (OMC) | F590Generator Circuit Breaker (GCB) Inspection | N/A
Cane Run 7 | Maintenance Outage | 16656 | HRH Drain Line Leak | F540Block shut down to repair leaking HRH drain line | N/A
Mill Creek 2 | Forced Outage | 5400.45 | 2A/2B Cooling Tower Pumps Unavailable | F0602A/2B Cooling Tower Pumps Unavailable | Mechanical Issue
2022-05-11 | 24635.237
Brown 5 CT | Forced Outage | 576 | Card failure | F820ATOS card failure caused blowoff vales to go open and tripped unit. | Mechanical Issue
Brown 7 CT | Forced Outage | 486.7 | High engine exhaust temperature | F750TAT temps would not permit EV burners to stay lit | Mechanical Issue
Cane Run 7 | Maintenance Derate | 8339.7793 | 2022 Spring Outage - Combustion Inspection (CI) - CT1 Extension | F5302022 planned spring outage (CT1 extension) | N/A
Ghent 2 | Forced Derate | 2457.9994 | Condenser Tube Leak | F540Load Reduction #10GH2 condenser hotwell condensate chemistry indicating a condenser tube leak. | Mechanical Issue
Ghent 2 | Forced Outage | 1302.7583 | Condenser Tube Leak | F540Outage #5Condenser tube leaks. | Mechanical Issue
Ghent 4 | Forced Outage | 11472 | #3 Turbine Bearing Overheated During Rollup | F820Outage #3Ghent 4 Divsion panel #3 Tube14 tube leaks were repaired at 16:50 hours on 5-2-2022. The unit was unable to be placed in service due to overheating of the #3 turbine bearing during initial roll up after tube leak repair. | Mechanical Issue

## 2022 - Forced MWh Lost Detail
Unit | Event Type | Daily Net Forced MWh Lost | Cause | Description | Forced Category
2022-12-24 | 31890.5164
Brown 10 CT | Forced Outage | 3312 | Exhaust Diffuser Issues | F060Exhaust diffuser sections have separated. Bolts need to be replaced and exhaust diffusers realigned. | Mechanical Issue
Brown 3 | Forced Derate | 1654.8672 | Ash disposal problem | FS00Baghouse issues | Mechanical Issue
Cane Run 7 | Forced Derate | 2190.3103 | Low Gas Pipeline Pressure | FX00Block derate due to low fuel gas pipeline pressure | Fuel Supply Disruption
Haefling 1 CT | Forced Outage | 209.3 | Power Station switchyard (non generating unit equipment) | F820Substation breaker will not remain closed. | Mechanical Issue
Haefling 2 CT | Forced Outage | 209.3 | Substation breaker will not remain closed. | F820Substation breaker will not remain closed. | Mechanical Issue
Trimble County 1 | Forced Outage | 8874 | Primary Submerged Chain Conveyor freezing | F340The unit was placed on a forced outage due to issues with the primary submerged chain conveyor. Outage duration was prolonged due to freezing issues around plant caused by unit offline. | Mechanical Issue
Trimble County 10 CT | Forced Derate | 2195.7333 | Lack of Fuel | Lack of Fuel | Fuel Supply Disruption
Trimble County 2 | Forced Derate | 539.2619 | Maintain Deaerator Tank Levels- Cold Weather | F780In order to slow demand to the water coil air heaters from the deaerator, the unit was placed on a derate to maintain deaerator tank level. | Cold Weather
Trimble County 2 | Forced Derate | 261.0505 | Leaking Closed cooling water valves | F540The unit was placed on derate in order to address a leaking closed cooling water valve used to maintain the level of the SSC. This was in addition to the deaerator level issues. | Mechanical Issue
Trimble County 2 | Forced Derate | 59.1598 | Maintain Deaerator tank level | F780In order to slow demand to the water coil air heaters from the deaerator, the unit was placed on a derate to maintain deaerator tank level. | Cold Weather
Trimble County 5 CT | Forced Outage | 4296 | Lack of Fuel | Lack of Fuel | Fuel Supply Disruption
Trimble County 6 CT | Forced Derate | 1933.2 | Lack of Fuel | Lack of Fuel | Fuel Supply Disruption
Trimble County 7 CT | Forced Derate | 2243.4667 | Lack of Fuel | Lack of Fuel | Fuel Supply Disruption
Trimble County 8 CT | Forced Derate | 2100.2667 | Lack of Fuel | Lack of Fuel | Fuel Supply Disruption
Trimble County 9 CT | Forced Derate | 1812.6 | Lack of Fuel | Lack of Fuel | Fuel Supply Disruption
2022-12-23 | 27074.652
Brown 10 CT | Forced Outage | 3312 | Exhaust Diffuser Issues | F060Exhaust diffuser sections have separated. Bolts need to be replaced and exhaust diffusers realigned. | Mechanical Issue
Brown 11 CT | Forced Outage | 298.6667 | Fuel piping and valves Frozen | F480Frozen fuel valves due to valves heaters to the 11N2 units kept going out. | Cold Weather
Brown 11 CT | Forced Outage | 179.2 | Flame trip | F820Flame trip | Mechanical Issue
Brown 3 | Forced Derate | 61.6694 | Pulverizer Mills high Tonage | FS00Mills on high tonage. | Mechanical Issue
Brown 3 | Forced Derate | 309.0699 | Baghouse Pluggage from Boiler Slagging | FS00Baghouse plugging up due to boiler slagging. | Mechanical Issue
Brown 3 | Forced Derate | 712.5123 | Ash disposal problem | FS00Baghouse issues | Mechanical Issue
Brown 5 CT | Forced Outage | 2067 | Fuel piping and valves Frozen | F480Fuel valves froze after valve heaters to 11N2 units were blown out. | Cold Weather
Brown 5 CT | Forced Derate | 92.2901 | Pressure Switch Fail | F570Pressure switch on U5 lube oil pump failed. | Mechanical Issue
Brown 8 CT | Forced Outage | 268.8 | Fuel piping and valves Frozen | F480Fuel valves froze because valves heaters to the 11N2 units kept going out. | Cold Weather
Brown 8 CT | Forced Outage | 362.6667 | Lube oil pumps Malfunction | F570Malfunctioning lube oil pump | Mechanical Issue
Brown 8 CT | Forced Derate | 133.8047 | Other miscellaneous pollution control equipment problems | FE00Generation limited due to high input temperature alarm. | Mechanical Issue
Brown 9 CT | Forced Outage | 322 | Fuel piping and valves Frozen | F480Frozen fuel valves due to valves heaters to the 11N2 units kept going out. | Cold Weather
Cane Run 7 | Forced Derate | 1443.7207 | Low Gas Pipeline Pressure | FX00Block derate due to low fuel gas pipeline pressure | Fuel Supply Disruption
Haefling 1 CT | Forced Outage | 188.3 | Power Station switchyard (non generating unit equipment) | F820Substation breaker will not remain closed. | Mechanical Issue
Haefling 2 CT | Forced Outage | 188.3 | Substation breaker will not remain closed. | F820Substation breaker will not remain closed. | Mechanical Issue
Mill Creek 4 | Forced Derate | 242.6914 | Coal Silo Tripper - Cold Weather | F480Coal Silo Tripper Issues - Cold Weather | Cold Weather
Paddy's Run 13 CT | Forced Outage | 107.9167 | Closed cooling water valves | F820Gen cold gas temp got too low. | Cold Weather
Trimble County 1 | Forced Outage | 8874 | Primary Submerged Chain Conveyor freezing | F340The unit was placed on a forced outage due to issues with the primary submerged chain conveyor. Outage duration was prolonged due to freezing issues around plant caused by unit offline. | Mechanical Issue
Trimble County 10 CT | Forced Derate | 933.1867 | Lack of Fuel | Lack of Fuel | Fuel Supply Disruption
Trimble County 2 | Forced Derate | 349.9662 | Maintain Deaerator Tank Levels- Cold Weather | F780In order to slow demand to the water coil air heaters from the deaerator, the unit was placed on a derate to maintain deaerator tank level. | Cold Weather
Trimble County 2 | Forced Derate | 524.3703 | Loss of B TDBFP | F480The unit was placed on derate due to frozen transmitter that caused the loss of the B TDBFP. | Cold Weather
Trimble County 2 | Forced Derate | 666.702 | Maintain Deaerator Tank Levels- Cold Weather | F480The unit was placed on a variable derate due to various cold weather issues encountered while trying to start-up the B TDBFP. | Cold Weather
Trimble County 2 | Forced Derate | 52.6334 | Maintain Deaerator Tank Levels- Cold Weather | F780In order to slow demand to the water coil air heaters from the deaerator, the unit was placed on a derate to maintain deaerator tank level. | Cold Weather
Trimble County 5 CT | Forced Outage | 119.3333 | Gas fuel system including controls and instrumentation | F820Lean Blow Out (LBO), and low fuel gas supply pressure. | Fuel Supply Disruption
Trimble County 5 CT | Forced Outage | 1825.8 | Lack of Fuel | Lack of Fuel | Fuel Supply Disruption
Trimble County 6 CT | Forced Derate | 821.61 | Lack of Fuel | Lack of Fuel | Fuel Supply Disruption
Trimble County 7 CT | Forced Derate | 953.4733 | Lack of Fuel | Lack of Fuel | Fuel Supply Disruption
Trimble County 8 CT | Forced Derate | 892.6133 | Lack of Fuel | Lack of Fuel | Fuel Supply Disruption
Trimble County 9 CT | Forced Derate | 770.355 | Lack of Fuel | Lack of Fuel | Fuel Supply Disruption
2022-12-25 | 23989.7828
Brown 10 CT | Forced Outage | 3312 | Exhaust Diffuser Issues | F060Exhaust diffuser sections have separated. Bolts need to be replaced and exhaust diffusers realigned. | Mechanical Issue
Brown 3 | Forced Derate | 126.4135 | Ash disposal problem | FS00Baghouse issues | Mechanical Issue
Brown 3 | Forced Derate | 782.6599 | Boiler Pluggage | F120Boiler suspect of pluggage | Mechanical Issue
Brown 3 | Forced Outage | 1144 | Boiler Pluggage | F120Boiler pluggage. Unable to keep unit online. | Mechanical Issue
Cane Run 7 | Forced Derate | 147.8525 | Low Gas Pipeline Pressure | FX00Block derate due to low fuel gas pipeline pressure | Fuel Supply Disruption
Trimble County 1 | Forced Outage | 8874 | Primary Submerged Chain Conveyor freezing | F340The unit was placed on a forced outage due to issues with the primary submerged chain conveyor. Outage duration was prolonged due to freezing issues around plant caused by unit offline. | Mechanical Issue
Trimble County 10 CT | Forced Derate | 1463.8222 | Lack of Fuel | Lack of Fuel | Fuel Supply Disruption
Trimble County 2 | Forced Derate | 631.0379 | Maintain Deaerator tank level | F780In order to slow demand to the water coil air heaters from the deaerator, the unit was placed on a derate to maintain deaerator tank level. | Cold Weather
Trimble County 5 CT | Forced Outage | 2109.2167 | Lack of Fuel | Lack of Fuel | Fuel Supply Disruption
Trimble County 6 CT | Forced Derate | 1288.8 | Lack of Fuel | Lack of Fuel | Fuel Supply Disruption
Trimble County 7 CT | Forced Derate | 1495.6444 | Lack of Fuel | Lack of Fuel | Fuel Supply Disruption
Trimble County 8 CT | Forced Derate | 1400.1778 | Lack of Fuel | Lack of Fuel | Fuel Supply Disruption
Trimble County 9 CT | Forced Derate | 653.2913 | Lack of Fuel | Lack of Fuel | Fuel Supply Disruption
Trimble County 9 CT | Forced Outage | 560.8667 | Lack of Fuel | Lack of Fuel | Fuel Supply Disruption
2022-12-26 | 23274.8879
Brown 10 CT | Forced Outage | 3312 | Exhaust Diffuser Issues | F060Exhaust diffuser sections have separated. Bolts need to be replaced and exhaust diffusers realigned. | Mechanical Issue
Brown 3 | Forced Outage | 9984 | Boiler Pluggage | F120Boiler pluggage. Unable to keep unit online. | Mechanical Issue
Mill Creek 2 | Forced Derate | 473.85 | B Mill Temperature Malfunction | F5202B Mill Temperature Malfunction | Mechanical Issue
Trimble County 1 | Forced Outage | 8874 | Primary Submerged Chain Conveyor freezing | F340The unit was placed on a forced outage due to issues with the primary submerged chain conveyor. Outage duration was prolonged due to freezing issues around plant caused by unit offline. | Mechanical Issue
Trimble County 2 | Forced Derate | 631.0379 | Maintain Deaerator tank level | F780In order to slow demand to the water coil air heaters from the deaerator, the unit was placed on a derate to maintain deaerator tank level. | Cold Weather
2022-05-12 | 23157.358
Ghent 2 | Forced Outage | 11652 | Condenser Tube Leak | F540Outage #5Condenser tube leaks. | Mechanical Issue
Ghent 4 | Forced Outage | 11472 | #3 Turbine Bearing Overheated During Rollup | F820Outage #3Ghent 4 Divsion panel #3 Tube14 tube leaks were repaired at 16:50 hours on 5-2-2022. The unit was unable to be placed in service due to overheating of the #3 turbine bearing during initial roll up after tube leak repair. | Mechanical Issue
Haefling 2 CT | Forced Outage | 33.358 | Air cooling system | F760Broken shear pin on cooling fan caused excessive oil temps | Mechanical Issue
2022-12-27 | 22603.8386
Brown 10 CT | Forced Outage | 3312 | Exhaust Diffuser Issues | F060Exhaust diffuser sections have separated. Bolts need to be replaced and exhaust diffusers realigned. | Mechanical Issue
Brown 3 | Forced Outage | 9984 | Boiler Pluggage | F120Boiler pluggage. Unable to keep unit online. | Mechanical Issue
Trimble County 1 | Forced Outage | 8874 | Primary Submerged Chain Conveyor freezing | F340The unit was placed on a forced outage due to issues with the primary submerged chain conveyor. Outage duration was prolonged due to freezing issues around plant caused by unit offline. | Mechanical Issue
Trimble County 2 | Forced Derate | 433.8386 | Maintain Deaerator tank level | F780In order to slow demand to the water coil air heaters from the deaerator, the unit was placed on a derate to maintain deaerator tank level. | Cold Weather
2022-12-29 | 22228.3333
Brown 10 CT | Forced Outage | 3312 | Exhaust Diffuser Issues | F060Exhaust diffuser sections have separated. Bolts need to be replaced and exhaust diffusers realigned. | Mechanical Issue
Brown 3 | Forced Outage | 9984 | Boiler Pluggage | F120Boiler pluggage. Unable to keep unit online. | Mechanical Issue
Paddy's Run 12 CT | Forced Outage | 58.3333 | Slam shut valve tripped | F840Loss of gas psi. Slam shut valve tripped. | Mechanical Issue
Trimble County 1 | Forced Outage | 8874 | Primary Submerged Chain Conveyor freezing | F340The unit was placed on a forced outage due to issues with the primary submerged chain conveyor. Outage duration was prolonged due to freezing issues around plant caused by unit offline. | Mechanical Issue
2022-12-28 | 22170
Brown 10 CT | Forced Outage | 3312 | Exhaust Diffuser Issues | F060Exhaust diffuser sections have separated. Bolts need to be replaced and exhaust diffusers realigned. | Mechanical Issue
Brown 3 | Forced Outage | 9984 | Boiler Pluggage | F120Boiler pluggage. Unable to keep unit online. | Mechanical Issue
Trimble County 1 | Forced Outage | 8874 | Primary Submerged Chain Conveyor freezing | F340The unit was placed on a forced outage due to issues with the primary submerged chain conveyor. Outage duration was prolonged due to freezing issues around plant caused by unit offline. | Mechanical Issue
2022-05-03 | 21408
Brown 3 | Forced Outage | 9936 | 3-4 BCWP Replacement | F780Replace 3-4 BCWP, Unable to run on two Bcwp's. | Mechanical Issue
Ghent 4 | Forced Outage | 11472 | #3 Turbine Bearing Overheated During Rollup | F820Outage #3Ghent 4 Divsion panel #3 Tube14 tube leaks were repaired at 16:50 hours on 5-2-2022. The unit was unable to be placed in service due to overheating of the #3 turbine bearing during initial roll up after tube leak repair. | Mechanical Issue
2022-05-31 | 19955.4333
Cane Run 7 | Forced Outage | 12827.4333 | Steam Turbine Coupling | F610Needing to Uncouple Steam Turbine Generator in order to run CT''s in Simple Cycle ode. Having issues uncoupling. | Mechanical Issue
Mill Creek 2 | Forced Outage | 7128 | 2A/2B Cooling Tower Pumps Unavailable | F0602A/2B Cooling Tower Pumps Unavailable | Mechanical Issue