## Cold Weather Event Days
- FDG - GADS EVENT INFO
UnitName | EventType | EventNo | CauseCode | Original Start* | Original End* | EventStart | EventEnd | Duration_Hrs | Equiv. Dur Hrs | MWH Lost |  | GAC | GMC | NMC | Cause | eventDescription
2014-01-06
BR11 | U1 | 3 | 5017 |  |  | 2014-01-06 17:57 | 2014-01-06 19:14 | 1.2833 | 1.2833 | 155.2833 |  | 0 | 122 | 121 | Low pressure compressor bleed valves | F550Loose limit switch on blow off valve caused unit to trip.
BR5 | U1 | 2 | 5054 |  |  | 2014-01-06 08:23 | 2014-01-06 11:47 | 3.4 | 3.4 | 442 |  | 0 | 131 | 130 | Water injection system | F480Instrument measuring DP across water injection control started to freeze. Operato
CR11 | U1 | 2 | 5130 |  | 2014-01-07 09:05 | 2014-01-06 20:13 | 2014-01-07 | 3.7833 | 3.7833 | 52.9667 |  | 0 | 14 | 14 | Starting system (including motor) | F030Broken terminal on battery cable causing Cane Run 11 starting diesel to be unable
GH2 | D1 | 1 | 9650 |  |  | 2014-01-06 11:20 | 2014-01-06 12:00 | 0.66667 | 0.22179 | 107.5705 |  | 347 | 520 | 485 | Other stack/exhaust emissions - fossil (use codes 9200 to 9290 if fuel quality causes pollution control equipment problems that result in excess stack emissions) | Load Reduction #1Lost SO3 mitigation system. Air pressure / injection causing H2S
HA1 | SF | 2 | 5160 |  | 2014-01-14 13:14 | 2014-01-06 21:22 | 2014-01-07 | 2.6333 | 2.6333 | 31.6 |  | 0 | 12 | 12 | Cooling and seal air system | F540Busted glycol line on radiator. Failed to ignite on start up.
MC2 | D1 | 7 | 1850 | 2014-01-05 05:35 |  | 2014-01-06 | 2014-01-06 01:00 | 1 | 0.21212 | 63 |  | 260 | 330 | 297 | Boiler water condition (not feedwater water quality) | F170High Silica
MC2 | D1 | 8 | 1850 |  |  | 2014-01-06 01:00 | 2014-01-06 09:28 | 8.4667 | 1.2828 | 381 |  | 280 | 330 | 297 | Boiler water condition (not feedwater water quality) | F170High Silica
MC2 | D1 | 9 | 1850 |  |  | 2014-01-06 09:28 | 2014-01-06 19:00 | 9.5333 | 0.28889 | 85.8 |  | 320 | 330 | 297 | Boiler water condition (not feedwater water quality) | F170High Silica
MC2 | D1 | 10 | 1850 |  |  | 2014-01-06 19:00 | 2014-01-06 22:36 | 3.6 | 0.32727 | 97.2 |  | 300 | 330 | 297 | Boiler water condition (not feedwater water quality) | F170High Silica
MC3 | D1 | 2 | 360 | 2014-01-05 23:16 |  | 2014-01-06 | 2014-01-06 02:00 | 2 | 0.43602 | 170.4834 |  | 330 | 422 | 391 | Burners | F7803A Mill - Burners High Temperature
MC4 | D1 | 3 | 380 |  |  | 2014-01-06 05:40 | 2014-01-06 05:48 | 0.13333 | 0.067569 | 32.2306 |  | 255 | 517 | 477 | Light off (igniter) systems (including fuel supply) | F4004C Mill - Gas Igniter Issue
MC4 | D1 | 4 | 380 |  |  | 2014-01-06 06:40 | 2014-01-06 08:55 | 2.25 | 0.77031 | 367.4376 |  | 340 | 517 | 477 | Light off (igniter) systems (including fuel supply) | F4004B & 4C Mills - Gas Igniter Issues
MC4 | D1 | 5 | 380 |  |  | 2014-01-06 08:55 | 2014-01-06 12:30 | 3.5833 | 0.67231 | 320.691 |  | 420 | 517 | 477 | Light off (igniter) systems (including fuel supply) | F7204C Mill - Gas Vent Valve Stuck Open
TC5 | U1 | 4 | 5246 |  |  | 2014-01-06 12:15 | 2014-01-06 14:08 | 1.8833 | 1.8833 | 299.45 |  | 0 | 160 | 159 | Gas Turbine Control System - hardware problems (including card failure) | F520Unit tripped on high exhaust temperature differential from a failed control system
TC6 | U1 | 4 | 5079 |  |  | 2014-01-06 02:17 | 2014-01-06 03:50 | 1.55 | 1.55 | 246.45 |  | 0 | 160 | 159 | Other combustor problems | F460Unit tripped due to a lean blowout.
TC6 | U1 | 6 | 5041 |  |  | 2014-01-06 13:52 | 2014-01-06 14:46 | 0.9 | 0.9 | 143.1 |  | 0 | 160 | 159 | Fuel piping and valves | F480Unit tripped due to a fuel gas valve (worker valve) not controlling properly.
TC8 | SF | 5 | 5130 | 2014-01-05 12:00 |  | 2014-01-06 | 2014-01-06 15:58 | 15.9667 | 15.9667 | 2538.7 |  | 0 | 160 | 159 | Starting system (including motor) | F330Startup failure due to issue with 89SS.
TC9 | U1 | 7 | 5130 |  |  | 2014-01-06 02:27 | 2014-01-06 02:57 | 0.5 | 0.5 | 79.5 |  | 0 | 160 | 159 | Starting system (including motor) | F340Forced outage due to issue with 89SS.
[10 empty] | 1/6/2014 MWH Lost | 2014 Daily Average MWH Lost |  | Cold weather
[10 empty] | 5614.4631 | 12734.6916 |  | 7.873%
% of Forced Outages
[13 empty] | Coal | 28.95%
[13 empty] | Gas | 71.05%
2014-01-07
BR9 | U1 | 3 | 5140 |  |  | 2014-01-07 09:33 | 2014-01-07 10:36 | 1.05 | 1.05 | 127.05 |  | 0 | 122 | 121 | Battery and charger system | F410Both battery chargers indicated failure. Failure was caused by low output current
CR11 | U1 | 2 | 5130 | 2014-01-06 20:13 |  | 2014-01-07 | 2014-01-07 09:05 | 9.0833 | 9.0833 | 127.1667 |  | 0 | 14 | 14 | Starting system (including motor) | F030Broken terminal on battery cable causing Cane Run 11 starting diesel to be unable
GH3 | U1 | 1 | 1455 |  | 2014-01-08 06:15 | 2014-01-07 21:20 | 2014-01-08 | 2.6667 | 2.6667 | 1282.6667 |  | 0 | 530 | 481 | Induced draft fans | F850Outage #13-2 ID fan tripped on high vibration on OB fan bearing. This caused
GH4 | D1 | 2 | 250 |  |  | 2014-01-07 03:55 | 2014-01-07 04:36 | 0.68333 | 0.1627 | 77.7698 |  | 400 | 525 | 478 | Pulverizer feeders | Load Reduction #14-4 Feeder tripped.
GR3 | D1 | 1 | 250 |  |  | 2014-01-07 13:15 | 2014-01-07 14:15 | 1 | 0.23611 | 16.0556 |  | 55 | 72 | 68 | Pulverizer feeders | FW004-4 Feeder plugged with coal and ice.
HA1 | SF | 2 | 5160 | 2014-01-06 21:22 | 2014-01-14 13:14 | 2014-01-07 | 2014-01-08 | 24 | 24 | 288 |  | 0 | 12 | 12 | Cooling and seal air system | F540Busted glycol line on radiator. Failed to ignite on start up.
MC1 | D1 | 1 | 8280 |  |  | 2014-01-07 07:15 | 2014-01-07 08:58 | 1.7167 | 0.36414 | 109.2424 |  | 260 | 330 | 300 | Reagent feed piping | F540FGD Reactant Feed Line - Leak
MC1 | D1 | 2 | 250 |  |  | 2014-01-07 16:50 | 2014-01-07 18:06 | 1.2667 | 0.26869 | 80.6061 |  | 260 | 330 | 300 | Pulverizer feeders | FW001D Coal Feeder - Plugged, Frozen/Wet Coal
MC2 | D1 | 11 | 250 |  |  | 2014-01-07 05:45 | 2014-01-07 07:15 | 1.5 | 0.40909 | 121.5 |  | 240 | 330 | 297 | Pulverizer feeders | FW002A Coal Feeder - Plugged, Frozen/Wet Coal
MC2 | D1 | 12 | 1850 |  | 2014-01-08 09:50 | 2014-01-07 12:15 | 2014-01-08 | 11.75 | 1.7803 | 528.75 |  | 280 | 330 | 297 | Boiler water condition (not feedwater water quality) | F170High Silica
TC1 | D1 | 6 | 280 |  |  | 2014-01-07 17:25 | 2014-01-07 21:08 | 3.7167 | 0.2805 | 138.2881 |  | 490 | 530 | 493 | Pulverizer fires | F780Derate required due to A & B coal mill fires.
TC5 | U1 | 6 | 5246 |  |  | 2014-01-07 01:25 | 2014-01-07 05:50 | 4.4167 | 4.4167 | 702.25 |  | 0 | 160 | 159 | Gas Turbine Control System - hardware problems (including card failure) | F520Forced outage due to compressor inlet thermocouple disagreement from a failed cont
TC6 | U1 | 8 | 5016 |  |  | 2014-01-07 01:25 | 2014-01-07 05:49 | 4.4 | 4.4 | 699.6 |  | 0 | 160 | 159 | High pressure compressor bleed valves | F480Forced outage due to compressor bleed valve frozen closed.
[10 empty] | 1/7/2014 MWH Lost | 2014 Daily Average MWH Lost |  | Cold weather
[10 empty] | 4298.9453 | 12734.6916 |  | 21.35%
% of Forced Outages
[13 empty] | Coal | 54.78%
[13 empty] | Gas | 45.22%
2015-02-19
BR10 | D1 | 1 | 5097 |  |  | 2015-01-01 | 2015-04-01 | 2160 |  |  |  | 120 | 122 | 121 | Other low pressure problems | F600Blade desing issues has unit limited to 120MWs.
BR11 | D1 | 1 | 5097 |  |  | 2015-01-01 | 2015-04-01 | 2160 |  |  |  | 120 | 122 | 121 | Other low pressure problems | F600Blade design issues has unit limited to 120MWs.
BR5 | D1 | 1 | 5097 |  |  | 2015-01-01 | 2015-04-01 | 2160 |  |  |  | 120 | 131 | 130 | Other low pressure problems | F600Blade design issues has unit limited to 120MWs.
BR8 | D1 | 1 | 5097 |  |  | 2015-01-01 | 2015-04-01 | 2160 |  |  |  | 120 | 122 | 121 | Other low pressure problems | F600Blade design issues has unit limited to 120MWs.
BR9 | D1 | 1 | 5097 |  |  | 2015-01-01 | 2015-04-01 | 2160 |  |  |  | 120 | 122 | 121 | Other low pressure problems | F600Blade desing issues has unit limited to 120MWs.
CR11 | U1 | 8 | 5150 |  |  | 2015-02-16 04:14 | 2015-03-01 11:28 | 319.23 |  |  |  | 0 | 14 | 14 | Turning gear and motor | F700Turning gear motor failure.
PR11 | U1 | 8 | 9290 |  |  | 2015-02-14 20:00 | 2015-02-21 20:10 | 168.17 |  |  |  | 0 | 12.5 | 12.5 | Other fuel quality problems (OMC) | F660Gas pressure problems.
PR12 | U1 | 8 | 9290 |  |  | 2015-02-14 20:00 | 2015-02-21 20:10 | 168.17 |  |  |  | 0 | 23 | 23 | Other fuel quality problems (OMC) | F660Gas pressure problems.
PR13 | U1 | 10 | 9290 |  |  | 2015-02-14 20:00 | 2015-02-21 | 148 |  |  |  | 0 | 148 | 147 | Other fuel quality problems (OMC) | F660Gas pressure problems.
TC1 | D1 | 28 | 1493 |  |  | 2015-02-11 07:11 | 2015-03-03 17:06 | 489.92 |  |  |  | 530 | 530 | 493 | Air heater fouling (regenerative) | FF00Differential pressure across the AH increased and required a derate in order to ke
TC1 | D1 | 29 | 310 |  |  | 2015-02-19 13:35 | 2015-02-19 14:20 | 0.75 | 0.21934 | 108.1344 |  | 375 | 530 | 493 | Pulverizer mills | FR00Unit derated due to 1D coal mill fire. D mill taken offline and out of service fo
TC2 | D1 | 6 | 4269 |  |  | 2015-01-12 19:00 | 2015-03-04 16:00 | 1221 |  |  |  | 789 | 781 | 732 | Other turbine valves (including LP steam admission valves) | F540Unit was derated 20MW due to HP turbine bypass valve leak through. This required
TC5 | U1 | 14 | 5079 |  |  | 2015-02-19 01:17 | 2015-02-19 02:42 | 1.4167 | 1.4167 | 225.25 |  | 0 | 160 | 159 | Other combustor problems | F820Unit tripped on lean blow out due to NOx adjustment set too low to maintain flame
TC5 | SF | 15 | 5130 |  |  | 2015-02-19 02:42 | 2015-02-19 07:57 | 5.25 | 5.25 | 834.75 |  | 0 | 160 | 159 | Starting system (including motor) | F340Loose wire problem on 89SS switch caused a not ready to start condition.
TC5 | U1 | 16 | 5079 |  |  | 2015-02-19 09:05 | 2015-02-19 12:37 | 3.5333 | 3.5333 | 561.8 |  | 0 | 160 | 159 | Other combustor problems | F820Unit tripped on lean blow out, extreme cold conditions caused autotune to lean com
TC5 | U1 | 17 | 5048 |  |  | 2015-02-19 22:06 | 2015-02-19 23:31 | 1.4167 | 1.4167 | 225.25 |  | 0 | 160 | 159 | Gas fuel system including controls and instrumentation | F820The autotune program was turned off, and this causes the machine to be susceptible
TC5 | SF | 18 | 5130 |  |  | 2015-02-19 23:31 | 2015-02-19 23:49 | 0.3 | 0.3 | 47.7 |  | 0 | 160 | 159 | Starting system (including motor) | F340This was not an excitation issue. The LCI was not reset after the previous start a
TC6 | U1 | 22 | 5079 |  |  | 2015-02-19 01:45 | 2015-02-19 03:00 | 1.25 | 1.25 | 198.75 |  | 0 | 160 | 159 | Other combustor problems | F820Autotune NOx setting too low to sustain flame in extreme low temperature. Lean blo
TC6 | D1 | 28 | 5109 |  |  | 2015-02-19 03:00 | 2015-02-19 06:34 | 3.5667 | 0.044583 | 7.0887 |  | 158 | 160 | 159 | Other exhaust problems (including high exhaust system temperature not attributable to a specific problem) | F750High exhaust thermocouple spreads and high dynamics cause a unit run back on load,
TC6 | U1 | 23 | 5079 |  |  | 2015-02-19 06:34 | 2015-02-19 08:15 | 1.6833 | 1.6833 | 267.65 |  | 0 | 160 | 159 | Other combustor problems | F820Lean blow out event. Thermocouple spread is the first sign of a combustion can blo
TC6 | D1 | 29 | 5079 |  |  | 2015-02-19 18:11 | 2015-02-19 22:45 | 4.5667 | 0.57083 | 90.7625 |  | 140 | 160 | 159 | Other combustor problems | FE00Load limit due to NOx readings going above our 12 PPM limit.
TC6 | U1 | 24 | 5079 |  | 2015-02-20 00:33 | 2015-02-19 22:45 | 2015-02-20 | 1.25 | 1.25 | 198.75 |  | 0 | 160 | 159 | Other combustor problems | F820Autotune NOx setting too low to sustain flame in extreme cold temperatures. Lean b
Z1 | D1 | 5 | 5108 | 2015-02-18 15:52 | 2015-02-20 11:57 | 2015-02-19 | 2015-02-20 | 24 | 6 | 96 |  | 12 | 16 | 16 | High engine exhaust temperature | F750Exhaust over temperature issues. Unit derated 4 MW.
[10 empty] | 2/19/2015 MWH Lost | 2015 Daily Average MWH Lost |  | Cold weather
[10 empty] | 2861.8857 | 13778.8755 |  | 33.52%
% of Forced Outages
[13 empty] | Coal | 3.778%
[13 empty] | Gas | 96.22%
2015-02-20
BR10 | D1 | 1 | 5097 |  |  | 2015-01-01 | 2015-04-01 | 2160 |  |  |  | 120 | 122 | 121 | Other low pressure problems | F600Blade desing issues has unit limited to 120MWs.
BR11 | D1 | 1 | 5097 |  |  | 2015-01-01 | 2015-04-01 | 2160 |  |  |  | 120 | 122 | 121 | Other low pressure problems | F600Blade design issues has unit limited to 120MWs.
BR3 | U1 | 12 | 90 |  |  | 2015-02-20 13:34 | 2015-02-20 15:55 | 2.35 | 2.35 | 968.2 |  | 0 | 455 | 412 | Bunker fires | FR00Unit 3 coal bunker fires in 3-4 and partially in 3-5 bunker
BR3 | D1 | 13 | 9270 |  | 2015-02-21 03:20 | 2015-02-20 22:16 | 2015-02-21 | 1.7333 | 0.4 | 164.8 |  | 350 | 455 | 412 | Wet coal (OMC) | FW00Wet Coal
BR5 | D1 | 1 | 5097 |  |  | 2015-01-01 | 2015-04-01 | 2160 |  |  |  | 120 | 131 | 130 | Other low pressure problems | F600Blade design issues has unit limited to 120MWs.
BR5 | D1 | 20 | 5009 |  |  | 2015-02-20 08:10 | 2015-02-20 11:14 | 3.0667 | 1.8962 | 246.5038 |  | 50 | 131 | 130 | Other inlet air problems | F480Screens on inlet of air filter house started to freeze causing implosion doors to
BR8 | D1 | 1 | 5097 |  |  | 2015-01-01 | 2015-04-01 | 2160 |  |  |  | 120 | 122 | 121 | Other low pressure problems | F600Blade design issues has unit limited to 120MWs.
BR8 | U1 | 14 | 3611 |  | 2015-02-22 10:52 | 2015-02-20 13:50 | 2015-02-21 | 10.1667 | 10.1667 | 1230.1667 |  | 0 | 122 | 121 | Switchyard circuit breakers - external (OMC) | F660Hydraulic pump in substation breaker quit working.
BR9 | D1 | 1 | 5097 |  | 2015-04-01 | 2015-01-01 | 2015-04-01 | 2160 |  |  |  | 120 | 122 | 121 | Other low pressure problems | F600Blade desing issues has unit limited to 120MWs.
CR11 | U1 | 8 | 5150 |  | 2015-03-01 11:28 | 2015-02-16 04:14 | 2015-03-01 11:28 | 319.2333 |  |  |  | 0 | 14 | 14 | Turning gear and motor | F700Turning gear motor failure.
GR3 | PD | 16 | 346 |  | 2015-02-21 01:02 | 2015-02-20 23:00 | 2015-02-21 | 1 | 0.097222 | 6.6111 |  | 65 | 72 | 68 | Pulverizer pyrite removal system | F5304-3 Pulv out of service to inspect pyrite flop gate. Suspect that flop gate is st
PR11 | U1 | 8 | 9290 |  |  | 2015-02-14 20:00 | 2015-02-21 20:10 | 168.1667 |  |  |  | 0 | 12.5 | 12.5 | Other fuel quality problems (OMC) | F660Gas pressure problems.
PR12 | U1 | 8 | 9290 |  |  | 2015-02-14 20:00 | 2015-02-21 20:10 | 168.1667 |  |  |  | 0 | 23 | 23 | Other fuel quality problems (OMC) | F660Gas pressure problems.
PR13 | U1 | 10 | 9290 |  |  | 2015-02-14 20:00 | 2015-02-21 | 148 |  |  |  | 0 | 148 | 147 | Other fuel quality problems (OMC) | F660Gas pressure problems.
TC1 | D1 | 28 | 1493 |  |  | 2015-02-11 07:11 | 2015-03-03 17:06 | 489.9167 |  |  |  | 530 | 530 | 493 | Air heater fouling (regenerative) | FF00Differential pressure across the AH increased and required a derate in order to ke
TC2 | D1 | 6 | 4269 |  |  | 2015-01-12 19:00 | 2015-03-04 16:00 | 1221 |  |  |  | 789 | 781 | 732 | Other turbine valves (including LP steam admission valves) | F540Unit was derated 20MW due to HP turbine bypass valve leak through. This required
TC5 | U1 | 19 | 5079 |  |  | 2015-02-20 14:09 | 2015-02-20 14:41 | 0.53333 | 0.53333 | 84.8 |  | 0 | 160 | 159 | Other combustor problems | F820This trip is similar to event #17, fuel gas heater not working causing low inlet f
TC6 | U1 | 24 | 5079 | 2015-02-19 22:45 |  | 2015-02-20 | 2015-02-20 00:33 | 0.55 | 0.55 | 87.45 |  | 0 | 160 | 159 | Other combustor problems | F820Autotune NOx setting too low to sustain flame in extreme cold temperatures. Lean b
TC6 | D1 | 30 | 5079 |  |  | 2015-02-20 00:33 | 2015-02-20 19:44 | 19.1833 | 0 | 0 |  | 160 | 160 | 159 | Other combustor problems | FE00Load limit due to NOx readings going above our 12 PPM limit.
Z1 | D1 | 5 | 5108 | 2015-02-18 15:52 |  | 2015-02-20 | 2015-02-20 11:57 | 11.95 | 2.9875 | 47.8 |  | 12 | 16 | 16 | High engine exhaust temperature | F750Exhaust over temperature issues. Unit derated 4 MW.
[10 empty] | 2/20/2015 MWH Lost | 2015 Daily Average MWH Lost |  | Cold weather
[10 empty] | 2836.3316 | 13778.8755 |  | 0%
% of Forced Outages
[13 empty] | Coal | 40.18%
[13 empty] | Gas | 59.82%
2022-12-23
BR10 | U1 | 59 | 5109 |  |  | 2022-12-03 18:26 | 2023-01-01 | 677.57 |  |  |  |  | 122 | 121 | Other exhaust problems (including high exhaust system temperature not attributable to a specific problem) | F060Exhaust diffuser sections have separated. Bolts need to be replaced and exhaust d
BR11 | U1 | 58 | 5041 |  |  | 2022-12-23 01:30 | 2022-12-23 03:50 | 2.3333 | 2.3333 | 282.3333 |  | 0 | 122 | 121 | Fuel piping and valves | F480Frozen fuel valves due to valves heaters to the 11N2 units kept going out.
BR11 | U1 | 60 | 5073 |  |  | 2022-12-23 15:39 | 2022-12-23 17:03 | 1.4 | 1.4 | 169.4 |  | 0 | 122 | 121 | Flame scanners | F820Flame trip
BR3 | D1 | 36 | 310 |  |  | 2022-12-23 07:17 | 2022-12-23 08:30 | 1.2167 | 0.14707 | 60.5927 |  | 400 | 455 | 412 | Pulverizer mills | FS00Mills on high tonage.
BR3 | D1 | 40 | 8650 |  |  | 2022-12-23 08:30 | 2022-12-23 13:40 | 5.1667 | 0.7381 | 304.0952 |  | 390 | 455 | 412 | "Baghouse systems, general" | FS00Baghouse plugging up due to boiler slagging.
BR3 | D1 | 37 | 9305 |  | 2022-12-25 01:50 | 2022-12-23 13:40 | 2022-12-24 | 10.3333 | 1.7033 | 701.7582 |  | 380 | 455 | 412 | Ash disposal problem | FS00Baghouse issues
BR5 | U1 | 55 | 5041 |  |  | 2022-12-23 01:28 | 2022-12-23 17:22 | 15.9 | 15.9 | 2067 |  | 0 | 131 | 130 | Fuel piping and valves | F480Fuel valves froze after valve heaters to 11N2 units were blown out.
BR5 | D1 | 57 | 5113 |  |  | 2022-12-23 18:00 | 2022-12-23 21:00 | 3 | 0.70992 | 92.2901 |  | 100 | 131 | 130 | Lube oil valves/piping | F570Pressure switch on U5 lube oil pump failed.
BR8 | U1 | 74 | 5041 |  |  | 2022-12-23 01:30 | 2022-12-23 03:36 | 2.1 | 2.1 | 254.1 |  | 0 | 122 | 121 | Fuel piping and valves | F480Fuel valves froze because valves heaters to the 11N2 units kept going out.
BR8 | U1 | 75 | 5111 |  |  | 2022-12-23 03:36 | 2022-12-23 06:26 | 2.8333 | 2.8333 | 342.8333 |  | 0 | 122 | 121 | Lube oil pumps | F570Malfunctioning lube oil pump
BR8 | D1 | 78 | 3974 |  |  | 2022-12-23 10:51 | 2022-12-23 15:30 | 4.65 | 0.83852 | 101.4615 |  | 100 | 122 | 121 | DCS - logic problems | F610Generation limited due to high input temp alarm that had been removed but not remo
BR9 | U1 | 58 | 5041 |  |  | 2022-12-23 01:30 | 2022-12-23 03:50 | 2.3333 | 2.3333 | 282.3333 |  | 0 | 122 | 121 | Fuel piping and valves | F480Frozen fuel valves due to valves heaters to the 11N2 units kept going out.
CR7 | D1 | 59 | 9130 |  | 2022-12-24 15:30 | 2022-12-23 13:47 | 2022-12-24 | 10.2167 | 1.8617 | 1232.4479 |  | 552 | 675 | 662 | "Lack of fuel (water from rivers or lakes, coal mines, gas lines, etc) where the operator is not in control of contracts, supply lines, or delivery of fuels" | FX00Block derate due to low fuel gas pipeline pressure
HA1 | U1 | 5 | 3700 |  | 2022-12-24 14:57 | 2022-12-23 10:33 | 2022-12-24 | 13.45 | 13.45 | 161.4 |  | 0 | 12 | 12 | Power Station switchyard (non generating unit equipment) | F820Substation breaker will not remain closed.
HA2 | U1 | 7 | 3700 |  | 2022-12-24 14:57 | 2022-12-23 10:33 | 2022-12-24 | 13.45 | 13.45 | 161.4 |  | 0 | 12 | 12 | Power Station switchyard (non generating unit equipment) | F820Substation breaker will not remain closed.
MC4 | D1 | 34 | 95 |  |  | 2022-12-23 16:34 | 2022-12-23 18:44 | 2.1667 | 0.47357 | 225.8907 |  | 404 | 517 | 477 | Bunker flow problems | F480Coal Silo Tripper Issues - Cold Weather
PR13 | U1 | 89 | 3822 |  |  | 2022-12-23 06:36 | 2022-12-23 07:13 | 0.61667 | 0.61667 | 90.65 |  | 0 | 148 | 147 | Closed cooling water valves | F820Gen cold gas temp got too low.
TC1 | U1 | 25 | 897 |  |  | 2022-12-22 15:35 | 2022-12-30 02:19 | 178.7333 |  |  |  | 0 | 530 | 493 | Bottom ash rotary (drag chain type) conveyor and motor | F340The unit was placed on a forced outage due to issues with the primary submerged ch
TC10 | D1 | 301 | 9130 |  | 2022-12-25 16:00 | 2022-12-23 13:48 | 2022-12-24 | 10.2 | 4.59 | 729.81 |  | 88 | 160 | 159 | "Lack of fuel (water from rivers or lakes, coal mines, gas lines, etc) where the operator is not in control of contracts, supply lines, or delivery of fuels" | FX00Low fuel gas supply pressure from transport company to the plant.
TC2 | D1 | 49 | 3344 |  |  | 2022-12-23 03:10 | 2022-12-23 15:48 | 12.6333 | 0.17793 | 130.2479 |  | 770 | 781 | 732 | Deaerator (including level control) | F780In order to slow demand to the water coil air heaters from the deaerator, the unit
TC2 | D1 | 50 | 1760 |  |  | 2022-12-23 15:48 | 2022-12-23 17:41 | 1.8833 | 0.885 | 647.8184 |  | 414 | 781 | 732 | Feedwater instrumentation (not local controls) | F480The unit was placed on derate due to frozen transmitter that caused the loss of th
TC2 | D1 | 51 | 1760 |  |  | 2022-12-23 17:41 | 2022-12-23 22:06 | 4.4167 | 1.0519 | 769.959 |  | 595 | 781 | 732 | Feedwater instrumentation (not local controls) | F480The unit was placed on a variable derate due to various cold weather issues encoun
TC2 | D1 | 52 | 3344 |  | 2022-12-24 19:28 | 2022-12-23 22:06 | 2022-12-24 | 1.9 | 0.026761 | 19.5887 |  | 770 | 781 | 732 | Deaerator (including level control) | F780In order to slow demand to the water coil air heaters from the deaerator, the unit
TC5 | U1 | 116 | 5048 |  |  | 2022-12-23 13:08 | 2022-12-23 13:48 | 0.66667 | 0.66667 | 106 |  | 0 | 160 | 159 | Gas fuel system including controls and instrumentation | F820Lean Blow Out (LBO) trip.
TC5 | U1 | 117 | 9130 |  | 2022-12-25 11:47 | 2022-12-23 13:48 | 2022-12-24 | 10.2 | 10.2 | 1621.8 |  | 0 | 160 | 159 | "Lack of fuel (water from rivers or lakes, coal mines, gas lines, etc) where the operator is not in control of contracts, supply lines, or delivery of fuels" | FX00Low fuel gas supply pressure from transport company to the plant.
TC6 | D1 | 103 | 9130 |  | 2022-12-25 16:00 | 2022-12-23 13:48 | 2022-12-24 | 10.2 | 3.8888 | 618.3113 |  | 99 | 160 | 159 | "Lack of fuel (water from rivers or lakes, coal mines, gas lines, etc) where the operator is not in control of contracts, supply lines, or delivery of fuels" | FX00Low fuel gas supply pressure from transport company to the plant.
TC7 | D1 | 137 | 9130 |  | 2022-12-25 16:00 | 2022-12-23 13:48 | 2022-12-24 | 10.2 | 4.7175 | 750.0825 |  | 86 | 160 | 159 | "Lack of fuel (water from rivers or lakes, coal mines, gas lines, etc) where the operator is not in control of contracts, supply lines, or delivery of fuels" | FX00Low fuel gas supply pressure from transport company to the plant.
TC8 | D1 | 201 | 9130 |  | 2022-12-25 16:00 | 2022-12-23 13:48 | 2022-12-24 | 10.2 | 4.335 | 689.265 |  | 92 | 160 | 159 | "Lack of fuel (water from rivers or lakes, coal mines, gas lines, etc) where the operator is not in control of contracts, supply lines, or delivery of fuels" | FX00Low fuel gas supply pressure from transport company to the plant.
TC9 | D1 | 142 | 9130 |  | 2022-12-25 08:39 | 2022-12-23 13:48 | 2022-12-24 | 10.2 | 4.845 | 770.355 |  | 84 | 160 | 159 | "Lack of fuel (water from rivers or lakes, coal mines, gas lines, etc) where the operator is not in control of contracts, supply lines, or delivery of fuels" | FX00Low fuel gas supply pressure from transport company to the plant.
[10 empty] | 12/23/2022 MWH Lost | 2022 Daily Average MWH Lost |  | Cold weather | Gas Press
[9 empty] | Including Gas press | 13383.2241 | 7863.7648 |  | 11.28% | 48.7%
[9 empty] | Excluding Gas press | 6865.1525 | 7863.7648
12/23/2022 MWH Lost
[9 empty] | All Events | 27074.652 |  |  | % of Forced Outages
[13 empty] | Coal | 13.4%
[13 empty] | Gas | 86.6%