## Outages
KPSC Case No. 2023-00008
KPSC's Post Hearing Data Requests
Dated February 29, 2024
Item No. 14
Unit Name | Start Date | End Date | Event Type* | Description of Outage Reason / Work Performed
Big Sandy 1 | 2020-09-12 05:54 | 2020-11-02 15:39 | PO | General Boiler inspect and repair, High Energy Piping, Nat Gas Valve , Double Flow LP Turbine & Generator Field Inspections
Rockport 1 | 2020-09-24 14:00 | 2020-11-05 23:37 | PO | Planned Outage. Start date delayed due to Forced Outage ISO#1472800
Mitchell 1 | 2020-10-03 04:37 | 2020-11-22 20:38 | PO | for #11 ID Fan Regulating Hub Replacement. Boiler inspect and repair, and Precipitator inspect and repair.
Rockport 1 | 2020-11-06 01:19 | 2020-11-06 02:34 | FO | Wet Coal Issues - Start Up Delay
Big Sandy 1 | 2020-11-12 02:39 | 2020-11-16 12:25 | MO | SCR Fall on BS2, North Hydrogen Cooling Water pump repairs, Boiler inspect and repair. Boiler Hydro, EHC System inspect and repair.
Rockport 1 | 2020-11-13 02:48 | 2020-12-18 17:30 | MO | Boiler, Precipitator and Auxiliary Equipment Work
Rockport 2 | 2020-11-21 01:50 | 2020-12-04 23:00 | MO | Boiler Ash Removal, Boiler Inspection, RMO-1 Circ Water Valve, #2 Turbine Intercept valve investigation, HP Condenser Leak Repair.
Big Sandy 1 | 2020-11-25 00:52 | 2020-11-29 06:50 | MO | Boiler inspect and repair, Boiler Hydro, West Circulating Water Discharge Valve inspect and repair , Clean Circulating Water Screens on the Condenser.
Rockport 2 | 2020-12-04 23:00 | 2020-12-17 16:42 | MO | Inspect and repair HP Turbine Control Valve "A" and #2 Gas Fan control damper
Mitchell 1 | 2020-12-07 07:00 | 2020-12-16 20:30 | MO | Uninterruptible Power Supply (UPS) Inverters rebuild
Big Sandy 1 | 2020-12-11 01:02 | 2020-12-16 13:45 | MO | Repair Turbine Oil Cooling Water leak, #1 West Transformer, and RV-1 & BFPT Governor Valve Reheat Steam Temperature Thermocouple
Big Sandy 1 | 2020-12-22 00:37 | 2020-12-26 07:00 | MO | Boiler inspect and repair and HP Heater Shell vent leak repairs
Rockport 1 | 2021-01-05 | 2021-01-14 23:12 | FO | HP Turbine Eccentricity Issues while on Turning Gear.
Mitchell 2 | 2021-01-12 07:00 | 2021-01-19 | MO | to inspect ID Fan Hubs, inspect and repair FMO-202, and replace #21 Clinker Grinder
Big Sandy 1 | 2021-01-13 00:45 | 2021-01-22 14:16 | MO | Boiler inspect and repair, Aux Boiler Feedpump inspect and repair.
Rockport 1 | 2021-01-15 05:24 | 2021-01-30 07:04 | FO | HP Turbine "C" Stop Valve inspection for leak through.
Mitchell 1 | 2021-01-23 | 2021-02-04 23:55 | MO | Inspect and repair #11 turbine bearing, inspect and repair 16 pulv, inspect boiler for slag due to HS burn, and repair condenser leak, boiler hydro and air test.
Mitchell 2 | 2021-02-01 10:09 | 2021-02-10 12:00 | FO | An approximately 75' of Unit 2 stack liner drain header failed and fell to the bottom of the stack. This failure occurred at elevation 250'
Mitchell 1 | 2021-02-06 15:45 | 2021-02-08 11:00 | FO | Turbine lift pump had cracked fitting
Mitchell 1 | 2021-02-09 00:31 | 2021-02-11 21:00 | FO | URV Control Valve Issue
Mitchell 2 | 2021-02-10 12:00 | 2021-02-11 19:36 | FO | The Aux Boiler is not available to start this unit
Mitchell 2 | 2021-02-12 14:05 | 2021-02-13 03:50 | FO | Low PH in cooling tower
Mitchell 1 | 2021-02-12 15:35 | 2021-02-13 21:36 | FO | ID fan trip during startup.
Mitchell 2 | 2021-02-13 06:41 | 2021-02-13 08:35 | FO | Unable to start while unit 1 is in start up. (unit has DA Award)
Rockport 2 | 2021-02-16 18:59 | 2021-02-17 04:25 | FO | Special Protection System (SPS) Emergency Unit Trip (EUT) caused by external issues on the transmission system creating a load loss potential on the Rockport to Jefferson 765kv line.
Big Sandy 1 | 2021-02-20 00:44 | 2021-02-26 15:33 | MO | Boiler inspect and repair, repair Nitrogen Supply leak on the West GSU, clean Cooling Tower Inlet Screens, repack Drum Blowdown Valve, replace Hydrogen Supply Regulator, Left BFP Governor Valve Steam leak inspect and repair, repair Hand shutoff on HP Heater Vents and River Makeup Building Switchgear inspect and repair.
Rockport 2 | 2021-02-23 12:00 | 2021-03-01 04:10 | MO | Boiler inspect and repair, Ash inspection, Oil Lighter cleaning and Feedwater Motor Operated Valve (FMO-2) inspect and repair.
Mitchell 1 | 2021-02-27 15:42 | 2021-03-01 | FO | Side wall Tube Leak
Mitchell 1 | 2021-03-01 | 2021-03-07 17:00 | MO | Sidewall Tube Leak.
Big Sandy 1 | 2021-03-02 | 2021-03-04 14:00 | MO | Boiler Outlet Duct inspect and repair
Rockport 2 | 2021-03-06 02:39 | 2021-03-20 18:45 | MO | Boiler inspect and repair, Ash Removal, Hydro & RSH/SSH Air Test and to install SCR Heaters.
Mitchell 2 | 2021-03-06 04:43 | 2021-04-26 02:19 | PO | Planned Outage
Rockport 1 | 2021-03-07 00:32 | 2021-03-26 19:19 | MO | Remove and inspect HP Turbine Bearings 2/2A and 1/1A, repair Turbine Bearing #3 oil leak, repair Air Oil Filter Housing Leak, replace Turbine Bearing Filters, to repair Boiler Safety Valve, and replace Precipitator 13.8 Kv Cable
Mitchell 1 | 2021-03-07 17:00 | 2021-03-23 10:33 | FO | turbine vibration
Rockport 1 | 2021-04-05 | 2021-04-15 23:00 | MO | To inspect and repair multiple tube leaks in the # 2 Auxiliary Boiler and conduct hydros, remove Safety Valves for offsite repair and install new FD Fan Damper Drives on #1 & #2 Auxiliary Boilers.
Rockport 2 | 2021-04-05 | 2021-04-15 23:00 | MO | To inspect and repair multiple tube leaks in the # 2 Auxiliary Boiler and conduct hydros, remove Safety Valves for offsite repair and install new FD Fan Damper Drives on #1 & #2 Auxiliary Boilers.
Mitchell 1 | 2021-04-09 20:29 | 2021-06-05 15:00 | FO | GSU Phase 1 failed due to a core ground, installed and commisioned system spare.
Big Sandy 1 | 2021-04-10 01:50 | 2021-05-08 07:00 | PO | Planned Outage to replace #1315667
Rockport 2 | 2021-04-15 23:00 | 2021-06-01 16:00 | MO | DSI Injection System piping upgrade.
Big Sandy 1 | 2021-05-28 12:00 | 2021-06-02 14:34 | MO | Repair steam leak under HP Turbine and to inspect East Air Heater Bull Gear
Mitchell 1 | 2021-06-05 15:00 | 2021-06-06 19:32 | FO | Leak on East H2 seal oil cooler
Rockport 2 | 2021-06-15 13:51 | 2021-06-23 19:21 | MO | Boiler inspect and repair, Ash Removal, Hydro & RSH/SSH Air Test and to install SCR Heaters.
Big Sandy 1 | 2021-06-22 06:00 | 2021-06-28 | MO | Boiler and governor valve inspection
Mitchell 2 | 2021-06-24 | 2021-06-26 | MO | Boiler Hydro, inspect and repair
Mitchell 2 | 2021-06-26 | 2021-07-04 04:15 | MO | to repair Precipitator Inlet Duct and internal inspection, drain FGD Absorber to repair an Agitator Seal and level probe B"
Big Sandy 1 | 2021-06-28 | 2021-07-01 | FO | Water wall tube leak repair
Big Sandy 1 | 2021-07-01 | 2021-07-04 21:13 | MO | to repair and replace Waterwall tubes on rear wall. X-rays show indications that will require replacement. Scaffold is already in place for current repairs. Replace gasket on Reheat isolation device.
Mitchell 1 | 2021-07-16 02:14 | 2021-07-23 23:01 | MO | Repair 11 ID Fan Pitch Blade Operator, install 11A Circulating Water Pump, Boiler inspect and repair.
Rockport 1 | 2021-07-18 02:50 | 2021-07-19 11:34 | MO | Repair Boiler Ash Hopper door
Rockport 1 | 2021-07-30 03:14 | 2021-08-05 23:21 | MO | Boiler inspect and repair
Big Sandy 1 | 2021-07-31 | 2021-08-07 07:00 | MO | Boiler inspect and repair
Mitchell 1 | 2021-08-03 21:40 | 2021-08-08 21:28 | FO | Tube Leak
Big Sandy 1 | 2021-08-14 00:40 | 2021-08-21 06:51 | MO | Boiler inspect and repair, clean the Main and Auxiliary Condensers and service the East and West Air Compressors.
Rockport 1 | 2021-08-19 05:30 | 2021-08-20 14:13 | FO | 11C Auxiliary Transformer Overall Differential Trip
Rockport 1 | 2021-08-21 | 2021-08-25 11:20 | MO | Repair Ash Hopper Door #223, Boiler inspect and repair, Boiler Duct Ash removal, Clean Circ. Water Pump Screens
Mitchell 1 | 2021-08-23 18:18 | 2021-09-01 19:58 | FO | Tube Leak
Big Sandy 1 | 2021-08-29 | 2021-09-04 07:00 | MO | to repair steam leak on lower left Reheat Line
Rockport 1 | 2021-08-30 05:52 | 2021-09-11 | MO | Boiler inspect and repair and duct ash removal; 13.8 Kv Transformer 11C inspect and repair; Pulverizer repairs
Mitchell 2 | 2021-09-04 01:54 | 2021-09-13 02:29 | MO | Repair 22 ID fan pitch blade issue. Patch leaks in precipitator duct. Boiler upper fill valve repair Boiler Hydro inspect and repair.
Rockport 2 | 2021-09-07 04:41 | 2021-10-09 | MO | Boiler inspect and repair, boiler duct ash removal, deslag boiler, generator stator tank hydrogen leak repair, #10 pulverizer tempering air and fuel output damper repair, #4 clinker grinder repair, economizer ash hopper repairs.
Rockport 1 | 2021-09-11 | 2021-12-15 14:00 | PO | High Energy Piping Inspection on RH Seamed Weld piping, High Pressure Turbine Stop Valve and Control Valve 1 through 4 rebuild, ReHeat Stop Valve and Intercept Valve #2 and #3 rebuild, BFP Element Replacement, SCR Catalyst Layer #2 Replacement, Recirc Gas Fan Repairs.
Mitchell 1 | 2021-09-16 02:35 | 2021-09-21 | FO | Tube Leak
Mitchell 1 | 2021-09-21 10:46 | 2021-09-23 08:44 | FO | Steam leak.
Big Sandy 1 | 2021-09-23 01:45 | 2021-10-08 22:00 | MO | Boiler inspect and repair, repair steam leak between RV-309 and the Lower Right RH steam line, repair #5 North HP Heater leak.
Mitchell 1 | 2021-09-27 16:55 | 2021-10-02 09:30 | FO | Loss of Air Heater
Mitchell 1 | 2021-10-05 22:37 | 2021-10-06 18:50 | FO | Under excitation limiter failed due to exciter tuning parameter.
Mitchell 1 | 2021-10-08 | 2021-10-08 01:46 | MO | Boiler inspect and repair; FGD repairs; ID Fan Pilot Valve inspections.
Mitchell 1 | 2021-10-08 01:46 | 2021-10-08 08:17 | MO | Boiler inspect and repair; FGD repairs; ID Fan Pilot Valve inspections.
Mitchell 1 | 2021-10-08 08:17 | 2021-10-08 08:27 | MO | Boiler inspect and repair; FGD repairs; ID Fan Pilot Valve inspections.
Mitchell 1 | 2021-10-08 08:27 | 2021-10-08 08:28 | MO | Boiler inspect and repair; FGD repairs; ID Fan Pilot Valve inspections.
Mitchell 1 | 2021-10-08 08:28 | 2021-10-08 08:33 | MO | Boiler inspect and repair; FGD repairs; ID Fan Pilot Valve inspections.
Mitchell 1 | 2021-10-08 08:33 | 2021-10-08 08:35 | MO | Boiler inspect and repair; FGD repairs; ID Fan Pilot Valve inspections.
Mitchell 1 | 2021-10-08 08:35 | 2021-10-16 | MO | Boiler inspect and repair; FGD repairs; ID Fan Pilot Valve inspections.
Rockport 2 | 2021-10-09 | 2021-11-30 14:50 | PO | Boiler inspect and repair.
Big Sandy 1 | 2021-10-09 22:00 | 2021-12-22 07:47 | PO | boiler inspect and repair, boiler inspect and repair, Turbine Exhaust High Energy Piping (HEP) inspections, Boiler corrosion fatigue inspections, Main and Aux Condenser eddy current testing, and Cooling Tower repairs.
Mitchell 1 | 2021-10-16 | 2021-12-09 13:31 | PO | Boiler inspect and repair, BOP repairs, SCR Catalyst #4 layer replacement, Boiler Feed Pump Element replacement.
Mitchell 2 | 2021-10-22 | 2021-11-06 09:54 | MO | Boiler inspect and repair, UMO-803 inspect and repair, Dry Fly Ash repairs, FGD repairs, FMO-101 inspect and repair, #1 Control Valve EHC line inspect and repair.
Mitchell 2 | 2021-11-13 07:44 | 2021-11-15 01:00 | FO | Steam Lead Drain Leak
Mitchell 2 | 2021-11-30 11:30 | 2021-12-02 05:38 | FO | Valve issue. Packing blew out on FRV-101(Main Steam Attemperator)
Mitchell 2 | 2021-12-04 08:00 | 2021-12-05 10:19 | FO | UMO-1 packing leak (super heater bypass line)
Mitchell 1 | 2021-12-19 07:00 | 2021-12-23 08:32 | MO | to dewater cooling tower and install 11B Circulating Water Pump
Mitchell 2 | 2021-12-22 00:18 | 2021-12-22 16:18 | FO | Reason Unknown. #1 Control valve LVDT positioner arm broke causing #1 control valve to close and become inoperable
Big Sandy 1 | 2022-01-19 03:11 | 2022-01-19 22:01 | FO | Reason Unknown - Deaerator level went high from RV 101
Rockport 1 | 2022-01-21 03:02 | 2022-02-06 21:57 | FO | Broken Pipe Hanger on Economizer Inlet - FWH-33 3 inch threaded support rod failed due to cyclic fatigue.
Big Sandy 1 | 2022-02-10 00:25 | 2022-02-18 15:00 | MO | Boiler inspect and repair, Vibration Probe inspect and repair, RV-101 (Hotwell level control) repair, RV-5 (Start-up Steam Attemperator Valve) inspect and repair, Nash Vacuum Pump inspect and repair, #5 HP Heater Feedwater Header leak repair.
Rockport 2 | 2022-02-10 08:33 | 2022-02-23 17:47 | MO | Boiler inspect and repair, Aux. Turbine Lube Oil Pump repair, Ductwork cleaning, Boiler cleaning.
Mitchell 2 | 2022-02-20 19:45 | 2022-03-26 05:00 | MO | Boiler inspect and repair, Hydro test, Precipitator inspect and repair, Roof Outlet Header SV-54 replacement, Deaerator leak repair, Drain FGD Absorber to replace 2H Agitator Seal, FGD Absorber Inlet Duct repairs, repair RH Attemperator Block Valves FMO-201 and 202 (Water Induction Protection Valves).
Big Sandy 1 | 2022-02-22 00:58 | 2022-02-27 11:55 | MO | Requesting a Maintenance Outage until 2-27-2022 @1600 for Boiler inspection, Drum door repairs, BFPT Y vibration probe repair, Clean cooling tower screens, Nash pump level float repair, Circulating water vent replacement.
Rockport 1 | 2022-03-01 14:58 | 2022-03-11 18:00 | MO | Ash survey, Boiler inspect and repair, Boiler hydro, Boiler-deslag, water leak repairs on turbine room Sump Discharge Header, Fire system header leak repairs, Bottom Ash Re-circ line repair, and Main Condenser inspect and repair / tube sheet.
Big Sandy 1 | 2022-03-17 | 2022-03-27 12:00 | MO | Boiler inspect and repair, State Drum inspection, BFPT 2Y vibration probe repair, BFPT Gasket replacement on Duplex Strainer, Boiler Penthouse inspection
Mitchell 1 | 2022-03-24 13:00 | 2022-03-27 03:41 | FO | Aux. Boiler O/S for inlet cone repairs
Mitchell 1 | 2022-03-27 11:00 | 2022-03-29 16:30 | FO | #16 Pulverizer Primary Air Ductwork failed.
Big Sandy 1 | 2022-03-30 01:27 | 2022-04-05 06:56 | MO | Boiler inspection
Rockport 1 | 2022-04-03 03:40 | 2022-05-14 | MO | Stress cracking on LP Turbine Blades of similar turbines in fleet, safety recommendation from GE.
Big Sandy 1 | 2022-04-06 04:42 | 2022-04-08 16:00 | FO | condenser leak.
Big Sandy 1 | 2022-04-08 16:00 | 2022-04-14 13:40 | MO | Drum door repairs
Mitchell 1 | 2022-04-13 17:24 | 2022-04-14 14:25 | FO | Extreme low deaerator alarm due to CRV-301 level control valve.
Mitchell 1 | 2022-04-14 14:26 | 2022-04-19 23:00 | MO | Deaerator Level control valve inspect and repair; Boiler casing air test; Boiler inspect and repair; Repair EHC leak on Reheat stop valve; Main Turbine 1st Reheat and HP Exhaust Steam Leads.
Mitchell 2 | 2022-04-15 16:03 | 2022-04-16 05:07 | FO | During Pressurization, Super heater bypass valves failed to respond causing the unit to trip on sub critical pressure.
Rockport 1 | 2022-05-14 | 2022-06-09 11:58 | PO | Boiler inspect and repair, Ash cleaning in Boiler and SCR, Misc. Valve repairs, Deslag.
Big Sandy 1 | 2022-05-24 07:00 | 2022-05-28 16:00 | MO | Boiler inspect and repair; Deaerator Positive Closing Check Valve repairs; Inspect 2Y vibration pickup on BFPT; Repair Drip Pot drain line to BFPT; Replace Seal on South Positive closing check valve; Inspect Aux Condenser Water Boxes.
Big Sandy 1 | 2022-06-02 07:00 | 2022-06-05 16:00 | MO | Boiler inspect and repair, BFPT 2Y Vibration Probe inspect and repair, RV-101 inspect and repair, 5N HP Heater leak repair, Turbine Valve Trip Logic inspect and repair, Stroke RV-910, Re-pack East Circulating Water Pump, North Heater Drain Pump coupling alignment check.
Mitchell 2 | 2022-06-08 | 2022-06-13 02:00 | MO | Boiler inspection
Rockport 2 | 2022-06-11 03:04 | 2022-06-19 23:59 | MO | Clean SCR Reactors due to Furnace pressure. Removal of ash from duct work, Replace DSI desiccant wheels, NERC relays, MISC. Coal and steam piping repairs, Bottom ash pump replacement.
Rockport 2 | 2022-06-19 23:59 | 2022-06-25 | FO | Clean SCR Reactors due to furnace pressure, removal of ash from duct work, replace DSI desiccant wheels, NERC relays inspect and repair, misc. coal and steam piping repairs, Bottom Ash Pump replacement.
Mitchell 2 | 2022-06-25 | 2022-07-02 14:34 | MO | Repair leaks
Rockport 2 | 2022-06-25 | 2022-06-27 19:36 | MO | Boiler Deslag, Superheat section.
Mitchell 1 | 2022-06-27 03:07 | 2022-07-05 02:00 | FO | Economizer tube leak
Rockport 2 | 2022-06-30 19:03 | 2022-07-14 09:44 | FO | Unit was removed from service due to excessive water loss in the steam generator. Tube leaks were identified and repaired in the secondary superheater section.
Big Sandy 1 | 2022-07-03 07:00 | 2022-07-09 14:00 | MO | Boiler inspect and repair, #2 Governor Valve - replace Servo, Lower Right RH Stop/Intercept Valve LVDT replacement, 5N Heater leak repair, West Air Compressor Oil Cooler - clean and replace Oil Pump, Aux Condenser Tube Sheet cleaning.
Mitchell 1 | 2022-07-05 05:34 | 2022-07-06 04:00 | FO | Possible leak in HP steam line
Mitchell 2 | 2022-07-11 15:00 | 2022-07-11 22:47 | FO | Reason Unknown
Mitchell 2 | 2022-07-16 03:33 | 2022-07-24 00:31 | MO | #21 ID Fan Thrust Bearing and Radial Bearing
Big Sandy 1 | 2022-07-26 07:00 | 2022-07-30 16:00 | MO | to troubleshoot and repair Governor Valve #1 and #2, RV-101; Boiler inspect and repair; West Condensate Booster Pump Mechanical Seal Repair; Measure EHC Hoses for fall outage repair; Turbine Room Crane repair
Rockport 1 | 2022-08-14 07:37 | 2022-08-21 | MO | Repair steam leak on high pressure steam valve URV-2 - boiler pressure regulating valve.
Big Sandy 1 | 2022-08-15 | 2022-08-17 08:00 | MO | Boiler inspect and repair, North Gland Seal leak Off Exhauster inspect and repair, RV-1003 (Low Pressure Steam Seal Regulator) positioner replacement.
Big Sandy 1 | 2022-08-27 | 2022-09-03 08:21 | MO | Remove 600V Feed (both A and B Bus) for measurements and to complete last stage blade inspection of the Boiler Feedpump Turbine and Main Turbine Double Flow Low Pressure Turbine Section.
Rockport 1 | 2022-09-03 | 2022-09-10 | MO | Pre-Planned Outage prep work, Boiler explosive de-slag, SCR cleaning.
Rockport 2 | 2022-09-03 04:40 | 2022-09-10 | MO | Pre-Planned Outage prep work, Boiler explosive de-slag, SCR cleaning.
Big Sandy 1 | 2022-09-08 | 2022-09-10 | MO | Pre-Planned Outage preparation.
Big Sandy 1 | 2022-09-10 | 2023-01-16 11:47 | PO | Boiler inspect and repair, Generator Field Out inspection/possible rewedge, Turbine Valve inspect and repair, Corrosion Fatigue inspect and repair, Cooling Tower inspect and repair, ReHeat Attemperator inspect and repair, Gas valve inspect and repair, FD Fan and Motor inspect and repair, High Energy Piping (HEP) inspect and repair, Flow Accelerated Corrosion (FAC) inspect and repair, Core Loop testing.
Mitchell 2 | 2022-09-10 | 2022-12-16 14:25 | PO | Boiler inspect and repair, Cooling Tower inspect and repair, Low Pressure Turbine A"&"B" Valve replacement
Rockport 2 | 2022-09-10 | 2022-11-20 19:00 | PO | Boiler inspect and repair, LP Turbine #3 and #4 Rotor replacement, SCR cleaning, BFP Rotor and Element replacement, BFP Control and Stop Valve inspect and repair, HP Turbine Control Valve inspect and repair, HP Generator Field in place inspect and repair, High Energy Piping assessment and inspect and repair, Coal Silo inspect and repair, Precipitator inspect and repair.
Rockport 1 | 2022-09-18 | 2022-10-09 | MO | Pre-Planned Outage work, Low Pressure Turbine disassembly.
Mitchell 1 | 2022-09-24 | 2022-10-08 | MO | Repair feed pump turbine steam supply regulating valve.
Mitchell 1 | 2022-10-08 | 2022-11-19 17:32 | PO | Boiler inspect and repair, Precip inspect and repair, Pulverizer/Feeder MATS inspect and repair, Economizer wash, Replace Precip Transformer power cables, Replace SCR XJ s 14,15 and 115, Replace Exit Duct XJ FGX-71009, Water Cannon upgrades, Ovation Evergreen upgrade, Inter-lock testing, HE Piping inspect and repair.
Rockport 1 | 2022-10-09 | 2022-11-03 16:30 | PO | Boiler inspect and repair, #2 & #4 LP Turbine inspect and repair and L-0 Blade removal, SCR cleaning.
Rockport 1 | 2022-11-16 02:29 | 2022-11-16 06:27 | FO | Start Failure - unable to keep the HP field breaker closed
Mitchell 1 | 2022-11-29 11:45 | 2022-11-29 18:03 | FO | Unable to get firing permissives.
Rockport 2 | 2022-11-29 12:40 | 2022-11-29 12:52 | FO | Valve issues
Rockport 2 | 2022-11-29 12:52 | 2022-12-02 07:39 | FO | Isolation Valves on Air Sweeps in SCR
Mitchell 1 | 2022-12-03 01:47 | 2022-12-08 09:18 | MO | Economizer tube leak repair
Mitchell 1 | 2022-12-08 11:45 | 2022-12-09 | FO | PH Issues
Mitchell 1 | 2022-12-09 | 2022-12-10 08:01 | FO | due to Urea from Hydrolyzer system entering the Condensate Return System. Samples will be collected and tested once the unit cools. Hydrolyzer will need pressurized to search for potential leaks.
Mitchell 1 | 2022-12-10 13:07 | 2022-12-13 16:30 | FO | Due to Primary Superheater Outlet valve . packing blew out. Superheater Bypass Control valve URV 4, controller failed closed due to burned up controller.
Mitchell 1 | 2022-12-14 02:45 | 2022-12-14 19:15 | FO | Start Failure
Mitchell 2 | 2022-12-16 14:52 | 2022-12-16 15:28 | PO | Boiler inspection and repair, Cooling Tower inspection and repair, Low Pressure Turbine A"&"B" Valve replacement
Mitchell 2 | 2022-12-17 14:12 | 2022-12-20 16:08 | FO | A Bus Relay PA Fan
Mitchell 1 | 2022-12-30 | 2023-01-22 17:59 | MO | Boiler inspection and repair, Boiler Hydro, Duct repairs, Clinker Removal, IK Soot Blower Repairs, 12 ID Fan Stall margin probe inspection and repair.
Rockport 2 | 2023-01-04 07:00 | 2023-01-24 18:30 | MO | Boiler inspection and repair, Ash Survey, Vacuum ash and clean Ducts.
Rockport 1 | 2023-01-05 05:13 | 2023-01-23 16:00 | MO | MO- Cable Tray Repairs from #9 coal silo fire/ SCR reactor cleaning
Mitchell 2 | 2023-01-07 | 2023-01-29 19:04 | MO | Precipitator inspection and repair, Balance Shot on LP turbines., Boiler inspection and repair, Duct Repairs.
Big Sandy 1 | 2023-01-14 11:47 | 2023-01-16 | PO | Boiler inspection and repair, Generator Field Out inspection/possible rewedge, Turbine Valve inspection and repair, Corrosion Fatigue inspection and repair, Cooling Tower inspection and repair, ReHeat Attemperator inspection and repair, Gas valve inspection and repair, FD Fan and Motor inspection and repair, High Energy Piping (HEP) inspection and repair, Flow Accelerated Corrosion (FAC) inspection and repair, Core Loop testing.
Rockport 1 | 2023-01-23 16:00 | 2023-01-24 23:52 | FO | FMO -2 Actuator Failure
Mitchell 1 | 2023-01-24 12:09 | 2023-02-03 16:27 | FO | UMO-1 PSO Outlet Valve packing failed.
Big Sandy 1 | 2023-01-29 07:21 | 2023-01-29 16:08 | FO | West Air Heater Upper Guide Bearing elevated vibration.
Big Sandy 1 | 2023-02-09 00:35 | 2023-02-09 14:17 | MO | Request MO for ICE to troubleshoot/repair issue with BFPT Governor Valve controls
Rockport 2 | 2023-02-14 18:00 | 2023-02-17 16:30 | MO | To repair weeper Tube Leak located 14th floor Aperture section of the Boiler; interior leak discovered while conducting Boiler Hydro.
Rockport 1 | 2023-03-11 | 2023-06-06 11:13 | PO | Boiler inspection and repair, HEP inspection and repair, Turbine inspection and repair, Ammonia Safety Valve replacement, SCR Catalyst replacement.
Rockport 2 | 2023-03-11 | 2023-06-09 16:31 | PO | Boiler inspection and repair, Steam Generator cleaning, Vacuum ash, BOP repairs, Ammonia Safety valve replacement, SCR Catalyst replacement, HEP inspection and repair, Stack inspection and repair.
Mitchell 1 | 2023-03-16 01:28 | 2023-03-16 14:53 | MO | Main Steam Lead greylock drain line leak
Mitchell 1 | 2023-03-16 14:53 | 2023-03-21 23:17 | MO | Main Steam Line Above Seat Drain steam leak
Mitchell 2 | 2023-03-23 09:10 | 2023-04-04 14:00 | FO | Feedwater Pump Thrust Bearing Failure
Big Sandy 1 | 2023-04-08 02:25 | 2023-05-13 12:00 | PO | Boiler inspection and repair, 600V Breaker upgrade.
Mitchell 2 | 2023-04-15 | 2023-04-30 14:35 | PO | Boiler inspection and repair, Sicon Conveyor Tail Pulley structural steel repairs, relocation of the #24 River Water feed to FGD in the foundation of the new ash bunker, BOP repairs, dual outage to prep for Fall Outage.
Mitchell 1 | 2023-04-15 04:31 | 2023-05-12 18:00 | PO | Boiler inspection and repair, Precipitator inspection and repair, Sicon Conveyor Tail Pulley structural steel repairs, relocation of the 2#4 River Water feed to FGD in the foundation of the new ash bunker, BOP repairs, dual outage to prep for Fall Outage.
Mitchell 1 | 2023-05-12 18:00 | 2023-05-19 07:25 | FO | Conductivity issues
Mitchell 2 | 2023-05-15 01:27 | 2023-06-01 | MO | Repair #3 Control Valve, Boiler inspection and repair, Boiler Feed Pump #2 Bearing oil leak repairs, FMO 402 (Second RH By-Pass Valve) repairs.
Mitchell 1 | 2023-05-19 11:27 | 2023-05-20 01:57 | FO | The unit tripped when we lost the aux boiler due to the air supply valve from unit 1 being closed. This valve was closed in error while attempting to supply air to unit 2 to restart the air compressors on that unit.
Big Sandy 1 | 2023-05-28 17:34 | 2023-05-28 21:37 | FO | Tripped - reason unknown
Mitchell 2 | 2023-06-01 | 2023-06-08 20:33 | FO | EHC Issues
Big Sandy 1 | 2023-06-13 07:00 | 2023-06-17 07:00 | MO | Request Maintenance Outage from 6-13-2023 0700hrs through 6-17-2023 @ 0700hrs
Mitchell 1 | 2023-06-15 15:12 | 2023-06-23 06:32 | FO | Tube Leak
Rockport 1 | 2023-06-23 19:04 | 2023-06-24 06:18 | FO | Suspect failing control card in 820 system caused a false trip on low steam generator pressure.
Rockport 2 | 2023-06-25 17:35 | 2023-06-27 01:04 | FO | Low Main Steam pressure.
Rockport 1 | 2023-07-02 12:10 | 2023-07-21 20:00 | FO | Tube leak
Big Sandy 1 | 2023-07-05 12:51 | 2023-07-05 19:51 | FO | unknown
Mitchell 1 | 2023-07-27 09:43 | 2023-08-06 19:30 | FO | Steam Generator Tube Leak
Rockport 2 | 2023-08-03 10:26 | 2023-08-11 16:26 | FO | HP Generator Ground
Rockport 2 | 2023-08-12 21:09 | 2023-08-15 05:34 | FO | RMO104, Cir Water Door Leak.
Rockport 1 | 2023-08-15 15:36 | 2023-08-17 03:44 | FO | #2 Air Heater has high motor amps.
Rockport 1 | 2023-09-09 | 2023-10-30 10:51 | PO | Boiler inspection and repair, LP-1, LP-2 Rotor Replacement, 3rd Layer SCR Catalyst Replacement, Ash Removal, BOP inspection and repair.
Mitchell 1 | 2023-09-09 05:29 | 2023-12-06 05:56 | PO | HP/RH Turbine replacement, LPT A replacement, Cooling Tower inspection and repair, AH Basket inspection and repair, BFPT Stop and Control Valve inspection and repair, ID Fan inspection and repair.
Mitchell 2 | 2023-09-11 01:36 | 2023-11-19 17:33 | PO | Boiler inspection and repair, Chemical Clean, Furnace Wall inspection and repair. Boiler inspection and repair, CCR/ELG Project.
Big Sandy 1 | 2023-09-11 09:09 | 2023-09-11 13:59 | FO | Potential card failure
Big Sandy 1 | 2023-09-16 01:24 | 2023-10-14 09:56 | PO | Boiler inspection and repair, Corrosion Fatigue inspection and repair, Cooling Tower inspection and repair, Furnace Wall inspection and repair.Installing new 600v breakers
Rockport 2 | 2023-11-04 | 2023-11-25 00:15 | PO | Boiler inspection and repair, Ash removal, SCR inspection and repair, BOP inspection and repair.
Big Sandy 1 | 2023-11-22 01:02 | 2023-12-01 10:00 | MO | Boiler inspection and repair, Reheat Isolation Device repair steam leak (this is critical path has to cool), Valve packing at lower stop, West Air Heater Lube Oil pump replacement, Casing Leaks inspection and repair, RV1 rebuild and stroking, ICE Control logic for Steam Flow transmitter. and smoothing suction flow, Misc BOP.
Mitchell 1 | 2023-12-06 15:07 | 2023-12-06 15:44 | PO | HP/RH Turbine replacement, LPT A replacement, Cooling Tower inspection and repair, AH Basket inspection and repair, BFPT Stop and Control Valve inspection and repair, ID Fan inspection and repair.
Mitchell 1 | 2023-12-09 01:36 | 2023-12-16 20:28 | MO | Main and Aux Condenser inspection and repair, Water Box inspections, Generator Hydrogen Cooler inspection and repair.
Mitchell 1 | 2023-12-19 17:16 | 2024-01-28 02:28 | FO | Fire protection valve failure introduced water into the exciter PPT. PPT was repaired by CMS. ISO phase bus duct was repaired and new PPT leads ran to transformer.
Rockport 1 | 2024-01-05 04:00 | 2024-01-05 18:00 | FO | Reheat Turbine #3 Bearing
Rockport 1 | 2024-01-05 18:00 | 2024-01-11 05:25 | FO | Reheat Turbine #3 Bearing
Big Sandy 1 | 2024-01-06 02:32 | 2024-01-12 03:53 | MO | West Economizer Check Valve inspection and repair, RV1 startup and low load Steam Valve inspection and repair, 5 South HP Header leak inspection and repair, Boiler inspection and repair,
Mitchell 2 | 2024-02-10 05:30 | 2024-02-26 09:01 | MO | Boiler inspection and repair, #22 Air Heater Gearbox and Motor inspection and repair, Steam Generator inspection and repair, Ductwork inspection and repair, Secondary Air Flowmeter inspection and repair.
Mitchell 1 | 2024-02-18 13:40 | 2024-02-20 10:07 | FO | Excitation PPT transformer temperature indication failed.
Mitchell 1 | 2024-02-20 10:29 | 2024-02-20 11:28 | FO | Turbine Vibration on T10 bearing.
*Event Type
FO | Forced Outage
MO | Maintenance Outage
PO | Planned Outage