## 5.1.22 - 10.31.22 Outges
KPSC Case No. 2023-00008
AG-KIUC's Second set of Data Requests
Dated November 16, 2023
Item No. 1
Page 1 of 1
Unit Name | Event Type | Start Date | End Date | Description
Big Sandy 1 | PO | 2022-09-10 | 2023-01-14 11:47 | Boiler inspection repair, Generator Field Out inspection/possible rewedge, Turbine Valve inspection repair, Corrosion Fatigue inspection repair, Cooling Tower inspection repair, ReHeat Attemperator inspection repair, Gas valve inspection repair, FD Fan and Motor inspection repair, High Energy Piping (HEP) inspection repair, Flow Accelerated Corrosion (FAC) inspection repair, Core Loop testing.
Mitchell 1 | MO | 2022-09-24 | 2022-10-08 | Repair feed pump turbine steam supply regulating valve.
Mitchell 1 | PO | 2022-10-08 | 2022-11-19 17:32 | Boiler inspection repair, Precip inspection repair, Pulverizer/Feeder MATS inspection repair, Economizer wash, Replace Precip Transformer power cables, Replace SCR XJ s 14,15 and 115, Replace Exit Duct XJ FGX-71009, Water Cannon upgrades, Ovation Evergreen upgrade, Inter-lock testing, HE Piping inspection repair.
Mitchell 2 | PO | 2022-09-10 | 2022-12-16 14:25 | Boiler inspection repair, Cooling Tower inspection repair, Low Pressure Turbine A"&"B" Valve replacement
Rockport 1 | MO | 2022-09-18 | 2022-10-09 | Pre-Planned Outage work, LP Turbine disassembly.
Rockport 1 | PO | 2022-10-09 | 2022-11-03 16:30 | Outage to address OEM (Alstom/GE) identified potential catastrophic turbine failure associated with design flaw in the DS52T L-0 blading. After further review and additional understanding of the failure mechanism out of concern for employee and equipment safety it was determined to crop the remaining last stag blades on LP Turbines 2 and 4. Additional Planned Outage work completed included; general boiler inspection and repair, ash cleaning in boiler and SCR, and steam valve inspection and repairs.
Rockport 2 | PO | 2022-09-10 | 2022-11-20 19:00 | Planned Outage work included; general boiler inspection and repair, LP Turbine 3&4 Rotor replacement, SCR cleaning, Boiler Feed Pump (BFP) element replacement, BFP Control and Stop Valve inspection and repair, HP Turbine Control Valve inspection and repair, and High Energy Piping (HEP) assessment and repair.