## Outages
KPSC Case No. 2023-00008
AG-KIUC's Second Set of Data Requests
Dated November 16, 2023
Item No. 3
Attachment 1
Page 1 of 1
Unit Name | Planned Start Date* | Planned End Date* | Actual Start Date | Actual End Date | Event Type** | Description of Outage Reason / Work Performed | Detail Regarding Outages With Changes in Start and End Dates
Big Sandy 1 | 2020-11-11 | 2020-11-16 | 2020-11-12 02:39 | 2020-11-16 12:25 | MO | SCR Fall on BS2, North Hydrogen Cooling Water pump repairs, Boiler inspect and repair. Boiler Hydro, EHC System inspect and repair. | The outage start date was delayed by one day due to the demolition team not being ready to start at the original start time.
Big Sandy 1 | 2020-09-12 | 2020-10-25 | 2020-09-12 05:54 | 2020-11-02 15:39 | PO | General Boiler inspect and repair, High Energy Piping, Nat Gas Valve , Double Flow LP Turbine & Generator Field Inspections | Required flushing, cleaning, and repeated operation of the main turbine steam admission valves due to debris detected in hydraulic hoses.
Rockport 1 |  |  | 2020-09-24 14:00 | 2020-11-05 23:37 | PO | Planned Outage. Start date delayed due to Forced Outage ISO#1472800
Mitchell 1 | 2020-10-03 | 2020-11-15 | 2020-10-03 04:37 | 2020-11-22 20:38 | PO | for #11 ID Fan Regulating Hub Replacement. Boiler inspect and repair, and Precipitator inspect and repair. | Outage extended to repair a problem with the number 11 induced draft fan regulating hub and actuator.
Rockport 1 |  |  | 2020-11-06 01:19 | 2020-11-06 02:34 | FO | Wet Coal Issues - Start Up Delay
Rockport 1 |  |  | 2020-11-13 02:48 | 2020-12-18 17:30 | MO | Boiler, Precipitator and Auxiliary Equipment Work
Rockport 2 |  |  | 2020-11-21 01:50 | 2020-12-04 23:00 | MO | Boiler Ash Removal, Boiler Inspection, RMO-1 Circ Water Valve, #2 Turbine Intercept valve investigation, HP Condenser Leak Repair.
Big Sandy 1 |  |  | 2020-11-25 00:52 | 2020-11-29 06:50 | MO | Boiler inspect and repair, Boiler Hydro, West Circulating Water Discharge Valve inspect and repair , Clean Circulating Water Screens on the Condenser.
Rockport 2 |  |  | 2020-12-04 23:00 | 2020-12-17 16:42 | MO | Inspect and repair HP Turbine Control Valve "A" and #2 Gas Fan control damper
Mitchell 1 |  |  | 2020-12-07 07:00 | 2020-12-16 20:30 | MO | Uninterruptible Power Supply (UPS) Inverters rebuild
Big Sandy 1 |  |  | 2020-12-11 01:02 | 2020-12-16 13:45 | MO | Repair Turbine Oil Cooling Water leak, #1 West Transformer, and RV-1 & BFPT Governor Valve Reheat Steam Temperature Thermocouple
Big Sandy 1 |  |  | 2020-12-22 00:37 | 2020-12-26 07:00 | MO | Boiler inspect and repair and HP Heater Shell vent leak repairs
Rockport 1 |  |  | 2021-01-05 | 2021-01-14 23:12 | FO | HP Turbine Eccentricity Issues while on Turning Gear.
Mitchell 2 |  |  | 2021-01-12 07:00 | 2021-01-19 | MO | to inspect ID Fan Hubs, inspect and repair FMO-202, and replace #21 Clinker Grinder
Big Sandy 1 | 2021-01-13 | 2021-01-19 | 2021-01-13 00:45 | 2021-01-22 14:16 | MO | Boiler inspect and repair, Aux Boiler Feedpump inspect and repair. | Outage extended for three days due to debris found in the auxiliary boiler feed pump inlet valve and an inspection to ensure there was not additional debris.
Rockport 1 |  |  | 2021-01-15 05:24 | 2021-01-30 07:04 | FO | HP Turbine "C" Stop Valve inspection for leak through.
Mitchell 1 | 2021-01-23 | 2021-02-01 | 2021-01-23 | 2021-02-04 23:55 | MO | Inspect and repair #11 turbine bearing, inspect and repair 16 pulv, inspect boiler for slag due to HS burn, and repair condenser leak, boiler hydro and air test. | Outage was extended due to difficulties locating and repairing a condenser tube leak.
Mitchell 2 |  |  | 2021-02-01 10:09 | 2021-02-10 12:00 | FO | An approximately 75' of Unit 2 stack liner drain header failed and fell to the bottom of the stack. This failure occurred at elevation 250'
Mitchell 1 |  |  | 2021-02-06 15:45 | 2021-02-08 11:00 | FO | Turbine lift pump had cracked fitting
Mitchell 1 |  |  | 2021-02-09 00:31 | 2021-02-11 21:00 | FO | URB Control Valve Issue
Mitchell 2 |  |  | 2021-02-10 12:00 | 2021-02-11 19:36 | FO | The Aux Boiler is not available to start this unit
Mitchell 2 |  |  | 2021-02-12 14:05 | 2021-02-13 03:50 | FO | Low PH in cooling tower
Mitchell 1 |  |  | 2021-02-12 15:35 | 2021-02-13 21:36 | FO | ID fan trip during startup.
Mitchell 2 |  |  | 2021-02-13 06:41 | 2021-02-13 08:35 | FO | Unable to start while unit i is in start up. (unit has DA Award)
Rockport 2 |  |  | 2021-02-16 18:59 | 2021-02-17 04:25 | FO | Special Protection System (SPS) Emergency Unit Trip (EUT) caused by external issues on the transmission system creating a load loss potential on the Rockport to Jefferson 765kv line.
Big Sandy 1 |  |  | 2021-02-20 00:44 | 2021-02-26 15:33 | MO | Boiler inspect and repair, repair Nitrogen Supply leak on the West GSU, clean Cooling Tower Inlet Screens, repack Drum Blowdown Valve, replace Hydrogen Supply Regulator, Left BFP Governor Valve Steam leak inspect and repair, repair Hand shutoff on HP Heater Vents and River Makeup Building Switchgear inspect and repair.
Rockport 2 |  |  | 2021-02-23 12:00 | 2021-03-01 04:10 | MO | Boiler inspect and repair, Ash inspection, Oil Lighter cleaning and Feedwater Motor Operated Valve (FMO-2) inspect and repair.
Mitchell 1 |  |  | 2021-02-27 15:42 | 2021-03-01 | FO | Side wall Tube Leak
Mitchell 1 |  |  | 2021-03-01 | 2021-03-07 17:00 | MO | Sidewall Tube Leak.
Big Sandy 1 |  |  | 2021-03-02 | 2021-03-04 14:00 | MO | Boiler Outlet Duct inspect and repair
Rockport 2 |  |  | 2021-03-06 02:39 | 2021-03-20 18:45 | MO | Boiler inspect and repair, Ash Removal, Hydro & RSH/SSH Air Test and to install SCR Heaters.
Mitchell 2 |  |  | 2021-03-06 04:43 | 2021-04-26 02:19 | PO | Planned Outage
Rockport 1 |  |  | 2021-03-07 00:32 | 2021-03-26 19:19 | MO | Remove and inspect HP Turbine Bearings 2/2A and 1/1A, repair Turbine Bearing #3 oil leak, repair Air Oil Filter Housing Leak, replace Turbine Bearing Filters, to repair Boiler Safety Valve, and replace Precipitator 13.8 Kv Cable
Mitchell 1 |  |  | 2021-03-07 17:00 | 2021-03-23 10:33 | FO | turbine vibration
Rockport 1 |  |  | 2021-04-05 | 2021-04-15 23:00 | MO | To inspect and repair multiple tube leaks in the # 2 Auxiliary Boiler and conduct hydros, remove Safety Valves for offsite repair and install new FD Fan Damper Drives on #1 & #2 Auxiliary Boilers.
Rockport 2 |  |  | 2021-04-05 | 2021-04-15 23:00 | MO | To inspect and repair multiple tube leaks in the # 2 Auxiliary Boiler and conduct hydros, remove Safety Valves for offsite repair and install new FD Fan Damper Drives on #1 & #2 Auxiliary Boilers.
Mitchell 1 |  |  | 2021-04-09 20:29 | 2021-06-05 15:00 | FO | Unknown at this time
Big Sandy 1 |  |  | 2021-04-10 01:50 | 2021-05-08 07:00 | PO | Planned Outage to replace #1315667
Rockport 2 |  |  | 2021-04-15 23:00 | 2021-06-01 16:00 | MO | DSI Injection System piping upgrade.
Big Sandy 1 |  |  | 2021-05-28 12:00 | 2021-06-02 14:34 | MO | Repair steam leak under HP Turbine and to inspect East Air Heater Bull Gear
Mitchell 1 |  |  | 2021-06-05 15:00 | 2021-06-06 19:32 | FO | Leak on East H2 seal oil cooler
Rockport 2 |  |  | 2021-06-15 13:51 | 2021-06-23 19:21 | MO | Boiler inspect and repair, Ash Removal, Hydro & RSH/SSH Air Test and to install SCR Heaters.
Big Sandy 1 | 2021-06-22 | 2021-06-25 | 2021-06-22 06:00 | 2021-06-28 | MO | Boiler and governor valve inspection | Outage extended to repair two tubes on the boiler rear wall due to a discovered leak.
Mitchell 2 |  |  | 2021-06-24 | 2021-06-26 | MO | Boiler Hydro, inspect and repair
Mitchell 2 | 2021-06-26 | 2021-07-04 | 2021-06-26 | 2021-07-04 04:15 | MO | to repair Precipitator Inlet Duct and internal inspection, drain FGD Absorber to repair an Agitator Seal and level probe B" | Repairs to the electrostatic precipitator inlet structural steel took longer than anticipated.
Big Sandy 1 |  |  | 2021-06-28 | 2021-07-01 | FO | Water wall tube leak repair
Big Sandy 1 | 2021-06-30 | 2021-07-04 | 2021-07-01 | 2021-07-04 21:13 | MO | to repair and replace Waterwall tubes on rear wall. X-rays show indications that will require replacement. Scaffold is already in place for current repairs. Replace gasket on Reheat isolation device. | This outage was extended for five hours for administrative purposes.
Mitchell 1 | 2021-07-16 | 2021-07-22 | 2021-07-16 02:14 | 2021-07-23 23:01 | MO | Repair 11 ID Fan Pitch Blade Operator, install 11A Circulating Water Pump, Boiler inspect and repair. | The extension was due to extensive damaged found with the induced draft fan pitch blade actuator.
Rockport 1 |  |  | 2021-07-18 02:50 | 2021-07-19 11:34 | MO | Repair Boiler Ash Hopper door
Rockport 1 |  |  | 2021-07-30 03:14 | 2021-08-05 23:21 | MO | Boiler inspect and repair
Big Sandy 1 |  |  | 2021-07-31 | 2021-08-07 07:00 | MO | Boiler inspect and repair
Mitchell 1 |  |  | 2021-08-03 21:40 | 2021-08-08 21:28 | FO | Tube Leak
Big Sandy 1 |  |  | 2021-08-14 00:40 | 2021-08-21 06:51 | MO | Boiler inspect and repair, clean the Main and Auxiliary Condensers and service the East and West Air Compressors.
Rockport 1 |  |  | 2021-08-19 05:30 | 2021-08-20 14:13 | FO | 11C Auxiliary Transformer Overall Differential Trip
Rockport 1 |  |  | 2021-08-21 | 2021-08-25 11:20 | MO | Repair Ash Hopper Door #223, Boiler inspect and repair, Boiler Duct Ash removal, Clean Circ. Water Pump Screens
Mitchell 1 |  |  | 2021-08-23 18:18 | 2021-09-01 19:58 | FO | Tube Leak
Big Sandy 1 |  |  | 2021-08-29 | 2021-09-04 07:00 | MO | to repair steam leak on lower left Reheat Line
Rockport 1 |  |  | 2021-08-30 05:52 | 2021-09-11 | MO | Boiler inspect and repair and duct ash removal; 13.8 Kv Transformer 11C inspect and repair; Pulverizer repairs
Mitchell 2 |  |  | 2021-09-04 01:54 | 2021-09-13 02:29 | MO | Repair 22 ID fan pitch blade issue. Patch leaks in precipitator duct. Boiler upper fill valve repair Boiler Hydro inspect and repair.
Rockport 2 |  |  | 2021-09-07 04:41 | 2021-10-09 | MO | Boiler inspect and repair, boiler duct ash removal, deslag boiler, generator stator tank hydrogen leak repair, #10 pulverizer tempering air and fuel output damper repair, #4 clinker grinder repair, economizer ash hopper repairs.
Rockport 1 | 2021-09-11 | 2021-12-05 | 2021-09-11 | 2021-12-15 14:00 | PO | High Energy Piping Inspection on RH Seamed Weld piping, High Pressure Turbine Stop Valve and Control Valve 1 through 4 rebuild, ReHeat Stop Valve and Intercept Valve #2 and #3 rebuild, BFP Element Replacement, SCR Catalyst Layer #2 Replacement, Recirc Gas Fan Repairs. | Outage duration extended to accommodate additional work scope related to the HP Turbine Exciter Sole Plate repairs, High Energy Piping repairs, and Seal Oil System regulating valves.
Mitchell 1 |  |  | 2021-09-16 02:35 | 2021-09-21 | FO | Tube Leak
Mitchell 1 |  |  | 2021-09-21 10:46 | 2021-09-23 08:44 | FO | Steam leak.
Big Sandy 1 | 2021-09-23 | 2021-10-01 | 2021-09-23 01:45 | 2021-10-08 22:00 | MO | Boiler inspect and repair, repair steam leak between RV-309 and the Lower Right RH steam line, repair #5 North HP Heater leak. | Outage extended due to an inspection of the reheat steam piping where are small leak had been repaired. This inspection was done to ensure safety and integrity of the piping.
Mitchell 1 |  |  | 2021-09-27 16:55 | 2021-10-02 09:30 | FO | Loss of Air Heater
Mitchell 1 |  |  | 2021-10-05 22:37 | 2021-10-06 18:50 | FO | Reason Unknown( Under Excitation trip)
Mitchell 1 |  |  | 2021-10-08 | 2021-10-08 01:46 | MO | Boiler inspect and repair; FGD repairs; ID Fan Pilot Valve inspections.
Mitchell 1 |  |  | 2021-10-08 01:46 | 2021-10-08 08:17 | MO | Boiler inspect and repair; FGD repairs; ID Fan Pilot Valve inspections.
Mitchell 1 |  |  | 2021-10-08 08:17 | 2021-10-08 08:27 | MO | Boiler inspect and repair; FGD repairs; ID Fan Pilot Valve inspections.
Mitchell 1 |  |  | 2021-10-08 08:27 | 2021-10-08 08:28 | MO | Boiler inspect and repair; FGD repairs; ID Fan Pilot Valve inspections.
Mitchell 1 |  |  | 2021-10-08 08:28 | 2021-10-08 08:33 | MO | Boiler inspect and repair; FGD repairs; ID Fan Pilot Valve inspections.
Mitchell 1 |  |  | 2021-10-08 08:33 | 2021-10-08 08:35 | MO | Boiler inspect and repair; FGD repairs; ID Fan Pilot Valve inspections.
Mitchell 1 |  |  | 2021-10-08 08:35 | 2021-10-16 | MO | Boiler inspect and repair; FGD repairs; ID Fan Pilot Valve inspections.
Big Sandy 1 | 2021-10-09 | 2021-11-21 | 2021-10-09 22:00 | 2021-12-22 07:47 | PO | boiler inspect and repair, boiler inspect and repair, Turbine Exhaust High Energy Piping (HEP) inspections, Boiler corrosion fatigue inspections, Main and Aux Condenser eddy current testing, and Cooling Tower repairs. | Outage extended due to a section of reheat steam piping that was discovered to need replacement. The new piping was not readily available and a safety plan had to be developed for replacement.
Rockport 2 | 2021-10-09 | 2021-11-28 | 2021-10-09 | 2021-11-30 14:50 | PO | Boiler inspect and repair. | The unit was in startup and then went back into an outage on 11/30/21 @ 14:50 due to a HP Flash Tank door leaking water. The door leak was repaired and the startup continued.
Mitchell 1 | 2021-10-16 | 2021-11-21 | 2021-10-16 | 2021-12-09 13:31 | PO | Boiler inspect and repair, BOP repairs, SCR Catalyst #4 layer replacement, Boiler Feed Pump Element replacement. | This outage was extended due to a significant contractor safety issue that needed to be addressed.
Mitchell 2 | 2021-10-22 | 2021-10-30 | 2021-10-22 | 2021-11-06 09:54 | MO | Boiler inspect and repair, UMO-803 inspect and repair, Dry Fly Ash repairs, FGD repairs, FMO-101 inspect and repair, #1 Control Valve EHC line inspect and repair. | Outage extended due to repairs to a hydraulic line leak on the turbine number 1 control valve being more complicated than expected.
Mitchell 2 |  |  | 2021-11-13 07:44 | 2021-11-15 01:00 | FO | Steam Lead Drain Leak
Mitchell 2 |  |  | 2021-11-30 11:30 | 2021-12-02 05:38 | FO | Valve issue. Packing blew out on FRV-101(Main Steam Attemperator)
Mitchell 2 |  |  | 2021-12-04 08:00 | 2021-12-05 10:19 | FO | UMO-1 packing leak (super heater bypass line)
Mitchell 1 |  |  | 2021-12-19 07:00 | 2021-12-23 08:32 | MO | to dewater cooling tower and install 11B Circulating Water Pump
Mitchell 2 |  |  | 2021-12-22 00:18 | 2021-12-22 16:18 | FO | Reason Unknown. #1 Control valve LVDT positioner arm broke causing #1 control valve to close and become inoperable
Big Sandy 1 |  |  | 2022-01-19 03:11 | 2022-01-19 22:01 | FO | Reason Unknown - Deaerator level went high from RV 101
Rockport 1 |  |  | 2022-01-21 03:02 | 2022-02-06 21:57 | FO | Broken Pipe Hanger on Economizer Inlet - FWH-33 3 inch threaded support rod failed due to cyclic fatigue.
Big Sandy 1 |  |  | 2022-02-10 00:25 | 2022-02-18 15:00 | MO | Boiler inspect and repair, Vibration Probe inspect and repair, RV-101 (Hotwell level control) repair, RV-5 (Start-up Steam Attemperator Valve) inspect and repair, Nash Vacuum Pump inspect and repair, #5 HP Heater Feedwater Header leak repair.
Rockport 2 |  |  | 2022-02-10 08:33 | 2022-02-23 17:47 | MO | Boiler inspect and repair, Aux. Turbine Lube Oil Pump repair, Ductwork cleaning, Boiler cleaning.
Mitchell 2 | 2022-02-20 | 2022-03-06 | 2022-02-20 19:45 | 2022-03-26 05:00 | MO | Boiler inspect and repair, Hydro test, Precipitator inspect and repair, Roof Outlet Header SV-54 replacement, Deaerator leak repair, Drain FGD Absorber to replace 2H Agitator Seal, FGD Absorber Inlet Duct repairs, repair RH Attemperator Block Valves FMO-201 and 202 (Water Induction Protection Valves). | Unexpected pluggage was found in the inlet section of the electrostatic precipitator and took considerable time to remove.
Big Sandy 1 |  |  | 2022-02-22 00:58 | 2022-02-27 11:55 | MO | Requesting a Maintenance Outage until 2-27-2022 @1600 for Boiler inspection, Drum door repairs, BFPT Y vibration probe repair, Clean cooling tower screens, Nash pump level float repair, Circulating water vent replacement.
Rockport 1 |  |  | 2022-03-01 14:58 | 2022-03-11 18:00 | MO | Ash survey, Boiler inspect and repair, Boiler hydro, Boiler-deslag, water leak repairs on turbine room Sump Discharge Header, Fire system header leak repairs, Bottom Ash Re-circ line repair, and Main Condenser inspect and repair / tube sheet.
Big Sandy 1 |  |  | 2022-03-17 | 2022-03-27 12:00 | MO | Boiler inspect and repair, State Drum inspection, BFPT 2Y vibration probe repair, BFPT Gasket replacement on Duplex Strainer, Boiler Penthouse inspection
Mitchell 1 |  |  | 2022-03-24 13:00 | 2022-03-27 03:41 | FO | Aux. Boiler O/S
Mitchell 1 |  |  | 2022-03-27 11:00 | 2022-03-29 16:30 | FO | #16 Pulverizer Primary Air Ductwork failed.
Big Sandy 1 | 2022-03-30 | 2022-04-02 | 2022-03-30 01:27 | 2022-04-05 06:56 | MO | Boiler inspection | Extension of outage was due to a slight leak found in the steam drum doors that needed to be repaired.
Rockport 1 |  |  | 2022-04-03 03:40 | 2022-05-14 | MO | Stress cracking on LP Turbine Blades of similar turbines in fleet, safety recommendation from GE.
Big Sandy 1 |  |  | 2022-04-06 04:42 | 2022-04-08 16:00 | FO | condenser leak.
Big Sandy 1 | 2022-04-08 | 2022-04-12 | 2022-04-08 16:00 | 2022-04-14 13:40 | MO | Drum door repairs | Outage extended to build water inventory for startup following repair of a condenser leak.
Mitchell 1 |  |  | 2022-04-13 17:24 | 2022-04-14 14:25 | FO | Extreme low deaerator alarm
Mitchell 1 | 2022-04-15 | 2022-04-18 | 2022-04-14 14:26 | 2022-04-19 23:00 | MO | Deaerator Level control valve inspect and repair; Boiler casing air test; Boiler inspect and repair; Repair EHC leak on Reheat stop valve; Main Turbine 1st Reheat and HP Exhaust Steam Leads. | The extension of this outage was due to a deaerator control valve needing to be disassembled to repair an unexpected problem.
Mitchell 2 |  |  | 2022-04-15 16:03 | 2022-04-16 05:07 | FO | During Pressurization, Super heater bypass valves failed to respond causing the unit to trip on sub critical pressure.
Rockport 1 | 2022-05-14 | 2022-06-12 | 2022-05-14 | 2022-06-09 11:58 | PO | Boiler inspect and repair, Ash cleaning in Boiler and SCR, Misc. Valve repairs, Deslag. | Unit released early from planned outage due to scheduled Turbine balance program not needed (turbine vibration on start up was within acceptable range).
Big Sandy 1 |  |  | 2022-05-24 07:00 | 2022-05-28 16:00 | MO | Boiler inspect and repair; Deaerator Positive Closing Check Valve repairs; Inspect 2Y vibration pickup on BFPT; Repair Drip Pot drain line to BFPT; Replace Seal on South Positive closing check valve; Inspect Aux Condenser Water Boxes.
Big Sandy 1 |  |  | 2022-06-02 07:00 | 2022-06-05 16:00 | MO | Boiler inspect and repair, BFPT 2Y Vibration Probe inspect and repair, RV-101 inspect and repair, 5N HP Heater leak repair, Turbine Valve Trip Logic inspect and repair, Stroke RV-910, Re-pack East Circulating Water Pump, North Heater Drain Pump coupling alignment check.
Mitchell 2 |  |  | 2022-06-08 | 2022-06-13 02:00 | MO | Boiler inspection
Rockport 2 |  |  | 2022-06-11 03:04 | 2022-06-19 23:59 | MO | Clean SCR Reactors due to Furnace pressure. Removal of ash from duct work, Replace DSI desiccant wheels, NERC relays, MISC. Coal and steam piping repairs, Bottom ash pump replacement.
Rockport 2 |  |  | 2022-06-19 23:59 | 2022-06-25 | FO | Clean SCR Reactors due to furnace pressure, removal of ash from duct work, replace DSI desiccant wheels, NERC relays inspect and repair, misc. coal and steam piping repairs, Bottom Ash Pump replacement.
Mitchell 2 |  |  | 2022-06-25 | 2022-07-02 14:34 | MO | Repair leaks
Rockport 2 |  |  | 2022-06-25 | 2022-06-27 19:36 | MO | Boiler Deslag, Superheat section.
Mitchell 1 |  |  | 2022-06-27 03:07 | 2022-07-05 02:00 | FO | Economizer tube leak
Rockport 2 |  |  | 2022-06-30 19:03 | 2022-07-14 09:44 | FO | Unit was removed from service due to excessive water loss in the steam generator. Tube leaks were identified and repaired in the secondary superheater section.
Big Sandy 1 |  |  | 2022-07-03 07:00 | 2022-07-09 14:00 | MO | Boiler inspect and repair, #2 Governor Valve - replace Servo, Lower Right RH Stop/Intercept Valve LVDT replacement, 5N Heater leak repair, West Air Compressor Oil Cooler - clean and replace Oil Pump, Aux Condenser Tube Sheet cleaning.
Mitchell 1 |  |  | 2022-07-05 05:34 | 2022-07-06 04:00 | FO | Possible leak in HP steam line
Mitchell 2 |  |  | 2022-07-11 15:00 | 2022-07-11 22:47 | FO | Reason Unknown
Mitchell 2 |  |  | 2022-07-16 03:33 | 2022-07-24 00:31 | MO | #21 ID Fan Thrust Bearing and Radial Bearing
Big Sandy 1 |  |  | 2022-07-26 07:00 | 2022-07-30 16:00 | MO | to troubleshoot and repair Governor Valve #1 and #2, RV-101; Boiler inspect and repair; West Condensate Booster Pump Mechanical Seal Repair; Measure EHC Hoses for fall outage repair; Turbine Room Crane repair
Rockport 1 |  |  | 2022-08-14 07:37 | 2022-08-21 | MO | Repair steam leak on high pressure steam valve URV-2 - boiler pressure regulating valve.
Big Sandy 1 | 2022-08-15 | 2022-08-16 | 2022-08-15 | 2022-08-17 08:00 | MO | Boiler inspect and repair, North Gland Seal leak Off Exhauster inspect and repair, RV-1003 (Low Pressure Steam Seal Regulator) positioner replacement. | Outage was extended by one day to complete repairs to the steam seal regulator.
Big Sandy 1 |  |  | 2022-08-27 | 2022-09-03 08:21 | MO | Remove 600V Feed (both A and B Bus) for measurements and to complete last stage blade inspection of the Boiler Feedpump Turbine and Main Turbine Double Flow Low Pressure Turbine Section.
Rockport 1 |  |  | 2022-09-03 | 2022-09-10 | MO | Pre-Planned Outage prep work, Boiler explosive de-slag, SCR cleaning.
Rockport 2 |  |  | 2022-09-03 04:40 | 2022-09-10 | MO | Pre-Planned Outage prep work, Boiler explosive de-slag, SCR cleaning.
Big Sandy 1 |  |  | 2022-09-08 | 2022-09-10 | MO | Pre-Planned Outage preparation.
Big Sandy 1 | 2022-09-10 | 2022-12-04 | 2022-09-10 | 2023-01-16 11:47 | PO | Boiler inspect and repair, Generator Field Out inspection/possible rewedge, Turbine Valve inspect and repair, Corrosion Fatigue inspect and repair, Cooling Tower inspect and repair, ReHeat Attemperator inspect and repair, Gas valve inspect and repair, FD Fan and Motor inspect and repair, High Energy Piping (HEP) inspect and repair, Flow Accelerated Corrosion (FAC) inspect and repair, Core Loop testing. | Outage was extended several times due to: a required generator re-wedge and corresponding loop testing to endure long-term reliability; replacement of a generator rotor retaining ring; repair of a leak on a hydrogen seal housing on the exciter end; and to repair a condenser leak to address water chemistry issues sdetected during a unit start-up attempt.
Rockport 2 |  |  | 2022-09-10 | 2022-11-20 19:00 | PO | Boiler inspect and repair, LP Turbine #3 and #4 Rotor replacement, SCR cleaning, BFP Rotor and Element replacement, BFP Control and Stop Valve inspect and repair, HP Turbine Control Valve inspect and repair, HP Generator Field in place inspect and repair, High Energy Piping assessment and inspect and repair, Coal Silo inspect and repair, Precipitator inspect and repair.
Mitchell 2 | 2022-09-10 | 2022-12-05 | 2022-09-10 | 2022-12-16 14:25 | PO | Boiler inspect and repair, Cooling Tower inspect and repair, Low Pressure Turbine A"&"B" Valve replacement | Stay plates in the air heaters were found to be eroded and had to be replaced, causing the extension.
Rockport 1 |  |  | 2022-09-18 | 2022-10-09 | MO | Pre-Planned Outage work, Low Pressure Turbine disassembly.
Mitchell 1 |  |  | 2022-09-24 | 2022-10-08 | MO | Repair feed pump turbine steam supply regulating valve.
Mitchell 1 |  |  | 2022-10-08 | 2022-11-19 17:32 | PO | Boiler inspect and repair, Precip inspect and repair, Pulverizer/Feeder MATS inspect and repair, Economizer wash, Replace Precip Transformer power cables, Replace SCR XJ s 14,15 and 115, Replace Exit Duct XJ FGX-71009, Water Cannon upgrades, Ovation Evergreen upgrade, Inter-lock testing, HE Piping inspect and repair.
Rockport 1 |  |  | 2022-10-09 | 2022-11-03 16:30 | PO | Boiler inspect and repair, #2 & #4 LP Turbine inspect and repair and L-0 Blade removal, SCR cleaning.
* If different than actual start and end date
**Event Type
FO |  |  | Forced Outage
MO |  |  | Maintenance Outage
PO |  |  | Planned Outage