## Export
Unit | Primary Fuel Type | Event Start | Event End | Event Type | Event Description | Event Duration Hours
East Bend Steam-2 | Coal | 2022-04-20 05:34 | 2022-05-07 04:16 | MO | Spring Maintenance Outage- Secondary Air Heater baskets and FGD duct work/ misc. | 406.7
East Bend Steam-2 | Coal | 2022-05-07 04:20 | 2022-05-07 06:00 | U1 | PA fan vibration | 1.67
East Bend Steam-2 | Coal | 2022-05-08 03:24 | 2022-05-09 17:28 | U1 | Unit Trip-Boiler Feed Pump recirc line repairs | 38.07
East Bend Steam-2 | Coal | 2022-05-31 02:16 | 2022-06-01 06:33 | U1 | Voltage regulator | 28.28
East Bend Steam-2 | Coal | 2022-06-01 07:16 | 2022-06-02 08:34 | U1 | 2-2 BFPT Trip - Unit trip on Low Drum Level | 25.3
East Bend Steam-2 | Coal | 2022-07-29 11:12 | 2022-07-31 05:50 | MO | Reheat boiler tube leak Maintenance Outage | 42.63
East Bend Steam-2 | Coal | 2022-08-05 17:58 | 2022-08-06 03:36 | U1 | Station air compressor tripped due to damaged seal air piping. | 9.63
East Bend Steam-2 | Coal | 2022-08-06 03:41 | 2022-08-06 04:55 | U1 | Drum Level trip | 1.23
East Bend Steam-2 | Coal | 2022-08-07 00:21 | 2022-08-07 10:22 | U1 | DCS Drop 25 Failure - MFT | 10.02
East Bend Steam-2 | Coal | 2022-08-07 10:28 | 2022-08-07 12:01 | U1 | Drum Level trip | 1.55
East Bend Steam-2 | Coal | 2022-08-12 04:50 | 2022-08-22 05:01 | MO | Generator Vibration balance | 240.18
East Bend Steam-2 | Coal | 2022-08-29 04:01 | 2022-09-06 12:10 | MO | IDBF 2-1 and 2-3 VIVs won't stroke 100% | 200.15
East Bend Steam-2 | Coal | 2022-09-24 04:00 | 2022-11-03 04:17 | PO | Planned Fall 2022 Outage - Critical path SAH Basket replacement | 960.28
Woodsdale CT-1 | Natural Gas | 2022-05-01 21:50 | 2022-05-02 19:47 | U1 | CT1 not reading Line Voltage. | 21.95
Woodsdale CT-1 | Natural Gas | 2022-05-20 10:00 | 2022-05-25 13:20 | PO | Inspect Turbine Blades | 123.33
Woodsdale CT-1 | Natural Gas | 2022-06-18 22:35 | 2022-06-18 23:10 | MO | Unavailable to switch to BOP to charge CB1504. | 0.58
Woodsdale CT-1 | Natural Gas | 2022-09-17 10:00 | 2022-09-23 18:50 | PO | Replace Natural Gas Valves. | 152.83
Woodsdale CT-2 | Natural Gas | 2022-05-13 19:22 | 2022-05-13 22:02 | SF | Starting Breaker Failure. | 2.67
Woodsdale CT-2 | Natural Gas | 2022-06-18 22:35 | 2022-06-18 23:40 | MO | Unavailable to switch to BOP to charge CB1504. | 1.08
Woodsdale CT-2 | Natural Gas | 2022-09-17 10:00 | 2022-09-23 20:20 | PO | Replace Natural Gas Valves. | 154.33
Woodsdale CT-3 | Natural Gas | 2022-03-18 10:00 | 2022-06-01 04:00 | PO | Generator Field Rewind | 1794
Woodsdale CT-3 | Natural Gas | 2022-06-01 04:00 | 2023-07-25 12:21 | U1 | Generator Rewind -span Peek Maintenance | 10064.35
Woodsdale CT-4 | Natural Gas | 2022-05-13 11:00 | 2022-05-13 21:20 | PO | Crane outage, for GT3 Gen Rotor. | 10.33
Woodsdale CT-4 | Natural Gas | 2022-06-06 14:05 | 2022-06-06 21:50 | PO | Crane outage, for GT3 Gen Rotor | 7.75
Woodsdale CT-4 | Natural Gas | 2022-06-18 22:35 | 2022-06-19 03:48 | MO | Recharging CB1504 with SF6 Gas. | 5.22
Woodsdale CT-4 | Natural Gas | 2022-10-01 10:00 | 2022-10-06 19:37 | PO | Replace Natural Gas Valves. | 129.62
Woodsdale CT-5 | Natural Gas | 2022-06-13 14:55 | 2022-06-13 20:13 | U1 | TRIP; Variable Inlet Guide Vanes Problem. | 5.3
Woodsdale CT-5 | Natural Gas | 2022-06-15 15:44 | 2022-06-16 14:29 | SF | TRIP during start up; Variable Inlet Guide Vanes Problem. | 22.75
Woodsdale CT-5 | Natural Gas | 2022-06-22 19:49 | 2022-06-23 22:30 | U1 | Fire Prot. tripped unit, enclosure heat detectors. CO2 discharged. | 26.68
Woodsdale CT-5 | Natural Gas | 2022-07-22 18:01 | 2022-07-26 15:11 | U1 | Fire Protection CO2 Trip, dumped CO2. | 93.17
Woodsdale CT-5 | Natural Gas | 2022-10-08 10:00 | 2022-10-13 19:14 | PO | Replace Natural Gas Valves. | 129.23
Woodsdale CT-5 | Natural Gas | 2022-10-13 23:06 | 2022-10-14 00:23 | SF | Flame out due to bad Thermocouple. | 1.28
Woodsdale CT-6 | Natural Gas | 2022-06-15 16:54 | 2022-06-15 17:32 | U1 | TRIP; UPS for Communications Drop Failed | 0.63
Woodsdale CT-6 | Natural Gas | 2022-08-08 15:22 | 2022-08-08 16:07 | U1 | TRIP; Flame Scanner Failure. | 0.75
Woodsdale CT-6 | Natural Gas | 2022-10-08 10:00 | 2022-10-13 19:17 | PO | Replace Natural Gas Valves. | 129.28
Woodsdale CT-6 | Natural Gas | 2022-10-31 09:00 | 2022-10-31 16:49 | PO | Natural Gas Flowmeter Calibration | 7.82
Event Type Key
MO | Maintenance Outage
PO | Planned Outage
SF | Startup Failure
U1 | Unplanned (Forced) Outage - Immediate