## 2016
PSC Outage Tabulation, 2016
Taylor County RECC
System:
Year |  | SAIDI | SAIFI | CAIDI
2011 |  | 89.4 | 1.1 | 81.7
2012 |  | 74.0 | 1.3 | 57.4
2013 |  | 386.84 | 4.24 | 91.27
2014 |  | 119.18 | 1.58 | 75.29
2015 |  | 198.6 | 1.3 | 150.7
2016 |  | 153.3 | 1.3 | 119.6
Outage Subcategory Breakdown:
Subcategory: |  | Mins:
Animal |  | 103989
Consumer |  | 160602
Equipment |  | 539113.8
Miscellaneous |  | 182098.2
Overload |  | 3833.4
Plan |  | 56784.6
Power Supplier |  | 54589.8
Tree |  | 111091.2
Weather |  | 2824388.4
2016 - Major outage day defined per IEEE standard
5yr avg Tmed for 16
99377
Major Outage Days - | 1/22 Weather(310,410), 5/11 Weather(103,084.2)
5/26 Weather(158,706.6), 7/3 Equipment(163,568.4), 7/7 Weather(1,150,537.8),
8/27 Weather(158,068.2), 11/19 Equipment(100,080)
2016 10 Worst Circuits per Category:
Substation | C | SAIDI | SAIFI | CAIDI | Maj. Out. Category
EAST CAMPBELLSVILLE | 2 | 670.7804 |  |  | WEATHER
COLUMBIA | 2 | 602.096 |  |  | WEATHER
COLUMBIA | 5 | 418.4033 |  |  | WEATHER
BASS | 2 | 399.4459 |  |  | WEATHER
MCKINNEY CORNER | 3 | 381.7277 |  |  | CONSUMER
EAST CAMPBELLSVILLE | 4 | 328.35 |  |  | WEATHER
EAST CAMPBELLSVILLE | 1 | 315.0195 |  |  | WEATHER
COBURG | 3 | 301.2195 |  |  | WEATHER
GARLIN | 5 | 282.7452 |  |  | WEATHER
WEST COLUMBIA | 3 | 267.8773 |  |  | WEATHER
MILE LANE | 5 |  | 4.235 |  | WEATHER
EAST CAMPBELLSVILLE | 1 |  | 3.748 |  | WEATHER
COLUMBIA | 2 |  | 3.4404 |  | WEATHER
EAST CAMPBELLSVILLE | 2 |  | 3.3501 |  | WEATHER
COLUMBIA | 5 |  | 2.9289 |  | WEATHER
GARLIN | 5 |  | 2.3078 |  | WEATHER
EAST CAMPBELLSVILLE | 4 |  | 2.125 |  | WEATHER
EAST CAMPBELLSVILLE | 5 |  | 2.0982 |  | WEATHER
CAMPBELLSVILLE | 3 |  | 2.0253 |  | EQUIPMENT
GREENSBURG | 3 |  | 1.8917 |  | WEATHER
CAMPBELLSVILLE | 6 |  |  | 480 | MISCELLANEOUS
GARLIN | 4 |  |  | 322.9535 | WEATHER
BASS | 2 |  |  | 263.9013 | WEATHER
WEST COLUMBIA | 2 |  |  | 247.0704 | WEATHER
COBURG | 2 |  |  | 235.2993 | WEATHER
MCKINNEY CORNER | 3 |  |  | 233.4036 | CONSUMER
EAST CAMPBELLSVILLE | 2 |  |  | 200.2241 | WEATHER
COBURG | 3 |  |  | 194.5815 | WEATHER
PHIL | 2 |  |  | 194.2188 | EQUIPMENT
COLUMBIA | 2 |  |  | 175.0077 | WEATHER
Vegetation Management Plan:
Plan is progressing as expected/desired
Continue to face occasional issue with yard tree clearance

## 2017
PSC Outage Tabulation, 2017
Taylor County RECC
System:
Year |  | SAIDI | SAIFI | CAIDI
2012 |  | 74.0 | 1.3 | 57.4
2013 |  | 386.84 | 4.24 | 91.27
2014 |  | 119.18 | 1.58 | 75.29
2015 |  | 198.6 | 1.3 | 150.7
2016 |  | 153.3 | 1.3 | 119.6
2017 |  | 126.25 | 1.25 | 100.96
Outage Subcategory Breakdown:
Subcategory: |  | Mins:
Animal |  | 119695.8
Consumer |  | 436894.8
Equipment |  | 315600.6
Miscellaneous |  | 413818.8
Overload |  | 1875
Plan |  | 109607.4
Power Supplier |  | 478654.8
Tree |  | 446910
Weather |  | 1017453
2017 - Major outage day defined per IEEE standard
5yr avg Tmed for 17
110572.1
Major Outage Days - | 3/27 Weather(231,778.8), 4/5 Weather(212,152.8)
5/1 Power Supply(194,387.4), 5/18 Equipment(111,415.8), 5/27 Weather(175,805.4),
9/16 Consumer(313,357.2), 11/18 Power Supply(255,423.6), 12/13 Miscellaneous(188,100)
2017 10 Worst Circuits per Category:
Substation | C | SAIDI | SAIFI | CAIDI | Maj. Out. Category
GARLIN | 3 | 529.2672 |  |  | CONSUMER
BASS | 1 | 395.2078 |  |  | MISCELLANEOUS
COLUMBIA | 5 | 354.5747 |  |  | WEATHER
COUMBIA | 2 | 307.7771 |  |  | WEATHER
BASS | 2 | 276.3579 |  |  | WEATHER
CRESTON | 2 | 208.3677 |  |  | WEATHER
COBURG | 3 | 207.2927 |  |  | WEATHER
MILE LANE | 5 | 205.7252 |  |  | WEATHER
COBURG | 2 | 198.2622 |  |  | EQUIPMENT
GARLIN | 5 | 197.1796 |  |  | EQUIPMENT
COUMBIA | 2 |  | 3.3505 |  | WEATHER
COLUMBIA | 5 |  | 3.0716 |  | WEATHER
SUMMERSVILLE | 3 |  | 2.6239 |  | MISCELLANEOUS
MILE LANE | 5 |  | 2.3673 |  | WEATHER
EAST CAMPBELLSVILLE | 2 |  | 2.1711 |  | POWER SUPPLY
GARLIN | 5 |  | 2.0259 |  | EQUIPMENT
CAMPBELLSVILLE | 1 |  | 2 |  | ANIMAL
EAST CAMPBELLSVILLE | 5 |  | 1.9894 |  | POWER SUPPLY
BASS | 2 |  | 1.883 |  | WEATHER
COBURG | 1 |  | 1.8496 |  | PLANNED
GARLIN | 3 |  |  | 450.0082 | CONSUMER
BASS | 1 |  |  | 232.7936 | MISCELLANEOUS
GREENSBURG | 6 |  |  | 215.8364 | MISCELLANEOUS
COLUMBIA | 3 |  |  | 199.8 | WEATHER
PHIL | 1 |  |  | 196.9177 | TREE
COBURG | 3 |  |  | 181.3811 | WEATHER
CRESTON | 2 |  |  | 147.0831 | WEATHER
BASS | 2 |  |  | 146.7615 | WEATHER
BASS | 3 |  |  | 140.9479 | WEATHER
MCKINNEY CORNER | 2 |  |  | 135.5838 | WEATHER
Vegetation Management Plan:
Plan is progressing as expected/desired
Continue to face occasional issue with yard tree clearance

## 2018
PSC Outage Tabulation, 2018
Taylor County RECC
System:
Year |  | SAIDI | SAIFI | CAIDI
2013 |  | 386.84 | 4.24 | 91.27
2014 |  | 119.18 | 1.58 | 75.29
2015 |  | 198.6 | 1.3 | 150.7
2016 |  | 153.3 | 1.3 | 119.6
2017 |  | 126.25 | 1.25 | 100.96
2018 |  | 123.15 | 1.63 | 75.42
Outage Subcategory Breakdown:
Subcategory: |  | Mins:
Animal |  | 182635.2
Consumer |  | 75231.6
Equipment |  | 518623.2
Miscellaneous |  | 507415.8
Overload |  | 3549.6
Plan |  | 69168.6
Power Supplier |  | 75655.8
Tree |  | 153910.8
Weather |  | 1661158.7
2018 - Major outage day defined per IEEE standard
5yr avg Tmed for 18
170893.75
Major Outage Days - | 6/25 Weather(127,652.9), 7/5 Weather(278,761.2),
7/21 Weather(145,712.4), 9/23 Weather(174,958.8), 11/14 Weather(240,077.4)
2018 10 Worst Circuits per Category:
Substation | C | SAIDI | SAIFI | CAIDI | Maj. Out. Category
PHIL | 3 | 407.5106 |  |  | WEATHER
COBURG | 4 | 393.11 |  |  | WEATHER
COBURG | 3 | 375.8854 |  |  | WEATHER
EC | 3 | 364.453 |  |  | EQUIPMENT
COLUMBIA | 5 | 353.2729 |  |  | WEATHER
ML | 5 | 285.8809 |  |  | WEATHER
COLUMBIA | 2 | 261.9008 |  |  | WEATHER
ML | 6 | 252.4998 |  |  | WEATHER
BASS | 3 | 241.2733 |  |  | WEATHER
SVILLE | 3 | 233.8748
PHIL | 3 |  | 5.9783 |  | WEATHER
COLUMBIA | 5 |  | 5.0468 |  | WEATHER
COLUMBIA | 2 |  | 4.398 |  | WEATHER
EC | 3 |  | 4.2564 |  | EQUIPMENT
PHIL | 5 |  | 4.242 |  | EQUIPMENT
SVILLE | 4 |  | 3.9766 |  | WEATHER
ML | 2 |  | 3.918 |  | WEATHER
SVILLE | 3 |  | 3.585 |  | ANIMAL
ML | 6 |  | 3.1776 |  | WEATHER
ML | 4 |  | 2.8111 |  | EQUIPMENT
COBURG | 4 |  |  | 264.6893 | WEATHER
CVILLE | 4 |  |  | 180 | WEATHER
COBURG | 3 |  |  | 149.8409 | WEATHER
GARLIN | 3 |  |  | 147.4266 | EQUIPMENT
ML | 5 |  |  | 130.324 | WEATHER
COLUMBIA | 6 |  |  | 130.2 | EQUIPMENT
GARLIN | 5 |  |  | 117.8263 | POWER SUPPLY
GBURG | 6 |  |  | 114.5908 | WEATHER
GRP | 3 |  |  | 109.8 | EQUIPMENT
GRP | 1 |  |  | 109.5974 | WEATHER
Vegetation Management Plan:
Plan is progressing as expected/desired
Continue to face occasional issue with yard tree clearance

## 2019
PSC Outage Tabulation, 2019
Taylor County RECC
System:
Year |  | SAIDI | SAIFI | CAIDI
2014 |  | 119.18 | 1.58 | 75.29
2015 |  | 198.6 | 1.3 | 150.7
2016 |  | 153.3 | 1.3 | 119.6
2017 |  | 126.25 | 1.25 | 100.96
2018 |  | 123.15 | 1.63 | 75.42
2019 |  | 111.02 | 1.14 | 97.06
Outage Subcategory Breakdown:
Subcategory: |  | Mins:
Animal |  | 183106.8
Consumer |  | 110619.6
Equipment |  | 484788
Miscellaneous |  | 282554.4
Overload |  | 5442
Plan |  | 25140
Power Supplier |  | 0
Tree |  | 241990.2
Weather |  | 1630287.6
2019 - Major outage day defined per IEEE standard
5yr avg Tmed for 19
119308.8
Major Outage Days - | 6/23 Weather(665,478)
2019 10 Worst Circuits per Category:
Substation | C | SAIDI | SAIFI | CAIDI | Maj. Out. Category
PHIL | 1 | 751.6 |  |  | WEATHER
COLUMBIA | 2 | 720.2 |  |  | WEATHER
CAMPBELLSVILLE | 1 | 720 |  |  | CONSUMER
EAST CAMPBELLSVILLE | 3 | 436.7 |  |  | WEATHER
PHIL | 5 | 282.7 |  |  | WEATHER
PHIL | 3 | 235.2 |  |  | WEATHER
CRESTON | 3 | 227.6 |  |  | EQUIPMENT
BASS | 3 | 203 |  |  | ANIMAL
BASS | 1 | 194.2 |  |  | WEATHER
COBURG | 2 | 163.3 |  |  | WEATHER
CAMPBELLSVILLE | 1 |  | 8 |  | CONSUMER
COLUMBIA | 2 |  | 4.7 |  | WEATHER
EAST CAMPBELLSVILLE | 3 |  | 4.2 |  | WEATHER
PHIL | 1 |  | 3.8 |  | WEATHER
GARLIN | 5 |  | 3.2 |  | EQUIPMENT
GARLIN | 4 |  | 2.5 |  | WEATHER
BASS | 3 |  | 2.3 |  | ANIMAL
PHIL | 3 |  | 2.1 |  | WEATHER
SUMMERSVILLE | 1 |  | 2.1 |  | WEATHER
CRESTON | 3 |  | 2.1 |  | EQUIPMENT
SUMMERSVILLE | 2 |  |  | 334.2 | TREE
GREEN RIVER PLAZA | 2 |  |  | 234.8 | EQUIPMENT
PHIL | 1 |  |  | 200.2 | WEATHER
PHIL | 5 |  |  | 197.7 | WEATHER
COLUMBIA | 5 |  |  | 170.6 | WEATHER
EAST CAMPBELLSVILLE | 5 |  |  | 164.3 | WEATHER
COBURG | 1 |  |  | 158.6 | WEATHER
COLUMBIA | 2 |  |  | 154.5 | WEATHER
MCKINNEY CORNER | 2 |  |  | 144.5 | WEATHER
BASS | 1 |  |  | 137.1 | WEATHER
Vegetation Management Plan:
Plan is progressing as expected/desired
Continue to face occasional issue with yard tree clearance

## 2020
PSC Outage Tabulation, 2020
Taylor County RECC
System:
Year |  | SAIDI | SAIFI | CAIDI
2015 |  | 198.6 | 1.3 | 150.7
2016 |  | 153.3 | 1.3 | 119.6
2017 |  | 126.25 | 1.25 | 100.96
2018 |  | 123.15 | 1.63 | 75.42
2019 |  | 111.02 | 1.14 | 97.06
2020 |  | 117.8 | 1.2 | 99
Outage Subcategory Breakdown:
Subcategory: |  | Mins:
Animal |  | 147683.4
Consumer |  | 129085.2
Equipment |  | 387757.8
Miscellaneous |  | 437217.6
Overload |  | 2155.8
Plan |  | 29968.8
Power Supplier |  | 513091.8
Tree |  | 219451.2
Weather |  | 1186449
2020 - Major outage day defined per IEEE standard
5yr avg Tmed for 20
105883.6
Major Outage Days - | 1/11 Weather (498,237), 12/4 Power Supply (324,880.8)
2020 10 Worst Circuits per Category:
Substation | C | SAIDI | SAIFI | CAIDI | Maj. Out. Category
COLUMBIA | 6 | 12262.84 |  |  | POWER SUPPLY
COLUMBIA | 2 | 594.6354 |  |  | POWER SUPPLY
EC | 3 | 363.9172 |  |  | POWER SUPPLY
COLUMBIA | 5 | 349.9426 |  |  | POWER SUPPLY
COLUMBIA | 3 | 313.9454 |  |  | POWER SUPPLY
EC | 2 | 255.0412 |  |  | POWER SUPPLY
PHIL | 1 | 254.7857 |  |  | WEATHER
CONTOWN | 2 | 238.8952 |  |  | MISCELLANEOUS
CONTOWN | 3 | 232.0568 |  |  | WEATHER
BASS | 2 | 228.5875 |  |  | WEATHER
COLUMBIA | 2 |  | 6.2013 |  | POWER SUPPLY
EC | 3 |  | 4.1529 |  | POWER SUPPLY
GBURG | 5 |  | 2.7332 |  | WEATHER
EC | 1 |  | 2.5589 |  | POWER SUPPLY
EC | 2 |  | 2.3672 |  | POWER SUPPLY
PHIL | 1 |  | 2.2629 |  | WEATHER
COLUMBIA | 3 |  | 2.2159 |  | POWER SUPPLY
COLUMBIA | 6 |  | 2.1333 |  | POWER SUPPLY
GARLIN | 4 |  | 2.066 |  | EQUIPMENT/MATERIAL
EC | 5 |  | 2.037 |  | POWER SUPPLY
COLUMBIA | 6 |  |  | 5748.2063 | POWER SUPPLY
PHIL | 4 |  |  | 490.2 | WEATHER
GARLIN | 1 |  |  | 454.8 | WEATHER
COLUMBIA | 4 |  |  | 199.8 | POWER SUPPLY
COLUMBIA | 1 |  |  | 199.8 | POWER SUPPLY
PHIL | 5 |  |  | 199.1297 | WEATHER
COLUMBIA | 5 |  |  | 194.1989 | POWER SUPPLY
CONTOWN | 2 |  |  | 189.3132 | MISCELLANEOUS
CRESTON | 3 |  |  | 144.0109 | WEATHER
GBURG | 6 |  |  | 143.4406 | WEATHER
Vegetation Management Plan:
Plan is progressing as expected/desired
Continue to face occasional issue with yard tree clearance

## 2021
PSC Outage Tabulation, 2021
Taylor County RECC
System:
Year |  | SAIDI | SAIFI | CAIDI
2016 |  | 153.3 | 1.3 | 119.6
2017 |  | 126.25 | 1.25 | 100.96
2018 |  | 123.15 | 1.63 | 75.42
2019 |  | 111.02 | 1.14 | 97.06
2020 |  | 117.8 | 1.2 | 99
2021 |  | 141.2 | 1.12 | 126.03
Outage Subcategory Breakdown:
Subcategory: |  | Mins:
Animal |  | 182789.4
Consumer |  | 192398.4
Equipment |  | 559372.8
Miscellaneous |  | 254791.2
Overload |  | 2145.6
Plan |  | 1639.2
Power Supplier |  | 402570
Tree |  | 467210.76
Weather |  | 1828740.6
2021 - Major outage day defined per IEEE standard
5yr avg Tmed for 21
109016.07
Major Outage Days - |  | 2/11 Weather (626,349.6), 2/28 Weather (133,470.0)
6/10 Power Supply (402,570.0), 7/30 Weather (158,584.2)
11/28 Equipment (213,345.0), 12/11 Weather (278,554.2)
2021 10 Worst Circuits per Category:
Substation | C | SAIDI | SAIFI | CAIDI | Maj. Out. Category
EC | 1 | 556.2649 |  |  | WEATHER
SVILLE | 3 | 547.244 |  |  | WEATHER
ML | 5 | 436.6238 |  |  | WEATHER
MCK | 2 | 386.6165 |  |  | POWER SUPPLY
MCK | 1 | 309.6363 |  |  | POWER SUPPLY
GRP | 3 | 305.5485 |  |  | WEATHER
CONTOWN | 3 | 297.939 |  |  | CONSUMER
CONTOWN | 1 | 286.2425 |  |  | WEATHER
ML | 4 | 274.2232 |  |  | EQUIPMENT/MATERIAL
PHIL | 3 | 239.7555 |  |  | TREE
MCK | 2 |  | 3.3054 |  | POWER SUPPLY
EC | 1 |  | 3.2981 |  | WEATHER
ML | 4 |  | 2.6065 |  | EQUIPMENT/MATERIAL
COLUMBIA | 2 |  | 2.5281 |  | WEATHER
MCK | 1 |  | 2.3625 |  | POWER SUPPLY
GRP | 3 |  | 1.9394 |  | WEATHER
PHIL | 3 |  | 1.8686 |  | TREE
PHIL | 5 |  | 1.8351 |  | EQUIPMENT/MATERIAL
EC | 5 |  | 1.8188 |  | TREE
SVILLE | 4 |  | 1.818 |  | WEATHER
SVILLE | 3 |  |  | 424.5859 | WEATHER
ML | 5 |  |  | 401.958 | WEATHER
CONTOWN | 3 |  |  | 232.3137 | CONSUMER
WC | 2 |  |  | 216.7635 | WEATHER
CONTOWN | 1 |  |  | 196.4296 | WEATHER
COBURG | 3 |  |  | 184.2876 | WEATHER
EC | 1 |  |  | 168.6616 | WEATHER
CRESTON | 3 |  |  | 168.2421 | TREE
GRP | 3 |  |  | 157.5484 | WEATHER
ML | 6 |  |  | 154.8722 | WEATHER
Vegetation Management Plan:
Plan is progressing as expected/desired
Continue to face occasional issue with yard tree clearance

## 2022
PSC Outage Tabulation, 2022
Taylor County RECC
System:
Year |  | SAIDI | SAIFI | CAIDI
2017 |  | 126.25 | 1.25 | 100.96
2018 |  | 123.15 | 1.63 | 75.42
2019 |  | 111.02 | 1.14 | 97.06
2020 |  | 117.8 | 1.2 | 99
2021 |  | 141.2 | 1.12 | 126.03
2022 |  | 203 | 1.7 | 117.8
Outage Subcategory Breakdown:
Subcategory: |  | Mins:
Animal |  | 151680
Consumer |  | 546521.4
Equipment |  | 486961.8
Miscellaneous |  | 513002.4
Overload |  | 3780.6
Plan |  | 8890.8
Power Supplier |  | 198676.8
Tree |  | 596039.4
Weather |  | 3166181.3
2022 - Major outage day defined per IEEE standard
5yr avg Tmed for 22
116392.17
Major Outage Days - |  | 1/1 Weather(272,272.2), 2/22 Consumer(192,288.6)
3/30 Weather(226,362.6), 4/13 Weather(399,374.4)
5/18 Weather(152,421), 6/7 Weather(199,625.4)
6/22 Weather(390,160.2), 6/23 Consumer(272,256.0)
7/28 Weather(183,885.4), 12/13 Power Supply(198,676.8)
2022 10 Worst Circuits per Category:
Substation | C | SAIDI | SAIFI | CAIDI | Maj. Out. Category
COBURG | 3 | 630.5884 |  |  | CONSUMER
GARLIN | 5 | 618.9162 |  |  | WEATHER
COLUMBIA | 2 | 460.7198 |  |  | WEATHER
MCK | 2 | 449.0693 |  |  | WEATHER
COLUMBIA | 4 | 417.1787 |  |  | WEATHER
ML | 4 | 396.376 |  |  | WEATHER
BASS | 3 | 386.4284 |  |  | WEATHER
GARLIN | 4 | 383.763 |  |  | WEATHER
PHIL | 3 | 338.2912 |  |  | WEATHER
COBURG | 4 | 323.457 |  |  | WEATHER
COLUMBIA | 2 |  | 5.2625 |  | WEATHER
ML | 3 |  | 4.3768 |  | EQUIPMENT
COBURG | 3 |  | 3.9831 |  | CONSUMER
ML | 4 |  | 3.917 |  | WEATHER
PHIL | 3 |  | 3.522 |  | WEATHER
MCK | 3 |  | 3.2556 |  | WEATHER
GBURG | 5 |  | 3.0228 |  | WEATHER
COBURG | 4 |  | 3.0106 |  | WEATHER
GARLIN | 3 |  | 2.9195 |  | WEATHER
GARLIN | 5 |  | 2.8084 |  | WEATHER
PHIL | 5 |  |  | 246.4667 | TREE
GARLIN | 4 |  |  | 230.4883 | WEATHER
GARLIN | 5 |  |  | 220.3817 | WEATHER
CONTOWN | 1 |  |  | 217.9702 | WEATHER
WC | 3 |  |  | 199.3982 | WEATHER
MCK | 1 |  |  | 195.973 | WEATHER
CRESTON | 1 |  |  | 182.7236 | MISCELLANEOUS
BASS | 3 |  |  | 178.4328 | WEATHER
GBURG | 3 |  |  | 176.9543 | WEATHER
CRESTON | 3 |  |  | 172.916 | WEATHER
Vegetation Management Plan:
Plan is progressing as expected/desired
Continue to face occasional issue with yard tree clearance