## Attachment 1
Unit Name | Event Type | Start Date | End Date | Loss (MWH) | Description
Big Sandy 1 | PO | 2021-10-08 22:00 | 2021-12-21 07:47 | 357074.5 | GBIR, GBIR, Turbine Exhaust High Energy Piping (HEP) inspections, Boiler corrosion fatigue inspections, Main and Aux Condenser eddy current testing, and Cooling Tower repairs.
Big Sandy 1 | D4 | 2022-01-09 03:00 | 2022-01-09 04:47 | 348.6 | Weekly Valve checks
Big Sandy 1 | U1 | 2022-01-19 03:11 | 2022-01-19 22:01 | 5563.3 | Reason Unknown - Deaerator level went high from RV 101
Big Sandy 1 | D1 | 2022-01-20 05:00 | 2022-01-26 04:28 | 5078.8 | North HP Heater Feedwater Head is leaking
Big Sandy 1 | D4 | 2022-01-26 01:00 | 2022-01-26 04:28 | 693.3 | Place North string of HP heaters in service, valve checks, backwash aux. condenser
Big Sandy 1 | D1 | 2022-02-05 23:20 | 2022-02-05 23:53 | 52.6 | Feed Pump Issue
Big Sandy 1 | D1 | 2022-02-05 23:53 | 2022-02-06 00:01 | 16 | Feed Pump Issue
Big Sandy 1 | D1 | 2022-02-06 00:01 | 2022-02-06 12:05 | 2835.5 | Feed Pump Issue
Big Sandy 1 | D1 | 2022-02-06 12:05 | 2022-02-06 12:58 | 48.4 | Feed Pump Issue
Big Sandy 1 | MO | 2022-02-10 00:25 | 2022-02-18 15:00 | 61024.6 | Boiler inpsection/repair, Vibration Probe inpsection/repair, RV-101 (Hotwell level control) repair, RV-5 (Start-up Steam Attemperator Valve) inpsection/repair, Nash Vacuum Pump inpsection/repair, #5 HP Heater Feedwater Header leak repair.
Big Sandy 1 | MO | 2022-02-22 00:58 | 2022-02-27 11:55 | 38682.6 | Requesting a Maintenance Outage until 2-27-2022 @1600 for Boiler inspection, Drum door repairs, BFPT Y vibration probe repair, Clean cooling tower screens, Nash pump level float repair, Circulating water vent replacement.
Big Sandy 1 | D1 | 2022-03-14 07:51 | 2022-03-15 05:00 | 748.8 | BFPT Gov. Valve has ran out 100% open
Big Sandy 1 | D3 | 2022-03-15 03:00 | 2022-03-15 03:35 | 116.7 | Need to backwash Aux Condenser due to BFPT Gov. Running out of range (100%)
Big Sandy 1 | MO | 2022-03-17 | 2022-03-27 12:00 | 74440.8 | Boiler inpsection/repair, State Drum inspection, BFPT 2Y vibration probe repair, BFPT Gasket replacement on Duplex Strainer, Boiler Penthouse inspection
Big Sandy 1* | MO | 2022-03-30 01:27 | 2022-04-05 06:56 | 44157.3 | Boiler inspection
Big Sandy 1 | U1 | 2022-04-06 04:42 | 2022-04-08 16:00 | 17517.2 | condenser leak.
Big Sandy 1 | MO | 2022-04-08 16:00 | 2022-04-14 13:40 | 41848.4 | Drum door repairs
Big Sandy 1 | D1 | 2022-04-23 17:49 | 2022-04-24 01:45 | 400 | Aux Condenser Backpressure
Big Sandy 1 | D1 | 2022-05-10 20:49 | 2022-05-10 21:16 | 42.8 | # 3 Heater Leak
Big Sandy 1 | D1 | 2022-05-10 21:16 | 2022-05-10 21:59 | 0.3 | # 3 Heater Leak
Big Sandy 1 | D1 | 2022-05-10 21:16 | 2022-05-10 21:59 | 53.8 | # 3 Heater Leak
Big Sandy 1 | D1 | 2022-05-10 21:59 | 2022-05-10 22:20 | 33.4 | # 3 Heater Leak
Big Sandy 1 | D1 | 2022-05-10 21:59 | 2022-05-10 22:20 | 0 | # 3 Heater Leak
Big Sandy 1 | D1 | 2022-05-20 15:25 | 2022-05-21 02:00 | 163.1 | boiler feed pump out of range
Big Sandy 1 | MO | 2022-05-24 07:00 | 2022-05-28 16:00 | 31017 | Boiler inpsection/repair; Deaerator Positive Closing Check Valve repairs; Inspect 2Y vibration pickup on BFPT; Repair Drip Pot drain line to BFPT; Replace Seal on South Positive closing check valve; Inspect Aux Condenser Water Boxes.
Big Sandy 1 | MO | 2022-06-02 07:00 | 2022-06-05 16:00 | 23927.4 | Boiler inpsection/repair, BFPT 2Y Vibration Probe inpsection/repair, RV-101 inpsection/repair, 5N HP Heater leak repair, Turbine Valve Trip Logic inpsection/repair, Stroke RV-910, Re-pack East Circulating Water Pump, North Heater Drain Pump coupling alignment check.
Big Sandy 1 | D1 | 2022-06-06 17:00 | 2022-06-11 15:19 | 4188.5 | North String of HP Heaters O/S to repair 5N Hp Heater Head Leak
Big Sandy 1 | D1 | 2022-06-16 14:44 | 2022-06-16 15:02 | 3.2 | Feed pump maxed
Big Sandy 1 | D1 | 2022-06-16 15:02 | 2022-06-17 | 224.2 | Feed pump maxed
Big Sandy 1 | D3 | 2022-06-18 01:00 | 2022-06-18 01:26 | 101.9 | Valve Checks
Big Sandy 1 | D1 | 2022-06-21 16:52 | 2022-06-21 17:02 | 39.3 | A1 breaker motor failure - if the unit trips it will not disconnect from the grid and will motor.
Big Sandy 1 | D1 | 2022-06-22 15:06 | 2022-06-22 15:32 | 4.4 | Feed pump out of range
Big Sandy 1 | D1 | 2022-06-22 15:32 | 2022-06-23 | 127 | Feed pump out of range
Big Sandy 1 | D4 | 2022-06-25 03:00 | 2022-06-25 03:10 | 39.3 | Weekly Valve Checks
Big Sandy 1 | D1 | 2022-06-30 17:42 | 2022-06-30 17:57 | 1.5 | Feed Pump Issue
Big Sandy 1 | D1 | 2022-06-30 17:57 | 2022-06-30 21:00 | 30.4 | Feed Pump Issue
Big Sandy 1 | D4 | 2022-07-02 01:00 | 2022-07-02 01:35 | 137.4 | Perform weekly turbine valve checks
Big Sandy 1 | MO | 2022-07-03 07:00 | 2022-07-09 14:00 | 44605.4 | Boiler inpsection/repair, #2 Governor Valve - replace Servo, Lower Right RH Stop/Intercept Valve LVDT replacement, 5N Heater leak repair, West Air Compressor Oil Cooler - clean and replace Oil Pump, Aux Condenser Tube Sheet cleaning.
Big Sandy 1 | D1 | 2022-07-12 22:22 | 2022-07-13 15:55 | 621.2 | South heater drain pump failure
Big Sandy 1 | D1 | 2022-07-13 15:55 | 2022-07-13 16:24 | 26.6 | South Heater Drain Pump o/s.
Big Sandy 1 | D1 | 2022-07-13 16:24 | 2022-07-15 17:30 | 3191.5 | South Heater Drain Pump o/s.
Big Sandy 1 | D4 | 2022-07-16 02:00 | 2022-07-16 02:23 | 90.1 | Weekend valve checks
Big Sandy 1 | D1 | 2022-07-16 11:03 | 2022-07-19 18:45 | 5212.3 | South Heater drain pump, motor bearing bad ,
Big Sandy 1 | D1 | 2022-07-20 15:37 | 2022-07-21 | 87.1 | Boiler Feed Pump
Big Sandy 1 | D1 | 2022-07-22 08:30 | 2022-07-22 08:58 | 109.9 | #1 governor valve
Big Sandy 1 | MO | 2022-07-26 07:00 | 2022-07-30 16:00 | 31017 | to troubleshoot and repair Governor Valve #1 and #2, RV-101; Boiler inpsection/repair; West Condensate Booster Pump Mechanical Seal Repair; Measure EHC Hoses for fall outage repair; Turbine Room Crane repair
Big Sandy 1 | D4 | 2022-08-06 02:00 | 2022-08-06 02:28 | 109.9 | Weekly Valve Checks
Big Sandy 1 | D1 | 2022-08-08 17:00 | 2022-08-08 22:00 | 52 | Feed pump out of range.
Big Sandy 1 | MO | 2022-08-15 | 2022-08-17 08:00 | 16542.4 | Boiler inpsection/repair, North Gland Seal leak Off Exhauster inpsection/repair, RV-1003 (Low Pressure Steam Seal Regulator) positioner replacement.
Big Sandy 1 | MO | 2022-08-27 | 2022-09-03 08:21 | 52093.8 | Remove 600V Feed (both A and B Bus) for measurements and to complete last stage blade inspection of the Boiler Feedpump Turbine and Main Turbine Double Flow Low Pressure Turbine Section.
Big Sandy 1 | MO | 2022-09-08 | 2022-09-10 | 14179.2 | Pre-Planned Outage preparation.
Big Sandy 1 | PO | 2022-09-10 | 2023-01-14 11:47 | 897065.7 | Boiler inpsection/repair, Generator Field Out inspection/possible rewedge, Turbine Valve inpsection/repair, Corrosion Fatigue inpsection/repair, Cooling Tower inpsection/repair, ReHeat Attemperator inpsection/repair, Gas valve inpsection/repair, FD Fan and Motor inpsection/repair, High Energy Piping (HEP) inpsection/repair, Flow Accelerated Corrosion (FAC) inpsection/repair, Core Loop testing.
Big Sandy 1 | PO | 2023-01-14 11:47 | 2023-01-16 | 10698.5 | Boiler inpsection/repair, Generator Field Out inspection/possible rewedge, Turbine Valve inpsection/repair, Corrosion Fatigue inpsection/repair, Cooling Tower inpsection/repair, ReHeat Attemperator inpsection/repair, Gas valve inpsection/repair, FD Fan and Motor inpsection/repair, High Energy Piping (HEP) inpsection/repair, Flow Accelerated Corrosion (FAC) inpsection/repair, Core Loop testing.
Big Sandy 1 | D3 | 2023-01-16 | 2023-01-17 22:00 | 10828.5 | High Silica and Iron levels in water.
Big Sandy 1 | D4 | 2023-01-17 22:00 | 2023-01-19 15:58 | 9879.1 | Blowdown for Water Chemistry.
Big Sandy 1 | D1 | 2023-01-19 19:00 | 2023-01-20 10:01 | 3535.1 | High Silica Level
Big Sandy 1 | D1 | 2023-01-20 10:01 | 2023-01-20 16:53 | 1201.7 | High Silica Level
Big Sandy 1 | D1 | 2023-01-20 16:53 | 2023-01-20 23:59 | 745.6 | High Silica Level
Big Sandy 1 | D4 | 2023-01-21 | 2023-01-21 07:00 | 1647.7 | Blowdown Boiler Silica.
Big Sandy 1 | D3 | 2023-01-21 07:00 | 2023-01-21 10:54 | 762.1 | Boiler Silica mitigation.
Big Sandy 1 | D3 | 2023-01-21 10:54 | 2023-01-21 11:18 | 70 | Boiler Silica mitigation.
Big Sandy 1 | D3 | 2023-01-21 11:18 | 2023-01-21 11:50 | 82.7 | Boiler Silica mitigation.
Big Sandy 1 | D3 | 2023-01-21 11:50 | 2023-01-21 12:54 | 143.9 | Boiler Silica mitigation.
Big Sandy 1 | D3 | 2023-01-21 12:54 | 2023-01-21 13:33 | 68.2 | Boiler Silica mitigation.
Big Sandy 1 | D3 | 2023-01-21 13:33 | 2023-01-21 14:51 | 123.5 | Boiler Silica mitigation.
Big Sandy 1 | D3 | 2023-01-21 14:51 | 2023-01-21 18:00 | 236.3 | Boiler Silica mitigation.
Big Sandy 1 | D3 | 2023-01-21 18:00 | 2023-01-21 19:00 | 39.9 | Boiler Silica mitigation.
Big Sandy 1 | D1 | 2023-01-21 19:25 | 2023-01-22 | 162.2 | Boiler Silica mitigation.
Big Sandy 1 | D4 | 2023-01-22 | 2023-01-22 07:00 | 1647.7 | Silica mitigation
Big Sandy 1 | D3 | 2023-01-22 07:00 | 2023-01-22 08:43 | 249.6 | Silica mitigation
Big Sandy 1 | D3 | 2023-01-22 08:43 | 2023-01-22 09:03 | 44.9 | Silica mitigation
Big Sandy 1 | D3 | 2023-01-22 09:03 | 2023-01-22 09:22 | 39.6 | Silica mitigation
Big Sandy 1 | D3 | 2023-01-22 09:22 | 2023-01-22 10:08 | 88 | Silica mitigation
Big Sandy 1 | D3 | 2023-01-22 10:08 | 2023-01-22 11:35 | 152.1 | Silica mitigation
Big Sandy 1 | D3 | 2023-01-22 11:35 | 2023-01-23 02:00 | 1369.5 | Silica mitigation
Big Sandy 1 | D4 | 2023-01-23 02:00 | 2023-01-23 06:00 | 941.7 | To blow down Silica
Big Sandy 1 | D3 | 2023-01-23 06:00 | 2023-01-23 11:00 | 477.1 | Silica Mitigation
Big Sandy 1 | D4 | 2023-01-24 | 2023-01-24 06:50 | 1608.5 | Come down to 60mw to blow down silica.
Big Sandy 1 | D3 | 2023-01-24 07:00 | 2023-01-24 10:43 | 205.9 | Exciter Brush Rigging sparking.
Big Sandy 1 | D3 | 2023-01-25 02:00 | 2023-01-25 05:54 | 918.1 | Blowdown Silica
Big Sandy 1 | D3 | 2023-01-26 02:00 | 2023-01-26 04:14 | 525.8 | Blowdown Silica.
Big Sandy 1 | D4 | 2023-01-27 08:00 | 2023-01-27 14:53 | 1620.3 | Vendor (Cutsforth) onsite to clean the Generator Brush Rigging.
Big Sandy 1 | U1 | 2023-01-29 07:21 | 2023-01-29 16:08 | 2594.5 | West Air Heater Upper Guide Bearing elevated vibration.
Big Sandy 1 | D1 | 2023-01-31 00:58 | 2023-01-31 05:47 | 459.6 | Feed pump governor issues
Big Sandy 1 | D1 | 2023-01-31 01:09 | 2023-01-31 01:47 | 0 | Feed pump governor issues
Big Sandy 1 | D1 | 2023-01-31 01:47 | 2023-01-31 03:16 | 0 | Feed pump governor issues
Big Sandy 1 | D1 | 2023-01-31 03:16 | 2023-01-31 04:06 | 0 | Feed pump governor issues
Big Sandy 1 | D1 | 2023-01-31 04:06 | 2023-01-31 05:47 | 16.2 | Feed pump governor issues
Big Sandy 1 | D1 | 2023-02-05 20:35 | 2023-02-06 01:25 | 654.3 | Feed Pump Govenor Valve issues
Big Sandy 1 | D1 | 2023-02-06 01:25 | 2023-02-09 | 9557.1 | Governor valve on boiler feed pump need calbrated
Big Sandy 1 | MO | 2023-02-09 00:35 | 2023-02-09 14:17 | 4047 | Request MO for ICE to troubleshoot/repair issue with BFPT Governor Valve controls
Big Sandy 1 | D4 | 2023-02-18 14:00 | 2023-02-18 14:20 | 65 | Weekly Valve check
Big Sandy 1 | D4 | 2023-02-25 03:00 | 2023-02-25 05:00 | 390.8 | Weekly Valve check
Big Sandy 1 | D1 | 2023-03-09 13:00 | 2023-03-09 13:34 | 133.5 | Air Heater Issues
Big Sandy 1 | D1 | 2023-03-09 13:34 | 2023-03-09 14:00 | 84.5 | Air Heater Issues
Big Sandy 1 | D1 | 2023-03-15 15:53 | 2023-03-15 17:00 | 218.3 | East/West FD Fan Inlet Dampers
Big Sandy 1 | D1 | 2023-03-15 17:00 | 2023-03-15 18:59 | 288.3 | Issues with the West FD Fan Inlet Damper
Big Sandy 1 | D1 | 2023-03-15 18:59 | 2023-03-15 22:17 | 561 | Issues with the West FD Fan Inlet Damper
Big Sandy 1 | D1 | 2023-03-15 22:17 | 2023-03-15 22:37 | 65 | Issues with the West FD Fan Inlet Damper
Big Sandy 1 | D1 | 2023-03-15 22:37 | 2023-03-16 | 256.4 | Issues with the West FD Fan Inlet Damper
Big Sandy 1 | D2 | 2023-03-16 | 2023-03-17 16:04 | 7428.4 | Issues with the West FD Fan Inlet Damper
Big Sandy 1 | D1 | 2023-03-23 13:19 | 2023-03-23 13:47 | 7.1 | Backpressure
Big Sandy 1 | D1 | 2023-03-23 13:47 | 2023-03-23 19:38 | 146.2 | Backpressure
Big Sandy 1 | D1 | 2023-03-23 19:38 | 2023-03-24 02:00 | 222.7 | Backpressure
Big Sandy 1 | D3 | 2023-03-24 02:00 | 2023-03-24 03:43 | 404.1 | Backwash Condenser
Big Sandy 1 | D4 | 2023-03-26 02:00 | 2023-03-26 05:16 | 768.9 | Weekly Valve check
Big Sandy 1 | D4 | 2023-03-31 08:00 | 2023-03-31 09:15 | 56.7 | ICE to stroke reheat attemperator RV-53
Big Sandy 1 | D1 | 2023-04-04 13:47 | 2023-04-04 16:03 | 46.4 | BFPT GV ran out.
Big Sandy 1 | D1 | 2023-04-04 16:03 | 2023-04-04 17:54 | 65.6 | BFPT GV ran out.
Big Sandy 1 | D1 | 2023-04-04 17:54 | 2023-04-05 06:00 | 665.5 | BFPT GV ran out.
Big Sandy 1 | D4 | 2023-04-05 06:00 | 2023-04-05 10:30 | 249.3 | Portersville to lift check Secondary Superheater Outlet Safety Valves
Big Sandy 1 | D4 | 2023-04-05 10:30 | 2023-04-05 12:45 | 124.7 | Portersville to lift check Reheat Outlet Header Safety Valves
Big Sandy 1 | D1 | 2023-04-05 15:57 | 2023-04-05 21:38 | 144.5 | BFPT GV ran out.
Big Sandy 1 | PO | 2023-04-08 02:25 | 2023-05-13 12:00 | 162346.8 | Boiler inpsection/repair, 600V Breaker upgrade.
Mitchell 1 | PO | 2021-10-16 | 2021-12-12 13:31 | 768957.9 | Boiler inpsection/repair, BOP repairs, SCR Catalyst #4 layer replacement, Boiler Feed Pump Element replacement.
Mitchell 1 | D4 | 2021-12-12 14:00 | 2021-12-19 07:00 | 19320.3 | #11 Pulverizer rebuild.
Mitchell 1 | MO | 2021-12-19 07:00 | 2021-12-23 08:32 | 75110.2 | to dewater cooling tower and install 11B Circulating Water Pump
Mitchell 1 | D4 | 2021-12-23 10:00 | 2021-12-31 07:37 | 22754.1 | #11 Pulverizer rebuild.
Mitchell 1 | U1 | 2022-03-24 13:00 | 2022-03-27 03:41 | 48272.2 | Aux. Boiler O/S
Mitchell 1 | U2 | 2022-03-27 11:00 | 2022-03-29 16:30 | 41200.4 | #16 Pulverizer Primary Air Ductwork failed.
Mitchell 1 | D1 | 2022-04-06 03:37 | 2022-04-06 10:47 | 2867.1 | Trona Ethernet communication issues.
Mitchell 1 | D4 | 2022-04-09 | 2022-04-09 16:19 | 1959.9 | #16 Pulverizer o/s
Mitchell 1 | D3 | 2022-04-10 19:00 | 2022-04-10 19:32 | 63.9 | Valve Checks
Mitchell 1 | D3 | 2022-04-10 19:32 | 2022-04-10 21:17 | 297.3 | Valve Checks
Mitchell 1 | U1 | 2022-04-13 17:24 | 2022-04-14 14:25 | 16185.2 | Extreme low deaerator alarm
Mitchell 1 | MO | 2022-04-14 14:26 | 2022-04-19 23:00 | 99009.4 | Deaerator Level control valve inpsection/repair; Boiler casing air test; Boiler inpsection/repair; Repair EHC leak on Reheat stop valve; Main Turbine 1st Reheat and HP Exhaust Steam Leads.
Mitchell 1 | D1 | 2022-04-25 21:03 | 2022-04-25 21:13 | 53.1 | Main steam issue
Mitchell 1 | D1 | 2022-04-25 21:13 | 2022-04-26 02:15 | 1611 | Main steam issue
Mitchell 1 | D4 | 2022-05-01 21:00 | 2022-05-01 22:33 | 418.9 | valve checks
Mitchell 1 | D4 | 2022-05-02 03:00 | 2022-05-02 20:00 | 1361.5 | 16 Pulverizer out of service to repair pyrite line.
Mitchell 1 | D1 | 2022-05-08 13:59 | 2022-05-09 18:45 | 2160.1 | #12 pulverizer feeder belt change out.
Mitchell 1 | D3 | 2022-05-10 | 2022-05-10 04:00 | 1600.3 | Must hold at 370Mw due to turning our silos over to Hi sulfur coal. This will set us up for 100% hi Sufur
Mitchell 1 | D4 | 2022-05-10 04:00 | 2022-05-10 10:16 | 2507.4 | 100% high sulfur coal operation testing.
Mitchell 1 | D4 | 2022-05-10 10:00 | 2022-05-10 11:15 | 315 | 100% high sulfur coal operation testing.
Mitchell 1 | D4 | 2022-05-10 11:15 | 2022-05-10 16:52 | 1236 | Ramp unit to 550MW for 100% High Sulfur testing
Mitchell 1 | D4 | 2022-05-10 16:52 | 2022-05-10 22:00 | 1129 | Raised Min to 550Mws. 100% high sulfur coal operation testing.
Mitchell 1 | D4 | 2022-05-10 23:00 | 2022-05-11 08:02 | 1987.6 | Max 550Mws. 100% high sulfur coal operation testing.
Mitchell 1 | D1 | 2022-05-11 16:29 | 2022-05-11 22:39 | 124 | ID fan High AMPS
Mitchell 1 | D1 | 2022-05-12 18:19 | 2022-05-12 23:00 | 94 | High ID Fan Amps
Mitchell 1 | D1 | 2022-05-14 16:12 | 2022-05-14 16:17 | 3.1 | ID fan Motor amps
Mitchell 1 | D1 | 2022-05-14 16:17 | 2022-05-15 | 154.8 | ID fan Motor amps
Mitchell 1 | D3 | 2022-05-14 23:00 | 2022-05-14 23:39 | 162.5 | Valve Checks
Mitchell 1 | D1 | 2022-05-17 15:00 | 2022-05-20 15:35 | 25048.3 | FMO-201 atemperator steam leak
Mitchell 1 | D1 | 2022-05-20 20:15 | 2022-05-21 11:04 | 1037.3 | Air cannon on 16 coal feeder broke off the side of raw coal pipe.
Mitchell 1 | D3 | 2022-05-21 14:00 | 2022-05-21 18:00 | 479.8 | Supply Start up steam to Unit 2
Mitchell 1 | D4 | 2022-05-21 18:00 | 2022-05-22 | 720 | Supply Start up steam to Unit 2
Mitchell 1 | D4 | 2022-05-22 | 2022-05-22 06:06 | 732.4 | Supply Start up steam to Unit 2
Mitchell 1 | D2 | 2022-05-23 01:22 | 2022-05-23 19:45 | 2206.3 | Supply Start up steam to Unit 2
Mitchell 1 | D1 | 2022-05-31 13:07 | 2022-05-31 14:10 | 10.8 | ESP Outlet pressure
Mitchell 1 | D1 | 2022-05-31 19:16 | 2022-05-31 20:00 | 7.7 | Precip ESP
Mitchell 1 | D1 | 2022-06-01 06:35 | 2022-06-01 09:54 | 1326.9 | Lost control of aux condenser level controller
Mitchell 1 | D4 | 2022-06-03 06:00 | 2022-06-04 15:59 | 2378.8 | #11 Pulverizer Pyrite Hopper Loop Seal leak repair.
Mitchell 1 | D4 | 2022-06-04 19:00 | 2022-06-04 20:49 | 490.6 | Weekly Valve Checks
Mitchell 1 | D4 | 2022-06-05 06:00 | 2022-06-05 16:16 | 718.5 | #12 Pulv 3000 Hr inpsection/repair
Mitchell 1 | D3 | 2022-06-07 06:00 | 2022-06-07 16:32 | 737 | 11 pulverizer pyrite hopper loop seal leak repair
Mitchell 1 | D4 | 2022-06-11 15:00 | 2022-06-11 16:34 | 422.8 | Weekend valve checks
Mitchell 1 | D2 | 2022-06-12 09:20 | 2022-06-13 14:56 | 595.3 | Supply steam to U2
Mitchell 1 | D1 | 2022-06-12 17:10 | 2022-06-12 17:52 | 42.4 | ESP outlet pressure
Mitchell 1 | D1 | 2022-06-12 17:52 | 2022-06-13 16:44 | 777.8 | ESP outlet pressure
Mitchell 1 | D1 | 2022-06-13 16:44 | 2022-06-13 17:00 | 7.7 | ESP outlet pressure
Mitchell 1 | D1 | 2022-06-13 17:00 | 2022-06-14 | 154 | ESP outlet pressure
Mitchell 1 | D1 | 2022-06-15 13:44 | 2022-06-15 15:00 | 13.1 | High Fan Amps on ID Fan
Mitchell 1 | D1 | 2022-06-15 15:00 | 2022-06-15 16:00 | 10 | High Fan Amps on ID Fan
Mitchell 1 | D1 | 2022-06-15 16:00 | 2022-06-15 17:26 | 21.6 | High Fan Amps on ID Fan
Mitchell 1 | D1 | 2022-06-15 17:26 | 2022-06-16 01:50 | 167.9 | High Fan Amps on ID Fan
Mitchell 1 | D1 | 2022-06-16 12:54 | 2022-06-16 13:53 | 20 | High Fan Amps on ID Fan
Mitchell 1 | D1 | 2022-06-16 13:53 | 2022-06-16 21:54 | 136.3 | High Fan Amps on ID Fan
Mitchell 1 | D4 | 2022-06-18 19:00 | 2022-06-18 20:51 | 499.8 | Valve Checks
Mitchell 1 | D3 | 2022-06-21 | 2022-06-23 | 964.9 | ID Fan amp limitations.
Mitchell 1 | D1 | 2022-06-22 15:00 | 2022-06-22 22:00 | 70.1 | ESP Outlet pressure
Mitchell 1 | D4 | 2022-06-24 21:00 | 2022-06-24 22:00 | 270.3 | Weekly Valve Checks
Mitchell 1 | D4 | 2022-06-25 06:00 | 2022-06-25 15:38 | 674.6 | 16 pulverizer out of service to repair lube oil piping
Mitchell 1 | D4 | 2022-06-25 15:38 | 2022-06-25 17:23 | 122.4 | 15 pulverizer out of service to repair lube oil piping
Mitchell 1 | D1 | 2022-06-27 00:30 | 2022-06-27 03:06 | 1040.4 | Ammonia Injection needs to be removed from service make repairs to leak on common line
Mitchell 1 | U1 | 2022-06-27 03:07 | 2022-07-05 02:00 | 146999 | Economizer tube leak
Mitchell 1 | U1 | 2022-07-05 05:34 | 2022-07-06 04:00 | 17275.7 | Possible leak in HP steam line
Mitchell 1 | D1 | 2022-07-07 16:10 | 2022-07-08 | 157.1 | High ESP Outlet Pressure
Mitchell 1 | D4 | 2022-07-09 14:00 | 2022-07-09 15:46 | 388.9 | Weekly Valve Checks
Mitchell 1 | D1 | 2022-07-11 15:22 | 2022-07-12 04:26 | 1177.5 | Supplying steam for #2 start up
Mitchell 1 | D4 | 2022-07-16 19:00 | 2022-07-16 20:47 | 481.3 | Weekend valve checks
Mitchell 1 | D1 | 2022-07-19 16:50 | 2022-07-19 17:08 | 23.1 | Trona/Injection Issues
Mitchell 1 | D1 | 2022-07-19 17:08 | 2022-07-19 21:15 | 1111.3 | Hydrolyzer Issues
Mitchell 1 | D1 | 2022-07-20 14:47 | 2022-07-20 16:44 | 78.6 | Outlet pressure and ID Fan Amps
Mitchell 1 | D1 | 2022-07-20 16:44 | 2022-07-21 07:00 | 499 | Outlet pressure and ID Fan Amps
Mitchell 1 | D1 | 2022-07-21 13:53 | 2022-07-21 15:38 | 52.4 | ESP Outlet pressure and ID Fan Amps
Mitchell 1 | D1 | 2022-07-21 15:38 | 2022-07-22 | 335 | ESP Outlet pressure and ID Fan Amps
Mitchell 1 | D1 | 2022-07-22 16:55 | 2022-07-22 17:54 | 29.3 | ESP Outlet pressure and ID Fan Amps
Mitchell 1 | D1 | 2022-07-22 17:54 | 2022-07-23 | 244.1 | ESP Outlet pressure and ID Fan Amps
Mitchell 1 | D4 | 2022-07-23 06:30 | 2022-07-24 05:24 | 1605.7 | Supply Start up steam to Unit 2
Mitchell 1 | D1 | 2022-07-24 15:00 | 2022-07-24 17:01 | 50.8 | ESP Outlet pressure and ID Fan Amps
Mitchell 1 | D1 | 2022-07-24 17:01 | 2022-07-24 18:32 | 7.7 | ESP Outlet pressure and ID Fan Amps
Mitchell 1 | D1 | 2022-07-24 18:32 | 2022-07-25 | 218.7 | ESP Outlet pressure and ID Fan Amps
Mitchell 1 | D1 | 2022-07-25 17:42 | 2022-07-26 | 189.4 | ESP Outlet pressure
Mitchell 1 | D1 | 2022-07-26 08:30 | 2022-07-26 12:55 | 1192.9 | B string of HP heaters o/s
Mitchell 1 | D1 | 2022-07-28 16:25 | 2022-07-28 16:51 | 8.5 | ESP outlet pressure
Mitchell 1 | D1 | 2022-07-28 16:51 | 2022-07-28 23:00 | 184.8 | ESP outlet pressure
Mitchell 1 | D4 | 2022-07-30 01:00 | 2022-07-30 02:10 | 315 | Valve Check
Mitchell 1 | D1 | 2022-08-01 15:26 | 2022-08-01 18:00 | 51.6 | ESP Outlet Pressure and ID Fan Amps
Mitchell 1 | D1 | 2022-08-01 18:00 | 2022-08-01 23:00 | 150.2 | ESP Outlet Pressure and ID Fan Amps
Mitchell 1 | D1 | 2022-08-02 13:54 | 2022-08-02 23:00 | 183.3 | ESP Outlet Pressure and ID Fan Amps
Mitchell 1 | D1 | 2022-08-03 07:00 | 2022-08-03 11:30 | 360.4 | #15 Pulverizer out of service to repair coal leaks
Mitchell 1 | D1 | 2022-08-03 16:46 | 2022-08-03 17:02 | 5.4 | ESP Outlet Pressure and ID Fan Amps
Mitchell 1 | D1 | 2022-08-03 17:02 | 2022-08-03 17:55 | 27 | ESP Outlet Pressure and ID Fan Amps
Mitchell 1 | D1 | 2022-08-03 17:55 | 2022-08-03 22:00 | 102.4 | ESP Outlet Pressure and ID Fan Amps
Mitchell 1 | D1 | 2022-08-04 15:35 | 2022-08-04 16:00 | 16.9 | ESP Outlet Pressure and ID Fan Amps
Mitchell 1 | D1 | 2022-08-04 16:00 | 2022-08-05 | 241 | ESP Outlet Pressure and ID Fan Amps
Mitchell 1 | D1 | 2022-08-05 16:32 | 2022-08-05 19:00 | 73.9 | ESP Outlet Pressure and ID Fan Amps
Mitchell 1 | D4 | 2022-08-06 07:48 | 2022-08-06 08:20 | 144 | Valve Check
Mitchell 1 | D4 | 2022-08-06 13:00 | 2022-08-06 13:30 | 14.6 | ESP Outlet Pressure and ID Fan Amps limitations
Mitchell 1 | D4 | 2022-08-06 13:30 | 2022-08-06 20:00 | 194.8 | ESP Outlet Pressure and ID Fan Amps limitations
Mitchell 1 | D4 | 2022-08-07 17:25 | 2022-08-07 21:00 | 107.8 | ESP Outlet Pressure and ID Fan Amps limitations
Mitchell 1 | D1 | 2022-08-08 04:55 | 2022-08-08 05:24 | 130.9 | Pulverizer
Mitchell 1 | D1 | 2022-08-08 05:24 | 2022-08-08 10:45 | 1632.6 | #15 and 16 Coal Mills o/s for repairs.
Mitchell 1 | D2 | 2022-08-08 10:45 | 2022-08-08 13:11 | 365 | 16 Mill out of service
Mitchell 1 | D2 | 2022-08-08 10:45 | 2022-08-08 11:00 | 37.7 | 15 mill out of service
Mitchell 1 | D1 | 2022-08-08 11:41 | 2022-08-08 11:47 | 12.3 | 15 mill - problem return mill to service.
Mitchell 1 | D2 | 2022-08-08 13:11 | 2022-08-08 16:26 | 260.3 | 16 Mill out of service
Mitchell 1 | D1 | 2022-08-08 13:46 | 2022-08-08 16:29 | 163.3 | HP heater string o/s
Mitchell 1 | D1 | 2022-08-08 16:30 | 2022-08-08 23:00 | 194.8 | ESP Outlet Pressure and ID Fan Amps limitations.
Mitchell 1 | D3 | 2022-08-09 13:00 | 2022-08-09 20:00 | 210.2 | ESP Outlet Pressure and ID Fan Amps limitations.
Mitchell 1 | D3 | 2022-08-10 11:00 | 2022-08-10 20:00 | 270.3 | ESP Outlet Pressure and ID Fan Amps limitations.
Mitchell 1 | D3 | 2022-08-11 11:00 | 2022-08-11 20:00 | 270.3 | ESP Outlet Pressure and ID Fan Amps limitations.
Mitchell 1 | D3 | 2022-08-12 11:00 | 2022-08-13 08:05 | 632.3 | ESP Outlet Pressure and ID Fan Amps limitations.
Mitchell 1 | D3 | 2022-08-13 11:00 | 2022-08-14 08:00 | 629.9 | ESP Outlet Pressure and ID Fan Amps limitations.
Mitchell 1 | D4 | 2022-08-13 23:00 | 2022-08-14 | 190.2 | Valve checks
Mitchell 1 | D1 | 2022-08-14 11:00 | 2022-08-15 08:00 | 632.3 | ESP Outlet Pressure and ID Fan Amps limitations.
Mitchell 1 | D1 | 2022-08-14 11:00 | 2022-08-15 08:00 | 1470.1 | ESP Outlet Pressure and ID Fan Amps limitations.
Mitchell 1 | D1 | 2022-08-15 11:00 | 2022-08-15 20:00 | 271.1 | ESP Outlet Pressure and ID Fan Amps limitations.
Mitchell 1 | D1 | 2022-08-17 04:39 | 2022-08-18 16:57 | 2904 | Coal Leaks on 12 Pulverizer
Mitchell 1 | D4 | 2022-08-17 06:00 | 2022-08-17 14:00 | 0.8 | Clean and inspect lube oil cooler on #13 pulverizer. Unit will be curtailed approximately 80 Mw from 0600-1500.
Mitchell 1 | D1 | 2022-08-17 14:00 | 2022-08-17 20:05 | 974.2 | Clean and inspect lube oil cooler on #13 pulverizer
Mitchell 1 | D4 | 2022-08-18 06:00 | 2022-08-18 16:57 | 0.8 | #12 Pulverizer o/s to inpsection/repair the Classifiers.
Mitchell 1 | D4 | 2022-08-19 20:00 | 2022-08-19 21:14 | 209.5 | Weekly Valve Check
Mitchell 1 | D1 | 2022-08-22 16:21 | 2022-08-22 17:12 | 33.9 | Opacity
Mitchell 1 | D1 | 2022-08-22 17:13 | 2022-08-22 18:00 | 47 | Opacity
Mitchell 1 | D1 | 2022-08-22 18:00 | 2022-08-23 | 540.6 | Opacity
Mitchell 1 | D1 | 2022-08-23 18:08 | 2022-08-24 | 205.6 | ESP Outlet pressure
Mitchell 1 | D1 | 2022-08-25 13:00 | 2022-08-25 17:18 | 129.4 | Expected ESP outlet pressure and ID fan amp issues
Mitchell 1 | D3 | 2022-08-25 13:00 | 2022-08-25 22:00 | 271.1 | Expected ESP outlet pressure and ID fan amp issues
Mitchell 1 | D1 | 2022-08-25 22:00 | 2022-08-26 07:00 | 271.1 | Expected ESP outlet pressure and ID fan amp issues
Mitchell 1 | D3 | 2022-08-25 22:05 | 2022-08-26 07:00 | 0 | Expected ESP outlet pressure and ID fan amp issues
Mitchell 1 | D3 | 2022-08-26 13:00 | 2022-08-27 13:00 | 722.4 | Anticipated ESP outlet pressure and ID Fan amp issues
Mitchell 1 | D4 | 2022-08-26 23:00 | 2022-08-27 | 240.3 | Weekly Valve Checks
Mitchell 1 | D4 | 2022-08-27 | 2022-08-27 00:01 | 0.8 | #16 Pulverizer o/s
Mitchell 1 | D3 | 2022-08-27 13:00 | 2022-08-28 13:00 | 722.4 | Anticipated ESP outlet pressure and ID Fan amp issues
Mitchell 1 | D3 | 2022-08-28 13:00 | 2022-08-29 13:00 | 722.4 | Anticipated ESP outlet pressure and ID Fan amp issues
Mitchell 1 | D3 | 2022-08-29 13:00 | 2022-08-29 22:00 | 271.1 | Anticipated ESP Outlet Pressure and ID Fan Amp limitations.
Mitchell 1 | D3 | 2022-08-31 13:30 | 2022-08-31 16:59 | 278.8 | #15 pulverizer coal feeder belt has a splice coming apart. May need belt changed.
Mitchell 1 | D1 | 2022-08-31 17:51 | 2022-08-31 23:59 | 429.7 | 13 pulverizer unavailable due to failed oil pump seal
Mitchell 1 | D1 | 2022-09-01 | 2022-09-01 16:52 | 1180.6 | 13 pulverizer unavailable due to failed oil pump seal.
Mitchell 1 | D4 | 2022-09-03 | 2022-09-04 17:00 | 3279.9 | #11 Pulverizer o/s
Mitchell 1 | D4 | 2022-09-03 00:40 | 2022-09-03 01:10 | 94.7 | Valve Check
Mitchell 1 | D4 | 2022-09-09 22:08 | 2022-09-09 23:22 | 333.5 | Weekly Valve Checks
Mitchell 1 | D1 | 2022-09-21 17:00 | 2022-09-21 17:29 | 43.9 | Opacity
Mitchell 1 | D1 | 2022-09-21 17:29 | 2022-09-22 | 489 | Opacity
Mitchell 1 | MO | 2022-09-24 | 2022-10-08 | 258753.6 | Repair feed pump turbine steam supply regulating valve.
Mitchell 1 | PO | 2022-10-08 | 2022-11-19 17:32 | 790533.1 | Boiler inpsection/repair, Precip inpsection/repair, Pulverizer/Feeder MATS inpsection/repair, Economizer wash, Replace Precip Transformer power cables, Replace SCR XJ s 14,15 and 115, Replace Exit Duct XJ FGX-71009, Water Cannon upgrades, Ovation Evergreen upgrade, Inter-lock testing, HE Piping inpsection/repair.
Mitchell 1 | D2 | 2022-11-30 10:37 | 2022-11-30 19:38 | 3112 | HP Heater drain 7A stuck open
Mitchell 1 | D1 | 2022-12-01 03:48 | 2022-12-01 04:01 | 37 | Ammonia injection issues.
Mitchell 1 | D1 | 2022-12-01 04:01 | 2022-12-01 08:40 | 1255.3 | Ammonia injection issues.
Mitchell 1 | D1 | 2022-12-01 08:40 | 2022-12-01 18:07 | 944.9 | 15 pulv oil lighter issues.
Mitchell 1 | D1 | 2022-12-01 10:19 | 2022-12-01 18:07 | 351.9 | Pulv damper issues
Mitchell 1 | D1 | 2022-12-01 13:12 | 2022-12-01 16:36 | 340.4 | Coal equipment issues
Mitchell 1 | D1 | 2022-12-01 18:44 | 2022-12-01 23:59 | 499 | Opacity
Mitchell 1 | D1 | 2022-12-01 20:00 | 2022-12-01 22:07 | 0 | Conduct a water loss test on Unit 1 from 2000-2200. This will require Unit 1 to be at a steady load for the duration of the test. Test will be conducted at 675 MW Net
Mitchell 1 | D1 | 2022-12-02 02:34 | 2022-12-02 02:41 | 3.9 | Opacity
Mitchell 1 | D1 | 2022-12-02 02:41 | 2022-12-02 03:33 | 34.7 | Opacity
Mitchell 1 | D1 | 2022-12-02 03:33 | 2022-12-02 21:00 | 610.7 | Opacity
Mitchell 1 | MO | 2022-12-03 01:47 | 2022-12-08 09:18 | 98200.8 | Economizer tube leak repair
Mitchell 1 | U1 | 2022-12-08 11:45 | 2022-12-09 | 9433.7 | PH Issues
Mitchell 1 | U1 | 2022-12-09 | 2022-12-10 08:01 | 24656.3 | due to Urea from Hydrolyzer system entering the Condensate Return System. Samples will be collected and tested once the unit cools. Hydrolyzer will need pressurized to search for potential leaks.
Mitchell 1 | U1 | 2022-12-10 13:07 | 2022-12-13 16:30 | 58052.4 | Due to Primary Superheater Outlet valve . packing blew out. Superheater Bypass Control valve URV 4, controller failed closed due to burned up controller.
Mitchell 1 | D1 | 2022-12-15 07:59 | 2022-12-15 08:36 | 43.1 | Opacity
Mitchell 1 | D1 | 2022-12-15 08:36 | 2022-12-15 08:56 | 14.6 | Opacity
Mitchell 1 | D1 | 2022-12-15 08:56 | 2022-12-15 09:10 | 9.2 | Opacity
Mitchell 1 | D1 | 2022-12-15 13:00 | 2022-12-15 19:01 | 422 | Supply Steam for Unit 2 Start up
Mitchell 1 | D1 | 2022-12-15 14:40 | 2022-12-15 16:28 | 90.1 | Coal leak on Mill, need to swap it
Mitchell 1 | D1 | 2022-12-15 19:01 | 2022-12-17 14:33 | 3051.9 | Supply Steam for Unit 2 Start up
Mitchell 1 | D1 | 2022-12-17 14:41 | 2022-12-17 16:37 | 135.5 | MATS TESTING
Mitchell 1 | D1 | 2022-12-18 15:14 | 2022-12-18 18:00 | 1106.6 | Hydrolyzer trip
Mitchell 1 | D1 | 2022-12-18 18:00 | 2022-12-18 22:00 | 1999.9 | Hydrolyzer trip. Loss of Ammonia injection
Mitchell 1 | D1 | 2022-12-18 22:00 | 2022-12-18 23:10 | 432 | Hydrolyzer trip. Loss of Ammonia injection
Mitchell 1 | D1 | 2022-12-18 23:10 | 2022-12-19 00:42 | 414.3 | Hydrolyzer trip. Loss of Ammonia injection
Mitchell 1 | D1 | 2022-12-19 01:20 | 2022-12-19 01:48 | 233.3 | Leak found in Ammonia injection valve
Mitchell 1 | D1 | 2022-12-19 04:43 | 2022-12-19 07:00 | 23.1 | Opacity
Mitchell 1 | D1 | 2022-12-19 17:30 | 2022-12-21 03:00 | 2345 | Supply Start up steam to Unit 2
Mitchell 1 | D1 | 2022-12-21 03:36 | 2022-12-21 07:00 | 85.5 | ESP Outlet Pressure
Mitchell 1 | D1 | 2022-12-21 05:02 | 2022-12-21 07:00 | 88.6 | opacity
Mitchell 1 | D1 | 2022-12-21 10:40 | 2022-12-22 08:00 | 428.9 | ESP Pressure
Mitchell 1 | D1 | 2022-12-21 20:52 | 2022-12-22 | 469.8 | Ammonia injection valve issue
Mitchell 1 | D3 | 2022-12-22 | 2022-12-30 | 6719.9 | Large clinker growing on North side of Boiler
Mitchell 1 | D1 | 2022-12-24 06:48 | 2022-12-24 07:06 | 139.4 | Reagent slurry feed tanks have frozen level indications and tanks were lower than expected
Mitchell 1 | D1 | 2022-12-24 07:06 | 2022-12-24 07:43 | 60.1 | Reagent slurry feed tanks have frozen level indications and tanks were lower than expected
Mitchell 1 | D1 | 2022-12-24 07:43 | 2022-12-24 08:20 | 286.5 | Reagent slurry feed tanks have frozen level indications and tanks were lower than expected
Mitchell 1 | D1 | 2022-12-24 08:20 | 2022-12-24 12:00 | 513.7 | Reagent slurry feed tanks have frozen level indications and tanks were lower than expected
Mitchell 1 | D1 | 2022-12-24 13:48 | 2022-12-24 19:34 | 462.1 | Opacity
Mitchell 1 | D1 | 2022-12-24 19:34 | 2022-12-25 09:00 | 1210.6 | Opacity
Mitchell 1 | D1 | 2022-12-25 10:07 | 2022-12-25 12:31 | 324.2 | Frozen lumps of coal causing conveyor trip out outs
Mitchell 1 | D1 | 2022-12-26 00:20 | 2022-12-26 08:29 | 367.3 | Opacity
Mitchell 1 | D1 | 2022-12-26 08:29 | 2022-12-26 08:46 | 16.9 | Opacity
Mitchell 1 | D1 | 2022-12-26 08:46 | 2022-12-27 | 1296.1 | Opacity
Mitchell 1 | D3 | 2022-12-27 | 2022-12-27 01:40 | 141.7 | Opacity
Mitchell 1 | D3 | 2022-12-27 01:40 | 2022-12-27 02:02 | 49.3 | Opacity
Mitchell 1 | D3 | 2022-12-27 02:02 | 2022-12-27 02:53 | 131.7 | Opacity
Mitchell 1 | D3 | 2022-12-27 02:53 | 2022-12-27 04:43 | 339.6 | Opacity
Mitchell 1 | D3 | 2022-12-27 04:43 | 2022-12-27 07:22 | 543.7 | Opacity
Mitchell 1 | D3 | 2022-12-27 07:22 | 2022-12-27 11:03 | 865.6 | Opacity
Mitchell 1 | D3 | 2022-12-27 11:03 | 2022-12-28 | 3174.4 | Opacity
Mitchell 1 | D3 | 2022-12-28 | 2022-12-28 00:50 | 195.6 | Opacity
Mitchell 1 | D3 | 2022-12-28 00:50 | 2022-12-28 05:41 | 921.8 | Opacity
Mitchell 1 | D3 | 2022-12-28 05:41 | 2022-12-28 08:14 | 803.2 | Opacity
Mitchell 1 | D3 | 2022-12-28 08:14 | 2022-12-30 | 12327.8 | Opacity
Mitchell 1 | MO | 2022-12-30 | 2023-01-22 17:59 | 438943.9 | Boiler inpsection/repair, Boiler Hydro, Duct repairs, Clinker Removal, IK Soot Blower Repairs, 12 ID Fan Stall margin probe inpsection/repair.
Mitchell 1 | U1 | 2023-01-24 12:09 | 2023-02-03 16:27 | 188135.4 | UMO-1 PSO Outlet Valve packing failed.
Mitchell 1 | D1 | 2023-02-12 02:59 | 2023-02-14 15:18 | 4831.6 | 13 Pulverizer unavailable due to 13 feeder gearbox needing replaced.
Mitchell 1 | D1 | 2023-02-15 12:47 | 2023-02-17 19:00 | 7861.2 | opacity limitations
Mitchell 1 | D1 | 2023-02-17 19:00 | 2023-02-22 | 7080.3 | #14 pulverizer gear box
Mitchell 1 | D3 | 2023-02-17 22:00 | 2023-02-18 00:41 | 536.8 | Valve Check
Mitchell 1 | D3 | 2023-02-22 | 2023-02-24 14:09 | 4356.5 | #14 pulverizer gear box
Mitchell 1 | D4 | 2023-02-22 05:00 | 2023-02-23 20:00 | 3506.3 | #11 pulverizer 3,000 hour inspection/repair.
Mitchell 1 | D3 | 2023-02-24 14:09 | 2023-03-16 | 28740.1 | #14 pulverizer Coal Feeder Gear Box
Mitchell 1 | D3 | 2023-02-25 09:00 | 2023-02-25 11:07 | 444.3 | Valve Check
Mitchell 1 | D4 | 2023-02-27 12:00 | 2023-03-01 14:42 | 1253.7 | #13 pulverizer 3,000 hour inspection/repair.
Mitchell 1 | D4 | 2023-03-02 05:00 | 2023-03-03 11:25 | 608.4 | #12 pulverizer 3,000 hour inspection/repair
Mitchell 1 | D4 | 2023-03-03 11:25 | 2023-03-03 11:29 | 43.1 | #12 pulverizer 3,000 hour inspection/repair
Mitchell 1 | D4 | 2023-03-03 11:29 | 2023-03-03 17:33 | 364.3 | #12 pulverizer 3,000 hour inspection/repair
Mitchell 1 | D4 | 2023-03-03 19:00 | 2023-03-03 20:52 | 392 | Perform weekly turbine valve checks
Mitchell 1 | D3 | 2023-03-11 19:00 | 2023-03-11 21:00 | 420.5 | Weekly Valve Checks
Mitchell 1 | MO | 2023-03-16 01:28 | 2023-03-16 14:53 | 10332.4 | Main Steam Lead greylock drain line leak
Mitchell 1 | MO | 2023-03-16 14:53 | 2023-03-21 23:17 | 98880.8 | Main Steam Line Above Seat Drain steam leak
Mitchell 1 | D3 | 2023-03-21 23:17 | 2023-04-06 16:47 | 24047.1 | #14 Pulverizer Coal Feeder Gear Box o/s.
Mitchell 1 | D4 | 2023-03-24 19:30 | 2023-03-24 21:05 | 332.7 | Weekly Valve check
Mitchell 1 | D4 | 2023-04-01 19:00 | 2023-04-01 21:00 | 420.5 | Weekly Valve check
Mitchell 1 | D4 | 2023-04-12 05:00 | 2023-04-13 16:15 | 4230.2 | #15 Pulverizer oil change
Mitchell 1 | PO | 2023-04-15 04:31 | 2023-05-12 18:00 | 292239.9 | Boiler inpsection/repair, Precipitator inpsection/repair, Sicon Conveyor Tail Pulley structural steel repairs, relocation of the 2#4 River Water feed to FGD in the foundation of the new ash bunker, BOP repairs, dual outage to prep for Fall Outage.
Mitchell 2 | MO | 2021-10-22 | 2021-11-06 09:54 | 102647 | Boiler inpsection/repair, UMO-803 inpsection/repair, Dry Fly Ash repairs, FGD repairs, FMO-101 inpsection/repair, #1 Control Valve EHC line inpsection/repair.
Mitchell 2 | U1 | 2021-11-13 07:44 | 2021-11-15 01:00 | 32609.2 | Steam Lead Drain Leak
Mitchell 2 | D1 | 2021-11-15 19:00 | 2021-11-15 19:21 | 66.4 | Opacity
Mitchell 2 | D1 | 2021-11-16 | 2021-11-16 00:35 | 134.3 | Pulverizer issues
Mitchell 2 | D1 | 2021-11-16 19:27 | 2021-11-16 20:14 | 94 | 26 feeder not receiving no coal alarm" when coal becomes plugged in coal chute to feeder."
Mitchell 2 | D1 | 2021-11-16 20:29 | 2021-11-17 15:06 | 2237.8 | 25 pulverizer capacity damper linkage broke off
Mitchell 2 | D1 | 2021-11-17 14:10 | 2021-11-17 14:38 | 45.8 | loss of #6 mill
Mitchell 2 | D1 | 2021-11-17 14:38 | 2021-11-17 15:05 | 53.7 | loss of #6 mill
Mitchell 2 | D1 | 2021-11-17 18:55 | 2021-11-17 20:13 | 65.6 | Opacity
Mitchell 2 | D1 | 2021-11-19 08:23 | 2021-11-19 13:47 | 621.9 | ICE to stroke #25 capacity Damper
Mitchell 2 | D1 | 2021-11-19 23:57 | 2021-11-20 | 11.9 | #25 Pulverizer Capacity Damper needs inspected. There is too much air on the pulverizer with minimal opening on the damper. This pulverizer is unavailable until this issue is resolved.
Mitchell 2 | D4 | 2021-11-20 | 2021-11-20 11:41 | 1403.4 | 22 pulverizer out of service.
Mitchell 2 | D1 | 2021-11-20 | 2021-11-20 11:41 | 1403.4 | #25 Pulverizer Capacity Damper needs inspected. There is too much air on the pulverizer with minimal opening on the damper. This pulverizer is unavailable until this issue is resolved.
Mitchell 2 | D1 | 2021-11-20 11:41 | 2021-11-21 16:57 | 3511.6 | #25 Pulverizer o/s
Mitchell 2 | D4 | 2021-11-20 11:48 | 2021-11-22 16:16 | 6296.3 | 22 pulverizer out of service - please refer to previously approved duration on eDART ticket # 1551019
Mitchell 2 | D1 | 2021-11-23 07:25 | 2021-11-23 11:55 | 181 | Opacity
Mitchell 2 | D1 | 2021-11-23 11:55 | 2021-11-23 15:00 | 92.5 | Opacity
Mitchell 2 | D1 | 2021-11-29 19:06 | 2021-11-30 11:28 | 166.7 | opacity
Mitchell 2 | D1 | 2021-11-30 09:25 | 2021-11-30 11:28 | 983.8 | Valve issue, Packing blew out on FRV-101(Main Steam Attemperator)
Mitchell 2 | U3 | 2021-11-30 11:30 | 2021-12-02 05:38 | 33293.5 | Valve issue. Packing blew out on FRV-101(Main Steam Attemperator)
Mitchell 2 | D1 | 2021-12-02 13:56 | 2021-12-02 15:26 | 90.1 | Opacity
Mitchell 2 | D1 | 2021-12-02 15:26 | 2021-12-02 23:00 | 302.6 | Opacity
Mitchell 2 | D1 | 2021-12-03 01:37 | 2021-12-03 10:34 | 1254.8 | Coal Leak #23 Pulverizer
Mitchell 2 | D1 | 2021-12-03 11:53 | 2021-12-04 07:00 | 386.4 | Opacity
Mitchell 2 | D4 | 2021-12-03 23:00 | 2021-12-04 00:33 | 341.4 | Weekly Valve check
Mitchell 2 | U2 | 2021-12-04 08:00 | 2021-12-05 10:19 | 20795.7 | UMO-1 packing leak (super heater bypass line)
Mitchell 2 | D1 | 2021-12-07 15:48 | 2021-12-07 16:31 | 7.1 | Opacity
Mitchell 2 | D1 | 2021-12-07 16:31 | 2021-12-08 07:05 | 291.6 | Opacity
Mitchell 2 | D1 | 2021-12-08 06:35 | 2021-12-08 07:04 | 9.5 | Opacity
Mitchell 2 | D1 | 2021-12-08 07:05 | 2021-12-08 07:31 | 21.3 | Opacity
Mitchell 2 | D1 | 2021-12-08 07:31 | 2021-12-08 17:16 | 682.7 | Opacity
Mitchell 2 | D1 | 2021-12-08 17:16 | 2021-12-09 06:18 | 1172.7 | Opacity
Mitchell 2 | D1 | 2021-12-09 06:18 | 2021-12-09 21:02 | 1326 | opacity issues
Mitchell 2 | D1 | 2021-12-09 21:02 | 2021-12-11 12:43 | 3968.4 | opacity issues
Mitchell 2 | D4 | 2021-12-11 | 2021-12-11 00:42 | 66.4 | Weekly Valve checks
Mitchell 2 | D1 | 2021-12-11 12:43 | 2021-12-11 12:46 | 23.7 | opacity issues
Mitchell 2 | D1 | 2021-12-11 12:46 | 2021-12-11 13:39 | 238.6 | opacity issues
Mitchell 2 | D1 | 2021-12-11 13:39 | 2021-12-13 22:25 | 5676.8 | opacity issues
Mitchell 2 | D1 | 2021-12-11 13:56 | 2021-12-11 14:41 | 285.3 | Coal Handler Issues
Mitchell 2 | D1 | 2021-12-13 22:25 | 2021-12-13 22:30 | 7.1 | opacity issues
Mitchell 2 | D1 | 2021-12-13 22:30 | 2021-12-15 10:30 | 3563.8 | opacity issues
Mitchell 2 | D1 | 2021-12-15 10:30 | 2021-12-15 23:00 | 1125.2 | opacity issues
Mitchell 2 | D4 | 2021-12-15 23:00 | 2021-12-16 06:00 | 3431 | Precipitator Power off Rap
Mitchell 2 | D1 | 2021-12-16 19:35 | 2021-12-16 20:00 | 25.3 | Opacity
Mitchell 2 | D1 | 2021-12-16 19:35 | 2021-12-16 19:36 | 0.8 | Opacity
Mitchell 2 | D1 | 2021-12-16 19:36 | 2021-12-16 20:32 | 32.4 | Opacity
Mitchell 2 | D1 | 2021-12-16 20:32 | 2021-12-20 15:18 | 9077 | Opacity
Mitchell 2 | D4 | 2021-12-18 02:00 | 2021-12-18 02:01 | 2.4 | Weekly Valve Check
Mitchell 2 | D4 | 2021-12-18 02:01 | 2021-12-18 03:00 | 0 | Weekly Valve Check
Mitchell 2 | D4 | 2021-12-18 02:01 | 2021-12-18 03:05 | 79.8 | Weekly Valve Check
Mitchell 2 | D4 | 2021-12-18 23:00 | 2021-12-19 05:06 | 2380.1 | Power off rapping to clean up precipitator.
Mitchell 2 | D4 | 2021-12-19 23:00 | 2021-12-20 06:00 | 2731.7 | Power off rapping to clean up precipitator.
Mitchell 2 | D1 | 2021-12-20 15:18 | 2021-12-20 23:00 | 577.6 | Opacity
Mitchell 2 | D4 | 2021-12-20 23:00 | 2021-12-21 04:05 | 2491.5 | Power off rapping
Mitchell 2 | D3 | 2021-12-21 06:00 | 2021-12-21 06:02 | 4 | Anticipated opacity
Mitchell 2 | D3 | 2021-12-21 06:02 | 2021-12-21 08:29 | 0 | Opacity
Mitchell 2 | D3 | 2021-12-21 06:02 | 2021-12-21 23:00 | 1019.4 | Anticipated opacity
Mitchell 2 | D3 | 2021-12-21 08:29 | 2021-12-21 09:22 | 0 | Opacity
Mitchell 2 | D3 | 2021-12-21 09:22 | 2021-12-21 12:39 | 0 | Opacity
Mitchell 2 | D3 | 2021-12-21 12:39 | 2021-12-21 16:43 | 0 | Opacity
Mitchell 2 | D3 | 2021-12-21 16:43 | 2021-12-21 17:17 | 0 | Opacity
Mitchell 2 | D3 | 2021-12-21 17:17 | 2021-12-21 19:46 | 0 | Opacity
Mitchell 2 | D3 | 2021-12-21 19:46 | 2021-12-21 23:00 | 0 | Opacity
Mitchell 2 | D4 | 2021-12-21 23:00 | 2021-12-22 00:18 | 636.9 | Power off rapping
Mitchell 2 | U1 | 2021-12-22 00:18 | 2021-12-22 16:18 | 12643.2 | Reason Unknown. #1 Control valve LVDT positioner arm broke causing #1 control valve to close and become inoperable
Mitchell 2 | D1 | 2021-12-23 04:15 | 2021-12-23 13:20 | 183.3 | Opacity
Mitchell 2 | D1 | 2021-12-23 13:20 | 2021-12-23 23:00 | 580 | Opacity
Mitchell 2 | D4 | 2021-12-23 23:00 | 2021-12-24 05:30 | 3186.1 | Precipitator Power off rapping the precipitator fields
Mitchell 2 | D1 | 2021-12-27 11:56 | 2021-12-27 12:19 | 72.7 | Reagent slurry
Mitchell 2 | D1 | 2021-12-27 12:19 | 2021-12-27 13:28 | 275.8 | Reagent slurry
Mitchell 2 | D3 | 2021-12-28 06:00 | 2021-12-28 13:49 | 1096 | 23E pulverizer burner line coal leak repair
Mitchell 2 | D1 | 2021-12-28 15:15 | 2021-12-28 22:00 | 676.4 | Opacity
Mitchell 2 | D1 | 2021-12-29 07:48 | 2021-12-29 21:05 | 1328.3 | Opacity limitations
Mitchell 2 | D1 | 2021-12-29 21:05 | 2021-12-29 23:00 | 211 | Opacity limitations
Mitchell 2 | D4 | 2021-12-29 23:00 | 2021-12-30 04:09 | 2523.1 | Power off Rap precipitator fields
Mitchell 2 | D3 | 2021-12-30 06:00 | 2021-12-30 23:00 | 1699.7 | Opacity limitations
Mitchell 2 | D4 | 2021-12-30 23:00 | 2021-12-31 05:05 | 2980.6 | Power off Rap precipitator fields
Mitchell 2 | D3 | 2021-12-31 05:05 | 2022-01-01 06:00 | 3000.4 | Opacity limitations
Mitchell 2 | D1 | 2021-12-31 17:10 | 2021-12-31 22:37 | 2126.4 | U2A Hydrolyzer valve leaking need to replace.
Mitchell 2 | D3 | 2022-01-01 06:00 | 2022-01-02 06:00 | 2159.6 | Opacity limitations
Mitchell 2 | D4 | 2022-01-02 18:28 | 2022-01-02 23:00 | 453.6 | Opacity limitations
Mitchell 2 | D4 | 2022-01-02 23:00 | 2022-01-03 06:00 | 3430.3 | Power off Rap precipitator fields
Mitchell 2 | D4 | 2022-01-03 06:00 | 2022-01-03 12:13 | 559.5 | Opacity limitations
Mitchell 2 | D1 | 2022-01-03 12:13 | 2022-01-03 12:26 | 19.8 | Opacity limitations
Mitchell 2 | D1 | 2022-01-03 12:26 | 2022-01-03 13:15 | 73.5 | Opacity limitations
Mitchell 2 | D1 | 2022-01-03 13:15 | 2022-01-03 16:18 | 305 | Opacity limitations
Mitchell 2 | D1 | 2022-01-03 16:18 | 2022-01-03 16:23 | 9.5 | Opacity limitations
Mitchell 2 | D1 | 2022-01-03 16:23 | 2022-01-03 17:16 | 97.2 | Opacity limitations
Mitchell 2 | D1 | 2022-01-03 17:16 | 2022-01-04 09:58 | 1753.5 | Opacity limitations
Mitchell 2 | D1 | 2022-01-03 20:00 | 2022-01-03 20:10 | 11.9 | lost pulverizer due to a hot burner tip
Mitchell 2 | D1 | 2022-01-03 20:10 | 2022-01-03 21:30 | 46.6 | lost pulverizer due to a hot burner tip
Mitchell 2 | D1 | 2022-01-03 21:30 | 2022-01-04 05:00 | 226.8 | Lost pulverizer due to a hot burner tip
Mitchell 2 | D1 | 2022-01-04 09:24 | 2022-01-04 09:58 | 19.8 | Boiler, roof outlet header safety valve 54 stuck closed
Mitchell 2 | D1 | 2022-01-04 09:58 | 2022-01-04 10:38 | 433.8 | Boiler, roof outlet header safety valve 54 stuck closed
Mitchell 2 | D1 | 2022-01-04 10:38 | 2022-01-04 10:39 | 2.4 | Boiler, roof outlet header safety valve 54 stuck closed
Mitchell 2 | D1 | 2022-01-04 10:39 | 2022-01-04 10:41 | 21.3 | Boiler, roof outlet header safety valve 54 stuck closed
Mitchell 2 | D1 | 2022-01-04 10:41 | 2022-01-04 10:50 | 97.2 | Boiler, roof outlet header safety valve 54 stuck closed
Mitchell 2 | D1 | 2022-01-04 10:50 | 2022-02-12 | 131226.9 | Boiler, roof outlet header safety valve 54 stuck closed
Mitchell 2 | D4 | 2022-01-08 08:00 | 2022-01-08 13:40 | 85.3 | Supply start up steam for Unit 1.
Mitchell 2 | D4 | 2022-01-08 13:40 | 2022-01-08 13:51 | 11.1 | Supply start up steam for Unit 1.
Mitchell 2 | D4 | 2022-01-08 13:51 | 2022-01-08 14:02 | 5.5 | Supply start up steam for Unit 1.
Mitchell 2 | D4 | 2022-01-08 14:02 | 2022-01-10 14:46 | 730.9 | Supply start up steam for Unit 1.
Mitchell 2 | D1 | 2022-01-15 10:57 | 2022-01-16 14:21 | 9589.9 | Valve leaking through in FGD Bleed System
Mitchell 2 | D1 | 2022-01-27 10:28 | 2022-01-27 13:20 | 1003.6 | <OMC!> Coal spill in coal tunnel
Mitchell 2 | D3 | 2022-01-30 10:00 | 2022-01-30 11:38 | 163.6 | Valve Checks
Mitchell 2 | D1 | 2022-02-02 05:56 | 2022-02-02 10:47 | 1697.3 | Coal system issues.
Mitchell 2 | D1 | 2022-02-03 08:14 | 2022-02-07 07:02 | 33170.2 | Deaerator leak, Per circular letter, The unit cannot be on AGC and has to stay at a stead load.
Mitchell 2 | D1 | 2022-02-07 07:02 | 2022-02-07 13:00 | 1491.9 | Deaerator leak, Per circular letter, The unit cannot be on AGC and has to stay at a steady load. Also blow slag.
Mitchell 2 | D2 | 2022-02-07 13:00 | 2022-02-09 06:00 | 14346.1 | Deaerator leak, Per circular letter, The unit cannot be on AGC and has to stay at a steady load.
Mitchell 2 | D1 | 2022-02-09 07:39 | 2022-02-09 08:05 | 138.3 | Grind out mill.
Mitchell 2 | D2 | 2022-02-09 08:30 | 2022-02-09 18:00 | 2375.3 | Blow slag
Mitchell 2 | D3 | 2022-02-09 18:00 | 2022-02-10 06:00 | 4199.1 | Deaerator leak, Per circular letter, The unit cannot be on AGC and has to stay at a steady load.
Mitchell 2 | D2 | 2022-02-10 20:00 | 2022-02-11 03:00 | 1400.2 | Deaerator leak, Per circular letter, The unit cannot be on AGC and has to stay at a steady load.
Mitchell 2 | D4 | 2022-02-11 03:00 | 2022-02-11 07:50 | 96.4 | Supply Start up steam to Unit 1.
Mitchell 2 | D1 | 2022-02-11 07:50 | 2022-02-12 | 323.2 | Deaerator leak, Per circular letter, The unit cannot be on AGC and has to stay at a steady load.
Mitchell 2 | D3 | 2022-02-12 | 2022-02-14 11:53 | 9593 | Boiler, roof outlet header safety valve 54 stuck closed.
Mitchell 2 | D3 | 2022-02-14 11:53 | 2022-02-15 08:15 | 3665.7 | Boiler roof outlet header safety valve 54 stuck closed.
Mitchell 2 | D3 | 2022-02-15 08:15 | 2022-02-15 16:55 | 1386.8 | Boiler roof outlet header safety valve 54 stuck closed.
Mitchell 2 | D3 | 2022-02-15 16:55 | 2022-02-16 | 1204.3 | Boiler roof outlet header safety valve 54 stuck closed.
Mitchell 2 | D3 | 2022-02-16 | 2022-02-17 13:50 | 6439.3 | Boiler roof outlet header safety valve 54 stuck closed.
Mitchell 2 | D1 | 2022-02-17 13:50 | 2022-02-17 15:37 | 303.4 | Boiler roof outlet header safety valve 54 stuck closed.
Mitchell 2 | D1 | 2022-02-17 15:37 | 2022-02-20 12:00 | 11625.4 | Boiler roof outlet header safety valve 54 stuck closed..
Mitchell 2 | D1 | 2022-02-17 20:44 | 2022-02-18 01:10 | 1419.2 | Loss of high sulfur coal
Mitchell 2 | MO | 2022-02-20 19:45 | 2022-03-26 05:00 | 632357.6 | Boiler inpsection/repair, Hydro test, Precipitator inpsection/repair, Roof Outlet Header SV-54 replacement, Deaerator leak repair, Drain FGD Absorber to replace 2H Agitator Seal, FGD Absorber Inlet Duct repairs, repair RH Attemperator Block Valves FMO-201 and 202 (Water Induction Protection Valves).
Mitchell 2 | U1 | 2022-04-15 16:03 | 2022-04-16 05:07 | 10325.5 | During Pressurization, Super heater bypass valves failed to respond causing the unit to trip on sub critical pressure.
Mitchell 2 | D1 | 2022-04-16 20:34 | 2022-04-18 07:12 | 4855.8 | #23 pulverizer pyrite line is plugged. Need to inspect and repair before pulverizer can be placed in service.
Mitchell 2 | D1 | 2022-04-16 20:36 | 2022-04-17 16:47 | 3027.3 | #21 coal feeder shuts down without a reason making it unreliable. Support groups need to be involved for troubleshooting.
Mitchell 2 | D1 | 2022-04-18 07:12 | 2022-04-22 17:55 | 8537.3 | #21 coal feeder shuts down without a reason making it unreliable. Support groups need to be involved for troubleshooting.
Mitchell 2 | D1 | 2022-04-18 12:02 | 2022-04-18 12:49 | 55.3 | Opacity
Mitchell 2 | D1 | 2022-04-18 12:49 | 2022-04-18 13:18 | 16.6 | Opacity
Mitchell 2 | D1 | 2022-04-18 13:18 | 2022-04-18 14:06 | 16.6 | Opacity
Mitchell 2 | D1 | 2022-04-19 11:58 | 2022-04-19 12:29 | 160.4 | Pulverizers Issues
Mitchell 2 | D1 | 2022-04-19 12:29 | 2022-04-19 14:05 | 256 | Pulverizers Issues
Mitchell 2 | D3 | 2022-04-22 07:00 | 2022-04-22 15:00 | 2399.8 | Repair flange leak associated with both Hydrolyzers
Mitchell 2 | D1 | 2022-04-23 03:47 | 2022-04-28 15:15 | 10517.6 | #21 coal feeder shuts down without a reason making it unreliable. Support groups need to be involved for troubleshooting.
Mitchell 2 | D4 | 2022-04-24 01:58 | 2022-04-25 05:26 | 2197.5 | Supply Start up steam to Unit 1.
Mitchell 2 | D1 | 2022-04-25 22:14 | 2022-04-27 14:46 | 3243 | 25 Pulverizer unavailable due to coal feeder issues.
Mitchell 2 | D1 | 2022-04-26 14:29 | 2022-04-26 15:54 | 312.1 | Circulating water line seal issue
Mitchell 2 | D1 | 2022-04-26 15:54 | 2022-04-27 06:12 | 1146.6 | Circulating water line seal issue
Mitchell 2 | D1 | 2022-04-27 06:12 | 2022-04-27 14:46 | 685.1 | 22B Circulating water pump seal water line gland failure
Mitchell 2 | D1 | 2022-04-27 14:47 | 2022-04-28 16:58 | 2094.8 | 24 Pulverizer out of service to repair coal leak on raw coal pipe leak.
Mitchell 2 | D1 | 2022-04-28 21:14 | 2022-05-02 09:30 | 8461.5 | # 21 coal feeder
Mitchell 2 | D1 | 2022-05-24 03:28 | 2022-05-24 16:30 | 1042.3 | 22 Pulverizer unavailable to to coal feeder issues.
Mitchell 2 | D4 | 2022-05-27 22:30 | 2022-05-27 22:47 | 53.7 | Valve Checks - Weekly
Mitchell 2 | D3 | 2022-05-30 00:47 | 2022-05-30 05:30 | 425.1 | Supply Steam for unit #1 - Startup
Mitchell 2 | D1 | 2022-05-30 05:30 | 2022-05-30 10:49 | 957.7 | Supply Steam for unit #1 - Startup
Mitchell 2 | D1 | 2022-05-30 17:00 | 2022-05-31 11:02 | 2167.5 | Opacity
Mitchell 2 | D1 | 2022-05-31 12:43 | 2022-06-02 | 2649.5 | Opacity
Mitchell 2 | MO | 2022-06-08 | 2022-06-13 02:00 | 96404.4 | Boiler inspection
Mitchell 2 | D1 | 2022-06-13 18:00 | 2022-06-13 19:55 | 184.1 | Opacity
Mitchell 2 | D1 | 2022-06-13 19:55 | 2022-06-13 20:34 | 45.8 | Opacity
Mitchell 2 | D1 | 2022-06-13 20:34 | 2022-06-13 23:00 | 207 | Opacity
Mitchell 2 | D3 | 2022-06-13 23:00 | 2022-06-14 19:07 | 1005.9 | Opacity
Mitchell 2 | D3 | 2022-06-14 19:07 | 2022-06-14 19:22 | 17.4 | Opacity
Mitchell 2 | D3 | 2022-06-14 19:22 | 2022-06-15 | 417.2 | Opacity
Mitchell 2 | D3 | 2022-06-15 | 2022-06-15 00:45 | 60.1 | 26 pulverizer out of service to remove metal stuck in the pyrite hopper.
Mitchell 2 | D1 | 2022-06-15 14:30 | 2022-06-15 14:56 | 44.3 | Opacity
Mitchell 2 | D1 | 2022-06-15 14:56 | 2022-06-15 15:01 | 7.1 | Opacity
Mitchell 2 | D1 | 2022-06-15 15:01 | 2022-06-16 | 1077.8 | Opacity
Mitchell 2 | D3 | 2022-06-16 | 2022-06-16 00:01 | 1.6 | Opacity.
Mitchell 2 | D3 | 2022-06-16 00:01 | 2022-06-16 12:13 | 1464.2 | Opacity.
Mitchell 2 | D3 | 2022-06-16 12:13 | 2022-06-16 12:26 | 22.1 | Opacity.
Mitchell 2 | D3 | 2022-06-16 12:26 | 2022-06-16 12:32 | 11.1 | Opacity.
Mitchell 2 | D3 | 2022-06-16 12:32 | 2022-06-16 13:59 | 166.7 | Opacity.
Mitchell 2 | D3 | 2022-06-16 13:59 | 2022-06-16 14:58 | 109.8 | Opacity.
Mitchell 2 | D3 | 2022-06-16 14:58 | 2022-06-16 15:37 | 74.3 | Opacity.
Mitchell 2 | D3 | 2022-06-16 15:37 | 2022-06-18 | 3886.2 | Opacity.
Mitchell 2 | D3 | 2022-06-18 | 2022-06-21 17:14 | 8031.6 | Opacity.
Mitchell 2 | D4 | 2022-06-18 09:00 | 2022-06-18 09:18 | 120.1 | Need To Remove 22B Circulator To Couple Up 22A Circulator
Mitchell 2 | D4 | 2022-06-19 10:00 | 2022-06-19 11:55 | 384 | Weekend valve checks
Mitchell 2 | D4 | 2022-06-20 06:00 | 2022-06-20 12:28 | 2587.9 | Couple 22A Circ. Water Pump
Mitchell 2 | D3 | 2022-06-21 17:14 | 2022-06-21 19:05 | 55.3 | Opacity.
Mitchell 2 | D3 | 2022-06-21 19:05 | 2022-06-21 20:01 | 102.7 | Opacity.
Mitchell 2 | D3 | 2022-06-21 20:01 | 2022-06-21 20:25 | 40.3 | Opacity.
Mitchell 2 | D3 | 2022-06-21 20:25 | 2022-06-21 20:30 | 9.5 | Opacity.
Mitchell 2 | D1 | 2022-06-21 20:30 | 2022-06-22 14:54 | 2027.7 | Opacity.
Mitchell 2 | D1 | 2022-06-22 14:54 | 2022-06-22 15:49 | 109.8 | Opacity.
Mitchell 2 | D1 | 2022-06-22 15:49 | 2022-06-23 07:00 | 1973.9 | Opacity.
Mitchell 2 | D1 | 2022-06-23 11:44 | 2022-06-23 12:44 | 91.7 | Opacity limitations
Mitchell 2 | D1 | 2022-06-23 12:44 | 2022-06-24 04:36 | 1585.1 | Opacity limitations
Mitchell 2 | MO | 2022-06-25 | 2022-07-02 14:34 | 144264.4 | Repair leaks
Mitchell 2 | D2 | 2022-07-04 02:00 | 2022-07-05 07:03 | 3491.9 | Start up steam for Mitchell Unit 1 Start up.
Mitchell 2 | D3 | 2022-07-05 07:03 | 2022-07-05 18:05 | 1216.1 | Curtailing Unit 2 due to expected opacity
Mitchell 2 | D1 | 2022-07-05 18:05 | 2022-07-06 19:45 | 3084.9 | Start up steam for Mitchell Unit 1 Start up.
Mitchell 2 | D1 | 2022-07-06 19:45 | 2022-07-07 15:30 | 2176.2 | Opacity
Mitchell 2 | D1 | 2022-07-07 15:30 | 2022-07-11 15:00 | 10523.9 | Opacity
Mitchell 2 | D4 | 2022-07-09 00:01 | 2022-07-09 17:56 | 0 | #24 pulverizer 3000 hour inspection/repair
Mitchell 2 | D4 | 2022-07-09 19:00 | 2022-07-09 21:13 | 288.4 | Weekly Valve Checks
Mitchell 2 | U1 | 2022-07-11 15:00 | 2022-07-11 22:47 | 6150.1 | Reason Unknown
Mitchell 2 | D3 | 2022-07-11 22:47 | 2022-07-16 | 10713.5 | Opacity
Mitchell 2 | D1 | 2022-07-12 05:30 | 2022-07-16 | 21720.2 | ID fan Thrust bearing
Mitchell 2 | D1 | 2022-07-14 07:35 | 2022-07-14 17:00 | 94 | Pulverizer testing
Mitchell 2 | MO | 2022-07-16 03:33 | 2022-07-24 00:31 | 149321.7 | #21 ID Fan Thrust Bearing and Radial Bearing
Mitchell 2 | D1 | 2022-07-24 14:26 | 2022-08-01 15:33 | 22872.3 | opacity
Mitchell 2 | D4 | 2022-07-30 19:00 | 2022-07-30 20:00 | 130.4 | Weekly Valve Checks
Mitchell 2 | D1 | 2022-08-01 15:33 | 2022-08-01 17:13 | 200.7 | Opacity
Mitchell 2 | D1 | 2022-08-01 17:13 | 2022-08-06 14:44 | 12950.6 | Opacity
Mitchell 2 | D1 | 2022-08-06 14:44 | 2022-08-06 14:50 | 6.3 | Opacity
Mitchell 2 | D1 | 2022-08-06 14:50 | 2022-08-08 14:36 | 9075.4 | Opacity
Mitchell 2 | D1 | 2022-08-08 14:36 | 2022-08-08 15:05 | 82.2 | Opacity
Mitchell 2 | D1 | 2022-08-08 15:05 | 2022-08-12 23:59 | 18881.8 | Opacity
Mitchell 2 | MO | 2022-09-03 | 2022-09-10 | 126168 | Pre Planned Outage prep work.
Mitchell 2 | PO | 2022-09-10 | 2022-12-16 14:25 | 1759906.2 | Boiler inpsection/repair, Cooling Tower inpsection/repair, Low Pressure Turbine A"&"B" Valve replacement
Mitchell 2 | PO | 2022-12-16 14:52 | 2022-12-16 15:28 | 474.1 | Boiler inpsection/repair, Cooling Tower inpsection/repair, Low Pressure Turbine A"&"B" Valve replacement
Mitchell 2 | U1 | 2022-12-17 14:12 | 2022-12-20 16:08 | 58421.9 | A Bus Relay PA Fan
Mitchell 2 | D1 | 2022-12-21 05:02 | 2022-12-21 05:03 | 1.6 | opacity
Mitchell 2 | D1 | 2022-12-22 06:00 | 2022-12-22 10:13 | 970.4 | Gen Field Ground
Mitchell 2 | D1 | 2022-12-22 10:13 | 2022-12-22 14:00 | 794.2 | Gen Field Ground
Mitchell 2 | D1 | 2022-12-23 10:10 | 2022-12-23 10:28 | 28.4 | 25 Pulv issue
Mitchell 2 | D1 | 2022-12-23 10:28 | 2022-12-23 17:44 | 654.3 | 25 Pulv issue, could not get dampers to operate
Mitchell 2 | D1 | 2022-12-23 12:07 | 2022-12-23 13:56 | 45.8 | Opacity
Mitchell 2 | D1 | 2022-12-23 13:56 | 2022-12-23 14:53 | 47.4 | Opacity
Mitchell 2 | D1 | 2022-12-23 14:53 | 2022-12-23 19:22 | 448 | Opacity
Mitchell 2 | D1 | 2022-12-23 19:22 | 2022-12-23 21:08 | 158.8 | Opacity
Mitchell 2 | D1 | 2022-12-23 21:08 | 2022-12-24 02:46 | 844.7 | Opacity
Mitchell 2 | D1 | 2022-12-24 02:46 | 2022-12-24 04:41 | 172.3 | Opacity
Mitchell 2 | D1 | 2022-12-24 04:41 | 2022-12-24 14:08 | 708.8 | Opacity
Mitchell 2 | D1 | 2022-12-24 06:48 | 2022-12-24 07:08 | 138.3 | Reagent slurry feed tanks have frozen level indications and tanks were lower than expected
Mitchell 2 | D1 | 2022-12-24 07:08 | 2022-12-24 12:00 | 1023.3 | Reagent slurry feed tanks have frozen level indications and tanks were lower than expected
Mitchell 2 | D1 | 2022-12-24 14:08 | 2022-12-25 | 888.2 | Opacity
Mitchell 2 | D3 | 2022-12-25 | 2022-12-26 | 4565 | Anticipated opacity
Mitchell 2 | D3 | 2022-12-26 | 2022-12-27 12:38 | 6968 | Opacity
Mitchell 2 | D3 | 2022-12-27 12:38 | 2022-12-27 14:02 | 294 | Opacity
Mitchell 2 | D3 | 2022-12-27 14:02 | 2022-12-27 15:12 | 268.7 | Opacity
Mitchell 2 | D3 | 2022-12-27 15:12 | 2022-12-27 16:08 | 317.7 | Opacity
Mitchell 2 | D3 | 2022-12-27 16:08 | 2022-12-28 23:40 | 11510.1 | Opacity
Mitchell 2 | D3 | 2022-12-28 23:40 | 2022-12-29 00:51 | 342.9 | Opacity
Mitchell 2 | D3 | 2022-12-29 00:51 | 2023-01-07 | 78839.8 | Opacity
Mitchell 2 | D1 | 2022-12-31 05:05 | 2023-01-01 | 2368.2 | Secondary Air Flow Meter
Mitchell 2 | MO | 2023-01-07 | 2023-01-29 19:04 | 432292.3 | Precipitator inpsection/repair, Balance Shot on LP turbines., Boiler inpsection/repair, Duct Repairs.
Mitchell 2 | D1 | 2023-01-30 11:22 | 2023-01-30 15:00 | 291.6 | # 24 pulv o/s
Mitchell 2 | D1 | 2023-01-31 17:10 | 2023-02-02 15:19 | 12042.6 | Issues with #22 ID Fan. Groups will gather information and determine a resolution on 2/1/23
Mitchell 2 | D1 | 2023-02-04 17:42 | 2023-02-04 20:10 | 1209 | Dry fly ash issues, all lines froze up.
Mitchell 2 | D1 | 2023-02-05 05:30 | 2023-02-05 16:09 | 854.2 | #24 pulverizer coal feeder gearbox failed
Mitchell 2 | D1 | 2023-02-08 17:13 | 2023-02-08 18:53 | 233.9 | 24 feeder
Mitchell 2 | D4 | 2023-02-09 18:00 | 2023-02-10 01:20 | 2090.9 | start up Steam for unit 1
Mitchell 2 | D1 | 2023-02-10 05:00 | 2023-02-10 07:07 | 298.7 | start up steam for unit 1
Mitchell 2 | D1 | 2023-02-10 07:07 | 2023-02-11 10:40 | 3862.5 | start up steam for unit 1
Mitchell 2 | D4 | 2023-02-12 | 2023-02-12 01:20 | 320 | Valve Check
Mitchell 2 | D1 | 2023-02-15 12:58 | 2023-02-17 17:50 | 4240.2 | 24 pulverizer feeder gearbox failure
Mitchell 2 | D1 | 2023-02-15 13:03 | 2023-02-21 | 10463 | 25 pulverizer gearbox issues
Mitchell 2 | D1 | 2023-02-17 09:21 | 2023-02-17 14:53 | 1439 | #22 Pulv has been tagged out to repair a splice on the coal feeder belt.
Mitchell 2 | D3 | 2023-02-17 23:00 | 2023-02-18 01:29 | 522.3 | Valve checks
Mitchell 2 | D3 | 2023-02-21 | 2023-02-21 14:22 | 2300.3 | 25 pulverizer gearbox issues
Mitchell 2 | D3 | 2023-02-21 14:22 | 2023-02-24 13:08 | 5661 | 25 pulverizer gearbox issues
Mitchell 2 | D4 | 2023-02-25 19:00 | 2023-02-25 20:46 | 512.8 | Valve Check
Mitchell 2 | D4 | 2023-02-27 06:00 | 2023-03-03 17:39 | 6841.6 | 25 Pulverizer 50 hour inspection.
Mitchell 2 | D1 | 2023-03-02 04:29 | 2023-03-02 16:23 | 714.3 | 24 Pulverizer Coal Feeder has coal leak at coal gate above feeder.
Mitchell 2 | D4 | 2023-03-03 21:00 | 2023-03-03 22:12 | 348.5 | Perform weekly turbine valve checks
Mitchell 2 | D1 | 2023-03-05 07:00 | 2023-03-05 14:43 | 3667.3 | Main steam attemperator issues
Mitchell 2 | D1 | 2023-03-06 09:00 | 2023-03-06 09:12 | 15.8 | #21 pulverizer 3,000 hour inspection/repair.
Mitchell 2 | D1 | 2023-03-06 09:12 | 2023-03-07 | 888.2 | #21 pulverizer 3,000 hour inspection/repair.
Mitchell 2 | D4 | 2023-03-07 | 2023-03-07 19:00 | 1141.8 | #21 pulverizer 3,000 hour inspection/repair.
Mitchell 2 | D4 | 2023-03-09 05:00 | 2023-03-10 13:20 | 1943.1 | #22 pulverizer 3,000 hour inspection/repair.
Mitchell 2 | D3 | 2023-03-11 21:00 | 2023-03-11 23:09 | 624.3 | Weekly Valve Checks
Mitchell 2 | D4 | 2023-03-13 06:00 | 2023-03-13 07:30 | 90.1 | Replace thrust bearing on input shaft on 22 pulverizer gearbox.
Mitchell 2 | D4 | 2023-03-18 07:00 | 2023-03-18 09:39 | 768.9 | Weekly Valve Check
Mitchell 2 | D4 | 2023-03-20 | 2023-03-23 09:10 | 4870 | Replace #22 Pulverizer Input Shaft Thrust bearing
Mitchell 2 | D4 | 2023-03-21 | 2023-03-21 06:45 | 541.3 | Supply Steam for ML1 startup.
Mitchell 2 | D4 | 2023-03-21 06:45 | 2023-03-22 07:53 | 3267.5 | Supply Steam for ML1 startup.
Mitchell 2 | U1 | 2023-03-23 09:10 | 2023-04-04 14:00 | 231396.6 | Feedwater Pump Thrust Bearing Failure
Mitchell 2 | PO | 2023-04-15 | 2023-04-30 14:35 | 295995.5 | Boiler inpsection/repair, Sicon Conveyor Tail Pulley structural steel repairs, relocation of the #24 River Water feed to FGD in the foundation of the new ash bunker, BOP repairs, dual outage to prep for Fall Outage.
*The rows highlighted green contain all of the outages and or derates taken during the test year (April 1, 2022 through March 31, 2024).
Event Type |  |  | North American Electric Reliability Corporation ("NERC") Definition**
D1 Unplanned (Forced) Derating — Immediate |  |  | This is a derating that requires an immediate reduction in capacity
D2 Unplanned (Forced) Derating — Delayed |  |  | This is a derating that does not require an immediate reduction in capacity, but rather within six hours.
D3 Unplanned (Forced) Derating — Postponed |  |  | This is a derating that can be postponed beyond six hours but requires a reduction in capacity before the end of the next weekend.
D4 Maintenance Derating |  |  | A Derating that can be deferred beyond the end of the next weekend but requires a reduction in capacity before the next Planned Outage (PO).
**NERC data source: NERC 2023 GADS Data Reporting Instructions (https://www.nerc.com/pa/RAPA/gads/DataReportingInstructions/GADS_DRI_2023.pdf)