## 2014
Year | Event Type | Start Date | End Date | Duration | Derating (MW) | NAC (MW) | Cause Code | Verbal Description
2014 | U2 - Forced - Delayed | 01/07/2014 23:16 CPT | 01/12/2014 12:47 CPT | 109:31 | 417 |  | 1050 - Second superheater | Tube leak in finishing super heater
2014 | U1 - Forced - Immediate | 01/12/2014 13:53 CPT | 01/12/2014 14:58 CPT | 1:05 | 417 |  | 1999 - Boiler; miscellaneous | unit tripped during startup on low drum level
2014 | D1 - Forced - Immediate | 02/01/2014 16:45 CPT | 02/01/2014 18:45 CPT | 2:00 | 115 | 302 | 0338 - Pulverizer control systems (temperature and pressure) | #5 mill tripped due to scanner problems
2014 | D1 - Forced - Immediate | 02/02/2014 22:30 CPT | 02/03/2014 02:57 CPT | 4:27 | 115 | 302 | 0250 - Pulverizer feeders | #4 feeder tripped, three mill operation
2014 | D2 - Forced - Delayed | 02/03/2014 11:00 CPT | 02/03/2014 19:00 CPT | 8:00 | 210 | 207 | 0890 - Bottom ash systems (wet or dry) | wet bottom failure due to slag fall
2014 | D2 - Forced - Delayed | 02/04/2014 22:42 CPT | 02/05/2014 03:37 CPT | 4:55 | 40 | 377 | 9270 - Wet coal | wet fuel
2014 | D2 - Forced - Delayed | 02/15/2014 08:20 CPT | 02/15/2014 09:55 CPT | 1:35 | 90 | 327 | 9270 - Wet coal | wet fuel
2014 | D2 - Forced - Delayed | 03/16/2014 19:20 CPT | 03/17/2014 07:11 CPT | 11:51 | 148 | 269 | 3410 - Feedwater pump | #2 BFP out of service due to leak on balance drum leak-off
2014 | D2 - Forced - Delayed | 03/17/2014 07:12 CPT | 03/17/2014 17:50 CPT | 10:38 | 200 | 217 | 0897 - Bottom ash rotary (drag chain type) conveyor and motor | Repair to drag chain required breaking the wet seal
2014 | D1 - Forced - Immediate | 03/29/2014 23:15 CPT | 03/30/2014 02:20 CPT | 3:05 | 110 | 307 | 0250 - Pulverizer feeders | #4 feeder tripped, three mill operation
2014 | D2 - Forced - Delayed | 04/02/2014 05:30 CPT | 04/02/2014 06:15 CPT | 0:45 | 20 | 397 | 9630 - Opacity (fossil) | Opacity exceedance
2014 | D2 - Forced - Delayed | 04/02/2014 17:15 CPT | 04/02/2014 17:30 CPT | 0:15 | 10 | 407 | 9630 - Opacity (fossil) | opacity exceedance
2014 | D1 - Forced - Immediate | 04/07/2014 11:54 CPT | 04/07/2014 13:15 CPT | 1:21 | 34.5 | 382.5 | 9300 - Transmission system problems other than catastrophes (do not include switchyard problems in this category; see codes 3600 to 3629) | External transmission interference, frequency correction response
2014 | D1 - Forced - Immediate | 04/10/2014 02:23 CPT | 04/10/2014 04:16 CPT | 1:53 | 106 | 311 | 0030 - Coal conveyors and feeders | #4 feeder tripped, trouble getting #3 mill on, three mill operation
2014 | D1 - Forced - Immediate | 04/28/2014 01:11 CPT | 04/28/2014 04:15 CPT | 3:04 | 130 | 287 | 0310 - Pulverizer mills | #2 mill tripped due to hot burner
2014 | D1 - Forced - Immediate | 04/28/2014 05:00 CPT | 04/28/2014 05:50 CPT | 0:50 | 130 | 287 | 0310 - Pulverizer mills | #3 mill tripped, three mill operation
2014 | U1 - Forced - Immediate | 06/23/2014 13:50 CPT | 06/23/2014 17:32 CPT | 3:42 | 417 |  | 1999 - Boiler; miscellaneous | Unit tripped on high drum level during startup
2014 | D1 - Forced - Immediate | 06/23/2014 17:33 CPT | 06/24/2014 07:25 CPT | 13:52 | 217 | 200 | 0260 - Primary air fan | High vibration on #2 PA Fan
2014 | D1 - Forced - Immediate | 06/24/2014 15:24 CPT | 06/25/2014 07:50 CPT | 16:26 | 85 | 332 | 0310 - Pulverizer mills | Multiple mill trips
2014 | D1 - Forced - Immediate | 07/02/2014 13:26 CPT | 07/02/2014 14:16 CPT | 0:50 | 24 | 393 | 3210 - Circulating water pumps | #3 CWP tripped, discharge valve did not close
2014 | U2 - Forced - Delayed | 07/08/2014 02:10 CPT | 07/09/2014 17:56 CPT | 39:46 | 417 |  | 1060 - First reheater | Tube leak in reheater
2014 | D2 - Forced - Delayed | 08/07/2014 18:24 CPT | 08/07/2014 19:03 CPT | 0:39 | 86 | 331 | 9270 - Wet coal | Water in bunkers when coal system deluged
2014 | D1 - Forced - Immediate | 08/11/2014 15:00 CPT | 08/11/2014 15:30 CPT | 0:30 | 48 | 369 | 9300 - Transmission system problems other than catastrophes (do not include switchyard problems in this category; see codes 3600 to 3629) | Lost both startup transformers
2014 | U2 - Forced - Delayed | 09/17/2014 13:07 CPT | 09/17/2014 19:14 CPT | 6:07 | 417 |  | 9300 - Transmission system problems other than catastrophes (do not include switchyard problems in this category; see codes 3600 to 3629) | broken disconnect switch on MOD 2079
2014 | U1 - Forced - Immediate | 11/16/2014 13:21 CPT | 11/16/2014 19:39 CPT | 6:18 | 417 |  | 4309 - Other turbine instrument and control problems | Unit tripped while performing the main turbine mechanical overspeed monthly trip test.
2014 | U1 - Forced - Immediate | 11/19/2014 19:30 CPT | 11/19/2014 23:17 CPT | 3:47 | 417 |  | 1799 - Other boiler instrumentation and control problems | Unit tripped on low drum level, mill trip resulted in boiler swing.
2014 | D1 - Forced - Immediate | 11/29/2014 19:32 CPT | 11/29/2014 20:12 CPT | 0:40 | 110 | 307 | 0310 - Pulverizer mills | #1 mill tripped because #1 bunker ran out of fuel
2014 | D1 - Forced - Immediate | 12/07/2014 14:50 CPT | 12/07/2014 15:15 CPT | 0:25 | 110 | 307 | 0335 - Pulverizer lube oil system | #2 mill tripped when lube oil pump coupling broke

## 2015
Year | Event Type | Start Date | End Date | Duration | Derating (MW) | NAC (MW) | Cause Code | Verbal Description
2015 | D1 - Forced - Immediate | 01/28/2015 00:33 CPT | 01/28/2015 02:20 CPT | 1:47 | 110 | 307 | 0310 - Pulverizer mills | #3 mill tripped because 3a oil gun would not stay on
2015 | D1 - Forced - Immediate | 02/16/2015 07:16 CPT | 02/16/2015 07:42 CPT | 0:26 | 85 | 332 | 9280 - Frozen coal | frozen chunk of coal in #4 feeder
2015 | U1 - Forced - Immediate | 02/16/2015 23:29 CPT | 02/18/2015 10:02 CPT | 34:33 | 417 |  | 1000 - Waterwall (Furnace wall) | Tube leak in nose section
2015 | U1 - Forced - Immediate | 02/18/2015 10:03 CPT | 02/18/2015 10:52 CPT | 0:49 | 417 |  | 4740 - Emergency generator trip devices | Unit tripped during startup on no load
2015 | D1 - Forced - Immediate | 03/04/2015 21:14 CPT | 03/04/2015 21:25 CPT | 0:11 | 110 | 307 | 0310 - Pulverizer mills | #1 Mill tripped when lost coal feed
2015 | D1 - Forced - Immediate | 03/21/2015 20:29 CPT | 03/21/2015 21:01 CPT | 0:32 | 110 | 307 | 0310 - Pulverizer mills | #5 mill tripped, three mill operation
2015 | D1 - Forced - Immediate | 03/24/2015 12:27 CPT | 03/25/2015 11:00 CPT | 22:33 | 110 | 307 | 0310 - Pulverizer mills | #3 mill tripped due to plugged classifier
2015 | U1 - Forced - Immediate | 04/03/2015 04:24 CPT | 04/03/2015 13:32 CPT | 9:08 | 417 |  | 4499 - Other miscellaneous steam turbine problems | Lightening strike resulted in turbine trip
2015 | D2 - Forced - Delayed | 04/25/2015 18:50 CPT | 04/26/2015 00:03 CPT | 5:13 | 216 | 201 | 9630 - Opacity (fossil) | High opacity after losing half the precips due to 6.9KV feeder trip
2015 | U1 - Forced - Immediate | 04/26/2015 00:03 CPT | 04/26/2015 05:03 CPT | 5:00 | 417 |  | 1740 - Boiler drum gage glasses/level indicator | Unit tripped on low drum level
2015 | U1 - Forced - Immediate | 05/08/2015 12:32 CPT | 05/08/2015 15:25 CPT | 2:53 | 417 |  | 3410 - Feedwater pump | Unit tripped due to #1 BFPT trip
2015 | U2 - Forced - Delayed | 07/29/2015 13:51 CPT | 07/31/2015 12:28 CPT | 46:37 | 417 |  | 1000 - Waterwall (Furnace wall) | Tube leak east water wall. Additional leaks found on hydro
2015 | D1 - Forced - Immediate | 08/10/2015 22:40 CPT | 08/10/2015 23:07 CPT | 0:27 | 110 | 307 | 0310 - Pulverizer mills | #2 mill tripped on air flow
2015 | U2 - Forced - Delayed | 09/19/2015 14:30 CPT | 09/22/2015 09:36 CPT | 67:06 | 417 |  | 1000 - Waterwall (Furnace wall) | Tube leak in nose section, additional water wall tube leak found on hydro
2015 | D2 - Forced - Delayed | 11/07/2015 12:12 CPT | 11/07/2015 13:50 CPT | 1:38 | 20 | 397 | 9630 - Opacity (fossil) | high opacity
2015 | D2 - Forced - Delayed | 11/11/2015 14:32 CPT | 11/11/2015 16:18 CPT | 1:46 | 15 | 402 | 3240 - Cooling tower fans | lost 12AA11 feed at cooling tower, 5 fans off
2015 | U1 - Forced - Immediate | 12/04/2015 01:50 CPT | 12/04/2015 13:09 CPT | 11:19 | 417 |  | 1999 - Boiler; miscellaneous | DA regulator problems, bypass would not close and lost unit on low drum level
2015 | D2 - Forced - Delayed | 12/04/2015 13:09 CPT | 12/07/2015 03:45 CPT | 62:36 | 65 | 352 | 3410 - Feedwater pump | Steam leak #1 BFPT
2015 | D1 - Forced - Immediate | 12/06/2015 07:52 CPT | 12/06/2015 09:20 CPT | 1:28 | 86 | 331 | 0310 - Pulverizer mills | #2 mill tripped due to 2c burning hot
2015 | U2 - Forced - Delayed | 12/07/2015 08:32 CPT | 12/12/2015 03:00 CPT | 114:28 | 417 |  | 1050 - Second superheater | Superheater tube leak
2015 | U2 - Forced - Delayed | 12/14/2015 06:11 CPT | 12/15/2015 01:03 CPT | 18:52 | 417 |  | 0799 - Other miscellaneous piping system problems | Steam leak in boiler vent pipe

## 2016
Year | Event Type | Start Date | End Date | Duration | Derating (MW) | NAC (MW) | Cause Code | Verbal Description
2016 | U2 - Forced - Delayed | 01/22/2016 02:18 CPT | 01/23/2016 13:42 CPT | 35:24 | 417 |  | 1000 - Waterwall (Furnace wall) | Tube leak in nose
2016 | D1 - Forced - Immediate | 03/18/2016 21:05 CPT | 03/18/2016 22:05 CPT | 1:00 | 90 | 327 | 3410 - Feedwater pump | #1 BFPT tripped causing #4 mill to trip
2016 | U2 - Forced - Delayed | 04/11/2016 07:46 CPT | 04/11/2016 19:19 CPT | 11:33 | 417 |  | 1140 - First superheater | Leak on pressure indicator line on the SH Spray
2016 | U2 - Forced - Delayed | 04/15/2016 16:57 CPT | 04/16/2016 17:55 CPT | 24:58 | 417 |  | 1000 - Waterwall (Furnace wall) | water wall tube leak in knees
2016 | U2 - Forced - Delayed | 04/30/2016 00:36 CPT | 05/02/2016 05:42 CPT | 53:06 | 417 |  | 1000 - Waterwall (Furnace wall) | ww tube leak in knees
2016 | D1 - Forced - Immediate | 06/22/2016 08:10 CPT | 06/22/2016 10:00 CPT | 1:50 | 95 | 322 | 0250 - Pulverizer feeders | #1 mill tripped due to low temp from oil purifier
2016 | U1 - Forced - Immediate | 06/25/2016 21:00 CPT | 06/28/2016 01:01 CPT | 52:01 | 417 |  | 1000 - Waterwall (Furnace wall) | Unit tripped due to tube lean in nose
2016 | U1 - Forced - Immediate | 07/04/2016 12:24 CPT | 07/04/2016 18:39 CPT | 6:15 | 417 |  | 3629 - Other switchyard or high voltage system problems - external | Lightening strike to switchyard
2016 | D2 - Forced - Delayed | 07/31/2016 18:10 CPT | 07/31/2016 23:30 CPT | 5:20 | 130 | 287 | 3620 - Main transformer | Partial loss of FGD function following 11BA Main trip
2016 | D1 - Forced - Immediate | 09/27/2016 12:45 CPT | 09/28/2016 00:00 CPT | 11:15 | 70 | 347 | 3410 - Feedwater pump | Leak on #1 BFP
2016 | U1 - Forced - Immediate | 10/30/2016 20:09 CPT | 11/01/2016 15:18 CPT | 43:09 | 417 |  | 1000 - Waterwall (Furnace wall) | Unit trip due to water wall tube leak
2016 | U1 - Forced - Immediate | 11/12/2016 00:48 CPT | 11/12/2016 05:36 CPT | 4:48 | 417 |  | 1455 - Induced draft fans | Unit trippped when IDF tripped
2016 | U1 - Forced - Immediate | 11/13/2016 16:44 CPT | 11/14/2016 14:08 CPT | 21:24 | 417 |  | 8817 - SCR NOx Control system | Unit tripped due to SCR flow path resulting in fuel trip
2016 | D1 - Forced - Immediate | 11/17/2016 01:23 CPT | 11/17/2016 04:55 CPT | 3:32 | 50 | 367 | 3631 - 480-volt circuit breakers | MCC12B12 tripped, lost boiler auxillary equipment
2016 | D2 - Forced - Delayed | 11/20/2016 06:49 CPT | 11/20/2016 16:45 CPT | 9:56 | 95 | 322 | 3410 - Feedwater pump | Repair balanced drum leak-off on #1 BFPT
2016 | D1 - Forced - Immediate | 12/06/2016 12:06 CPT | 12/06/2016 12:45 CPT | 0:39 | 95 | 322 | 0250 - Pulverizer feeders | #5 feeder tripped
2016 | D1 - Forced - Immediate | 12/18/2016 14:07 CPT | 12/18/2016 14:48 CPT | 0:41 | 120 | 297 | 0320 - Foreign object in Pulverizers mill | #4 feeder tripped due to metal in the feeder
2016 | D1 - Forced - Immediate | 12/18/2016 16:38 CPT | 12/18/2016 22:05 CPT | 5:27 | 68 | 349 | 9270 - Wet coal | multiple feeder/mill trips due to wet fuel
2016 | D1 - Forced - Immediate | 12/20/2016 05:41 CPT | 12/20/2016 08:25 CPT | 2:44 | 166 | 251 | 3682 - Other voltage system conductors and buses | Loss of 11B Buss resulted in loss of SCR
2016 | U1 - Forced - Immediate | 12/24/2016 18:50 CPT | 12/26/2016 19:03 CPT | 48:13 | 417 |  | 1000 - Waterwall (Furnace wall) | Water wall tube leak
2016 | SF - Startup Failure | 12/26/2016 19:03 CPT | 12/27/2016 10:23 CPT | 15:20 | 417 |  | 3610 - Switchyard circuit breakers - (not outside management control) | bad CCVT on B phase in switchyard prevented synchronization with the grid
2016 | U1 - Forced - Immediate | 12/28/2016 16:20 CPT | 12/28/2016 23:06 CPT | 6:46 | 417 |  | 3612 - Switchyard system protection devices - external | Lightening strike blew fuse for 63-1/AST trip circuit & main gen bkr closed circuit

## 2017
Year | Event Type | Start Date | End Date | Duration | Derating (MW) | NAC (MW) | Cause Code | Verbal Description
2017 | SF - Startup Failure | 01/03/2017 11:30 CPT | 01/04/2017 15:07 CPT | 27:37 | 417 |  | 1000 - Waterwall (Furnace wall) | WW tube leak found on hydro
2017 | U2 - Forced - Delayed | 02/04/2017 14:48 CPT | 02/08/2017 19:38 CPT | 100:50 | 417 |  | 1000 - Waterwall (Furnace wall) | WW Tube Leak
2017 | U1 - Forced - Immediate | 02/08/2017 19:52 CPT | 02/08/2017 22:55 CPT | 3:03 | 417 |  | 4099 - Other high pressure turbine problems | Unit tripped due to crossover pressure differential
2017 | U1 - Forced - Immediate | 02/09/2017 04:05 CPT | 02/09/2017 07:15 CPT | 3:10 | 417 |  | 1740 - Boiler drum gage glasses/level indicator | Unit tripped on low drum level due to problem with #1 BFPT
2017 | U1 - Forced - Immediate | 02/12/2017 17:13 CPT | 02/12/2017 21:02 CPT | 3:49 | 417 |  | 3410 - Feedwater pump | Unit tripped due to #1 BFPT
2017 | D1 - Forced - Immediate | 02/12/2017 21:03 CPT | 02/15/2017 23:00 CPT | 73:57 | 70 | 347 | 3410 - Feedwater pump | high outboard bearing vibration on #1 BFPT
2017 | D1 - Forced - Immediate | 02/27/2017 19:11 CPT | 03/06/2017 08:55 CPT | 157:44 | 254 | 163 | 1455 - Induced draft fans | #2 IDF tripped on ground
2017 | D2 - Forced - Delayed | 03/06/2017 08:55 CPT | 03/09/2017 21:28 CPT | 84:33 | 246 | 171 | 1470 - Induced draft fan motors and drives | IDF #2 out of service for motor repairs
2017 | U1 - Forced - Immediate | 03/09/2017 21:28 CPT | 03/10/2017 05:48 CPT | 8:20 | 417 |  | 1455 - Induced draft fans | Unit tripped when lost #1 IDF while #2 IDF is out of service
2017 | U1 - Forced - Immediate | 03/10/2017 05:49 CPT | 03/10/2017 07:29 CPT | 1:40 | 417 |  | 4750 - Other generator controls and metering problems | No load trip
2017 | D2 - Forced - Delayed | 03/10/2017 07:30 CPT | 03/14/2017 19:02 CPT | 106:32 | 246 | 171 | 1470 - Induced draft fan motors and drives | #2 IDF motor issues
2017 | U1 - Forced - Immediate | 04/15/2017 19:03 CPT | 04/18/2017 06:08 CPT | 59:05 | 417 |  | 1000 - Waterwall (Furnace wall) | Water wall tube leak
2017 | U1 - Forced - Immediate | 04/21/2017 07:27 CPT | 04/21/2017 11:42 CPT | 4:15 | 417 |  | 9300 - Transmission system problems other than catastrophes (do not include switchyard problems in this category; see codes 3600 to 3629) | Lightening strike, lost both Startup Transformers
2017 | U1 - Forced - Immediate | 04/29/2017 19:04 CPT | 04/30/2017 17:46 CPT | 22:42 | 417 |  | 9300 - Transmission system problems other than catastrophes (do not include switchyard problems in this category; see codes 3600 to 3629) | Unit tripped due to blown fuse while doing transmission work
2017 | U3 - Forced - Postponed | 05/02/2017 06:21 CPT | 05/02/2017 21:08 CPT | 14:47 | 417 |  | 0897 - Bottom ash rotary (drag chain type) conveyor and motor | Unit removed from service to make repairs to drag chain
2017 | D1 - Forced - Immediate | 05/28/2017 12:20 CPT | 05/28/2017 15:50 CPT | 3:30 | 242 | 175 | 0270 - Primary air duct and dampers | Failed solenoid on #2 PA Fan let to mill trips on low air flow
2017 | U2 - Forced - Delayed | 05/30/2017 15:50 CPT | 06/14/2017 08:18 CPT | 352:28 | 417 |  | 4261 - Control valves | Leak in Main Steam line, weld failure on HMV 170
2017 | D2 - Forced - Delayed | 07/04/2017 08:57 CPT | 07/04/2017 16:58 CPT | 8:01 | 180 | 237 | 8551 - Electrostatic precipitator field out of service | Lost 12A3 feed to duct 2 resulting in loss of half of precips
2017 | U2 - Forced - Delayed | 07/23/2017 23:23 CPT | 07/28/2017 01:32 CPT | 98:09 | 417 |  | 1488 - Air heater (regenerative) | #2 PAH locked up due to upper guide bearing failure
2017 | U2 - Forced - Delayed | 07/30/2017 10:28 CPT | 07/31/2017 05:25 CPT | 18:57 | 417 |  | 0620 - Other desuperheater/attemperator problems | Leak in SH spray line
2017 | U2 - Forced - Delayed | 08/17/2017 15:56 CPT | 08/20/2017 21:26 CPT | 77:30 | 417 |  | 1080 - Economizer | Tube leak in economizer
2017 | D1 - Forced - Immediate | 08/29/2017 12:57 CPT | 08/29/2017 22:43 CPT | 9:46 | 265 | 152 | 1488 - Air heater (regenerative) | #2 PAH locked up
2017 | U2 - Forced - Delayed | 08/29/2017 22:43 CPT | 09/01/2017 21:04 CPT | 70:21 | 417 |  | 1488 - Air heater (regenerative) | Unit removed from service to repair #2 PAH
2017 | U2 - Forced - Delayed | 09/25/2017 05:31 CPT | 09/25/2017 12:49 CPT | 7:18 | 417 |  | 1488 - Air heater (regenerative) | #2 PAH locked up
2017 | D2 - Forced - Delayed | 09/26/2017 00:55 CPT | 09/26/2017 03:12 CPT | 2:17 | 230 | 187 | 8551 - Electrostatic precipitator field out of service | Lost 11A3 power feed and lost half of precips
2017 | U1 - Forced - Immediate | 09/26/2017 03:12 CPT | 09/26/2017 10:07 CPT | 6:55 | 417 |  | 1455 - Induced draft fans | #2 IDF tripped with #1 IDF out of service
2017 | D2 - Forced - Delayed | 09/26/2017 08:43 CPT | 09/27/2017 01:00 CPT | 16:17 | 285 | 132 | 8551 - Electrostatic precipitator field out of service | Above daily limit for particulates
2017 | D2 - Forced - Delayed | 09/26/2017 10:08 CPT | 09/26/2017 20:42 CPT | 10:34 | 265 | 152 | 8551 - Electrostatic precipitator field out of service | East precips out of service
2017 | D2 - Forced - Delayed | 10/05/2017 09:52 CPT | 10/05/2017 16:40 CPT | 6:48 | 155 | 262 | 8160 - Mist eliminators/demisters and washdown | ME Spray line blew appart, dropped load to prevent environmental issues
2017 | D1 - Forced - Immediate | 10/17/2017 09:41 CPT | 10/17/2017 11:09 CPT | 1:28 | 116 | 301 | 0338 - Pulverizer control systems (temperature and pressure) | #3 mill tripped on high thruse bearing temp
2017 | D1 - Forced - Immediate | 10/17/2017 18:15 CPT | 10/18/2017 02:20 CPT | 8:05 | 86 | 331 | 0250 - Pulverizer feeders | #2 feeer tripped when feeder coupling broke
2017 | D2 - Forced - Delayed | 10/18/2017 06:06 CPT | 10/19/2017 03:06 CPT | 21:00 | 110 | 307 | 0310 - Pulverizer mills | Maintenance issue with weel shield in #3 mill
2017 | U3 - Forced - Postponed | 11/07/2017 23:58 CPT | 11/11/2017 18:38 CPT | 90:40 | 417 |  | 8199 - Other scrubber problems | Clean and make repairs to FGD

## 2018
Year | Event Type | Start Date | End Date | Duration | Derating (MW) | NAC (MW) | Cause Code | Verbal Description
2018 | D1 - Forced - Immediate | 02/01/2018 12:15 CPT | 02/01/2018 19:30 CPT | 7:15 | 260 | 157 | 1410 - Forced draft fan motors | Lost #2 FDF due to bad motor lead
2018 | D2 - Forced - Delayed | 02/02/2018 16:37 CPT | 02/02/2018 20:10 CPT | 3:33 | 110 | 307 | 0360 - Burners | #4 mill removed from service to inspect and purge a hot burner, three mill operation
2018 | D2 - Forced - Delayed | 02/26/2018 11:20 CPT | 02/26/2018 12:44 CPT | 1:24 | 50 | 367 | 8100 - Scrubber/absorber tower or module | Scrubber chemistry
2018 | D2 - Forced - Delayed | 02/26/2018 12:44 CPT | 02/27/2018 12:30 CPT | 23:46 | 154 | 263 | 8199 - Other scrubber problems | Scrubber chemistry
2018 | D2 - Forced - Delayed | 02/27/2018 12:30 CPT | 02/27/2018 16:00 CPT | 3:30 | 117 | 300 | 8199 - Other scrubber problems | Scrubber chemistry
2018 | D2 - Forced - Delayed | 02/27/2018 16:00 CPT | 03/01/2018 06:45 CPT | 38:45 | 97 | 320 | 8199 - Other scrubber problems | Scrubber Chemistry
2018 | D2 - Forced - Delayed | 03/01/2018 06:45 CPT | 03/02/2018 09:00 CPT | 26:15 | 30 | 387 | 8199 - Other scrubber problems | Scrubber Chemistry
2018 | D1 - Forced - Immediate | 03/11/2018 01:20 CPT | 03/11/2018 03:02 CPT | 0:42 | 110 | 307 | 9260 - Low Btu oil | lost #5 mill due to pluggage
2018 | D1 - Forced - Immediate | 03/12/2018 11:01 CPT | 03/12/2018 16:49 CPT | 5:48 | 100 | 317 | 9280 - Frozen coal | #1 mill trip due to 1C igniter and multiple mill issues related to frozen coal
2018 | D1 - Forced - Immediate | 03/12/2018 22:20 CPT | 03/13/2018 01:30 CPT | 3:10 | 110 | 307 | 0360 - Burners | Lost #1 mill due to hot burner
2018 | U1 - Forced - Immediate | 03/13/2018 23:33 CPT | 03/14/2018 04:02 CPT | 4:29 | 417 |  | 1999 - Boiler; miscellaneous | Unit tripped on low drum level
2018 | U1 - Forced - Immediate | 03/23/2018 07:46 CPT | 03/25/2018 11:45 CPT | 51:59 | 417 |  | 1000 - Waterwall (Furnace wall) | Unit tripped due to tube leak
2018 | U1 - Forced - Immediate | 03/25/2018 17:50 CPT | 03/26/2018 17:30 CPT | 23:40 | 417 |  | 1000 - Waterwall (Furnace wall) | tube leak found while performing pre-start up checks
2018 | U1 - Forced - Immediate | 03/26/2018 17:32 CPT | 03/26/2018 17:39 CPT | 0:07 | 417 |  | 1799 - Other boiler instrumentation and control problems | Unit tripped on No Load
2018 | U2 - Forced - Delayed | 04/01/2018 14:05 CPT | 04/06/2018 00:18 CPT | 106:13 | 417 |  | 1000 - Waterwall (Furnace wall) | Water wall tube leak, NE corner
2018 | D1 - Forced - Immediate | 04/06/2018 04:50 CPT | 04/06/2018 05:33 CPT | 0:43 | 110 | 307 | 0250 - Pulverizer feeders | #4 feeder trip
2018 | D1 - Forced - Immediate | 04/23/2018 05:35 CPT | 04/23/2018 06:47 CPT | 1:12 | 110 | 307 | 0310 - Pulverizer mills | #3 mill trip
2018 | D1 - Forced - Immediate | 04/23/2018 09:06 CPT | 04/23/2018 12:23 CPT | 3:17 | 110 | 307 | 0310 - Pulverizer mills | #3 mill trip
2018 | D1 - Forced - Immediate | 04/24/2018 22:42 CPT | 04/24/2018 23:15 CPT | 0:33 | 110 | 307 | 0250 - Pulverizer feeders | #4 mill tripped due to air flow
2018 | D1 - Forced - Immediate | 04/24/2018 23:20 CPT | 04/24/2018 23:40 CPT | 0:20 | 110 | 307 | 0250 - Pulverizer feeders | #4 mill tripped due to air flow
2018 | D1 - Forced - Immediate | 05/07/2018 04:02 CPT | 05/07/2018 04:42 CPT | 0:40 | 110 | 307 | 0320 - Foreign object in Pulverizers mill | #1 feeder tripped when piece of metal lodged in drag chain
2018 | D1 - Forced - Immediate | 05/19/2018 11:17 CPT | 05/19/2018 12:37 CPT | 1:20 | 110 | 307 | 9270 - Wet coal | #2 feeder tripped due to plugged chute
2018 | D1 - Forced - Immediate | 05/20/2018 03:58 CPT | 05/20/2018 04:47 CPT | 0:49 | 110 | 307 | 9270 - Wet coal | #5 mill tripped due to plugged chute
2018 | D2 - Forced - Delayed | 06/01/2018 17:40 CPT | 06/04/2018 08:45 CPT | 63:05 | 32 | 385 | 8652 - Shakers and rappers | Precipitator malfunction
2018 | D2 - Forced - Delayed | 06/04/2018 08:45 CPT | 06/05/2018 09:00 CPT | 24:15 | 22 | 395 | 8652 - Shakers and rappers | Precipitator Malfunction
2018 | D1 - Forced - Immediate | 06/26/2018 04:30 CPT | 06/26/2018 05:00 CPT | 0:30 | 110 | 307 | 9270 - Wet coal | #2 feeder plugged due to wet fuel
2018 | D1 - Forced - Immediate | 06/29/2018 22:55 CPT | 06/29/2018 23:35 CPT | 0:40 | 110 | 307 | 0310 - Pulverizer mills | #2 mill tripped on low oil pressure
2018 | D2 - Forced - Delayed | 07/05/2018 08:31 CPT | 07/05/2018 09:19 CPT | 0:48 | 120 | 297 | 3240 - Cooling tower fans | 11AA1M tripped resulting in loss of all odd Cooling Tower fans
2018 | D2 - Forced - Delayed | 07/06/2018 20:07 CPT | 07/06/2018 20:26 CPT | 0:19 | 33 | 384 | 3441 - Other high pressure heater problems (see condensate system for LP and IP heater codes) | #6 HP heater excursion
2018 | U2 - Forced - Delayed | 07/28/2018 01:29 CPT | 07/28/2018 17:28 CPT | 15:59 | 417 |  | 0600 - Desuperheater/attemperator spray nozzles | Leak on SH spray line
2018 | D2 - Forced - Delayed | 08/03/2018 20:59 CPT | 08/03/2018 21:56 CPT | 0:57 | 10 | 407 | 1455 - Induced draft fans | ID fan stalled resulting in Boiler Master to manual due to air flow issues
2018 | D3 - Forced - Postponed | 08/24/2018 12:50 CPT | 08/24/2018 15:01 CPT | 2:11 | 117 | 300 | 3300 - Condensate water pre-treatment | Leak in river water piping in filter water building
2018 | D2 - Forced - Delayed | 09/12/2018 08:30 CPT | 09/12/2018 23:55 CPT | 15:25 | 12 | 405 | 1455 - Induced draft fans | tube leak caused increase in IDF amps
2018 | U2 - Forced - Delayed | 09/12/2018 23:55 CPT | 09/16/2018 02:39 CPT | 74:44 | 417 |  | 1000 - Waterwall (Furnace wall) | water wall tube leak
2018 | D1 - Forced - Immediate | 09/20/2018 04:59 CPT | 09/20/2018 05:01 CPT | 0:02 | 110 | 307 | 0250 - Pulverizer feeders | Lost coal to #4 feeder
2018 | D2 - Forced - Delayed | 09/22/2018 11:08 CPT | 09/22/2018 14:29 CPT | 3:21 | 117 | 300 | 8560 - Electrostatic precipitator problems | Problems with precips
2018 | D1 - Forced - Immediate | 09/24/2018 15:21 CPT | 09/24/2018 15:31 CPT | 0:10 | 110 | 307 | 0250 - Pulverizer feeders | lost coal to #4 feeder
2018 | D2 - Forced - Delayed | 09/28/2018 07:16 CPT | 09/28/2018 09:20 CPT | 2:04 | 68 | 349 | 8560 - Electrostatic precipitator problems | Problems with precips
2018 | D2 - Forced - Delayed | 09/28/2018 09:20 CPT | 09/29/2018 00:00 CPT | 14:40 | 88 | 329 | 8560 - Electrostatic precipitator problems | Problems with precips
2018 | U2 - Forced - Delayed | 12/30/2018 18:07 CPT | 01/01/2019 00:00 CPT | 29:53 | 417 |  | 1000 - Waterwall (Furnace wall) | water wall tube leak

## 2019
Year | Event Type | Start Date | End Date | Duration | Derating (MW) | NAC (MW) | Cause Code | Verbal Description
2019 | U2 - Forced - Delayed | 01/01/2019 00:00 CPT | 01/01/2019 11:17 CPT | 11:17 | 417 |  | 1000 - Waterwall (Furnace wall) | Continuation of water wall tube leak outage
2019 | D2 - Forced - Delayed | 01/01/2019 11:17 CPT | 01/01/2019 13:30 CPT | 2:13 | 76 | 341 | 3410 - Feedwater pump | Contractor failed to connect oil lines prior to the #2 BFP being started after PO
2019 | D2 - Forced - Delayed | 01/01/2019 13:30 CPT | 01/02/2019 10:30 CPT | 21:00 | 280 | 137 | 8199 - Other scrubber problems | Scrubber chemistry issues after extended planned outage
2019 | D2 - Forced - Delayed | 01/02/2019 10:30 CPT | 01/03/2019 18:05 CPT | 31:35 | 150 | 267 | 8199 - Other scrubber problems | Scrubber chemistry
2019 | U1 - Forced - Immediate | 01/03/2019 18:05 CPT | 01/04/2019 07:32 CPT | 13:27 | 417 |  | 4099 - Other high pressure turbine problems | Unit tripped on turbine rotor position. Black plant followed when aux didn''t transfer
2019 | D2 - Forced - Delayed | 01/04/2019 07:32 CPT | 01/05/2019 00:31 CPT | 16:59 | 70 | 347 | 3410 - Feedwater pump | #2 BFP out of service
2019 | U2 - Forced - Delayed | 01/05/2019 00:31 CPT | 01/12/2019 12:07 CPT | 179:36 | 417 |  | 1040 - First superheater | Tube leak in platen SH
2019 | D2 - Forced - Delayed | 01/12/2019 13:30 CPT | 01/12/2019 16:09 CPT | 2:39 | 406 | 11 | 4099 - Other high pressure turbine problems | Unit held at 44 mwh while monitoring turbine vibration
2019 | U2 - Forced - Delayed | 01/12/2019 16:09 CPT | 01/13/2019 01:24 CPT | 9:15 | 417 |  | 4099 - Other high pressure turbine problems | Unit taken offline to perform turbine balance
2019 | D2 - Forced - Delayed | 01/13/2019 04:30 CPT | 01/13/2019 06:00 CPT | 1:30 | 180 | 237 | 8199 - Other scrubber problems | Scrubber chemistry
2019 | D2 - Forced - Delayed | 01/13/2019 06:00 CPT | 01/13/2019 23:00 CPT | 17:00 | 115 | 302 | 8199 - Other scrubber problems | scrubber chemistry
2019 | D2 - Forced - Delayed | 01/13/2019 23:00 CPT | 01/22/2019 12:24 CPT | 205:24 | 70 | 347 | 3410 - Feedwater pump | #2 BFP out of service
2019 | D2 - Forced - Delayed | 01/22/2019 12:24 CPT | 01/22/2019 14:25 CPT | 2:01 | 115 | 302 | 0330 - Pulverizer coal leak (pulverizers only) | Coal leak on 3B coal pipe
2019 | D2 - Forced - Delayed | 01/22/2019 14:25 CPT | 01/24/2019 04:44 CPT | 38:19 | 70 | 347 | 3410 - Feedwater pump | #2 BFP out of service
2019 | D2 - Forced - Delayed | 01/24/2019 05:50 CPT | 01/24/2019 09:30 CPT | 3:40 | 70 | 347 | 1999 - Boiler; miscellaneous | Reheat safety lifting
2019 | U1 - Forced - Immediate | 02/02/2019 01:34 CPT | 02/02/2019 10:39 CPT | 9:05 | 417 |  | 4490 - Turbine performance testing (use code 9999 for total unit performance testing) | Unit trip during routine turbine test
2019 | D1 - Forced - Immediate | 02/02/2019 14:25 CPT | 02/02/2019 14:35 CPT | 0:10 | 110 | 307 | 0310 - Pulverizer mills | #1 mill tripped due to hot coal pipe
2019 | D1 - Forced - Immediate | 02/04/2019 01:40 CPT | 02/04/2019 02:45 CPT | 1:05 | 117 | 300 | 3631 - 480-volt circuit breakers | Breaker trip resulting in lost of SCR, Precips and CEMS
2019 | D1 - Forced - Immediate | 02/11/2019 05:00 CPT | 02/11/2019 05:35 CPT | 0:35 | 110 | 307 | 0310 - Pulverizer mills | #2 mill tripped while trying to clear pluggage
2019 | D1 - Forced - Immediate | 02/12/2019 15:40 CPT | 02/12/2019 16:30 CPT | 0:50 | 150 | 267 | 9270 - Wet coal | Multiple mills plugged due to wet coal
2019 | D2 - Forced - Delayed | 02/27/2019 17:41 CPT | 02/28/2019 16:30 CPT | 22:49 | 290 | 127 | 1190 - Other tube slagging or fouling | Slag fall resulted in damage to the wet bottom
2019 | D2 - Forced - Delayed | 02/28/2019 23:00 CPT | 03/01/2019 06:40 CPT | 7:40 | 110 | 307 | 0330 - Pulverizer coal leak (pulverizers only) | 3A coal pipe leak
2019 | D2 - Forced - Delayed | 03/01/2019 10:48 CPT | 03/02/2019 01:45 CPT | 14:57 | 110 | 307 | 0330 - Pulverizer coal leak (pulverizers only) | Unable to put #5 mill on due to coal pipe leaks. #3 mill out of service
2019 | D2 - Forced - Delayed | 03/03/2019 08:57 CPT | 03/03/2019 14:04 CPT | 5:07 | 110 | 307 | 0330 - Pulverizer coal leak (pulverizers only) | #5 mill 5E coal pipe leaking
2019 | D1 - Forced - Immediate | 03/07/2019 06:45 CPT | 03/07/2019 08:23 CPT | 1:38 | 240 | 177 | 0260 - Primary air fan | PA fan DC damper went closed resulting in #2 & #5 mill trips
2019 | D2 - Forced - Delayed | 03/07/2019 08:23 CPT | 03/07/2019 09:00 CPT | 0:37 | 116 | 301 | 0310 - Pulverizer mills | #5 mill out of service
2019 | D2 - Forced - Delayed | 03/07/2019 09:54 CPT | 03/07/2019 11:00 CPT | 1:06 | 116 | 301 | 0360 - Burners | Fire in 1A burner barrel
2019 | U2 - Forced - Delayed | 03/24/2019 22:00 CPT | 03/27/2019 02:59 CPT | 52:59 | 417 |  | 1000 - Waterwall (Furnace wall) | Tube leak west side knees
2019 | SF - Startup Failure | 03/27/2019 02:59 CPT | 03/27/2019 12:25 CPT | 9:26 | 417 |  | 3410 - Feedwater pump | Aux BFP tripped during startup
2019 | SF - Startup Failure | 03/27/2019 12:25 CPT | 03/27/2019 15:12 CPT | 2:47 | 417 |  | 4499 - Other miscellaneous steam turbine problems | Turbine tripped during startup
2019 | D2 - Forced - Delayed | 03/27/2019 19:55 CPT | 03/27/2019 21:33 CPT | 1:38 | 50 | 367 | 3431 - Other feedwater valves | Unable to maintain DA level due to partially closed valve
2019 | D1 - Forced - Immediate | 04/01/2019 19:20 CPT | 04/15/2019 03:49 CPT | 320:29 | 220 | 197 | 1470 - Induced draft fan motors and drives | #1 IDF motor went to ground
2019 | D2 - Forced - Delayed | 04/08/2019 12:00 CPT | 04/10/2019 10:00 CPT | 46:00 | 10 | 407 | 1480 - Other induced draft fan problems | Derate with #1 IDF out of service increased due to high amps on #2 IDF
2019 | U1 - Forced - Immediate | 04/15/2019 03:49 CPT | 04/16/2019 14:31 CPT | 34:42 | 417 |  | 1470 - Induced draft fan motors and drives | #2 IDF tripped when motor went to ground while #1 IDF out of service
2019 | D3 - Forced - Postponed | 04/16/2019 14:31 CPT | 05/01/2019 00:00 CPT | 345:29 | 220 | 197 | 1470 - Induced draft fan motors and drives | #2 IDF unavailable due to motor going to ground but unit entered RS status
2019 | D2 - Forced - Delayed | 04/27/2019 18:20 CPT | 04/27/2019 19:30 CPT | 1:10 | 10 | 407 | 4261 - Control valves | #2 gov valve swinging due to loose wires
2019 | D3 - Forced - Postponed | 05/01/2019 00:00 CPT | 05/11/2019 05:47 CPT | 245:47 | 208 | 209 | 1470 - Induced draft fan motors and drives | #2 IDF unavailable, motor send off for repairs
2019 | D3 - Forced - Postponed | 05/11/2019 14:23 CPT | 05/11/2019 16:43 CPT | 2:20 | 110 | 307 | 0330 - Pulverizer coal leak (pulverizers only) | Coal pipe leak on #1 Mill with #3 mill out of service
2019 | D2 - Forced - Delayed | 05/27/2019 16:15 CPT | 05/27/2019 22:45 CPT | 6:30 | 312 | 105 | 0920 - Other slag and ash removal problems A | Slag fall resulted in separation of wet bottom
2019 | D2 - Forced - Delayed | 06/23/2019 11:55 CPT | 06/23/2019 15:20 CPT | 3:25 | 17 | 400 | 3211 - Circulating water pump motors | High back pressure with #1 CWP out of service
2019 | D2 - Forced - Delayed | 06/23/2019 16:00 CPT | 06/23/2019 18:00 CPT | 2:00 | 7 | 410 | 3211 - Circulating water pump motors | High back pressure with #1 CWP out of service
2019 | D2 - Forced - Delayed | 06/26/2019 13:24 CPT | 06/26/2019 21:20 CPT | 7:56 | 3 | 414 | 3211 - Circulating water pump motors | High back pressure with #1 CWP out of service
2019 | D2 - Forced - Delayed | 06/28/2019 13:08 CPT | 06/28/2019 21:44 CPT | 8:36 | 8 | 409 | 3211 - Circulating water pump motors | High back pressure with #1 CWP out of service
2019 | D2 - Forced - Delayed | 07/01/2019 13:12 CPT | 07/01/2019 13:19 CPT | 0:07 | 17 | 400 | 3211 - Circulating water pump motors | High back pressure with #1 CWP out of service
2019 | D2 - Forced - Delayed | 07/02/2019 09:56 CPT | 07/02/2019 18:56 CPT | 9:00 | 22 | 395 | 3211 - Circulating water pump motors | High BP with #1 CWP out of service
2019 | D1 - Forced - Immediate | 07/06/2019 04:58 CPT | 07/06/2019 05:20 CPT | 0:22 | 208 | 209 | 1455 - Induced draft fans | #2 IDF Tripped
2019 | U2 - Forced - Delayed | 07/06/2019 05:20 CPT | 07/06/2019 14:12 CPT | 8:52 | 417 |  | 1487 - Air heater (tubular) | lost MCC12B12, secondary AH electric drive and back up air drive, high exit gas temp
2019 | D1 - Forced - Immediate | 07/07/2019 02:55 CPT | 07/07/2019 04:24 CPT | 1:29 | 280 | 137 | 1455 - Induced draft fans | lost MCC12B12, lost sootblower, lost #2 IDF
2019 | U2 - Forced - Delayed | 08/08/2019 15:11 CPT | 08/13/2019 22:25 CPT | 127:14 | 417 |  | 1040 - First superheater | SH tube leak
2019 | D1 - Forced - Immediate | 08/14/2019 14:15 CPT | 08/14/2019 15:30 CPT | 1:15 | 94 | 323 | 0250 - Pulverizer feeders | #4 mill tripped due to feed issue
2019 | D1 - Forced - Immediate | 08/14/2019 16:35 CPT | 08/14/2019 17:30 CPT | 0:55 | 85 | 332 | 0250 - Pulverizer feeders | #4 feeder tripped
2019 | D1 - Forced - Immediate | 08/16/2019 16:50 CPT | 08/16/2019 17:20 CPT | 0:30 | 85 | 332 | 0250 - Pulverizer feeders | #4 feeder tripped
2019 | D1 - Forced - Immediate | 08/17/2019 11:18 CPT | 08/17/2019 11:58 CPT | 0:40 | 85 | 332 | 0250 - Pulverizer feeders | #4 feeder tripped
2019 | D2 - Forced - Delayed | 09/03/2019 21:47 CPT | 09/03/2019 23:46 CPT | 1:59 | 250 | 167 | 1455 - Induced draft fans | Removed #2 IDF from service to replace breaker
2019 | D1 - Forced - Immediate | 09/08/2019 06:30 CPT | 09/10/2019 21:00 CPT | 62:30 | 110 | 307 | 0310 - Pulverizer mills | #3 mill tripped with #1 mill out of service
2019 | D2 - Forced - Delayed | 09/17/2019 06:45 CPT | 09/18/2019 03:55 CPT | 21:10 | 110 | 307 | 0310 - Pulverizer mills | #3 mill removed from service due to coal leak, #1 mill out of service
2019 | D1 - Forced - Immediate | 09/18/2019 22:54 CPT | 09/19/2019 00:02 CPT | 1:08 | 110 | 307 | 0310 - Pulverizer mills | #3 mill trip with #1 mill out of service
2019 | U1 - Forced - Immediate | 09/22/2019 14:00 CPT | 09/22/2019 20:48 CPT | 6:48 | 417 |  | 4302 - Turbine trip devices (including instruments) | fault in electrical relay 51NAT11 that resulted in turbine trip
2019 | U3 - Forced - Postponed | 10/01/2019 23:59 CPT | 10/02/2019 14:23 CPT | 14:24 | 417 |  | 3833 - Auxiliary steam controls and instruments | Leak in SH Spray Sensing line
2019 | U1 - Forced - Immediate | 10/08/2019 07:26 CPT | 10/08/2019 15:30 CPT | 8:04 | 417 |  | 3621 - Unit auxiliaries transformer | AT-11Bus failure
2019 | SF - Startup Failure | 10/10/2019 00:02 CPT | 10/10/2019 01:17 CPT | 1:15 | 417 |  | 1799 - Other boiler instrumentation and control problems | Boiler Control Trip
2019 | D1 - Forced - Immediate | 10/21/2019 08:08 CPT | 10/21/2019 15:23 CPT | 7:15 | 110 | 307 | 0310 - Pulverizer mills | Three mills available
2019 | U2 - Forced - Delayed | 10/22/2019 09:26 CPT | 10/22/2019 21:39 CPT | 12:13 | 417 |  | 3833 - Auxiliary steam controls and instruments | SH Spray Sensing line leak
2019 | D2 - Forced - Delayed | 10/23/2019 14:15 CPT | 10/23/2019 18:30 CPT | 4:15 | 110 | 307 | 0360 - Burners | 2 mill removed from service due to burner fire
2019 | D1 - Forced - Immediate | 10/29/2019 18:13 CPT | 10/29/2019 19:37 CPT | 1:24 | 110 | 307 | 0250 - Pulverizer feeders | 4 feeder tripped
2019 | D3 - Forced - Postponed | 11/06/2019 22:04 CPT | 11/06/2019 23:16 CPT | 1:12 | 110 | 307 | 1455 - Induced draft fans | Took 4 mill out of service to all load drop due to 2 IDF
2019 | D3 - Forced - Postponed | 11/06/2019 23:18 CPT | 11/07/2019 01:00 CPT | 1:42 | 215 | 202 | 1455 - Induced draft fans | 2 IDF removed from service for repair
2019 | U1 - Forced - Immediate | 11/15/2019 14:51 CPT | 11/15/2019 18:05 CPT | 3:14 | 417 |  | 1799 - Other boiler instrumentation and control problems | Boiler Control Trip
2019 | U1 - Forced - Immediate | 11/15/2019 21:02 CPT | 11/16/2019 09:42 CPT | 12:40 | 417 |  | 1799 - Other boiler instrumentation and control problems | Boiler Control Trip

## 2020
Year | Event Type | Start Date | End Date | Duration | Derating (MW) | NAC (MW) | Cause Code | Verbal Description
2020 | D2 - Forced - Delayed | 01/10/2020 09:30 CPT | 01/10/2020 11:15 CPT | 1:45 | 110 | 307 | 3416 - Other feedwater pump problems | Failed DC Oil pump test
2020 | D1 - Forced - Immediate | 01/20/2020 10:35 CPT | 01/20/2020 11:42 CPT | 1:07 | 110 | 307 | 0250 - Pulverizer feeders | 4 feeder tripped with 1 mill out of service, three mill operation
2020 | D1 - Forced - Immediate | 01/20/2020 22:15 CPT | 01/20/2020 22:45 CPT | 0:30 | 110 | 307 | 0250 - Pulverizer feeders | 1 feeder trip, three mill operation
2020 | D1 - Forced - Immediate | 01/21/2020 00:12 CPT | 01/21/2020 01:18 CPT | 1:06 | 110 | 307 | 0250 - Pulverizer feeders | 1 mill tripped, three mill operation
2020 | D1 - Forced - Immediate | 01/21/2020 08:00 CPT | 01/21/2020 08:21 CPT | 0:21 | 110 | 307 | 0250 - Pulverizer feeders | multiple mill trips
2020 | D1 - Forced - Immediate | 01/21/2020 17:20 CPT | 01/21/2020 17:50 CPT | 0:30 | 110 | 307 | 0250 - Pulverizer feeders | multiple mill trips
2020 | D2 - Forced - Delayed | 02/05/2020 23:25 CPT | 02/06/2020 00:00 CPT | 0:35 | 175 | 242 | 4269 - Other turbine valves (including LP steam admission valves) | SH spray block valve closed causing Safety on Aux steam to lift
2020 | D3 - Forced - Postponed | 02/06/2020 09:30 CPT | 02/06/2020 12:00 CPT | 2:30 | 110 | 307 | 0110 - Other coal fuel supply problems up through bunkers | tripper room deluged, mills 1 and 3 red tagged to check weather heads for water
2020 | D1 - Forced - Immediate | 02/13/2020 19:36 CPT | 02/13/2020 20:03 CPT | 0:27 | 100 | 317 | 0250 - Pulverizer feeders | 2 feeder trip/chute plugged
2020 | D1 - Forced - Immediate | 02/17/2020 05:16 CPT | 02/17/2020 08:50 CPT | 3:34 | 110 | 307 | 0310 - Pulverizer mills | 1 mill tripped/lube oil pump sheered off
2020 | D2 - Forced - Delayed | 02/26/2020 17:15 CPT | 02/27/2020 03:08 CPT | 9:53 | 117 | 300 | 0320 - Foreign object in Pulverizers mill | 2 mill taken out of service due to metal in pyrite pit
2020 | U2 - Forced - Delayed | 02/29/2020 18:53 CPT | 03/01/2020 03:22 CPT | 8:29 | 417 |  | 4261 - Control valves | Leak in first stage spray water control valve
2020 | D3 - Forced - Postponed | 04/22/2020 08:00 CPT | 04/23/2020 16:00 CPT | 32:00 | 82 | 335 | 3431 - Other feedwater valves | #2 BFP Control valve
2020 | D1 - Forced - Immediate | 05/18/2020 23:25 CPT | 05/19/2020 00:28 CPT | 1:03 | 55 | 362 | 0250 - Pulverizer feeders | #2 feeder direct drive key broken between motor and shaft
2020 | U1 - Forced - Immediate | 05/19/2020 13:00 CPT | 05/19/2020 21:24 CPT | 8:24 | 417 |  | 4750 - Other generator controls and metering problems | Two generator RTDs went to bad quality
2020 | RS - Reserve Shutdown | 05/22/2020 00:58 CPT | 05/25/2020 18:22 CPT | 89:24 | 417 |  | 0000 - Reserve shutdown | RESERVE SHUTDOWN
2020 | U1 - Forced - Immediate | 05/25/2020 19:07 CPT | 05/26/2020 01:51 CPT | 6:44 | 417 |  | 3431 - Other feedwater valves | Aux boiler feed pump recirc valve failure
2020 | D1 - Forced - Immediate | 06/10/2020 09:14 CPT | 06/10/2020 09:49 CPT | 0:35 | 155 | 262 | 0310 - Pulverizer mills | multiple mill trips
2020 | D2 - Forced - Delayed | 06/23/2020 11:05 CPT | 06/23/2020 12:19 CPT | 1:14 | 65 | 352 | 0320 - Foreign object in Pulverizers mill | High burner temp #4 mill due to piece of tile from burner tube
2020 | D1 - Forced - Immediate | 07/21/2020 15:25 CPT | 07/21/2020 21:31 CPT | 6:06 | 232 | 185 | 1455 - Induced draft fans | #1 IDF tripped
2020 | D1 - Forced - Immediate | 08/25/2020 08:06 CPT | 08/25/2020 09:07 CPT | 1:01 | 117 | 300 | 0385 - Igniters | Work on 3C Igniter, went to ground blowing fuse to entire deck and igniter ctrl valve
2020 | D1 - Forced - Immediate | 10/05/2020 09:45 CPT | 10/05/2020 10:48 CPT | 1:03 | 50 | 367 | 3410 - Feedwater pump | #2 BFP tripped
2020 | U1 - Forced - Immediate | 10/19/2020 01:04 CPT | 10/19/2020 05:37 CPT | 4:33 | 417 |  | 3415 - Feedwater pump/drive lube oil system | Unit tripped following #2 BFP trip due to problem with the lube oil pump
2020 | U1 - Forced - Immediate | 10/19/2020 09:41 CPT | 10/19/2020 12:13 CPT | 2:32 | 417 |  | 1740 - Boiler drum gage glasses/level indicator | Unit tripped on low drum level
2020 | U1 - Forced - Immediate | 10/19/2020 21:29 CPT | 10/20/2020 05:08 CPT | 7:39 | 417 |  | 1740 - Boiler drum gage glasses/level indicator | Unit tripped on low drum level
2020 | D2 - Forced - Delayed | 10/20/2020 11:15 CPT | 10/20/2020 13:24 CPT | 2:09 | 99 | 318 | 3410 - Feedwater pump | Problem with #1 BFP
2020 | U2 - Forced - Delayed | 10/23/2020 17:20 CPT | 10/24/2020 01:24 CPT | 8:04 | 417 |  | 4261 - Control valves | EH Fluid Leak on #2 Governor Valve
2020 | D2 - Forced - Delayed | 10/24/2020 13:06 CPT | 10/24/2020 21:31 CPT | 8:25 | 87 | 330 | 4261 - Control valves | Bound #1 Throttle Valve
2020 | U2 - Forced - Delayed | 12/04/2020 23:35 CPT | 12/06/2020 01:18 CPT | 25:43 | 417 |  | 1000 - Waterwall (Furnace wall) | water wall tube leak

## 2021
Year | Event Type | Start Date | End Date | Duration | Derating (MW) | NAC (MW) | Cause Code | Verbal Description
2021 | D1 - Forced - Immediate | 01/30/2021 01:27 CPT | 01/30/2021 02:51 CPT | 1:24 | 110 | 307 | 0360 - Burners | #2 mill tripped due to 2E burner temp
2021 | D2 - Forced - Delayed | 02/03/2021 09:26 CPT | 02/03/2021 16:20 CPT | 6:54 | 227 | 190 | 0897 - Bottom ash rotary (drag chain type) conveyor and motor | Drag chain came off sprocket
2021 | D3 - Forced - Postponed | 02/03/2021 23:19 CPT | 02/04/2021 07:00 CPT | 7:41 | 227 | 190 | 0890 - Bottom ash systems (wet or dry) | made repairs to wet bottom
2021 | D1 - Forced - Immediate | 02/04/2021 11:11 CPT | 02/04/2021 12:35 CPT | 1:24 | 127 | 290 | 0265 - Primary air heater | overloads tripped on #1 PAH
2021 | D2 - Forced - Delayed | 02/05/2021 09:45 CPT | 02/05/2021 10:58 CPT | 1:13 | 37 | 380 | 0265 - Primary air heater | Continued problems with #1 PAH
2021 | D2 - Forced - Delayed | 02/08/2021 02:45 CPT | 02/08/2021 03:50 CPT | 1:05 | 110 | 307 | 3352 - Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | boiler chemistry issues
2021 | D2 - Forced - Delayed | 02/08/2021 03:50 CPT | 02/08/2021 05:03 CPT | 1:13 | 47 | 370 | 3352 - Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | boiler chemistry issues
2021 | D2 - Forced - Delayed | 02/08/2021 10:15 CPT | 02/08/2021 12:35 CPT | 2:20 | 177 | 240 | 9270 - Wet coal | Activation of deluge valves resulted in wet fuel in bunkers
2021 | SF - Startup Failure | 02/25/2021 01:00 CPT | 02/25/2021 07:30 CPT | 6:30 | 417 |  | 0265 - Primary air heater | #1 PAH Motor
2021 | D2 - Forced - Delayed | 03/03/2021 13:17 CPT | 03/03/2021 15:05 CPT | 1:48 | 56 | 361 | 0270 - Primary air duct and dampers | High PAH leakage, unable to reach full load without 5 mills and #2 mill out of service
2021 | D2 - Forced - Delayed | 03/06/2021 10:16 CPT | 03/06/2021 11:42 CPT | 1:26 | 60 | 357 | 4269 - Other turbine valves (including LP steam admission valves) | 1st stage east spray valve packing leak
2021 | U1 - Forced - Immediate | 03/17/2021 16:15 CPT | 03/18/2021 17:21 CPT | 25:06 | 417 |  | 1080 - Economizer | Boiler tube leak on economizer header
2021 | U2 - Forced - Delayed | 04/16/2021 00:43 CPT | 04/16/2021 11:13 CPT | 10:30 | 417 |  | 1423 - Secondary air fan/blower motors - variable speed | Unit removed from service when lost 12B12 MCC causing 2 SAH motor drive to trip
2021 | D1 - Forced - Immediate | 04/19/2021 07:45 CPT | 04/19/2021 10:09 CPT | 2:24 | 100 | 317 | 0310 - Pulverizer mills | 1 Mill tripped with one mill out of service. Three mill operation
2021 | U1 - Forced - Immediate | 05/14/2021 11:45 CPT | 05/16/2021 03:09 CPT | 39:24 | 417 |  | 1000 - Waterwall (Furnace wall) | Tube leak on west side slope
2021 | U1 - Forced - Immediate | 06/06/2021 15:54 CPT | 06/06/2021 20:12 CPT | 4:18 | 417 |  | 3211 - Circulating water pump motors | Lost 3 and 2 CWPs. 3 went to ground first and 2 tripped when trying to restart 3
2021 | U1 - Forced - Immediate | 06/09/2021 05:37 CPT | 06/11/2021 10:08 CPT | 52:31 | 417 |  | 1000 - Waterwall (Furnace wall) | Boiler tube leak in economizer section
2021 | D3 - Forced - Postponed | 06/12/2021 17:45 CPT | 06/12/2021 21:09 CPT | 3:24 | 277 | 140 | 1455 - Induced draft fans | Removed 1 IDF from service to replace the trip coil.
2021 | D1 - Forced - Immediate | 06/14/2021 09:20 CPT | 06/14/2021 10:24 CPT | 1:04 | 110 | 307 | 0310 - Pulverizer mills | 4 mill tripped, three mill operation
2021 | U1 - Forced - Immediate | 06/21/2021 01:09 CPT | 06/21/2021 04:51 CPT | 3:42 | 417 |  | 1740 - Boiler drum gage glasses/level indicator | Feed trip let to FW excursion when DA regulator stuck open, low drum level trip
2021 | D2 - Forced - Delayed | 07/02/2021 18:59 CPT | 07/03/2021 12:30 CPT | 17:31 | 227 | 190 | 0897 - Bottom ash rotary (drag chain type) conveyor and motor | Flights on drag chain worn excessively creating maintenance issues on system
2021 | U1 - Forced - Immediate | 07/04/2021 03:22 CPT | 07/04/2021 05:27 CPT | 2:05 | 417 |  | 4263 - Reheat stop valves | Unit tripped while testing RH Stop Valve
2021 | D2 - Forced - Delayed | 07/05/2021 01:00 CPT | 07/05/2021 11:11 CPT | 10:11 | 227 | 190 | 0897 - Bottom ash rotary (drag chain type) conveyor and motor | drag chain flights worn excessively causing maintenance issues with system
2021 | D1 - Forced - Immediate | 07/05/2021 11:11 CPT | 07/05/2021 15:21 CPT | 4:10 | 327 | 90 | 1455 - Induced draft fans | IDF tripped
2021 | U1 - Forced - Immediate | 07/12/2021 19:20 CPT | 07/15/2021 01:10 CPT | 53:50 | 417 |  | 1421 - Secondary air fans/blowers | Secondary Air heater drive locked up
2021 | D2 - Forced - Delayed | 07/20/2021 22:07 CPT | 07/21/2021 01:30 CPT | 3:23 | 140 | 277 | 0897 - Bottom ash rotary (drag chain type) conveyor and motor | Drag chain flights excessively worn creating maintenance issues with system
2021 | D2 - Forced - Delayed | 07/21/2021 01:30 CPT | 07/21/2021 15:14 CPT | 13:44 | 230 | 187 | 0897 - Bottom ash rotary (drag chain type) conveyor and motor | drag chain flights excessively worn creating maintenance issues with system
2021 | U1 - Forced - Immediate | 07/26/2021 17:13 CPT | 07/27/2021 22:46 CPT | 29:33 | 417 |  | 1000 - Waterwall (Furnace wall) | Water wall tube leaks
2021 | D2 - Forced - Delayed | 08/07/2021 05:09 CPT | 08/07/2021 17:55 CPT | 12:46 | 230 | 187 | 0897 - Bottom ash rotary (drag chain type) conveyor and motor | Drag chain flights excessively worn creating issues with the system
2021 | D2 - Forced - Delayed | 08/10/2021 04:28 CPT | 08/10/2021 06:56 CPT | 2:28 | 117 | 300 | 0897 - Bottom ash rotary (drag chain type) conveyor and motor | Drag chain flights worn excessively creating issue with the system
2021 | D2 - Forced - Delayed | 08/10/2021 06:56 CPT | 08/10/2021 13:38 CPT | 6:42 | 232 | 185 | 0897 - Bottom ash rotary (drag chain type) conveyor and motor | drag chain flights causing issue with system
2021 | D1 - Forced - Immediate | 08/28/2021 20:30 CPT | 08/28/2021 22:00 CPT | 1:30 | 192 | 225 | 0270 - Primary air duct and dampers | Two mills tripped with one unavailable, two mill operation
2021 | D2 - Forced - Delayed | 08/28/2021 22:00 CPT | 08/28/2021 23:15 CPT | 1:15 | 100 | 317 | 0270 - Primary air duct and dampers | One mill out of service due to air flow with one mill unavailable
2021 | D2 - Forced - Delayed | 09/06/2021 10:30 CPT | 09/06/2021 13:40 CPT | 3:10 | 25 | 392 | 1400 - Forced draft fans | 2 FDF Stalling
2021 | U2 - Forced - Delayed | 09/11/2021 09:15 CPT | 09/12/2021 00:23 CPT | 15:08 | 417 |  | 4269 - Other turbine valves (including LP steam admission valves) | HMV-170 MS Isolation Valve packing leak
2021 | D1 - Forced - Immediate | 09/29/2021 21:00 CPT | 09/30/2021 01:57 CPT | 4:57 | 127 | 290 | 3622 - Station service startup transformer | Forced derate when lost SU power
2021 | U1 - Forced - Immediate | 10/27/2021 14:51 CPT | 10/28/2021 04:51 CPT | 14:00 | 417 |  | 3700 - Power Station switchyard (non generating unit equipment) | Manual switchyard diconnect
2021 | U1 - Forced - Immediate | 11/14/2021 13:46 CPT | 11/16/2021 02:48 CPT | 37:02 | 417 |  | 1000 - Waterwall (Furnace wall) | Tube leak around nose west side
2021 | U1 - Forced - Immediate | 11/16/2021 03:36 CPT | 11/17/2021 00:53 CPT | 21:17 | 417 |  | 0339 - Pulverizer System Puff | 2 Mill puff
2021 | D2 - Forced - Delayed | 11/17/2021 00:53 CPT | 11/22/2021 01:46 CPT | 120:53 | 117 | 300 | 0300 - Pulverizer motors and drives | Mill availability with 2 mill unavailable and 4 mill needs gearbox repairs
2021 | U1 - Forced - Immediate | 11/22/2021 01:46 CPT | 11/22/2021 07:59 CPT | 6:13 | 417 |  | 3211 - Circulating water pump motors | 2 CWP went to ground
2021 | D2 - Forced - Delayed | 11/24/2021 03:05 CPT | 11/24/2021 09:37 CPT | 6:32 | 117 | 300 | 0310 - Pulverizer mills | 4 mill oil pump coupling issue
2021 | U2 - Forced - Delayed | 12/10/2021 23:17 CPT | 12/11/2021 07:48 CPT | 8:31 | 417 |  | 1455 - Induced draft fans | 1 IDF tripped causing runback Unit pre-emptively tripped during major storm event

## 2022
Year | Event Type | Start Date | End Date | Duration | Derating (MW) | NAC (MW) | Cause Code | Verbal Description
2022 | D2 - Forced - Delayed | 01/01/2022 00:00 CPT | 01/01/2022 01:30 CPT | 1:30 | 200 | 217 | 0897 - Bottom ash rotary (drag chain type) conveyor and motor | Broken link in drag chain
2022 | U2 - Forced - Delayed | 01/18/2022 04:36 CPT | 01/18/2022 20:43 CPT | 16:07 | 417 |  | 0520 - Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HMV-170 MS isolation valve leak
2022 | U1 - Forced - Immediate | 01/19/2022 01:34 CPT | 01/19/2022 04:42 CPT | 3:08 | 417 |  | 0480 - Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | ID Fans overamped following electrical issue with #2 FDF
2022 | U2 - Forced - Delayed | 02/13/2022 13:22 CPT | 02/15/2022 20:42 CPT | 55:20 | 417 |  | 1060 - First reheater | Tube leak in reheater
2022 | D2 - Forced - Delayed | 03/14/2022 05:24 CPT | 03/15/2022 03:48 CPT | 22:24 | 260 | 157 | 8551 - Electrostatic precipitator field out of service | Precips out of service following 6.9 KV trip
2022 | U1 - Forced - Immediate | 03/15/2022 03:48 CPT | 03/15/2022 12:53 CPT | 9:05 | 417 |  | 1999 - Boiler; miscellaneous | Unit tripped when closing 12A3 feeder breaker
2022 | U1 - Forced - Immediate | 04/14/2022 10:44 CPT | 04/14/2022 16:01 CPT | 5:17 | 417 |  | 4609 - Other exciter problems | water leak on the exciter
2022 | U1 - Forced - Immediate | 05/12/2022 03:33 CPT | 05/12/2022 14:08 CPT | 10:35 | 417 |  | 4289 - Other lube oil system problems | low EHF pressure
2022 | U1 - Forced - Immediate | 05/15/2022 08:43 CPT | 05/17/2022 07:40 CPT | 46:57 | 417 |  | 1080 - Economizer | Economizer tube leak near penthouse floor
2022 | U2 - Forced - Delayed | 05/21/2022 13:32 CPT | 05/25/2022 02:16 CPT | 84:44 | 417 |  | 1050 - Second superheater | Tube leak in reheat outlet header
2022 | D2 - Forced - Delayed | 06/08/2022 22:00 CPT | 06/09/2022 17:06 CPT | 19:06 | 117 | 300 | 0310 - Pulverizer mills | broken pitot tube on 2 mill with 5 mill out of service
2022 | U1 - Forced - Immediate | 06/17/2022 10:02 CPT | 06/20/2022 10:56 CPT | 72:54 | 417 |  | 8823 - SCR NOx Other ammonia system problems | loss of SCR flow path
2022 | U2 - Forced - Delayed | 07/02/2022 05:17 CPT | 07/02/2022 12:42 CPT | 7:25 | 417 |  | 1495 - Other air heater fouling (heat pipe; plate-type) | High SAH temp after lost MCC resulting in loss of two AH and an air drive
2022 | U2 - Forced - Delayed | 07/06/2022 23:51 CPT | 07/11/2022 12:36 CPT | 108:45 | 417 |  | 1040 - First superheater | Tube leak in platen SH
2022 | D1 - Forced - Immediate | 07/19/2022 17:35 CPT | 07/19/2022 18:35 CPT | 1:00 | 105 | 312 | 0250 - Pulverizer feeders | #4 feeder tripped with #3 feeder unavailable
2022 | D2 - Forced - Delayed | 08/01/2022 02:02 CPT | 08/02/2022 14:13 CPT | 36:11 | 262 | 155 | 1455 - Induced draft fans | High amps on #1 IDF
2022 | D2 - Forced - Delayed | 08/02/2022 14:13 CPT | 08/03/2022 04:30 CPT | 14:17 | 162 | 255 | 1455 - Induced draft fans | High amps on #1 IDF
2022 | D2 - Forced - Delayed | 08/03/2022 04:30 CPT | 08/03/2022 15:00 CPT | 10:30 | 117 | 300 | 1455 - Induced draft fans | High amps on #1 IDF and Maintenance issues on FGD
2022 | D2 - Forced - Delayed | 08/03/2022 15:00 CPT | 08/03/2022 19:15 CPT | 4:15 | 222 | 195 | 1455 - Induced draft fans | High amps on #1 IDF and Maintenance issues on FGD
2022 | D2 - Forced - Delayed | 08/03/2022 19:15 CPT | 08/03/2022 21:45 CPT | 2:30 | 131 | 286 | 1455 - Induced draft fans | High amps on #1 IDF and Maintenance issues on FGD
2022 | D2 - Forced - Delayed | 08/03/2022 21:45 CPT | 08/04/2022 00:00 CPT | 2:15 | 22 | 395 | 1455 - Induced draft fans | High amps on #1 IDF and Maintenance issues on FGD
2022 | D2 - Forced - Delayed | 08/04/2022 00:00 CPT | 08/04/2022 04:30 CPT | 4:30 | 10 | 407 | 1455 - Induced draft fans | High amps on #1 IDF and Maintenance issues on FGD
2022 | D2 - Forced - Delayed | 08/05/2022 07:15 CPT | 08/05/2022 08:45 CPT | 1:30 | 75 | 342 | 1455 - Induced draft fans | High amps on #1 IDF and Maintenance issues on FGD
2022 | D2 - Forced - Delayed | 08/05/2022 08:45 CPT | 08/06/2022 00:00 CPT | 15:15 | 10 | 407 | 1455 - Induced draft fans | High amps on #1 IDF and Maintenance issues on FGD
2022 | D2 - Forced - Delayed | 08/06/2022 00:00 CPT | 08/08/2022 01:30 CPT | 49:30 | 20 | 397 | 1455 - Induced draft fans | High amps on #1 IDF and Maintenance issues on FGD
2022 | D2 - Forced - Delayed | 08/08/2022 06:00 CPT | 08/09/2022 00:00 CPT | 18:00 | 6 | 411 | 1455 - Induced draft fans | High amps on #1 IDF and Maintenance issues on FGD
2022 | D2 - Forced - Delayed | 08/09/2022 00:00 CPT | 08/12/2022 21:00 CPT | 93:00 | 17 | 400 | 1455 - Induced draft fans | High amps on #1 IDF and Maintenance issues on FGD
2022 | D2 - Forced - Delayed | 08/12/2022 21:00 CPT | 08/13/2022 00:00 CPT | 3:00 | 200 | 217 | 1455 - Induced draft fans | High amps on #1 IDF and Maintenance issues on FGD
2022 | D2 - Forced - Delayed | 08/13/2022 00:00 CPT | 08/13/2022 05:43 CPT | 5:43 | 187 | 230 | 8100 - Scrubber/absorber tower or module | Module removed from service for maintenance and cleaning
2022 | D2 - Forced - Delayed | 08/13/2022 05:43 CPT | 08/13/2022 13:08 CPT | 7:25 | 110 | 307 | 1455 - Induced draft fans | High amps on #1 IDF and Maintenance issues on FGD
2022 | D2 - Forced - Delayed | 08/13/2022 13:08 CPT | 08/14/2022 15:30 CPT | 26:22 | 32 | 385 | 1455 - Induced draft fans | High amps on #1 IDF and Maintenance issues on FGD
2022 | D2 - Forced - Delayed | 08/14/2022 15:30 CPT | 08/15/2022 07:00 CPT | 15:30 | 32 | 385 | 8100 - Scrubber/absorber tower or module | Module removed from service for maintenance and cleaning
2022 | D2 - Forced - Delayed | 08/15/2022 07:00 CPT | 08/15/2022 11:10 CPT | 4:10 | 22 | 395 | 1455 - Induced draft fans | High amps on #1 IDF and Maintenance issues on FGD
2022 | D2 - Forced - Delayed | 08/15/2022 11:10 CPT | 08/16/2022 00:00 CPT | 12:50 | 72 | 345 | 1455 - Induced draft fans | High amps on #1 IDF and Maintenance issues on FGD
2022 | D2 - Forced - Delayed | 08/16/2022 00:00 CPT | 08/16/2022 04:15 CPT | 4:15 | 42 | 375 | 1455 - Induced draft fans | High amps on #1 IDF and Maintenance issues on FGD
2022 | D2 - Forced - Delayed | 08/16/2022 04:15 CPT | 08/16/2022 23:58 CPT | 19:43 | 62 | 355 | 1455 - Induced draft fans | High amps on #1 IDF and Maintenance issues on FGD
2022 | SF - Startup Failure | 08/20/2022 03:10 CPT | 08/20/2022 04:09 CPT | 0:59 | 417 |  | 1799 - Other boiler instrumentation and control problems | startup failure
2022 | D2 - Forced - Delayed | 08/20/2022 04:09 CPT | 08/21/2022 00:00 CPT | 19:51 | 117 | 300 | 1455 - Induced draft fans | High amps on #1 IDF and Maintenance issues on FGD
2022 | D2 - Forced - Delayed | 08/21/2022 00:00 CPT | 08/21/2022 08:45 CPT | 8:45 | 87 | 330 | 1455 - Induced draft fans | High amps on #1 IDF and Maintenance issues on FGD
2022 | D2 - Forced - Delayed | 08/21/2022 08:45 CPT | 08/22/2022 08:45 CPT | 24:00 | 67 | 350 | 1455 - Induced draft fans | High amps on #1 IDF and Maintenance issues on FGD
2022 | D2 - Forced - Delayed | 08/22/2022 08:45 CPT | 08/23/2022 00:00 CPT | 15:15 | 75 | 342 | 3410 - Feedwater pump | #2 BFPT offline for repairs
2022 | D2 - Forced - Delayed | 08/24/2022 00:00 CPT | 08/24/2022 07:40 CPT | 7:40 | 65 | 352 | 3410 - Feedwater pump | #2 BFP offline for repairs
2022 | U2 - Forced - Delayed | 08/24/2022 07:40 CPT | 08/26/2022 03:09 CPT | 43:29 | 417 |  | 1487 - Air heater (tubular) | #1 PAH not turning
2022 | D2 - Forced - Delayed | 08/26/2022 03:09 CPT | 09/01/2022 00:00 CPT | 140:51 | 14.4 | 402.6 | 1455 - Induced draft fans | High amps on #1 IDF and Maintenance issues on FGD
2022 | D2 - Forced - Delayed | 09/01/2022 00:00 CPT | 09/01/2022 22:00 CPT | 22:00 | 10 | 407 | 1455 - Induced draft fans | High amps on #1 IDF and Maintenance issues on FGD
2022 | D2 - Forced - Delayed | 09/01/2022 22:00 CPT | 09/02/2022 02:06 CPT | 4:06 | 147 | 270 | 1455 - Induced draft fans | High amps on #1 IDF and Maintenance issues on FGD
2022 | D2 - Forced - Delayed | 09/02/2022 02:06 CPT | 09/02/2022 05:06 CPT | 3:00 | 171 | 246 | 1455 - Induced draft fans | High amps on #1 IDF and Maintenance issues on FGD
2022 | D2 - Forced - Delayed | 09/02/2022 05:06 CPT | 09/02/2022 20:36 CPT | 15:30 | 53 | 364 | 1455 - Induced draft fans | High amps on #1 IDF and Maintenance issues on FGD
2022 | D2 - Forced - Delayed | 09/02/2022 20:36 CPT | 09/03/2022 04:36 CPT | 8:00 | 207 | 210 | 1455 - Induced draft fans | High amps on #1 IDF and Maintenance issues on FGD
2022 | D2 - Forced - Delayed | 09/03/2022 04:36 CPT | 09/03/2022 19:23 CPT | 14:47 | 51 | 366 | 1455 - Induced draft fans | High amps on #1 IDF and Maintenance issues on FGD
2022 | D2 - Forced - Delayed | 09/03/2022 19:23 CPT | 09/04/2022 00:45 CPT | 5:22 | 157 | 260 | 1455 - Induced draft fans | High amps on #1 IDF and Maintenance issues on FGD
2022 | D2 - Forced - Delayed | 09/04/2022 00:45 CPT | 09/04/2022 03:00 CPT | 2:15 | 217 | 200 | 1455 - Induced draft fans | High amps on #1 IDF and Maintenance issues on FGD
2022 | D2 - Forced - Delayed | 09/04/2022 03:00 CPT | 09/04/2022 08:35 CPT | 5:35 | 167 | 250 | 1455 - Induced draft fans | High amps on #1 IDF and Maintenance issues on FGD
2022 | D2 - Forced - Delayed | 09/04/2022 08:35 CPT | 09/05/2022 00:00 CPT | 15:25 | 47 | 370 | 1455 - Induced draft fans | High amps on #1 IDF and Maintenance issues on FGD
2022 | D2 - Forced - Delayed | 09/05/2022 00:00 CPT | 09/06/2022 00:00 CPT | 24:00 | 28 | 389 | 1455 - Induced draft fans | High amps on #1 IDF and Maintenance issues on FGD
2022 | D2 - Forced - Delayed | 09/06/2022 00:00 CPT | 09/07/2022 00:00 CPT | 24:00 | 26.96 | 390.04 | 1455 - Induced draft fans | High amps on #1 IDF and Maintenance issues on FGD
2022 | D2 - Forced - Delayed | 09/07/2022 00:00 CPT | 09/08/2022 00:00 CPT | 24:00 | 15.47 | 401.53 | 1455 - Induced draft fans | High amps on #1 IDF and Maintenance issues on FGD
2022 | D2 - Forced - Delayed | 09/08/2022 00:00 CPT | 09/09/2022 00:00 CPT | 24:00 | 19.43 | 397.57 | 1455 - Induced draft fans | High amps on #1 IDF and Maintenance issues on FGD
2022 | D2 - Forced - Delayed | 09/09/2022 00:00 CPT | 09/10/2022 00:00 CPT | 24:00 | 92.73 | 324.27 | 8100 - Scrubber/absorber tower or module | Cleaning and repairs to components
2022 | D2 - Forced - Delayed | 09/10/2022 00:00 CPT | 09/11/2022 00:00 CPT | 24:00 | 76.6 | 340.4 | 8100 - Scrubber/absorber tower or module | Cleaning and repairs to components
2022 | D2 - Forced - Delayed | 09/11/2022 00:00 CPT | 09/11/2022 00:29 CPT | 0:29 | 34 | 383 | 1455 - Induced draft fans | High amps on #1 IDF and Maintenance issues on FGD
2022 | U2 - Forced - Delayed | 09/11/2022 00:29 CPT | 09/14/2022 01:45 CPT | 73:16 | 417 |  | 1035 - Platen superheater | tube leak B Platen SH
2022 | U1 - Forced - Immediate | 09/15/2022 06:15 CPT | 09/16/2022 12:40 CPT | 30:25 | 417 |  | 1080 - Economizer | tube leak econ inlet header
2022 | D2 - Forced - Delayed | 09/17/2022 17:53 CPT | 09/18/2022 00:00 CPT | 6:07 | 85 | 332 | 1455 - Induced draft fans | High amps on #1 IDF and Maintenance issues on FGD
2022 | D2 - Forced - Delayed | 09/18/2022 00:00 CPT | 09/19/2022 00:00 CPT | 24:00 | 11 | 406 | 1455 - Induced draft fans | High amps on #1 IDF and Maintenance issues on FGD
2022 | D2 - Forced - Delayed | 09/19/2022 00:00 CPT | 09/20/2022 00:00 CPT | 24:00 | 19.75 | 397.25 | 1455 - Induced draft fans | High amps on #1 IDF and Maintenance issues on FGD
2022 | D2 - Forced - Delayed | 09/20/2022 06:00 CPT | 09/20/2022 09:30 CPT | 3:30 | 300 | 117 | 1455 - Induced draft fans | #1 IDF tripped
2022 | D2 - Forced - Delayed | 09/20/2022 09:30 CPT | 09/21/2022 04:35 CPT | 19:05 | 25 | 392 | 1455 - Induced draft fans | High amps on #1 IDF and Maintenance issues on FGD
2022 | D2 - Forced - Delayed | 09/21/2022 08:10 CPT | 09/21/2022 11:20 CPT | 3:10 | 9 | 408 | 1455 - Induced draft fans | High amps on #1 IDF and Maintenance issues on FGD
2022 | D2 - Forced - Delayed | 09/21/2022 11:20 CPT | 09/21/2022 22:00 CPT | 10:40 | 25 | 392 | 1455 - Induced draft fans | High amps on #1 IDF and Maintenance issues on FGD
2022 | D2 - Forced - Delayed | 09/21/2022 22:00 CPT | 09/22/2022 05:30 CPT | 7:30 | 97 | 320 | 1455 - Induced draft fans | High amps on #1 IDF and Maintenance issues on FGD
2022 | D2 - Forced - Delayed | 09/22/2022 05:30 CPT | 09/22/2022 16:30 CPT | 11:00 | 25 | 392 | 1455 - Induced draft fans | High amps on #1 IDF and Maintenance issues on FGD
2022 | D2 - Forced - Delayed | 09/24/2022 04:15 CPT | 09/24/2022 13:10 CPT | 8:55 | 5 | 412 | 1455 - Induced draft fans | High amps on #1 IDF and Maintenance issues on FGD
2022 | D2 - Forced - Delayed | 09/24/2022 13:10 CPT | 09/25/2022 00:55 CPT | 11:45 | 16 | 401 | 1455 - Induced draft fans | High amps on #1 IDF and Maintenance issues on FGD
2022 | D2 - Forced - Delayed | 09/25/2022 00:55 CPT | 09/25/2022 03:45 CPT | 2:50 | 115 | 302 | 8100 - Scrubber/absorber tower or module | Cleaning and repairs to components
2022 | D2 - Forced - Delayed | 09/25/2022 03:45 CPT | 09/25/2022 07:00 CPT | 3:15 | 94 | 323 | 8100 - Scrubber/absorber tower or module | Cleaning and repairs to components
2022 | D2 - Forced - Delayed | 09/25/2022 07:00 CPT | 09/26/2022 00:00 CPT | 17:00 | 15 | 402 | 1455 - Induced draft fans | High amps on #1 IDF and Maintenance issues on FGD
2022 | D2 - Forced - Delayed | 09/26/2022 00:00 CPT | 09/26/2022 14:00 CPT | 14:00 | 20 | 397 | 1455 - Induced draft fans | High amps on #1 IDF and Maintenance issues on FGD
2022 | D2 - Forced - Delayed | 09/27/2022 00:00 CPT | 09/27/2022 12:00 CPT | 12:00 | 10 | 407 | 1455 - Induced draft fans | High amps on #1 IDF and Maintenance issues on FGD
2022 | D2 - Forced - Delayed | 09/28/2022 00:00 CPT | 09/29/2022 00:00 CPT | 24:00 | 7 | 410 | 1455 - Induced draft fans | High amps on #1 IDF and Maintenance issues on FGD
2022 | D2 - Forced - Delayed | 09/29/2022 00:00 CPT | 09/30/2022 00:00 CPT | 24:00 | 15 | 402 | 1455 - Induced draft fans | High amps on #1 IDF and Maintenance issues on FGD
2022 | D2 - Forced - Delayed | 09/30/2022 00:00 CPT | 10/01/2022 00:00 CPT | 24:00 | 18 | 399 | 1455 - Induced draft fans | High amps on #1 IDF and Maintenance issues on FGD
2022 | U1 - Forced - Immediate | 11/21/2022 16:35 CPT | 11/21/2022 20:17 CPT | 3:42 | 417 |  | 1740 - Boiler drum gage glasses/level indicator | Unit tripped on low drum level while at low load for AVR Testing
2022 | U1 - Forced - Immediate | 11/22/2022 10:38 CPT | 11/22/2022 13:59 CPT | 3:21 | 417 |  | 1740 - Boiler drum gage glasses/level indicator | Unit tripped on low drum level during AVR testing
2022 | U1 - Forced - Immediate | 11/22/2022 14:26 CPT | 11/22/2022 17:24 CPT | 2:58 | 417 |  | 1740 - Boiler drum gage glasses/level indicator | Unit tripped on low drum level while at very low load for AVR testing
2022 | D2 - Forced - Delayed | 11/22/2022 18:49 CPT | 11/22/2022 22:20 CPT | 3:31 | 227 | 190 | 1455 - Induced draft fans | High vibration on ID Fans
2022 | D2 - Forced - Delayed | 11/22/2022 22:20 CPT | 11/23/2022 03:46 CPT | 5:26 | 287 | 130 | 1455 - Induced draft fans | High vibration on ID Fans
2022 | U2 - Forced - Delayed | 11/23/2022 03:46 CPT | 11/23/2022 22:21 CPT | 18:35 | 417 |  | 1455 - Induced draft fans | Unit removed from service due to high vibration on ID Fans
2022 | D2 - Forced - Delayed | 11/23/2022 18:36 CPT | 11/24/2022 05:40 CPT | 11:04 | 133 | 284 | 1455 - Induced draft fans | High vibration on ID Fans
2022 | D2 - Forced - Delayed | 11/24/2022 05:40 CPT | 11/24/2022 13:20 CPT | 7:40 | 193 | 224 | 1455 - Induced draft fans | High vibration on ID Fans
2022 | D2 - Forced - Delayed | 11/24/2022 13:20 CPT | 11/25/2022 04:25 CPT | 15:05 | 160 | 257 | 1455 - Induced draft fans | High vibration on ID Fans
2022 | U2 - Forced - Delayed | 11/25/2022 04:25 CPT | 11/26/2022 18:14 CPT | 37:49 | 417 |  | 1455 - Induced draft fans | #2 IDF out of service
2022 | D2 - Forced - Delayed | 11/25/2022 18:14 CPT | 11/27/2022 22:13 CPT | 51:59 | 10 | 407 | 1599 - Other miscellaneous boiler air and gas system problems | combustion issues related to air flow
2022 | D2 - Forced - Delayed | 11/28/2022 14:50 CPT | 11/28/2022 16:30 CPT | 1:40 | 117 | 300 | 1455 - Induced draft fans | High vibration on ID Fans
2022 | D2 - Forced - Delayed | 11/28/2022 16:30 CPT | 11/28/2022 22:30 CPT | 6:00 | 57 | 360 | 1455 - Induced draft fans | High vibration on ID Fans
2022 | D2 - Forced - Delayed | 11/28/2022 22:30 CPT | 11/29/2022 10:00 CPT | 11:30 | 27 | 390 | 1455 - Induced draft fans | High vibration on ID Fans
2022 | D2 - Forced - Delayed | 11/29/2022 14:50 CPT | 11/29/2022 22:45 CPT | 7:55 | 42 | 375 | 1455 - Induced draft fans | High vibration on ID Fans
2022 | D2 - Forced - Delayed | 12/01/2022 00:00 CPT | 12/02/2022 09:43 CPT | 33:43 | 3 | 414 | 1599 - Other miscellaneous boiler air and gas system problems | combustion issues related to air flow
2022 | U2 - Forced - Delayed | 12/02/2022 09:43 CPT | 12/02/2022 12:00 CPT | 2:17 | 417 |  | 8499 - Other miscellaneous wet scrubber problems | Operators removed from service to protect the new FGD/ all four recycle pumps offline
2022 | D2 - Forced - Delayed | 12/04/2022 23:44 CPT | 12/18/2022 06:00 CPT | 318:16 | 3 | 414 | 1599 - Other miscellaneous boiler air and gas system problems | combustion issues related to air flow
2022 | U1 - Forced - Immediate | 12/18/2022 09:36 CPT | 12/18/2022 12:59 CPT | 3:23 | 417 |  | 1740 - Boiler drum gage glasses/level indicator | Unit tripped on low drum level during AVR testing
2022 | D2 - Forced - Delayed | 12/18/2022 12:59 CPT | 12/19/2022 05:20 CPT | 16:21 | 3 | 414 | 1599 - Other miscellaneous boiler air and gas system problems | combustion issue related to air flow
2022 | D1 - Forced - Immediate | 12/19/2022 06:06 CPT | 12/19/2022 09:01 CPT | 2:55 | 207 | 210 | 1455 - Induced draft fans | Lost #2 IDF
2022 | U2 - Forced - Delayed | 12/19/2022 09:01 CPT | 12/19/2022 13:54 CPT | 4:53 | 417 |  | 8499 - Other miscellaneous wet scrubber problems | Lost communication with new fgd, all four recycle pumps off
2022 | D2 - Forced - Delayed | 12/19/2022 13:54 CPT | 12/22/2022 23:21 CPT | 81:27 | 204 | 213 | 1455 - Induced draft fans | #2 IDF out of service
2022 | U1 - Forced - Immediate | 12/22/2022 23:21 CPT | 12/23/2022 01:56 CPT | 2:35 | 417 |  | 1455 - Induced draft fans | wet/frozen fuel led to air flow issues with #2 IDF out of service
2022 | D2 - Forced - Delayed | 12/23/2022 01:56 CPT | 12/23/2022 19:53 CPT | 17:57 | 204 | 213 | 1455 - Induced draft fans | #2 IDF out of service
2022 | D2 - Forced - Delayed | 12/28/2022 09:30 CPT | 01/01/2023 00:00 CPT | 86:30 | 200 | 217 | 1455 - Induced draft fans | #2 IDF out of service

## 2023
Year | Event Type | Start Date | End Date | Duration | Derating (MW) | NAC (MW) | Cause Code | Verbal Description
2023 | D2 - Forced - Delayed | 01/01/2023 00:00 CPT | 01/02/2023 19:22 CPT | 43:22 | 200 | 217 | 1455 - Induced draft fans | 2 IDF out of service
2023 | D2 - Forced - Delayed | 01/02/2023 19:22 CPT | 01/05/2023 13:00 CPT | 65:38 | 3 | 414 | 1455 - Induced draft fans | air flow issues related to IDFs
2023 | D1 - Forced - Immediate | 01/17/2023 05:16 CPT | 01/18/2023 07:37 CPT | 26:21 | 217 | 200 | 1455 - Induced draft fans | 1 IDF tripped
2023 | U1 - Forced - Immediate | 01/18/2023 17:37 CPT | 01/21/2023 21:41 CPT | 76:04 | 417 |  | 1400 - Forced draft fans | Unit tripped due to breaker issue and Platen SH tube leak
2023 | D2 - Forced - Delayed | 01/22/2023 16:15 CPT | 01/24/2023 08:30 CPT | 40:15 | 250 | 167 | 3110 - Condenser tube leaks | condenser leaks
2023 | U1 - Forced - Immediate | 01/30/2023 07:07 CPT | 01/30/2023 13:52 CPT | 6:45 | 417 |  | 3410 - Feedwater pump | Outboard bearing vibration and lost 1 BFP
2023 | U2 - Forced - Delayed | 02/16/2023 06:05 CPT | 02/16/2023 15:23 CPT | 9:18 | 417 |  | 8199 - Other scrubber problems | Loss of power to FGD following lightening strike
2023 | U2 - Forced - Delayed | 03/03/2023 12:40 CPT | 03/03/2023 23:28 CPT | 10:48 | 417 |  | 8199 - Other scrubber problems | loss of power to FGD
2023 | D2 - Forced - Delayed | 03/12/2023 20:37 CPT | 03/13/2023 21:30 CPT | 24:53 | 17 | 400 | 1455 - Induced draft fans | High vibration on 2 IDF
2023 | D1 - Forced - Immediate | 03/13/2023 21:30 CPT | 03/13/2023 22:30 CPT | 1:00 | 250 | 167 | 1455 - Induced draft fans | lost 2 IDF and 2 FDF
2023 | D2 - Forced - Delayed | 03/13/2023 22:30 CPT | 03/17/2023 23:50 CPT | 97:20 | 17 | 400 | 1455 - Induced draft fans | High vibration on 2 IDF
2023 | D1 - Forced - Immediate | 03/27/2023 23:24 CPT | 03/28/2023 00:21 CPT | 0:57 | 155 | 262 | 3410 - Feedwater pump | 2 BFPT tripped
2023 | D2 - Forced - Delayed | 03/28/2023 03:22 CPT | 03/29/2023 04:00 CPT | 24:38 | 137 | 280 | 8199 - Other scrubber problems | PLC problem at Ball Mills
2023 | D2 - Forced - Delayed | 03/31/2023 21:50 CPT | 04/01/2023 06:05 CPT | 8:15 | 137 | 280 | 8199 - Other scrubber problems | PLC problems at ball mills
2023 | D2 - Forced - Delayed | 04/01/2023 06:05 CPT | 04/01/2023 07:30 CPT | 1:25 | 240 | 177 | 8010 - Crushers/mills | Control issues with ball mills resulting in problems with limestone supply
2023 | D2 - Forced - Delayed | 04/01/2023 07:30 CPT | 04/01/2023 11:46 CPT | 4:16 | 247 | 170 | 8010 - Crushers/mills | Ball mill control issues resulting affecting limestone supply
2023 | D2 - Forced - Delayed | 04/01/2023 11:46 CPT | 04/01/2023 17:34 CPT | 5:48 | 280 | 137 | 8010 - Crushers/mills | Ball mill control issues interupting limestone supply
2023 | U2 - Forced - Delayed | 05/26/2023 14:26 CPT | 05/30/2023 23:36 CPT | 105:10 | 417 |  | 1060 - First reheater | tube leak reheat section
2023 | D2 - Forced - Delayed | 05/31/2023 07:15 CPT | 05/31/2023 20:30 CPT | 13:15 | 237 | 180 | 3110 - Condenser tube leaks | Took half of condenser out of service due to tube leaks
2023 | D2 - Forced - Delayed | 05/31/2023 20:30 CPT | 05/31/2023 23:35 CPT | 3:05 | 157 | 260 | 3410 - Feedwater pump | #2 BFPT out of service
2023 | D2 - Forced - Delayed | 06/02/2023 21:11 CPT | 06/02/2023 22:15 CPT | 1:04 | 203 | 214 | 3620 - Main transformer | Loss of amps on 11A 6.9 Main Buss
2023 | D1 - Forced - Immediate | 06/02/2023 22:15 CPT | 06/03/2023 01:21 CPT | 3:06 | 290 | 127 | 3410 - Feedwater pump | Operator tripped 11A Main Breaker resulting in loss of #1 BPT then #1 IDF and #1 FDF
2023 | U2 - Forced - Delayed | 06/03/2023 01:21 CPT | 06/05/2023 15:17 CPT | 61:56 | 417 |  | 1799 - Other boiler instrumentation and control problems | Operator tripped unit due to indication of boiler pH excursion related to chiller trip
2023 | D2 - Forced - Delayed | 06/05/2023 15:17 CPT | 07/02/2023 14:01 CPT | 646:44 | 177 | 240 | 1455 - Induced draft fans | #1 IDF out of service
2023 | D2 - Forced - Delayed | 08/05/2023 00:28 CPT | 08/05/2023 13:17 CPT | 12:49 | 267 | 150 | 0897 - Bottom ash rotary (drag chain type) conveyor and motor | Broken drag chain
2023 | D2 - Forced - Delayed | 08/05/2023 13:46 CPT | 08/06/2023 10:00 CPT | 20:14 | 169 | 248 | 0920 - Other slag and ash removal problems A | work on wet bottom and remove bottom ash
2023 | D2 - Forced - Delayed | 08/10/2023 01:54 CPT | 08/10/2023 10:45 CPT | 8:51 | 267 | 150 | 0030 - Coal conveyors and feeders | lost power to coal handling
2023 | D2 - Forced - Delayed | 08/11/2023 14:48 CPT | 08/11/2023 21:10 CPT | 6:22 | 267 | 150 | 0030 - Coal conveyors and feeders | lost power to coal handling
2023 | D2 - Forced - Delayed | 08/20/2023 17:37 CPT | 08/21/2023 04:45 CPT | 11:08 | 232 | 185 | 1455 - Induced draft fans | High inboard motor temp on #2 IDF
2023 | D2 - Forced - Delayed | 08/21/2023 04:46 CPT | 08/22/2023 12:40 CPT | 31:54 | 197 | 220 | 1455 - Induced draft fans | High inboard motor temp on #2 IDF
2023 | U1 - Forced - Immediate | 09/06/2023 10:30 CPT | 09/09/2023 03:00 CPT | 64:30 | 417 |  | 1000 - Waterwall (Furnace wall) | Water wall tube leak and also found RH tube leak
2023 | U2 - Forced - Delayed | 09/10/2023 08:30 CPT | 09/13/2023 00:42 CPT | 64:12 | 417 |  | 0260 - Primary air fan | #2 PAF and also elevated boiler chemistry (condenser leaks)
2023 | D2 - Forced - Delayed | 09/13/2023 00:42 CPT | 09/13/2023 15:00 CPT | 14:18 | 286 | 131 | 0260 - Primary air fan | Problems with #2 PAF
2023 | D2 - Forced - Delayed | 09/13/2023 15:00 CPT | 09/15/2023 01:20 CPT | 34:20 | 267 | 150 | 0260 - Primary air fan | Problems with #2 PAF
2023 | D2 - Forced - Delayed | 09/15/2023 01:20 CPT | 09/15/2023 12:20 CPT | 11:00 | 259 | 158 | 0260 - Primary air fan | Problems with #2 PAF
2023 | D2 - Forced - Delayed | 09/15/2023 16:15 CPT | 09/15/2023 22:25 CPT | 6:10 | 267 | 150 | 0260 - Primary air fan | Maintenance on #2 PAF after blew out expansion joint
2023 | U2 - Forced - Delayed | 09/26/2023 07:58 CPT | 09/26/2023 21:16 CPT | 13:18 | 417 |  | 8199 - Other scrubber problems | Loss of vital equip to new FGD leading to elevated gas temps
2023 | U2 - Forced - Delayed | 09/27/2023 11:05 CPT | 09/27/2023 16:04 CPT | 4:59 | 417 |  | 8199 - Other scrubber problems | Loss of vital equip to new FGD leading to elevated gas temps
2023 | D3 - Forced - Postponed | 10/10/2023 22:30 CPT | 10/11/2023 02:30 CPT | 4:00 | 200 | 217 | 0260 - Primary air fan | Repair expansion joint on #2 PAF
2023 | D2 - Forced - Delayed | 11/03/2023 11:23 CPT | 11/05/2023 04:20 CPT | 41:57 | 275 | 142 | 3690 - Station Service Power Distribution System; General | Lost 6.9 power feeds to coal handling and ball mills
2023 | U2 - Forced - Delayed | 11/05/2023 04:20 CPT | 11/08/2023 09:40 CPT | 77:20 | 417 |  | 3661 - 4160-volt circuit breakers | Main and Tie breakers to Ball Mills will not close
2023 | D2 - Forced - Delayed | 11/08/2023 21:50 CPT | 11/09/2023 19:20 CPT | 21:30 | 200 | 217 | 8000 - Chemical feed storage; mill feeders; and conveyors | Low absorber pH
2023 | D2 - Forced - Delayed | 11/09/2023 19:20 CPT | 11/09/2023 23:45 CPT | 4:25 | 90 | 327 | 8000 - Chemical feed storage; mill feeders; and conveyors | low absorber pH
2023 | D2 - Forced - Delayed | 11/24/2023 08:15 CPT | 11/24/2023 22:00 CPT | 13:45 | 70 | 347 | 8020 - Mill slurry tanks supply problems | Ball Mill issues
2023 | U2 - Forced - Delayed | 12/07/2023 22:07 CPT | 12/11/2023 06:29 CPT | 80:22 | 417 |  | 3299 - Other circulating water system problems | Ruptured Circulating Water discharge line
2023 | D2 - Forced - Delayed | 12/13/2023 14:52 CPT | 12/13/2023 17:41 CPT | 2:49 | 115 | 302 | 1400 - Forced draft fans | Stack fans out of service resulting in inability to maintain adequate O2 levels
2023 | D3 - Forced - Postponed | 12/14/2023 07:08 CPT | 12/14/2023 15:08 CPT | 8:00 | 36 | 381 | 1400 - Forced draft fans | Stack fans out of service resulting in inability to maintain adequate O2 levels
2023 | D3 - Forced - Postponed | 12/15/2023 07:00 CPT | 12/15/2023 13:32 CPT | 6:32 | 40 | 377 | 1400 - Forced draft fans | Stack fans out of service resulting in inability to maintain adequate O2 levels