## Cold Weather Event Days
UnitName | EventType | EventNo | CauseCode | Original Start* | Original End* | EventStartforCalc | EventEndforCalc | Duration_Hrs | Equiv. Dur Hrs | MWH Lost | GAC | GMC | NMC | Cause | eventDescription
2014-01-06
BR11 | U1 | 3 | 5017 |  |  | 2014-01-06 17:57 | 2014-01-06 19:14 | 1.2833 | 1.2833 | 164.2667 | 0 | 129 | 128 | Low pressure compressor bleed valves | F550Loose limit switch on blow off valve caused unit to trip.
BR5 | U1 | 2 | 5054 |  |  | 2014-01-06 08:23 | 2014-01-06 11:47 | 3.4 | 3.4 | 442 | 0 | 131 | 130 | Water injection system | F480Instrument measuring DP across water injection control started to freeze. Operato
CR11 | U1 | 2 | 5130 |  | 2014-01-07 09:05 | 2014-01-06 20:13 | 2014-01-07 | 3.7833 | 3.7833 | 52.9667 | 0 | 14 | 14 | Starting system (including motor) | F030Broken terminal on battery cable causing Cane Run 11 starting diesel to be unable
GH2 | D1 | 1 | 9650 |  |  | 2014-01-06 11:20 | 2014-01-06 12:00 | 0.66667 | 0.21218 | 101.2102 | 347 | 509 | 477 | Other stack/exhaust emissions - fossil (use codes 9200 to 9290 if fuel quality causes pollution control equipment problems that result in excess stack emissions) | Load Reduction #1Lost SO3 mitigation system. Air pressure / injection causing H2S
HA1 | SF | 2 | 5160 |  | 2014-01-14 13:14 | 2014-01-06 21:22 | 2014-01-07 | 2.6333 | 2.6333 | 36.8667 | 0 | 14 | 14 | Cooling and seal air system | F540Busted glycol line on radiator. Failed to ignite on start up.
MC2 | D1 | 7 | 1850 | 2014-01-05 05:35 |  | 2014-01-06 | 2014-01-06 01:00 | 1 | 0.21212 | 63.4242 | 260 | 330 | 299 | Boiler water condition (not feedwater water quality) | F170High Silica
MC2 | D1 | 8 | 1850 |  |  | 2014-01-06 01:00 | 2014-01-06 09:28 | 8.4667 | 1.2828 | 383.5657 | 280 | 330 | 299 | Boiler water condition (not feedwater water quality) | F170High Silica
MC2 | D1 | 9 | 1850 |  |  | 2014-01-06 09:28 | 2014-01-06 19:00 | 9.5333 | 0.28889 | 86.3778 | 320 | 330 | 299 | Boiler water condition (not feedwater water quality) | F170High Silica
MC2 | D1 | 10 | 1850 |  |  | 2014-01-06 19:00 | 2014-01-06 22:36 | 3.6 | 0.32727 | 97.8545 | 300 | 330 | 299 | Boiler water condition (not feedwater water quality) | F170High Silica
MC3 | D1 | 2 | 360 | 2014-01-05 23:16 |  | 2014-01-06 | 2014-01-06 02:00 | 2 | 0.43972 | 173.2482 | 330 | 423 | 394 | Burners | F7803A Mill - Burners High Temperature
MC4 | D1 | 3 | 380 |  |  | 2014-01-06 05:40 | 2014-01-06 05:48 | 0.13333 | 0.068571 | 33.3257 | 255 | 525 | 486 | Light off (igniter) systems (including fuel supply) | F4004C Mill - Gas Igniter Issue
MC4 | D1 | 4 | 380 |  |  | 2014-01-06 06:40 | 2014-01-06 08:55 | 2.25 | 0.79286 | 385.3286 | 340 | 525 | 486 | Light off (igniter) systems (including fuel supply) | F4004B & 4C Mills - Gas Igniter Issues
MC4 | D1 | 5 | 380 |  |  | 2014-01-06 08:55 | 2014-01-06 12:30 | 3.5833 | 0.71667 | 348.3 | 420 | 525 | 486 | Light off (igniter) systems (including fuel supply) | F7204C Mill - Gas Vent Valve Stuck Open
TC5 | U1 | 4 | 5246 |  |  | 2014-01-06 12:15 | 2014-01-06 14:08 | 1.8833 | 1.8833 | 331.4667 | 0 | 180 | 176 | Gas Turbine Control System - hardware problems (including card failure) | F520Unit tripped on high exhaust temperature differential from a failed control system
TC6 | U1 | 4 | 5079 |  |  | 2014-01-06 02:17 | 2014-01-06 03:50 | 1.55 | 1.55 | 272.8 | 0 | 180 | 176 | Other combustor problems | F460Unit tripped due to a lean blowout.
TC6 | U1 | 6 | 5041 |  |  | 2014-01-06 13:52 | 2014-01-06 14:46 | 0.9 | 0.9 | 158.4 | 0 | 180 | 176 | Fuel piping and valves | F480Unit tripped due to a fuel gas valve (worker valve) not controlling properly.
TC8 | SF | 5 | 5130 | 2014-01-05 12:00 |  | 2014-01-06 | 2014-01-06 15:58 | 15.9667 | 15.9667 | 2810.1333 | 0 | 180 | 176 | Starting system (including motor) | F330Startup failure due to issue with 89SS.
TC9 | U1 | 7 | 5130 |  |  | 2014-01-06 02:27 | 2014-01-06 02:57 | 0.5 | 0.5 | 88 | 0 | 180 | 176 | Starting system (including motor) | F340Forced outage due to issue with 89SS.
1/6/2014 MWH Lost
6029.535
2014-01-07
BR9 | U1 | 3 | 5140 |  |  | 2014-01-07 09:33 | 2014-01-07 10:36 | 1.05 | 1.05 | 144.9 | 0 | 139 | 138 | Battery and charger system | F410Both battery chargers indicated failure. Failure was caused by low output current
CR11 | U1 | 2 | 5130 | 2014-01-06 20:13 |  | 2014-01-07 | 2014-01-07 09:05 | 9.0833 | 9.0833 | 127.1667 | 0 | 14 | 14 | Starting system (including motor) | F030Broken terminal on battery cable causing Cane Run 11 starting diesel to be unable
GH3 | U1 | 1 | 1455 |  | 2014-01-08 06:15 | 2014-01-07 21:20 | 2014-01-08 | 2.6667 | 2.6667 | 1285.3333 | 0 | 527 | 482 | Induced draft fans | F850Outage #13-2 ID fan tripped on high vibration on OB fan bearing. This caused
GH4 | D1 | 2 | 250 |  |  | 2014-01-07 03:55 | 2014-01-07 04:36 | 0.68333 | 0.17147 | 84.1933 | 400 | 534 | 491 | Pulverizer feeders | Load Reduction #14-4 Feeder tripped.
GR3 | D1 | 1 | 250 |  |  | 2014-01-07 13:15 | 2014-01-07 14:15 | 1 | 0.26667 | 18.9333 | 55 | 75 | 71 | Pulverizer feeders | FW004-4 Feeder plugged with coal and ice.
HA1 | SF | 2 | 5160 | 2014-01-06 21:22 | 2014-01-14 13:14 | 2014-01-07 | 2014-01-08 | 24 | 24 | 336 | 0 | 14 | 14 | Cooling and seal air system | F540Busted glycol line on radiator. Failed to ignite on start up.
MC1 | D1 | 1 | 8280 |  |  | 2014-01-07 07:15 | 2014-01-07 08:58 | 1.7167 | 0.36414 | 110.3348 | 260 | 330 | 303 | Reagent feed piping | F540FGD Reactant Feed Line - Leak
MC1 | D1 | 2 | 250 |  |  | 2014-01-07 16:50 | 2014-01-07 18:06 | 1.2667 | 0.26869 | 81.4121 | 260 | 330 | 303 | Pulverizer feeders | FW001D Coal Feeder - Plugged, Frozen/Wet Coal
MC2 | D1 | 11 | 250 |  |  | 2014-01-07 05:45 | 2014-01-07 07:15 | 1.5 | 0.40909 | 122.3182 | 240 | 330 | 299 | Pulverizer feeders | FW002A Coal Feeder - Plugged, Frozen/Wet Coal
MC2 | D1 | 12 | 1850 |  | 2014-01-08 09:50 | 2014-01-07 12:15 | 2014-01-08 | 11.75 | 1.7803 | 532.3106 | 280 | 330 | 299 | Boiler water condition (not feedwater water quality) | F170High Silica
TC1 | D1 | 6 | 280 |  |  | 2014-01-07 17:25 | 2014-01-07 21:08 | 3.7167 | 0.38073 | 145.8202 | 368 | 410 | 383 | Pulverizer fires | F780Derate required due to A & B coal mill fires.
TC5 | U1 | 6 | 5246 |  |  | 2014-01-07 01:25 | 2014-01-07 05:50 | 4.4167 | 4.4167 | 777.3333 | 0 | 180 | 176 | Gas Turbine Control System - hardware problems (including card failure) | F520Forced outage due to compressor inlet thermocouple disagreement from a failed cont
CR4 | D1 | 1 | 8280 |  |  | 2014-01-07 21:20 | 2014-01-07 23:43 | 2.3833 | 0.7377 | 114.3433 | 116 | 168 | 155 | Wet Scrubber - Reagent Feed Piping | Reactive feed line from supply pump frozen.
TC6 | U1 | 8 | 5016 |  |  | 2014-01-07 01:25 | 2014-01-07 05:49 | 4.4 | 4.4 | 774.4 | 0 | 180 | 176 | High pressure compressor bleed valves | F480Forced outage due to compressor bleed valve frozen closed.
1/7/2014 MWH Lost
4654.7992
2015-02-19
BR10 | D1 | 1 | 5097 | 2015-01-01 | 2015-04-01 | 2015-02-19 | 2015-02-20 | 24 | 3.2806 | 452.7194 | 120 | 139 | 138 | Other low pressure problems | F600Blade desing issues has unit limited to 120MWs.
BR11 | D1 | 1 | 5097 | 2015-01-01 | 2015-04-01 | 2015-02-19 | 2015-02-20 | 24 | 1.6744 | 214.3256 | 120 | 129 | 128 | Other low pressure problems | F600Blade design issues has unit limited to 120MWs.
BR5 | D1 | 1 | 5097 | 2015-01-01 | 2015-04-01 | 2015-02-19 | 2015-02-20 | 24 | 2.0153 | 261.9847 | 120 | 131 | 130 | Other low pressure problems | F600Blade design issues has unit limited to 120MWs.
BR8 | D1 | 1 | 5097 | 2015-01-01 | 2015-04-01 | 2015-02-19 | 2015-02-20 | 24 | 1.6744 | 214.3256 | 120 | 129 | 128 | Other low pressure problems | F600Blade design issues has unit limited to 120MWs.
BR9 | D1 | 1 | 5097 | 2015-01-01 | 2015-04-01 | 2015-02-19 | 2015-02-20 | 24 | 3.2806 | 452.7194 | 120 | 139 | 138 | Other low pressure problems | F600Blade desing issues has unit limited to 120MWs.
CR11 | U1 | 8 | 5150 | 2015-02-16 04:14 | 2015-03-01 11:28 | 2015-02-19 | 2015-02-20 | 24 | 24 | 336 | 0 | 14 | 14 | Turning gear and motor | F700Turning gear motor failure.
PR11 | U1 | 8 | 9290 | 2015-02-14 20:00 | 2015-02-21 20:10 | 2015-02-19 | 2015-02-20 | 24 | 24 | 312 | 0 | 13 | 13 | Other fuel quality problems (OMC) | F660Gas pressure problems.
PR12 | U1 | 8 | 9290 | 2015-02-14 20:00 | 2015-02-21 20:10 | 2015-02-19 | 2015-02-20 | 24 | 24 | 672 | 0 | 28 | 28 | Other fuel quality problems (OMC) | F660Gas pressure problems.
PR13 | U1 | 10 | 9290 | 2015-02-14 20:00 | 2015-02-21 | 2015-02-19 | 2015-02-20 | 24 | 24 | 4200 | 0 | 176 | 175 | Other fuel quality problems (OMC) | F660Gas pressure problems.
TC1 | D1 | 28 | 1493 | 2015-02-11 07:11 | 2015-03-03 17:06 | 2015-02-19 | 2015-02-20 | 24 | 0.73171 | 280.2439 | 397.5 | 410 | 383 | Air heater fouling (regenerative) | FF00Differential pressure across the AH increased and required a derate in order to ke
TC1 | D1 | 29 | 310 |  |  | 2015-02-19 13:35 | 2015-02-19 14:20 | 0.75 | 0.23552 | 90.2035 | 281.25 | 410 | 383 | Pulverizer mills | FR00Unit derated due to 1D coal mill fire. D mill taken offline and out of service fo
TC2 | D1 | 6 | 4269 | 2015-01-12 19:00 | 2015-03-04 16:00 | 2015-02-19 | 2015-02-20 | 24 | 0.60297 | 343.6903 | 591.75 | 607 | 570 | Other turbine valves (including LP steam admission valves) | F540Unit was derated 20MW due to HP turbine bypass valve leak through. This required
TC5 | U1 | 14 | 5079 |  |  | 2015-02-19 01:17 | 2015-02-19 02:42 | 1.4167 | 1.4167 | 249.3333 | 0 | 180 | 176 | Other combustor problems | F820Unit tripped on lean blow out due to NOx adjustment set too low to maintain flame
TC5 | SF | 15 | 5130 |  |  | 2015-02-19 02:42 | 2015-02-19 07:57 | 5.25 | 5.25 | 924 | 0 | 180 | 176 | Starting system (including motor) | F340Loose wire problem on 89SS switch caused a not ready to start condition.
TC5 | U1 | 16 | 5079 |  |  | 2015-02-19 09:05 | 2015-02-19 12:37 | 3.5333 | 3.5333 | 621.8667 | 0 | 180 | 176 | Other combustor problems | F820Unit tripped on lean blow out, extreme cold conditions caused autotune to lean com
TC5 | U1 | 17 | 5048 |  |  | 2015-02-19 22:06 | 2015-02-19 23:31 | 1.4167 | 1.4167 | 249.3333 | 0 | 180 | 176 | Gas fuel system including controls and instrumentation | F820The autotune program was turned off, and this causes the machine to be susceptible
TC5 | SF | 18 | 5130 |  |  | 2015-02-19 23:31 | 2015-02-19 23:49 | 0.3 | 0.3 | 52.8 | 0 | 180 | 176 | Starting system (including motor) | F340This was not an excitation issue. The LCI was not reset after the previous start a
TC6 | U1 | 22 | 5079 |  |  | 2015-02-19 01:45 | 2015-02-19 03:00 | 1.25 | 1.25 | 220 | 0 | 180 | 176 | Other combustor problems | F820Autotune NOx setting too low to sustain flame in extreme low temperature. Lean blo
TC6 | D1 | 28 | 5109 |  |  | 2015-02-19 03:00 | 2015-02-19 06:34 | 3.5667 | 0.43593 | 76.723 | 158 | 180 | 176 | Other exhaust problems (including high exhaust system temperature not attributable to a specific problem) | F750High exhaust thermocouple spreads and high dynamics cause a unit run back on load,
TC6 | U1 | 23 | 5079 |  |  | 2015-02-19 06:34 | 2015-02-19 08:15 | 1.6833 | 1.6833 | 296.2667 | 0 | 180 | 176 | Other combustor problems | F820Lean blow out event. Thermocouple spread is the first sign of a combustion can blo
TC6 | D1 | 29 | 5079 |  |  | 2015-02-19 18:11 | 2015-02-19 22:45 | 4.5667 | 1.0148 | 178.6074 | 140 | 180 | 176 | Other combustor problems | FE00Load limit due to NOx readings going above our 12 PPM limit.
TC6 | U1 | 24 | 5079 |  | 2015-02-20 00:33 | 2015-02-19 22:45 | 2015-02-20 | 1.25 | 1.25 | 220 | 0 | 180 | 176 | Other combustor problems | F820Autotune NOx setting too low to sustain flame in extreme cold temperatures. Lean b
CR5 | D1 | 12 | 310 | 2015-02-18 17:40 |  | 2015-02-19 | 2015-02-19 07:56 | 7.9333 | 2.4545 | 412.358 | 125 | 181 | 168 | Pulverizer mills | 5B coal mill - #2 mill roller replacement.
CR6 | D1 | 26 | 3979 |  |  | 2015-02-19 03:43 | 2015-02-19 04:27 | 0.73333 | 0.42427 | 101.8238 | 110 | 261 | 240 | Other DCS problems | DCS screens - loss of indication to FGD equipment along with voltage indication.
Z1 | D1 | 5 | 5108 | 2015-02-18 15:52 | 2015-02-20 11:57 | 2015-02-19 | 2015-02-20 | 24 | 6 | 96 | 12 | 16 | 16 | High engine exhaust temperature | F750Exhaust over temperature issues. Unit derated 4 MW.
2/19/2015 MWH Lost
11529.3246
[9 empty] | Excluding prior events | 3789.3156
2015-02-20 | [9 empty] | 7740.0089
BR10 | D1 | 1 | 5097 | 2015-01-01 | 2015-04-01 | 2015-02-20 | 2015-02-21 | 24 | 3.2806 | 452.7194 | 120 | 139 | 138 | Other low pressure problems | F600Blade desing issues has unit limited to 120MWs.
BR11 | D1 | 1 | 5097 | 2015-01-01 | 2015-04-01 | 2015-02-20 | 2015-02-21 | 24 | 1.6744 | 214.3256 | 120 | 129 | 128 | Other low pressure problems | F600Blade design issues has unit limited to 120MWs.
BR3 | U1 | 12 | 90 |  |  | 2015-02-20 13:34 | 2015-02-20 15:55 | 2.35 | 2.35 | 972.9 | 0 | 457 | 414 | Bunker fires | FR00Unit 3 coal bunker fires in 3-4 and partially in 3-5 bunker
BR3 | D1 | 13 | 9270 |  | 2015-02-21 03:20 | 2015-02-20 22:16 | 2015-02-21 | 1.7333 | 0.40584 | 168.0158 | 350 | 457 | 414 | Wet coal (OMC) | FW00Wet Coal
BR5 | D1 | 1 | 5097 | 2015-01-01 | 2015-04-01 | 2015-02-20 | 2015-02-21 | 24 | 2.0153 | 261.9847 | 120 | 131 | 130 | Other low pressure problems | F600Blade design issues has unit limited to 120MWs.
BR5 | D1 | 20 | 5009 |  |  | 2015-02-20 08:10 | 2015-02-20 11:14 | 3.0667 | 1.8962 | 246.5038 | 50 | 131 | 130 | Other inlet air problems | F480Screens on inlet of air filter house started to freeze causing implosion doors to
BR8 | D1 | 1 | 5097 | 2015-01-01 | 2015-04-01 | 2015-02-20 | 2015-02-21 | 24 | 1.6744 | 214.3256 | 120 | 129 | 128 | Other low pressure problems | F600Blade design issues has unit limited to 120MWs.
BR8 | U1 | 14 | 3611 |  | 2015-02-22 10:52 | 2015-02-20 13:50 | 2015-02-21 | 10.1667 | 10.1667 | 1301.3333 | 0 | 129 | 128 | Switchyard circuit breakers - external (OMC) | F660Hydraulic pump in substation breaker quit working.
BR9 | D1 | 1 | 5097 | 2015-01-01 | 2015-04-01 | 2015-02-20 | 2015-02-21 | 24 | 3.2806 | 452.7194 | 120 | 139 | 138 | Other low pressure problems | F600Blade desing issues has unit limited to 120MWs.
CR11 | U1 | 8 | 5150 |  | 2015-03-01 11:28 | 2015-02-20 | 2015-02-21 | 24 | 24 | 336 | 0 | 14 | 14 | Turning gear and motor | F700Turning gear motor failure.
GR3 | PD | 16 | 346 |  | 2015-02-21 01:02 | 2015-02-20 23:00 | 2015-02-21 | 1 | 0.13333 | 9.4667 | 65 | 75 | 71 | Pulverizer pyrite removal system | F5304-3 Pulv out of service to inspect pyrite flop gate. Suspect that flop gate is st
PR11 | U1 | 8 | 9290 | 2015-02-14 20:00 | 2015-02-21 20:10 | 2015-02-20 | 2015-02-21 | 24 | 24 | 312 | 0 | 13 | 13 | Other fuel quality problems (OMC) | F660Gas pressure problems.
PR12 | U1 | 8 | 9290 | 2015-02-14 20:00 | 2015-02-21 20:10 | 2015-02-20 | 2015-02-21 | 24 | 24 | 672 | 0 | 28 | 28 | Other fuel quality problems (OMC) | F660Gas pressure problems.
PR13 | U1 | 10 | 9290 | 2015-02-14 20:00 | 2015-02-21 | 2015-02-20 | 2015-02-21 | 24 | 24 | 4200 | 0 | 176 | 175 | Other fuel quality problems (OMC) | F660Gas pressure problems.
TC1 | D1 | 28 | 1493 | 2015-02-11 07:11 | 2015-03-03 17:06 | 2015-02-20 | 2015-02-21 | 24 | 0.73171 | 280.2439 | 397.5 | 410 | 383 | Air heater fouling (regenerative) | FF00Differential pressure across the AH increased and required a derate in order to ke
TC2 | D1 | 6 | 4269 | 2015-01-12 19:00 | 2015-03-04 16:00 | 2015-02-20 | 2015-02-21 | 24 | 0.60297 | 343.6903 | 591.75 | 607 | 570 | Other turbine valves (including LP steam admission valves) | F540Unit was derated 20MW due to HP turbine bypass valve leak through. This required
TC5 | U1 | 19 | 5079 |  |  | 2015-02-20 14:09 | 2015-02-20 14:41 | 0.53333 | 0.53333 | 93.8667 | 0 | 180 | 176 | Other combustor problems | F820This trip is similar to event #17, fuel gas heater not working causing low inlet f
TC6 | U1 | 24 | 5079 | 2015-02-19 22:45 |  | 2015-02-20 | 2015-02-20 00:33 | 0.55 | 0.55 | 96.8 | 0 | 180 | 176 | Other combustor problems | F820Autotune NOx setting too low to sustain flame in extreme cold temperatures. Lean b
TC6 | D1 | 30 | 5079 |  |  | 2015-02-20 00:33 | 2015-02-20 19:44 | 19.1833 | 2.1315 | 375.1407 | 160 | 180 | 176 | Other combustor problems | FE00Load limit due to NOx readings going above our 12 PPM limit.
CR6 | D1 | 27 | 3979 |  |  | 2015-02-20 02:07 | 2015-02-20 03:55 | 1.8 | 0.31724 | 76.1379 | 215 | 261 | 240 | Other DCS problems | DCS screens - loss of indication to FGD equipment along with voltage indication.
Z1 | D1 | 5 | 5108 | 2015-02-18 15:52 |  | 2015-02-20 | 2015-02-20 11:57 | 11.95 | 2.9875 | 47.8 | 12 | 16 | 16 | High engine exhaust temperature | F750Exhaust over temperature issues. Unit derated 4 MW.
2/20/2015 MWH Lost
11127.9738
[9 empty] | Excluding prior events | 3387.9649
2022-12-23 | [9 empty] | 7740.0089
BR10 | U1 | 59 | 5109 | 2022-12-03 18:26 | 2023-01-01 | 2022-12-23 | 2022-12-24 | 24 | 24 | 3312 | 0 | 139 | 138 | Other exhaust problems (including high exhaust system temperature not attributable to a specific problem) | F060Exhaust diffuser sections have separated. Bolts need to be replaced and exhaust d
BR11 | U1 | 58 | 5041 |  |  | 2022-12-23 01:30 | 2022-12-23 03:50 | 2.3333 | 2.3333 | 298.6667 | 0 | 129 | 128 | Fuel piping and valves | F480Frozen fuel valves due to valves heaters to the 11N2 units kept going out.
BR11 | U1 | 60 | 5073 |  |  | 2022-12-23 15:39 | 2022-12-23 17:03 | 1.4 | 1.4 | 179.2 | 0 | 129 | 128 | Flame scanners | F820Flame trip
BR3 | D1 | 36 | 310 |  |  | 2022-12-23 07:17 | 2022-12-23 08:30 | 1.2167 | 0.14824 | 61.6694 | 400 | 455.5 | 416 | Pulverizer mills | FS00Mills on high tonage.
BR3 | D1 | 40 | 8650 |  |  | 2022-12-23 08:30 | 2022-12-23 13:40 | 5.1667 | 0.74296 | 309.0699 | 390 | 455.5 | 416 | "Baghouse systems, general" | FS00Baghouse plugging up due to boiler slagging.
BR3 | D1 | 37 | 9305 |  | 2022-12-25 01:50 | 2022-12-23 13:40 | 2022-12-24 | 10.3333 | 1.7128 | 712.5123 | 380 | 455.5 | 416 | Ash disposal problem | FS00Baghouse issues
BR5 | U1 | 55 | 5041 |  |  | 2022-12-23 01:28 | 2022-12-23 17:22 | 15.9 | 15.9 | 2067 | 0 | 131 | 130 | Fuel piping and valves | F480Fuel valves froze after valve heaters to 11N2 units were blown out.
BR5 | D1 | 57 | 5113 |  |  | 2022-12-23 18:00 | 2022-12-23 21:00 | 3 | 0.70992 | 92.2901 | 100 | 131 | 130 | Lube oil valves/piping | F570Pressure switch on U5 lube oil pump failed.
BR8 | U1 | 74 | 5041 |  |  | 2022-12-23 01:30 | 2022-12-23 03:36 | 2.1 | 2.1 | 268.8 | 0 | 129 | 128 | Fuel piping and valves | F480Fuel valves froze because valves heaters to the 11N2 units kept going out.
BR8 | U1 | 75 | 5111 |  |  | 2022-12-23 03:36 | 2022-12-23 06:26 | 2.8333 | 2.8333 | 362.6667 | 0 | 129 | 128 | Lube oil pumps | F570Malfunctioning lube oil pump
BR8 | D1 | 78 | 3974 |  |  | 2022-12-23 10:51 | 2022-12-23 15:30 | 4.65 | 1.0453 | 133.8047 | 100 | 129 | 128 | DCS - logic problems | F610Generation limited due to high input temp alarm that had been removed but not remo
BR9 | U1 | 58 | 5041 |  |  | 2022-12-23 01:30 | 2022-12-23 03:50 | 2.3333 | 2.3333 | 322 | 0 | 139 | 138 | Fuel piping and valves | F480Frozen fuel valves due to valves heaters to the 11N2 units kept going out.
CR7 | D1 | 59 | 9130 |  | 2022-12-24 15:30 | 2022-12-23 13:47 | 2022-12-24 | 10.2167 | 2.1138 | 1443.7207 | 552 | 696 | 683 | "Lack of fuel (water from rivers or lakes, coal mines, gas lines, etc) where the operator is not in control of contracts, supply lines, or delivery of fuels" | FX00Block derate due to low fuel gas pipeline pressure
HA1 | U1 | 5 | 3700 |  | 2022-12-24 14:57 | 2022-12-23 10:33 | 2022-12-24 | 13.45 | 13.45 | 188.3 | 0 | 14 | 14 | Power Station switchyard (non generating unit equipment) | F820Substation breaker will not remain closed.
HA2 | U1 | 7 | 3700 |  | 2022-12-24 14:57 | 2022-12-23 10:33 | 2022-12-24 | 13.45 | 13.45 | 188.3 | 0 | 14 | 14 | Power Station switchyard (non generating unit equipment) | F820Substation breaker will not remain closed.
MC4 | D1 | 34 | 95 |  |  | 2022-12-23 16:34 | 2022-12-23 18:44 | 2.1667 | 0.49937 | 242.6914 | 404 | 525 | 486 | Bunker flow problems | F480Coal Silo Tripper Issues - Cold Weather
PR13 | U1 | 89 | 3822 |  |  | 2022-12-23 06:36 | 2022-12-23 07:13 | 0.61667 | 0.61667 | 107.9167 | 0 | 176 | 175 | Closed cooling water valves | F820Gen cold gas temp got too low.
TC1 | U1 | 25 | 897 | 2022-12-22 15:35 | 2022-12-30 02:19 | 2022-12-23 | 2022-12-24 | 24 | 24 | 8874 | 0 | 397.5 | 369.75 | Bottom ash rotary (drag chain type) conveyor and motor | F340The unit was placed on a forced outage due to issues with the primary submerged ch
TC10 | D1 | 301 | 9130 |  | 2022-12-25 16:00 | 2022-12-23 13:48 | 2022-12-24 | 10.2 | 5.2133 | 933.1867 | 88 | 180 | 179 | "Lack of fuel (water from rivers or lakes, coal mines, gas lines, etc) where the operator is not in control of contracts, supply lines, or delivery of fuels" | FX00Low fuel gas supply pressure from transport company to the plant.
TC2 | D1 | 49 | 3344 |  |  | 2022-12-23 03:10 | 2022-12-23 15:48 | 12.6333 | 0.61398 | 349.9662 | 577.5 | 607 | 570 | Deaerator (including level control) | F780In order to slow demand to the water coil air heaters from the deaerator, the unit
TC2 | D1 | 50 | 1760 |  |  | 2022-12-23 15:48 | 2022-12-23 17:41 | 1.8833 | 0.91995 | 524.3703 | 310.5 | 607 | 570 | Feedwater instrumentation (not local controls) | F480The unit was placed on derate due to frozen transmitter that caused the loss of th
TC2 | D1 | 51 | 1760 |  |  | 2022-12-23 17:41 | 2022-12-23 22:06 | 4.4167 | 1.1697 | 666.702 | 446.25 | 607 | 570 | Feedwater instrumentation (not local controls) | F480The unit was placed on a variable derate due to various cold weather issues encoun
TC2 | D1 | 52 | 3344 |  | 2022-12-24 19:28 | 2022-12-23 22:06 | 2022-12-24 | 1.9 | 0.092339 | 52.6334 | 577.5 | 607 | 570 | Deaerator (including level control) | F780In order to slow demand to the water coil air heaters from the deaerator, the unit
TC5 | U1 | 116 | 5048 |  |  | 2022-12-23 13:08 | 2022-12-23 13:48 | 0.66667 | 0.66667 | 119.3333 | 0 | 180 | 179 | Gas fuel system including controls and instrumentation | F820Lean Blow Out (LBO) trip.
TC5 | U1 | 117 | 9130 |  | 2022-12-25 11:47 | 2022-12-23 13:48 | 2022-12-24 | 10.2 | 10.2 | 1825.8 | 0 | 180 | 179 | "Lack of fuel (water from rivers or lakes, coal mines, gas lines, etc) where the operator is not in control of contracts, supply lines, or delivery of fuels" | FX00Low fuel gas supply pressure from transport company to the plant.
TC6 | D1 | 103 | 9130 |  | 2022-12-25 16:00 | 2022-12-23 13:48 | 2022-12-24 | 10.2 | 4.59 | 821.61 | 99 | 180 | 179 | "Lack of fuel (water from rivers or lakes, coal mines, gas lines, etc) where the operator is not in control of contracts, supply lines, or delivery of fuels" | FX00Low fuel gas supply pressure from transport company to the plant.
TC7 | D1 | 137 | 9130 |  | 2022-12-25 16:00 | 2022-12-23 13:48 | 2022-12-24 | 10.2 | 5.3267 | 953.4733 | 86 | 180 | 179 | "Lack of fuel (water from rivers or lakes, coal mines, gas lines, etc) where the operator is not in control of contracts, supply lines, or delivery of fuels" | FX00Low fuel gas supply pressure from transport company to the plant.
TC8 | D1 | 201 | 9130 |  | 2022-12-25 16:00 | 2022-12-23 13:48 | 2022-12-24 | 10.2 | 4.9867 | 892.6133 | 92 | 180 | 179 | "Lack of fuel (water from rivers or lakes, coal mines, gas lines, etc) where the operator is not in control of contracts, supply lines, or delivery of fuels" | FX00Low fuel gas supply pressure from transport company to the plant.
TC9 | D1 | 142 | 9130 |  | 2022-12-25 08:39 | 2022-12-23 13:48 | 2022-12-24 | 10.2 | 4.845 | 770.355 | 84 | 160 | 159 | "Lack of fuel (water from rivers or lakes, coal mines, gas lines, etc) where the operator is not in control of contracts, supply lines, or delivery of fuels" | FX00Low fuel gas supply pressure from transport company to the plant.
12/23/2022 MWH Lost
[9 empty] | All Events | 27074.652
[9 empty] | Including Gas press, excluding prior events | 14888.652
[9 empty] | Excluding Gas press and prior events | 7128.5596
[9 empty] | Excluding gas press only | 20247.7463

## MWh Lost Chart - Updated
| Total MWh Lost | Days | Annual Average | Cold Weather Event Day | Date
2014-01-01 | 4648163.9672 | 365 | 12734.6958
2015-01-01 | 5029592.8767 | 365 | 13779.7065
2016-01-01 | 4732794.8205 | 366 | 12931.1334
2017-01-01 | 3992438.5012 | 365 | 10938.1877
2018-01-01 | 3408979.1399 | 365 | 9339.6689
2019-01-01 | 2859966.4164 | 365 | 7835.5244
2020-01-01 | 2918351.2991 | 366 | 7973.6374
2021-01-01 | 2652909 | 365 | 7268.2438
2022-01-01 | 2872773 | 365 | 7870.611
2014-01-01 |  |  | 12734.6958 | 6029.53 | 1/6/2014
2014-01-01 |  |  | 12734.6958 | 4654.8 | 2014-01-07
2015-01-01 |  |  | 13779.7065 | 3789.3156 | 2/19/2015
2015-01-01 |  |  | 13779.7065 | 3387.9649 | 2/20/2015
2022-01-01 |  |  | 7870.611 | 14888.652 | 12/23/2022
2022-01-01 |  |  | 7870.611 | 7128.5596 | 2022-12-23 | w/o gas pressure