## SC Q1.34
Brown - BR10
Unit | Event | Type | Start |  |  |  |  | End |  | GAC | NAC | Duration | Equiv Hrs | Equiv MWH | Cont | Work Start | Work End |  | Hours |  |  | Gross Capacity Impact (MW)
BR10 | 19 | U1 | 2014-04-02 12:45 |  |  |  |  | 2014-04-02 14:28 |  | 0 | 0 | 1.717 | 1.7167 | 175.1 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 5039 |  |  | - |  | Other compressor problems | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410PK2 Transmitter Failure.
BR10 | 34 | SF | 2014-09-25 13:56 |  |  |  |  | 2014-09-25 14:25 |  | 0 | 0 | 0.483 | 0.4833 | 49.3 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410SFC failure on U11 caused forced outage on U10.
BR10 | 38 | SF | 2014-10-30 06:11 |  |  |  |  | 2014-10-30 06:50 |  | 0 | 0 | 0.65 | 0.65 | 89.7 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 5048 |  |  | - |  | Gas fuel system including controls and instrumentation | [8 empty] | AMP CODE: |  | 46
|  | DESCRIPTION : |  | F460Gas valve failed to go open. Stroked gas valve offline. Successful test after.
BR10 | 6 | SF | 2015-02-05 06:01 |  |  |  |  | 2015-02-05 06:27 |  | 0 | 0 | 0.433 | 0.4333 | 59.8 | 1 |  |  |  | 0 |  |  | 139
|  | CAUSE CODE : |  | 5050 |  |  | - |  | Ignition system | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Unit failed to light off.
BR10 | 8 | U1 | 2015-02-06 10:00 |  |  |  |  | 2015-02-07 17:01 |  | 0 | 0 | 31.017 | 31.0167 | 4280.3 | 1 |  |  |  | 0 |  |  | 139
|  | CAUSE CODE : |  | 5050 |  |  | - |  | Ignition system | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Unit would not light off.
BR10 | 13 | U1 | 2015-02-17 08:32 |  |  |  |  | 2015-02-17 12:30 |  | 0 | 0 | 3.967 | 3.9667 | 547.4 | 1 |  |  |  | 0 |  |  | 139
|  | CAUSE CODE : |  | 5065 |  |  | - |  | NOx water injection system including pump | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F060Outage to repair busted NOx water line.
BR10 | 16 | SF | 2015-02-23 18:03 |  |  |  |  | 2015-02-23 20:32 |  | 0 | 0 | 2.483 | 2.4833 | 342.7 | 1 |  |  |  | 0 |  |  | 139
|  | CAUSE CODE : |  | 3619 |  |  | - |  | Other switchyard equipment - external (OMC) | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Failure of MOS limit switches kept unit's GCB from being able to close.
BR10 | 27 | U1 | 2015-05-08 13:43 |  |  |  |  | 2015-05-08 15:02 |  | 0 | 0 | 1.317 | 1.3167 | 134.3 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 5049 |  |  | - |  | Other fuel system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F410PLS due to fuel extractor air seperator.
BR10 | 32 | U1 | 2015-05-12 12:14 |  |  |  |  | 2015-05-13 10:28 |  | 0 | 0 | 22.233 | 22.2333 | 2267.8 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 5601 |  |  | - |  | Load shaft and bearings | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F020Outage to adjust tilt of #1 bearing in turbine exhaust.
BR10 | 33 | U1 | 2015-05-13 11:24 |  |  |  |  | 2015-05-14 09:07 |  | 0 | 0 | 21.717 | 21.7167 | 2215.1 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 5601 |  |  | - |  | Load shaft and bearings | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F020Outage to adjust bearing tilt on #1 bearing exhaust end
BR10 | 34 | U1 | 2015-05-14 10:05 |  |  |  |  | 2015-05-15 08:09 |  | 0 | 0 | 22.067 | 22.0667 | 2250.8 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 5601 |  |  | - |  | Load shaft and bearings | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F020Outage to adjust bearing tilt on #1 exhaust end bearing.
BR10 | 35 | U1 | 2015-05-15 08:15 |  |  |  |  | 2015-05-15 11:32 |  | 0 | 0 | 3.283 | 3.2833 | 334.9 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 5601 |  |  | - |  | Load shaft and bearings | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F020Outage to adjust tilt on exhaust end bearing.
BR10 | 36 | U1 | 2015-05-15 12:41 |  |  |  |  | 2015-05-16 08:40 |  | 0 | 0 | 19.983 | 19.9833 | 2038.3 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 5601 |  |  | - |  | Load shaft and bearings | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F020Outage to adjust bearing tilt on exhaust end bearing.
BR10 | 37 | U1 | 2015-05-16 10:44 |  |  |  |  | 2015-05-17 08:49 |  | 0 | 0 | 22.083 | 22.0833 | 2252.5 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 5601 |  |  | - |  | Load shaft and bearings | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F020Outage to adjust bearing tilt on exhaust end bearing.
BR10 | 47 | SF | 2015-05-31 16:10 |  |  |  |  | 2015-05-31 16:21 |  | 0 | 0 | 0.183 | 0.1833 | 18.7 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 5530 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410U11's 3 Position ISO switch did not travel due to problem on mechanical hold card
BR10 | 68 | U1 | 2015-08-04 10:00 |  |  |  |  | 2015-08-04 10:20 |  | 0 | 0 | 0.333 | 0.3333 | 40.333 | 1 |  |  |  | 0 |  |  | 122
|  | CAUSE CODE : |  | 7820 |  |  | - |  | Bearings | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F780High temperature exhaust bearing CT001.
BR10 | 104 | SF | 2015-10-21 09:02 |  |  |  |  | 2015-10-21 12:35 |  | 0 | 0 | 3.55 | 3.55 | 489.9 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 3611 |  |  | - |  | Switchyard circuit breakers - external (OMC) | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Failure of electro-mechanical relay in substation house for MOS.
BR10 | 128 | SF | 2015-12-09 04:51 |  |  |  |  | 2015-12-09 07:33 |  | 0 | 0 | 2.7 | 2.7 | 372.6 | 1 |  |  |  | 0 |  |  | 139
|  | CAUSE CODE : |  | 5041 |  |  | - |  | Fuel piping and valves | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Unit would not sync to grid. Possible issue with gas control valve.
BR10 | 3 | SF | 2016-01-10 16:24 |  |  |  |  | 2016-01-10 23:01 |  | 0 | 0 | 6.617 | 6.6167 | 913.1 | 1 |  |  |  | 0 |  |  | 139
|  | CAUSE CODE : |  | 3619 |  |  | - |  | Other switchyard equipment - external (OMC) | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Limit switched not made up on motor operated switch in substation. This would not
BR10 | 11 | SF | 2016-01-17 15:30 |  |  |  |  | 2016-01-17 17:22 |  | 0 | 0 | 1.867 | 1.8667 | 257.6 | 1 |  |  |  | 0 |  |  | 139
|  | CAUSE CODE : |  | 3611 |  |  | - |  | Switchyard circuit breakers - external (OMC) | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Limit switchs not making up on motor operated switch in substation caused unit not
BR10 | 92 | U1 | 2016-09-07 22:00 |  |  |  |  | 2016-09-07 22:43 |  | 0 | 0 | 0.717 | 0.7167 | 84.567 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 3971 |  |  | - |  | DCS - data highway | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410DCS LAN went down causing 11N2 system to lose communication.
BR10 | 112 | U1 | 2016-12-02 06:49 |  |  |  |  | 2016-12-02 07:15 |  | 0 | 0 | 0.433 | 0.4333 | 59.8 | 1 |  |  |  | 0 |  |  | 139
|  | CAUSE CODE : |  | 7820 |  |  | - |  | Bearings | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F020Unit tripped due to exhaust end bearing TC going high on start up.
BR10 | 22 | U1 | 2017-04-17 07:29 |  |  |  |  | 2017-04-17 07:30 |  | 0 | 0 | 0.017 | 0.0167 | 1.967 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 5017 |  |  | - |  | Low pressure compressor bleed valves | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F520Limit on Blow off valve did not make forcing unit offline.
BR10 | 23 | U1 | 2017-04-17 07:30 |  |  |  |  | 2017-04-17 07:42 |  | 0 | 0 | 0.2 | 0.2 | 23.6 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 5017 |  |  | - |  | Low pressure compressor bleed valves | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F520Limit switch on compressor blow off valve did not make forcing unit offline
BR10 | 28 | SF | 2017-04-29 12:02 |  |  |  |  | 2017-04-29 13:20 |  | 0 | 0 | 1.3 | 1.3 | 153.4 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 5248 |  |  | - |  | Gas Turbine Control System - logic problems | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Switch over unit logic prevented gas turbine from starting.
BR10 | 32 | U1 | 2017-05-16 13:13 |  |  |  |  | 2017-05-16 16:05 |  | 0 | 0 | 2.867 | 2.8667 | 338.267 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 5454 |  |  | - |  | Water injection system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F410Trip due to failure of IP on Nox water control valve.
BR10 | 36 | U1 | 2017-05-19 06:59 |  |  |  |  | 2017-05-19 09:51 |  | 0 | 0 | 2.867 | 2.8667 | 338.267 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 5065 |  |  | - |  | NOx water injection system including pump | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Forced outage to change out NOx water control valve IP.
BR10 | 70 | U1 | 2017-09-08 08:36 |  |  |  |  | 2017-09-08 13:57 |  | 0 | 0 | 5.35 | 5.35 | 631.3 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 3612 |  |  | - |  | Switchyard system protection devices - external (OMC) | [8 empty] | AMP CODE: |  | X0
|  | DESCRIPTION : |  | FX00Brown North Substation Protection Disabled.
BR10 | 86 | U1 | 2017-12-08 05:22 |  |  |  |  | 2017-12-08 05:41 |  | 0 | 0 | 0.317 | 0.3167 | 43.7 | 1 |  |  |  | 0 |  |  | 139
|  | CAUSE CODE : |  | 5039 |  |  | - |  | Other compressor problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F540Blow off valve failed to close.
BR10 | 19 | SF | 2018-05-01 17:00 |  |  |  |  | 2018-05-01 17:35 |  | 0 | 0 | 0.583 | 0.5833 | 68.833 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 3611 |  |  | - |  | Switchyard circuit breakers - external (OMC) | [8 empty] | AMP CODE: |  | 42
|  | DESCRIPTION : |  | F420MOS in substation not restored correctly after LOTO.
BR10 | 26 | U1 | 2018-05-15 20:43 |  |  |  |  | 2018-05-15 23:00 |  | 0 | 0 | 2.283 | 2.2833 | 269.433 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 5047 |  |  | - |  | Liquid fuel purge system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F410False trip from Fuel Oil drain tank, Cleaned and repaired level switch on tank. No
BR10 | 45 | SF | 2018-09-07 16:35 |  |  |  |  | 2018-09-07 20:13 |  | 0 | 0 | 3.633 | 3.6333 | 428.733 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 3610 |  |  | - |  | Switchyard circuit breakers - external (not OMC) | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Looks as if unit controls did not see feedback from substation breaker that breake
BR10 | 55 | U1 | 2018-10-07 17:28 |  |  |  |  | 2018-10-07 19:44 |  | 0 | 0 | 2.267 | 2.2667 | 267.467 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 3621 |  |  | - |  | Unit auxiliaries transformer | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F030Ligthning arrestor on BOP north transformer went to ground. Substation Crew did f
BR10 | 62 | SF | 2018-11-14 03:55 |  |  |  |  | 2018-11-14 04:25 |  | 0 | 0 | 0.5 | 0.5 | 59 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410U11 was calling for SFC. Prevented U10 from starting. Investigating how U11 sequ
BR10 | 6 | U1 | 2019-01-20 12:10 |  |  |  |  | 2019-01-20 12:26 |  | 0 | 0 | 0.267 | 0.2667 | 36.8 | 1 |  |  |  | 0 |  |  | 139
|  | CAUSE CODE : |  | 5039 |  |  | - |  | Other compressor problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F410Blow off valve limit switch needed adjustment.
BR10 | 8 | U1 | 2019-01-29 20:54 |  |  |  |  | 2019-01-29 21:30 |  | 0 | 0 | 0.6 | 0.6 | 82.8 | 1 |  |  |  | 0 |  |  | 139
|  | CAUSE CODE : |  | 4555 |  |  | - |  | Bearing cooling system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F010Exhaust bearing metal temperature went high during start up. Tried another start
BR10 | 12 | SF | 2019-03-04 17:12 |  |  |  |  | 2019-03-04 19:05 |  | 0 | 0 | 1.883 | 1.8833 | 222.233 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 5050 |  |  | - |  | Ignition system | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Unit would not light off due to ignition glow plug supervisory check current relay
BR10 | 38 | SF | 2019-09-10 11:33 |  |  |  |  | 2019-09-11 11:13 |  | 0 | 0 | 23.667 | 23.6667 | 2792.667 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 5450 |  |  | - |  | Ignition system | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Failed glow plug. Pulled nozzle to replace.
BR10 | 40 | SF | 2019-09-12 11:31 |  |  |  |  | 2019-09-12 12:03 |  | 0 | 0 | 0.533 | 0.5333 | 62.933 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 5041 |  |  | - |  | Fuel piping and valves | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Voith Relief valve failed to go close. Diagnostic on IO had shorted circuit. Did
BR10 | 53 | U1 | 2019-11-04 06:31 |  |  |  |  | 2019-11-04 09:02 |  | 0 | 0 | 2.517 | 2.5167 | 296.967 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 5201 |  |  | - |  | Load shaft and bearings | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F780Exhaust end bearing temperature went high.
BR10 | 69 | U1 | 2019-12-18 06:08 |  |  |  |  | 2019-12-18 20:01 |  | 0 | 0 | 13.883 | 13.8833 | 1915.9 | 1 |  |  |  | 0 |  |  | 139
|  | CAUSE CODE : |  | 5570 |  |  | - |  | Cooling water system | [8 empty] | AMP CODE: |  | 06
|  | DESCRIPTION : |  | F060Glycol cooling water pump leaking. Replaced pump and motor.
BR10 | 4 | U1 | 2020-02-14 04:30 |  |  |  |  | 2020-02-14 05:01 |  | 0 | 0 | 0.517 | 0.5167 | 71.3 | 1 |  |  |  | 0 |  |  | 139
|  | CAUSE CODE : |  | 5447 |  |  | - |  | Gas fuel system including controls and instrumentation | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F480Regulating valves in reducing station developed swing. Pressure regulating valves
BR10 | 5 | U1 | 2020-02-14 06:12 |  |  |  |  | 2020-02-14 09:23 |  | 0 | 0 | 3.183 | 3.1833 | 439.3 | 1 |  |  |  | 0 |  |  | 139
|  | CAUSE CODE : |  | 5120 |  |  | - |  | Hydraulic oil system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F540Power oil line to fuel oil control valve developed leak causing small fire. Fire
BR10 | 24 | U1 | 2020-07-05 20:46 |  |  |  |  | 2020-07-06 00:46 |  | 0 | 0 | 4 | 4 | 484 | 1 |  |  |  | 0 |  |  | 122
|  | CAUSE CODE : |  | 5550 |  |  | - |  | Turning gear and motor | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Rotor Barring issue. Replaced prox switch on piston. Changed out solenoid
BR10 | 44 | U1 | 2020-11-19 10:08 |  |  |  |  | 2020-11-19 15:32 |  | 0 | 0 | 5.4 | 5.4 | 637.2 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 3864 |  |  | - |  | Fire protection system instrumentation and controls | [8 empty] | AMP CODE: |  | 49
|  | DESCRIPTION : |  | F490Fire protection panel indicated an abnormal power condition
BR10 | 51 | SF | 2020-12-26 04:29 |  |  |  |  | 2020-12-26 07:09 |  | 0 | 0 | 2.667 | 2.6667 | 368 | 1 |  |  |  | 0 |  |  | 139
|  | CAUSE CODE : |  | 3641 |  |  | - |  | AC Circuit breakers | [8 empty] | AMP CODE: |  | 55
|  | DESCRIPTION : |  | F550Found loose connection on breaker power feed to TRIO block.
BR10 | 6 | U1 | 2021-01-28 12:38 |  |  |  |  | 2021-01-28 15:03 |  | 0 | 0 | 2.417 | 2.4167 | 333.5 | 1 |  |  |  | 0 |  |  | 139
|  | CAUSE CODE : |  | 3611 |  |  | - |  | Switchyard circuit breakers - external (OMC) | [8 empty] | AMP CODE: |  | 59
|  | DESCRIPTION : |  | F590Hydraulic hose on substation breaker blown out.
BR10 | 8 | U1 | 2021-02-09 15:33 |  |  |  |  | 2021-02-11 19:00 |  | 0 | 0 | 51.45 | 51.45 | 7100.1 | 1 |  |  |  | 0 |  |  | 139
|  | CAUSE CODE : |  | 3864 |  |  | - |  | Fire protection system instrumentation and controls | [8 empty] | AMP CODE: |  | 06
|  | DESCRIPTION : |  | F060Fire control panel would not power up.
BR10 | 14 | U1 | 2021-03-22 12:47 |  |  |  |  | 2021-03-22 13:32 |  | 0 | 0 | 0.75 | 0.75 | 88.5 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 5087 |  |  | - |  | Thrust bearing | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Loose connection on thrust bearing rtd caused unit trip.
BR10 | 34 | SF | 2021-07-15 12:36 |  |  |  |  | 2021-07-15 14:17 |  | 0 | 0 | 1.683 | 1.6833 | 203.683 | 1 |  |  |  | 0 |  |  | 122
|  | CAUSE CODE : |  | 5122 |  |  | - |  | Hydraulic oil system piping/valves | [8 empty] | AMP CODE: |  | 69
|  | DESCRIPTION : |  | F690Staging valve stuck casuing flame trip.
BR10 | 4 | SF | 2022-01-27 03:46 |  |  |  |  | 2022-01-27 12:08 |  | 0 | 0 | 8.367 | 8.3667 | 1154.6 | 1 |  |  |  | 0 |  |  | 139
|  | CAUSE CODE : |  | 4603 |  |  | - |  | Solid state exciter element | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340SUF due to failed 48v relay in the SFC
BR10 | 59 | U1 | 2022-12-03 18:26 |  |  |  |  | 2023-01-01 |  | 0 | 0 | 677.567 | 677.5667 | 93504.2 | 1 |  |  |  | 0 |  |  | 139
|  | CAUSE CODE : |  | 5109 |  |  | - |  | Other exhaust problems (including high exhaust system temperature not attributable to a specific problem) | [8 empty] | AMP CODE: |  | 06
|  | DESCRIPTION : |  | F060Exhaust diffuser sections have separated. Bolts need to be replaced and exhaust d
BR10 | 1 | U1 | 2023-01-01 |  |  |  |  | 2023-01-06 14:18 |  | 0 | 0 | 134.3 | 134.3 | 18533.4 | 1 |  |  |  | 0 |  |  | 139
|  | CAUSE CODE : |  | 5109 |  |  | - |  | Other exhaust problems (including high exhaust system temperature not attributable to a specific problem) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F060Exhaust diffuser sections have separated. Bolts need to be replaced and exhaust d
BR10 | 25 | U1 | 2023-06-17 15:08 |  |  |  |  | 2023-06-17 18:42 |  | 0 | 0 | 3.567 | 3.5667 | 431.567 | 1 |  |  |  | 0 |  |  | 122
|  | CAUSE CODE : |  | 5150 |  |  | - |  | Turning gear and motor | [8 empty] | AMP CODE: |  | 06
|  | DESCRIPTION : |  | F060Rotobarring system is not turning the rotor.
BR10 | 27 | U1 | 2023-06-19 05:14 |  |  |  |  | 2023-06-19 15:39 |  | 0 | 0 | 10.417 | 10.4167 | 1260.417 | 1 |  |  |  | 0 |  |  | 122
|  | CAUSE CODE : |  | 5113 |  |  | - |  | Lube oil valves/piping | [8 empty] | AMP CODE: |  | 54
|  | DESCRIPTION : |  | F540Lube oil leak in the vacinity of bearing 2.
Brown - BR11
Unit | Event | Type | Start |  |  |  |  | End |  | GAC | NAC | Duration | Equiv Hrs | Equiv MWH | Cont | Work Start | Work End |  | Hours |  |  | Gross Capacity Impact (MW)
BR11 | 3 | U1 | 2014-01-06 17:57 |  |  |  |  | 2014-01-06 19:14 |  | 0 | 0 | 1.283 | 1.2833 | 164.267 | 1 |  |  |  | 0 |  |  | 129
|  | CAUSE CODE : |  | 5017 |  |  | - |  | Low pressure compressor bleed valves | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F550Loose limit switch on blow off valve caused unit to trip.
BR11 | 16 | U1 | 2014-01-30 03:36 |  |  |  |  | 2014-01-30 07:40 |  | 0 | 0 | 4.067 | 4.0667 | 520.533 | 1 |  |  |  | 0 |  |  | 129
|  | CAUSE CODE : |  | 5017 |  |  | - |  | Low pressure compressor bleed valves | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F410Loose limit switch on compressor blow off valve
BR11 | 27 | SF | 2014-03-19 10:23 |  |  |  |  | 2014-03-19 12:46 |  | 0 | 0 | 2.383 | 2.3833 | 305.067 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 5041 |  |  | - |  | Fuel piping and valves | [8 empty] | AMP CODE: |  | 56
|  | DESCRIPTION : |  | F560Control Gas Valve swinging during start up.
BR11 | 41 | SF | 2014-07-08 00:21 |  |  |  |  | 2014-07-08 00:41 |  | 0 | 0 | 0.333 | 0.3333 | 34 | 1 |  |  |  | 0 |  |  | 122
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 59
|  | DESCRIPTION : |  | F590Main breaker for SFC failed.
BR11 | 51 | SF | 2014-09-25 13:56 |  |  |  |  | 2014-09-25 14:53 |  | 0 | 0 | 0.95 | 0.95 | 96.9 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410SFC failure during startup.
BR11 | 53 | SF | 2014-10-07 18:34 |  |  |  |  | 2014-10-07 18:35 |  | 0 | 0 | 0.017 | 0.0167 | 2.133 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 5049 |  |  | - |  | Other fuel system problems | [8 empty] | AMP CODE: |  | 42
|  | DESCRIPTION : |  | F420Gas supply not set up correctly.
BR11 | 8 | U1 | 2015-02-03 10:48 |  |  |  |  | 2015-02-03 14:48 |  | 0 | 0 | 4 | 4 | 512 | 1 |  |  |  | 0 |  |  | 129
|  | CAUSE CODE : |  | 5110 |  |  | - |  | Lube oil system - general | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Contactor failed on main lube oil pump. Failure caused small fire in the MCC cubi
BR11 | 12 | U1 | 2015-02-17 08:46 |  |  |  |  | 2015-02-17 12:30 |  | 0 | 0 | 3.733 | 3.7333 | 477.867 | 1 |  |  |  | 0 |  |  | 129
|  | CAUSE CODE : |  | 5065 |  |  | - |  | NOx water injection system including pump | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F060Outage to repair busted NOx water line
BR11 | 18 | U1 | 2015-03-06 08:05 |  |  |  |  | 2015-03-06 11:05 |  | 0 | 0 | 3 | 3 | 384 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 5002 |  |  | - |  | Inlet air filters | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F480Fog / Mist started to freeze up inlet screens. Implosion doors went open.
BR11 | 23 | SF | 2015-04-13 18:29 |  |  |  |  | 2015-04-13 19:23 |  | 0 | 0 | 0.9 | 0.9 | 108.9 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Medium voltage breaker failure on static starting device.
BR11 | 45 | SF | 2015-05-31 16:10 |  |  |  |  | 2015-05-31 16:46 |  | 0 | 0 | 0.6 | 0.6 | 72.6 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 5530 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F4103 Position ISO drive did not operate due to mechanical key switch failure when rem
BR11 | 57 | U1 | 2015-06-20 22:45 |  |  |  |  | 2015-06-21 01:25 |  | 0 | 0 | 2.667 | 2.6667 | 322.667 | 1 |  |  |  | 0 |  |  | 122
|  | CAUSE CODE : |  | 3610 |  |  | - |  | Switchyard circuit breakers - external (not OMC) | [8 empty] | AMP CODE: |  | 54
|  | DESCRIPTION : |  | F540Main substation breaker hydraulic pump replacement
BR11 | 69 | SF | 2015-07-17 10:16 |  |  |  |  | 2015-07-17 10:53 |  | 0 | 0 | 0.617 | 0.6167 | 74.617 | 1 |  |  |  | 0 |  |  | 122
|  | CAUSE CODE : |  | 5049 |  |  | - |  | Other fuel system problems | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Failed to light. Did not look to get signal from controller.
BR11 | 71 | SF | 2015-07-18 09:06 |  |  |  |  | 2015-07-18 10:01 |  | 0 | 0 | 0.917 | 0.9167 | 110.917 | 1 |  |  |  | 0 |  |  | 122
|  | CAUSE CODE : |  | 5110 |  |  | - |  | Lube oil system - general | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Lube oil control sequence not functioning propoerly. Likely pressure switch for e
BR11 | 91 | U1 | 2015-09-21 11:45 |  |  |  |  | 2015-09-21 14:19 |  | 0 | 0 | 2.567 | 2.5667 | 310.567 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 3611 |  |  | - |  | Switchyard circuit breakers - external (OMC) | [8 empty] | AMP CODE: |  | X0
|  | DESCRIPTION : |  | FX00Hydraulic oil leak on substation breaker.
BR11 | 94 | U1 | 2015-09-24 09:21 |  |  |  |  | 2015-09-24 10:40 |  | 0 | 0 | 1.317 | 1.3167 | 159.317 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 3624 |  |  | - |  | Auxiliary generator voltage supply system | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Bad card in AVR control system. Card for switching between auto/manual control fai
BR11 | 109 | U1 | 2015-11-16 04:11 |  |  |  |  | 2015-11-16 10:02 |  | 0 | 0 | 5.85 | 5.85 | 748.8 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 5510 |  |  | - |  | Lube oil system | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Motor failed on the lube oil vapor extractor.
BR11 | 15 | SF | 2016-03-29 06:12 |  |  |  |  | 2016-03-29 06:37 |  | 0 | 0 | 0.417 | 0.4167 | 49.167 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 69
|  | DESCRIPTION : |  | F690Brush lift off device failed to go closed on start up of SFC.
BR11 | 19 | U1 | 2016-04-01 08:44 |  |  |  |  | 2016-04-01 15:26 |  | 0 | 0 | 6.7 | 6.7 | 790.6 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 5111 |  |  | - |  | Lube oil pumps | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Aux jacking oil pump motor failed during operation.
BR11 | 34 | SF | 2016-06-22 13:46 |  |  |  |  | 2016-06-22 17:31 |  | 0 | 0 | 3.75 | 3.75 | 453.75 | 1 |  |  |  | 0 |  |  | 122
|  | CAUSE CODE : |  | 5041 |  |  | - |  | Fuel piping and valves | [8 empty] | AMP CODE: |  | 06
|  | DESCRIPTION : |  | F060Limit switch broke inside limittorque actuator for main gas control valve.
BR11 | 38 | U1 | 2016-06-26 15:49 |  |  |  |  | 2016-06-26 16:14 |  | 0 | 0 | 0.417 | 0.4167 | 50.417 | 1 |  |  |  | 0 |  |  | 122
|  | CAUSE CODE : |  | 9020 |  |  | - |  | Lightning | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F410Unit tripped due to gas valves in reducing station going closed due to lightning s
BR11 | 66 | U1 | 2016-07-25 08:08 |  |  |  |  | 2016-07-25 10:57 |  | 0 | 0 | 2.817 | 2.8167 | 340.817 | 1 |  |  |  | 0 |  |  | 122
|  | CAUSE CODE : |  | 3610 |  |  | - |  | Switchyard circuit breakers - external (not OMC) | [8 empty] | AMP CODE: |  | 66
|  | DESCRIPTION : |  | F660Substation Breaker- Investigating Hydraulic pump running continuously.
BR11 | 78 | SF | 2016-08-25 09:24 |  |  |  |  | 2016-08-25 10:07 |  | 0 | 0 | 0.717 | 0.7167 | 86.717 | 1 |  |  |  | 0 |  |  | 122
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 69
|  | DESCRIPTION : |  | F690Unit would not start due to failure of Brush lift off device. Wire rope cable had
BR11 | 84 | U1 | 2016-09-07 22:00 |  |  |  |  | 2016-09-07 22:43 |  | 0 | 0 | 0.717 | 0.7167 | 84.567 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 3971 |  |  | - |  | DCS - data highway | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410DCS LAN went down causing 11N2 system to lose communication.
BR11 | 94 | U1 | 2016-10-05 20:19 |  |  |  |  | 2016-10-05 20:29 |  | 0 | 0 | 0.167 | 0.1667 | 19.667 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 3618 |  |  | - |  | Other switchyard equipment - external (not OMC) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F410Unit tripped when opening the MOS on unit 10. Opening the MOS on U10 caused a spee
BR11 | 4 | U1 | 2017-01-08 07:34 |  |  |  |  | 2017-01-08 11:18 |  | 0 | 0 | 3.733 | 3.7333 | 477.867 | 1 |  |  |  | 0 |  |  | 129
|  | CAUSE CODE : |  | 5039 |  |  | - |  | Other compressor problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F660Compressor blow off valve did not go close.
BR11 | 14 | U1 | 2017-03-02 11:42 |  |  |  |  | 2017-03-03 12:12 |  | 0 | 0 | 24.5 | 24.5 | 2891 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 4609 |  |  | - |  | Other exciter problems | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Voltage regulator controls tripping supply breaker.
BR11 | 16 | SF | 2017-03-04 05:45 |  |  |  |  | 2017-03-04 09:42 |  | 0 | 0 | 3.95 | 3.95 | 466.1 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 3611 |  |  | - |  | Switchyard circuit breakers - external (OMC) | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Unit would not sync to grid due to broken or loose wire in substation GCB control
BR11 | 23 | U1 | 2017-04-29 12:02 |  |  |  |  | 2017-04-29 13:20 |  | 0 | 0 | 1.3 | 1.3 | 153.4 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 5248 |  |  | - |  | Gas Turbine Control System - logic problems | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Switchover unit logic prevented units from being able to start.
BR11 | 35 | U1 | 2017-09-08 08:36 |  |  |  |  | 2017-09-08 13:57 |  | 0 | 0 | 5.35 | 5.35 | 631.3 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 3612 |  |  | - |  | Switchyard system protection devices - external (OMC) | [8 empty] | AMP CODE: |  | X0
|  | DESCRIPTION : |  | FX00Brown North Substation Protection Disabled.
BR11 | 9 | U1 | 2018-01-18 10:19 |  |  |  |  | 2018-01-31 14:10 |  | 0 | 0 | 315.85 | 315.85 | 40428.8 | 1 |  |  |  | 0 |  |  | 129
|  | CAUSE CODE : |  | 5070 |  |  | - |  | Combustor casing | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F750Unit could not meet TAT spread exhaust temperature limits.
BR11 | 16 | U1 | 2018-04-11 04:29 |  |  |  |  | 2018-04-11 12:59 |  | 0 | 0 | 8.5 | 8.5 | 1003 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 3979 |  |  | - |  | Other DCS problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F410Bad Control board on SKF redundant overspeed. Unit tripped on false overspeed sig
BR11 | 55 | U1 | 2018-12-29 02:42 |  |  |  |  | 2018-12-29 16:43 |  | 0 | 0 | 14.017 | 14.0167 | 1794.133 | 1 |  |  |  | 0 |  |  | 129
|  | CAUSE CODE : |  | 5550 |  |  | - |  | Turning gear and motor | [8 empty] | AMP CODE: |  | 06
|  | DESCRIPTION : |  | F060Broken spring in rotor barring piston. Replaced spring with spare.
BR11 | 36 | SF | 2020-12-26 04:34 |  |  |  |  | 2020-12-26 13:16 |  | 0 | 0 | 8.7 | 8.7 | 1113.6 | 1 |  |  |  | 0 |  |  | 129
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 48
|  | DESCRIPTION : |  | F4803 position iso switch was frozen and not operable
BR11 | 18 | SF | 2021-05-12 08:13 |  |  |  |  | 2021-05-12 09:35 |  | 0 | 0 | 1.367 | 1.3667 | 161.267 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 5050 |  |  | - |  | Ignition system | [8 empty] | AMP CODE: |  | 46
|  | DESCRIPTION : |  | F460Unit failed to light on oil.
BR11 | 4 | U1 | 2022-01-27 03:46 |  |  |  |  | 2022-01-27 12:08 |  | 0 | 0 | 8.367 | 8.3667 | 1070.933 | 1 |  |  |  | 0 |  |  | 129
|  | CAUSE CODE : |  | 4603 |  |  | - |  | Solid state exciter element | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F34048v relay failed on shared SFC
BR11 | 25 | SF | 2022-06-22 10:03 |  |  |  |  | 2022-06-22 10:18 |  | 0 | 0 | 0.25 | 0.25 | 30.25 | 1 |  |  |  | 0 |  |  | 122
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410SFC voltage issue. Unit would not properly roll up.
BR11 | 37 | U1 | 2022-07-20 11:19 |  |  |  |  | 2022-07-20 15:59 |  | 0 | 0 | 4.667 | 4.6667 | 564.667 | 1 |  |  |  | 0 |  |  | 122
|  | CAUSE CODE : |  | 4511 |  |  | - |  | "Rotor, General" | [8 empty] | AMP CODE: |  | 70
|  | DESCRIPTION : |  | F700Rotor Barring System - faulty amplifier
BR11 | 58 | U1 | 2022-12-23 01:30 |  |  |  |  | 2022-12-23 03:50 |  | 0 | 0 | 2.333 | 2.3333 | 298.667 | 1 |  |  |  | 0 |  |  | 129
|  | CAUSE CODE : |  | 5041 |  |  | - |  | Fuel piping and valves | [8 empty] | AMP CODE: |  | 48
|  | DESCRIPTION : |  | F480Frozen fuel valves due to valves heaters to the 11N2 units kept going out.
BR11 | 60 | U1 | 2022-12-23 15:39 |  |  |  |  | 2022-12-23 17:03 |  | 0 | 0 | 1.4 | 1.4 | 179.2 | 1 |  |  |  | 0 |  |  | 129
|  | CAUSE CODE : |  | 5073 |  |  | - |  | Flame scanners | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Flame trip
Brown - BR3
Unit | Event | Type | Start |  |  |  |  | End |  | GAC | NAC | Duration | Equiv Hrs | Equiv MWH | Cont | Work Start | Work End |  | Hours |  |  | Gross Capacity Impact (MW)
BR3 | 8 | U1 | 2014-01-30 03:57 |  |  |  |  | 2014-02-01 16:05 |  | 0 | 0 | 60.133 | 60.1333 | 24895.199 | 1 |  |  |  | 0 |  |  | 456
|  | CAUSE CODE : |  | 0339 |  |  | - |  | Pulverizer System Puff | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | 3-5 Mill puff causing D corner burner damage and associated boiler tube leak.
BR3 | 20 | U1 | 2014-03-19 10:32 |  |  |  |  | 2014-03-19 12:29 |  | 0 | 0 | 1.95 | 1.95 | 807.3 | 1 |  |  |  | 0 |  |  | 455.5
|  | CAUSE CODE : |  | 0740 |  |  | - |  | Boiler recirculation pumps | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | Boiler trip due to BCWP differential pressure
BR3 | 22 | U1 | 2014-03-19 23:04 |  |  |  |  | 2014-03-21 06:05 |  | 0 | 0 | 31.017 | 31.0167 | 12840.9 | 1 |  |  |  | 0 |  |  | 455.5
|  | CAUSE CODE : |  | 0310 |  |  | - |  | Pulverizer mills | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | 3-5 mill explosion, damage inspection and repair
BR3 | 31 | SF | 2014-04-28 18:30 |  |  |  |  | 2014-04-30 05:45 |  | 0 | 0 | 35.25 | 35.25 | 14452.5 | 1 |  |  |  | 0 |  |  | 455.5
|  | CAUSE CODE : |  | 1000 |  |  | - |  | Waterwall (Furnace wall) | [8 empty] | AMP CODE: |  | 54
|  | DESCRIPTION : |  | Lower waterwall tube leak found during startup
BR3 | 32 | SF | 2014-04-30 05:45 |  |  |  |  | 2014-05-01 01:28 |  | 0 | 0 | 19.717 | 19.7167 | 8083.833 | 1 |  |  |  | 0 |  |  | 455.5
|  | CAUSE CODE : |  | 1090 |  |  | - |  | Other boiler tube leaks | [8 empty] | AMP CODE: |  | 54
|  | DESCRIPTION : |  | Sample line from steam drum leaking 6566287
BR3 | 47 | U1 | 2014-06-10 16:09 |  |  |  |  | 2014-06-11 04:21 |  | 0 | 0 | 12.2 | 12.2 | 5002 | 1 |  |  |  | 0 |  |  | 455
|  | CAUSE CODE : |  | 4860 |  |  | - |  | Generator neutral grounding equipment | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | Loose wire on ground neutral transformer 6579166
BR3 | 48 | U1 | 2014-06-11 08:52 |  |  |  |  | 2014-06-11 23:07 |  | 0 | 0 | 14.25 | 14.25 | 5842.5 | 1 |  |  |  | 0 |  |  | 455
|  | CAUSE CODE : |  | 3621 |  |  | - |  | Unit auxiliaries transformer | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | "A" Auxiliary Transformer A phase bushing failure 6579361
BR3 | 50 | U1 | 2014-06-14 22:56 |  |  |  |  | 2014-06-16 08:10 |  | 0 | 0 | 33.233 | 33.2333 | 13625.666 | 1 |  |  |  | 0 |  |  | 455
|  | CAUSE CODE : |  | 1000 |  |  | - |  | Waterwall (Furnace wall) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | Waterwall tube leak at C corner upper burner level 6579764
BR3 | 52 | U1 | 2014-07-01 12:10 |  |  |  |  | 2014-07-01 13:20 |  | 0 | 0 | 1.167 | 1.1667 | 478.333 | 1 |  |  |  | 0 |  |  | 455
|  | CAUSE CODE : |  | 9910 |  |  | - |  | Maintenance personnel error | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | Transmission employee tripped West Cliff substation feed to unit 3 6585768
BR3 | 53 | U1 | 2014-07-17 13:11 |  |  |  |  | 2014-07-22 15:50 |  | 0 | 0 | 122.65 | 122.65 | 50286.5 | 1 |  |  |  | 0 |  |  | 455
|  | CAUSE CODE : |  | 3245 |  |  | - |  | Other cooling tower problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | 3-2 Cooloing tower cell damage 6589856
BR3 | 54 | SF | 2014-07-22 15:50 |  |  |  |  | 2014-07-22 20:41 |  | 0 | 0 | 4.85 | 4.85 | 1988.5 | 1 |  |  |  | 0 |  |  | 455
|  | CAUSE CODE : |  | 3210 |  |  | - |  | Circulating water pumps | [8 empty] | AMP CODE: |  | 19
|  | DESCRIPTION : |  | 3-2 CWP discharge valve not fully open. 3-1 CWP unavailable 6591462
BR3 | 64 | U1 | 2014-09-17 13:05 |  |  |  |  | 2014-09-20 13:36 |  | 0 | 0 | 72.517 | 72.5167 | 29731.833 | 1 |  |  |  | 0 |  |  | 455.5
|  | CAUSE CODE : |  | 4281 |  |  | - |  | Lube oil coolers | [8 empty] | AMP CODE: |  | 54
|  | DESCRIPTION : |  | 3-1 Turbine Oil cooler leak. 6606790
BR3 | 77 | U1 | 2014-11-12 17:24 |  |  |  |  | 2014-11-17 04:41 |  | 0 | 0 | 107.283 | 107.2833 | 44415.3 | 1 |  |  |  | 0 |  |  | 455.5
|  | CAUSE CODE : |  | 1070 |  |  | - |  | Second reheater | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | Reheat tube leak 6622981
BR3 | 5 | U1 | 2015-01-22 19:00 |  |  |  |  | 2015-01-22 22:02 |  | 0 | 0 | 3.033 | 3.0333 | 1255.8 | 1 |  |  |  | 0 |  |  | 456
|  | CAUSE CODE : |  | 4609 |  |  | - |  | Other exciter problems | [8 empty] | AMP CODE: |  | 54
|  | DESCRIPTION : |  | Exciter cooler piping leak
BR3 | 7 | SF | 2015-01-25 21:08 |  |  |  |  | 2015-01-26 18:20 |  | 0 | 0 | 21.2 | 21.2 | 8776.8 | 1 |  |  |  | 0 |  |  | 456
|  | CAUSE CODE : |  | 0500 |  |  | - |  | Main steam piping up to turbine stop valves | [8 empty] | AMP CODE: |  | 54
|  | DESCRIPTION : |  | Pin hole leak in main steam drain line prior to isolation valve.
BR3 | 11 | U1 | 2015-02-06 09:08 |  |  |  |  | 2015-02-06 19:03 |  | 0 | 0 | 9.917 | 9.9167 | 4105.5 | 1 |  |  |  | 0 |  |  | 456
|  | CAUSE CODE : |  | 4560 |  |  | - |  | Generator vibration (excluding vibration due to failed bearing and other components) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | #7 generator/exciter bearing vibration
BR3 | 12 | U1 | 2015-02-20 13:34 |  |  |  |  | 2015-02-20 15:55 |  | 0 | 0 | 2.35 | 2.35 | 972.9 | 1 |  |  |  | 0 |  |  | 456
|  | CAUSE CODE : |  | 0090 |  |  | - |  | Bunker fires | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | FR00Unit 3 coal bunker fires in 3-4 and partially in 3-5 bunker
BR3 | 16 | U1 | 2015-03-06 01:49 |  |  |  |  | 2015-03-07 03:19 |  | 0 | 0 | 25.5 | 25.5 | 10556.999 | 1 |  |  |  | 0 |  |  | 455.5
|  | CAUSE CODE : |  | 0500 |  |  | - |  | Main steam piping up to turbine stop valves | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | Leak in main steam drain line 6660146
BR3 | 22 | U1 | 2015-05-11 12:20 |  |  |  |  | 2015-05-11 13:06 |  | 0 | 0 | 0.767 | 0.7667 | 314.333 | 1 |  |  |  | 0 |  |  | 455.5
|  | CAUSE CODE : |  | 3211 |  |  | - |  | Circulating water pump motors | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | 3-2 CWP trip leading to turbine trip
BR3 | 42 | U1 | 2015-07-15 03:49 |  |  |  |  | 2015-07-15 06:52 |  | 0 | 0 | 3.05 | 3.05 | 1250.5 | 1 |  |  |  | 0 |  |  | 455
|  | CAUSE CODE : |  | 9270 |  |  | - |  | Wet coal (OMC) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | Unit trip due to wet coal
BR3 | 43 | SF | 2015-07-15 06:52 |  |  |  |  | 2015-07-15 12:21 |  | 0 | 0 | 5.483 | 5.4833 | 2248.167 | 1 |  |  |  | 0 |  |  | 455
|  | CAUSE CODE : |  | 9270 |  |  | - |  | Wet coal (OMC) | [8 empty] | AMP CODE: |  | W0
|  | DESCRIPTION : |  | Startup failure due to wet coal conditions
BR3 | 70 | U1 | 2015-11-23 12:09 |  |  |  |  | 2015-11-23 23:00 |  | 0 | 0 | 10.85 | 10.85 | 4491.9 | 1 |  |  |  | 0 |  |  | 455.5
|  | CAUSE CODE : |  | 3399 |  |  | - |  | Other miscellaneous condensate system problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | Repair DA level transmitter
BR3 | 71 | SF | 2015-11-23 23:00 |  |  |  |  | 2015-11-24 03:16 |  | 0 | 0 | 4.267 | 4.2667 | 1766.4 | 1 |  |  |  | 0 |  |  | 455.5
|  | CAUSE CODE : |  | 9930 |  |  | - |  | Operating procedure error | [8 empty] | AMP CODE: |  | P0
|  | DESCRIPTION : |  | Trouble with rolling off 3-1 BFP
BR3 | 16 | U1 | 2016-03-17 12:39 |  |  |  |  | 2016-03-17 15:05 |  | 0 | 0 | 2.433 | 2.4333 | 1000.1 | 1 |  |  |  | 0 |  |  | 455.5
|  | CAUSE CODE : |  | 9900 |  |  | - |  | Operator error | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | Error in managing feedwater system during unit startup
BR3 | 18 | SF | 2016-04-16 17:15 |  |  |  |  | 2016-04-18 05:59 |  | 0 | 0 | 36.733 | 36.7333 | 15097.4 | 1 |  |  |  | 0 |  |  | 455.5
|  | CAUSE CODE : |  | 1591 |  |  | - |  | Stack damper and linkage | [8 empty] | AMP CODE: |  | 59
|  | DESCRIPTION : |  | U3 FGD shutoff damper motor failed
BR3 | 19 | U1 | 2016-04-18 09:14 |  |  |  |  | 2016-04-19 08:41 |  | 0 | 0 | 23.45 | 23.45 | 9637.95 | 1 |  |  |  | 0 |  |  | 455.5
|  | CAUSE CODE : |  | 1999 |  |  | - |  | "Boiler, miscellaneous" | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | Lower mud drum header gasket blown
BR3 | 41 | U1 | 2016-07-01 12:21 |  |  |  |  | 2016-07-05 15:36 |  | 0 | 0 | 99.25 | 99.25 | 40593.25 | 1 |  |  |  | 0 |  |  | 455
|  | CAUSE CODE : |  | 1160 |  |  | - |  | First reheater | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | Reheat tube leak
BR3 | 43 | U1 | 2016-07-05 21:43 |  |  |  |  | 2016-07-07 10:41 |  | 0 | 0 | 36.967 | 36.9667 | 15119.366 | 1 |  |  |  | 0 |  |  | 455
|  | CAUSE CODE : |  | 1512 |  |  | - |  | Flue gas expansion joints | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | 3-1 ID Fan expansion joint leak
BR3 | 54 | U1 | 2016-08-17 22:43 |  |  |  |  | 2016-08-18 21:43 |  | 0 | 0 | 23 | 23 | 9407 | 1 |  |  |  | 0 |  |  | 455
|  | CAUSE CODE : |  | 0740 |  |  | - |  | Boiler recirculation pumps | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | 3-2 BCWP discharge valve bypass line leak
BR3 | 59 | U1 | 2016-08-29 13:20 |  |  |  |  | 2016-08-31 17:30 |  | 0 | 0 | 52.167 | 52.1667 | 21336.167 | 1 |  |  |  | 0 |  |  | 455
|  | CAUSE CODE : |  | 1090 |  |  | - |  | Other boiler tube leaks | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | Waterwall leak from tube rupture
BR3 | 65 | U1 | 2016-11-01 06:56 |  |  |  |  | 2016-11-10 14:05 |  | 0 | 0 | 223.15 | 223.15 | 91714.65 | 1 |  |  |  | 0 |  |  | 455.5
|  | CAUSE CODE : |  | 4609 |  |  | - |  | Other exciter problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | Exciter insulation damaged
BR3 | 66 | U1 | 2016-11-10 14:34 |  |  |  |  | 2016-11-11 04:55 |  | 0 | 0 | 14.35 | 14.35 | 5897.85 | 1 |  |  |  | 0 |  |  | 455.5
|  | CAUSE CODE : |  | 4710 |  |  | - |  | Generator metering devices | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | Blown fuses on metering and GCB circuits
BR3 | 67 | U1 | 2016-11-11 13:22 |  |  |  |  | 2016-11-11 15:12 |  | 0 | 0 | 1.833 | 1.8333 | 753.5 | 1 |  |  |  | 0 |  |  | 455.5
|  | CAUSE CODE : |  | 4609 |  |  | - |  | Other exciter problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | Balance adjustment to temporary static exciter
BR3 | 68 | U1 | 2016-11-11 19:06 |  |  |  |  | 2016-11-12 01:01 |  | 0 | 0 | 5.917 | 5.9167 | 2431.75 | 1 |  |  |  | 0 |  |  | 455.5
|  | CAUSE CODE : |  | 4609 |  |  | - |  | Other exciter problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | Balance adjustment to temporary static exciter
BR3 | 69 | SF | 2016-11-12 01:01 |  |  |  |  | 2016-11-12 04:08 |  | 0 | 0 | 3.117 | 3.1167 | 1280.95 | 1 |  |  |  | 0 |  |  | 455.5
|  | CAUSE CODE : |  | 4609 |  |  | - |  | Other exciter problems | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | Generator lockout due to lockout in temporary exciter circuits
BR3 | 7 | SF | 2017-02-28 03:41 |  |  |  |  | 2017-02-28 12:06 |  | 0 | 0 | 8.417 | 8.4167 | 3476.083 | 1 |  |  |  | 0 |  |  | 456
|  | CAUSE CODE : |  | 0440 |  |  | - |  | Fuel oil pumps (general) | [8 empty] | AMP CODE: |  | FR
|  | DESCRIPTION : |  | Boiler trip on loss of fuel oil pump
BR3 | 8 | U1 | 2017-03-08 08:58 |  |  |  |  | 2017-03-09 06:19 |  | 0 | 0 | 21.35 | 21.35 | 8774.85 | 1 |  |  |  | 0 |  |  | 455.5
|  | CAUSE CODE : |  | 1000 |  |  | - |  | Waterwall (Furnace wall) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | Waterwall tube leak, "A" corner below conveyor level.
BR3 | 12 | U1 | 2017-03-24 11:33 |  |  |  |  | 2017-03-24 12:02 |  | 0 | 0 | 0.483 | 0.4833 | 198.65 | 1 |  |  |  | 0 |  |  | 455.5
|  | CAUSE CODE : |  | 9900 |  |  | - |  | Operator error | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | GCB opened by mistake when performing non related switching
BR3 | 21 | U1 | 2017-05-12 10:56 |  |  |  |  | 2017-05-12 12:30 |  | 0 | 0 | 1.567 | 1.5667 | 643.9 | 1 |  |  |  | 0 |  |  | 455.5
|  | CAUSE CODE : |  | 4609 |  |  | - |  | Other exciter problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | Water leak inside exciter housing
BR3 | 36 | U1 | 2017-08-14 16:13 |  |  |  |  | 2017-08-14 23:04 |  | 0 | 0 | 6.85 | 6.85 | 2801.65 | 1 |  |  |  | 0 |  |  | 455
|  | CAUSE CODE : |  | 4430 |  |  | - |  | Gland seal system | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | BFPT gland steam desuperheater plugged. cannot control temperature
BR3 | 40 | U1 | 2017-09-05 11:46 |  |  |  |  | 2017-09-07 15:47 |  | 0 | 0 | 52.017 | 52.0167 | 21378.85 | 1 |  |  |  | 0 |  |  | 455.5
|  | CAUSE CODE : |  | 1180 |  |  | - |  | Economizer | [8 empty] | AMP CODE: |  | 54
|  | DESCRIPTION : |  | Economizer tube leak
BR3 | 41 | U1 | 2017-09-08 08:36 |  |  |  |  | 2017-09-08 13:57 |  | 0 | 0 | 5.35 | 5.35 | 2198.85 | 1 |  |  |  | 0 |  |  | 455.5
|  | CAUSE CODE : |  | 3612 |  |  | - |  | Switchyard system protection devices - external (OMC) | [8 empty] | AMP CODE: |  | X0
|  | DESCRIPTION : |  | FX00loss of Brown North transmission lines protective relaying.
BR3 | 53 | U1 | 2017-12-25 06:20 |  |  |  |  | 2017-12-25 06:37 |  | 0 | 0 | 0.283 | 0.2833 | 117.017 | 1 |  |  |  | 0 |  |  | 456
|  | CAUSE CODE : |  | 0385 |  |  | - |  | Igniters | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | Lost oil guns on unit startup
BR3 | 54 | U1 | 2017-12-27 01:41 |  |  |  |  | 2017-12-29 21:50 |  | 0 | 0 | 68.15 | 68.15 | 28145.951 | 1 |  |  |  | 0 |  |  | 456
|  | CAUSE CODE : |  | 1180 |  |  | - |  | Economizer | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | Economizer tube leak
BR3 | 2 | U1 | 2018-01-04 17:21 |  |  |  |  | 2018-01-05 19:29 |  | 0 | 0 | 26.133 | 26.1333 | 10793.067 | 1 |  |  |  | 0 |  |  | 456
|  | CAUSE CODE : |  | 1090 |  |  | - |  | Other boiler tube leaks | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | Boiler leak in lower waterwall above ash hopper
BR3 | 4 | U1 | 2018-01-11 16:30 |  |  |  |  | 2018-01-15 14:57 |  | 0 | 0 | 94.45 | 94.45 | 39007.85 | 1 |  |  |  | 0 |  |  | 456
|  | CAUSE CODE : |  | 1090 |  |  | - |  | Other boiler tube leaks | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | Various leak repairs in reheat section of boiler
BR3 | 6 | U1 | 2018-01-15 16:48 |  |  |  |  | 2018-01-15 21:06 |  | 0 | 0 | 4.3 | 4.3 | 1775.9 | 1 |  |  |  | 0 |  |  | 456
|  | CAUSE CODE : |  | 1710 |  |  | - |  | "Combustion/steam condition controls (report local controls - burners, pulverizers, etc., - with component or system)" | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | Boiler trip while removing oil guns. Natural draft purge required
BR3 | 15 | U1 | 2018-03-12 01:42 |  |  |  |  | 2018-03-13 05:45 |  | 0 | 0 | 28.05 | 28.05 | 11528.55 | 1 |  |  |  | 0 |  |  | 455.5
|  | CAUSE CODE : |  | 3621 |  |  | - |  | Unit auxiliaries transformer | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Generator lockout due to 60 fl vt fuse loss grnd neut. overcurrent 86u 3-1 86u 3-2
BR3 | 16 | SF | 2018-03-13 05:45 |  |  |  |  | 2018-03-13 07:09 |  | 0 | 0 | 1.4 | 1.4 | 575.4 | 1 |  |  |  | 0 |  |  | 455.5
|  | CAUSE CODE : |  | 3621 |  |  | - |  | Unit auxiliaries transformer | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | Bad Potential transformer preventing sync
BR3 | 34 | U2 | 2018-07-20 18:20 |  |  |  |  | 2018-08-05 08:48 |  | 0 | 0 | 374.467 | 374.4667 | 153156.867 | 1 |  |  |  | 0 |  |  | 455
|  | CAUSE CODE : |  | 3245 |  |  | - |  | Other cooling tower problems | [8 empty] | AMP CODE: |  | 20
|  | DESCRIPTION : |  | F2003-1 and 3-2 cooling towers serverly damaged by high storm winds. loss of all fans.
BR3 | 43 | U1 | 2018-08-17 09:42 |  |  |  |  | 2018-08-17 11:26 |  | 0 | 0 | 1.733 | 1.7333 | 708.933 | 1 |  |  |  | 0 |  |  | 455
|  | CAUSE CODE : |  | 1455 |  |  | - |  | Induced draft fans | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820MFT due to loss of ID Fans while speed switching.
BR3 | 48 | U1 | 2018-08-21 12:31 |  |  |  |  | 2018-08-21 15:25 |  | 0 | 0 | 2.9 | 2.9 | 1186.1 | 1 |  |  |  | 0 |  |  | 455
|  | CAUSE CODE : |  | 1480 |  |  | - |  | Other induced draft fan problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Lost 3-1 ID fan resulting in MFT
BR3 | 63 | U1 | 2018-10-03 12:12 |  |  |  |  | 2018-10-03 14:00 |  | 0 | 0 | 1.8 | 1.8 | 739.8 | 1 |  |  |  | 0 |  |  | 455.5
|  | CAUSE CODE : |  | 4609 |  |  | - |  | Other exciter problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F850Turb trip due to vib on exciter bearing caused by rapid VAR loading from system.
BR3 | 7 | U1 | 2019-02-26 11:24 |  |  |  |  | 2019-02-26 11:57 |  | 0 | 0 | 0.55 | 0.55 | 227.15 | 1 |  |  |  | 0 |  |  | 456
|  | CAUSE CODE : |  | 3149 |  |  | - |  | "Loss of vacuum not attributable to a particular component such as air ejectors or valves, or high back pressure not attributable to high circulating water temperature, or vacuum losses from a known cause." | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Tripped due to loss of vaccum after CWP tripped on power factor. Lock out 86G3
BR3 | 15 | U1 | 2019-07-01 06:01 |  |  |  |  | 2019-07-01 10:56 |  | 0 | 0 | 4.917 | 4.9167 | 2010.917 | 1 |  |  |  | 0 |  |  | 455
|  | CAUSE CODE : |  | 8545 |  |  | - |  | Electrical failures | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F430CT wiring failure caused a lock out g86
BR3 | 16 | SF | 2019-07-01 10:56 |  |  |  |  | 2019-07-03 07:11 |  | 0 | 0 | 44.25 | 44.25 | 18098.25 | 1 |  |  |  | 0 |  |  | 455
|  | CAUSE CODE : |  | 4420 |  |  | - |  | Vibration of the turbine generator unit that cannot be attributed to a specific cause such as bearings or blades (use this code for balance moves) | [8 empty] | AMP CODE: |  | 85
|  | DESCRIPTION : |  | F850Vibration on roll up
BR3 | 25 | U1 | 2019-07-19 00:31 |  |  |  |  | 2019-07-19 14:21 |  | 0 | 0 | 13.833 | 13.8333 | 5657.833 | 1 |  |  |  | 0 |  |  | 455
|  | CAUSE CODE : |  | 9020 |  |  | - |  | Lightning | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Generator lock 86g due to issues with lighting arrester in south sub.
BR3 | 31 | U1 | 2019-08-30 05:55 |  |  |  |  | 2019-08-30 06:23 |  | 0 | 0 | 0.467 | 0.4667 | 190.867 | 1 |  |  |  | 0 |  |  | 455
|  | CAUSE CODE : |  | 0385 |  |  | - |  | Igniters | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F460MFT due to loss of igniters and oil guns.
BR3 | 32 | U1 | 2019-08-30 06:53 |  |  |  |  | 2019-08-30 09:55 |  | 0 | 0 | 3.033 | 3.0333 | 1240.633 | 1 |  |  |  | 0 |  |  | 455
|  | CAUSE CODE : |  | 0385 |  |  | - |  | Igniters | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F460MFT due to loss of igniters and oil guns.
BR3 | 33 | U1 | 2019-08-30 10:45 |  |  |  |  | 2019-08-30 13:14 |  | 0 | 0 | 2.483 | 2.4833 | 1015.683 | 1 |  |  |  | 0 |  |  | 455
|  | CAUSE CODE : |  | 0385 |  |  | - |  | Igniters | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F460MFT due to loss of igniters and oil guns.
BR3 | 36 | U1 | 2019-09-03 12:32 |  |  |  |  | 2019-09-03 17:49 |  | 0 | 0 | 5.283 | 5.2833 | 2171.45 | 1 |  |  |  | 0 |  |  | 455.5
|  | CAUSE CODE : |  | 4700 |  |  | - |  | Generator voltage control | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Generator lockout due to incorrect setting in the automatic voltage regulator.
BR3 | 39 | U1 | 2019-12-16 21:14 |  |  |  |  | 2019-12-20 22:00 |  | 0 | 0 | 96.767 | 96.7667 | 39964.633 | 1 |  |  |  | 0 |  |  | 456
|  | CAUSE CODE : |  | 1999 |  |  | - |  | "Boiler, miscellaneous" | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F540MFT due to BCWP east diff press sensing line leak. 3e heater extraction piping le
BR3 | 46 | U1 | 2019-12-22 11:36 |  |  |  |  | 2019-12-22 18:30 |  | 0 | 0 | 6.9 | 6.9 | 2849.7 | 1 |  |  |  | 0 |  |  | 456
|  | CAUSE CODE : |  | 3344 |  |  | - |  | Deaerator (including level control) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F540DA storage tank manway door gasket leaking
BR3 | 41 | U1 | 2019-12-22 18:30 |  |  |  |  | 2019-12-23 02:08 |  | 0 | 0 | 7.633 | 7.6333 | 3152.567 | 1 |  |  |  | 0 |  |  | 456
|  | CAUSE CODE : |  | 4262 |  |  | - |  | Intercept valves | [8 empty] | AMP CODE: |  | 54
|  | DESCRIPTION : |  | F540RH intercept valve EH leak - seal blown
BR3 | 4 | U1 | 2020-01-20 05:59 |  |  |  |  | 2020-01-20 13:10 |  | 0 | 0 | 7.183 | 7.1833 | 2988.267 | 1 |  |  |  | 0 |  |  | 456
|  | CAUSE CODE : |  | 4302 |  |  | - |  | Turbine trip devices (including instruments) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Generator 86U trip from when inverter caused and issue with EH trip skid solenoids
BR3 | 27 | U2 | 2020-12-07 15:51 |  |  |  |  | 2020-12-10 05:22 |  | 0 | 0 | 61.517 | 61.5167 | 25590.933 | 1 |  |  |  | 0 |  |  | 456
|  | CAUSE CODE : |  | 1060 |  |  | - |  | First reheater | [8 empty] | AMP CODE: |  | 54
|  | DESCRIPTION : |  | F540Reheat tube leak
BR3 | 29 | U1 | 2020-12-10 07:47 |  |  |  |  | 2020-12-11 01:02 |  | 0 | 0 | 17.25 | 17.25 | 7176.001 | 1 |  |  |  | 0 |  |  | 456
|  | CAUSE CODE : |  | 1350 |  |  | - |  | Other miscellaneous boiler tube problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F540mud drum door gasket leak
BR3 | 28 | U1 | 2020-12-11 02:40 |  |  |  |  | 2020-12-11 14:16 |  | 0 | 0 | 11.6 | 11.6 | 4825.6 | 1 |  |  |  | 0 |  |  | 456
|  | CAUSE CODE : |  | 1350 |  |  | - |  | Other miscellaneous boiler tube problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F540Mud drum door gasket leak
BR3 | 31 | U1 | 2020-12-14 20:20 |  |  |  |  | 2020-12-16 07:59 |  | 0 | 0 | 35.65 | 35.65 | 14830.4 | 1 |  |  |  | 0 |  |  | 456
|  | CAUSE CODE : |  | 1350 |  |  | - |  | Other miscellaneous boiler tube problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F540mud drum access door repair
BR3 | 5 | U2 | 2021-03-02 08:41 |  |  |  |  | 2021-03-04 10:00 |  | 0 | 0 | 49.317 | 49.3167 | 20417.1 | 1 |  |  |  | 0 |  |  | 455.5
|  | CAUSE CODE : |  | 1060 |  |  | - |  | First reheater | [8 empty] | AMP CODE: |  | 54
|  | DESCRIPTION : |  | F540Reheat tube leak front RH pendant assembly 1
BR3 | 11 | U1 | 2021-04-20 12:39 |  |  |  |  | 2021-04-22 16:58 |  | 0 | 0 | 52.317 | 52.3167 | 21659.1 | 1 |  |  |  | 0 |  |  | 455.5
|  | CAUSE CODE : |  | 1488 |  |  | - |  | Air heater (regenerative) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F8603-1 Air heater guide bearing failure
BR3 | 17 | SF | 2021-05-19 03:35 |  |  |  |  | 2021-05-19 12:19 |  | 0 | 0 | 8.733 | 8.7333 | 3615.6 | 1 |  |  |  | 0 |  |  | 455.5
|  | CAUSE CODE : |  | 3122 |  |  | - |  | Gaskets and seals | [8 empty] | AMP CODE: |  | 54
|  | DESCRIPTION : |  | F540Condenser cw waterbox door gasket leaking badly
BR3 | 19 | U1 | 2021-06-13 00:36 |  |  |  |  | 2021-06-13 21:50 |  | 0 | 0 | 21.233 | 21.2333 | 8748.134 | 1 |  |  |  | 0 |  |  | 455
|  | CAUSE CODE : |  | 1100 |  |  | - |  | Waterwall (Furnace wall) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F540Water wall boiler leak B corner
BR3 | 25 | U1 | 2021-08-06 06:36 |  |  |  |  | 2021-08-07 01:48 |  | 0 | 0 | 19.2 | 19.2 | 7910.4 | 1 |  |  |  | 0 |  |  | 455
|  | CAUSE CODE : |  | 0830 |  |  | - |  | Doors | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F540Mud drum gasket door blow out
BR3 | 26 | U1 | 2021-08-08 00:22 |  |  |  |  | 2021-08-08 19:12 |  | 0 | 0 | 18.833 | 18.8333 | 7759.333 | 1 |  |  |  | 0 |  |  | 455
|  | CAUSE CODE : |  | 4293 |  |  | - |  | Hydraulic system pipes and valves | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F540eh leak on drain valve
BR3 | 2 | U1 | 2022-02-03 21:24 |  |  |  |  | 2022-02-04 15:03 |  | 0 | 0 | 17.65 | 17.65 | 7342.4 | 1 |  |  |  | 0 |  |  | 456
|  | CAUSE CODE : |  | 3621 |  |  | - |  | Unit auxiliaries transformer | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Tripped due to loss of A Aux Transformer. 86U Lock out trip mechanism.
BR3 | 14 | U1 | 2022-05-02 14:14 |  |  |  |  | 2022-05-04 13:59 |  | 0 | 0 | 47.75 | 47.75 | 19768.5 | 1 |  |  |  | 0 |  |  | 455.5
|  | CAUSE CODE : |  | 0741 |  |  | - |  | Boiler recirculation pumps - motors | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F780Replace 3-4 BCWP, Unable to run on two Bcwp's.
BR3 | 19 | U1 | 2022-06-16 02:23 |  |  |  |  | 2022-06-16 10:10 |  | 0 | 0 | 7.783 | 7.7833 | 3206.733 | 1 |  |  |  | 0 |  |  | 455
|  | CAUSE CODE : |  | 3619 |  |  | - |  | Other switchyard equipment - external (OMC) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F060Insulator failed in west cliff sub station causing loss of A res feed
BR3 | 28 | U1 | 2022-09-26 10:50 |  |  |  |  | 2022-09-28 18:32 |  | 0 | 0 | 55.7 | 55.7 | 23059.8 | 1 |  |  |  | 0 |  |  | 455.5
|  | CAUSE CODE : |  | 1000 |  |  | - |  | Waterwall (Furnace wall) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F540Water wall boiler leak lower slope sidewall interface
BR3 | 39 | U1 | 2022-12-25 21:15 |  |  |  |  | 2023-01-01 |  | 0 | 0 | 146.75 | 146.75 | 61048 | 1 |  |  |  | 0 |  |  | 456
|  | CAUSE CODE : |  | 0920 |  |  | - |  | Other slag and ash removal problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F120Boiler pluggage. Unable to keep unit online.
BR3 | 1 | U1 | 2023-01-01 |  |  |  |  | 2023-01-06 10:45 |  | 0 | 0 | 130.75 | 130.75 | 54392 | 1 |  |  |  | 0 |  |  | 456
|  | CAUSE CODE : |  | 0920 |  |  | - |  | Other slag and ash removal problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F120Boiler pluggage. Unable to keep unit online.
BR3 | 2 | U1 | 2023-01-08 21:08 |  |  |  |  | 2023-01-10 13:23 |  | 0 | 0 | 40.25 | 40.25 | 16744 | 1 |  |  |  | 0 |  |  | 456
|  | CAUSE CODE : |  | 1090 |  |  | - |  | Other boiler tube leaks | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F540Boiler tube leak around IK 8 and IK 18
BR3 | 6 | U1 | 2023-01-21 03:53 |  |  |  |  | 2023-01-22 00:30 |  | 0 | 0 | 20.617 | 20.6167 | 8576.533 | 1 |  |  |  | 0 |  |  | 456
|  | CAUSE CODE : |  | 0830 |  |  | - |  | Doors | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F540Mud drum door gasket issues.
BR3 | 7 | U1 | 2023-01-22 11:22 |  |  |  |  | 2023-01-26 09:58 |  | 0 | 0 | 94.6 | 94.6 | 39353.6 | 1 |  |  |  | 0 |  |  | 456
|  | CAUSE CODE : |  | 3122 |  |  | - |  | Gaskets and seals | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F540Mud drum door gasket blew out.
BR3 | 9 | U1 | 2023-02-01 21:16 |  |  |  |  | 2023-02-03 17:43 |  | 0 | 0 | 44.45 | 44.45 | 18491.201 | 1 |  |  |  | 0 |  |  | 456
|  | CAUSE CODE : |  | 0740 |  |  | - |  | Boiler recirculation pumps | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F6903-1,3-3,3-4 BCWP not available
BR3 | 22 | SF | 2023-05-21 18:05 |  |  |  |  | 2023-05-22 23:21 |  | 0 | 0 | 29.267 | 29.2667 | 12116.4 | 1 |  |  |  | 0 |  |  | 455.5
|  | CAUSE CODE : |  | 1060 |  |  | - |  | First reheater | [8 empty] | AMP CODE: |  | 54
|  | DESCRIPTION : |  | F540Unable to hold vacuum to roll due to high cond air leakage from reheat tube leak.
BR3 | 23 | SF | 2023-05-22 23:21 |  |  |  |  | 2023-05-26 08:25 |  | 0 | 0 | 81.067 | 81.0667 | 33561.6 | 1 |  |  |  | 0 |  |  | 455.5
|  | CAUSE CODE : |  | 1060 |  |  | - |  | First reheater | [8 empty] | AMP CODE: |  | 54
|  | DESCRIPTION : |  | F540Still have RH leaks causing cond vac issues on startup.
BR3 | 24 | U1 | 2023-05-27 18:44 |  |  |  |  | 2023-06-03 07:36 |  | 0 | 0 | 156.867 | 156.8667 | 64831.6 | 1 |  |  |  | 0 |  |  | 455.5
|  | CAUSE CODE : |  | 1060 |  |  | - |  | First reheater | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F540RH tube leaks
BR3 | 25 | U1 | 2023-06-19 04:39 |  |  |  |  | 2023-06-20 15:21 |  | 0 | 0 | 34.7 | 34.7 | 14296.4 | 1 |  |  |  | 0 |  |  | 455
|  | CAUSE CODE : |  | 1000 |  |  | - |  | Waterwall (Furnace wall) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F540Waterwall tube leaks, dead air space B corner leak,
BR3 | 41 | SF | 2023-12-14 11:00 |  |  |  |  | 2023-12-16 10:45 |  | 0 | 0 | 47.75 | 47.75 | 19864 | 1 |  |  |  | 0 |  |  | 456
|  | CAUSE CODE : |  | 8100 |  |  | - |  | Scrubber/absorber tower or module | [8 empty] | AMP CODE: |  | 54
|  | DESCRIPTION : |  | F540Foam event in scrubber vessel that resulted in inlet duct work filling with slurry
BR3 | 42 | SF | 2023-12-16 10:45 |  |  |  |  | 2023-12-17 06:30 |  | 0 | 0 | 19.75 | 19.75 | 8216 | 1 |  |  |  | 0 |  |  | 456
|  | CAUSE CODE : |  | 8100 |  |  | - |  | Scrubber/absorber tower or module | [8 empty] | AMP CODE: |  | 54
|  | DESCRIPTION : |  | F540Foam event in scrubber vessel that resulted in inlet duct work filling with slurry
Brown - BR5
Unit | Event | Type | Start |  |  |  |  | End |  | GAC | NAC | Duration | Equiv Hrs | Equiv MWH | Cont | Work Start | Work End |  | Hours |  |  | Gross Capacity Impact (MW)
BR5 | 2 | U1 | 2014-01-06 08:23 |  |  |  |  | 2014-01-06 11:47 |  | 0 | 0 | 3.4 | 3.4 | 442 | 1 |  |  |  | 0 |  |  | 131
|  | CAUSE CODE : |  | 5054 |  |  | - |  | Water injection system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F480Instrument measuring DP across water injection control started to freeze. Operato
BR5 | 36 | SF | 2014-08-06 12:00 |  |  |  |  | 2014-08-07 11:25 |  | 0 | 0 | 23.417 | 23.4167 | 2622.667 | 1 |  |  |  | 0 |  |  | 131
|  | CAUSE CODE : |  | 5050 |  |  | - |  | Ignition system | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Grounded spark plug
BR5 | 39 | U1 | 2014-08-26 06:08 |  |  |  |  | 2014-08-26 14:38 |  | 0 | 0 | 8.5 | 8.5 | 952 | 1 |  |  |  | 0 |  |  | 131
|  | CAUSE CODE : |  | 3612 |  |  | - |  | Switchyard system protection devices - external (OMC) | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410On inrush, transformer differential 87T tripped in substation
BR5 | 41 | U1 | 2014-09-30 23:37 |  |  |  |  | 2014-10-01 00:11 |  | 0 | 0 | 0.567 | 0.5667 | 66.766 | 1 |  |  |  | 0 |  |  | 121
|  | CAUSE CODE : |  | 5049 |  |  | - |  | Other fuel system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F410Gas detector fault tripped unit.
BR5 | 19 | SF | 2015-02-14 16:48 |  |  |  |  | 2015-02-14 17:07 |  | 0 | 0 | 0.317 | 0.3167 | 41.167 | 1 |  |  |  | 0 |  |  | 131
|  | CAUSE CODE : |  | 5550 |  |  | - |  | Turning gear and motor | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Rotor barring failure
BR5 | 35 | U1 | 2015-03-06 09:15 |  |  |  |  | 2015-03-06 14:07 |  | 0 | 0 | 4.867 | 4.8667 | 632.667 | 1 |  |  |  | 0 |  |  | 121
|  | CAUSE CODE : |  | 3869 |  |  | - |  | Other fire protection system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F410Gas detection system false signal caused trip
BR5 | 44 | SF | 2015-03-30 05:19 |  |  |  |  | 2015-03-30 06:30 |  | 0 | 0 | 1.183 | 1.1833 | 153.833 | 1 |  |  |  | 0 |  |  | 121
|  | CAUSE CODE : |  | 5246 |  |  | - |  | Gas Turbine Control System - hardware problems (including card failure) | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Proximitor amplifier on speed channel failed
BR5 | 72 | U1 | 2015-05-13 14:37 |  |  |  |  | 2015-05-13 15:38 |  | 0 | 0 | 1.017 | 1.0167 | 113.867 | 1 |  |  |  | 0 |  |  | 121
|  | CAUSE CODE : |  | 4810 |  |  | - |  | Generator output breaker | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F410Outage to trouble shoot generator circuit breaker low spring energy alarm.
BR5 | 111 | SF | 2015-07-18 12:40 |  |  |  |  | 2015-07-18 16:23 |  | 0 | 0 | 3.717 | 3.7167 | 483.167 | 1 |  |  |  | 0 |  |  | 131
|  | CAUSE CODE : |  | 5050 |  |  | - |  | Ignition system | [8 empty] | AMP CODE: |  | 55
|  | DESCRIPTION : |  | F550Issue with propane pressure regulator. Regulator setpoint was low by 15 PSI.
BR5 | 119 | SF | 2015-08-08 12:06 |  |  |  |  | 2015-08-08 13:04 |  | 0 | 0 | 0.967 | 0.9667 | 125.667 | 1 |  |  |  | 0 |  |  | 131
|  | CAUSE CODE : |  | 5050 |  |  | - |  | Ignition system | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Unit would not light off during start up.
BR5 | 123 | U1 | 2015-08-13 07:59 |  |  |  |  | 2015-08-13 14:03 |  | 0 | 0 | 6.067 | 6.0667 | 788.667 | 1 |  |  |  | 0 |  |  | 131
|  | CAUSE CODE : |  | 5450 |  |  | - |  | Ignition system | [8 empty] | AMP CODE: |  | 40
|  | DESCRIPTION : |  | F400FO to troubleshoot propane ignition torch.
BR5 | 130 | SF | 2015-09-02 11:01 |  |  |  |  | 2015-09-02 11:29 |  | 0 | 0 | 0.467 | 0.4667 | 60.667 | 1 |  |  |  | 0 |  |  | 121
|  | CAUSE CODE : |  | 5530 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Overcurrent trip on static frequency converter.
BR5 | 137 | SF | 2015-10-19 05:32 |  |  |  |  | 2015-10-19 06:31 |  | 0 | 0 | 0.983 | 0.9833 | 127.833 | 1 |  |  |  | 0 |  |  | 121
|  | CAUSE CODE : |  | 5414 |  |  | - |  | Compressor diaphragms/vanes | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Failed ATOS card on the compressor blow off valves.
BR5 | 144 | SF | 2015-11-24 06:00 |  |  |  |  | 2015-11-24 10:16 |  | 0 | 0 | 4.267 | 4.2667 | 554.667 | 1 |  |  |  | 0 |  |  | 121
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410SFC Controller locked up during startup
BR5 | 146 | U1 | 2015-11-25 09:16 |  |  |  |  | 2015-11-25 10:15 |  | 0 | 0 | 0.983 | 0.9833 | 127.833 | 1 |  |  |  | 0 |  |  | 121
|  | CAUSE CODE : |  | 5640 |  |  | - |  | Fire detection and extinguishing system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F410False gas alarm signal caused unit to trip off line
BR5 | 3 | U1 | 2016-01-10 19:31 |  |  |  |  | 2016-01-10 23:01 |  | 0 | 0 | 3.5 | 3.5 | 455 | 1 |  |  |  | 0 |  |  | 131
|  | CAUSE CODE : |  | 5401 |  |  | - |  | Inlet air vanes/nozzles | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410VIGV pos alarms kept unit from rolling up.
BR5 | 5 | U1 | 2016-01-11 01:55 |  |  |  |  | 2016-01-11 05:56 |  | 0 | 0 | 4.017 | 4.0167 | 522.167 | 1 |  |  |  | 0 |  |  | 131
|  | CAUSE CODE : |  | 5170 |  |  | - |  | Cooling water system | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Cooling water pump tripping 480V breaker
BR5 | 7 | U1 | 2016-01-12 18:16 |  |  |  |  | 2016-01-12 19:06 |  | 0 | 0 | 0.833 | 0.8333 | 108.333 | 1 |  |  |  | 0 |  |  | 131
|  | CAUSE CODE : |  | 5401 |  |  | - |  | Inlet air vanes/nozzles | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F410Unit tripped due to Atos card on R3 guide vanes.
BR5 | 8 | U1 | 2016-01-12 19:24 |  |  |  |  | 2016-01-12 22:28 |  | 0 | 0 | 3.067 | 3.0667 | 398.667 | 1 |  |  |  | 0 |  |  | 131
|  | CAUSE CODE : |  | 5401 |  |  | - |  | Inlet air vanes/nozzles | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F410Unit tripped due to failure of R3 Atos card on inlet guide vanes.
BR5 | 33 | SF | 2016-05-27 13:26 |  |  |  |  | 2016-05-27 14:47 |  | 0 | 0 | 1.35 | 1.35 | 162 | 1 |  |  |  | 0 |  |  | 121
|  | CAUSE CODE : |  | 5530 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Unit tripped due to SFC temperature alarm and acceleration alarm.
BR5 | 41 | U1 | 2016-06-15 11:09 |  |  |  |  | 2016-06-15 11:49 |  | 0 | 0 | 0.667 | 0.6667 | 86.667 | 1 |  |  |  | 0 |  |  | 131
|  | CAUSE CODE : |  | 5001 |  |  | - |  | Inlet air vanes/nozzles | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Inlet guide vane malfunction
BR5 | 43 | U1 | 2016-06-16 10:52 |  |  |  |  | 2016-06-16 12:19 |  | 0 | 0 | 1.45 | 1.45 | 188.5 | 1 |  |  |  | 0 |  |  | 131
|  | CAUSE CODE : |  | 5001 |  |  | - |  | Inlet air vanes/nozzles | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F820Inlet guide vane issues
BR5 | 49 | U1 | 2016-06-22 13:16 |  |  |  |  | 2016-06-22 16:22 |  | 0 | 0 | 3.1 | 3.1 | 403 | 1 |  |  |  | 0 |  |  | 131
|  | CAUSE CODE : |  | 5414 |  |  | - |  | Compressor diaphragms/vanes | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Unit tripped shortly after going online due to variable inlet guide vanes.
BR5 | 54 | U1 | 2016-06-26 15:44 |  |  |  |  | 2016-06-26 16:01 |  | 0 | 0 | 0.283 | 0.2833 | 36.833 | 1 |  |  |  | 0 |  |  | 131
|  | CAUSE CODE : |  | 9020 |  |  | - |  | Lightning | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F410Gas valves in reducing station closed due to lightning strike.
BR5 | 62 | SF | 2016-08-25 13:18 |  |  |  |  | 2016-08-25 14:56 |  | 0 | 0 | 1.633 | 1.6333 | 212.333 | 1 |  |  |  | 0 |  |  | 131
|  | CAUSE CODE : |  | 5017 |  |  | - |  | Low pressure compressor bleed valves | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Bad I/O control card failed to close the compressor blow off valve. Unit tripped a
BR5 | 66 | U1 | 2016-09-07 22:00 |  |  |  |  | 2016-09-07 22:43 |  | 0 | 0 | 0.717 | 0.7167 | 86 | 1 |  |  |  | 0 |  |  | 121
|  | CAUSE CODE : |  | 3971 |  |  | - |  | DCS - data highway | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410DCS LAN went down causing 11N2 system to lose communication.
BR5 | 9 | U1 | 2017-03-18 16:24 |  |  |  |  | 2017-03-19 07:13 |  | 0 | 0 | 14.817 | 14.8167 | 1778 | 1 |  |  |  | 0 |  |  | 121
|  | CAUSE CODE : |  | 3972 |  |  | - |  | DCS - hardware problems (including card failure) | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Lost communication to Bently Nevada vibration system.
BR5 | 14 | U1 | 2017-05-25 17:58 |  |  |  |  | 2017-05-25 20:00 |  | 0 | 0 | 2.033 | 2.0333 | 244 | 1 |  |  |  | 0 |  |  | 121
|  | CAUSE CODE : |  | 5110 |  |  | - |  | Lube oil system - general | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Failed contactor on jacking oil pump motor.
BR5 | 17 | SF | 2017-07-11 11:15 |  |  |  |  | 2017-07-11 13:20 |  | 0 | 0 | 2.083 | 2.0833 | 270.833 | 1 |  |  |  | 0 |  |  | 131
|  | CAUSE CODE : |  | 5050 |  |  | - |  | Ignition system | [8 empty] | AMP CODE: |  | 66
|  | DESCRIPTION : |  | F660Unit did not light off.
BR5 | 24 | SF | 2017-07-21 11:06 |  |  |  |  | 2017-07-21 11:24 |  | 0 | 0 | 0.3 | 0.3 | 39 | 1 |  |  |  | 0 |  |  | 131
|  | CAUSE CODE : |  | 5110 |  |  | - |  | Lube oil system - general | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Unit was not seeing rotor barring on. Looks to be issue with speed signal. Had t
BR5 | 29 | U1 | 2017-09-08 08:36 |  |  |  |  | 2017-09-08 13:57 |  | 0 | 0 | 5.35 | 5.35 | 642 | 1 |  |  |  | 0 |  |  | 121
|  | CAUSE CODE : |  | 3612 |  |  | - |  | Switchyard system protection devices - external (OMC) | [8 empty] | AMP CODE: |  | X0
|  | DESCRIPTION : |  | FX00Brown North Substation Protection Disabled.
BR5 | 36 | U1 | 2017-11-20 08:48 |  |  |  |  | 2017-11-20 13:30 |  | 0 | 0 | 4.7 | 4.7 | 564 | 1 |  |  |  | 0 |  |  | 121
|  | CAUSE CODE : |  | 5250 |  |  | - |  | Other controls and instrumentation problems | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Issue with enclosure fan control system.
BR5 | 38 | U1 | 2017-11-27 05:37 |  |  |  |  | 2017-11-27 13:40 |  | 0 | 0 | 8.05 | 8.05 | 966 | 1 |  |  |  | 0 |  |  | 121
|  | CAUSE CODE : |  | 5048 |  |  | - |  | Gas fuel system including controls and instrumentation | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F410Gas pressure swinging caused VGV Ref / Act pls.
BR5 | 42 | U1 | 2017-12-26 04:55 |  |  |  |  | 2017-12-26 11:11 |  | 0 | 0 | 6.267 | 6.2667 | 814.667 | 1 |  |  |  | 0 |  |  | 131
|  | CAUSE CODE : |  | 5115 |  |  | - |  | Oil vapor extractor | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Fuse blown on IO card feeding vapor extractor contactor.
BR5 | 44 | SF | 2017-12-27 04:01 |  |  |  |  | 2017-12-27 10:40 |  | 0 | 0 | 6.65 | 6.65 | 864.5 | 1 |  |  |  | 0 |  |  | 131
|  | CAUSE CODE : |  | 5170 |  |  | - |  | Cooling water system | [8 empty] | AMP CODE: |  | 66
|  | DESCRIPTION : |  | F660Low cooling water pressure prevented system from starting.
BR5 | 2 | SF | 2018-01-02 07:58 |  |  |  |  | 2018-01-02 08:58 |  | 0 | 0 | 1 | 1 | 130 | 1 |  |  |  | 0 |  |  | 131
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 69
|  | DESCRIPTION : |  | F690Medium voltage breaker feeding SFC would not charge.
BR5 | 5 | U1 | 2018-01-08 13:22 |  |  |  |  | 2018-01-08 15:52 |  | 0 | 0 | 2.5 | 2.5 | 325 | 1 |  |  |  | 0 |  |  | 131
|  | CAUSE CODE : |  | 7920 |  |  | - |  | Lube oil system | [8 empty] | AMP CODE: |  | 54
|  | DESCRIPTION : |  | F540Leak on rotor barring piston connection.
BR5 | 13 | U1 | 2018-03-04 20:44 |  |  |  |  | 2018-03-23 12:53 |  | 0 | 0 | 448.15 | 448.15 | 53778 | 1 |  |  |  | 0 |  |  | 121
|  | CAUSE CODE : |  | 5530 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Failure of PSR2 controls on SFC.
BR5 | 29 | U1 | 2018-05-20 13:32 |  |  |  |  | 2018-05-20 14:13 |  | 0 | 0 | 0.683 | 0.6833 | 82 | 1 |  |  |  | 0 |  |  | 121
|  | CAUSE CODE : |  | 3972 |  |  | - |  | DCS - hardware problems (including card failure) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F410Failure of siesmic vibration probe. Unhooked probe.
BR5 | 40 | SF | 2018-06-12 10:16 |  |  |  |  | 2018-06-12 11:30 |  | 0 | 0 | 1.233 | 1.2333 | 160.333 | 1 |  |  |  | 0 |  |  | 131
|  | CAUSE CODE : |  | 7930 |  |  | - |  | Controls and instrumentation | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Bad P&F transmitter for bearing No1 metal temp. Replaced P&F transmitter.
BR5 | 63 | SF | 2018-07-11 12:05 |  |  |  |  | 2018-07-11 15:35 |  | 0 | 0 | 3.5 | 3.5 | 455 | 1 |  |  |  | 0 |  |  | 131
|  | CAUSE CODE : |  | 5050 |  |  | - |  | Ignition system | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Unit tripped while accellerating to 3600 RPMs. Then unit would not light off. C
BR5 | 84 | U1 | 2018-08-23 19:00 |  |  |  |  | 2018-08-24 13:33 |  | 0 | 0 | 18.55 | 18.55 | 2411.5 | 1 |  |  |  | 0 |  |  | 131
|  | CAUSE CODE : |  | 5111 |  |  | - |  | Lube oil pumps | [8 empty] | AMP CODE: |  | 62
|  | DESCRIPTION : |  | F620Emergency DC lube oil pump failed. Motor had to be replaced.
BR5 | 106 | SF | 2018-10-02 11:44 |  |  |  |  | 2018-10-02 12:03 |  | 0 | 0 | 0.317 | 0.3167 | 38 | 1 |  |  |  | 0 |  |  | 121
|  | CAUSE CODE : |  | 5073 |  |  | - |  | Flame scanners | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Moisture in flame scanner head prevented unit from showing flame on.
BR5 | 112 | U1 | 2018-10-07 17:34 |  |  |  |  | 2018-10-07 18:52 |  | 0 | 0 | 1.3 | 1.3 | 156 | 1 |  |  |  | 0 |  |  | 121
|  | CAUSE CODE : |  | 3621 |  |  | - |  | Unit auxiliaries transformer | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F030Ligthning arrestor on BOP north transformer went to ground. Substation Crew did f
BR5 | 118 | SF | 2018-10-18 04:43 |  |  |  |  | 2018-10-18 05:28 |  | 0 | 0 | 0.75 | 0.75 | 90 | 1 |  |  |  | 0 |  |  | 121
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 64
|  | DESCRIPTION : |  | F640Overcurrent on starting device. TAT release temperature held unit out from an imm
BR5 | 120 | U1 | 2018-10-23 09:22 |  |  |  |  | 2018-10-24 17:04 |  | 0 | 0 | 31.7 | 31.7 | 3804 | 1 |  |  |  | 0 |  |  | 121
|  | CAUSE CODE : |  | 5150 |  |  | - |  | Turning gear and motor | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Rotor barring pump motor burned up. Replaced pump and motor to previous system.
BR5 | 3 | SF | 2019-01-20 09:42 |  |  |  |  | 2019-01-20 09:58 |  | 0 | 0 | 0.267 | 0.2667 | 34.667 | 1 |  |  |  | 0 |  |  | 131
|  | CAUSE CODE : |  | 5050 |  |  | - |  | Ignition system | [8 empty] | AMP CODE: |  | 72
|  | DESCRIPTION : |  | F720Flame trip due to failure to light off.
BR5 | 12 | SF | 2019-04-02 04:20 |  |  |  |  | 2019-04-02 04:49 |  | 0 | 0 | 0.483 | 0.4833 | 58 | 1 |  |  |  | 0 |  |  | 121
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Failed start due to trip of SFC at 2200 RPM. Fix was to start Unit 6 then try Uni
BR5 | 25 | SF | 2019-05-17 11:10 |  |  |  |  | 2019-05-17 12:28 |  | 0 | 0 | 1.3 | 1.3 | 156 | 1 |  |  |  | 0 |  |  | 121
|  | CAUSE CODE : |  | 5450 |  |  | - |  | Ignition system | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Unit would not light off. Investigation ongoing. Did change out all propane syst
BR5 | 33 | U1 | 2019-06-27 00:20 |  |  |  |  | 2019-06-27 02:30 |  | 0 | 0 | 2.167 | 2.1667 | 281.667 | 1 |  |  |  | 0 |  |  | 131
|  | CAUSE CODE : |  | 5120 |  |  | - |  | Hydraulic oil system | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Rotor Barring would not work. Had to reset manually.
BR5 | 72 | SF | 2019-11-04 06:26 |  |  |  |  | 2019-11-04 10:26 |  | 0 | 0 | 4 | 4 | 480 | 1 |  |  |  | 0 |  |  | 121
|  | CAUSE CODE : |  | 5640 |  |  | - |  | Fire detection and extinguishing system | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Loose wire in combustor emergency trip pushbutton station. Retightened wire.
BR5 | 74 | U1 | 2019-11-04 11:54 |  |  |  |  | 2019-11-04 14:29 |  | 0 | 0 | 2.583 | 2.5833 | 310 | 1 |  |  |  | 0 |  |  | 121
|  | CAUSE CODE : |  | 4810 |  |  | - |  | Generator output breaker | [8 empty] | AMP CODE: |  | 66
|  | DESCRIPTION : |  | F660Low SF6 gas for generator circuit breaker. Substation crew came out to add.
BR5 | 76 | SF | 2019-11-06 05:25 |  |  |  |  | 2019-11-06 08:55 |  | 0 | 0 | 3.5 | 3.5 | 420 | 1 |  |  |  | 0 |  |  | 121
|  | CAUSE CODE : |  | 3974 |  |  | - |  | DCS - logic problems | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Stuck in start up sequence. Potentially low glycol pressure.
BR5 | 5 | SF | 2020-02-14 08:13 |  |  |  |  | 2020-02-14 14:17 |  | 0 | 0 | 6.067 | 6.0667 | 788.667 | 1 |  |  |  | 0 |  |  | 131
|  | CAUSE CODE : |  | 5170 |  |  | - |  | Cooling water system | [8 empty] | AMP CODE: |  | 19
|  | DESCRIPTION : |  | F190Low cooling water pressue upon cooling fan startup prevented unit from starting.
BR5 | 7 | SF | 2020-02-27 06:00 |  |  |  |  | 2020-02-27 06:07 |  | 0 | 0 | 0.117 | 0.1167 | 15.167 | 1 |  |  |  | 0 |  |  | 131
|  | CAUSE CODE : |  | 5450 |  |  | - |  | Ignition system | [8 empty] | AMP CODE: |  | 40
|  | DESCRIPTION : |  | F400Flame trip at ignition.
BR5 | 9 | U1 | 2020-03-10 17:58 |  |  |  |  | 2020-03-11 16:24 |  | 0 | 0 | 22.433 | 22.4333 | 2692 | 1 |  |  |  | 0 |  |  | 121
|  | CAUSE CODE : |  | 5050 |  |  | - |  | Ignition system | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Failed to light off. Pulled nozzle and tested propane system outside of unit. Ch
BR5 | 17 | SF | 2020-05-27 09:15 |  |  |  |  | 2020-06-04 18:18 |  | 0 | 0 | 201.05 | 201.05 | 25029 | 1 |  |  |  | 0 |  |  | 121
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410SFC failure upon start up. T49 Trip Converter overexcitation.ABB coming to site
BR5 | 4 | SF | 2021-02-15 08:17 |  |  |  |  | 2021-02-15 10:02 |  | 0 | 0 | 1.75 | 1.75 | 227.5 | 1 |  |  |  | 0 |  |  | 131
|  | CAUSE CODE : |  | 4609 |  |  | - |  | Other exciter problems | [8 empty] | AMP CODE: |  | P0
|  | DESCRIPTION : |  | FP00AVR tourbleshooting week of 2/1 caused a relay to operate. Personnel did not notic
BR5 | 21 | U1 | 2021-07-16 09:44 |  |  |  |  | 2021-07-20 10:30 |  | 0 | 0 | 96.767 | 96.7667 | 12579.667 | 1 |  |  |  | 0 |  |  | 131
|  | CAUSE CODE : |  | 3974 |  |  | - |  | DCS - logic problems | [8 empty] | AMP CODE: |  | 40
|  | DESCRIPTION : |  | F400Unit will trip off line once generator is sync'd due to controls not loading unit.
BR5 | 22 | U2 | 2021-07-20 18:07 |  |  |  |  | 2021-07-23 15:26 |  | 0 | 0 | 69.317 | 69.3167 | 9011.166 | 1 |  |  |  | 0 |  |  | 131
|  | CAUSE CODE : |  | 4730 |  |  | - |  | Generator current and potential transformers | [8 empty] | AMP CODE: |  | 70
|  | DESCRIPTION : |  | F700Terminal block for CT wiring failed, resulting in an arc and damaging CT wiring wh
BR5 | 40 | U1 | 2021-11-04 06:38 |  |  |  |  | 2021-11-04 07:13 |  | 0 | 0 | 0.583 | 0.5833 | 70 | 1 |  |  |  | 0 |  |  | 121
|  | CAUSE CODE : |  | 5041 |  |  | - |  | Fuel piping and valves | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F480Pilot valves for reducing station control valves were froze and inoperable.
BR5 | 12 | U1 | 2022-05-11 17:50 |  |  |  |  | 2022-05-11 22:38 |  | 0 | 0 | 4.8 | 4.8 | 576 | 1 |  |  |  | 0 |  |  | 121
|  | CAUSE CODE : |  | 3972 |  |  | - |  | DCS - hardware problems (including card failure) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820ATOS card failure caused blowoff vales to go open and tripped unit.
BR5 | 23 | U1 | 2022-07-11 17:01 |  |  |  |  | 2022-07-13 12:52 |  | 0 | 0 | 43.85 | 43.85 | 5700.5 | 1 |  |  |  | 0 |  |  | 131
|  | CAUSE CODE : |  | 4750 |  |  | - |  | Other generator controls and metering problems | [8 empty] | AMP CODE: |  | 70
|  | DESCRIPTION : |  | F700Malfunctioning generator protection relay.
BR5 | 36 | SF | 2022-08-19 11:47 |  |  |  |  | 2022-08-19 16:20 |  | 0 | 0 | 4.55 | 4.55 | 591.5 | 1 |  |  |  | 0 |  |  | 131
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 40
|  | DESCRIPTION : |  | F400SFC malfunction. Unknown alarm coming in in the control cabinet but not on displa
BR5 | 55 | U1 | 2022-12-23 01:28 |  |  |  |  | 2022-12-23 17:22 |  | 0 | 0 | 15.9 | 15.9 | 2067 | 1 |  |  |  | 0 |  |  | 131
|  | CAUSE CODE : |  | 5041 |  |  | - |  | Fuel piping and valves | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F480Fuel valves froze after valve heaters to 11N2 units were blown out.
BR5 | 8 | U1 | 2023-06-01 16:19 |  |  |  |  | 2023-06-01 16:41 |  | 0 | 0 | 0.367 | 0.3667 | 47.667 | 1 |  |  |  | 0 |  |  | 131
|  | CAUSE CODE : |  | 5250 |  |  | - |  | Other controls and instrumentation problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Unit tripped on TAT spread due to bad thermal couple reading.
BR5 | 9 | U1 | 2023-06-01 18:41 |  |  |  |  | 2023-06-01 18:50 |  | 0 | 0 | 0.15 | 0.15 | 19.5 | 1 |  |  |  | 0 |  |  | 131
|  | CAUSE CODE : |  | 5250 |  |  | - |  | Other controls and instrumentation problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Unit tripped on TAT spread due to bad thermal couple reading.
Brown - BR6
Unit | Event | Type | Start |  |  |  |  | End |  | GAC | NAC | Duration | Equiv Hrs | Equiv MWH | Cont | Work Start | Work End |  | Hours |  |  | Gross Capacity Impact (MW)
BR6 | 2 | SF | 2014-01-02 16:13 |  |  |  |  | 2014-01-02 17:03 |  | 0 | 0 | 0.833 | 0.8333 | 142.5 | 1 |  |  |  | 0 |  |  | 172
|  | CAUSE CODE : |  | 4810 |  |  | - |  | Generator output breaker | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Generator circuit breaker loss of 120VAC control power prevented the unit from sta
BR6 | 7 | U1 | 2014-01-23 13:31 |  |  |  |  | 2014-01-23 14:49 |  | 0 | 0 | 1.3 | 1.3 | 222.3 | 1 |  |  |  | 0 |  |  | 172
|  | CAUSE CODE : |  | 5109 |  |  | - |  | Other exhaust problems (including high exhaust system temperature not attributable to a specific problem) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F410Loss TC on TAT2 readings. TC reading was coming in and out of service that caused
BR6 | 18 | U1 | 2014-03-05 13:12 |  |  |  |  | 2014-03-05 14:45 |  | 0 | 0 | 1.55 | 1.55 | 265.05 | 1 |  |  |  | 0 |  |  | 158
|  | CAUSE CODE : |  | 5160 |  |  | - |  | Cooling and seal air system | [8 empty] | AMP CODE: |  | 54
|  | DESCRIPTION : |  | F540Leak on water injection lance on HP quench vessel.
BR6 | 21 | U1 | 2014-03-13 08:59 |  |  |  |  | 2014-03-14 17:25 |  | 0 | 0 | 32.433 | 32.4333 | 5546.1 | 1 |  |  |  | 0 |  |  | 158
|  | CAUSE CODE : |  | 5160 |  |  | - |  | Cooling and seal air system | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F540Air Leak on HP quench cooler.
BR6 | 35 | U1 | 2014-04-23 15:10 |  |  |  |  | 2014-04-23 15:59 |  | 0 | 0 | 0.817 | 0.8167 | 119.233 | 1 |  |  |  | 0 |  |  | 158
|  | CAUSE CODE : |  | 5049 |  |  | - |  | Other fuel system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F420Operator closed inlet valve to gas heater without opening by-pass valve
BR6 | 66 | SF | 2014-06-18 09:48 |  |  |  |  | 2014-06-18 10:06 |  | 0 | 0 | 0.3 | 0.3 | 43.8 | 1 |  |  |  | 0 |  |  | 147
|  | CAUSE CODE : |  | 5050 |  |  | - |  | Ignition system | [8 empty] | AMP CODE: |  | 78
|  | DESCRIPTION : |  | F780Unit failed to light off.
BR6 | 73 | U1 | 2014-07-07 09:47 |  |  |  |  | 2014-07-07 11:17 |  | 0 | 0 | 1.5 | 1.5 | 219 | 1 |  |  |  | 0 |  |  | 147
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 59
|  | DESCRIPTION : |  | F590Medium Voltage Breaker failed to close on starting device while starting up CT7. C
BR6 | 112 | U1 | 2014-10-02 09:18 |  |  |  |  | 2014-10-02 09:52 |  | 0 | 0 | 0.567 | 0.5667 | 96.9 | 1 |  |  |  | 0 |  |  | 158
|  | CAUSE CODE : |  | 5248 |  |  | - |  | Gas Turbine Control System - logic problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F460Implementing new operation concept. Unit tripped after switchover.
BR6 | 113 | U1 | 2014-10-02 09:56 |  |  |  |  | 2014-10-02 11:46 |  | 0 | 0 | 1.833 | 1.8333 | 313.5 | 1 |  |  |  | 0 |  |  | 158
|  | CAUSE CODE : |  | 5248 |  |  | - |  | Gas Turbine Control System - logic problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F460Implementing new operations concept. Unit tripped after switchover.
BR6 | 131 | U1 | 2014-12-04 06:47 |  |  |  |  | 2014-12-04 07:27 |  | 0 | 0 | 0.667 | 0.6667 | 114 | 1 |  |  |  | 0 |  |  | 172
|  | CAUSE CODE : |  | 5049 |  |  | - |  | Other fuel system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F460Reverse Power at HP2. Looks to be PLS caused by high pulsations.
BR6 | 2 | U1 | 2015-01-05 17:23 |  |  |  |  | 2015-01-05 19:22 |  | 0 | 0 | 1.983 | 1.9833 | 339.15 | 1 |  |  |  | 0 |  |  | 172
|  | CAUSE CODE : |  | 9136 |  |  | - |  | Problems with Primary Fuel for Units with Secondary Fuel Operation | [8 empty] | AMP CODE: |  | FR
|  | DESCRIPTION : |  | F750Changes in gas composition caused unit 7 to trip offline.
BR6 | 5 | U1 | 2015-01-26 05:55 |  |  |  |  | 2015-01-26 06:03 |  | 0 | 0 | 0.133 | 0.1333 | 22.8 | 1 |  |  |  | 0 |  |  | 172
|  | CAUSE CODE : |  | 5039 |  |  | - |  | Other compressor problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F410Blow off valve not staying closed while unit is online
BR6 | 6 | U1 | 2015-01-26 06:16 |  |  |  |  | 2015-01-26 09:04 |  | 0 | 0 | 2.8 | 2.8 | 478.8 | 1 |  |  |  | 0 |  |  | 172
|  | CAUSE CODE : |  | 5039 |  |  | - |  | Other compressor problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F410Compressor blow off valve not staying closed while unit online
BR6 | 9 | SF | 2015-01-28 04:51 |  |  |  |  | 2015-01-28 05:13 |  | 0 | 0 | 0.367 | 0.3667 | 62.7 | 1 |  |  |  | 0 |  |  | 172
|  | CAUSE CODE : |  | 5079 |  |  | - |  | Other combustor problems | [8 empty] | AMP CODE: |  | 46
|  | DESCRIPTION : |  | F460Unit would not sync to grid. Multiple attempts tripped GCB on reverse power.
BR6 | 15 | U1 | 2015-02-22 14:29 |  |  |  |  | 2015-02-22 20:13 |  | 0 | 0 | 5.733 | 5.7333 | 980.4 | 1 |  |  |  | 0 |  |  | 172
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Controls processor failed on static starting device.
BR6 | 18 | U1 | 2015-02-26 17:19 |  |  |  |  | 2015-02-26 17:49 |  | 0 | 0 | 0.5 | 0.5 | 85.5 | 1 |  |  |  | 0 |  |  | 172
|  | CAUSE CODE : |  | 5479 |  |  | - |  | Other combustor problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F780Unit could not achieve SEV On.
BR6 | 19 | U1 | 2015-02-26 19:51 |  |  |  |  | 2015-02-27 08:31 |  | 0 | 0 | 12.667 | 12.6667 | 2166 | 1 |  |  |  | 0 |  |  | 172
|  | CAUSE CODE : |  | 5479 |  |  | - |  | Other combustor problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F780Unit could not achieve SEV on.
BR6 | 20 | U1 | 2015-02-27 08:48 |  |  |  |  | 2015-02-27 15:06 |  | 0 | 0 | 6.3 | 6.3 | 1077.3 | 1 |  |  |  | 0 |  |  | 172
|  | CAUSE CODE : |  | 5479 |  |  | - |  | Other combustor problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F780Unit could not initiate SEV on.
BR6 | 4 | U1 | 2016-01-21 03:24 |  |  |  |  | 2016-01-21 07:03 |  | 0 | 0 | 3.65 | 3.65 | 624.15 | 1 |  |  |  | 0 |  |  | 172
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410I/O card failure on static frequency converter
BR6 | 8 | U1 | 2016-02-23 09:08 |  |  |  |  | 2016-02-23 12:22 |  | 0 | 0 | 3.233 | 3.2333 | 552.9 | 1 |  |  |  | 0 |  |  | 172
|  | CAUSE CODE : |  | 5046 |  |  | - |  | Liquid fuel oil transfer/forwarding pump | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F540Leak on Fuel Oil Sump Pump drain tank non return check valve flange.
BR6 | 17 | U1 | 2016-05-11 06:05 |  |  |  |  | 2016-05-11 07:02 |  | 0 | 0 | 0.95 | 0.95 | 149.15 | 1 |  |  |  | 0 |  |  | 158
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410I/O card for SFC controls went bad. Possibly due to lightning storm.
BR6 | 27 | U1 | 2016-07-25 10:56 |  |  |  |  | 2016-07-25 11:35 |  | 0 | 0 | 0.65 | 0.65 | 94.9 | 1 |  |  |  | 0 |  |  | 147
|  | CAUSE CODE : |  | 5079 |  |  | - |  | Other combustor problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F460Trip due to SEV combustor protection. Swing in unit caused the rate of change pre
BR6 | 35 | U1 | 2016-09-07 22:00 |  |  |  |  | 2016-09-07 22:43 |  | 0 | 0 | 0.717 | 0.7167 | 112.517 | 1 |  |  |  | 0 |  |  | 158
|  | CAUSE CODE : |  | 3971 |  |  | - |  | DCS - data highway | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410DCS LAN went down causing 11N2 system to loose communication
BR6 | 44 | U1 | 2016-10-22 13:25 |  |  |  |  | 2016-10-24 14:17 |  | 0 | 0 | 48.867 | 48.8667 | 7672.066 | 1 |  |  |  | 0 |  |  | 158
|  | CAUSE CODE : |  | 4810 |  |  | - |  | Generator output breaker | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F410Forced outage to correct issues caused by check out of sudden load rejection relay
BR6 | 2 | SF | 2017-01-06 05:24 |  |  |  |  | 2017-01-06 07:11 |  | 0 | 0 | 1.783 | 1.7833 | 304.95 | 1 |  |  |  | 0 |  |  | 172
|  | CAUSE CODE : |  | 3624 |  |  | - |  | Auxiliary generator voltage supply system | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Field breaker would not close automatically
BR6 | 28 | U1 | 2017-07-20 10:20 |  |  |  |  | 2017-07-20 10:56 |  | 0 | 0 | 0.6 | 0.6 | 87.6 | 1 |  |  |  | 0 |  |  | 147
|  | CAUSE CODE : |  | 5048 |  |  | - |  | Gas fuel system including controls and instrumentation | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F460Unit tripped due to swing in MWs.
BR6 | 31 | U1 | 2017-09-08 08:36 |  |  |  |  | 2017-09-08 13:57 |  | 0 | 0 | 5.35 | 5.35 | 839.95 | 1 |  |  |  | 0 |  |  | 158
|  | CAUSE CODE : |  | 3612 |  |  | - |  | Switchyard system protection devices - external (OMC) | [8 empty] | AMP CODE: |  | X0
|  | DESCRIPTION : |  | FX00Brown North Substation Protection Disabled.
BR6 | 42 | U1 | 2017-11-06 21:23 |  |  |  |  | 2017-11-07 |  | 0 | 0 | 2.617 | 2.6167 | 410.817 | 1 |  |  |  | 0 |  |  | 158
|  | CAUSE CODE : |  | 5246 |  |  | - |  | Gas Turbine Control System - hardware problems (including card failure) | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410PLC for gas detection system went bad.
BR6 | 46 | SF | 2017-11-20 05:27 |  |  |  |  | 2017-11-21 09:34 |  | 0 | 0 | 28.117 | 28.1167 | 4414.317 | 1 |  |  |  | 0 |  |  | 158
|  | CAUSE CODE : |  | 4700 |  |  | - |  | Generator voltage control | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410AVR fault while trying to sync.
BR6 | 55 | U1 | 2017-12-26 04:50 |  |  |  |  | 2017-12-28 17:31 |  | 0 | 0 | 60.683 | 60.6833 | 10376.85 | 1 |  |  |  | 0 |  |  | 172
|  | CAUSE CODE : |  | 5450 |  |  | - |  | Ignition system | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Outage began with issue with the SFC during U7 start. Then we could not get unit
BR6 | 1 | U1 | 2018-01-02 09:06 |  |  |  |  | 2018-01-02 12:24 |  | 0 | 0 | 3.3 | 3.3 | 564.3 | 1 |  |  |  | 0 |  |  | 172
|  | CAUSE CODE : |  | 5048 |  |  | - |  | Gas fuel system including controls and instrumentation | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F660Low gas line pressure caused unit to start swinging. Unit tripped during deload.
BR6 | 2 | U1 | 2018-01-02 12:53 |  |  |  |  | 2018-01-02 18:40 |  | 0 | 0 | 5.783 | 5.7833 | 988.95 | 1 |  |  |  | 0 |  |  | 172
|  | CAUSE CODE : |  | 5248 |  |  | - |  | Gas Turbine Control System - logic problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F780Unit would not increase load after SEV on.
BR6 | 3 | U1 | 2018-01-02 18:48 |  |  |  |  | 2018-01-02 19:15 |  | 0 | 0 | 0.45 | 0.45 | 76.95 | 1 |  |  |  | 0 |  |  | 172
|  | CAUSE CODE : |  | 5248 |  |  | - |  | Gas Turbine Control System - logic problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F780Unit would not increase load after SEV on.
BR6 | 4 | U1 | 2018-01-02 19:24 |  |  |  |  | 2018-01-03 10:17 |  | 0 | 0 | 14.883 | 14.8833 | 2545.05 | 1 |  |  |  | 0 |  |  | 172
|  | CAUSE CODE : |  | 5248 |  |  | - |  | Gas Turbine Control System - logic problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F780Unit tripped after SEV on and trying to increase load.
BR6 | 6 | SF | 2018-01-12 15:07 |  |  |  |  | 2018-01-14 13:16 |  | 0 | 0 | 46.15 | 46.15 | 7891.65 | 1 |  |  |  | 0 |  |  | 172
|  | CAUSE CODE : |  | 5050 |  |  | - |  | Ignition system | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Propane ignitor would not ligth off.
BR6 | 11 | U1 | 2018-02-02 06:43 |  |  |  |  | 2018-02-02 16:18 |  | 0 | 0 | 9.583 | 9.5833 | 1638.75 | 1 |  |  |  | 0 |  |  | 172
|  | CAUSE CODE : |  | 5170 |  |  | - |  | Cooling water system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F410LP quench control valve stuck.
BR6 | 14 | SF | 2018-02-08 06:15 |  |  |  |  | 2018-02-08 14:39 |  | 0 | 0 | 8.4 | 8.4 | 1436.4 | 1 |  |  |  | 0 |  |  | 172
|  | CAUSE CODE : |  | 5450 |  |  | - |  | Ignition system | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Unit failed to light off.
BR6 | 19 | U1 | 2018-02-23 10:22 |  |  |  |  | 2018-02-23 12:38 |  | 0 | 0 | 2.267 | 2.2667 | 387.6 | 1 |  |  |  | 0 |  |  | 172
|  | CAUSE CODE : |  | 5510 |  |  | - |  | Lube oil system | [8 empty] | AMP CODE: |  | 55
|  | DESCRIPTION : |  | F550MCC tie breaker would not reset.
BR6 | 33 | SF | 2018-04-23 05:26 |  |  |  |  | 2018-04-23 15:00 |  | 0 | 0 | 9.567 | 9.5667 | 1501.967 | 1 |  |  |  | 0 |  |  | 158
|  | CAUSE CODE : |  | 5450 |  |  | - |  | Ignition system | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Unit would not light off.
BR6 | 47 | U1 | 2018-10-07 17:28 |  |  |  |  | 2018-10-07 18:52 |  | 0 | 0 | 1.4 | 1.4 | 219.8 | 1 |  |  |  | 0 |  |  | 158
|  | CAUSE CODE : |  | 3621 |  |  | - |  | Unit auxiliaries transformer | [8 empty] | AMP CODE: |  | 03
|  | DESCRIPTION : |  | F030Ligthning arrestor on BOP north transformer went to ground. Substation Crew did f
BR6 | 3 | SF | 2019-01-19 15:22 |  |  |  |  | 2019-01-19 20:38 |  | 0 | 0 | 5.267 | 5.2667 | 900.6 | 1 |  |  |  | 0 |  |  | 172
|  | CAUSE CODE : |  | 5050 |  |  | - |  | Ignition system | [8 empty] | AMP CODE: |  | 72
|  | DESCRIPTION : |  | F720Air regulator supplying ingnitors failed. While trying to troubleshoot swagelok f
BR6 | 9 | U1 | 2019-02-13 06:47 |  |  |  |  | 2019-02-13 06:57 |  | 0 | 0 | 0.167 | 0.1667 | 28.5 | 1 |  |  |  | 0 |  |  | 172
|  | CAUSE CODE : |  | 5248 |  |  | - |  | Gas Turbine Control System - logic problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Unit would synchronize to system and then immediately trip on reverse power.
BR6 | 10 | U1 | 2019-02-13 06:58 |  |  |  |  | 2019-02-13 07:01 |  | 0 | 0 | 0.05 | 0.05 | 8.55 | 1 |  |  |  | 0 |  |  | 172
|  | CAUSE CODE : |  | 5248 |  |  | - |  | Gas Turbine Control System - logic problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Unit would synchronize to system and then immediately trip on reverse power.
BR6 | 11 | U1 | 2019-02-13 07:02 |  |  |  |  | 2019-02-13 07:04 |  | 0 | 0 | 0.033 | 0.0333 | 5.7 | 1 |  |  |  | 0 |  |  | 172
|  | CAUSE CODE : |  | 5248 |  |  | - |  | Gas Turbine Control System - logic problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Unit would synchronize to system and then immediately trip on reverse power. Trie
BR6 | 12 | U1 | 2019-02-13 07:05 |  |  |  |  | 2019-02-13 07:20 |  | 0 | 0 | 0.25 | 0.25 | 42.75 | 1 |  |  |  | 0 |  |  | 172
|  | CAUSE CODE : |  | 5248 |  |  | - |  | Gas Turbine Control System - logic problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Unit would synchronize to system and then immediately trip on reverse power. Clos
BR6 | 13 | U1 | 2019-02-13 07:21 |  |  |  |  | 2019-02-13 07:25 |  | 0 | 0 | 0.067 | 0.0667 | 11.4 | 1 |  |  |  | 0 |  |  | 172
|  | CAUSE CODE : |  | 5248 |  |  | - |  | Gas Turbine Control System - logic problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Unit would synchronize to system and then immediately trip on reverse power. Unit
BR6 | 14 | U1 | 2019-02-13 07:26 |  |  |  |  | 2019-02-13 07:40 |  | 0 | 0 | 0.233 | 0.2333 | 39.9 | 1 |  |  |  | 0 |  |  | 172
|  | CAUSE CODE : |  | 5248 |  |  | - |  | Gas Turbine Control System - logic problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Unit would synchronize to system and then immediately trip on reverse power. Open
BR6 | 15 | U1 | 2019-02-13 07:41 |  |  |  |  | 2019-02-13 07:43 |  | 0 | 0 | 0.033 | 0.0333 | 5.7 | 1 |  |  |  | 0 |  |  | 172
|  | CAUSE CODE : |  | 5248 |  |  | - |  | Gas Turbine Control System - logic problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Unit would synchronize to system and then immediately trip on reverse power. Func
BR6 | 16 | U1 | 2019-02-13 07:44 |  |  |  |  | 2019-02-13 13:39 |  | 0 | 0 | 5.917 | 5.9167 | 1011.75 | 1 |  |  |  | 0 |  |  | 172
|  | CAUSE CODE : |  | 5248 |  |  | - |  | Gas Turbine Control System - logic problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Unit would synchronize to system and then immediately trip on reverse power. Chan
BR6 | 18 | SF | 2019-02-19 06:03 |  |  |  |  | 2019-02-19 12:05 |  | 0 | 0 | 6.033 | 6.0333 | 1031.7 | 1 |  |  |  | 0 |  |  | 172
|  | CAUSE CODE : |  | 5050 |  |  | - |  | Ignition system | [8 empty] | AMP CODE: |  | 66
|  | DESCRIPTION : |  | F660Failure of propane ignition. Top torch had broken spark rod, and right side torch
BR6 | 26 | U1 | 2019-04-01 03:16 |  |  |  |  | 2019-04-01 13:18 |  | 0 | 0 | 10.033 | 10.0333 | 1575.233 | 1 |  |  |  | 0 |  |  | 158
|  | CAUSE CODE : |  | 5079 |  |  | - |  | Other combustor problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F410Bad EV pulsation transducer. Changed out transducer.
BR6 | 34 | U1 | 2019-06-02 10:25 |  |  |  |  | 2019-06-02 10:52 |  | 0 | 0 | 0.45 | 0.45 | 65.7 | 1 |  |  |  | 0 |  |  | 147
|  | CAUSE CODE : |  | 5660 |  |  | - |  | Major overhaul (use for non-specific overhaul only; see page B-CCGT-2) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F410Testing during outage. Unit tripped.
BR6 | 35 | U1 | 2019-06-02 12:09 |  |  |  |  | 2019-06-02 12:11 |  | 0 | 0 | 0.033 | 0.0333 | 4.867 | 1 |  |  |  | 0 |  |  | 147
|  | CAUSE CODE : |  | 5441 |  |  | - |  | Fuel piping and valves | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F540Gas leak on SEV forced unit off. Did not trip unit, was able to come back online t
BR6 | 36 | U1 | 2019-06-03 01:09 |  |  |  |  | 2019-06-03 06:26 |  | 0 | 0 | 5.283 | 5.2833 | 771.367 | 1 |  |  |  | 0 |  |  | 147
|  | CAUSE CODE : |  | 5441 |  |  | - |  | Fuel piping and valves | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F540Cool down for compressor run in. Worked on SEV pulsation probe, changed cable. W
BR6 | 37 | U1 | 2019-06-03 08:35 |  |  |  |  | 2019-06-04 06:56 |  | 0 | 0 | 22.35 | 22.35 | 3263.1 | 1 |  |  |  | 0 |  |  | 147
|  | CAUSE CODE : |  | 5441 |  |  | - |  | Fuel piping and valves | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F540Gas Leak on SEV FDS. Need to replace tubing and Swagelok fittings.
BR6 | 38 | U1 | 2019-06-04 09:16 |  |  |  |  | 2019-06-04 15:53 |  | 0 | 0 | 6.617 | 6.6167 | 966.033 | 1 |  |  |  | 0 |  |  | 147
|  | CAUSE CODE : |  | 5441 |  |  | - |  | Fuel piping and valves | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F540Gas leaks on SEV. Worked on replacing ferrels on two swagelok SEV gas fittings.
BR6 | 41 | U1 | 2019-06-07 12:58 |  |  |  |  | 2019-06-07 13:44 |  | 0 | 0 | 0.767 | 0.7667 | 111.933 | 1 |  |  |  | 0 |  |  | 147
|  | CAUSE CODE : |  | 5441 |  |  | - |  | Fuel piping and valves | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F540Leak on SEV gas tubing. Tighten fittings.
BR6 | 46 | U1 | 2019-06-21 18:57 |  |  |  |  | 2019-06-22 10:30 |  | 0 | 0 | 15.55 | 15.55 | 2270.3 | 1 |  |  |  | 0 |  |  | 147
|  | CAUSE CODE : |  | 5449 |  |  | - |  | Other fuel system problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F780SEV band 2 pulsations forced unit offline. Unit could not go over 137MW. Decision
BR6 | 49 | U1 | 2019-06-28 11:57 |  |  |  |  | 2019-06-28 12:12 |  | 0 | 0 | 0.25 | 0.25 | 36.5 | 1 |  |  |  | 0 |  |  | 147
|  | CAUSE CODE : |  | 5051 |  |  | - |  | Pilot fuel piping and valves | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F410Unit tripped during switchover from pilot to premix. It looked to be an issue wit
BR6 | 53 | U1 | 2019-07-03 16:51 |  |  |  |  | 2019-07-03 22:28 |  | 0 | 0 | 5.617 | 5.6167 | 820.033 | 1 |  |  |  | 0 |  |  | 147
|  | CAUSE CODE : |  | 5041 |  |  | - |  | Fuel piping and valves | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F410Trip due to deviation in SEV control valve. Possible lightning strike.
BR6 | 55 | U1 | 2019-07-08 19:23 |  |  |  |  | 2019-07-09 10:31 |  | 0 | 0 | 15.133 | 15.1333 | 2209.466 | 1 |  |  |  | 0 |  |  | 147
|  | CAUSE CODE : |  | 5048 |  |  | - |  | Gas fuel system including controls and instrumentation | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F410Trip of unit at base load. First out had SEV control valve deviation.
BR6 | 75 | U1 | 2019-08-11 10:04 |  |  |  |  | 2019-08-11 11:21 |  | 0 | 0 | 1.283 | 1.2833 | 187.367 | 1 |  |  |  | 0 |  |  | 147
|  | CAUSE CODE : |  | 5280 |  |  | - |  | Vibration (not engine) in unit not attributable to bearings or other components | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F410Erratic seismic probe on number 2 bearing. Repaired connection.
BR6 | 81 | SF | 2019-08-20 09:31 |  |  |  |  | 2019-08-20 10:40 |  | 0 | 0 | 1.15 | 1.15 | 167.9 | 1 |  |  |  | 0 |  |  | 147
|  | CAUSE CODE : |  | 3610 |  |  | - |  | Switchyard circuit breakers - external (not OMC) | [8 empty] | AMP CODE: |  | 06
|  | DESCRIPTION : |  | F060Closing coil latching mechanism had screw back out preventing beaker from closing.
BR6 | 104 | U1 | 2019-10-01 07:16 |  |  |  |  | 2019-10-01 08:48 |  | 0 | 0 | 1.533 | 1.5333 | 240.733 | 1 |  |  |  | 0 |  |  | 158
|  | CAUSE CODE : |  | 3611 |  |  | - |  | Switchyard circuit breakers - external (OMC) | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Substation Breaker will not close
BR6 | 110 | SF | 2019-10-10 10:09 |  |  |  |  | 2019-10-10 13:20 |  | 0 | 0 | 3.183 | 3.1833 | 499.783 | 1 |  |  |  | 0 |  |  | 158
|  | CAUSE CODE : |  | 5049 |  |  | - |  | Other fuel system problems | [8 empty] | AMP CODE: |  | 06
|  | DESCRIPTION : |  | F060Solenoid valve on Nitrogen purge valve actuator failed to operate. Changed out so
BR6 | 111 | U1 | 2019-10-10 15:44 |  |  |  |  | 2019-10-11 09:06 |  | 0 | 0 | 17.367 | 17.3667 | 2726.567 | 1 |  |  |  | 0 |  |  | 158
|  | CAUSE CODE : |  | 5640 |  |  | - |  | Fire detection and extinguishing system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F410Shorted cable going to enclosure ventalation system tripped out enclosure controls
BR6 | 115 | SF | 2019-10-17 05:06 |  |  |  |  | 2019-10-17 13:36 |  | 0 | 0 | 8.5 | 8.5 | 1334.5 | 1 |  |  |  | 0 |  |  | 158
|  | CAUSE CODE : |  | 5048 |  |  | - |  | Gas fuel system including controls and instrumentation | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Purge sequence failure
BR6 | 5 | SF | 2020-02-14 07:20 |  |  |  |  | 2020-02-14 13:08 |  | 0 | 0 | 5.8 | 5.8 | 991.8 | 1 |  |  |  | 0 |  |  | 172
|  | CAUSE CODE : |  | 5017 |  |  | - |  | Low pressure compressor bleed valves | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Problem with start up sequencer preventing unit from starting. 1st stage blow-off
BR6 | 9 | SF | 2020-03-16 04:45 |  |  |  |  | 2020-03-16 06:01 |  | 0 | 0 | 1.267 | 1.2667 | 198.867 | 1 |  |  |  | 0 |  |  | 158
|  | CAUSE CODE : |  | 5246 |  |  | - |  | Gas Turbine Control System - hardware problems (including card failure) | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Blown fuse on DCS card. Replaced fuses.
BR6 | 10 | U1 | 2020-03-16 06:04 |  |  |  |  | 2020-03-16 09:41 |  | 0 | 0 | 3.617 | 3.6167 | 567.817 | 1 |  |  |  | 0 |  |  | 158
|  | CAUSE CODE : |  | 5248 |  |  | - |  | Gas Turbine Control System - logic problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F750Flamed out during swtichover. Happened after third nitrogen purge of pilot. Sent
BR6 | 14 | SF | 2020-03-20 12:34 |  |  |  |  | 2020-03-20 17:11 |  | 0 | 0 | 4.617 | 4.6167 | 724.817 | 1 |  |  |  | 0 |  |  | 158
|  | CAUSE CODE : |  | 3681 |  |  | - |  | Other voltage circuit breakers | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Charging motor on field breaker had burned up. Changed field breaker.
BR6 | 17 | U1 | 2020-04-03 01:22 |  |  |  |  | 2020-04-08 20:30 |  | 0 | 0 | 139.133 | 139.1333 | 21843.933 | 1 |  |  |  | 0 |  |  | 158
|  | CAUSE CODE : |  | 5550 |  |  | - |  | Turning gear and motor | [8 empty] | AMP CODE: |  | 69
|  | DESCRIPTION : |  | F690Unit would not go on rotor barring.
BR6 | 40 | U1 | 2020-07-17 07:40 |  |  |  |  | 2020-07-17 08:01 |  | 0 | 0 | 0.35 | 0.35 | 51.1 | 1 |  |  |  | 0 |  |  | 147
|  | CAUSE CODE : |  | 3611 |  |  | - |  | Switchyard circuit breakers - external (OMC) | [8 empty] | AMP CODE: |  | X0
|  | DESCRIPTION : |  | FX00Unit 6 substation breaker would not close. Substation maintenance came on site to
BR6 | 46 | U1 | 2020-07-23 12:30 |  |  |  |  | 2020-07-24 13:52 |  | 0 | 0 | 25.367 | 25.3667 | 3703.533 | 1 |  |  |  | 0 |  |  | 147
|  | CAUSE CODE : |  | 3690 |  |  | - |  | "Station Service Power Distribution System, General" | [8 empty] | AMP CODE: |  | 06
|  | DESCRIPTION : |  | F060Unit 6 emergency generator starter failed during test start
BR6 | 53 | U1 | 2020-08-26 17:14 |  |  |  |  | 2020-08-26 17:36 |  | 0 | 0 | 0.367 | 0.3667 | 53.533 | 1 |  |  |  | 0 |  |  | 147
|  | CAUSE CODE : |  | 3864 |  |  | - |  | Fire protection system instrumentation and controls | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Two enclosure temperature sensors went into alarm causing unit trip.
BR6 | 2 | SF | 2021-01-18 06:41 |  |  |  |  | 2021-01-21 16:34 |  | 0 | 0 | 81.883 | 81.8833 | 14002.05 | 1 |  |  |  | 0 |  |  | 172
|  | CAUSE CODE : |  | 4609 |  |  | - |  | Other exciter problems | [8 empty] | AMP CODE: |  | 70
|  | DESCRIPTION : |  | F700Cable from SFC to BR6 AVR was grounded.
BR6 | 4 | SF | 2021-01-22 06:30 |  |  |  |  | 2021-01-22 11:28 |  | 0 | 0 | 4.967 | 4.9667 | 849.3 | 1 |  |  |  | 0 |  |  | 172
|  | CAUSE CODE : |  | 5050 |  |  | - |  | Ignition system | [8 empty] | AMP CODE: |  | 06
|  | DESCRIPTION : |  | F060Unit would not light off. Found bad ignition torch.
BR6 | 15 | U1 | 2021-06-18 10:42 |  |  |  |  | 2021-06-18 11:56 |  | 0 | 0 | 1.233 | 1.2333 | 180.067 | 1 |  |  |  | 0 |  |  | 147
|  | CAUSE CODE : |  | 4560 |  |  | - |  | Generator vibration (excluding vibration due to failed bearing and other components) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F850Vibration spiked causing unit to trip.
BR6 | 30 | U1 | 2021-08-08 10:32 |  |  |  |  | 2021-08-08 11:23 |  | 0 | 0 | 0.85 | 0.85 | 124.1 | 1 |  |  |  | 0 |  |  | 147
|  | CAUSE CODE : |  | 5088 |  |  | - |  | Gas turbine cooling system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820HP quench cooler valve lost indication resulting in unit trip
BR6 | 55 | SF | 2021-11-02 06:00 |  |  |  |  | 2021-11-02 06:21 |  | 0 | 0 | 0.35 | 0.35 | 54.95 | 1 |  |  |  | 0 |  |  | 158
|  | CAUSE CODE : |  | 5001 |  |  | - |  | Inlet air vanes/nozzles | [8 empty] | AMP CODE: |  | 40
|  | DESCRIPTION : |  | F400Inlet vanes were not at light off position.
BR6 | 3 | U1 | 2022-01-17 20:33 |  |  |  |  | 2022-01-18 14:20 |  | 0 | 0 | 17.783 | 17.7833 | 3040.95 | 1 |  |  |  | 0 |  |  | 172
|  | CAUSE CODE : |  | 4740 |  |  | - |  | Emergency generator trip devices | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Generator breaker would not open on normal shutdown until substation breaker was o
BR6 | 6 | U1 | 2022-01-21 07:57 |  |  |  |  | 2022-01-21 07:59 |  | 0 | 0 | 0.033 | 0.0333 | 5.7 | 1 |  |  |  | 0 |  |  | 172
|  | CAUSE CODE : |  | 3974 |  |  | - |  | DCS - logic problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830SEV would not light despite being at proper temperature
BR6 | 10 | U1 | 2022-03-05 18:59 |  |  |  |  | 2022-03-06 01:32 |  | 0 | 0 | 6.55 | 6.55 | 1028.35 | 1 |  |  |  | 0 |  |  | 158
|  | CAUSE CODE : |  | 3864 |  |  | - |  | Fire protection system instrumentation and controls | [8 empty] | AMP CODE: |  | 70
|  | DESCRIPTION : |  | F700U6 gas detection controls processor failed.
BR6 | 5 | U1 | 2023-03-24 10:32 |  |  |  |  | 2023-03-24 13:33 |  | 0 | 0 | 3.017 | 3.0167 | 473.617 | 1 |  |  |  | 0 |  |  | 158
|  | CAUSE CODE : |  | 3631 |  |  | - |  | 400-700 volt circuit breakers | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410480V MCC tie breaker couldn't reset after monthly checks.
BR6 | 9 | SF | 2023-05-24 13:36 |  |  |  |  | 2023-05-24 13:59 |  | 0 | 0 | 0.383 | 0.3833 | 60.183 | 1 |  |  |  | 0 |  |  | 158
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 87
|  | DESCRIPTION : |  | F870BR7 trip caused SFC trip on BR6
BR6 | 16 | SF | 2023-06-04 14:44 |  |  |  |  | 2023-06-04 16:02 |  | 0 | 0 | 1.3 | 1.3 | 189.8 | 1 |  |  |  | 0 |  |  | 147
|  | CAUSE CODE : |  | 5250 |  |  | - |  | Other controls and instrumentation problems | [8 empty] | AMP CODE: |  | 40
|  | DESCRIPTION : |  | F400AVR locked up, preventing the unit from going online.
BR6 | 33 | U1 | 2023-08-25 18:46 |  |  |  |  | 2023-08-25 19:24 |  | 0 | 0 | 0.633 | 0.6333 | 92.467 | 1 |  |  |  | 0 |  |  | 147
|  | CAUSE CODE : |  | 3864 |  |  | - |  | Fire protection system instrumentation and controls | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Unit tripped after enclosure fans tripped and temperature rose causing a fire alar
BR6 | 39 | SF | 2023-10-04 13:12 |  |  |  |  | 2023-10-04 14:20 |  | 0 | 0 | 1.133 | 1.1333 | 177.933 | 1 |  |  |  | 0 |  |  | 158
|  | CAUSE CODE : |  | 5246 |  |  | - |  | Gas Turbine Control System - hardware problems (including card failure) | [8 empty] | AMP CODE: |  | 06
|  | DESCRIPTION : |  | F060PEC for the AVR lost signal from channel 1.
Brown - BR7
Unit | Event | Type | Start |  |  |  |  | End |  | GAC | NAC | Duration | Equiv Hrs | Equiv MWH | Cont | Work Start | Work End |  | Hours |  |  | Gross Capacity Impact (MW)
BR7 | 4 | U1 | 2014-01-04 06:11 |  |  |  |  | 2014-01-04 11:16 |  | 0 | 0 | 5.083 | 5.0833 | 869.25 | 1 |  |  |  | 0 |  |  | 172
|  | CAUSE CODE : |  | 4700 |  |  | - |  | Generator voltage control | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410AVR Fault due to loss of channel one processor.
BR7 | 7 | U1 | 2014-01-13 08:05 |  |  |  |  | 2014-01-14 13:30 |  | 0 | 0 | 29.417 | 29.4167 | 5030.25 | 1 |  |  |  | 0 |  |  | 172
|  | CAUSE CODE : |  | 5150 |  |  | - |  | Turning gear and motor | [8 empty] | AMP CODE: |  | 66
|  | DESCRIPTION : |  | F660Unit will not stay on rotor barring.
BR7 | 12 | U1 | 2014-02-10 17:14 |  |  |  |  | 2014-02-10 19:34 |  | 0 | 0 | 2.333 | 2.3333 | 399 | 1 |  |  |  | 0 |  |  | 172
|  | CAUSE CODE : |  | 5049 |  |  | - |  | Other fuel system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F660Issue with pressure regulators in reducing station.
BR7 | 27 | U1 | 2014-03-24 04:51 |  |  |  |  | 2014-03-24 06:53 |  | 0 | 0 | 2.033 | 2.0333 | 347.7 | 1 |  |  |  | 0 |  |  | 158
|  | CAUSE CODE : |  | 5160 |  |  | - |  | Cooling and seal air system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F780Tripped unit due to high temperature on HP quench system. Problem looks to be tha
BR7 | 38 | U1 | 2014-04-23 15:10 |  |  |  |  | 2014-04-23 16:09 |  | 0 | 0 | 0.983 | 0.9833 | 143.567 | 1 |  |  |  | 0 |  |  | 158
|  | CAUSE CODE : |  | 5049 |  |  | - |  | Other fuel system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F420Operator closed inlet valve to gas heater without opening by-pass valve.
BR7 | 52 | SF | 2014-05-27 10:39 |  |  |  |  | 2014-05-27 11:44 |  | 0 | 0 | 1.083 | 1.0833 | 158.167 | 1 |  |  |  | 0 |  |  | 158
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Key Switch on Starting Isolator switch out of position
BR7 | 63 | U1 | 2014-06-11 10:00 |  |  |  |  | 2014-06-11 13:37 |  | 0 | 0 | 3.617 | 3.6167 | 528.033 | 1 |  |  |  | 0 |  |  | 147
|  | CAUSE CODE : |  | 5054 |  |  | - |  | Water injection system | [8 empty] | AMP CODE: |  | 06
|  | DESCRIPTION : |  | F060Broken valve stem on SEV Nox water purge and fill valve
BR7 | 78 | SF | 2014-07-07 09:47 |  |  |  |  | 2014-07-07 11:17 |  | 0 | 0 | 1.5 | 1.5 | 219 | 1 |  |  |  | 0 |  |  | 147
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 59
|  | DESCRIPTION : |  | F590Medium Voltage breaker tripped, had to change breaker
BR7 | 94 | SF | 2014-07-26 13:15 |  |  |  |  | 2014-07-26 14:55 |  | 0 | 0 | 1.667 | 1.6667 | 243.333 | 1 |  |  |  | 0 |  |  | 147
|  | CAUSE CODE : |  | 5049 |  |  | - |  | Other fuel system problems | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Solenoid on fuel oil drain valve was bad.
BR7 | 119 | SF | 2014-09-29 11:05 |  |  |  |  | 2014-09-29 11:33 |  | 0 | 0 | 0.467 | 0.4667 | 68.133 | 1 |  |  |  | 0 |  |  | 158
|  | CAUSE CODE : |  | 5248 |  |  | - |  | Gas Turbine Control System - logic problems | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Nitrogen Purge Sequencer out of sync. Issue was from DC ground on wash cart valve.
BR7 | 123 | SF | 2014-10-06 08:11 |  |  |  |  | 2014-10-06 13:46 |  | 0 | 0 | 5.583 | 5.5833 | 954.75 | 1 |  |  |  | 0 |  |  | 158
|  | CAUSE CODE : |  | 5050 |  |  | - |  | Ignition system | [8 empty] | AMP CODE: |  | 78
|  | DESCRIPTION : |  | F780Unit trip at Flame on.
BR7 | 125 | U1 | 2014-10-07 05:54 |  |  |  |  | 2014-10-08 11:19 |  | 0 | 0 | 29.417 | 29.4167 | 5030.25 | 1 |  |  |  | 0 |  |  | 158
|  | CAUSE CODE : |  | 5108 |  |  | - |  | High engine exhaust temperature | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F750High TIT1 temperatures during switchover.
BR7 | 139 | U1 | 2014-11-21 05:22 |  |  |  |  | 2014-11-21 10:57 |  | 0 | 0 | 5.583 | 5.5833 | 954.75 | 1 |  |  |  | 0 |  |  | 158
|  | CAUSE CODE : |  | 3624 |  |  | - |  | Auxiliary generator voltage supply system | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Bad CPU model on AVR controls
BR7 | 141 | U1 | 2014-11-21 14:51 |  |  |  |  | 2014-11-21 18:53 |  | 0 | 0 | 4.033 | 4.0333 | 689.7 | 1 |  |  |  | 0 |  |  | 158
|  | CAUSE CODE : |  | 3624 |  |  | - |  | Auxiliary generator voltage supply system | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Replaced bad gate control card, and loaded arcnet configuration to the controllers
BR7 | 2 | U1 | 2015-01-05 17:23 |  |  |  |  | 2015-01-06 06:48 |  | 0 | 0 | 13.417 | 13.4167 | 2294.25 | 1 |  |  |  | 0 |  |  | 172
|  | CAUSE CODE : |  | 9290 |  |  | - |  | Other fuel quality problems (OMC) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F750Unit tripped offline due to rapid changes to gas composition.
BR7 | 14 | U1 | 2015-02-22 14:29 |  |  |  |  | 2015-02-22 19:29 |  | 0 | 0 | 5 | 5 | 855 | 1 |  |  |  | 0 |  |  | 172
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Control processor on static starting device failed.
BR7 | 16 | SF | 2015-02-25 04:40 |  |  |  |  | 2015-02-25 05:12 |  | 0 | 0 | 0.533 | 0.5333 | 91.2 | 1 |  |  |  | 0 |  |  | 172
|  | CAUSE CODE : |  | 3624 |  |  | - |  | Auxiliary generator voltage supply system | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Unit did not sync on first attempt. AVR back up channel being out did not allow u
BR7 | 28 | SF | 2015-03-27 18:34 |  |  |  |  | 2015-03-27 19:03 |  | 0 | 0 | 0.483 | 0.4833 | 82.65 | 1 |  |  |  | 0 |  |  | 158
|  | CAUSE CODE : |  | 5248 |  |  | - |  | Gas Turbine Control System - logic problems | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Fuel Valve sequencer stuck in logic.
BR7 | 44 | U1 | 2015-05-04 09:38 |  |  |  |  | 2015-05-04 12:15 |  | 0 | 0 | 2.617 | 2.6167 | 382.033 | 1 |  |  |  | 0 |  |  | 158
|  | CAUSE CODE : |  | 5115 |  |  | - |  | Oil vapor extractor | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Failure of motor bearing for the lube oil vapor extractor.
BR7 | 3 | U1 | 2016-01-06 09:15 |  |  |  |  | 2016-01-12 13:48 |  | 0 | 0 | 148.55 | 148.55 | 25402.05 | 1 |  |  |  | 0 |  |  | 172
|  | CAUSE CODE : |  | 5670 |  |  | - |  | Hot end inspection | [8 empty] | AMP CODE: |  | 53
|  | DESCRIPTION : |  | F530Inspection needed due to water ingress from failure of NOx water pump.
BR7 | 6 | SF | 2016-01-21 03:24 |  |  |  |  | 2016-01-21 06:19 |  | 0 | 0 | 2.917 | 2.9167 | 498.75 | 1 |  |  |  | 0 |  |  | 172
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Bad I/O card on static frequency converter.
BR7 | 8 | U1 | 2016-02-25 06:16 |  |  |  |  | 2016-02-25 10:00 |  | 0 | 0 | 3.733 | 3.7333 | 638.4 | 1 |  |  |  | 0 |  |  | 172
|  | CAUSE CODE : |  | 7930 |  |  | - |  | Controls and instrumentation | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F660Unit tripped while performing emissions testing at 80 MWs due to pulsations. Puls
BR7 | 15 | U1 | 2016-05-11 06:05 |  |  |  |  | 2016-05-11 07:02 |  | 0 | 0 | 0.95 | 0.95 | 149.15 | 1 |  |  |  | 0 |  |  | 158
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410I/O card for SFC controls went bad. Lost communications to card. Possibly due to
BR7 | 33 | U1 | 2016-09-07 22:00 |  |  |  |  | 2016-09-07 22:43 |  | 0 | 0 | 0.717 | 0.7167 | 112.517 | 1 |  |  |  | 0 |  |  | 158
|  | CAUSE CODE : |  | 3971 |  |  | - |  | DCS - data highway | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410DCS LAN went down causing 11N2 system to loose communication.
BR7 | 16 | SF | 2017-06-21 12:16 |  |  |  |  | 2017-06-21 18:12 |  | 0 | 0 | 5.933 | 5.9333 | 866.267 | 1 |  |  |  | 0 |  |  | 147
|  | CAUSE CODE : |  | 4810 |  |  | - |  | Generator output breaker | [8 empty] | AMP CODE: |  | 69
|  | DESCRIPTION : |  | F690Ground switch drive motor failed. Motor was found hot and would not rotate.
BR7 | 22 | U1 | 2017-09-08 08:36 |  |  |  |  | 2017-09-08 13:57 |  | 0 | 0 | 5.35 | 5.35 | 839.95 | 1 |  |  |  | 0 |  |  | 158
|  | CAUSE CODE : |  | 3612 |  |  | - |  | Switchyard system protection devices - external (OMC) | [8 empty] | AMP CODE: |  | X0
|  | DESCRIPTION : |  | FX00Brown North Substation Protection Disabled.
BR7 | 32 | SF | 2017-12-26 04:50 |  |  |  |  | 2017-12-26 11:11 |  | 0 | 0 | 6.35 | 6.35 | 1085.85 | 1 |  |  |  | 0 |  |  | 172
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410SFC tripped upon start up.
BR7 | 34 | SF | 2017-12-27 03:54 |  |  |  |  | 2017-12-29 18:29 |  | 0 | 0 | 62.583 | 62.5833 | 10701.75 | 1 |  |  |  | 0 |  |  | 172
|  | CAUSE CODE : |  | 3974 |  |  | - |  | DCS - logic problems | [8 empty] | AMP CODE: |  | 78
|  | DESCRIPTION : |  | F780Unit will not sync online. Goes online and then trips back off due to reverse pow
BR7 | 25 | U1 | 2018-05-23 16:32 |  |  |  |  | 2018-05-23 20:17 |  | 0 | 0 | 3.75 | 3.75 | 588.75 | 1 |  |  |  | 0 |  |  | 158
|  | CAUSE CODE : |  | 3972 |  |  | - |  | DCS - hardware problems (including card failure) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F410Lost CLC2 Primary DCS controller. Replaced controller and returned unit to servic
BR7 | 31 | U1 | 2018-06-18 12:58 |  |  |  |  | 2018-06-19 08:00 |  | 0 | 0 | 19.033 | 19.0333 | 2778.867 | 1 |  |  |  | 0 |  |  | 147
|  | CAUSE CODE : |  | 5016 |  |  | - |  | High pressure compressor bleed valves | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F410Control driver card for blow off valves failed. Replaced card and calibrated. Hot
BR7 | 34 | SF | 2018-07-03 09:07 |  |  |  |  | 2018-07-03 10:26 |  | 0 | 0 | 1.317 | 1.3167 | 192.233 | 1 |  |  |  | 0 |  |  | 147
|  | CAUSE CODE : |  | 4810 |  |  | - |  | Generator output breaker | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Isolation Key Switch had vibrated to the wrong position. WO was created to remove
BR7 | 50 | U1 | 2018-10-07 17:28 |  |  |  |  | 2018-10-07 18:52 |  | 0 | 0 | 1.4 | 1.4 | 219.8 | 1 |  |  |  | 0 |  |  | 158
|  | CAUSE CODE : |  | 3621 |  |  | - |  | Unit auxiliaries transformer | [8 empty] | AMP CODE: |  | 03
|  | DESCRIPTION : |  | F030Ligthning arrestor on BOP north transformer went to ground. Substation Crew did f
BR7 | 11 | U1 | 2019-06-30 09:00 |  |  |  |  | 2019-08-04 13:26 |  | 0 | 0 | 844.433 | 844.4333 | 123287.267 | 1 |  |  |  | 0 |  |  | 147
|  | CAUSE CODE : |  | 4511 |  |  | - |  | "Rotor, General" | [8 empty] | AMP CODE: |  | 06
|  | DESCRIPTION : |  | F060Generator rotor sent to service shop. Field turn supports to be changed to new de
BR7 | 5 | SF | 2020-01-30 06:00 |  |  |  |  | 2020-01-30 06:14 |  | 0 | 0 | 0.233 | 0.2333 | 39.9 | 1 |  |  |  | 0 |  |  | 172
|  | CAUSE CODE : |  | 4750 |  |  | - |  | Other generator controls and metering problems | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Issue with contacter on starting device.
BR7 | 6 | SF | 2020-02-14 07:50 |  |  |  |  | 2020-02-14 13:20 |  | 0 | 0 | 5.5 | 5.5 | 940.5 | 1 |  |  |  | 0 |  |  | 172
|  | CAUSE CODE : |  | 5102 |  |  | - |  | Vanes/nozzles | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Bad output control card. Proportional valve driver (ATOS Card) went bad. Changed
BR7 | 9 | SF | 2020-03-16 05:15 |  |  |  |  | 2020-03-16 06:17 |  | 0 | 0 | 1.033 | 1.0333 | 162.233 | 1 |  |  |  | 0 |  |  | 158
|  | CAUSE CODE : |  | 5246 |  |  | - |  | Gas Turbine Control System - hardware problems (including card failure) | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Bad TAT2 measurement spiked during start up. Pulled thermocouple.
BR7 | 13 | U1 | 2020-06-09 11:29 |  |  |  |  | 2020-06-09 14:23 |  | 0 | 0 | 2.9 | 2.9 | 423.4 | 1 |  |  |  | 0 |  |  | 147
|  | CAUSE CODE : |  | 5079 |  |  | - |  | Other combustor problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F410EV pulsation probe went bad during run. Replaced probe during outage.
BR7 | 18 | U1 | 2020-06-22 12:20 |  |  |  |  | 2020-06-22 14:15 |  | 0 | 0 | 1.917 | 1.9167 | 279.833 | 1 |  |  |  | 0 |  |  | 147
|  | CAUSE CODE : |  | 5479 |  |  | - |  | Other combustor problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F410Erratic circuit for EV pulsation probe. Changed out signal conditioner and galvan
BR7 | 22 | U1 | 2020-07-06 14:51 |  |  |  |  | 2020-07-06 16:03 |  | 0 | 0 | 1.2 | 1.2 | 175.2 | 1 |  |  |  | 0 |  |  | 147
|  | CAUSE CODE : |  | 3864 |  |  | - |  | Fire protection system instrumentation and controls | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Insulation in poor shape resulting in elevated enclosure temperatures. Two heat de
BR7 | 31 | SF | 2020-07-20 07:59 |  |  |  |  | 2020-07-20 09:59 |  | 0 | 0 | 2 | 2 | 292 | 1 |  |  |  | 0 |  |  | 147
|  | CAUSE CODE : |  | 5050 |  |  | - |  | Ignition system | [8 empty] | AMP CODE: |  | 06
|  | DESCRIPTION : |  | F060Ignition torch on unit was not sparking correctly
BR7 | 37 | SF | 2020-07-28 11:00 |  |  |  |  | 2020-07-28 15:31 |  | 0 | 0 | 4.517 | 4.5167 | 659.433 | 1 |  |  |  | 0 |  |  | 147
|  | CAUSE CODE : |  | 5047 |  |  | - |  | Liquid fuel purge system | [8 empty] | AMP CODE: |  | 06
|  | DESCRIPTION : |  | F060Three way fuel water drain valve would not operate.
BR7 | 61 | SF | 2020-12-03 05:45 |  |  |  |  | 2020-12-03 06:21 |  | 0 | 0 | 0.6 | 0.6 | 102.6 | 1 |  |  |  | 0 |  |  | 172
|  | CAUSE CODE : |  | 4700 |  |  | - |  | Generator voltage control | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410AVR controls would not allow unit to sync to grid. Believe the AVR start sequence
BR7 | 62 | U1 | 2020-12-03 06:26 |  |  |  |  | 2020-12-03 14:54 |  | 0 | 0 | 8.467 | 8.4667 | 1447.8 | 1 |  |  |  | 0 |  |  | 172
|  | CAUSE CODE : |  | 5041 |  |  | - |  | Fuel piping and valves | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F720N2 purge valve for EV burner would not operate. Caused a PLST trip.
BR7 | 2 | SF | 2021-01-18 07:02 |  |  |  |  | 2021-01-18 11:37 |  | 0 | 0 | 4.583 | 4.5833 | 783.75 | 1 |  |  |  | 0 |  |  | 172
|  | CAUSE CODE : |  | 4609 |  |  | - |  | Other exciter problems | [8 empty] | AMP CODE: |  | 70
|  | DESCRIPTION : |  | F700Found bad cable from SFC to BR6 AVR. SFC is shared between both BR6 and BR7
BR7 | 15 | SF | 2021-05-11 10:33 |  |  |  |  | 2021-05-11 13:17 |  | 0 | 0 | 2.733 | 2.7333 | 429.133 | 1 |  |  |  | 0 |  |  | 158
|  | CAUSE CODE : |  | 5050 |  |  | - |  | Ignition system | [8 empty] | AMP CODE: |  | 06
|  | DESCRIPTION : |  | F060Replaced bad ignition torch.
BR7 | 19 | SF | 2021-05-25 09:46 |  |  |  |  | 2021-05-25 10:50 |  | 0 | 0 | 1.067 | 1.0667 | 167.467 | 1 |  |  |  | 0 |  |  | 158
|  | CAUSE CODE : |  | 5050 |  |  | - |  | Ignition system | [8 empty] | AMP CODE: |  | 06
|  | DESCRIPTION : |  | F060Bad ignition torch
BR7 | 26 | U1 | 2021-06-20 14:38 |  |  |  |  | 2021-06-22 08:00 |  | 0 | 0 | 41.367 | 41.3667 | 6039.533 | 1 |  |  |  | 0 |  |  | 147
|  | CAUSE CODE : |  | 5016 |  |  | - |  | High pressure compressor bleed valves | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F540Blow off line flange gasket leak.
BR7 | 67 | U1 | 2021-12-13 17:43 |  |  |  |  | 2021-12-13 19:00 |  | 0 | 0 | 1.283 | 1.2833 | 219.45 | 1 |  |  |  | 0 |  |  | 172
|  | CAUSE CODE : |  | 3974 |  |  | - |  | DCS - logic problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | FP00Online tuning revision by GE commissioning engineer caused a unit trip.
BR7 | 6 | U1 | 2022-01-21 08:26 |  |  |  |  | 2022-01-21 15:24 |  | 0 | 0 | 6.967 | 6.9667 | 1191.3 | 1 |  |  |  | 0 |  |  | 172
|  | CAUSE CODE : |  | 5048 |  |  | - |  | Gas fuel system including controls and instrumentation | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Unit tripped due to to pulsations.
BR7 | 25 | SF | 2022-05-11 12:00 |  |  |  |  | 2022-05-11 15:06 |  | 0 | 0 | 3.1 | 3.1 | 486.7 | 1 |  |  |  | 0 |  |  | 158
|  | CAUSE CODE : |  | 5108 |  |  | - |  | High engine exhaust temperature | [8 empty] | AMP CODE: |  | 75
|  | DESCRIPTION : |  | F750TAT temps would not permit EV burners to stay lit
BR7 | 46 | U1 | 2022-06-15 08:02 |  |  |  |  | 2022-06-15 13:56 |  | 0 | 0 | 5.9 | 5.9 | 861.4 | 1 |  |  |  | 0 |  |  | 147
|  | CAUSE CODE : |  | 3972 |  |  | - |  | DCS - hardware problems (including card failure) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F700Primary controller card failure.
BR7 | 60 | SF | 2022-07-21 10:54 |  |  |  |  | 2022-07-21 16:00 |  | 0 | 0 | 5.1 | 5.1 | 744.6 | 1 |  |  |  | 0 |  |  | 147
|  | CAUSE CODE : |  | 8656 |  |  | - |  | Controls and instrumentation | [8 empty] | AMP CODE: |  | 52
|  | DESCRIPTION : |  | F520A malfunctioning RTD in the excitation transformer was sending a false signal to t
BR7 | 75 | U1 | 2022-08-29 09:56 |  |  |  |  | 2022-08-29 11:09 |  | 0 | 0 | 1.217 | 1.2167 | 177.633 | 1 |  |  |  | 0 |  |  | 147
|  | CAUSE CODE : |  | 4619 |  |  | - |  | Other hydrogen system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Generator tripped on reverse power.
BR7 | 81 | SF | 2022-10-18 06:00 |  |  |  |  | 2022-10-21 11:58 |  | 0 | 0 | 77.967 | 77.9667 | 12240.767 | 1 |  |  |  | 0 |  |  | 158
|  | CAUSE CODE : |  | 5001 |  |  | - |  | Inlet air vanes/nozzles | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Inlet guide vane controller issue well as AVR card issue
BR7 | 83 | U1 | 2022-10-24 11:07 |  |  |  |  | 2022-10-24 11:30 |  | 0 | 0 | 0.383 | 0.3833 | 60.183 | 1 |  |  |  | 0 |  |  | 158
|  | CAUSE CODE : |  | 5048 |  |  | - |  | Gas fuel system including controls and instrumentation | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Trip during switch over
BR7 | 6 | U1 | 2023-04-05 08:52 |  |  |  |  | 2023-04-05 09:34 |  | 0 | 0 | 0.7 | 0.7 | 109.9 | 1 |  |  |  | 0 |  |  | 158
|  | CAUSE CODE : |  | 5051 |  |  | - |  | Pilot fuel piping and valves | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Unit tripped during switchover. Temperature and MWs dipped during the last nitrog
BR7 | 10 | U1 | 2023-05-24 13:36 |  |  |  |  | 2023-05-24 14:13 |  | 0 | 0 | 0.617 | 0.6167 | 96.817 | 1 |  |  |  | 0 |  |  | 158
|  | CAUSE CODE : |  | 5048 |  |  | - |  | Gas fuel system including controls and instrumentation | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Nitrogen purge valve issue.
BR7 | 17 | U1 | 2023-06-06 20:51 |  |  |  |  | 2023-06-08 20:00 |  | 0 | 0 | 47.15 | 47.15 | 6883.9 | 1 |  |  |  | 0 |  |  | 147
|  | CAUSE CODE : |  | 5150 |  |  | - |  | Turning gear and motor | [8 empty] | AMP CODE: |  | 05
|  | DESCRIPTION : |  | F050Unit came off of rotor barring which resulted in slight seal rub.
BR7 | 21 | U1 | 2023-06-30 11:15 |  |  |  |  | 2023-06-30 18:04 |  | 0 | 0 | 6.817 | 6.8167 | 995.233 | 1 |  |  |  | 0 |  |  | 147
|  | CAUSE CODE : |  | 5073 |  |  | - |  | Flame scanners | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F780TAT spread alarm lead to combustion issues and pulsation alarms and an eventual tr
Brown - BR8
Unit | Event | Type | Start |  |  |  |  | End |  | GAC | NAC | Duration | Equiv Hrs | Equiv MWH | Cont | Work Start | Work End |  | Hours |  |  | Gross Capacity Impact (MW)
BR8 | 23 | U1 | 2014-03-31 05:56 |  |  |  |  | 2014-03-31 06:05 |  | 0 | 0 | 0.15 | 0.15 | 19.2 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 5016 |  |  | - |  | High pressure compressor bleed valves | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F660Trip due to compressor blow off valve not being closed. Unit tripped immediately
BR8 | 44 | SF | 2014-08-05 13:27 |  |  |  |  | 2014-08-05 14:34 |  | 0 | 0 | 1.117 | 1.1167 | 113.9 | 1 |  |  |  | 0 |  |  | 122
|  | CAUSE CODE : |  | 5048 |  |  | - |  | Gas fuel system including controls and instrumentation | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410MOS in substation did not go closed.
BR8 | 48 | U1 | 2014-08-19 11:44 |  |  |  |  | 2014-08-19 13:22 |  | 0 | 0 | 1.633 | 1.6333 | 166.6 | 1 |  |  |  | 0 |  |  | 122
|  | CAUSE CODE : |  | 5120 |  |  | - |  | Hydraulic oil system | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Bad current limiting plug on DC solenoid for DC trip block.
BR8 | 53 | SF | 2014-09-25 13:56 |  |  |  |  | 2014-09-25 14:18 |  | 0 | 0 | 0.367 | 0.3667 | 37.4 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410SFC trip due to Mod 300 IO diagnostic
BR8 | 65 | U1 | 2014-11-24 07:09 |  |  |  |  | 2014-11-24 11:11 |  | 0 | 0 | 4.033 | 4.0333 | 516.267 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 5246 |  |  | - |  | Gas Turbine Control System - hardware problems (including card failure) | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Speed Card Failure
BR8 | 8 | SF | 2015-01-26 07:36 |  |  |  |  | 2015-01-26 09:50 |  | 0 | 0 | 2.233 | 2.2333 | 285.867 | 1 |  |  |  | 0 |  |  | 129
|  | CAUSE CODE : |  | 5530 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Power oil valve on trip block not showing fully closed in controls.
BR8 | 12 | U1 | 2015-02-17 08:28 |  |  |  |  | 2015-02-17 12:30 |  | 0 | 0 | 4.033 | 4.0333 | 516.267 | 1 |  |  |  | 0 |  |  | 129
|  | CAUSE CODE : |  | 5065 |  |  | - |  | NOx water injection system including pump | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F060Outage to repair busted nox water line
BR8 | 14 | U1 | 2015-02-20 13:50 |  |  |  |  | 2015-02-22 10:52 |  | 0 | 0 | 45.033 | 45.0333 | 5764.266 | 1 |  |  |  | 0 |  |  | 129
|  | CAUSE CODE : |  | 3611 |  |  | - |  | Switchyard circuit breakers - external (OMC) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F660Hydraulic pump in substation breaker quit working.
BR8 | 21 | U1 | 2015-04-11 06:58 |  |  |  |  | 2015-04-11 07:02 |  | 0 | 0 | 0.067 | 0.0667 | 6.8 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 5246 |  |  | - |  | Gas Turbine Control System - hardware problems (including card failure) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F410Speed card failure on one channel tripped unit offline
BR8 | 27 | SF | 2015-05-04 12:49 |  |  |  |  | 2015-05-04 13:26 |  | 0 | 0 | 0.617 | 0.6167 | 62.9 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 3611 |  |  | - |  | Switchyard circuit breakers - external (OMC) | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Unit Generator circuit breaker went closed and immediately opened
BR8 | 30 | SF | 2015-05-07 10:44 |  |  |  |  | 2015-05-07 10:53 |  | 0 | 0 | 0.15 | 0.15 | 15.3 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 3611 |  |  | - |  | Switchyard circuit breakers - external (OMC) | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Generator circuit breaker went closed then immediately opened back up.
BR8 | 32 | SF | 2015-05-11 12:25 |  |  |  |  | 2015-05-11 12:33 |  | 0 | 0 | 0.133 | 0.1333 | 13.6 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 3610 |  |  | - |  | Switchyard circuit breakers - external (not OMC) | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Switchyear breaker would not close.
BR8 | 33 | U1 | 2015-05-11 12:59 |  |  |  |  | 2015-05-11 13:04 |  | 0 | 0 | 0.083 | 0.0833 | 8.5 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 5248 |  |  | - |  | Gas Turbine Control System - logic problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F410Unit deloaded itself.
BR8 | 34 | U1 | 2015-05-11 13:28 |  |  |  |  | 2015-05-11 13:29 |  | 0 | 0 | 0.017 | 0.0167 | 1.7 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 5248 |  |  | - |  | Gas Turbine Control System - logic problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F410Unit deloaded on its own.
BR8 | 35 | U1 | 2015-05-11 13:42 |  |  |  |  | 2015-05-11 13:43 |  | 0 | 0 | 0.017 | 0.0167 | 1.7 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 5248 |  |  | - |  | Gas Turbine Control System - logic problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F410Unit deloaded till offline
BR8 | 36 | U1 | 2015-05-11 13:58 |  |  |  |  | 2015-05-11 14:57 |  | 0 | 0 | 0.983 | 0.9833 | 100.3 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 5248 |  |  | - |  | Gas Turbine Control System - logic problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F410Unit deloaded until offline
BR8 | 38 | U1 | 2015-05-12 09:58 |  |  |  |  | 2015-05-12 13:31 |  | 0 | 0 | 3.55 | 3.55 | 362.1 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 3610 |  |  | - |  | Switchyard circuit breakers - external (not OMC) | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Substation crew outage to investigate substation breaker issues.
BR8 | 40 | U1 | 2015-05-13 08:33 |  |  |  |  | 2015-05-13 08:39 |  | 0 | 0 | 0.1 | 0.1 | 10.2 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 5248 |  |  | - |  | Gas Turbine Control System - logic problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F410Unit deloaded until offline.
BR8 | 41 | U1 | 2015-05-13 09:27 |  |  |  |  | 2015-05-13 12:13 |  | 0 | 0 | 2.767 | 2.7667 | 282.2 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 5248 |  |  | - |  | Gas Turbine Control System - logic problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F410Unit deloaded until offline.
BR8 | 43 | U1 | 2015-05-14 10:51 |  |  |  |  | 2015-05-14 12:28 |  | 0 | 0 | 1.617 | 1.6167 | 164.9 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 3610 |  |  | - |  | Switchyard circuit breakers - external (not OMC) | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F540Hydraulic leak on Substation generator circuit breaker would not allow breaker to
BR8 | 51 | SF | 2015-05-31 16:10 |  |  |  |  | 2015-05-31 16:32 |  | 0 | 0 | 0.367 | 0.3667 | 37.4 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410U9 3 position ISO drive stopped mid travel. This tied up the U8/U9 starting devic
BR8 | 61 | U1 | 2015-06-26 12:16 |  |  |  |  | 2015-06-26 14:17 |  | 0 | 0 | 2.017 | 2.0167 | 205.7 | 1 |  |  |  | 0 |  |  | 122
|  | CAUSE CODE : |  | 5201 |  |  | - |  | Load shaft and bearings | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F410Eractic #1 bearing thermocouple tripped unit on false signal.
BR8 | 74 | SF | 2015-07-17 09:05 |  |  |  |  | 2015-07-17 10:55 |  | 0 | 0 | 1.833 | 1.8333 | 221.833 | 1 |  |  |  | 0 |  |  | 122
|  | CAUSE CODE : |  | 5049 |  |  | - |  | Other fuel system problems | [8 empty] | AMP CODE: |  | 32
|  | DESCRIPTION : |  | F320Gas Control valve swinging during ramp up
BR8 | 76 | U1 | 2015-07-17 21:36 |  |  |  |  | 2015-07-23 16:00 |  | 0 | 0 | 138.4 | 138.4 | 16746.4 | 1 |  |  |  | 0 |  |  | 122
|  | CAUSE CODE : |  | 7820 |  |  | - |  | Bearings | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Cable bad for No1 bearing TCs. Extension cable melted from junction box to cablin
BR8 | 86 | SF | 2015-08-30 10:55 |  |  |  |  | 2015-08-30 12:11 |  | 0 | 0 | 1.267 | 1.2667 | 153.267 | 1 |  |  |  | 0 |  |  | 122
|  | CAUSE CODE : |  | 3611 |  |  | - |  | Switchyard circuit breakers - external (OMC) | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Start up failure due to failure to synchronize.
BR8 | 88 | SF | 2015-09-08 10:10 |  |  |  |  | 2015-09-08 10:23 |  | 0 | 0 | 0.217 | 0.2167 | 26.217 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 5048 |  |  | - |  | Gas fuel system including controls and instrumentation | [8 empty] | AMP CODE: |  | 72
|  | DESCRIPTION : |  | F720Unit swings due to pilot valve on gas control valve keep unit from syncing to grid
BR8 | 108 | SF | 2015-11-02 06:50 |  |  |  |  | 2015-11-02 06:55 |  | 0 | 0 | 0.083 | 0.0833 | 10.667 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 5447 |  |  | - |  | Gas fuel system including controls and instrumentation | [8 empty] | AMP CODE: |  | 72
|  | DESCRIPTION : |  | F720Unit breaker tripping open at sync causing MOS to go open.
BR8 | 24 | SF | 2016-03-14 06:12 |  |  |  |  | 2016-03-14 06:27 |  | 0 | 0 | 0.25 | 0.25 | 29.5 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 5051 |  |  | - |  | Pilot fuel piping and valves | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Gas control valve swinging caused issues during synchronization.
BR8 | 38 | SF | 2016-05-12 09:01 |  |  |  |  | 2016-05-12 10:38 |  | 0 | 0 | 1.617 | 1.6167 | 190.767 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Ice cube relay in controls for SFC switch over device failed.
BR8 | 42 | SF | 2016-05-27 08:58 |  |  |  |  | 2016-05-27 09:32 |  | 0 | 0 | 0.567 | 0.5667 | 66.867 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 3610 |  |  | - |  | Switchyard circuit breakers - external (not OMC) | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Trouble snychronizing to the grid. Breaker tripped open as soon as closing.
BR8 | 45 | SF | 2016-05-29 09:53 |  |  |  |  | 2016-05-29 10:19 |  | 0 | 0 | 0.433 | 0.4333 | 51.133 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 3610 |  |  | - |  | Switchyard circuit breakers - external (not OMC) | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Unit failed to sync to grid. Breaker tripped out as soon as it went closed.
BR8 | 47 | SF | 2016-05-30 09:35 |  |  |  |  | 2016-05-30 11:53 |  | 0 | 0 | 2.3 | 2.3 | 271.4 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 3610 |  |  | - |  | Switchyard circuit breakers - external (not OMC) | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Unit failed to sync online. Substation breaker tripped out as soon as going onlin
BR8 | 51 | SF | 2016-06-02 11:47 |  |  |  |  | 2016-06-03 09:35 |  | 0 | 0 | 21.8 | 21.8 | 2637.8 | 1 |  |  |  | 0 |  |  | 122
|  | CAUSE CODE : |  | 3610 |  |  | - |  | Switchyard circuit breakers - external (not OMC) | [8 empty] | AMP CODE: |  | 72
|  | DESCRIPTION : |  | F720Unit would not sync to the grid. Issue was the generator circuit breaker in the s
BR8 | 116 | U1 | 2016-09-07 22:00 |  |  |  |  | 2016-09-07 22:43 |  | 0 | 0 | 0.717 | 0.7167 | 84.567 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 3971 |  |  | - |  | DCS - data highway | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410DCS LAN went down causing 11N2 system to loose communication.
BR8 | 123 | U1 | 2016-10-05 10:28 |  |  |  |  | 2016-10-05 12:13 |  | 0 | 0 | 1.75 | 1.75 | 206.5 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 5454 |  |  | - |  | Water injection system | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F120Pressure switch for NOx pump discharge pressure leaking and clogged at snubber. A
BR8 | 124 | U1 | 2016-10-05 13:18 |  |  |  |  | 2016-10-05 15:54 |  | 0 | 0 | 2.6 | 2.6 | 306.8 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 5454 |  |  | - |  | Water injection system | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F120Outage to change pressure switch and clean line.
BR8 | 149 | SF | 2016-12-15 19:17 |  |  |  |  | 2016-12-16 02:59 |  | 0 | 0 | 7.7 | 7.7 | 985.6 | 1 |  |  |  | 0 |  |  | 129
|  | CAUSE CODE : |  | 4750 |  |  | - |  | Other generator controls and metering problems | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Speed probe or noise reduction capacitor went bad for speed measurement.
BR8 | 11 | SF | 2017-02-17 07:10 |  |  |  |  | 2017-02-17 14:01 |  | 0 | 0 | 6.85 | 6.85 | 876.8 | 1 |  |  |  | 0 |  |  | 129
|  | CAUSE CODE : |  | 5017 |  |  | - |  | Low pressure compressor bleed valves | [8 empty] | AMP CODE: |  | 54
|  | DESCRIPTION : |  | F540Regulators for blow off valve found to be leaking. Unit would not go online with
BR8 | 15 | U1 | 2017-02-25 21:24 |  |  |  |  | 2017-02-25 23:56 |  | 0 | 0 | 2.533 | 2.5333 | 324.267 | 1 |  |  |  | 0 |  |  | 129
|  | CAUSE CODE : |  | 4609 |  |  | - |  | Other exciter problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F410Loose connection in the generator voltage regulator cabinet.
BR8 | 28 | U1 | 2017-04-29 12:02 |  |  |  |  | 2017-04-29 13:20 |  | 0 | 0 | 1.3 | 1.3 | 153.4 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 5248 |  |  | - |  | Gas Turbine Control System - logic problems | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Switchover unit logic prevented units from being able to start.
BR8 | 34 | SF | 2017-05-19 09:09 |  |  |  |  | 2017-05-19 09:26 |  | 0 | 0 | 0.283 | 0.2833 | 33.433 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 3624 |  |  | - |  | Auxiliary generator voltage supply system | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Start up failure due to field breaker tripping upon closure.
BR8 | 63 | SF | 2017-07-31 12:20 |  |  |  |  | 2017-07-31 13:43 |  | 0 | 0 | 1.383 | 1.3833 | 167.383 | 1 |  |  |  | 0 |  |  | 122
|  | CAUSE CODE : |  | 3611 |  |  | - |  | Switchyard circuit breakers - external (OMC) | [8 empty] | AMP CODE: |  | 55
|  | DESCRIPTION : |  | F550Loose bolt on operating mechanism for the substation circuit breaker would not all
BR8 | 68 | SF | 2017-08-09 13:32 |  |  |  |  | 2017-08-09 13:51 |  | 0 | 0 | 0.317 | 0.3167 | 38.317 | 1 |  |  |  | 0 |  |  | 122
|  | CAUSE CODE : |  | 4700 |  |  | - |  | Generator voltage control | [8 empty] | AMP CODE: |  | 87
|  | DESCRIPTION : |  | F870Unit would not sync to grid due to substation voltage being low.
BR8 | 76 | U1 | 2017-09-08 08:36 |  |  |  |  | 2017-09-08 13:57 |  | 0 | 0 | 5.35 | 5.35 | 631.3 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 3612 |  |  | - |  | Switchyard system protection devices - external (OMC) | [8 empty] | AMP CODE: |  | X0
|  | DESCRIPTION : |  | FX00Brown North Substation Protection Disabled.
BR8 | 80 | SF | 2017-09-21 10:44 |  |  |  |  | 2017-09-21 13:31 |  | 0 | 0 | 2.783 | 2.7833 | 328.433 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 5049 |  |  | - |  | Other fuel system problems | [8 empty] | AMP CODE: |  | 72
|  | DESCRIPTION : |  | F720Failed start due to gas control valve swinging.
BR8 | 100 | SF | 2017-12-27 02:01 |  |  |  |  | 2017-12-27 14:10 |  | 0 | 0 | 12.15 | 12.15 | 1555.2 | 1 |  |  |  | 0 |  |  | 129
|  | CAUSE CODE : |  | 5530 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 72
|  | DESCRIPTION : |  | F720Found bad limit switch on three position ISO switch.
BR8 | 32 | SF | 2018-05-29 13:32 |  |  |  |  | 2018-05-29 13:40 |  | 0 | 0 | 0.133 | 0.1333 | 15.733 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 5250 |  |  | - |  | Other controls and instrumentation problems | [8 empty] | AMP CODE: |  | 42
|  | DESCRIPTION : |  | F420Dehumidifier for unit left in manual.
BR8 | 39 | SF | 2018-06-17 12:37 |  |  |  |  | 2018-06-17 16:54 |  | 0 | 0 | 4.283 | 4.2833 | 518.283 | 1 |  |  |  | 0 |  |  | 122
|  | CAUSE CODE : |  | 5246 |  |  | - |  | Gas Turbine Control System - hardware problems (including card failure) | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Synch sequencer failed.
BR8 | 63 | SF | 2018-09-04 12:39 |  |  |  |  | 2018-09-04 13:27 |  | 0 | 0 | 0.8 | 0.8 | 94.4 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 5048 |  |  | - |  | Gas fuel system including controls and instrumentation | [8 empty] | AMP CODE: |  | 69
|  | DESCRIPTION : |  | F690Varnish in Gas Turbine Control valve actuator. Cleaned pilot valve.
BR8 | 79 | U1 | 2018-10-07 17:28 |  |  |  |  | 2018-10-07 19:44 |  | 0 | 0 | 2.267 | 2.2667 | 267.467 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 3621 |  |  | - |  | Unit auxiliaries transformer | [8 empty] | AMP CODE: |  | 03
|  | DESCRIPTION : |  | F030Ligthning arrestor on BOP north transformer went to ground. Substation Crew did f
BR8 | 30 | U1 | 2019-10-21 09:08 |  |  |  |  | 2019-10-21 13:32 |  | 0 | 0 | 4.4 | 4.4 | 519.2 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 3612 |  |  | - |  | Switchyard system protection devices - external (OMC) | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Failed current transformer on substation circuit breaker for 87 Diff protection of
BR8 | 36 | U1 | 2019-11-16 12:52 |  |  |  |  | 2019-11-19 14:54 |  | 0 | 0 | 74.033 | 74.0333 | 8735.933 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 5550 |  |  | - |  | Turning gear and motor | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Rotor Barring motor replacement. After replacing pump would not prime. Replace p
BR8 | 39 | U1 | 2019-12-18 08:22 |  |  |  |  | 2019-12-18 11:40 |  | 0 | 0 | 3.3 | 3.3 | 422.4 | 1 |  |  |  | 0 |  |  | 129
|  | CAUSE CODE : |  | 5449 |  |  | - |  | Other fuel system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F090Tripped due to omega during fuel oil to gas switchover.
BR8 | 8 | U1 | 2020-03-23 14:53 |  |  |  |  | 2020-03-23 18:27 |  | 0 | 0 | 3.567 | 3.5667 | 420.867 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 5150 |  |  | - |  | Turning gear and motor | [8 empty] | AMP CODE: |  | 40
|  | DESCRIPTION : |  | F400Replaced rotor barring piston that had eroded.
BR8 | 20 | SF | 2020-06-26 09:48 |  |  |  |  | 2020-06-26 09:54 |  | 0 | 0 | 0.1 | 0.1 | 12.1 | 1 |  |  |  | 0 |  |  | 122
|  | CAUSE CODE : |  | 3619 |  |  | - |  | Other switchyard equipment - external (OMC) | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Limit switch on MOS in substation did not make. Substation crew will adjust.
BR8 | 35 | SF | 2020-10-09 10:53 |  |  |  |  | 2020-10-09 12:17 |  | 0 | 0 | 1.4 | 1.4 | 165.2 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 5050 |  |  | - |  | Ignition system | [8 empty] | AMP CODE: |  | 55
|  | DESCRIPTION : |  | F550Unit 8 would not light off resulting in start up failure
BR8 | 42 | SF | 2020-12-02 05:57 |  |  |  |  | 2020-12-02 06:23 |  | 0 | 0 | 0.433 | 0.4333 | 55.467 | 1 |  |  |  | 0 |  |  | 129
|  | CAUSE CODE : |  | 3823 |  |  | - |  | Closed cooling water heat exchangers | [8 empty] | AMP CODE: |  | V0
|  | DESCRIPTION : |  | FV00Unit fin fans would not run due to ice accumulation on blades. Fans would trip on
BR8 | 8 | U1 | 2021-02-17 03:48 |  |  |  |  | 2021-02-17 07:18 |  | 0 | 0 | 3.5 | 3.5 | 448 | 1 |  |  |  | 0 |  |  | 129
|  | CAUSE CODE : |  | 5016 |  |  | - |  | High pressure compressor bleed valves | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F690Had a compressor blow off valve that was slow to operate to closed posiiton. Once
BR8 | 12 | SF | 2021-03-16 05:52 |  |  |  |  | 2021-03-16 07:59 |  | 0 | 0 | 2.117 | 2.1167 | 249.767 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 4511 |  |  | - |  | "Rotor, General" | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340SFC control relay would not operate to apply starting field to roll unit.
BR8 | 36 | SF | 2021-08-29 16:44 |  |  |  |  | 2021-08-29 16:51 |  | 0 | 0 | 0.117 | 0.1167 | 14.117 | 1 |  |  |  | 0 |  |  | 122
|  | CAUSE CODE : |  | 3629 |  |  | - |  | Other switchyard or high voltage system problems - external | [8 empty] | AMP CODE: |  | 40
|  | DESCRIPTION : |  | F400Unit 8 motor operated switch would not operate. Had to manually actuate control re
BR8 | 43 | SF | 2021-11-02 05:36 |  |  |  |  | 2021-11-02 19:06 |  | 0 | 0 | 13.5 | 13.5 | 1593 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 5050 |  |  | - |  | Ignition system | [8 empty] | AMP CODE: |  | 06
|  | DESCRIPTION : |  | F060Spark plug faulty
BR8 | 23 | U1 | 2022-04-30 18:15 |  |  |  |  | 2022-04-30 20:15 |  | 0 | 0 | 2 | 2 | 236 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 4604 |  |  | - |  | Exciter drive - shaft | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Exciter vibration probe failed causing unit trip
BR8 | 41 | SF | 2022-07-06 08:54 |  |  |  |  | 2022-07-06 11:49 |  | 0 | 0 | 2.917 | 2.9167 | 352.917 | 1 |  |  |  | 0 |  |  | 122
|  | CAUSE CODE : |  | 5530 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 72
|  | DESCRIPTION : |  | F720Brush lifting device malfunction. Pulley stuck, causing cable to fall off.
BR8 | 56 | SF | 2022-08-31 09:58 |  |  |  |  | 2022-08-31 10:18 |  | 0 | 0 | 0.333 | 0.3333 | 40.333 | 1 |  |  |  | 0 |  |  | 122
|  | CAUSE CODE : |  | 5650 |  |  | - |  | Other controls and instrumentation problems | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340A limit switch on U8 ISO switch malfuctioned and failed to send the propper signal
BR8 | 74 | U1 | 2022-12-23 01:30 |  |  |  |  | 2022-12-23 03:36 |  | 0 | 0 | 2.1 | 2.1 | 268.8 | 1 |  |  |  | 0 |  |  | 129
|  | CAUSE CODE : |  | 5041 |  |  | - |  | Fuel piping and valves | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F480Fuel valves froze because valves heaters to the 11N2 units kept going out.
BR8 | 75 | U1 | 2022-12-23 03:36 |  |  |  |  | 2022-12-23 06:26 |  | 0 | 0 | 2.833 | 2.8333 | 362.667 | 1 |  |  |  | 0 |  |  | 129
|  | CAUSE CODE : |  | 5111 |  |  | - |  | Lube oil pumps | [8 empty] | AMP CODE: |  | 57
|  | DESCRIPTION : |  | F570Malfunctioning lube oil pump
BR8 | 25 | SF | 2023-07-14 11:29 |  |  |  |  | 2023-07-14 13:43 |  | 0 | 0 | 2.233 | 2.2333 | 270.233 | 1 |  |  |  | 0 |  |  | 122
|  | CAUSE CODE : |  | 3611 |  |  | - |  | Switchyard circuit breakers - external (OMC) | [8 empty] | AMP CODE: |  | X0
|  | DESCRIPTION : |  | FX00Substation breaker limit switch was broken
BR8 | 36 | SF | 2023-09-21 13:00 |  |  |  |  | 2023-09-21 13:04 |  | 0 | 0 | 0.067 | 0.0667 | 7.867 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 3611 |  |  | - |  | Switchyard circuit breakers - external (OMC) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340Substation breaker closed and then reopened which led to an issue requiring the MO
Brown - BR9
Unit | Event | Type | Start |  |  |  |  | End |  | GAC | NAC | Duration | Equiv Hrs | Equiv MWH | Cont | Work Start | Work End |  | Hours |  |  | Gross Capacity Impact (MW)
BR9 | 3 | U1 | 2014-01-07 09:33 |  |  |  |  | 2014-01-07 10:36 |  | 0 | 0 | 1.05 | 1.05 | 144.9 | 1 |  |  |  | 0 |  |  | 139
|  | CAUSE CODE : |  | 5140 |  |  | - |  | Battery and charger system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F410Both battery chargers indicated failure. Failure was caused by low output current
BR9 | 17 | U1 | 2014-03-04 09:27 |  |  |  |  | 2014-03-04 10:06 |  | 0 | 0 | 0.65 | 0.65 | 89.7 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 5246 |  |  | - |  | Gas Turbine Control System - hardware problems (including card failure) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F410Unit tripped when unit 11's MOS opened.
BR9 | 38 | SF | 2014-09-25 13:56 |  |  |  |  | 2014-09-25 14:14 |  | 0 | 0 | 0.3 | 0.3 | 30.6 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410SFC trip due to Mod 300 IO diagnostic
BR9 | 40 | U1 | 2014-10-07 18:34 |  |  |  |  | 2014-10-07 18:35 |  | 0 | 0 | 0.017 | 0.0167 | 2.3 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 5049 |  |  | - |  | Other fuel system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F420Gas supply not set up correctly.
BR9 | 11 | U1 | 2015-02-17 08:40 |  |  |  |  | 2015-02-17 12:30 |  | 0 | 0 | 3.833 | 3.8333 | 529 | 1 |  |  |  | 0 |  |  | 139
|  | CAUSE CODE : |  | 5065 |  |  | - |  | NOx water injection system including pump | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F060Outage to repair busted Nox water line
BR9 | 43 | SF | 2015-05-31 16:10 |  |  |  |  | 2015-05-31 16:46 |  | 0 | 0 | 0.6 | 0.6 | 61.2 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 72
|  | DESCRIPTION : |  | F7203 Position ISO switch stopped mid travel. This tied up SFC for two units.
BR9 | 85 | U1 | 2015-08-19 00:01 |  |  |  |  | 2015-08-19 04:52 |  | 0 | 0 | 4.85 | 4.85 | 586.85 | 1 |  |  |  | 0 |  |  | 122
|  | CAUSE CODE : |  | 3979 |  |  | - |  | Other DCS problems | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410SKF overspeed device showing trip after start up of roter barring system.
BR9 | 87 | U1 | 2015-08-21 12:26 |  |  |  |  | 2015-08-21 15:27 |  | 0 | 0 | 3.017 | 3.0167 | 365.017 | 1 |  |  |  | 0 |  |  | 122
|  | CAUSE CODE : |  | 5111 |  |  | - |  | Lube oil pumps | [8 empty] | AMP CODE: |  | 06
|  | DESCRIPTION : |  | F060Sheared coupling on unit's jacking oil pump.
BR9 | 104 | U1 | 2015-10-21 08:31 |  |  |  |  | 2015-10-21 10:36 |  | 0 | 0 | 2.083 | 2.0833 | 287.5 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 3624 |  |  | - |  | Auxiliary generator voltage supply system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F410Trip due to AVR. Believe issue was caused by relay setting being to tight on AVR
BR9 | 112 | SF | 2015-10-30 05:10 |  |  |  |  | 2015-10-30 05:16 |  | 0 | 0 | 0.1 | 0.1 | 13.8 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 5246 |  |  | - |  | Gas Turbine Control System - hardware problems (including card failure) | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410IO diagnostice caused starting device function group not to release.
BR9 | 21 | SF | 2016-03-15 18:10 |  |  |  |  | 2016-03-15 19:46 |  | 0 | 0 | 1.6 | 1.6 | 188.8 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 5530 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Brush lift off device for the SFC did not engage. Unit would not roll up past 20M
BR9 | 24 | SF | 2016-03-28 09:04 |  |  |  |  | 2016-03-28 13:24 |  | 0 | 0 | 4.333 | 4.3333 | 511.333 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 5530 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 69
|  | DESCRIPTION : |  | F690Start up failure due to brush lift off device not going closed.
BR9 | 29 | SF | 2016-04-11 05:35 |  |  |  |  | 2016-04-11 06:30 |  | 0 | 0 | 0.917 | 0.9167 | 108.167 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 5050 |  |  | - |  | Ignition system | [8 empty] | AMP CODE: |  | 46
|  | DESCRIPTION : |  | F460Unit failed to light off due to possible low propane pressure for ignitor system.
BR9 | 31 | U1 | 2016-04-17 09:54 |  |  |  |  | 2016-04-18 14:14 |  | 0 | 0 | 28.333 | 28.3333 | 3343.333 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 5240 |  |  | - |  | Fire detection and extinguishing system (including hazardous gas detection system) | [8 empty] | AMP CODE: |  | 54
|  | DESCRIPTION : |  | F540Main discharge valve for CO2 suppression system is leaking through. This caused V
BR9 | 34 | SF | 2016-04-20 09:50 |  |  |  |  | 2016-04-20 12:08 |  | 0 | 0 | 2.3 | 2.3 | 271.4 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 5050 |  |  | - |  | Ignition system | [8 empty] | AMP CODE: |  | 46
|  | DESCRIPTION : |  | F460Unit failed to light off.
BR9 | 41 | SF | 2016-05-12 07:59 |  |  |  |  | 2016-05-14 09:06 |  | 0 | 0 | 49.117 | 49.1167 | 5795.767 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 5450 |  |  | - |  | Ignition system | [8 empty] | AMP CODE: |  | 43
|  | DESCRIPTION : |  | F430Unit failed to light off.
BR9 | 62 | U1 | 2016-06-26 15:46 |  |  |  |  | 2016-06-26 16:08 |  | 0 | 0 | 0.367 | 0.3667 | 44.367 | 1 |  |  |  | 0 |  |  | 122
|  | CAUSE CODE : |  | 9020 |  |  | - |  | Lightning | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F410Unit tripped due to gas valves in reducing station going closed due to lightning s
BR9 | 98 | U1 | 2016-08-20 10:14 |  |  |  |  | 2016-08-20 10:43 |  | 0 | 0 | 0.483 | 0.4833 | 58.483 | 1 |  |  |  | 0 |  |  | 122
|  | CAUSE CODE : |  | 5250 |  |  | - |  | Other controls and instrumentation problems | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Redundant overspeed lost power. Triped unit control system. We believe breaker tr
BR9 | 107 | SF | 2016-09-06 11:18 |  |  |  |  | 2016-09-06 15:07 |  | 0 | 0 | 3.817 | 3.8167 | 450.367 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 3972 |  |  | - |  | DCS - hardware problems (including card failure) | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Trip channel did not reset for one of the protection processors causing unit not t
BR9 | 110 | U1 | 2016-09-07 22:00 |  |  |  |  | 2016-09-07 22:43 |  | 0 | 0 | 0.717 | 0.7167 | 84.567 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 3971 |  |  | - |  | DCS - data highway | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410DCS LAN went down causing 11N2 system to lose communication.
BR9 | 118 | U1 | 2016-09-19 14:45 |  |  |  |  | 2016-09-19 14:46 |  | 0 | 0 | 0.017 | 0.0167 | 1.967 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 3610 |  |  | - |  | Switchyard circuit breakers - external (not OMC) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F410Substation GCB opened when Unit 11's motor operated switch went closed.
BR9 | 121 | U1 | 2016-09-22 20:51 |  |  |  |  | 2016-09-22 21:15 |  | 0 | 0 | 0.4 | 0.4 | 47.2 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 3610 |  |  | - |  | Switchyard circuit breakers - external (not OMC) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F410Unit tripped when U11's motor operated switch went open. Controls tripped due to
BR9 | 126 | U1 | 2016-10-05 21:39 |  |  |  |  | 2016-10-05 21:49 |  | 0 | 0 | 0.167 | 0.1667 | 19.667 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 3610 |  |  | - |  | Switchyard circuit breakers - external (not OMC) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F410Unit tripped when U11 MOS was opened. Tripped on speed disturbance.
BR9 | 131 | SF | 2016-10-17 11:18 |  |  |  |  | 2016-10-17 11:48 |  | 0 | 0 | 0.5 | 0.5 | 59 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 5050 |  |  | - |  | Ignition system | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Glow plug for ignition system looked to be faulty. Unit did start up on second at
BR9 | 132 | U1 | 2016-10-17 21:22 |  |  |  |  | 2016-10-19 07:21 |  | 0 | 0 | 33.983 | 33.9833 | 4010.033 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 5050 |  |  | - |  | Ignition system | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F410Outage to replace glow plug for unit.
BR9 | 136 | U1 | 2016-10-27 17:34 |  |  |  |  | 2016-10-27 17:35 |  | 0 | 0 | 0.017 | 0.0167 | 1.967 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 5246 |  |  | - |  | Gas Turbine Control System - hardware problems (including card failure) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F410Unit tripped when unit 11 came offline and MOS opened in the substation.
BR9 | 3 | U1 | 2017-01-08 11:25 |  |  |  |  | 2017-01-08 11:40 |  | 0 | 0 | 0.25 | 0.25 | 34.5 | 1 |  |  |  | 0 |  |  | 139
|  | CAUSE CODE : |  | 3979 |  |  | - |  | Other DCS problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F410Unit tripped when Unit 11's MOS went open.
BR9 | 17 | U1 | 2017-04-27 11:51 |  |  |  |  | 2017-04-27 11:52 |  | 0 | 0 | 0.017 | 0.0167 | 1.967 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 3624 |  |  | - |  | Auxiliary generator voltage supply system | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F420Voltage regulator found on line supply after commissioning.
BR9 | 19 | U1 | 2017-04-29 12:02 |  |  |  |  | 2017-04-29 13:20 |  | 0 | 0 | 1.3 | 1.3 | 153.4 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 5248 |  |  | - |  | Gas Turbine Control System - logic problems | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Switch over unit logic prevent units from being able to start.
BR9 | 46 | U1 | 2017-09-08 08:36 |  |  |  |  | 2017-09-08 13:57 |  | 0 | 0 | 5.35 | 5.35 | 631.3 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 3612 |  |  | - |  | Switchyard system protection devices - external (OMC) | [8 empty] | AMP CODE: |  | X0
|  | DESCRIPTION : |  | FX00Brown North Substation Protection Disabled.
BR9 | 64 | U1 | 2017-12-27 02:01 |  |  |  |  | 2017-12-27 04:34 |  | 0 | 0 | 2.55 | 2.55 | 351.9 | 1 |  |  |  | 0 |  |  | 139
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Start up failure on U8 tied up SFC preventing unit 9 from starting.
BR9 | 14 | U1 | 2018-03-05 06:37 |  |  |  |  | 2018-03-05 14:37 |  | 0 | 0 | 8 | 8 | 944 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 5065 |  |  | - |  | NOx water injection system including pump | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F410I to P failed on the NOx water injection control valve.
BR9 | 30 | SF | 2018-08-07 11:07 |  |  |  |  | 2018-08-07 13:12 |  | 0 | 0 | 2.083 | 2.0833 | 252.083 | 1 |  |  |  | 0 |  |  | 122
|  | CAUSE CODE : |  | 3619 |  |  | - |  | Other switchyard equipment - external (OMC) | [8 empty] | AMP CODE: |  | 06
|  | DESCRIPTION : |  | F060Limit switch not working on substation MOS.
BR9 | 35 | SF | 2018-09-18 09:36 |  |  |  |  | 2018-09-18 10:07 |  | 0 | 0 | 0.517 | 0.5167 | 60.967 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 3611 |  |  | - |  | Switchyard circuit breakers - external (OMC) | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410MOS limit in substation would not allow substation breaker to go closed for unit t
BR9 | 41 | U1 | 2018-10-07 17:28 |  |  |  |  | 2018-10-07 19:44 |  | 0 | 0 | 2.267 | 2.2667 | 267.467 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 3621 |  |  | - |  | Unit auxiliaries transformer | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F030Ligthning arrestor on BOP north transformer went to ground. Substation Crew did f
BR9 | 12 | SF | 2019-03-04 16:50 |  |  |  |  | 2019-03-04 20:00 |  | 0 | 0 | 3.167 | 3.1667 | 373.667 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 06
|  | DESCRIPTION : |  | F060Broken limit switch in 3 position ISO drive. Replaced limit switch.
BR9 | 26 | U1 | 2019-05-13 19:20 |  |  |  |  | 2019-05-14 15:42 |  | 0 | 0 | 20.367 | 20.3667 | 2403.267 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 5150 |  |  | - |  | Turning gear and motor | [8 empty] | AMP CODE: |  | 62
|  | DESCRIPTION : |  | F620Outage to replace pump and motor for rotor barring system. Motor was changed firs
BR9 | 41 | SF | 2019-08-10 14:25 |  |  |  |  | 2019-08-10 16:02 |  | 0 | 0 | 1.617 | 1.6167 | 195.617 | 1 |  |  |  | 0 |  |  | 122
|  | CAUSE CODE : |  | 3610 |  |  | - |  | Switchyard circuit breakers - external (not OMC) | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Limit switch on MOS would trip breaker upon closure. Thought issue was a diagnost
BR9 | 43 | SF | 2019-08-11 12:58 |  |  |  |  | 2019-08-11 14:36 |  | 0 | 0 | 1.633 | 1.6333 | 197.633 | 1 |  |  |  | 0 |  |  | 122
|  | CAUSE CODE : |  | 3610 |  |  | - |  | Switchyard circuit breakers - external (not OMC) | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Limit switch in MOS tripped substation breaker upon closure. Will adjust limit sw
BR9 | 51 | SF | 2019-08-20 12:35 |  |  |  |  | 2019-08-20 14:41 |  | 0 | 0 | 2.1 | 2.1 | 254.1 | 1 |  |  |  | 0 |  |  | 122
|  | CAUSE CODE : |  | 5050 |  |  | - |  | Ignition system | [8 empty] | AMP CODE: |  | 43
|  | DESCRIPTION : |  | F430Failed glow plug prevented propane ignition. Third attempt was a succesful light
BR9 | 53 | U1 | 2019-08-20 15:54 |  |  |  |  | 2019-08-22 12:07 |  | 0 | 0 | 44.217 | 44.2167 | 5350.217 | 1 |  |  |  | 0 |  |  | 122
|  | CAUSE CODE : |  | 5450 |  |  | - |  | Ignition system | [8 empty] | AMP CODE: |  | 43
|  | DESCRIPTION : |  | F430Flame on test failed. Problem was glow plug and not being able to light off. Fue
BR9 | 70 | SF | 2019-10-21 09:08 |  |  |  |  | 2019-10-21 13:32 |  | 0 | 0 | 4.4 | 4.4 | 519.2 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 3612 |  |  | - |  | Switchyard system protection devices - external (OMC) | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Failed current transformer on substation circuit breaker for 87 Diff protection of
BR9 | 11 | SF | 2020-03-28 03:06 |  |  |  |  | 2020-03-28 09:26 |  | 0 | 0 | 6.333 | 6.3333 | 747.333 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 3611 |  |  | - |  | Switchyard circuit breakers - external (OMC) | [8 empty] | AMP CODE: |  | 54
|  | DESCRIPTION : |  | F540Hydraulic Oil Leak Substation Breaker.
BR9 | 54 | U1 | 2020-12-26 09:29 |  |  |  |  | 2020-12-26 09:41 |  | 0 | 0 | 0.2 | 0.2 | 27.6 | 1 |  |  |  | 0 |  |  | 139
|  | CAUSE CODE : |  | 5011 |  |  | - |  | High pressure bearings | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Erratic temperature indication. Bearing temperature spiked causing unit PLST. Appe
BR9 | 10 | SF | 2021-02-17 04:57 |  |  |  |  | 2021-02-17 07:29 |  | 0 | 0 | 2.533 | 2.5333 | 349.6 | 1 |  |  |  | 0 |  |  | 139
|  | CAUSE CODE : |  | 3661 |  |  | - |  | 4000-7000 volt circuit breakers | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340Medium voltage breaker for starting transformer would not close.
BR9 | 20 | U1 | 2021-04-12 07:44 |  |  |  |  | 2021-04-12 09:31 |  | 0 | 0 | 1.783 | 1.7833 | 210.433 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 5250 |  |  | - |  | Other controls and instrumentation problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820#1 bearing temperature was erratic and resulted in a unit trip.
BR9 | 10 | SF | 2022-03-23 06:51 |  |  |  |  | 2022-03-23 08:05 |  | 0 | 0 | 1.233 | 1.2333 | 145.533 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 4609 |  |  | - |  | Other exciter problems | [8 empty] | AMP CODE: |  | 70
|  | DESCRIPTION : |  | F700Failed 48 VDC contact relay for SFC controls prevented unit from rolling up.
BR9 | 12 | U1 | 2022-04-06 21:53 |  |  |  |  | 2022-04-07 00:46 |  | 0 | 0 | 2.883 | 2.8833 | 340.234 | 1 |  |  |  | 0 |  |  | 119
|  | CAUSE CODE : |  | 3611 |  |  | - |  | Switchyard circuit breakers - external (OMC) | [8 empty] | AMP CODE: |  | 54
|  | DESCRIPTION : |  | F540Hydraulic leak on breaker.
BR9 | 19 | U1 | 2022-06-07 09:40 |  |  |  |  | 2022-06-07 13:37 |  | 0 | 0 | 3.95 | 3.95 | 477.95 | 1 |  |  |  | 0 |  |  | 122
|  | CAUSE CODE : |  | 5121 |  |  | - |  | Hydraulic oil system pumps | [8 empty] | AMP CODE: |  | 06
|  | DESCRIPTION : |  | F060Lift oil pump had bad motor
BR9 | 35 | SF | 2022-07-06 09:16 |  |  |  |  | 2022-07-06 12:04 |  | 0 | 0 | 2.8 | 2.8 | 338.8 | 1 |  |  |  | 0 |  |  | 122
|  | CAUSE CODE : |  | 3618 |  |  | - |  | Other switchyard equipment - external (not OMC) | [8 empty] | AMP CODE: |  | 72
|  | DESCRIPTION : |  | F720Motor operated switch in the substation, after the breaker, was hung up and would
BR9 | 58 | U1 | 2022-12-23 01:30 |  |  |  |  | 2022-12-23 03:50 |  | 0 | 0 | 2.333 | 2.3333 | 322 | 1 |  |  |  | 0 |  |  | 139
|  | CAUSE CODE : |  | 5041 |  |  | - |  | Fuel piping and valves | [8 empty] | AMP CODE: |  | 48
|  | DESCRIPTION : |  | F480Frozen fuel valves due to valves heaters to the 11N2 units kept going out.
BR9 | 26 | U1 | 2023-07-27 14:01 |  |  |  |  | 2023-07-27 14:36 |  | 0 | 0 | 0.583 | 0.5833 | 70.583 | 1 |  |  |  | 0 |  |  | 122
|  | CAUSE CODE : |  | 5041 |  |  | - |  | Fuel piping and valves | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Fuel gas feed valve did not actuate properly.
Cane Run - CR7
Unit | Event | Type | Start |  |  |  |  | End |  | GAC | NAC | Duration | Equiv Hrs | Equiv MWH | Cont | Work Start | Work End |  | Hours |  |  | Gross Capacity Impact (MW)
CR7 | 13 | U1 | 2015-07-21 19:17 |  |  |  |  | 2015-07-22 06:06 |  | 0 | 0 | 10.817 | 10.8167 | 6944.3 | 1 |  |  |  | 0 |  |  | 675
|  | CAUSE CODE : |  | 3681 |  |  | - |  | Other voltage circuit breakers | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F870Blown fuse on 6.9 kV Switchgear 004 PT circuit. Fuse replaced
CR7 | 15 | SF | 2015-07-22 06:06 |  |  |  |  | 2015-07-22 06:49 |  | 0 | 0 | 0.717 | 0.7167 | 460.1 | 1 |  |  |  | 0 |  |  | 675
|  | CAUSE CODE : |  | 3431 |  |  | - |  | Other feedwater valves | [8 empty] | AMP CODE: |  | 40
|  | DESCRIPTION : |  | F400BFP 101 recirculation flow too low. Recirculation valve tuned
CR7 | 29 | SF | 2015-08-08 14:38 |  |  |  |  | 2015-08-08 15:08 |  | 0 | 0 | 0.5 | 0.5 | 321 | 1 |  |  |  | 0 |  |  | 675
|  | CAUSE CODE : |  | 5250 |  |  | - |  | Other controls and instrumentation problems | [8 empty] | AMP CODE: |  | 40
|  | DESCRIPTION : |  | F400Loss of CT2 speed indication. Speed pickups reset
CR7 | 30 | U1 | 2015-08-08 16:30 |  |  |  |  | 2015-08-08 17:40 |  | 0 | 0 | 1.167 | 1.1667 | 749 | 1 |  |  |  | 0 |  |  | 675
|  | CAUSE CODE : |  | 6112 |  |  | - |  | Other HP steam valves (including vent and drain valves but not including the turbine stop valves) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F420Pressure differential across HRSG 1 steam blending valves too high
CR7 | 51 | U1 | 2015-09-14 01:10 |  |  |  |  | 2015-09-14 06:12 |  | 0 | 0 | 5.033 | 5.0333 | 3231.4 | 1 |  |  |  | 0 |  |  | 707
|  | CAUSE CODE : |  | 3830 |  |  | - |  | Auxiliary boiler | [8 empty] | AMP CODE: |  | 52
|  | DESCRIPTION : |  | F520Aux. boiler failed to start due to drum level probes. Probes cleaned
CR7 | 53 | U1 | 2015-09-14 06:42 |  |  |  |  | 2015-09-14 08:06 |  | 0 | 0 | 1.4 | 1.4 | 898.8 | 1 |  |  |  | 0 |  |  | 707
|  | CAUSE CODE : |  | 3320 |  |  | - |  | Condensate piping | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F120Cond. strainer clogged causing loss of cond. pump and BFP 201. Cleaned
CR7 | 62 | U1 | 2015-10-12 14:02 |  |  |  |  | 2015-10-12 15:42 |  | 0 | 0 | 1.667 | 1.6667 | 1145 | 1 |  |  |  | 0 |  |  | 707
|  | CAUSE CODE : |  | 3350 |  |  | - |  | Condensate polishing and filtering systems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F420Both BFPs tripped when condensate polisher placed in service
CR7 | 6 | U1 | 2016-01-11 13:46 |  |  |  |  | 2016-01-12 06:25 |  | 0 | 0 | 16.65 | 16.65 | 11371.95 | 1 |  |  |  | 0 |  |  | 696
|  | CAUSE CODE : |  | 0775 |  |  | - |  | Economizer piping | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F540HRSG1 IP Economizer Inlet Relief Valve lifting. Valve rebuilt
CR7 | 16 | U1 | 2016-02-01 08:22 |  |  |  |  | 2016-02-01 10:02 |  | 0 | 0 | 1.667 | 1.6667 | 1138.333 | 1 |  |  |  | 0 |  |  | 696
|  | CAUSE CODE : |  | 3689 |  |  | - |  | Other voltage problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F450Auxiliary bus lost when CT2 GSU isolated and tie-breaker not closed
CR7 | 23 | U1 | 2016-02-21 15:04 |  |  |  |  | 2016-02-21 15:45 |  | 0 | 0 | 0.683 | 0.6833 | 466.717 | 1 |  |  |  | 0 |  |  | 696
|  | CAUSE CODE : |  | 0540 |  |  | - |  | Hot reheat steam piping up to turbine stop valves | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F420HRSG 1 HRH header pressure too high when bypass vlv couldn't be opened
CR7 | 67 | U1 | 2016-10-05 00:10 |  |  |  |  | 2016-10-05 03:42 |  | 0 | 0 | 3.533 | 3.5333 | 2452.133 | 1 |  |  |  | 0 |  |  | 707
|  | CAUSE CODE : |  | 3230 |  |  | - |  | Circulating water valves | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F130Cooling tower riser valve closed causing circ water pump, block trip
CR7 | 68 | U1 | 2016-10-05 04:50 |  |  |  |  | 2016-10-05 06:18 |  | 0 | 0 | 1.467 | 1.4667 | 1017.867 | 1 |  |  |  | 0 |  |  | 707
|  | CAUSE CODE : |  | 3407 |  |  | - |  | Feedwater pump suction screens | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F120BFP 201 tripped because of high suction strainer DP
CR7 | 69 | U1 | 2016-10-05 07:10 |  |  |  |  | 2016-10-05 11:00 |  | 0 | 0 | 3.833 | 3.8333 | 2660.333 | 1 |  |  |  | 0 |  |  | 707
|  | CAUSE CODE : |  | 3407 |  |  | - |  | Feedwater pump suction screens | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F120BFP 101 tripped because of high suction strainer DP
CR7 | 81 | U1 | 2016-12-08 23:56 |  |  |  |  | 2016-12-09 03:37 |  | 0 | 0 | 3.683 | 3.6833 | 2515.716 | 1 |  |  |  | 0 |  |  | 696
|  | CAUSE CODE : |  | 9290 |  |  | - |  | Other fuel quality problems (OMC) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | FX00Poor gas quality caused turbine unloads resulting in block outage
CR7 | 2 | U1 | 2017-02-06 10:06 |  |  |  |  | 2017-02-06 11:59 |  | 0 | 0 | 1.883 | 1.8833 | 1286.317 | 1 |  |  |  | 0 |  |  | 696
|  | CAUSE CODE : |  | 6174 |  |  | - |  | IP startup bypass instrumentation and controls | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F120HRSG 1 HRH bypass spray flow transmitter line plugged. Cleared and calibrated
CR7 | 5 | U1 | 2017-02-07 21:58 |  |  |  |  | 2017-02-08 03:02 |  | 0 | 0 | 5.067 | 5.0667 | 3460.534 | 1 |  |  |  | 0 |  |  | 696
|  | CAUSE CODE : |  | 6171 |  |  | - |  | IP Startup bypass system valves | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F420HRH bypass valve opened causing CT1 and ST trip, CT2 startup failure
CR7 | 11 | U1 | 2017-02-13 13:18 |  |  |  |  | 2017-02-15 08:30 |  | 0 | 0 | 43.2 | 43.2 | 29505.6 | 1 |  |  |  | 0 |  |  | 696
|  | CAUSE CODE : |  | 6171 |  |  | - |  | IP Startup bypass system valves | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F540HRSG 1 HRH bypass valve spray nozzle leaking. Replaced soft goods
CR7 | 48 | U1 | 2017-06-22 19:17 |  |  |  |  | 2017-06-22 20:29 |  | 0 | 0 | 1.2 | 1.2 | 794.4 | 1 |  |  |  | 0 |  |  | 675
|  | CAUSE CODE : |  | 6171 |  |  | - |  | IP Startup bypass system valves | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F300HRSG 2 HRH bypass valve stuck closed causing extreme water loss. CT2 shutdown
CR7 | 53 | U1 | 2017-07-13 11:15 |  |  |  |  | 2017-07-13 12:56 |  | 0 | 0 | 1.683 | 1.6833 | 1114.367 | 1 |  |  |  | 0 |  |  | 675
|  | CAUSE CODE : |  | 3310 |  |  | - |  | Condensate/hotwell pumps | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F420Condensate pump trip after cut-in of suction strainer caused block trip
CR7 | 54 | U1 | 2017-07-13 13:00 |  |  |  |  | 2017-07-13 13:59 |  | 0 | 0 | 0.983 | 0.9833 | 650.967 | 1 |  |  |  | 0 |  |  | 675
|  | CAUSE CODE : |  | 6120 |  |  | - |  | IP steam piping up to turbine stop valves - Between 200 & 600 PSIG (see 0790 for piping supports) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F780CT2 tripped due to high IP steam outlet temperature
CR7 | 56 | U1 | 2017-07-13 16:19 |  |  |  |  | 2017-07-13 19:11 |  | 0 | 0 | 2.867 | 2.8667 | 1897.733 | 1 |  |  |  | 0 |  |  | 675
|  | CAUSE CODE : |  | 6171 |  |  | - |  | IP Startup bypass system valves | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F300HRSG 2 HRH bypass valve stuck closed causing extreme water loss. CT2 shutdown
CR7 | 59 | U1 | 2017-07-14 02:53 |  |  |  |  | 2017-07-14 02:57 |  | 0 | 0 | 0.067 | 0.0667 | 44.133 | 1 |  |  |  | 0 |  |  | 675
|  | CAUSE CODE : |  | 6171 |  |  | - |  | IP Startup bypass system valves | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F300HRSG2 HRH bypass valve stuck closed. CT1 shutdown to facilitate Unit 2 restart
CR7 | 61 | U1 | 2017-07-14 04:46 |  |  |  |  | 2017-07-14 05:45 |  | 0 | 0 | 0.983 | 0.9833 | 650.967 | 1 |  |  |  | 0 |  |  | 675
|  | CAUSE CODE : |  | 6171 |  |  | - |  | IP Startup bypass system valves | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F300HRSG 2 HRH bypass valve stuck closed causing extreme water loss. CT2 shutdown
CR7 | 12 | U1 | 2018-02-24 11:53 |  |  |  |  | 2018-02-24 13:15 |  | 0 | 0 | 1.367 | 1.3667 | 933.433 | 1 |  |  |  | 0 |  |  | 696
|  | CAUSE CODE : |  | 5247 |  |  | - |  | Gas Turbine Control System - internal and termination wiring | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F700CT1 Stage A Fuel Gas Valve solenoid wiring short, causing erratic operation
CR7 | 13 | SF | 2018-02-24 13:15 |  |  |  |  | 2018-02-25 01:50 |  | 0 | 0 | 12.583 | 12.5833 | 8594.417 | 1 |  |  |  | 0 |  |  | 696
|  | CAUSE CODE : |  | 5247 |  |  | - |  | Gas Turbine Control System - internal and termination wiring | [8 empty] | AMP CODE: |  | 70
|  | DESCRIPTION : |  | F700CT1 Stage A Fuel Gas Valve solenoid wiring short, causing erratic operation
CR7 | 4 | U1 | 2019-02-02 23:05 |  |  |  |  | 2019-02-03 00:42 |  | 0 | 0 | 1.617 | 1.6167 | 1104.183 | 1 |  |  |  | 0 |  |  | 696
|  | CAUSE CODE : |  | 3210 |  |  | - |  | Circulating water pumps | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F420CWP B tripped when CWP A motor was started for rotation check
CR7 | 29 | U1 | 2019-08-10 14:17 |  |  |  |  | 2019-08-10 17:17 |  | 0 | 0 | 3 | 3 | 1986 | 1 |  |  |  | 0 |  |  | 675
|  | CAUSE CODE : |  | 3350 |  |  | - |  | Condensate polishing and filtering systems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F420Both BFPs tripped during condensate polisher swap causing CR7 block outage
CR7 | 16 | U1 | 2020-04-03 16:06 |  |  |  |  | 2020-04-04 00:35 |  | 0 | 0 | 8.483 | 8.4833 | 5887.433 | 1 |  |  |  | 0 |  |  | 707
|  | CAUSE CODE : |  | 5041 |  |  | - |  | Fuel piping and valves | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F120CT2 trip on blade path spread due to clogged fuel strainer. Cleaned strainer and r
CR7 | 26 | U1 | 2020-05-04 23:05 |  |  |  |  | 2020-05-05 00:16 |  | 0 | 0 | 1.183 | 1.1833 | 821.234 | 1 |  |  |  | 0 |  |  | 707
|  | CAUSE CODE : |  | 3430 |  |  | - |  | Feedwater regulating (boiler level control) valve | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F400CT1, ST tripped during HRSG 2 unblending on high HRSG 1 IP drum level. Restarted
CR7 | 46 | U3 | 2020-11-12 23:20 |  |  |  |  | 2020-11-13 13:58 |  | 0 | 0 | 14.633 | 14.6333 | 10155.533 | 1 |  |  |  | 0 |  |  | 707
|  | CAUSE CODE : |  | 6114 |  |  | - |  | HP steam isolation/boundary valves | [8 empty] | AMP CODE: |  | 54
|  | DESCRIPTION : |  | F540HRSG 1 main steam header isolation valve packing leak. Replaced packing
CR7 | 47 | U1 | 2020-11-13 18:19 |  |  |  |  | 2020-11-15 17:36 |  | 0 | 0 | 47.283 | 47.2833 | 32814.633 | 1 |  |  |  | 0 |  |  | 707
|  | CAUSE CODE : |  | 6114 |  |  | - |  | HP steam isolation/boundary valves | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F540HRSG 1 main steam header isolation valve bonnet leak. Rebuilt valve with new press
CR7 | 6 | U1 | 2021-02-23 10:32 |  |  |  |  | 2021-02-23 12:47 |  | 0 | 0 | 2.25 | 2.25 | 1536.75 | 1 |  |  |  | 0 |  |  | 696
|  | CAUSE CODE : |  | 3350 |  |  | - |  | Condensate polishing and filtering systems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F660Block trip on loss of condensate during polisher swap due to level switch malfunct
CR7 | 9 | SF | 2022-05-01 13:47 |  |  |  |  | 2022-05-01 14:52 |  | 0 | 0 | 1.083 | 1.0833 | 751.833 | 1 |  |  |  | 0 |  |  | 707
|  | CAUSE CODE : |  | 5041 |  |  | - |  | Fuel piping and valves | [8 empty] | AMP CODE: |  | 72
|  | DESCRIPTION : |  | F720CT2 overfuel protection trip due to malfunctioning gas vent valve. Restarted
CR7 | 10 | U1 | 2022-05-01 15:39 |  |  |  |  | 2022-05-01 19:25 |  | 0 | 0 | 3.767 | 3.7667 | 2614.067 | 1 |  |  |  | 0 |  |  | 707
|  | CAUSE CODE : |  | 3407 |  |  | - |  | Feedwater pump suction screens | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F120CT2 tripped following BFP 201 trip due to high strainer DP
CR7 | 11 | U1 | 2022-05-01 20:16 |  |  |  |  | 2022-05-01 21:46 |  | 0 | 0 | 1.5 | 1.5 | 1041 | 1 |  |  |  | 0 |  |  | 707
|  | CAUSE CODE : |  | 6122 |  |  | - |  | Other IP steam valves (including vent and drain valves but not including the turbine stop valves) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F660CT2 tripped due to low kettle boiler level. Restarted
CR7 | 12 | U1 | 2022-05-01 22:43 |  |  |  |  | 2022-05-01 23:54 |  | 0 | 0 | 1.183 | 1.1833 | 821.233 | 1 |  |  |  | 0 |  |  | 707
|  | CAUSE CODE : |  | 6122 |  |  | - |  | Other IP steam valves (including vent and drain valves but not including the turbine stop valves) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F660CT2 tripped due to low kettle boiler level. Restarted
CR7 | 13 | SF | 2022-05-01 23:54 |  |  |  |  | 2022-05-02 00:20 |  | 0 | 0 | 0.433 | 0.4333 | 300.733 | 1 |  |  |  | 0 |  |  | 707
|  | CAUSE CODE : |  | 5050 |  |  | - |  | Ignition system | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340CT2 ignition failure due to improperly installed ignitor
CR7 | 15 | SF | 2022-05-02 00:20 |  |  |  |  | 2022-05-02 01:16 |  | 0 | 0 | 0.933 | 0.9333 | 647.733 | 1 |  |  |  | 0 |  |  | 707
|  | CAUSE CODE : |  | 5050 |  |  | - |  | Ignition system | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340CT2 ignition failure due to improperly installed ignitor
CR7 | 27 | U1 | 2022-05-31 05:30 |  |  |  |  | 2022-06-01 07:40 |  | 0 | 0 | 26.167 | 26.1667 | 17914.333 | 1 |  |  |  | 0 |  |  | 707
|  | CAUSE CODE : |  | 4800 |  |  | - |  | Generator main leads | [8 empty] | AMP CODE: |  | 03
|  | DESCRIPTION : |  | F030CT1 / CT2 unavailable to facilitate uncoupling of ST generator
CR7 | 31 | SF | 2022-06-10 09:07 |  |  |  |  | 2022-06-10 09:49 |  | 0 | 0 | 0.7 | 0.7 | 463.4 | 1 |  |  |  | 0 |  |  | 675
|  | CAUSE CODE : |  | 5050 |  |  | - |  | Ignition system | [8 empty] | AMP CODE: |  | 40
|  | DESCRIPTION : |  | F400CT1 ignition failure. Restarted
CR7 | 55 | U1 | 2022-12-13 09:18 |  |  |  |  | 2022-12-13 11:05 |  | 0 | 0 | 1.783 | 1.7833 | 1218.017 | 1 |  |  |  | 0 |  |  | 696
|  | CAUSE CODE : |  | 3330 |  |  | - |  | Condensate valves | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F420Block trip on loss of condensate pressure when pump suction valve was opened
CR7 | 56 | U1 | 2022-12-13 13:35 |  |  |  |  | 2022-12-13 14:24 |  | 0 | 0 | 0.817 | 0.8167 | 557.783 | 1 |  |  |  | 0 |  |  | 696
|  | CAUSE CODE : |  | 5041 |  |  | - |  | Fuel piping and valves | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F130Block trip when fuel gas regulating station slam-shut valves tripped
CR7 | 57 | SF | 2022-12-13 14:24 |  |  |  |  | 2022-12-13 15:34 |  | 0 | 0 | 1.167 | 1.1667 | 796.833 | 1 |  |  |  | 0 |  |  | 696
|  | CAUSE CODE : |  | 0801 |  |  | - |  | HP Drum (including drum level trips not attributable to other causes) | [8 empty] | AMP CODE: |  | 40
|  | DESCRIPTION : |  | F400CT2 trip during startup due to low HP drum level. Restarted
CR7 | 4 | SF | 2023-01-18 15:03 |  |  |  |  | 2023-01-18 16:04 |  | 0 | 0 | 1.017 | 1.0167 | 694.383 | 1 |  |  |  | 0 |  |  | 696
|  | CAUSE CODE : |  | 5041 |  |  | - |  | Fuel piping and valves | [8 empty] | AMP CODE: |  | 66
|  | DESCRIPTION : |  | F660CT2 operator-initiated fired abort to correct lifting fuel gas pressure relief val
CR7 | 5 | U1 | 2023-01-18 16:40 |  |  |  |  | 2023-01-18 17:44 |  | 0 | 0 | 1.067 | 1.0667 | 728.533 | 1 |  |  |  | 0 |  |  | 696
|  | CAUSE CODE : |  | 6122 |  |  | - |  | Other IP steam valves (including vent and drain valves but not including the turbine stop valves) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F400CT2 trip on low kettle boiler level when HRH startup vent left in manual
CR7 | 10 | U1 | 2023-05-01 06:25 |  |  |  |  | 2023-05-01 10:05 |  | 0 | 0 | 3.667 | 3.6667 | 2544.667 | 1 |  |  |  | 0 |  |  | 707
|  | CAUSE CODE : |  | 5160 |  |  | - |  | Cooling and seal air system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F520CT1 trip on high RAC temperature due to incorrectly calibrated level transmitters
CR7 | 11 | U1 | 2023-05-01 11:49 |  |  |  |  | 2023-05-01 13:08 |  | 0 | 0 | 1.317 | 1.3167 | 913.767 | 1 |  |  |  | 0 |  |  | 707
|  | CAUSE CODE : |  | 3822 |  |  | - |  | Closed cooling water valves | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F420CT1 trip after BFP due to high oil temp. CCCW temp control left in manual
CR7 | 12 | U1 | 2023-05-01 17:47 |  |  |  |  | 2023-05-02 10:50 |  | 0 | 0 | 17.05 | 17.05 | 11832.7 | 1 |  |  |  | 0 |  |  | 707
|  | CAUSE CODE : |  | 6171 |  |  | - |  | IP Startup bypass system valves | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F540Block shutdown to recover demineralized water supply after prolonged venting
DIX - Dix 1
Unit | Event | Type | Start |  |  |  |  | End |  | GAC | NAC | Duration | Equiv Hrs | Equiv MWH | Cont | Work Start | Work End |  | Hours |  |  | Gross Capacity Impact (MW)
Dix 1 | 3 | U1 | 2014-01-03 15:36 |  |  |  |  | 2014-02-06 13:21 |  | 0 | 0 | 813.75 | 813.75 | 6510 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 7121 |  |  | - |  | Shutoff valves | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | Johnson valve failed to close fully
Dix 1 | 29 | SF | 2014-10-09 05:59 |  |  |  |  | 2014-10-09 06:43 |  | 0 | 0 | 0.733 | 0.7333 | 5.867 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 7121 |  |  | - |  | Shutoff valves | [8 empty] | AMP CODE: |  | 52
|  | DESCRIPTION : |  | F520Limit switch for the johnson valve went bad
Dix 1 | 30 | U1 | 2014-10-09 07:20 |  |  |  |  | 2014-10-09 09:19 |  | 0 | 0 | 1.983 | 1.9833 | 15.867 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 7121 |  |  | - |  | Shutoff valves | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F400Johnson valve was drifting shut.
Dix 1 | 31 | U1 | 2014-10-09 09:34 |  |  |  |  | 2014-10-09 12:53 |  | 0 | 0 | 3.317 | 3.3167 | 26.533 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 7121 |  |  | - |  | Shutoff valves | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F400Johnson valve drifting closed.
Dix 1 | 32 | U1 | 2014-10-09 13:09 |  |  |  |  | 2014-10-09 13:47 |  | 0 | 0 | 0.633 | 0.6333 | 5.067 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 7121 |  |  | - |  | Shutoff valves | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F400Johnson valve drifting closed.
Dix 1 | 1 | U1 | 2016-01-01 07:34 |  |  |  |  | 2016-01-01 08:20 |  | 0 | 0 | 0.767 | 0.7667 | 8.05 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 4552 |  |  | - |  | Generator lube oil system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F570Low Oil Pressure auto-trip
Dix 1 | 2 | U1 | 2016-01-01 08:25 |  |  |  |  | 2016-01-01 08:45 |  | 0 | 0 | 0.333 | 0.3333 | 3.5 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 4552 |  |  | - |  | Generator lube oil system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F570Low Oil Pressure auto-trip
Dix 1 | 6 | U1 | 2016-01-18 23:19 |  |  |  |  | 2016-01-19 01:05 |  | 0 | 0 | 1.767 | 1.7667 | 18.55 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 3898 |  |  | - |  | Miscellaneous plant auxiliary process and services instrumentation and controls | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F570Governor Oil Pressure Low Indication
Dix 1 | 7 | U1 | 2016-01-19 01:06 |  |  |  |  | 2016-01-19 02:36 |  | 0 | 0 | 1.5 | 1.5 | 15.75 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 7053 |  |  | - |  | Governor oil system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F570Low Oil Flow indication
Dix 1 | 8 | U1 | 2016-01-19 02:37 |  |  |  |  | 2016-01-19 08:30 |  | 0 | 0 | 5.883 | 5.8833 | 61.775 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 7003 |  |  | - |  | Lube oil system (use code 7007 to report bearing failures due to lube oil problems) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F570Guide Bearing Oil Flow Low Trip
Dix 1 | 15 | U1 | 2016-02-16 20:47 |  |  |  |  | 2016-02-16 22:48 |  | 0 | 0 | 2.017 | 2.0167 | 21.175 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 7003 |  |  | - |  | Lube oil system (use code 7007 to report bearing failures due to lube oil problems) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F570Governing Oil System Needed Filter Replacement Caused Trip
Dix 1 | 17 | SF | 2016-03-07 06:05 |  |  |  |  | 2016-03-07 07:56 |  | 0 | 0 | 1.85 | 1.85 | 19.425 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 3899 |  |  | - |  | Other miscellaneous auxiliary system problems | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | Possible Breaker Pannel Issue
Dix 1 | 19 | SF | 2016-03-08 05:31 |  |  |  |  | 2016-03-08 08:18 |  | 0 | 0 | 2.783 | 2.7833 | 29.225 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 3899 |  |  | - |  | Other miscellaneous auxiliary system problems | [8 empty] | AMP CODE: |  | 55
|  | DESCRIPTION : |  | Possible Loose Wire for pannel
Dix 1 | 33 | U1 | 2016-05-26 21:34 |  |  |  |  | 2016-05-26 22:47 |  | 0 | 0 | 1.217 | 1.2167 | 12.775 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 7053 |  |  | - |  | Governor oil system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F120Governor Oil
Dix 1 | 90 | SF | 2016-11-02 12:56 |  |  |  |  | 2016-11-02 15:11 |  | 0 | 0 | 2.25 | 2.25 | 23.625 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 7052 |  |  | - |  | "Other turbine control problems (Report specific wicket gate controls, etc., using the code for the appropriate equipment item.)" | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | Speed No-Load Trip due to incorrect timeout setting
Dix 1 | 3 | U1 | 2017-01-25 14:57 |  |  |  |  | 2017-01-25 15:26 |  | 0 | 0 | 0.483 | 0.4833 | 5.075 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 7053 |  |  | - |  | Governor oil system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | Clogged filter on turbine governing oil system.
Dix 1 | 85 | U1 | 2017-10-14 10:56 |  |  |  |  | 2017-10-14 12:03 |  | 0 | 0 | 1.117 | 1.1167 | 11.725 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 7052 |  |  | - |  | "Other turbine control problems (Report specific wicket gate controls, etc., using the code for the appropriate equipment item.)" | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | Turbine governor controls unresponsive
Dix 1 | 86 | U1 | 2017-10-14 12:07 |  |  |  |  | 2017-10-14 14:33 |  | 0 | 0 | 2.433 | 2.4333 | 25.55 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 7052 |  |  | - |  | "Other turbine control problems (Report specific wicket gate controls, etc., using the code for the appropriate equipment item.)" | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | Turbine governor controls unresponsive
Dix 1 | 34 | U1 | 2018-09-23 11:43 |  |  |  |  | 2018-09-23 13:19 |  | 0 | 0 | 1.6 | 1.6 | 16.8 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 7053 |  |  | - |  | Governor oil system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F120Unit tripped due to clogged gov oil filter.
Dix 1 | 44 | U1 | 2018-11-05 14:19 |  |  |  |  | 2018-11-05 15:08 |  | 0 | 0 | 0.817 | 0.8167 | 8.575 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 7052 |  |  | - |  | "Other turbine control problems (Report specific wicket gate controls, etc., using the code for the appropriate equipment item.)" | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F410Unit would not load up due to control room HMI issue.
Dix 1 | 50 | U1 | 2018-12-07 16:09 |  |  |  |  | 2018-12-07 21:43 |  | 0 | 0 | 5.567 | 5.5667 | 58.45 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 3684 |  |  | - |  | Other voltage protection devices | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F490Differential trip caused by ground on CT cirtuit
Dix 1 | 51 | U1 | 2018-12-10 11:53 |  |  |  |  | 2018-12-10 13:57 |  | 0 | 0 | 2.067 | 2.0667 | 21.7 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 7009 |  |  | - |  | Bearing oil system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | Tripped due to bearing low oil flow
Dix 1 | 52 | U1 | 2018-12-10 13:59 |  |  |  |  | 2018-12-10 16:21 |  | 0 | 0 | 2.367 | 2.3667 | 24.85 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 7009 |  |  | - |  | Bearing oil system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | Tripped due to low bearing oil flow
Dix 1 | 8 | U1 | 2020-04-13 07:40 |  |  |  |  | 2020-04-13 08:09 |  | 0 | 0 | 0.483 | 0.4833 | 5.075 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 7053 |  |  | - |  | Governor oil system | [8 empty] | AMP CODE: |  | 66
|  | DESCRIPTION : |  | F660Low gov oil resevoir level
Dix 1 | 18 | U1 | 2020-04-27 00:19 |  |  |  |  | 2020-04-27 01:49 |  | 0 | 0 | 1.5 | 1.5 | 15.75 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 7053 |  |  | - |  | Governor oil system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F120Low gov oil press - swapped filter.
Dix 1 | 29 | U1 | 2020-06-11 20:10 |  |  |  |  | 2020-06-12 02:20 |  | 0 | 0 | 6.167 | 6.1667 | 64.75 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 3720 |  |  | - |  | Transmission equipment at the 1st substation (see code 9300 if applicable) | [8 empty] | AMP CODE: |  | 79
|  | DESCRIPTION : |  | F790Testing the DX 3 GSU and needed DX 1 offline.
Dix 1 | 71 | U1 | 2020-12-29 11:57 |  |  |  |  | 2020-12-30 12:26 |  | 0 | 0 | 24.483 | 24.4833 | 257.075 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 4602 |  |  | - |  | Exciter commutator and brushes | [8 empty] | AMP CODE: |  | 10
|  | DESCRIPTION : |  | F100Issue with exciter brushes.
Dix 1 | 72 | U1 | 2020-12-30 12:34 |  |  |  |  | 2021-01-01 |  | 0 | 0 | 35.433 | 35.4333 | 372.05 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 4602 |  |  | - |  | Exciter commutator and brushes | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F100Issue with exciter brushes. Honing exciter ring.
Dix 1 | 1 | U1 | 2021-01-01 |  |  |  |  | 2021-01-18 14:10 |  | 0 | 0 | 422.167 | 422.1667 | 4432.75 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 4602 |  |  | - |  | Exciter commutator and brushes | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F100Issue with exciter brushes. Honing exciter ring.
Dix 1 | 87 | U1 | 2021-12-28 08:40 |  |  |  |  | 2021-12-28 09:18 |  | 0 | 0 | 0.633 | 0.6333 | 6.65 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 7009 |  |  | - |  | Bearing oil system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F120Guide bearing low oil flow
Dix 1 | 88 | U1 | 2021-12-28 09:19 |  |  |  |  | 2021-12-28 09:57 |  | 0 | 0 | 0.633 | 0.6333 | 6.65 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 7009 |  |  | - |  | Bearing oil system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F120Guide bearing low oil flow - replaced pressure switch.
Dix 1 | 4 | U1 | 2022-02-15 15:34 |  |  |  |  | 2022-03-03 15:38 |  | 0 | 0 | 384.067 | 384.0667 | 4032.7 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 7160 |  |  | - |  | Pressure regulating valve | [8 empty] | AMP CODE: |  | 72
|  | DESCRIPTION : |  | F720Control valve for Johnson valve out for repairs.
Dix 1 | 13 | U1 | 2023-03-27 10:00 |  |  |  |  | 2023-03-29 07:30 |  | 0 | 0 | 45.5 | 45.5 | 477.75 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 4560 |  |  | - |  | Generator vibration (excluding vibration due to failed bearing and other components) | [8 empty] | AMP CODE: |  | 85
|  | DESCRIPTION : |  | F850High guide bearing vibration on startup caused lockout
Dix 1 | 34 | U1 | 2023-10-04 04:33 |  |  |  |  | 2023-10-04 08:27 |  | 0 | 0 | 3.9 | 3.9 | 40.95 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 7121 |  |  | - |  | Shutoff valves | [8 empty] | AMP CODE: |  | 72
|  | DESCRIPTION : |  | F720Johnson Valve Issue
DIX - Dix 2
Unit | Event | Type | Start |  |  |  |  | End |  | GAC | NAC | Duration | Equiv Hrs | Equiv MWH | Cont | Work Start | Work End |  | Hours |  |  | Gross Capacity Impact (MW)
Dix 2 | 8 | SF | 2014-03-25 16:00 |  |  |  |  | 2014-03-25 17:48 |  | 0 | 0 | 1.8 | 1.8 | 14.4 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 7199 |  |  | - |  | Other water supply/discharge problems (use for equipment related problems; use codes 9135 or 9320 for lack of water or discharge limit related problems) | [8 empty] | AMP CODE: |  | X0
|  | DESCRIPTION : |  | Johnson valve would not open
Dix 2 | 23 | SF | 2015-05-04 04:50 |  |  |  |  | 2015-05-04 06:32 |  | 0 | 0 | 1.7 | 1.7 | 17.85 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 7121 |  |  | - |  | Shutoff valves | [8 empty] | AMP CODE: |  | 06
|  | DESCRIPTION : |  | F060Johnson Valve would not open after long service and first close
Dix 2 | 68 | U1 | 2015-12-06 20:31 |  |  |  |  | 2015-12-06 21:39 |  | 0 | 0 | 1.133 | 1.1333 | 11.9 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 3898 |  |  | - |  | Miscellaneous plant auxiliary process and services instrumentation and controls | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | FX00Unknown Johnson Valve or Wicket Gate issue. Issue still under investigation.
Dix 2 | 69 | U1 | 2015-12-08 08:29 |  |  |  |  | 2015-12-09 17:52 |  | 0 | 0 | 33.383 | 33.3833 | 350.525 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 3898 |  |  | - |  | Miscellaneous plant auxiliary process and services instrumentation and controls | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | FP00After looking into any/all connection issues, E&I along with Generation engineerin
Dix 2 | 9 | SF | 2016-03-07 06:05 |  |  |  |  | 2016-03-07 08:01 |  | 0 | 0 | 1.933 | 1.9333 | 20.3 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 3899 |  |  | - |  | Other miscellaneous auxiliary system problems | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | Possible Breaker Pannel issue.
Dix 2 | 11 | SF | 2016-03-08 05:31 |  |  |  |  | 2016-03-08 08:20 |  | 0 | 0 | 2.817 | 2.8167 | 29.575 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 3899 |  |  | - |  | Other miscellaneous auxiliary system problems | [8 empty] | AMP CODE: |  | 43
|  | DESCRIPTION : |  | New heating system power connected to start up power and taking too much draw when uni
Dix 2 | 24 | U1 | 2016-05-27 07:26 |  |  |  |  | 2016-05-27 07:45 |  | 0 | 0 | 0.317 | 0.3167 | 3.325 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 9910 |  |  | - |  | Maintenance personnel error | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | FX00Generator Lockout: Bearing water strainers human error trip.
Dix 2 | 85 | U1 | 2016-12-21 17:39 |  |  |  |  | 2016-12-22 08:19 |  | 0 | 0 | 14.667 | 14.6667 | 154 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 4710 |  |  | - |  | Generator metering devices | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | Lost generator bearing temperature indications
Dix 2 | 87 | U1 | 2016-12-22 11:49 |  |  |  |  | 2016-12-22 13:45 |  | 0 | 0 | 1.933 | 1.9333 | 20.3 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 4710 |  |  | - |  | Generator metering devices | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | Lost generator bearing temperature indications.
Dix 2 | 89 | U1 | 2016-12-22 14:38 |  |  |  |  | 2016-12-22 15:33 |  | 0 | 0 | 0.917 | 0.9167 | 9.625 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 4710 |  |  | - |  | Generator metering devices | [8 empty] | AMP CODE: |  | 52
|  | DESCRIPTION : |  | Swapped control card with Dix #3 to restore gen brg temp indications.
Dix 2 | 50 | U1 | 2017-06-26 15:09 |  |  |  |  | 2017-06-26 15:48 |  | 0 | 0 | 0.65 | 0.65 | 6.825 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 4750 |  |  | - |  | Other generator controls and metering problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | Issue with VAR control limited generator output
Dix 2 | 51 | U1 | 2017-06-26 16:04 |  |  |  |  | 2017-06-26 16:52 |  | 0 | 0 | 0.8 | 0.8 | 8.4 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 4750 |  |  | - |  | Other generator controls and metering problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | Issue with VAR control limited generator output
Dix 2 | 43 | U1 | 2018-12-12 18:08 |  |  |  |  | 2018-12-12 20:25 |  | 0 | 0 | 2.283 | 2.2833 | 23.975 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 7009 |  |  | - |  | Bearing oil system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | Tripped due to low bearing oil flow
Dix 2 | 44 | U1 | 2018-12-13 01:30 |  |  |  |  | 2018-12-13 08:51 |  | 0 | 0 | 7.35 | 7.35 | 77.175 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 7009 |  |  | - |  | Bearing oil system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | Tripped due to low bearing oil flow
Dix 2 | 5 | U1 | 2020-04-13 07:40 |  |  |  |  | 2020-04-13 08:09 |  | 0 | 0 | 0.483 | 0.4833 | 5.075 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 7053 |  |  | - |  | Governor oil system | [8 empty] | AMP CODE: |  | 66
|  | DESCRIPTION : |  | F660Low gov oil resevoir level
Dix 2 | 26 | U1 | 2020-06-11 20:10 |  |  |  |  | 2020-06-12 02:20 |  | 0 | 0 | 6.167 | 6.1667 | 64.75 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 3720 |  |  | - |  | Transmission equipment at the 1st substation (see code 9300 if applicable) | [8 empty] | AMP CODE: |  | 79
|  | DESCRIPTION : |  | F790Testing the DX 3 GSU and needed DX 2 offline.
Dix 2 | 28 | U1 | 2020-06-15 15:02 |  |  |  |  | 2020-06-15 15:29 |  | 0 | 0 | 0.45 | 0.45 | 4.725 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 4560 |  |  | - |  | Generator vibration (excluding vibration due to failed bearing and other components) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F850Tripped due to generator vibration
Dix 2 | 29 | U1 | 2020-06-15 15:30 |  |  |  |  | 2020-06-15 16:36 |  | 0 | 0 | 1.1 | 1.1 | 11.55 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 4560 |  |  | - |  | Generator vibration (excluding vibration due to failed bearing and other components) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F850Tripped due to generator vibration
Dix 2 | 2 | U1 | 2021-01-08 07:13 |  |  |  |  | 2021-01-08 12:02 |  | 0 | 0 | 4.817 | 4.8167 | 50.575 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 3644 |  |  | - |  | AC Protection devices | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F550Loss of main power feed panel due blown fuse caused by suspected loose wire.
Dix 2 | 6 | U1 | 2021-01-08 12:15 |  |  |  |  | 2021-01-08 13:09 |  | 0 | 0 | 0.9 | 0.9 | 9.45 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 7199 |  |  | - |  | Other water supply/discharge problems (use for equipment related problems; use codes 9135 or 9320 for lack of water or discharge limit related problems) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F590Removed unit to pump down water sumps.
Dix 2 | 21 | U1 | 2021-03-26 10:46 |  |  |  |  | 2021-04-09 14:16 |  | 0 | 0 | 339.5 | 339.5 | 3564.75 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 4609 |  |  | - |  | Other exciter problems | [8 empty] | AMP CODE: |  | 53
|  | DESCRIPTION : |  | F530Sent exciter out for repair due to low reading on DAR testing.
Dix 2 | 81 | U1 | 2021-11-12 12:48 |  |  |  |  | 2021-11-12 13:31 |  | 0 | 0 | 0.717 | 0.7167 | 7.525 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 7121 |  |  | - |  | Shutoff valves | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F120Tripped Due to Unexpected Johnson Valve Operation caused by clogged strainer
Dix 2 | 87 | U1 | 2021-11-19 06:04 |  |  |  |  | 2021-11-19 06:38 |  | 0 | 0 | 0.567 | 0.5667 | 5.95 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 7121 |  |  | - |  | Shutoff valves | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F120Johnson valve tripped shut.
Dix 2 | 88 | U1 | 2021-11-19 06:53 |  |  |  |  | 2021-11-19 07:38 |  | 0 | 0 | 0.75 | 0.75 | 7.875 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 7121 |  |  | - |  | Shutoff valves | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F120Johnson valve tripped shut.
Dix 2 | 89 | U1 | 2021-11-19 07:51 |  |  |  |  | 2021-11-19 09:33 |  | 0 | 0 | 1.7 | 1.7 | 17.85 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 7121 |  |  | - |  | Shutoff valves | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F120Johnson valve tripped shut.
Dix 2 | 97 | U1 | 2021-12-08 15:58 |  |  |  |  | 2021-12-08 16:44 |  | 0 | 0 | 0.767 | 0.7667 | 8.05 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 7052 |  |  | - |  | "Other turbine control problems (Report specific wicket gate controls, etc., using the code for the appropriate equipment item.)" | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Johnson Valve lost open limit.
Dix 2 | 98 | U1 | 2021-12-08 16:45 |  |  |  |  | 2021-12-08 17:31 |  | 0 | 0 | 0.767 | 0.7667 | 8.05 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 7052 |  |  | - |  | "Other turbine control problems (Report specific wicket gate controls, etc., using the code for the appropriate equipment item.)" | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Johnson Valve lost open limit.
Dix 2 | 99 | U1 | 2021-12-08 17:32 |  |  |  |  | 2021-12-08 19:26 |  | 0 | 0 | 1.9 | 1.9 | 19.95 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 7052 |  |  | - |  | "Other turbine control problems (Report specific wicket gate controls, etc., using the code for the appropriate equipment item.)" | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Johnson Valve lost open limit.
Dix 2 | 17 | U1 | 2022-08-14 11:26 |  |  |  |  | 2022-08-14 13:49 |  | 0 | 0 | 2.383 | 2.3833 | 25.025 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 4550 |  |  | - |  | Generator bearings and lube oil system (including thrust bearings on hydro units) | [8 empty] | AMP CODE: |  | 76
|  | DESCRIPTION : |  | F760Problem with thrust bearing temperature.
Dix 2 | 18 | U1 | 2022-08-14 13:51 |  |  |  |  | 2022-08-14 17:52 |  | 0 | 0 | 4.017 | 4.0167 | 42.175 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 4550 |  |  | - |  | Generator bearings and lube oil system (including thrust bearings on hydro units) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F760Removed due to high thrust bearing temp. Adjusted thrust shoe.
DIX - Dix 3
Unit | Event | Type | Start |  |  |  |  | End |  | GAC | NAC | Duration | Equiv Hrs | Equiv MWH | Cont | Work Start | Work End |  | Hours |  |  | Gross Capacity Impact (MW)
Dix 3 | 9 | SF | 2014-02-03 06:00 |  |  |  |  | 2014-02-03 06:26 |  | 0 | 0 | 0.433 | 0.4333 | 3.467 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 7121 |  |  | - |  | Shutoff valves | [8 empty] | AMP CODE: |  | 69
|  | DESCRIPTION : |  | Johnson Valve wouldn't move for Operations, Valve stroked fine for Maintenance.
Dix 3 | 12 | U1 | 2014-02-15 02:49 |  |  |  |  | 2014-02-17 12:02 |  | 0 | 0 | 57.217 | 57.2167 | 457.734 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 3970 |  |  | - |  | Distributive Control System (DCS) - process computer | [8 empty] | AMP CODE: |  | X0
|  | DESCRIPTION : |  | Lost HMI control power
Dix 3 | 34 | U1 | 2015-07-06 12:47 |  |  |  |  | 2015-07-06 13:48 |  | 0 | 0 | 1.017 | 1.0167 | 10.675 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 4720 |  |  | - |  | Generator synchronization equipment | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Unit failed to synchronize
Dix 3 | 65 | U1 | 2015-11-20 18:52 |  |  |  |  | 2015-11-20 20:42 |  | 0 | 0 | 1.833 | 1.8333 | 19.25 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 3898 |  |  | - |  | Miscellaneous plant auxiliary process and services instrumentation and controls | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | FX00Low Oil Flow Inidcated
Dix 3 | 73 | U1 | 2015-12-15 06:47 |  |  |  |  | 2015-12-15 09:12 |  | 0 | 0 | 2.417 | 2.4167 | 25.375 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 3611 |  |  | - |  | Switchyard circuit breakers - external (OMC) | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | Substation Disconnect
Dix 3 | 74 | U1 | 2015-12-15 10:09 |  |  |  |  | 2015-12-15 10:31 |  | 0 | 0 | 0.367 | 0.3667 | 3.85 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 3611 |  |  | - |  | Switchyard circuit breakers - external (OMC) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | Substation Disconnect
Dix 3 | 78 | U1 | 2015-12-22 16:09 |  |  |  |  | 2015-12-22 17:30 |  | 0 | 0 | 1.35 | 1.35 | 14.175 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 3899 |  |  | - |  | Other miscellaneous auxiliary system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | 0 Forced general lockout
Dix 3 | 79 | U1 | 2015-12-23 00:09 |  |  |  |  | 2015-12-23 10:08 |  | 0 | 0 | 9.983 | 9.9833 | 104.825 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 3899 |  |  | - |  | Other miscellaneous auxiliary system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | 0 Forced plant lockout believed to be from digital gov resildual issue.
Dix 3 | 81 | U1 | 2015-12-23 15:52 |  |  |  |  | 2015-12-29 09:09 |  | 0 | 0 | 137.283 | 137.2833 | 1441.475 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 3899 |  |  | - |  | Other miscellaneous auxiliary system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | Issues believed to be rooted in digital gov. associated issues.
Dix 3 | 82 | U1 | 2015-12-29 18:21 |  |  |  |  | 2015-12-30 13:45 |  | 0 | 0 | 19.4 | 19.4 | 203.7 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 3899 |  |  | - |  | Other miscellaneous auxiliary system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | Sensor for oil pressure may have indication issues.
Dix 3 | 12 | U1 | 2016-02-05 08:02 |  |  |  |  | 2016-02-05 08:20 |  | 0 | 0 | 0.3 | 0.3 | 3.15 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 4552 |  |  | - |  | Generator lube oil system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F570The unit tripped for lack of oil pressure. Filters changes fixed issue.
Dix 3 | 20 | U1 | 2016-03-01 19:00 |  |  |  |  | 2016-03-02 05:08 |  | 0 | 0 | 10.133 | 10.1333 | 106.4 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 3899 |  |  | - |  | Other miscellaneous auxiliary system problems | [8 empty] | AMP CODE: |  | 55
|  | DESCRIPTION : |  | F430Loose Wire caused unit to show tripped unavailable status in the middle of reserve
Dix 3 | 21 | U1 | 2016-03-02 10:23 |  |  |  |  | 2016-03-02 11:02 |  | 0 | 0 | 0.65 | 0.65 | 6.825 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 3899 |  |  | - |  | Other miscellaneous auxiliary system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F430Loose Wire
Dix 3 | 22 | U1 | 2016-03-02 11:03 |  |  |  |  | 2016-03-02 13:13 |  | 0 | 0 | 2.167 | 2.1667 | 22.75 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 3899 |  |  | - |  | Other miscellaneous auxiliary system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F430Loose Wiring finally located : Mccray
Dix 3 | 35 | U1 | 2016-05-14 17:24 |  |  |  |  | 2016-05-14 18:12 |  | 0 | 0 | 0.8 | 0.8 | 8.4 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 3898 |  |  | - |  | Miscellaneous plant auxiliary process and services instrumentation and controls | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F120Governor filter alarm. Tripped after filter left unchanged, Changed filter and bro
Dix 3 | 40 | U1 | 2016-06-02 12:54 |  |  |  |  | 2016-06-02 13:10 |  | 0 | 0 | 0.267 | 0.2667 | 2.8 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 3684 |  |  | - |  | Other voltage protection devices | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F410Voltage Regulator Trip
Dix 3 | 41 | U1 | 2016-06-02 13:13 |  |  |  |  | 2016-06-03 07:43 |  | 0 | 0 | 18.5 | 18.5 | 194.25 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 3684 |  |  | - |  | Other voltage protection devices | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F410Voltage Regulator Trip
Dix 3 | 60 | SF | 2016-08-02 05:00 |  |  |  |  | 2016-08-02 09:30 |  | 0 | 0 | 4.5 | 4.5 | 47.25 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 3970 |  |  | - |  | Distributive Control System (DCS) - process computer | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | Lost control screen
Dix 3 | 99 | U1 | 2016-12-22 14:38 |  |  |  |  | 2016-12-22 15:33 |  | 0 | 0 | 0.917 | 0.9167 | 9.625 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 4710 |  |  | - |  | Generator metering devices | [8 empty] | AMP CODE: |  | 52
|  | DESCRIPTION : |  | Moved gen brg temp control card to Dix 2
Dix 3 | 2 | U1 | 2017-01-19 22:57 |  |  |  |  | 2017-01-20 00:37 |  | 0 | 0 | 1.667 | 1.6667 | 17.5 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 7053 |  |  | - |  | Governor oil system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | Clogged filter on turbine governor control oil system
Dix 3 | 69 | U1 | 2017-08-23 11:29 |  |  |  |  | 2017-09-18 14:48 |  | 0 | 0 | 627.317 | 627.3167 | 6586.825 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 3612 |  |  | - |  | Switchyard system protection devices - external (OMC) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Faulty CT on the generator differential circuit
Dix 3 | 9 | U1 | 2018-04-10 00:06 |  |  |  |  | 2018-04-10 01:57 |  | 0 | 0 | 1.85 | 1.85 | 19.425 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 7053 |  |  | - |  | Governor oil system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | Tripped due to low gov oil press. Replaced filter.
Dix 3 | 10 | U1 | 2018-04-14 07:20 |  |  |  |  | 2018-04-14 15:18 |  | 0 | 0 | 7.967 | 7.9667 | 83.65 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 7299 |  |  | - |  | Other miscellaneous hydro turbine/pump problems (use generator codes and balance of plant electrical and auxiliary codes as appropriate) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | Unit offline for swiftwater rescue training
Dix 3 | 11 | U1 | 2018-04-15 07:13 |  |  |  |  | 2018-04-15 13:42 |  | 0 | 0 | 6.483 | 6.4833 | 68.075 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 7299 |  |  | - |  | Other miscellaneous hydro turbine/pump problems (use generator codes and balance of plant electrical and auxiliary codes as appropriate) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | Unit offline for swiftwater rescue training
Dix 3 | 35 | U1 | 2018-10-24 14:12 |  |  |  |  | 2018-10-26 10:53 |  | 0 | 0 | 44.683 | 44.6833 | 469.175 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 7052 |  |  | - |  | "Other turbine control problems (Report specific wicket gate controls, etc., using the code for the appropriate equipment item.)" | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F400Issue with turbine speed sensor
Dix 3 | 8 | U1 | 2019-02-17 12:33 |  |  |  |  | 2019-02-17 14:40 |  | 0 | 0 | 2.117 | 2.1167 | 22.225 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 7053 |  |  | - |  | Governor oil system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | Tripped due to clogged turbine gov oil filter
Dix 3 | 20 | U1 | 2019-05-24 09:22 |  |  |  |  | 2019-05-24 09:41 |  | 0 | 0 | 0.317 | 0.3167 | 3.325 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 9930 |  |  | - |  | Operating procedure error | [8 empty] | AMP CODE: |  | 59
|  | DESCRIPTION : |  | F590Protective lockout caused by Maint cycling power on PLC
Dix 3 | 22 | SF | 2019-06-07 22:36 |  |  |  |  | 2019-06-07 23:55 |  | 0 | 0 | 1.317 | 1.3167 | 13.825 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 7121 |  |  | - |  | Shutoff valves | [8 empty] | AMP CODE: |  | 72
|  | DESCRIPTION : |  | F720Johnson valve would not open
Dix 3 | 21 | U1 | 2020-04-13 07:40 |  |  |  |  | 2020-04-13 08:09 |  | 0 | 0 | 0.483 | 0.4833 | 5.075 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 7053 |  |  | - |  | Governor oil system | [8 empty] | AMP CODE: |  | 66
|  | DESCRIPTION : |  | F660Low gov oil resevoir level
Dix 3 | 28 | U1 | 2020-04-27 00:33 |  |  |  |  | 2020-04-27 00:42 |  | 0 | 0 | 0.15 | 0.15 | 1.575 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 7053 |  |  | - |  | Governor oil system | [8 empty] | AMP CODE: |  | 57
|  | DESCRIPTION : |  | F570Unit put in outage due to low gov oil press trip on U1 until it was confirmed that
Dix 3 | 40 | U1 | 2020-06-11 16:51 |  |  |  |  | 2020-06-12 11:15 |  | 0 | 0 | 18.4 | 18.4 | 193.2 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 3720 |  |  | - |  | Transmission equipment at the 1st substation (see code 9300 if applicable) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Tree fell on GSU.
Dix 3 | 1 | U1 | 2021-01-08 07:13 |  |  |  |  | 2021-01-08 13:30 |  | 0 | 0 | 6.283 | 6.2833 | 65.975 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 3644 |  |  | - |  | AC Protection devices | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F550Loss of main power feed due to blown fuse from suspected loose wire.
Dix 3 | 3 | U1 | 2021-01-12 09:12 |  |  |  |  | 2021-01-12 09:47 |  | 0 | 0 | 0.583 | 0.5833 | 6.125 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 9910 |  |  | - |  | Maintenance personnel error | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F700Dropped meter probe during troubleshooting resulting in blown fuse on gov oil pump
Dix 3 | 24 | U1 | 2022-08-13 06:25 |  |  |  |  | 2022-08-13 10:43 |  | 0 | 0 | 4.3 | 4.3 | 45.15 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 7009 |  |  | - |  | Bearing oil system | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F570Bearing oil leak due to felt seal.
Dix 3 | 36 | U1 | 2022-12-14 12:52 |  |  |  |  | 2022-12-14 14:24 |  | 0 | 0 | 1.533 | 1.5333 | 16.1 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 3653 |  |  | - |  | DC protection devices | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F490Blown fuse on 125v dc control circuit.
Dix 3 | 34 | U1 | 2023-10-04 04:33 |  |  |  |  | 2023-10-04 07:49 |  | 0 | 0 | 3.267 | 3.2667 | 34.3 | 1 |  |  |  | 0 |  |  | 10.5
|  | CAUSE CODE : |  | 4720 |  |  | - |  | Generator synchronization equipment | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340Unit would not synch
Ghent - GH1
Unit | Event | Type | Start |  |  |  |  | End |  | GAC | NAC | Duration | Equiv Hrs | Equiv MWH | Cont | Work Start | Work End |  | Hours |  |  | Gross Capacity Impact (MW)
GH1 | 17 | U1 | 2014-03-05 00:42 |  |  |  |  | 2014-03-05 23:00 |  | 0 | 0 | 22.3 | 22.3 | 10726.3 | 1 |  |  |  | 0 |  |  | 520
|  | CAUSE CODE : |  | 1000 |  |  | - |  | Waterwall (Furnace wall) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | Outage #3Water water tube leak blew out on the upper slope of the boiler about 15
GH1 | 77 | U1 | 2014-12-09 23:46 |  |  |  |  | 2014-12-11 03:07 |  | 0 | 0 | 27.35 | 27.35 | 13155.35 | 1 |  |  |  | 0 |  |  | 520
|  | CAUSE CODE : |  | 1060 |  |  | - |  | First reheater | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | Outage #7Reheat pendant tube ruptured a few feet out from the east side of the boi
GH1 | 12 | U1 | 2015-02-10 09:28 |  |  |  |  | 2015-02-11 10:07 |  | 0 | 0 | 24.65 | 24.65 | 11856.651 | 1 |  |  |  | 0 |  |  | 520
|  | CAUSE CODE : |  | 1040 |  |  | - |  | First superheater | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | Outage #1Boiler had been running several weeks with tube leak in upper furnace and
GH1 | 18 | U1 | 2015-05-18 15:28 |  |  |  |  | 2015-05-18 22:07 |  | 0 | 0 | 6.65 | 6.65 | 3185.35 | 1 |  |  |  | 0 |  |  | 520
|  | CAUSE CODE : |  | 4293 |  |  | - |  | Hydraulic system pipes and valves | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | Outage #3The unit developed a leak on the Main Turbine Governor Valve #1 EH fittin
GH1 | 35 | U1 | 2015-07-19 09:31 |  |  |  |  | 2015-07-19 10:28 |  | 0 | 0 | 0.95 | 0.95 | 450.3 | 1 |  |  |  | 0 |  |  | 520
|  | CAUSE CODE : |  | 8650 |  |  | - |  | "Baghouse systems, general" | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | Outage #6PJFF inlet pressure reached tripping point and tripped one set of ID fans
GH1 | 41 | U2 | 2015-08-04 06:24 |  |  |  |  | 2015-08-05 05:12 |  | 0 | 0 | 22.8 | 22.8 | 10807.2 | 1 |  |  |  | 0 |  |  | 520
|  | CAUSE CODE : |  | 1040 |  |  | - |  | First superheater | [8 empty] | AMP CODE: |  | 54
|  | DESCRIPTION : |  | Outage #7Tube leak was heard in backpass of boiler around the Primary Superheat in
GH1 | 44 | U2 | 2015-08-12 21:49 |  |  |  |  | 2015-08-16 00:39 |  | 0 | 0 | 74.833 | 74.8333 | 35471 | 1 |  |  |  | 0 |  |  | 520
|  | CAUSE CODE : |  | 0520 |  |  | - |  | Other main steam valves (including vent and drain valves but not including the turbine stop valves) | [8 empty] | AMP CODE: |  | 54
|  | DESCRIPTION : |  | Outage #8A leak developed in the Main Steam line drain S9. Removed the unit from
GH1 | 47 | U2 | 2015-08-26 22:15 |  |  |  |  | 2015-09-01 21:46 |  | 0 | 0 | 143.517 | 143.5167 | 68026.899 | 1 |  |  |  | 0 |  |  | 520
|  | CAUSE CODE : |  | 1040 |  |  | - |  | First superheater | [8 empty] | AMP CODE: |  | 38
|  | DESCRIPTION : |  | F380Outage #9Unit 1 developed what appeared to be a leak in the Primary Superheate
GH1 | 48 | U2 | 2015-09-08 09:56 |  |  |  |  | 2015-09-10 15:29 |  | 0 | 0 | 53.55 | 53.55 | 25382.7 | 1 |  |  |  | 0 |  |  | 520
|  | CAUSE CODE : |  | 1080 |  |  | - |  | Economizer | [8 empty] | AMP CODE: |  | 91
|  | DESCRIPTION : |  | F910Outage #10Unit 1 developed a tube leak in the Economizer section of the boiler
GH1 | 53 | U1 | 2015-11-13 22:23 |  |  |  |  | 2015-11-16 08:28 |  | 0 | 0 | 58.083 | 58.0833 | 27647.666 | 1 |  |  |  | 0 |  |  | 520
|  | CAUSE CODE : |  | 4810 |  |  | - |  | Generator output breaker | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | Outage #13GH1 generator breaker 165-716 manual disconnect failed, which caused the
GH1 | 54 | U1 | 2015-11-16 09:23 |  |  |  |  | 2015-11-16 10:39 |  | 0 | 0 | 1.267 | 1.2667 | 602.933 | 1 |  |  |  | 0 |  |  | 520
|  | CAUSE CODE : |  | 4610 |  |  | - |  | Hydrogen cooling system piping and valves | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | Outage #14GH1 tripped off line due to high generator hydrogen gas temperature.
GH1 | 3 | U1 | 2016-01-20 09:17 |  |  |  |  | 2016-01-20 10:18 |  | 0 | 0 | 1.017 | 1.0167 | 483.933 | 1 |  |  |  | 0 |  |  | 520
|  | CAUSE CODE : |  | 1480 |  |  | - |  | Other induced draft fan problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | Outage #1GH1 was removed from service due to loss of ID fans causing MFT. ID fans
GH1 | 7 | U1 | 2016-01-27 15:12 |  |  |  |  | 2016-01-28 17:49 |  | 0 | 0 | 26.617 | 26.6167 | 12669.533 | 1 |  |  |  | 0 |  |  | 520
|  | CAUSE CODE : |  | 1060 |  |  | - |  | First reheater | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Outage #2Unit 1 was removed from service due to a reheat tube leak at the IK #
GH1 | 8 | U1 | 2016-02-04 10:48 |  |  |  |  | 2016-02-06 19:50 |  | 0 | 0 | 57.033 | 57.0333 | 27147.867 | 1 |  |  |  | 0 |  |  | 520
|  | CAUSE CODE : |  | 1060 |  |  | - |  | First reheater | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Outage #3Unit 1 was removed from service due to reheat tube leak at the IK #6
GH1 | 9 | U1 | 2016-02-06 19:50 |  |  |  |  | 2016-02-07 11:00 |  | 0 | 0 | 15.167 | 15.1667 | 7219.333 | 1 |  |  |  | 0 |  |  | 520
|  | CAUSE CODE : |  | 3220 |  |  | - |  | Circulating water piping | [8 empty] | AMP CODE: |  | 54
|  | DESCRIPTION : |  | Outage #4GH1 Forced Outage was changed from a Reheat tube leak, once repairs were
GH1 | 11 | U1 | 2016-02-18 02:00 |  |  |  |  | 2016-02-18 23:47 |  | 0 | 0 | 21.783 | 21.7833 | 10368.866 | 1 |  |  |  | 0 |  |  | 520
|  | CAUSE CODE : |  | 1040 |  |  | - |  | First superheater | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | Outage #5Unit 1 was removed from service due to a Reheat tube leak at the IK #6 ar
GH1 | 14 | U1 | 2016-03-20 03:31 |  |  |  |  | 2016-03-20 04:55 |  | 0 | 0 | 1.4 | 1.4 | 665 | 1 |  |  |  | 0 |  |  | 520
|  | CAUSE CODE : |  | 1710 |  |  | - |  | "Combustion/steam condition controls (report local controls - burners, pulverizers, etc., - with component or system)" | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | Outage #8Unit 1 tripped due to loss of boiler fire.
GH1 | 26 | U1 | 2016-05-15 13:30 |  |  |  |  | 2016-05-15 14:14 |  | 0 | 0 | 0.733 | 0.7333 | 348.333 | 1 |  |  |  | 0 |  |  | 520
|  | CAUSE CODE : |  | 3133 |  |  | - |  | Vacuum pumps | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | Outage #11Unit 1 tripped due to loss of 1-1 main condenser vacuum pump seal water
GH1 | 27 | U1 | 2016-05-15 14:39 |  |  |  |  | 2016-05-15 15:30 |  | 0 | 0 | 0.85 | 0.85 | 403.75 | 1 |  |  |  | 0 |  |  | 520
|  | CAUSE CODE : |  | 3210 |  |  | - |  | Circulating water pumps | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | Outage #12Unit 1 tripped off line due to boiler swing causing a low differential p
GH1 | 53 | U1 | 2016-09-16 18:36 |  |  |  |  | 2016-09-23 01:56 |  | 0 | 0 | 151.333 | 151.3333 | 71883.333 | 1 |  |  |  | 0 |  |  | 520
|  | CAUSE CODE : |  | 1040 |  |  | - |  | First superheater | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Outage #15Unit 1 came off line due to a Primary Superheat tube leak.
GH1 | 56 | U1 | 2016-09-25 00:41 |  |  |  |  | 2016-09-25 01:41 |  | 0 | 0 | 1 | 1 | 475 | 1 |  |  |  | 0 |  |  | 520
|  | CAUSE CODE : |  | 4261 |  |  | - |  | Control valves | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F540Outage #16Unit 1 was removed from service due to an EH leak on the Main Turbin
GH1 | 5 | U1 | 2017-01-18 16:51 |  |  |  |  | 2017-01-22 00:04 |  | 0 | 0 | 79.217 | 79.2167 | 37707.133 | 1 |  |  |  | 0 |  |  | 520
|  | CAUSE CODE : |  | 1040 |  |  | - |  | First superheater | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | Outage #3Unit 1 off line for a tube leak in the Low Temp SH section of the boiler.
GH1 | 10 | U1 | 2017-02-07 22:49 |  |  |  |  | 2017-02-08 15:47 |  | 0 | 0 | 16.967 | 16.9667 | 8076.134 | 1 |  |  |  | 0 |  |  | 520
|  | CAUSE CODE : |  | 0891 |  |  | - |  | Bottom ash hoppers (including gates) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | FS00Outage #6B-Side Wet Ash Hopper bridged over with slag. Removed the unit from
GH1 | 22 | U1 | 2017-06-14 22:06 |  |  |  |  | 2017-06-18 04:29 |  | 0 | 0 | 78.383 | 78.3833 | 37232.083 | 1 |  |  |  | 0 |  |  | 520
|  | CAUSE CODE : |  | 1080 |  |  | - |  | Economizer | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F540Outage #10GH1 was forced off line due to an economizer tube leak.
GH1 | 44 | U1 | 2017-10-18 22:54 |  |  |  |  | 2017-10-19 21:54 |  | 0 | 0 | 23 | 23 | 10925 | 1 |  |  |  | 0 |  |  | 520
|  | CAUSE CODE : |  | 1100 |  |  | - |  | Waterwall (Furnace wall) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F540Outage #16 GH1 was forced offline due to water wall tube leak on 4th elevation
GH1 | 11 | U1 | 2018-02-07 18:31 |  |  |  |  | 2018-02-07 21:21 |  | 0 | 0 | 2.833 | 2.8333 | 1357.167 | 1 |  |  |  | 0 |  |  | 520
|  | CAUSE CODE : |  | 1450 |  |  | - |  | Other air supply problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | Outage #1Loss of ID fans due to furance pressure caused a flame out of the boiler.
GH1 | 14 | U1 | 2018-02-24 17:00 |  |  |  |  | 2018-02-27 03:43 |  | 0 | 0 | 58.717 | 58.7167 | 28125.283 | 1 |  |  |  | 0 |  |  | 520
|  | CAUSE CODE : |  | 1000 |  |  | - |  | Waterwall (Furnace wall) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | Outage #2Unit was removed from service due to a water wall leak on 7th floor.
GH1 | 16 | U1 | 2018-02-28 15:45 |  |  |  |  | 2018-02-28 17:45 |  | 0 | 0 | 2 | 2 | 958 | 1 |  |  |  | 0 |  |  | 520
|  | CAUSE CODE : |  | 3520 |  |  | - |  | HP Extraction steam piping | [8 empty] | AMP CODE: |  | 54
|  | DESCRIPTION : |  | Outage #4Unit was placed on a forced outage due to a drain line broken off the ext
GH1 | 52 | U1 | 2018-10-02 19:11 |  |  |  |  | 2018-10-02 21:02 |  | 0 | 0 | 1.85 | 1.85 | 882.45 | 1 |  |  |  | 0 |  |  | 520
|  | CAUSE CODE : |  | 1475 |  |  | - |  | Induced draft fan controls | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | Outage # 8Unit tripped due to ID fan trouble.
GH1 | 9 | U1 | 2019-05-10 13:54 |  |  |  |  | 2019-05-11 15:52 |  | 0 | 0 | 25.967 | 25.9667 | 12386.1 | 1 |  |  |  | 0 |  |  | 520
|  | CAUSE CODE : |  | 4613 |  |  | - |  | Hydrogen seals | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F590Forced Outage #2Hydrogen seals.
GH1 | 10 | U1 | 2019-05-11 18:00 |  |  |  |  | 2019-05-14 11:54 |  | 0 | 0 | 65.9 | 65.9 | 31434.3 | 1 |  |  |  | 0 |  |  | 520
|  | CAUSE CODE : |  | 4560 |  |  | - |  | Generator vibration (excluding vibration due to failed bearing and other components) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F590Forced Outage #3Generator vibration.
GH1 | 25 | U1 | 2019-06-29 03:18 |  |  |  |  | 2019-06-29 11:12 |  | 0 | 0 | 7.9 | 7.9 | 3752.5 | 1 |  |  |  | 0 |  |  | 520
|  | CAUSE CODE : |  | 0350 |  |  | - |  | Pulverized fuel and air piping (from pulverizer to wind box) (see code 0898 for pulverizer reject system problems) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | Outage #4GH1 tripped due to pulverier and air piping issues.
GH1 | 26 | U1 | 2019-06-29 11:54 |  |  |  |  | 2019-06-29 18:10 |  | 0 | 0 | 6.267 | 6.2667 | 2976.667 | 1 |  |  |  | 0 |  |  | 520
|  | CAUSE CODE : |  | 4308 |  |  | - |  | Automatic turbine control systems - digital control and monitoring | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | Outage #5Unit tripped - automatic digital control and monitoring.
GH1 | 8 | U1 | 2020-04-02 07:45 |  |  |  |  | 2020-04-04 08:00 |  | 0 | 0 | 48.25 | 48.25 | 23015.25 | 1 |  |  |  | 0 |  |  | 520
|  | CAUSE CODE : |  | 1000 |  |  | - |  | Waterwall (Furnace wall) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Outage #6GH1 was forced off-line due to a water wall tube leak on "D" corner 6
GH1 | 24 | U1 | 2020-05-27 06:53 |  |  |  |  | 2020-05-27 13:22 |  | 0 | 0 | 6.483 | 6.4833 | 3092.55 | 1 |  |  |  | 0 |  |  | 520
|  | CAUSE CODE : |  | 3653 |  |  | - |  | DC protection devices | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Outage #9 Forced-Immediate Outage due to experiencing several DC ground relate
GH1 | 30 | U1 | 2020-07-11 12:34 |  |  |  |  | 2020-07-11 15:29 |  | 0 | 0 | 2.917 | 2.9167 | 1385.417 | 1 |  |  |  | 0 |  |  | 520
|  | CAUSE CODE : |  | 3664 |  |  | - |  | 4000-7000 volt protection devices | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Outage #11GH1 tripped offline due to 4KV "A" Bus Lockout.
GH1 | 64 | U1 | 2020-10-11 05:39 |  |  |  |  | 2020-10-11 16:47 |  | 0 | 0 | 11.133 | 11.1333 | 5310.6 | 1 |  |  |  | 0 |  |  | 520
|  | CAUSE CODE : |  | 4293 |  |  | - |  | Hydraulic system pipes and valves | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Outage #12GH1 tripped off-line due to E.H. line broken off of #5 governor valv
GH1 | 17 | U1 | 2021-05-17 18:52 |  |  |  |  | 2021-05-17 20:06 |  | 0 | 0 | 1.233 | 1.2333 | 588.3 | 1 |  |  |  | 0 |  |  | 520
|  | CAUSE CODE : |  | 4302 |  |  | - |  | Turbine trip devices (including instruments) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Outage #5Unit tripped off-line due to false vibration indication on U1 main tu
GH1 | 35 | U1 | 2021-08-04 06:40 |  |  |  |  | 2021-08-04 09:16 |  | 0 | 0 | 2.6 | 2.6 | 1235 | 1 |  |  |  | 0 |  |  | 520
|  | CAUSE CODE : |  | 4609 |  |  | - |  | Other exciter problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Outage# 8Drain line leak on exciter cooler
GH1 | 36 | U1 | 2021-08-11 20:22 |  |  |  |  | 2021-08-12 00:47 |  | 0 | 0 | 4.417 | 4.4167 | 2097.916 | 1 |  |  |  | 0 |  |  | 520
|  | CAUSE CODE : |  | 4619 |  |  | - |  | Other hydrogen system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Outage #9Hydrogen gas temperature high due to loss of low pressure service wat
GH1 | 39 | U1 | 2021-08-12 21:49 |  |  |  |  | 2021-08-13 12:13 |  | 0 | 0 | 14.4 | 14.4 | 6840 | 1 |  |  |  | 0 |  |  | 520
|  | CAUSE CODE : |  | 3431 |  |  | - |  | Other feedwater valves | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Outage #101F1 heat valve high pressure heater inlet valve packing blown out.
GH1 | 45 | U1 | 2021-08-28 23:57 |  |  |  |  | 2021-08-30 12:26 |  | 0 | 0 | 36.483 | 36.4833 | 17329.583 | 1 |  |  |  | 0 |  |  | 520
|  | CAUSE CODE : |  | 0775 |  |  | - |  | Economizer piping | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Outage# 12 Economizer header inspection port leaking, internal boiler.
GH1 | 7 | U1 | 2022-02-20 11:30 |  |  |  |  | 2022-02-21 04:00 |  | 0 | 0 | 16.5 | 16.5 | 7903.5 | 1 |  |  |  | 0 |  |  | 520
|  | CAUSE CODE : |  | 3110 |  |  | - |  | Condenser tube leaks | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Outage #1Elevated silica as a result of a condenser tube leak.
GH1 | 17 | U1 | 2022-06-21 01:11 |  |  |  |  | 2022-06-21 08:31 |  | 0 | 0 | 7.333 | 7.3333 | 3483.333 | 1 |  |  |  | 0 |  |  | 520
|  | CAUSE CODE : |  | 1000 |  |  | - |  | Waterwall (Furnace wall) | [8 empty] | AMP CODE: |  | 54
|  | DESCRIPTION : |  | F830Outage #5SUF fires out of boiler due to a water wall leak on 8 1/3 "D" corner
GH1 | 29 | U1 | 2022-08-31 00:46 |  |  |  |  | 2022-08-31 07:24 |  | 0 | 0 | 6.633 | 6.6333 | 3150.833 | 1 |  |  |  | 0 |  |  | 520
|  | CAUSE CODE : |  | 3812 |  |  | - |  | Service water valves | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Outage #82-1 LPSW discharge valve was leaking and had to be replaced, all LPSW
GH1 | 30 | U1 | 2022-09-01 14:32 |  |  |  |  | 2022-09-01 18:32 |  | 0 | 0 | 4 | 4 | 1908 | 1 |  |  |  | 0 |  |  | 520
|  | CAUSE CODE : |  | 3972 |  |  | - |  | DCS - hardware problems (including card failure) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830GH1 was forced offline due loss of DCS boiler controls power supplies. The Primary
GH1 | 32 | U1 | 2022-09-01 21:40 |  |  |  |  | 2022-09-02 12:52 |  | 0 | 0 | 15.2 | 15.2 | 7250.4 | 1 |  |  |  | 0 |  |  | 520
|  | CAUSE CODE : |  | 0400 |  |  | - |  | Burner wind box fires | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Outage #10GH1 was forced offline due to 1-3 "D" burner line fire causing hole
GH1 | 33 | U1 | 2022-09-13 08:07 |  |  |  |  | 2022-09-13 08:55 |  | 0 | 0 | 0.8 | 0.8 | 381.6 | 1 |  |  |  | 0 |  |  | 520
|  | CAUSE CODE : |  | 3972 |  |  | - |  | DCS - hardware problems (including card failure) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Outage #11GH1 was forced offline due to loss of DCS boiler control power suppl
GH1 | 9 | U1 | 2023-03-19 19:26 |  |  |  |  | 2023-03-20 09:20 |  | 0 | 0 | 13.9 | 13.9 | 6630.3 | 1 |  |  |  | 0 |  |  | 520
|  | CAUSE CODE : |  | 4730 |  |  | - |  | Generator current and potential transformers | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Outage #3Forced Outage due to faulty current transformer feed cable going to g
GH1 | 38 | U1 | 2023-09-26 21:25 |  |  |  |  | 2023-09-29 00:47 |  | 0 | 0 | 51.367 | 51.3667 | 24501.9 | 1 |  |  |  | 0 |  |  | 520
|  | CAUSE CODE : |  | 1040 |  |  | - |  | First superheater | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Outage #11Forced Outage due to an economizer tube leak.
Ghent - GH2
Unit | Event | Type | Start |  |  |  |  | End |  | GAC | NAC | Duration | Equiv Hrs | Equiv MWH | Cont | Work Start | Work End |  | Hours |  |  | Gross Capacity Impact (MW)
GH2 | 30 | U1 | 2014-04-28 06:35 |  |  |  |  | 2014-04-28 09:19 |  | 0 | 0 | 2.733 | 2.7333 | 1353 | 1 |  |  |  | 0 |  |  | 520
|  | CAUSE CODE : |  | 9020 |  |  | - |  | Lightning | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | Outage #3Lightning strike triped U2 FGD electric feed, ID fans tripped. Transform
GH2 | 45 | U1 | 2014-07-23 09:00 |  |  |  |  | 2014-07-23 14:33 |  | 0 | 0 | 5.55 | 5.55 | 2747.25 | 1 |  |  |  | 0 |  |  | 520
|  | CAUSE CODE : |  | 3416 |  |  | - |  | Other feedwater pump problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | Outage #4While pulling the breaker for 2-1 BFPT High Pressure Oil Control Fluid Pu
GH2 | 75 | U1 | 2014-10-16 07:55 |  |  |  |  | 2014-10-16 08:59 |  | 0 | 0 | 1.067 | 1.0667 | 508.8 | 1 |  |  |  | 0 |  |  | 520
|  | CAUSE CODE : |  | 4619 |  |  | - |  | Other hydrogen system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | Outage #6Unit 2 tripped off line when a fuse blew in the Generator Hydrogen cabine
GH2 | 5 | U1 | 2015-01-25 15:00 |  |  |  |  | 2015-01-25 20:38 |  | 0 | 0 | 5.633 | 5.6333 | 2687.1 | 1 |  |  |  | 0 |  |  | 520
|  | CAUSE CODE : |  | 3621 |  |  | - |  | Unit auxiliaries transformer | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | Outage #1Unit Auxiliary Transformer 2A tripped on differential on 'B' and 'C' phas
GH2 | 6 | SF | 2015-01-25 20:38 |  |  |  |  | 2015-01-26 19:52 |  | 0 | 0 | 23.233 | 23.2333 | 11082.3 | 1 |  |  |  | 0 |  |  | 520
|  | CAUSE CODE : |  | 4309 |  |  | - |  | Other turbine instrument and control problems | [8 empty] | AMP CODE: |  | 40
|  | DESCRIPTION : |  | Outage #2During the previous event of the UAT-2 differential, the Main Turbine wen
GH2 | 13 | U1 | 2015-02-11 02:06 |  |  |  |  | 2015-02-11 03:05 |  | 0 | 0 | 0.983 | 0.9833 | 469.05 | 1 |  |  |  | 0 |  |  | 520
|  | CAUSE CODE : |  | 0690 |  |  | - |  | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | Outage #4While unit was raising load from just coming back on line from previous e
GH2 | 53 | U2 | 2015-08-23 20:03 |  |  |  |  | 2015-08-24 20:02 |  | 0 | 0 | 23.983 | 23.9833 | 11871.75 | 1 |  |  |  | 0 |  |  | 520
|  | CAUSE CODE : |  | 1000 |  |  | - |  | Waterwall (Furnace wall) | [8 empty] | AMP CODE: |  | 54
|  | DESCRIPTION : |  | Outage #8Unit 2 developed a water wall tube leak. Removed the unit from service f
GH2 | 59 | U2 | 2015-09-16 07:13 |  |  |  |  | 2015-09-17 07:33 |  | 0 | 0 | 24.333 | 24.3333 | 12045 | 1 |  |  |  | 0 |  |  | 520
|  | CAUSE CODE : |  | 1000 |  |  | - |  | Waterwall (Furnace wall) | [8 empty] | AMP CODE: |  | 37
|  | DESCRIPTION : |  | F370Outage #9Unit 2 developed a water wall tube leak on 7 1/2 floor, south side of
GH2 | 3 | U1 | 2016-01-13 09:17 |  |  |  |  | 2016-01-13 14:43 |  | 0 | 0 | 5.433 | 5.4333 | 2580.833 | 1 |  |  |  | 0 |  |  | 520
|  | CAUSE CODE : |  | 0260 |  |  | - |  | Primary air fan | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | Outage #1Unit 2 Primary air fan catastrophic failure of fan and motor.
GH2 | 30 | U1 | 2016-07-08 14:27 |  |  |  |  | 2016-07-10 11:25 |  | 0 | 0 | 44.967 | 44.9667 | 22168.567 | 1 |  |  |  | 0 |  |  | 520
|  | CAUSE CODE : |  | 3121 |  |  | - |  | Expansion joint | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F540Outage #3The unit was removed from service to repair a main condenser expansio
GH2 | 43 | U1 | 2016-10-24 08:27 |  |  |  |  | 2016-10-24 19:53 |  | 0 | 0 | 11.433 | 11.4333 | 5533.733 | 1 |  |  |  | 0 |  |  | 520
|  | CAUSE CODE : |  | 9930 |  |  | - |  | Operating procedure error | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Outage #6Unit 2 was forced off line to remove scaffold from 2-2 air heater.
GH2 | 12 | U1 | 2017-04-13 10:15 |  |  |  |  | 2017-04-14 02:37 |  | 0 | 0 | 16.367 | 16.3667 | 7954.2 | 1 |  |  |  | 0 |  |  | 520
|  | CAUSE CODE : |  | 1000 |  |  | - |  | Waterwall (Furnace wall) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F540Outage #5The unit was forced off line due to a water wall tube leak.
GH2 | 33 | U1 | 2017-09-27 12:15 |  |  |  |  | 2017-09-29 01:21 |  | 0 | 0 | 37.1 | 37.1 | 17956.4 | 1 |  |  |  | 0 |  |  | 520
|  | CAUSE CODE : |  | 1000 |  |  | - |  | Waterwall (Furnace wall) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F540Outage # 11Water wall tube leak on east wall.
GH2 | 40 | U1 | 2017-11-11 20:55 |  |  |  |  | 2017-11-12 09:33 |  | 0 | 0 | 12.633 | 12.6333 | 6114.533 | 1 |  |  |  | 0 |  |  | 520
|  | CAUSE CODE : |  | 3441 |  |  | - |  | Other high pressure heater problems (see condensate system for LP and IP heater codes) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F540Outage #13Unit 2 was forced off line due to F heater inlet valve packing leak.
GH2 | 41 | U1 | 2018-09-07 17:03 |  |  |  |  | 2018-09-11 16:01 |  | 0 | 0 | 94.967 | 94.9667 | 46153.8 | 1 |  |  |  | 0 |  |  | 520
|  | CAUSE CODE : |  | 1040 |  |  | - |  | First superheater | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F540Outage # 3Boiler tube leak. SH leak repaired and then found a WW leak 9/11/@
GH2 | 12 | U1 | 2019-04-20 11:49 |  |  |  |  | 2019-04-22 00:22 |  | 0 | 0 | 36.55 | 36.55 | 17763.3 | 1 |  |  |  | 0 |  |  | 520
|  | CAUSE CODE : |  | 0360 |  |  | - |  | Burners | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | FR00Forced Outage Burner fire @ B corner windbox.
GH2 | 35 | U1 | 2019-11-19 15:42 |  |  |  |  | 2019-11-19 16:22 |  | 0 | 0 | 0.667 | 0.6667 | 324 | 1 |  |  |  | 0 |  |  | 520
|  | CAUSE CODE : |  | 3661 |  |  | - |  | 4000-7000 volt circuit breakers | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Outage #6Unit 2 switchgear that was replaced during the 2019 Fall Outage. When
GH2 | 39 | U1 | 2019-12-25 03:24 |  |  |  |  | 2019-12-25 05:30 |  | 0 | 0 | 2.1 | 2.1 | 1020.6 | 1 |  |  |  | 0 |  |  | 520
|  | CAUSE CODE : |  | 3631 |  |  | - |  | 400-700 volt circuit breakers | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Outage # 8Failed 480V feed breaker to the essential service.
GH2 | 40 | U1 | 2019-12-25 06:07 |  |  |  |  | 2019-12-25 09:55 |  | 0 | 0 | 3.8 | 3.8 | 1846.8 | 1 |  |  |  | 0 |  |  | 520
|  | CAUSE CODE : |  | 4535 |  |  | - |  | "Stator, General" | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | Outage #9Failed stator water flow transmitter.
GH2 | 46 | U1 | 2020-12-14 11:21 |  |  |  |  | 2020-12-15 15:18 |  | 0 | 0 | 27.95 | 27.95 | 13583.7 | 1 |  |  |  | 0 |  |  | 520
|  | CAUSE CODE : |  | 1060 |  |  | - |  | First reheater | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Outage #10Forced offline due to a tube leak in the RH section of the boiler
GH2 | 34 | U1 | 2021-09-26 04:12 |  |  |  |  | 2021-09-26 06:48 |  | 0 | 0 | 2.6 | 2.6 | 1262.3 | 1 |  |  |  | 0 |  |  | 520
|  | CAUSE CODE : |  | 1470 |  |  | - |  | Induced draft fan motors and drives | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Outage #3Forced outage due to the loss of ID fans coolant pumps.
GH2 | 35 | U1 | 2021-10-06 23:20 |  |  |  |  | 2021-10-07 04:44 |  | 0 | 0 | 5.4 | 5.4 | 2621.7 | 1 |  |  |  | 0 |  |  | 520
|  | CAUSE CODE : |  | 4311 |  |  | - |  | Steam Turbine Control System - hardware problems (including card failure) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820OUTAGE# 4 GH2 was forced offline due to the control card on the #1 control valv
GH2 | 7 | U1 | 2022-01-02 13:50 |  |  |  |  | 2022-01-02 15:41 |  | 0 | 0 | 1.85 | 1.85 | 899.1 | 1 |  |  |  | 0 |  |  | 520
|  | CAUSE CODE : |  | 3499 |  |  | - |  | Other feedwater system problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Outage #2 Forced off due to low drum level.
GH2 | 16 | U1 | 2022-05-11 21:19 |  |  |  |  | 2022-05-13 01:06 |  | 0 | 0 | 27.783 | 27.7833 | 13488.808 | 1 |  |  |  | 0 |  |  | 520
|  | CAUSE CODE : |  | 3110 |  |  | - |  | Condenser tube leaks | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F540Outage #5Condenser tube leaks.
GH2 | 32 | U1 | 2022-11-19 18:22 |  |  |  |  | 2022-11-19 20:11 |  | 0 | 0 | 1.817 | 1.8167 | 881.992 | 1 |  |  |  | 0 |  |  | 520
|  | CAUSE CODE : |  | 3499 |  |  | - |  | Other feedwater system problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Outage #11Forced Outage.
GH2 | 4 | U1 | 2023-04-26 12:18 |  |  |  |  | 2023-04-28 07:13 |  | 0 | 0 | 42.917 | 42.9167 | 20836.042 | 1 |  |  |  | 0 |  |  | 520
|  | CAUSE CODE : |  | 0580 |  |  | - |  | Desuperheater/attemperator piping | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Outgae #1Foreced Outage due to a leak in the west superheat spray header locat
GH2 | 15 | U1 | 2023-11-07 06:41 |  |  |  |  | 2023-11-07 08:01 |  | 0 | 0 | 1.333 | 1.3333 | 647.333 | 1 |  |  |  | 0 |  |  | 520
|  | CAUSE CODE : |  | 3408 |  |  | - |  | Feedwater pump drive - local controls | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Outage #3Tripped off-line on a Forced Immediate Outage due to loss of feedwate
Ghent - GH3
Unit | Event | Type | Start |  |  |  |  | End |  | GAC | NAC | Duration | Equiv Hrs | Equiv MWH | Cont | Work Start | Work End |  | Hours |  |  | Gross Capacity Impact (MW)
GH3 | 1 | U1 | 2014-01-07 21:20 |  |  |  |  | 2014-01-08 06:15 |  | 0 | 0 | 8.917 | 8.9167 | 4297.833 | 1 |  |  |  | 0 |  |  | 525
|  | CAUSE CODE : |  | 1455 |  |  | - |  | Induced draft fans | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F850Outage #13-2 ID fan tripped on high vibration on OB fan bearing. This caused
GH3 | 4 | SF | 2014-01-13 03:25 |  |  |  |  | 2014-01-13 06:19 |  | 0 | 0 | 2.9 | 2.9 | 1397.8 | 1 |  |  |  | 0 |  |  | 525
|  | CAUSE CODE : |  | 4609 |  |  | - |  | Other exciter problems | [8 empty] | AMP CODE: |  | 52
|  | DESCRIPTION : |  | Outage #3During the previous event, the unit had been rolled up to synchronise spe
GH3 | 7 | U1 | 2014-01-25 03:33 |  |  |  |  | 2014-01-26 19:21 |  | 0 | 0 | 39.8 | 39.8 | 19183.6 | 1 |  |  |  | 0 |  |  | 525
|  | CAUSE CODE : |  | 1040 |  |  | - |  | First superheater | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | Outage #4Unit 3 was taken off line after developing a boiler tube leak in the Prim
GH3 | 45 | SF | 2014-05-17 16:17 |  |  |  |  | 2014-05-17 20:46 |  | 0 | 0 | 4.483 | 4.4833 | 2192.35 | 1 |  |  |  | 0 |  |  | 527.5
|  | CAUSE CODE : |  | 4700 |  |  | - |  | Generator voltage control | [8 empty] | AMP CODE: |  | 52
|  | DESCRIPTION : |  | Outage #9While trying to synchronize the unit after the Sping Outage the Generator
GH3 | 84 | U1 | 2014-09-25 13:42 |  |  |  |  | 2014-09-25 14:26 |  | 0 | 0 | 0.733 | 0.7333 | 358.6 | 1 |  |  |  | 0 |  |  | 527.5
|  | CAUSE CODE : |  | 3408 |  |  | - |  | Feedwater pump drive - local controls | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | Outage #11The unit tripped off line due to low drum level. This was caused by 3-2
GH3 | 4 | SF | 2015-01-20 04:45 |  |  |  |  | 2015-01-20 11:29 |  | 0 | 0 | 6.733 | 6.7333 | 3245.467 | 1 |  |  |  | 0 |  |  | 525
|  | CAUSE CODE : |  | 3613 |  |  | - |  | Switchyard system protection devices - external (not OMC) | [8 empty] | AMP CODE: |  | 06
|  | DESCRIPTION : |  | F060Outage #2Unit 3 was removed from service to repair air heater seals. When the
GH3 | 17 | U1 | 2015-04-18 09:23 |  |  |  |  | 2015-04-19 20:14 |  | 0 | 0 | 34.85 | 34.85 | 17041.651 | 1 |  |  |  | 0 |  |  | 527.5
|  | CAUSE CODE : |  | 0270 |  |  | - |  | Primary air duct and dampers | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | Outage #3Air Heater seals are leaking badly on the unit causing large swings in th
GH3 | 22 | U1 | 2015-06-10 22:27 |  |  |  |  | 2015-06-12 07:13 |  | 0 | 0 | 32.767 | 32.7667 | 16022.9 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 1080 |  |  | - |  | Economizer | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F540Outage #5Unit 3 was removed from service after peak with an economizer tube le
GH3 | 23 | U1 | 2015-06-13 20:24 |  |  |  |  | 2015-06-14 23:41 |  | 0 | 0 | 27.283 | 27.2833 | 13341.549 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 1000 |  |  | - |  | Waterwall (Furnace wall) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | Outage #6A tube leak could be heard, but location could not be detected in the upp
GH3 | 27 | U2 | 2015-08-14 02:20 |  |  |  |  | 2015-08-15 21:10 |  | 0 | 0 | 42.833 | 42.8333 | 20774.166 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 1040 |  |  | - |  | First superheater | [8 empty] | AMP CODE: |  | 54
|  | DESCRIPTION : |  | Outage #8Primary Superheater developed a tube leak that required the unit to be re
GH3 | 31 | U1 | 2015-08-30 10:52 |  |  |  |  | 2015-09-02 14:15 |  | 0 | 0 | 75.383 | 75.3833 | 36560.917 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 1080 |  |  | - |  | Economizer | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | Outage #10Unit 3 developed a tube leak in the Economizer section of the Boiler. R
GH3 | 32 | U2 | 2015-09-02 16:17 |  |  |  |  | 2015-09-03 02:35 |  | 0 | 0 | 10.3 | 10.3 | 4995.5 | 1 |  |  |  | 0 |  |  | 527.5
|  | CAUSE CODE : |  | 0500 |  |  | - |  | Main steam piping up to turbine stop valves | [8 empty] | AMP CODE: |  | 54
|  | DESCRIPTION : |  | Outage #11Unit 3 developed a leak in the Main Steam line drain line just before th
GH3 | 3 | U1 | 2016-01-11 11:50 |  |  |  |  | 2016-01-13 01:20 |  | 0 | 0 | 37.5 | 37.5 | 17925 | 1 |  |  |  | 0 |  |  | 525
|  | CAUSE CODE : |  | 4800 |  |  | - |  | Generator main leads | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | Outage #2Unit 3 was removed from service due to generator bus duct overheating.
GH3 | 16 | U1 | 2016-06-09 06:47 |  |  |  |  | 2016-06-09 18:19 |  | 0 | 0 | 11.533 | 11.5333 | 5593.667 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 4291 |  |  | - |  | Hydraulic system coolers | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Outage #8Unit 3 was removed from service to investigate an H2 cooler leak.
GH3 | 18 | U1 | 2016-06-11 17:43 |  |  |  |  | 2016-06-11 19:20 |  | 0 | 0 | 1.617 | 1.6167 | 784.083 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 4261 |  |  | - |  | Control valves | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Outage #10Unit 3 was removed from service when an EH leak was detected at the
GH3 | 19 | U1 | 2016-06-11 19:20 |  |  |  |  | 2016-06-15 17:45 |  | 0 | 0 | 94.417 | 94.4167 | 45792.083 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 4500 |  |  | - |  | Rotor windings (including damper windings and fan blades on hydro units) | [8 empty] | AMP CODE: |  | 49
|  | DESCRIPTION : |  | F540Outage #11Unit 3 generator could not be put in service due to a generator grou
GH3 | 21 | U1 | 2016-07-01 21:22 |  |  |  |  | 2016-07-03 05:06 |  | 0 | 0 | 31.733 | 31.7333 | 15390.667 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 1040 |  |  | - |  | First superheater | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Outage #12Unit 3 was removed from service due to a boiler superheat tube leak.
GH3 | 24 | U2 | 2016-07-19 21:37 |  |  |  |  | 2016-07-20 18:32 |  | 0 | 0 | 20.917 | 20.9167 | 10144.583 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 1040 |  |  | - |  | First superheater | [8 empty] | AMP CODE: |  | 54
|  | DESCRIPTION : |  | F540Outage #13The unit was removed from service due to a Primary SH tube leak. The
GH3 | 26 | U1 | 2016-08-12 01:09 |  |  |  |  | 2016-08-13 03:35 |  | 0 | 0 | 26.433 | 26.4333 | 12820.167 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 1040 |  |  | - |  | First superheater | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Outage #14The unit was removed from service due to a boiler Primary Superheat
GH3 | 28 | U1 | 2016-09-22 02:36 |  |  |  |  | 2016-09-23 23:40 |  | 0 | 0 | 45.067 | 45.0667 | 21722.133 | 1 |  |  |  | 0 |  |  | 527.5
|  | CAUSE CODE : |  | 1060 |  |  | - |  | First reheater | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Outage #15U3 came off line with a Reheat tube leak.
GH3 | 4 | SF | 2017-02-22 19:09 |  |  |  |  | 2017-02-22 22:42 |  | 0 | 0 | 3.55 | 3.55 | 1696.9 | 1 |  |  |  | 0 |  |  | 525
|  | CAUSE CODE : |  | 4899 |  |  | - |  | Other miscellaneous generator problems | [8 empty] | AMP CODE: |  | 49
|  | DESCRIPTION : |  | F430Outage #3Generator exciter field ground detection issues resulted in a startup
GH3 | 5 | U1 | 2017-04-15 16:24 |  |  |  |  | 2017-04-19 04:13 |  | 0 | 0 | 83.817 | 83.8167 | 40148.183 | 1 |  |  |  | 0 |  |  | 527.5
|  | CAUSE CODE : |  | 1080 |  |  | - |  | Economizer | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F540Outage #4Unit 3 was forced off line due to a tube leak in the upper economizer
GH3 | 24 | SF | 2017-11-15 10:07 |  |  |  |  | 2017-11-15 21:32 |  | 0 | 0 | 11.417 | 11.4167 | 5502.833 | 1 |  |  |  | 0 |  |  | 527.5
|  | CAUSE CODE : |  | 0800 |  |  | - |  | Drums and drum internals (single drum only) | [8 empty] | AMP CODE: |  | 54
|  | DESCRIPTION : |  | F540SUF Outage #11Drum door gasket leaking.
GH3 | 23 | U1 | 2017-11-19 10:36 |  |  |  |  | 2017-11-23 00:15 |  | 0 | 0 | 85.65 | 85.65 | 41283.3 | 1 |  |  |  | 0 |  |  | 527.5
|  | CAUSE CODE : |  | 1040 |  |  | - |  | First superheater | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F540Outage #10 Unit 3 was forced off-line due to superheat tube leak.
GH3 | 5 | U1 | 2018-03-03 11:30 |  |  |  |  | 2018-03-04 03:22 |  | 0 | 0 | 15.867 | 15.8667 | 7600.133 | 1 |  |  |  | 0 |  |  | 527.5
|  | CAUSE CODE : |  | 3220 |  |  | - |  | Circulating water piping | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F540Outage #4Unit was forced off line due to Circulating water bypass line leak.
GH3 | 8 | U1 | 2018-04-29 07:41 |  |  |  |  | 2018-04-29 09:43 |  | 0 | 0 | 2.033 | 2.0333 | 973.967 | 1 |  |  |  | 0 |  |  | 527.5
|  | CAUSE CODE : |  | 3412 |  |  | - |  | Feedwater pump drive - steam turbine | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | Outage #5Boiler tripped on low drum level due to the loss of 3-2 BFPT. Unit was r
GH3 | 10 | U1 | 2018-06-16 23:21 |  |  |  |  | 2018-06-17 06:07 |  | 0 | 0 | 6.767 | 6.7667 | 3254.767 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 4535 |  |  | - |  | "Stator, General" | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | Outage # 6Unit was removed from service due to stator system low flow transmitter
GH3 | 21 | U1 | 2018-11-20 00:40 |  |  |  |  | 2018-11-27 05:56 |  | 0 | 0 | 173.267 | 173.2667 | 82994.734 | 1 |  |  |  | 0 |  |  | 527.5
|  | CAUSE CODE : |  | 1040 |  |  | - |  | First superheater | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | Outage #11Multiple tube leaks in 3rd division panel.
GH3 | 22 | U1 | 2018-11-27 16:39 |  |  |  |  | 2018-11-30 09:16 |  | 0 | 0 | 64.617 | 64.6167 | 30951.383 | 1 |  |  |  | 0 |  |  | 527.5
|  | CAUSE CODE : |  | 1350 |  |  | - |  | Other miscellaneous boiler tube problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | Outage #12Removed tube 20 and 21 from the 3rd SH division panel, capped tubes at t
GH3 | 23 | U1 | 2018-12-01 18:04 |  |  |  |  | 2018-12-04 13:50 |  | 0 | 0 | 67.767 | 67.7667 | 35577.5 | 1 |  |  |  | 0 |  |  | 525
|  | CAUSE CODE : |  | 1350 |  |  | - |  | Other miscellaneous boiler tube problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | Outage # 13Tube leak primary superheater panel 95. Removed debris from superheat
GH3 | 33 | U1 | 2019-04-22 01:22 |  |  |  |  | 2019-04-22 23:17 |  | 0 | 0 | 21.917 | 21.9167 | 10498.083 | 1 |  |  |  | 0 |  |  | 527.5
|  | CAUSE CODE : |  | 4609 |  |  | - |  | Other exciter problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F540Outage #1Exiter cooler leaked causing a generator ground detection.
GH3 | 34 | U1 | 2019-04-26 01:55 |  |  |  |  | 2019-04-26 17:32 |  | 0 | 0 | 15.617 | 15.6167 | 7480.383 | 1 |  |  |  | 0 |  |  | 527.5
|  | CAUSE CODE : |  | 4609 |  |  | - |  | Other exciter problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F540Forced OutageExternal leak in GH3 lower exciter cooler piping caused a generat
GH3 | 48 | U1 | 2019-11-15 22:00 |  |  |  |  | 2019-11-16 13:34 |  | 0 | 0 | 15.567 | 15.5667 | 7456.433 | 1 |  |  |  | 0 |  |  | 527.5
|  | CAUSE CODE : |  | 4630 |  |  | - |  | Liquid cooling system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | Outage #5Unit was forced off line due to an internal cooling water leak on the exc
GH3 | 55 | U1 | 2019-12-28 06:46 |  |  |  |  | 2019-12-28 15:10 |  | 0 | 0 | 8.4 | 8.4 | 4410 | 1 |  |  |  | 0 |  |  | 525
|  | CAUSE CODE : |  | 4609 |  |  | - |  | Other exciter problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Outage #8Exciter cooler leak.
GH3 | 6 | U1 | 2020-03-31 02:29 |  |  |  |  | 2020-04-03 03:33 |  | 0 | 0 | 73.067 | 73.0667 | 34998.933 | 1 |  |  |  | 0 |  |  | 527.5
|  | CAUSE CODE : |  | 3611 |  |  | - |  | Switchyard circuit breakers - external (OMC) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F700Outage #3Electrical component went to ground.
GH3 | 14 | U1 | 2020-06-02 03:29 |  |  |  |  | 2020-06-02 07:03 |  | 0 | 0 | 3.567 | 3.5667 | 1715.567 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 1480 |  |  | - |  | Other induced draft fan problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Outage #8Immediate Forced Outage. 3-5 mill unloaded causing furance pressure e
GH3 | 15 | U1 | 2020-09-01 09:19 |  |  |  |  | 2020-09-01 10:23 |  | 0 | 0 | 1.067 | 1.0667 | 510.933 | 1 |  |  |  | 0 |  |  | 527.5
|  | CAUSE CODE : |  | 4308 |  |  | - |  | Automatic turbine control systems - digital control and monitoring | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Outage #9Trip #3 Turbine bearing vibration.
GH3 | 18 | SF | 2020-10-29 12:30 |  |  |  |  | 2020-10-29 15:09 |  | 0 | 0 | 2.65 | 2.65 | 1269.35 | 1 |  |  |  | 0 |  |  | 527.5
|  | CAUSE CODE : |  | 4240 |  |  | - |  | Bearings | [8 empty] | AMP CODE: |  | 54
|  | DESCRIPTION : |  | F540Outage #12Start-up failure due to #3 turbine bearing oil leak,
GH3 | 19 | U1 | 2020-11-20 12:42 |  |  |  |  | 2020-11-20 13:32 |  | 0 | 0 | 0.833 | 0.8333 | 399.167 | 1 |  |  |  | 0 |  |  | 527.5
|  | CAUSE CODE : |  | 4302 |  |  | - |  | Turbine trip devices (including instruments) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Outage #13Tripped off-line due to loss turbine thrust indication when fuses we
GH3 | 7 | U1 | 2021-09-22 23:30 |  |  |  |  | 2021-09-23 00:32 |  | 0 | 0 | 1.033 | 1.0333 | 494.45 | 1 |  |  |  | 0 |  |  | 527.5
|  | CAUSE CODE : |  | 4281 |  |  | - |  | Lube oil coolers | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Outage#1 GH3 was forced off line due to loss of turbine lube oil pressure.
GH3 | 10 | U1 | 2021-11-02 05:47 |  |  |  |  | 2021-11-03 10:01 |  | 0 | 0 | 28.233 | 28.2333 | 13509.65 | 1 |  |  |  | 0 |  |  | 527.5
|  | CAUSE CODE : |  | 1060 |  |  | - |  | First reheater | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Outage #4Boiler Trip - Tube Leak. Unit was removed from service due to tube le
GH3 | 2 | U1 | 2022-01-02 18:31 |  |  |  |  | 2022-01-02 20:30 |  | 0 | 0 | 1.983 | 1.9833 | 944.067 | 1 |  |  |  | 0 |  |  | 525
|  | CAUSE CODE : |  | 1488 |  |  | - |  | Air heater (regenerative) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830OUTAGE# 1 Forced off due to loss of boiler flame causing low main steam temps (
GH3 | 5 | U1 | 2022-01-06 02:09 |  |  |  |  | 2022-01-06 03:07 |  | 0 | 0 | 0.967 | 0.9667 | 460.133 | 1 |  |  |  | 0 |  |  | 525
|  | CAUSE CODE : |  | 4308 |  |  | - |  | Automatic turbine control systems - digital control and monitoring | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Outage# 4 Automatic turbine Control system.
GH3 | 7 | U1 | 2022-04-20 00:01 |  |  |  |  | 2022-04-20 09:46 |  | 0 | 0 | 9.75 | 9.75 | 4665.375 | 1 |  |  |  | 0 |  |  | 527.5
|  | CAUSE CODE : |  | 4740 |  |  | - |  | Emergency generator trip devices | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Outage#6 3-A unit auxilary transformer protective relay failed.
GH3 | 6 | U1 | 2023-02-13 11:47 |  |  |  |  | 2023-02-14 19:17 |  | 0 | 0 | 31.5 | 31.5 | 14993.999 | 1 |  |  |  | 0 |  |  | 525
|  | CAUSE CODE : |  | 1040 |  |  | - |  | First superheater | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Outage #6Forced outage due to a superheat tube leak.
Ghent - GH4
Unit | Event | Type | Start |  |  |  |  | End |  | GAC | NAC | Duration | Equiv Hrs | Equiv MWH | Cont | Work Start | Work End |  | Hours |  |  | Gross Capacity Impact (MW)
GH4 | 7 | U1 | 2014-02-09 03:51 |  |  |  |  | 2014-02-09 05:38 |  | 0 | 0 | 1.783 | 1.7833 | 875.617 | 1 |  |  |  | 0 |  |  | 525
|  | CAUSE CODE : |  | 0250 |  |  | - |  | Pulverizer feeders | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | Outage #24-6 Mill Feeder coal inlet plugged causing controls to see this feeder as
GH4 | 17 | U1 | 2014-04-21 21:22 |  |  |  |  | 2014-04-22 00:08 |  | 0 | 0 | 2.767 | 2.7667 | 1297.566 | 1 |  |  |  | 0 |  |  | 525
|  | CAUSE CODE : |  | 1475 |  |  | - |  | Induced draft fan controls | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | Outage #3Unit 4 is running with furnace pressure control on only the 4-2 ID Fan du
GH4 | 47 | U1 | 2014-08-25 10:14 |  |  |  |  | 2014-08-26 07:28 |  | 0 | 0 | 21.233 | 21.2333 | 9958.433 | 1 |  |  |  | 0 |  |  | 525
|  | CAUSE CODE : |  | 1000 |  |  | - |  | Waterwall (Furnace wall) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | Outage #9Water wall tube blew out in boiler causing furnace to trip on high furnac
GH4 | 48 | U1 | 2014-08-26 09:53 |  |  |  |  | 2014-08-26 11:00 |  | 0 | 0 | 1.117 | 1.1167 | 523.717 | 1 |  |  |  | 0 |  |  | 525
|  | CAUSE CODE : |  | 1599 |  |  | - |  | Other miscellaneous boiler air and gas system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | Outage #10While starting 4-4 mill soon after Unit 4 start up, a furnace pressure e
GH4 | 49 | U1 | 2014-08-27 08:34 |  |  |  |  | 2014-08-29 21:18 |  | 0 | 0 | 60.733 | 60.7333 | 28483.932 | 1 |  |  |  | 0 |  |  | 525
|  | CAUSE CODE : |  | 1000 |  |  | - |  | Waterwall (Furnace wall) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | Outage #11A water wall tube leak ruptured causing the furnace to trip on high furn
GH4 | 50 | U1 | 2014-09-04 17:31 |  |  |  |  | 2014-09-05 16:20 |  | 0 | 0 | 22.817 | 22.8167 | 10701.016 | 1 |  |  |  | 0 |  |  | 525
|  | CAUSE CODE : |  | 3110 |  |  | - |  | Condenser tube leaks | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F540Outage #12Conditions started showing signs of a bad Condenser tube leak. Remo
GH4 | 54 | U1 | 2014-09-12 05:47 |  |  |  |  | 2014-09-12 06:00 |  | 0 | 0 | 0.217 | 0.2167 | 101.617 | 1 |  |  |  | 0 |  |  | 525
|  | CAUSE CODE : |  | 9900 |  |  | - |  | Operator error | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | Outage #14Unit 4 was running with a suspected condenser tube leak in 4-2 auxiliary
GH4 | 62 | U1 | 2014-12-05 01:44 |  |  |  |  | 2014-12-05 06:51 |  | 0 | 0 | 5.117 | 5.1167 | 2512.283 | 1 |  |  |  | 0 |  |  | 525
|  | CAUSE CODE : |  | 4470 |  |  | - |  | Differential expansion | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | Outage #17After start up of U4 after major overhaul on the turbine, the turbine wa
GH4 | 63 | U1 | 2014-12-05 07:31 |  |  |  |  | 2014-12-05 12:18 |  | 0 | 0 | 4.783 | 4.7833 | 2348.617 | 1 |  |  |  | 0 |  |  | 525
|  | CAUSE CODE : |  | 4470 |  |  | - |  | Differential expansion | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | Outage #18After start up of U4 after major overhaul on the turbine, the turbine wa
GH4 | 64 | U1 | 2014-12-05 13:04 |  |  |  |  | 2014-12-05 14:06 |  | 0 | 0 | 1.033 | 1.0333 | 507.367 | 1 |  |  |  | 0 |  |  | 525
|  | CAUSE CODE : |  | 4470 |  |  | - |  | Differential expansion | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | Outage #19After start up of U4 after major overhaul on the turbine, the turbine wa
GH4 | 66 | U1 | 2014-12-07 15:18 |  |  |  |  | 2014-12-08 09:46 |  | 0 | 0 | 18.467 | 18.4667 | 9067.133 | 1 |  |  |  | 0 |  |  | 525
|  | CAUSE CODE : |  | 3431 |  |  | - |  | Other feedwater valves | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | Outage #20Packing blew out on the flue economizer inlet valve causing a tremendous
GH4 | 71 | U1 | 2014-12-10 09:35 |  |  |  |  | 2014-12-10 12:36 |  | 0 | 0 | 3.017 | 3.0167 | 1481.183 | 1 |  |  |  | 0 |  |  | 525
|  | CAUSE CODE : |  | 1470 |  |  | - |  | Induced draft fan motors and drives | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | Outage #21U4 Boiler tripped on low furnace pressure while working on 4-2 FD fan in
GH4 | 76 | U1 | 2014-12-12 23:03 |  |  |  |  | 2014-12-13 04:14 |  | 0 | 0 | 5.183 | 5.1833 | 2545.017 | 1 |  |  |  | 0 |  |  | 525
|  | CAUSE CODE : |  | 1455 |  |  | - |  | Induced draft fans | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | Outage #22U4 Boiler tripped on "Low Furnace Pressure" when the 4-2A and 4-2B ID fa
GH4 | 4 | U1 | 2015-01-25 18:00 |  |  |  |  | 2015-01-27 00:22 |  | 0 | 0 | 30.367 | 30.3667 | 14910.033 | 1 |  |  |  | 0 |  |  | 525
|  | CAUSE CODE : |  | 1310 |  |  | - |  | Water side cleaning (acid cleaning) | [8 empty] | AMP CODE: |  | 54
|  | DESCRIPTION : |  | Outage #2While filling the boiler for startup from the previous Maintenance event,
GH4 | 5 | U1 | 2015-01-27 02:39 |  |  |  |  | 2015-01-27 04:11 |  | 0 | 0 | 1.533 | 1.5333 | 752.867 | 1 |  |  |  | 0 |  |  | 525
|  | CAUSE CODE : |  | 1475 |  |  | - |  | Induced draft fan controls | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | Outage #3After Unit 4 had just come back on line and while placing mills in servic
GH4 | 6 | U1 | 2015-02-04 11:39 |  |  |  |  | 2015-02-05 12:57 |  | 0 | 0 | 25.3 | 25.3 | 12422.3 | 1 |  |  |  | 0 |  |  | 525
|  | CAUSE CODE : |  | 1080 |  |  | - |  | Economizer | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F540Outage #4Boiler developed leak in Economizer section of the boiler. Removed u
GH4 | 16 | U1 | 2015-03-23 08:41 |  |  |  |  | 2015-03-24 15:30 |  | 0 | 0 | 30.817 | 30.8167 | 15130.983 | 1 |  |  |  | 0 |  |  | 525
|  | CAUSE CODE : |  | 3110 |  |  | - |  | Condenser tube leaks | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | Outage #5Unit 4 was experiencing signs of a bad condenser leak. Removed the unit
GH4 | 29 | U1 | 2015-07-03 01:12 |  |  |  |  | 2015-07-03 05:09 |  | 0 | 0 | 3.95 | 3.95 | 1836.75 | 1 |  |  |  | 0 |  |  | 525
|  | CAUSE CODE : |  | 4302 |  |  | - |  | Turbine trip devices (including instruments) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | Outage #7Main Turbine thrust bearing showed movement about the trip point tripping
GH4 | 37 | U1 | 2015-08-14 13:47 |  |  |  |  | 2015-08-14 15:08 |  | 0 | 0 | 1.35 | 1.35 | 627.75 | 1 |  |  |  | 0 |  |  | 525
|  | CAUSE CODE : |  | 3430 |  |  | - |  | Feedwater regulating (boiler level control) valve | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | Outage #9Adjustments were being made to HP heater level controls and the HP heater
GH4 | 6 | U1 | 2016-03-14 06:18 |  |  |  |  | 2016-03-17 13:19 |  | 0 | 0 | 79.017 | 79.0167 | 37611.933 | 1 |  |  |  | 0 |  |  | 525
|  | CAUSE CODE : |  | 1080 |  |  | - |  | Economizer | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | Outage #1Unit 4 came off line due to a leak in the economizer.
GH4 | 18 | U1 | 2016-07-23 15:02 |  |  |  |  | 2016-07-30 21:06 |  | 0 | 0 | 174.067 | 174.0667 | 80941 | 1 |  |  |  | 0 |  |  | 525
|  | CAUSE CODE : |  | 3220 |  |  | - |  | Circulating water piping | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Outage #4GH4 off line due to failure of the U4 cooling tower south distributio
GH4 | 7 | U1 | 2017-02-12 07:58 |  |  |  |  | 2017-02-12 23:26 |  | 0 | 0 | 15.467 | 15.4667 | 7532.267 | 1 |  |  |  | 0 |  |  | 525
|  | CAUSE CODE : |  | 3412 |  |  | - |  | Feedwater pump drive - steam turbine | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F540Outage #1Unit 4 was forced off line due to 4-2 Boiler Feed Pump Turbine high p
GH4 | 16 | U1 | 2017-05-03 01:57 |  |  |  |  | 2017-05-04 20:34 |  | 0 | 0 | 42.617 | 42.6167 | 20370.766 | 1 |  |  |  | 0 |  |  | 525
|  | CAUSE CODE : |  | 1040 |  |  | - |  | First superheater | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | Outage #3GH4 was removed from service due to a tube leak in the PSH area of the bo
GH4 | 19 | U1 | 2017-07-15 18:33 |  |  |  |  | 2017-07-17 20:03 |  | 0 | 0 | 49.5 | 49.5 | 23017.5 | 1 |  |  |  | 0 |  |  | 525
|  | CAUSE CODE : |  | 1040 |  |  | - |  | First superheater | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | Outage #4Unit 4 came off one due to a tube leak in the Primary Superheat section o
GH4 | 20 | U1 | 2017-07-25 02:30 |  |  |  |  | 2017-07-26 17:26 |  | 0 | 0 | 38.933 | 38.9333 | 18104 | 1 |  |  |  | 0 |  |  | 525
|  | CAUSE CODE : |  | 1040 |  |  | - |  | First superheater | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Outage #5GH4 was brought off line due to a tube leak in the Superheat section
GH4 | 24 | U1 | 2017-11-18 17:32 |  |  |  |  | 2017-11-21 07:34 |  | 0 | 0 | 62.033 | 62.0333 | 29527.866 | 1 |  |  |  | 0 |  |  | 525
|  | CAUSE CODE : |  | 3220 |  |  | - |  | Circulating water piping | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F540Outage #6GH4 was Forced off line due to Circulating water line leak.
GH4 | 25 | U1 | 2017-12-07 15:08 |  |  |  |  | 2017-12-07 20:23 |  | 0 | 0 | 5.25 | 5.25 | 2556.75 | 1 |  |  |  | 0 |  |  | 525
|  | CAUSE CODE : |  | 4800 |  |  | - |  | Generator main leads | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | FV00Outage # 7 GH 4 Forced off line due to vibration in generator lead box.
GH4 | 15 | U1 | 2018-06-13 13:18 |  |  |  |  | 2018-06-14 20:21 |  | 0 | 0 | 31.05 | 31.05 | 14841.9 | 1 |  |  |  | 0 |  |  | 525
|  | CAUSE CODE : |  | 3320 |  |  | - |  | Condensate piping | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | Outage #2Unit was removed from service due to a leak in the condensate supply to t
GH4 | 5 | U1 | 2020-03-02 09:34 |  |  |  |  | 2020-03-03 17:03 |  | 0 | 0 | 31.483 | 31.4833 | 15049.032 | 1 |  |  |  | 0 |  |  | 525
|  | CAUSE CODE : |  | 1040 |  |  | - |  | First superheater | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F540Outage #1Forced outage due to a leak in the primary superheater.
GH4 | 11 | U1 | 2020-05-14 23:24 |  |  |  |  | 2020-05-16 02:38 |  | 0 | 0 | 27.233 | 27.2333 | 13017.533 | 1 |  |  |  | 0 |  |  | 525
|  | CAUSE CODE : |  | 1060 |  |  | - |  | First reheater | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F540Outage #7Forced outage. Leak in reheat section of the boiler.
GH4 | 23 | U1 | 2020-09-11 06:10 |  |  |  |  | 2020-09-14 04:26 |  | 0 | 0 | 70.267 | 70.2667 | 33587.467 | 1 |  |  |  | 0 |  |  | 525
|  | CAUSE CODE : |  | 0400 |  |  | - |  | Burner wind box fires | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Outage #11Windbox Fire.
GH4 | 13 | U1 | 2021-09-18 01:30 |  |  |  |  | 2021-09-19 16:55 |  | 0 | 0 | 39.417 | 39.4167 | 18841.167 | 1 |  |  |  | 0 |  |  | 525
|  | CAUSE CODE : |  | 1040 |  |  | - |  | First superheater | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Outage# 4 GH4 was forced offline due to a SH leak in the penthouse section of t
GH4 | 2 | U1 | 2022-04-30 11:16 |  |  |  |  | 2022-05-02 16:50 |  | 0 | 0 | 53.567 | 53.5667 | 25604.867 | 1 |  |  |  | 0 |  |  | 525
|  | CAUSE CODE : |  | 1040 |  |  | - |  | First superheater | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Outage #2Forced Outage due to tube leak in division panel #3 tube 14.
GH4 | 3 | U1 | 2022-05-02 22:52 |  |  |  |  | 2022-05-18 08:15 |  | 0 | 0 | 369.383 | 369.3833 | 176565.233 | 1 |  |  |  | 0 |  |  | 525
|  | CAUSE CODE : |  | 4240 |  |  | - |  | Bearings | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F820Outage #3Ghent 4 Divsion panel #3 Tube14 tube leaks were repaired at 16:50 hou
GH4 | 6 | U1 | 2023-09-16 13:30 |  |  |  |  | 2023-09-18 11:53 |  | 0 | 0 | 46.383 | 46.3833 | 22171.233 | 1 |  |  |  | 0 |  |  | 525
|  | CAUSE CODE : |  | 3412 |  |  | - |  | Feedwater pump drive - steam turbine | [8 empty] | AMP CODE: |  | 42
|  | DESCRIPTION : |  | F420Outage #4GH 4 was switched from reserve outage to forced outage status to insp
Haefling - HA1
Unit | Event | Type | Start |  |  |  |  | End |  | GAC | NAC | Duration | Equiv Hrs | Equiv MWH | Cont | Work Start | Work End |  | Hours |  |  | Gross Capacity Impact (MW)
HA1 | 2 | SF | 2014-01-06 21:22 |  |  |  |  | 2014-01-14 13:14 |  | 0 | 0 | 183.867 | 183.8667 | 2574.134 | 1 |  |  |  | 0 |  |  | 13.7
|  | CAUSE CODE : |  | 5160 |  |  | - |  | Cooling and seal air system | [8 empty] | AMP CODE: |  | 54
|  | DESCRIPTION : |  | F540Busted glycol line on radiator. Failed to ignite on start up.
HA1 | 4 | U1 | 2014-01-16 12:31 |  |  |  |  | 2014-01-17 14:09 |  | 0 | 0 | 25.633 | 25.6333 | 358.867 | 1 |  |  |  | 0 |  |  | 13.7
|  | CAUSE CODE : |  | 5120 |  |  | - |  | Hydraulic oil system | [8 empty] | AMP CODE: |  | 54
|  | DESCRIPTION : |  | F540Oil leak on diesel starting engine.
HA1 | 5 | U1 | 2014-01-17 14:23 |  |  |  |  | 2014-01-20 14:33 |  | 0 | 0 | 72.167 | 72.1667 | 1010.333 | 1 |  |  |  | 0 |  |  | 13.7
|  | CAUSE CODE : |  | 5108 |  |  | - |  | High engine exhaust temperature | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F410Lost two exhaust gas thermocouples during run.
HA1 | 7 | U1 | 2014-01-30 06:30 |  |  |  |  | 2014-01-30 07:01 |  | 0 | 0 | 0.517 | 0.5167 | 7.233 | 1 |  |  |  | 0 |  |  | 13.7
|  | CAUSE CODE : |  | 5050 |  |  | - |  | Ignition system | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Ignition torch failed to light
HA1 | 9 | U1 | 2014-02-08 02:53 |  |  |  |  | 2014-02-08 19:05 |  | 0 | 0 | 16.2 | 16.2 | 226.8 | 1 |  |  |  | 0 |  |  | 13.7
|  | CAUSE CODE : |  | 3611 |  |  | - |  | Switchyard circuit breakers - external (OMC) | [8 empty] | AMP CODE: |  | X0
|  | DESCRIPTION : |  | FX00Loss of power to 138KV sub.
HA1 | 15 | SF | 2014-11-17 14:24 |  |  |  |  | 2014-11-17 15:17 |  | 0 | 0 | 0.883 | 0.8833 | 12.367 | 1 |  |  |  | 0 |  |  | 12.8
|  | CAUSE CODE : |  | 5050 |  |  | - |  | Ignition system | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Failed to ignite
HA1 | 2 | SF | 2015-01-06 23:19 |  |  |  |  | 2015-01-06 23:44 |  | 0 | 0 | 0.417 | 0.4167 | 5.833 | 1 |  |  |  | 0 |  |  | 13.7
|  | CAUSE CODE : |  | 5051 |  |  | - |  | Pilot fuel piping and valves | [8 empty] | AMP CODE: |  | 69
|  | DESCRIPTION : |  | F690Oil valve stuck to diesel starting engine.
HA1 | 3 | U1 | 2015-01-08 09:28 |  |  |  |  | 2015-01-08 14:29 |  | 0 | 0 | 5.017 | 5.0167 | 70.233 | 1 |  |  |  | 0 |  |  | 13.7
|  | CAUSE CODE : |  | 5680 |  |  | - |  | Vibration (not engine) in unit not attributable to bearings or other components | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F410High Vibration trip on #2 bearing. Signal look to be false, and loose wire was fo
HA1 | 11 | U1 | 2015-07-20 12:56 |  |  |  |  | 2015-07-20 14:06 |  | 0 | 0 | 1.167 | 1.1667 | 14 | 1 |  |  |  | 0 |  |  | 12
|  | CAUSE CODE : |  | 4899 |  |  | - |  | Other miscellaneous generator problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Powerblock Emergency Trip
HA1 | 2 | U1 | 2016-04-14 10:23 |  |  |  |  | 2016-04-14 11:54 |  | 0 | 0 | 1.517 | 1.5167 | 19.717 | 1 |  |  |  | 0 |  |  | 12.8
|  | CAUSE CODE : |  | 5248 |  |  | - |  | Gas Turbine Control System - logic problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F410Unit would not load up after going online.
HA1 | 3 | U1 | 2016-04-14 13:31 |  |  |  |  | 2016-04-15 07:52 |  | 0 | 0 | 18.35 | 18.35 | 238.55 | 1 |  |  |  | 0 |  |  | 12.8
|  | CAUSE CODE : |  | 5248 |  |  | - |  | Gas Turbine Control System - logic problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F410Unit would not load up after going online.
HA1 | 2 | U1 | 2018-01-03 11:12 |  |  |  |  | 2018-01-03 12:12 |  | 0 | 0 | 1 | 1 | 14 | 1 |  |  |  | 0 |  |  | 13.7
|  | CAUSE CODE : |  | 5510 |  |  | - |  | Lube oil system | [8 empty] | AMP CODE: |  | 54
|  | DESCRIPTION : |  | F540Replace Ratchet Pump
HA1 | 4 | U1 | 2018-01-03 14:34 |  |  |  |  | 2018-01-03 16:43 |  | 0 | 0 | 2.15 | 2.15 | 30.1 | 1 |  |  |  | 0 |  |  | 13.7
|  | CAUSE CODE : |  | 3610 |  |  | - |  | Switchyard circuit breakers - external (not OMC) | [8 empty] | AMP CODE: |  | 48
|  | DESCRIPTION : |  | F480Breaker frozen
HA1 | 12 | SF | 2018-12-06 13:00 |  |  |  |  | 2018-12-11 11:25 |  | 0 | 0 | 118.417 | 118.4167 | 1657.833 | 1 |  |  |  | 0 |  |  | 13.7
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 72
|  | DESCRIPTION : |  | F720Clutch will not disengage. Believe issue is with starting diesel. Still investig
HA1 | 14 | U1 | 2018-12-19 12:50 |  |  |  |  | 2019-01-01 |  | 0 | 0 | 299.167 | 299.1667 | 4188.333 | 1 |  |  |  | 0 |  |  | 13.7
|  | CAUSE CODE : |  | 5445 |  |  | - |  | Liquid fuel oil transfer/forwarding pump | [8 empty] | AMP CODE: |  | 54
|  | DESCRIPTION : |  | F540Replace fuel oil piping going to unit from forwarding skid.
HA1 | 1 | U1 | 2019-01-01 |  |  |  |  | 2019-03-22 10:32 |  | 0 | 0 | 1930.533 | 1930.5333 | 26512.933 | 1 |  |  |  | 0 |  |  | 13.7
|  | CAUSE CODE : |  | 5445 |  |  | - |  | Liquid fuel oil transfer/forwarding pump | [8 empty] | AMP CODE: |  | 54
|  | DESCRIPTION : |  | F540Replace fuel oil piping going to unit from forwarding skid.
HA1 | 3 | SF | 2020-05-14 11:30 |  |  |  |  | 2020-05-14 12:33 |  | 0 | 0 | 1.05 | 1.05 | 13.44 | 1 |  |  |  | 0 |  |  | 12.8
|  | CAUSE CODE : |  | 5520 |  |  | - |  | Hydraulic oil system | [8 empty] | AMP CODE: |  | 72
|  | DESCRIPTION : |  | F720Hydraulic safety oil dump valve sticking. Clean oil.
HA1 | 5 | U1 | 2021-07-15 14:35 |  |  |  |  | 2021-07-16 12:21 |  | 0 | 0 | 21.767 | 21.7667 | 261.2 | 1 |  |  |  | 0 |  |  | 12
|  | CAUSE CODE : |  | 4620 |  |  | - |  | Air cooling system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Shear pin on fan failed.
HA1 | 7 | SF | 2021-11-03 06:00 |  |  |  |  | 2021-11-03 07:55 |  | 0 | 0 | 1.917 | 1.9167 | 24.533 | 1 |  |  |  | 0 |  |  | 12.8
|  | CAUSE CODE : |  | 5050 |  |  | - |  | Ignition system | [8 empty] | AMP CODE: |  | 40
|  | DESCRIPTION : |  | F400Unit came to speed but did not light off.
HA1 | 5 | U1 | 2022-12-23 10:33 |  |  |  |  | 2022-12-24 14:57 |  | 0 | 0 | 28.4 | 28.4 | 389.08 | 1 |  |  |  | 0 |  |  | 13.7
|  | CAUSE CODE : |  | 3700 |  |  | - |  | Power Station switchyard (non generating unit equipment) | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F820Substation breaker will not remain closed.
HA1 | 5 | SF | 2023-12-20 11:02 |  |  |  |  | 2024-01-01 |  | 0 | 0 | 276.967 | 276.9667 | 3794.443 | 1 |  |  |  | 0 |  |  | 13.7
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Engine starter failed
Haefling - HA2
Unit | Event | Type | Start |  |  |  |  | End |  | GAC | NAC | Duration | Equiv Hrs | Equiv MWH | Cont | Work Start | Work End |  | Hours |  |  | Gross Capacity Impact (MW)
HA2 | 4 | U1 | 2014-02-08 02:53 |  |  |  |  | 2014-02-08 19:05 |  | 0 | 0 | 16.2 | 16.2 | 226.8 | 1 |  |  |  | 0 |  |  | 13.7
|  | CAUSE CODE : |  | 3611 |  |  | - |  | Switchyard circuit breakers - external (OMC) | [8 empty] | AMP CODE: |  | X0
|  | DESCRIPTION : |  | FX00Loss power to 138KV bus in substation
HA2 | 15 | U1 | 2015-12-01 10:22 |  |  |  |  | 2015-12-01 14:03 |  | 0 | 0 | 3.683 | 3.6833 | 51.567 | 1 |  |  |  | 0 |  |  | 13.7
|  | CAUSE CODE : |  | 5111 |  |  | - |  | Lube oil pumps | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410DC emergency lube oil pump motor bad
HA2 | 2 | U1 | 2016-04-14 09:13 |  |  |  |  | 2016-04-15 12:09 |  | 0 | 0 | 26.933 | 26.9333 | 350.133 | 1 |  |  |  | 0 |  |  | 12.8
|  | CAUSE CODE : |  | 5248 |  |  | - |  | Gas Turbine Control System - logic problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F410Unit would not load up after going online.
HA2 | 3 | U1 | 2017-07-13 17:53 |  |  |  |  | 2017-07-19 08:05 |  | 0 | 0 | 134.2 | 134.2 | 1610.4 | 1 |  |  |  | 0 |  |  | 12
|  | CAUSE CODE : |  | 4602 |  |  | - |  | Exciter commutator and brushes | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F030Unit tripped due to a rotor ground fault. Excitation brushes failed causing the f
HA2 | 2 | SF | 2018-01-03 14:34 |  |  |  |  | 2018-01-03 16:43 |  | 0 | 0 | 2.15 | 2.15 | 30.1 | 1 |  |  |  | 0 |  |  | 13.7
|  | CAUSE CODE : |  | 3610 |  |  | - |  | Switchyard circuit breakers - external (not OMC) | [8 empty] | AMP CODE: |  | 48
|  | DESCRIPTION : |  | F480Substation breaker hydraulics frozen
HA2 | 10 | SF | 2018-12-06 13:00 |  |  |  |  | 2018-12-07 11:01 |  | 0 | 0 | 22.017 | 22.0167 | 308.233 | 1 |  |  |  | 0 |  |  | 13.7
|  | CAUSE CODE : |  | 5510 |  |  | - |  | Lube oil system | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Lube oil heater out of service. Also an issue with lube oil header pressure trans
HA2 | 3 | SF | 2020-05-14 11:30 |  |  |  |  | 2020-05-21 13:55 |  | 0 | 0 | 170.417 | 170.4167 | 2181.333 | 1 |  |  |  | 0 |  |  | 12.8
|  | CAUSE CODE : |  | 5120 |  |  | - |  | Hydraulic oil system | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Failure of servo pilot valve to main gas ratio valve. Replace servo valve.
HA2 | 4 | SF | 2020-05-21 13:55 |  |  |  |  | 2020-05-22 12:52 |  | 0 | 0 | 22.95 | 22.95 | 293.76 | 1 |  |  |  | 0 |  |  | 12.8
|  | CAUSE CODE : |  | 5450 |  |  | - |  | Ignition system | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Replaced ignition transformers.
HA2 | 6 | SF | 2020-12-11 11:28 |  |  |  |  | 2020-12-14 12:41 |  | 0 | 0 | 73.217 | 73.2167 | 1003.069 | 1 |  |  |  | 0 |  |  | 13.7
|  | CAUSE CODE : |  | 5041 |  |  | - |  | Fuel piping and valves | [8 empty] | AMP CODE: |  | 06
|  | DESCRIPTION : |  | F060Fuel valve would not operate. Solenoid was tested and found grounded.
HA2 | 6 | SF | 2021-11-03 06:00 |  |  |  |  | 2021-11-03 08:10 |  | 0 | 0 | 2.167 | 2.1667 | 27.733 | 1 |  |  |  | 0 |  |  | 12.8
|  | CAUSE CODE : |  | 5450 |  |  | - |  | Ignition system | [8 empty] | AMP CODE: |  | 40
|  | DESCRIPTION : |  | F400Unit came to speed but did not light off.
HA2 | 3 | U1 | 2022-05-12 13:25 |  |  |  |  | 2022-05-12 16:01 |  | 0 | 0 | 2.6 | 2.6 | 33.28 | 1 |  |  |  | 0 |  |  | 12.8
|  | CAUSE CODE : |  | 4620 |  |  | - |  | Air cooling system | [8 empty] | AMP CODE: |  | 76
|  | DESCRIPTION : |  | F760Broken shear pin on cooling fan caused excessive oil temps
HA2 | 7 | U1 | 2022-12-23 10:33 |  |  |  |  | 2022-12-24 14:57 |  | 0 | 0 | 28.4 | 28.4 | 389.08 | 1 |  |  |  | 0 |  |  | 13.7
|  | CAUSE CODE : |  | 3700 |  |  | - |  | Power Station switchyard (non generating unit equipment) | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F820Substation breaker will not remain closed.
HA2 | 8 | U1 | 2022-12-24 14:57 |  |  |  |  | 2022-12-28 10:30 |  | 0 | 0 | 91.55 | 91.55 | 1254.235 | 1 |  |  |  | 0 |  |  | 13.7
|  | CAUSE CODE : |  | 5110 |  |  | - |  | Lube oil system - general | [8 empty] | AMP CODE: |  | 48
|  | DESCRIPTION : |  | F480Lube oil temperature too low.
HA2 | 5 | SF | 2023-12-20 14:22 |  |  |  |  | 2024-01-01 |  | 0 | 0 | 273.633 | 273.6333 | 3748.777 | 1 |  |  |  | 0 |  |  | 13.7
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Engine starter failed
Mill Creek - MC1
Unit | Event | Type | Start |  |  |  |  | End |  | GAC | NAC | Duration | Equiv Hrs | Equiv MWH | Cont | Work Start | Work End |  | Hours |  |  | Gross Capacity Impact (MW)
MC1 | 10 | U1 | 2014-01-18 08:33 |  |  |  |  | 2014-01-18 11:21 |  | 0 | 0 | 2.8 | 2.8 | 848.4 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 0800 |  |  | - |  | Drums and drum internals (single drum only) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820High Drum Level Trip due to Turbine #2 Control Valve Issue, Replaced Fast Acting S
MC1 | 42 | SF | 2014-02-21 22:16 |  |  |  |  | 2014-02-22 17:58 |  | 0 | 0 | 19.7 | 19.7 | 5969.1 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 4261 |  |  | - |  | Control valves | [8 empty] | AMP CODE: |  | 59
|  | DESCRIPTION : |  | F590Turbine #2 & #3 Control Valves - Cleaned Servovalves
MC1 | 70 | U1 | 2014-04-08 03:53 |  |  |  |  | 2014-04-08 06:50 |  | 0 | 0 | 2.95 | 2.95 | 893.85 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 9270 |  |  | - |  | Wet coal (OMC) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Boiler Trip - Wet Coal Issues
MC1 | 89 | U1 | 2014-04-19 14:45 |  |  |  |  | 2014-04-19 17:39 |  | 0 | 0 | 2.9 | 2.9 | 878.7 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 3662 |  |  | - |  | 4000-7000 volt conductors and buses | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F870B Bus Undervoltage - Blown Fuse
MC1 | 91 | U1 | 2014-04-19 17:49 |  |  |  |  | 2014-04-19 19:43 |  | 0 | 0 | 1.9 | 1.9 | 575.7 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 4309 |  |  | - |  | Other turbine instrument and control problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Turbine Trip - Unknown Reason
MC1 | 102 | U1 | 2014-05-24 22:30 |  |  |  |  | 2014-05-24 23:30 |  | 0 | 0 | 1 | 1 | 303 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 0800 |  |  | - |  | Drums and drum internals (single drum only) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820High Drum Level Trip - Turbine Controls
MC1 | 121 | U1 | 2014-06-29 17:28 |  |  |  |  | 2014-06-29 19:33 |  | 0 | 0 | 2.083 | 2.0833 | 631.25 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 0800 |  |  | - |  | Drums and drum internals (single drum only) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820High Drum Level Trip due to Control Logic Issue
MC1 | 134 | U1 | 2014-07-29 02:10 |  |  |  |  | 2014-07-29 06:13 |  | 0 | 0 | 4.05 | 4.05 | 1227.15 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 4499 |  |  | - |  | Other miscellaneous steam turbine problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Turbine Manual Trip
MC1 | 145 | U1 | 2014-08-17 03:38 |  |  |  |  | 2014-08-17 09:45 |  | 0 | 0 | 6.117 | 6.1167 | 1853.35 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 0800 |  |  | - |  | Drums and drum internals (single drum only) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820High Drum Level Trip - Lost 1D Coal Feeder
MC1 | 29 | U1 | 2015-05-18 |  |  |  |  | 2015-05-23 07:35 |  | 0 | 0 | 127.583 | 127.5833 | 38657.75 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 1488 |  |  | - |  | Air heater (regenerative) | [8 empty] | AMP CODE: |  | 08
|  | DESCRIPTION : |  | F080Air pre-heater baskets
MC1 | 31 | U1 | 2015-05-24 16:31 |  |  |  |  | 2015-05-24 23:31 |  | 0 | 0 | 7 | 7 | 2121 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 4630 |  |  | - |  | Liquid cooling system | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F890Generator Stator manual drain weld
MC1 | 34 | U1 | 2015-05-26 21:22 |  |  |  |  | 2015-05-27 05:04 |  | 0 | 0 | 7.7 | 7.7 | 2333.1 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 4630 |  |  | - |  | Liquid cooling system | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F890Generator stator manual drain weld
MC1 | 53 | U1 | 2015-06-08 02:28 |  |  |  |  | 2015-06-08 03:47 |  | 0 | 0 | 1.317 | 1.3167 | 398.95 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 0800 |  |  | - |  | Drums and drum internals (single drum only) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F660Pressure swing bringing mill online
MC1 | 92 | U1 | 2015-08-15 13:06 |  |  |  |  | 2015-08-15 13:59 |  | 0 | 0 | 0.883 | 0.8833 | 265 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 0800 |  |  | - |  | Drums and drum internals (single drum only) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820High Drum Level Trip
MC1 | 94 | U1 | 2015-08-15 14:35 |  |  |  |  | 2015-08-15 15:13 |  | 0 | 0 | 0.633 | 0.6333 | 190 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 0800 |  |  | - |  | Drums and drum internals (single drum only) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820High Drum Level Trip
MC1 | 95 | SF | 2015-08-15 15:13 |  |  |  |  | 2015-08-15 19:02 |  | 0 | 0 | 3.817 | 3.8167 | 1145 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 3644 |  |  | - |  | AC Protection devices | [8 empty] | AMP CODE: |  | 40
|  | DESCRIPTION : |  | F400Generator Lockout - Protective Relays
MC1 | 97 | U1 | 2015-08-18 06:30 |  |  |  |  | 2015-08-18 08:11 |  | 0 | 0 | 1.683 | 1.6833 | 505 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 0800 |  |  | - |  | Drums and drum internals (single drum only) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820High Drum Level Trip
MC1 | 114 | U1 | 2015-10-12 17:43 |  |  |  |  | 2015-10-14 19:35 |  | 0 | 0 | 49.867 | 49.8667 | 14960 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 4750 |  |  | - |  | Other generator controls and metering problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F490Generator Lockout
MC1 | 134 | U1 | 2015-12-29 02:21 |  |  |  |  | 2015-12-29 06:18 |  | 0 | 0 | 3.95 | 3.95 | 1185 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 0800 |  |  | - |  | Drums and drum internals (single drum only) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Drum level trip
MC1 | 35 | U1 | 2016-03-29 11:31 |  |  |  |  | 2016-03-29 13:07 |  | 0 | 0 | 1.6 | 1.6 | 480 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 0800 |  |  | - |  | Drums and drum internals (single drum only) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Drum level trip
MC1 | 55 | SF | 2016-05-15 20:30 |  |  |  |  | 2016-05-17 20:06 |  | 0 | 0 | 47.6 | 47.6 | 14280 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 4263 |  |  | - |  | Reheat stop valves | [8 empty] | AMP CODE: |  | 72
|  | DESCRIPTION : |  | F720RH Valve would not open
MC1 | 90 | U1 | 2016-10-06 15:26 |  |  |  |  | 2016-10-07 07:13 |  | 0 | 0 | 15.783 | 15.7833 | 4735 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 3110 |  |  | - |  | Condenser tube leaks | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F540Condenser Tube Leak
MC1 | 7 | U1 | 2017-01-11 09:20 |  |  |  |  | 2017-01-13 20:07 |  | 0 | 0 | 58.783 | 58.7833 | 17635 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 1160 |  |  | - |  | First reheater | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | FS00Deslag
MC1 | 24 | U1 | 2017-02-27 16:15 |  |  |  |  | 2017-02-27 21:38 |  | 0 | 0 | 5.383 | 5.3833 | 1615 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 1455 |  |  | - |  | Induced draft fans | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820ID Fan Index Trip
MC1 | 35 | U1 | 2017-05-01 07:41 |  |  |  |  | 2017-05-01 10:59 |  | 0 | 0 | 3.3 | 3.3 | 990 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 0800 |  |  | - |  | Drums and drum internals (single drum only) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Drum Level Trip
MC1 | 38 | U1 | 2017-05-05 10:45 |  |  |  |  | 2017-05-05 11:57 |  | 0 | 0 | 1.2 | 1.2 | 360 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 0770 |  |  | - |  | Other boiler recirculation problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F420'Loss of BCP's (Breaker Switching Error)
MC1 | 66 | U1 | 2017-09-02 00:23 |  |  |  |  | 2017-09-02 02:16 |  | 0 | 0 | 1.883 | 1.8833 | 565 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 4460 |  |  | - |  | Turbine overspeed trip test | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Weekly Mechanical Over Speed Trip Test Malfunction
MC1 | 11 | U1 | 2018-03-26 12:53 |  |  |  |  | 2018-03-26 17:48 |  | 0 | 0 | 4.917 | 4.9167 | 1475 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 3344 |  |  | - |  | Deaerator (including level control) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Deaerator Door Leak
MC1 | 26 | U1 | 2018-06-11 19:07 |  |  |  |  | 2018-06-11 22:31 |  | 0 | 0 | 3.4 | 3.4 | 1020 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 0800 |  |  | - |  | Drums and drum internals (single drum only) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F8201A ID Fan Index Trip / Drum Level
MC1 | 3 | U1 | 2019-01-14 11:01 |  |  |  |  | 2019-01-18 15:38 |  | 0 | 0 | 100.617 | 100.6167 | 30185 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 0540 |  |  | - |  | Hot reheat steam piping up to turbine stop valves | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F540Hot Reheat Steam Line Leak
MC1 | 9 | U1 | 2019-05-06 18:00 |  |  |  |  | 2019-05-08 08:55 |  | 0 | 0 | 38.917 | 38.9167 | 11675 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 4640 |  |  | - |  | Seal oil system and seals | [8 empty] | AMP CODE: |  | 70
|  | DESCRIPTION : |  | F830Emergency Seal Oil Pump
MC1 | 10 | U1 | 2019-05-08 10:01 |  |  |  |  | 2019-05-08 10:33 |  | 0 | 0 | 0.533 | 0.5333 | 160 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 9900 |  |  | - |  | Operator error | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Drum Level Trip
MC1 | 12 | U1 | 2019-05-10 08:36 |  |  |  |  | 2019-05-10 18:36 |  | 0 | 0 | 10 | 10 | 3000 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 4420 |  |  | - |  | Vibration of the turbine generator unit that cannot be attributed to a specific cause such as bearings or blades (use this code for balance moves) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F830High Turbine Vibration
MC1 | 13 | U1 | 2019-05-16 01:28 |  |  |  |  | 2019-05-16 02:15 |  | 0 | 0 | 0.783 | 0.7833 | 235 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 4299 |  |  | - |  | Other hydraulic system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820EHC Pump Trip
MC1 | 49 | U1 | 2019-09-19 17:09 |  |  |  |  | 2019-09-20 14:04 |  | 0 | 0 | 20.917 | 20.9167 | 6275 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 3110 |  |  | - |  | Condenser tube leaks | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Condenser Tube Leaks
MC1 | 70 | U1 | 2019-12-28 13:34 |  |  |  |  | 2019-12-28 18:00 |  | 0 | 0 | 4.433 | 4.4333 | 1330 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 3273 |  |  | - |  | "Debris in circulating water from outside sources (leaves, mud, etc.)" | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Backpressure
MC1 | 7 | U1 | 2020-01-25 19:58 |  |  |  |  | 2020-01-26 02:52 |  | 0 | 0 | 6.9 | 6.9 | 2070 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 4270 |  |  | - |  | Crossover or under piping | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Crossover Steam Leak
MC1 | 16 | U1 | 2020-03-17 02:21 |  |  |  |  | 2020-03-17 16:29 |  | 0 | 0 | 14.133 | 14.1333 | 4240 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 0741 |  |  | - |  | Boiler recirculation pumps - motors | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F8201B/1C BCPs Unavailable
MC1 | 28 | U1 | 2020-04-22 07:06 |  |  |  |  | 2020-04-22 12:56 |  | 0 | 0 | 5.833 | 5.8333 | 1750 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 1475 |  |  | - |  | Induced draft fan controls | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820ID Fan Run-Back - Battery Pulled
MC1 | 29 | U1 | 2020-05-07 09:50 |  |  |  |  | 2020-05-07 11:36 |  | 0 | 0 | 1.767 | 1.7667 | 530 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 0370 |  |  | - |  | Burner instruments and controls (except light off) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Burner Management System - Battery Pulled
MC1 | 37 | U1 | 2020-07-09 07:28 |  |  |  |  | 2020-07-10 23:05 |  | 0 | 0 | 39.617 | 39.6167 | 11885 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 0782 |  |  | - |  | Headers and caps | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Tube Leak - Economizer
MC1 | 43 | U1 | 2020-08-09 05:47 |  |  |  |  | 2020-08-09 09:04 |  | 0 | 0 | 3.283 | 3.2833 | 985 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 3972 |  |  | - |  | DCS - hardware problems (including card failure) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820DCS Card Malfunction
MC1 | 48 | U1 | 2020-09-16 01:39 |  |  |  |  | 2020-09-16 02:34 |  | 0 | 0 | 0.917 | 0.9167 | 275 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 3972 |  |  | - |  | DCS - hardware problems (including card failure) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820DCS Card Malfunction - Generator Lockout
MC1 | 49 | U1 | 2020-09-17 00:12 |  |  |  |  | 2020-09-17 01:26 |  | 0 | 0 | 1.233 | 1.2333 | 370 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 3972 |  |  | - |  | DCS - hardware problems (including card failure) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820DCS Card Malfunction - Sudden Load Rejection
MC1 | 65 | U1 | 2020-10-24 04:48 |  |  |  |  | 2020-10-24 05:36 |  | 0 | 0 | 0.8 | 0.8 | 240 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 0740 |  |  | - |  | Boiler recirculation pumps | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820BCP Differential
MC1 | 68 | U1 | 2020-12-01 06:53 |  |  |  |  | 2020-12-01 22:24 |  | 0 | 0 | 15.517 | 15.5167 | 4655 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 0740 |  |  | - |  | Boiler recirculation pumps | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F8201A BCP Trip
MC1 | 11 | U1 | 2021-02-10 18:21 |  |  |  |  | 2021-02-10 23:22 |  | 0 | 0 | 5.017 | 5.0167 | 1505 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 0800 |  |  | - |  | Drums and drum internals (single drum only) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Drum Level Trip
MC1 | 25 | U1 | 2021-04-02 23:50 |  |  |  |  | 2021-04-03 01:18 |  | 0 | 0 | 1.467 | 1.4667 | 440 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 4261 |  |  | - |  | Control valves | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820#2 Control Valve False Indication
MC1 | 28 | U1 | 2021-04-04 01:59 |  |  |  |  | 2021-04-04 03:01 |  | 0 | 0 | 1.033 | 1.0333 | 310 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 0800 |  |  | - |  | Drums and drum internals (single drum only) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Drum Level Trip
MC1 | 29 | U1 | 2021-04-04 04:51 |  |  |  |  | 2021-04-05 11:49 |  | 0 | 0 | 30.967 | 30.9667 | 9290 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 4640 |  |  | - |  | Seal oil system and seals | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Main Seal Oil Pump Trip
MC1 | 44 | U1 | 2021-07-15 13:14 |  |  |  |  | 2021-07-16 01:44 |  | 0 | 0 | 12.5 | 12.5 | 3750 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 9720 |  |  | - |  | Other safety problems | [8 empty] | AMP CODE:
|  | DESCRIPTION : |  | F830Station Service Water Out of Service
MC1 | 81 | U1 | 2021-11-17 21:20 |  |  |  |  | 2021-11-20 02:24 |  | 0 | 0 | 53.067 | 53.0667 | 15920 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 1080 |  |  | - |  | Economizer | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Economizer Tube Leak
MC1 | 2 | SF | 2022-01-03 14:30 |  |  |  |  | 2022-01-03 18:58 |  | 0 | 0 | 4.467 | 4.4667 | 1340 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 4499 |  |  | - |  | Other miscellaneous steam turbine problems | [8 empty] | AMP CODE: |  | 78
|  | DESCRIPTION : |  | F780Reserve Shutdown - 16hr Limit - Startup Failure
MC1 | 37 | U1 | 2022-06-02 15:49 |  |  |  |  | 2022-06-02 19:01 |  | 0 | 0 | 3.2 | 3.2 | 960 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 4264 |  |  | - |  | Combined intercept valves | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F540Left Intercept RH Stop Valve - EHC Leak
MC1 | 39 | U1 | 2022-06-22 15:40 |  |  |  |  | 2022-06-22 16:56 |  | 0 | 0 | 1.267 | 1.2667 | 380 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 1455 |  |  | - |  | Induced draft fans | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Loss of ID/FD Fans
MC1 | 43 | SF | 2022-10-07 09:15 |  |  |  |  | 2022-10-08 20:40 |  | 0 | 0 | 35.417 | 35.4167 | 10625 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 4280 |  |  | - |  | Lube oil pumps | [8 empty] | AMP CODE: |  | 06
|  | DESCRIPTION : |  | F060Lube Oil Pump Failure
MC1 | 7 | U1 | 2023-01-23 06:18 |  |  |  |  | 2023-01-23 08:34 |  | 0 | 0 | 2.267 | 2.2667 | 680 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 1750 |  |  | - |  | Burner management system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Boiler Controls Issue
MC1 | 16 | U1 | 2023-02-22 10:28 |  |  |  |  | 2023-02-22 12:20 |  | 0 | 0 | 1.867 | 1.8667 | 560 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 3210 |  |  | - |  | Circulating water pumps | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F8201A Circulating Water Pump
Mill Creek - MC2
Unit | Event | Type | Start |  |  |  |  | End |  | GAC | NAC | Duration | Equiv Hrs | Equiv MWH | Cont | Work Start | Work End |  | Hours |  |  | Gross Capacity Impact (MW)
MC2 | 24 | U1 | 2014-01-25 22:11 |  |  |  |  | 2014-01-26 12:32 |  | 0 | 0 | 14.35 | 14.35 | 4290.65 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 4267 |  |  | - |  | Control valve testing | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Turbine Control Valve Test - Trip
MC2 | 35 | U1 | 2014-02-01 23:37 |  |  |  |  | 2014-02-02 06:35 |  | 0 | 0 | 6.967 | 6.9667 | 2083.034 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 3149 |  |  | - |  | "Loss of vacuum not attributable to a particular component such as air ejectors or valves, or high back pressure not attributable to high circulating water temperature, or vacuum losses from a known cause." | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Condenser Vacuum Trip
MC2 | 58 | SF | 2014-02-17 22:00 |  |  |  |  | 2014-02-18 13:40 |  | 0 | 0 | 15.667 | 15.6667 | 4684.333 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 0380 |  |  | - |  | Light off (igniter) systems (including fuel supply) | [8 empty] | AMP CODE: |  | 40
|  | DESCRIPTION : |  | F400Gas Igniter Issues
MC2 | 183 | U1 | 2014-11-30 20:54 |  |  |  |  | 2014-12-01 12:58 |  | 0 | 0 | 16.067 | 16.0667 | 4803.933 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 3110 |  |  | - |  | Condenser tube leaks | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F540Condenser Tube Leak
MC2 | 185 | SF | 2014-12-04 22:21 |  |  |  |  | 2014-12-05 12:06 |  | 0 | 0 | 13.75 | 13.75 | 4111.25 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 3619 |  |  | - |  | Other switchyard equipment - external (OMC) | [8 empty] | AMP CODE: |  | 40
|  | DESCRIPTION : |  | F400Relay & Switchyard Issues - Problem Synchronizing
MC2 | 187 | U1 | 2014-12-05 15:19 |  |  |  |  | 2014-12-07 16:26 |  | 0 | 0 | 49.117 | 49.1167 | 14685.883 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 3110 |  |  | - |  | Condenser tube leaks | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F540Condenser Tube Leak
MC2 | 203 | SF | 2014-12-22 22:26 |  |  |  |  | 2015-01-01 |  | 0 | 0 | 217.567 | 217.5667 | 65052.433 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 3620 |  |  | - |  | Main transformer | [8 empty] | AMP CODE: |  | 70
|  | DESCRIPTION : |  | F700Main Transformer A Phase
MC2 | 1 | SF | 2015-01-01 |  |  |  |  | 2015-01-05 19:15 |  | 0 | 0 | 115.25 | 115.25 | 34459.75 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 3620 |  |  | - |  | Main transformer | [8 empty] | AMP CODE: |  | 70
|  | DESCRIPTION : |  | F700Main Transformer Replacement
MC2 | 3 | U1 | 2015-01-05 20:57 |  |  |  |  | 2015-01-06 08:19 |  | 0 | 0 | 11.367 | 11.3667 | 3398.633 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 4700 |  |  | - |  | Generator voltage control | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F400Generator Field - Voltage Regulator Issues
MC2 | 33 | U1 | 2015-05-05 19:47 |  |  |  |  | 2015-05-09 09:32 |  | 0 | 0 | 85.75 | 85.75 | 25810.75 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 3620 |  |  | - |  | Main transformer | [8 empty] | AMP CODE: |  | 59
|  | DESCRIPTION : |  | F5902 B phase Main Transformer - Filter and clean the oil
MC2 | 119 | U1 | 2015-12-18 09:27 |  |  |  |  | 2015-12-18 12:16 |  | 0 | 0 | 2.817 | 2.8167 | 830.917 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 0770 |  |  | - |  | Other boiler recirculation problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F6402B boiler circ. pump lube oil pump motor overloads
MC2 | 124 | SF | 2015-12-23 16:53 |  |  |  |  | 2015-12-24 09:46 |  | 0 | 0 | 16.883 | 16.8833 | 4980.584 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 1455 |  |  | - |  | Induced draft fans | [8 empty] | AMP CODE: |  | 06
|  | DESCRIPTION : |  | F060Loss of ID Fan Alarm - Blown Fuse in HPM
MC2 | 65 | U1 | 2016-10-22 10:51 |  |  |  |  | 2016-10-23 10:45 |  | 0 | 0 | 23.9 | 23.9 | 7074.4 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 3220 |  |  | - |  | Circulating water piping | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F540Cooling Tower Header Rupture
MC2 | 18 | U1 | 2017-04-29 07:44 |  |  |  |  | 2017-04-29 12:29 |  | 0 | 0 | 4.75 | 4.75 | 1406 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 0800 |  |  | - |  | Drums and drum internals (single drum only) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Drum Level Trip
MC2 | 50 | U1 | 2017-07-24 07:52 |  |  |  |  | 2017-07-24 09:07 |  | 0 | 0 | 1.25 | 1.25 | 371.25 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 9930 |  |  | - |  | Operating procedure error | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Tripped - Steam/Feedwater Flow
MC2 | 72 | U1 | 2017-08-29 04:02 |  |  |  |  | 2017-08-29 04:59 |  | 0 | 0 | 0.95 | 0.95 | 282.15 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 0250 |  |  | - |  | Pulverizer feeders | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Loss of Flame - Debris in Coal Feeder
MC2 | 7 | U1 | 2018-02-19 10:23 |  |  |  |  | 2018-02-20 15:03 |  | 0 | 0 | 28.667 | 28.6667 | 8456.667 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 3211 |  |  | - |  | Circulating water pump motors | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F8204KV Under Voltage - Lost Both Cooling Tower Pumps (Electrical)
MC2 | 22 | U1 | 2018-05-27 06:28 |  |  |  |  | 2018-05-27 16:13 |  | 0 | 0 | 9.75 | 9.75 | 2886 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 4302 |  |  | - |  | Turbine trip devices (including instruments) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Turbine Master Trip
MC2 | 23 | U1 | 2018-06-15 00:48 |  |  |  |  | 2018-06-15 02:36 |  | 0 | 0 | 1.8 | 1.8 | 534.6 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 1799 |  |  | - |  | Other boiler instrumentation and control problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Master Fuel Trip - Under Investigation
MC2 | 77 | SF | 2018-12-03 01:00 |  |  |  |  | 2018-12-04 02:27 |  | 0 | 0 | 25.45 | 25.45 | 7507.75 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 1475 |  |  | - |  | Induced draft fan controls | [8 empty] | AMP CODE: |  | 19
|  | DESCRIPTION : |  | F5702A ID Fan VFD Fault
MC2 | 11 | U1 | 2019-02-13 04:46 |  |  |  |  | 2019-02-13 06:34 |  | 0 | 0 | 1.8 | 1.8 | 531 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 9270 |  |  | - |  | Wet coal (OMC) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Boiler Trip - Wet Coal
MC2 | 28 | U1 | 2019-04-20 17:42 |  |  |  |  | 2019-04-20 22:00 |  | 0 | 0 | 4.3 | 4.3 | 1272.8 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 3650 |  |  | - |  | DC instrument power battery chargers | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Loss of DC Battery Systems
MC2 | 29 | U1 | 2019-04-20 22:28 |  |  |  |  | 2019-04-20 23:58 |  | 0 | 0 | 1.5 | 1.5 | 444 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 1455 |  |  | - |  | Induced draft fans | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820ID Fan Index Trip
MC2 | 56 | U1 | 2019-09-08 17:15 |  |  |  |  | 2019-09-10 12:34 |  | 0 | 0 | 43.317 | 43.3167 | 12821.733 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 1030 |  |  | - |  | "Boiler screen, wing wall, or slag screen (water tubes only)" | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Boiler Tube Leak - Waterwall
MC2 | 62 | U1 | 2019-10-19 03:16 |  |  |  |  | 2019-10-19 05:34 |  | 0 | 0 | 2.3 | 2.3 | 680.8 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 4260 |  |  | - |  | Main stop valves | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F540Main Stop Valve - EHC Leak
MC2 | 78 | U1 | 2019-12-18 21:54 |  |  |  |  | 2019-12-21 05:06 |  | 0 | 0 | 55.2 | 55.2 | 16284 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 1000 |  |  | - |  | Waterwall (Furnace wall) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Boiler Tube Leak - Waterwall
MC2 | 40 | U1 | 2020-11-05 19:02 |  |  |  |  | 2020-11-06 07:08 |  | 0 | 0 | 12.1 | 12.1 | 3581.6 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 4299 |  |  | - |  | Other hydraulic system problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830EHC Leak - CV#1
MC2 | 41 | U1 | 2020-11-17 08:04 |  |  |  |  | 2020-11-17 09:18 |  | 0 | 0 | 1.233 | 1.2333 | 365.067 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 1470 |  |  | - |  | Induced draft fan motors and drives | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820ID Fan - Vibration Interface Card
MC2 | 8 | U1 | 2021-01-25 21:03 |  |  |  |  | 2021-01-25 21:34 |  | 0 | 0 | 0.517 | 0.5167 | 153.45 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 9271 |  |  | - |  | Wet coal (not OMC) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Feeder Pluggage - Wet Coal
MC2 | 23 | U1 | 2021-04-23 19:12 |  |  |  |  | 2021-04-25 09:39 |  | 0 | 0 | 38.45 | 38.45 | 11419.65 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 4240 |  |  | - |  | Bearings | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820High Turbine Vibration
MC2 | 25 | U1 | 2021-04-25 10:18 |  |  |  |  | 2021-04-25 16:59 |  | 0 | 0 | 6.683 | 6.6833 | 1984.95 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 4240 |  |  | - |  | Bearings | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820High Turbine Vibration
MC2 | 44 | U1 | 2021-06-18 05:48 |  |  |  |  | 2021-06-18 07:56 |  | 0 | 0 | 2.133 | 2.1333 | 633.6 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 0250 |  |  | - |  | Pulverizer feeders | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F8202B Feeder Trip
MC2 | 56 | U1 | 2021-07-15 13:14 |  |  |  |  | 2021-07-16 02:36 |  | 0 | 0 | 13.367 | 13.3667 | 3969.9 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 9720 |  |  | - |  | Other safety problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Station Service Water Out of Service
MC2 | 2 | U1 | 2022-01-03 07:38 |  |  |  |  | 2022-01-03 09:41 |  | 0 | 0 | 2.05 | 2.05 | 608.85 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 1530 |  |  | - |  | Other flue gas problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820ID Fan Index Trip - Wet Coal
MC2 | 7 | U1 | 2022-01-10 08:19 |  |  |  |  | 2022-01-10 09:25 |  | 0 | 0 | 1.1 | 1.1 | 326.7 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 0250 |  |  | - |  | Pulverizer feeders | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Feeders Plugged - Wet Coal
MC2 | 23 | U1 | 2022-02-19 13:52 |  |  |  |  | 2022-02-26 14:35 |  | 0 | 0 | 168.717 | 168.7167 | 50108.85 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 3999 |  |  | - |  | Other miscellaneous balance of plant problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Various Control System Issues
MC2 | 24 | SF | 2022-02-26 14:35 |  |  |  |  | 2022-02-27 21:39 |  | 0 | 0 | 31.067 | 31.0667 | 9226.8 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 0710 |  |  | - |  | Blowdown system piping | [8 empty] | AMP CODE: |  | 54
|  | DESCRIPTION : |  | F540Startup Failure - Continuous Blowdown Line Repair
MC2 | 52 | SF | 2022-05-27 05:49 |  |  |  |  | 2022-06-05 03:30 |  | 0 | 0 | 213.683 | 213.6833 | 63463.95 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 3235 |  |  | - |  | Cooling tower booster pump | [8 empty] | AMP CODE: |  | 06
|  | DESCRIPTION : |  | F0602A/2B Cooling Tower Pumps Unavailable
MC2 | 68 | U1 | 2022-08-02 21:41 |  |  |  |  | 2022-08-03 10:38 |  | 0 | 0 | 12.95 | 12.95 | 3846.15 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 1799 |  |  | - |  | Other boiler instrumentation and control problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Boiler Control Board Trip
MC2 | 69 | U1 | 2022-08-05 03:16 |  |  |  |  | 2022-08-05 05:17 |  | 0 | 0 | 2.017 | 2.0167 | 598.95 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 1710 |  |  | - |  | "Combustion/steam condition controls (report local controls - burners, pulverizers, etc., - with component or system)" | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Boiler Air Flow Transmitter Inaccurate
MC2 | 70 | U1 | 2022-08-05 06:10 |  |  |  |  | 2022-08-05 08:15 |  | 0 | 0 | 2.083 | 2.0833 | 618.75 | 1 |  |  |  | 0 |  |  | 330
|  | CAUSE CODE : |  | 0800 |  |  | - |  | Drums and drum internals (single drum only) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Drum Level
Mill Creek - MC3
Unit | Event | Type | Start |  |  |  |  | End |  | GAC | NAC | Duration | Equiv Hrs | Equiv MWH | Cont | Work Start | Work End |  | Hours |  |  | Gross Capacity Impact (MW)
MC3 | 78 | U1 | 2014-05-03 02:37 |  |  |  |  | 2014-05-03 08:04 |  | 0 | 0 | 5.45 | 5.45 | 2130.95 | 1 |  |  |  | 0 |  |  | 422.5
|  | CAUSE CODE : |  | 1710 |  |  | - |  | "Combustion/steam condition controls (report local controls - burners, pulverizers, etc., - with component or system)" | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F420High Furnace Pressure Trip - Operator Error
MC3 | 92 | U1 | 2014-05-20 05:32 |  |  |  |  | 2014-05-23 18:02 |  | 0 | 0 | 84.5 | 84.5 | 33039.5 | 1 |  |  |  | 0 |  |  | 422.5
|  | CAUSE CODE : |  | 1080 |  |  | - |  | Economizer | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F540Boiler Tube Leak - Economizer Inlet
MC3 | 96 | U1 | 2014-06-05 18:39 |  |  |  |  | 2014-06-09 02:50 |  | 0 | 0 | 80.183 | 80.1833 | 31351.683 | 1 |  |  |  | 0 |  |  | 422
|  | CAUSE CODE : |  | 1080 |  |  | - |  | Economizer | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F540Boiler Tube Leak - Economizer
MC3 | 97 | U1 | 2014-06-09 02:51 |  |  |  |  | 2014-06-09 07:03 |  | 0 | 0 | 4.2 | 4.2 | 1642.2 | 1 |  |  |  | 0 |  |  | 422
|  | CAUSE CODE : |  | 4302 |  |  | - |  | Turbine trip devices (including instruments) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F400Unit Trip - 2% Load Set Timer Issues
MC3 | 99 | U1 | 2014-07-02 18:54 |  |  |  |  | 2014-07-03 08:30 |  | 0 | 0 | 13.6 | 13.6 | 5317.6 | 1 |  |  |  | 0 |  |  | 422
|  | CAUSE CODE : |  | 1799 |  |  | - |  | Other boiler instrumentation and control problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Master Fuel Trip
MC3 | 100 | U1 | 2014-07-03 16:04 |  |  |  |  | 2014-07-03 19:02 |  | 0 | 0 | 2.967 | 2.9667 | 1159.967 | 1 |  |  |  | 0 |  |  | 422
|  | CAUSE CODE : |  | 3431 |  |  | - |  | Other feedwater valves | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F690Low Drum Level - TDBFP Recirc Valve Issues
MC3 | 121 | U1 | 2014-08-14 23:41 |  |  |  |  | 2014-08-15 01:25 |  | 0 | 0 | 1.733 | 1.7333 | 677.734 | 1 |  |  |  | 0 |  |  | 422
|  | CAUSE CODE : |  | 1400 |  |  | - |  | Forced draft fans | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820High Furnace Vacuum Trip - 3B Forced Draft Fan Inlet Damper Stuck
MC3 | 146 | SF | 2014-10-12 09:07 |  |  |  |  | 2014-10-12 10:10 |  | 0 | 0 | 1.05 | 1.05 | 413.7 | 1 |  |  |  | 0 |  |  | 422.5
|  | CAUSE CODE : |  | 4309 |  |  | - |  | Other turbine instrument and control problems | [8 empty] | AMP CODE: |  | 40
|  | DESCRIPTION : |  | F820Turbine Master Trip
MC3 | 57 | U1 | 2015-05-31 15:57 |  |  |  |  | 2015-06-01 09:18 |  | 0 | 0 | 17.35 | 17.35 | 6783.85 | 1 |  |  |  | 0 |  |  | 422.5
|  | CAUSE CODE : |  | 3661 |  |  | - |  | 4000-7000 volt circuit breakers | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | FR003A-2 Main Aux. breaker fire
MC3 | 59 | U1 | 2015-06-01 09:19 |  |  |  |  | 2015-06-01 10:22 |  | 0 | 0 | 1.05 | 1.05 | 410.55 | 1 |  |  |  | 0 |  |  | 422
|  | CAUSE CODE : |  | 4740 |  |  | - |  | Emergency generator trip devices | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F420Sequential trip
MC3 | 70 | U1 | 2015-06-22 12:05 |  |  |  |  | 2015-06-22 14:32 |  | 0 | 0 | 2.45 | 2.45 | 957.95 | 1 |  |  |  | 0 |  |  | 422
|  | CAUSE CODE : |  | 3220 |  |  | - |  | Circulating water piping | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Cooling tower pump trip
MC3 | 103 | U1 | 2015-08-31 04:23 |  |  |  |  | 2015-08-31 05:46 |  | 0 | 0 | 1.383 | 1.3833 | 540.883 | 1 |  |  |  | 0 |  |  | 422
|  | CAUSE CODE : |  | 3412 |  |  | - |  | Feedwater pump drive - steam turbine | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Boiler Feed Pump Turbine Driven - Tripped, HMI Failure
MC3 | 117 | U1 | 2015-10-18 15:09 |  |  |  |  | 2015-10-18 17:58 |  | 0 | 0 | 2.817 | 2.8167 | 1109.767 | 1 |  |  |  | 0 |  |  | 422.5
|  | CAUSE CODE : |  | 3412 |  |  | - |  | Feedwater pump drive - steam turbine | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Turbine Driven Boiler Feed Pump - Trip, Unexpected Reboot
MC3 | 126 | U1 | 2015-11-20 17:33 |  |  |  |  | 2015-11-23 06:40 |  | 0 | 0 | 61.117 | 61.1167 | 24079.967 | 1 |  |  |  | 0 |  |  | 422.5
|  | CAUSE CODE : |  | 1080 |  |  | - |  | Economizer | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F540Boiler tube leak - economizer
MC3 | 30 | U1 | 2016-03-15 18:07 |  |  |  |  | 2016-03-25 02:11 |  | 0 | 0 | 224.067 | 224.0667 | 88058.2 | 1 |  |  |  | 0 |  |  | 422.5
|  | CAUSE CODE : |  | 3620 |  |  | - |  | Main transformer | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | FR00"A" Phase main transformer fire
MC3 | 50 | SF | 2016-06-03 20:08 |  |  |  |  | 2016-06-04 16:04 |  | 0 | 0 | 19.933 | 19.9333 | 7793.934 | 1 |  |  |  | 0 |  |  | 422
|  | CAUSE CODE : |  | 1475 |  |  | - |  | Induced draft fan controls | [8 empty] | AMP CODE: |  | 43
|  | DESCRIPTION : |  | F430Relay on breaker took out ID fans
MC3 | 51 | U1 | 2016-06-06 11:30 |  |  |  |  | 2016-06-06 12:44 |  | 0 | 0 | 1.233 | 1.2333 | 482.233 | 1 |  |  |  | 0 |  |  | 422
|  | CAUSE CODE : |  | 1475 |  |  | - |  | Induced draft fan controls | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F660ID Fan Index Trip
MC3 | 55 | U1 | 2016-06-25 14:58 |  |  |  |  | 2016-06-25 20:55 |  | 0 | 0 | 5.95 | 5.95 | 2326.45 | 1 |  |  |  | 0 |  |  | 422
|  | CAUSE CODE : |  | 1470 |  |  | - |  | Induced draft fan motors and drives | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F8503A ID Fan trip - high vibration
MC3 | 69 | U1 | 2016-07-15 02:40 |  |  |  |  | 2016-07-15 06:07 |  | 0 | 0 | 3.45 | 3.45 | 1348.95 | 1 |  |  |  | 0 |  |  | 422
|  | CAUSE CODE : |  | 9900 |  |  | - |  | Operator error | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | FP00Furnace Pressure Trip
MC3 | 75 | U1 | 2016-08-04 12:18 |  |  |  |  | 2016-08-05 02:56 |  | 0 | 0 | 14.633 | 14.6333 | 5721.633 | 1 |  |  |  | 0 |  |  | 422
|  | CAUSE CODE : |  | 8656 |  |  | - |  | Controls and instrumentation | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F410'Loss of UPS & Fire on 3A oxidation air compressor
MC3 | 94 | U1 | 2016-10-30 16:22 |  |  |  |  | 2016-10-30 23:30 |  | 0 | 0 | 7.133 | 7.1333 | 2803.4 | 1 |  |  |  | 0 |  |  | 422.5
|  | CAUSE CODE : |  | 1480 |  |  | - |  | Other induced draft fan problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F1903A ID Fan Coolant
MC3 | 98 | U1 | 2016-11-14 08:45 |  |  |  |  | 2016-11-14 11:07 |  | 0 | 0 | 2.367 | 2.3667 | 930.1 | 1 |  |  |  | 0 |  |  | 422.5
|  | CAUSE CODE : |  | 9300 |  |  | - |  | "Transmission system problems other than catastrophes (do not include switchyard problems in this category; see codes 3600 to 3629, 3720 to 3730)" | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Power Circuit Breaker Trip
MC3 | 103 | U1 | 2016-12-18 18:40 |  |  |  |  | 2016-12-18 21:19 |  | 0 | 0 | 2.65 | 2.65 | 1044.1 | 1 |  |  |  | 0 |  |  | 423
|  | CAUSE CODE : |  | 3416 |  |  | - |  | Other feedwater pump problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Feedwater Flow (Tripped during TDBFP Testing)
MC3 | 7 | U1 | 2017-02-26 22:49 |  |  |  |  | 2017-02-27 03:01 |  | 0 | 0 | 4.2 | 4.2 | 1654.8 | 1 |  |  |  | 0 |  |  | 423
|  | CAUSE CODE : |  | 0370 |  |  | - |  | Burner instruments and controls (except light off) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Master Fuel Trip (Lost Flame Scanner)
MC3 | 26 | U1 | 2017-05-20 01:17 |  |  |  |  | 2017-05-20 16:41 |  | 0 | 0 | 15.4 | 15.4 | 6052.2 | 1 |  |  |  | 0 |  |  | 422.5
|  | CAUSE CODE : |  | 0520 |  |  | - |  | Other main steam valves (including vent and drain valves but not including the turbine stop valves) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Main Steam Non-Return Valve Packing Leak
MC3 | 28 | U1 | 2017-05-25 06:02 |  |  |  |  | 2017-05-25 07:15 |  | 0 | 0 | 1.217 | 1.2167 | 478.15 | 1 |  |  |  | 0 |  |  | 422.5
|  | CAUSE CODE : |  | 0800 |  |  | - |  | Drums and drum internals (single drum only) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820High Drum Level (Lost B Mill)
MC3 | 29 | U1 | 2017-06-08 09:09 |  |  |  |  | 2017-06-08 12:53 |  | 0 | 0 | 3.733 | 3.7333 | 1459.733 | 1 |  |  |  | 0 |  |  | 422
|  | CAUSE CODE : |  | 1475 |  |  | - |  | Induced draft fan controls | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820ID Fan Trip
MC3 | 86 | U1 | 2017-11-25 02:32 |  |  |  |  | 2017-11-25 16:52 |  | 0 | 0 | 14.333 | 14.3333 | 5633 | 1 |  |  |  | 0 |  |  | 422.5
|  | CAUSE CODE : |  | 0110 |  |  | - |  | Other coal fuel supply problems up through bunkers | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F490Coal Supply To Bunker Issues - Conveyor
MC3 | 20 | U1 | 2018-02-19 22:37 |  |  |  |  | 2018-02-22 09:16 |  | 0 | 0 | 58.65 | 58.65 | 23108.1 | 1 |  |  |  | 0 |  |  | 423
|  | CAUSE CODE : |  | 1050 |  |  | - |  | Second superheater | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Boiler Tube Leak - Secondary Superheat
MC3 | 63 | U1 | 2018-08-13 07:07 |  |  |  |  | 2018-08-13 09:13 |  | 0 | 0 | 2.1 | 2.1 | 821.1 | 1 |  |  |  | 0 |  |  | 422
|  | CAUSE CODE : |  | 1480 |  |  | - |  | Other induced draft fan problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F8203B ID Fan Trip - Coolant Level
MC3 | 89 | U1 | 2018-12-20 20:37 |  |  |  |  | 2018-12-20 20:52 |  | 0 | 0 | 0.25 | 0.25 | 98.5 | 1 |  |  |  | 0 |  |  | 423
|  | CAUSE CODE : |  | 0359 |  |  | - |  | Gas burner piping and valves | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Gas Valve Trip - MFT
MC3 | 19 | U1 | 2019-02-18 13:04 |  |  |  |  | 2019-02-18 23:18 |  | 0 | 0 | 10.233 | 10.2333 | 4031.933 | 1 |  |  |  | 0 |  |  | 423
|  | CAUSE CODE : |  | 4630 |  |  | - |  | Liquid cooling system | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Rectifier Cooling Water Leak
MC3 | 32 | U1 | 2019-04-20 12:39 |  |  |  |  | 2019-04-24 20:30 |  | 0 | 0 | 103.85 | 103.85 | 40813.05 | 1 |  |  |  | 0 |  |  | 422.5
|  | CAUSE CODE : |  | 3129 |  |  | - |  | Other condenser casing or shell and internal problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Condenser Waterbox Leaks
MC3 | 33 | U1 | 2019-04-25 15:01 |  |  |  |  | 2019-04-27 18:16 |  | 0 | 0 | 51.25 | 51.25 | 20141.25 | 1 |  |  |  | 0 |  |  | 422.5
|  | CAUSE CODE : |  | 1050 |  |  | - |  | Second superheater | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Boiler Tube Leak - Secondary Superheater
MC3 | 57 | U1 | 2019-09-19 17:07 |  |  |  |  | 2019-09-19 23:19 |  | 0 | 0 | 6.2 | 6.2 | 2436.6 | 1 |  |  |  | 0 |  |  | 422.5
|  | CAUSE CODE : |  | 1471 |  |  | - |  | Induced draft fan motors - variable speed | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F8203A ID Fan - VFD Fault
MC3 | 63 | U1 | 2019-12-06 20:17 |  |  |  |  | 2019-12-07 09:50 |  | 0 | 0 | 13.55 | 13.55 | 5338.7 | 1 |  |  |  | 0 |  |  | 423
|  | CAUSE CODE : |  | 4420 |  |  | - |  | Vibration of the turbine generator unit that cannot be attributed to a specific cause such as bearings or blades (use this code for balance moves) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820High Turbine Vibration - #2 Bearing
MC3 | 65 | U1 | 2019-12-08 19:13 |  |  |  |  | 2019-12-09 07:22 |  | 0 | 0 | 12.15 | 12.15 | 4787.1 | 1 |  |  |  | 0 |  |  | 423
|  | CAUSE CODE : |  | 4420 |  |  | - |  | Vibration of the turbine generator unit that cannot be attributed to a specific cause such as bearings or blades (use this code for balance moves) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820High Turbine Vibration - #3 Bearing
MC3 | 66 | U1 | 2019-12-09 23:54 |  |  |  |  | 2019-12-10 09:21 |  | 0 | 0 | 9.45 | 9.45 | 3723.3 | 1 |  |  |  | 0 |  |  | 423
|  | CAUSE CODE : |  | 4420 |  |  | - |  | Vibration of the turbine generator unit that cannot be attributed to a specific cause such as bearings or blades (use this code for balance moves) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820High Turbine Vibration - #3 Bearing
MC3 | 16 | U1 | 2020-02-20 15:30 |  |  |  |  | 2020-02-20 19:27 |  | 0 | 0 | 3.95 | 3.95 | 1556.3 | 1 |  |  |  | 0 |  |  | 423
|  | CAUSE CODE : |  | 4420 |  |  | - |  | Vibration of the turbine generator unit that cannot be attributed to a specific cause such as bearings or blades (use this code for balance moves) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820High Turbine Vibration - #3 Bearing
MC3 | 22 | U1 | 2020-03-02 10:31 |  |  |  |  | 2020-03-02 12:30 |  | 0 | 0 | 1.983 | 1.9833 | 779.45 | 1 |  |  |  | 0 |  |  | 422.5
|  | CAUSE CODE : |  | 4420 |  |  | - |  | Vibration of the turbine generator unit that cannot be attributed to a specific cause such as bearings or blades (use this code for balance moves) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820High Turbine Vibration - #3 Bearing
MC3 | 59 | U1 | 2020-07-09 01:11 |  |  |  |  | 2020-07-09 03:54 |  | 0 | 0 | 2.717 | 2.7167 | 1062.217 | 1 |  |  |  | 0 |  |  | 422
|  | CAUSE CODE : |  | 1799 |  |  | - |  | Other boiler instrumentation and control problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Lose of Two Mills
MC3 | 70 | U1 | 2020-11-01 21:18 |  |  |  |  | 2020-11-01 23:42 |  | 0 | 0 | 2.4 | 2.4 | 943.2 | 1 |  |  |  | 0 |  |  | 422.5
|  | CAUSE CODE : |  | 3412 |  |  | - |  | Feedwater pump drive - steam turbine | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820TDBFP Trip
MC3 | 71 | U1 | 2020-11-01 23:48 |  |  |  |  | 2020-11-02 00:39 |  | 0 | 0 | 0.85 | 0.85 | 334.05 | 1 |  |  |  | 0 |  |  | 422.5
|  | CAUSE CODE : |  | 0800 |  |  | - |  | Drums and drum internals (single drum only) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Drum Level Trip
MC3 | 14 | U1 | 2021-03-05 23:50 |  |  |  |  | 2021-03-06 03:58 |  | 0 | 0 | 4.133 | 4.1333 | 1622.334 | 1 |  |  |  | 0 |  |  | 422.5
|  | CAUSE CODE : |  | 1488 |  |  | - |  | Air heater (regenerative) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F8303A Air Heater Drive Motor Replacment
MC3 | 16 | U1 | 2021-03-09 20:34 |  |  |  |  | 2021-03-09 23:36 |  | 0 | 0 | 3.033 | 3.0333 | 1190.583 | 1 |  |  |  | 0 |  |  | 422.5
|  | CAUSE CODE : |  | 3245 |  |  | - |  | Other cooling tower problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Cooling Tower Level Low
MC3 | 46 | U1 | 2021-07-15 13:16 |  |  |  |  | 2021-07-16 03:55 |  | 0 | 0 | 14.65 | 14.65 | 5728.15 | 1 |  |  |  | 0 |  |  | 422
|  | CAUSE CODE : |  | 9720 |  |  | - |  | Other safety problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Station Service Water Out of Service
MC3 | 61 | SF | 2021-11-29 14:32 |  |  |  |  | 2021-11-30 11:45 |  | 0 | 0 | 21.217 | 21.2167 | 8327.542 | 1 |  |  |  | 0 |  |  | 422.5
|  | CAUSE CODE : |  | 1488 |  |  | - |  | Air heater (regenerative) | [8 empty] | AMP CODE: |  | 92
|  | DESCRIPTION : |  | F9203A AH Gearbox - Bearing
MC3 | 6 | SF | 2022-02-20 21:00 |  |  |  |  | 2022-02-21 13:01 |  | 0 | 0 | 16.017 | 16.0167 | 6310.566 | 1 |  |  |  | 0 |  |  | 423
|  | CAUSE CODE : |  | 0730 |  |  | - |  | Other blowdown system problems | [8 empty] | AMP CODE: |  | 54
|  | DESCRIPTION : |  | F540Startup Failure - Failed Rupture Disk
MC3 | 19 | U1 | 2022-04-20 08:40 |  |  |  |  | 2022-04-21 16:05 |  | 0 | 0 | 31.417 | 31.4167 | 12331.041 | 1 |  |  |  | 0 |  |  | 422.5
|  | CAUSE CODE : |  | 1080 |  |  | - |  | Economizer | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Economizer Tube Leak
MC3 | 43 | U1 | 2022-12-01 14:40 |  |  |  |  | 2022-12-01 15:45 |  | 0 | 0 | 1.083 | 1.0833 | 426.833 | 1 |  |  |  | 0 |  |  | 423
|  | CAUSE CODE : |  | 1421 |  |  | - |  | Secondary air fans/blowers | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Secondary Air Flow - High Duct Pressure
MC3 | 8 | U1 | 2023-04-06 00:13 |  |  |  |  | 2023-04-06 05:50 |  | 0 | 0 | 5.617 | 5.6167 | 2207.35 | 1 |  |  |  | 0 |  |  | 422.5
|  | CAUSE CODE : |  | 1412 |  |  | - |  | Forced draft fan drives (other than motor) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F8203A FD Fan - Beck Drive Bad Card
MC3 | 29 | U1 | 2023-08-12 05:39 |  |  |  |  | 2023-08-12 13:41 |  | 0 | 0 | 8.033 | 8.0333 | 3141.033 | 1 |  |  |  | 0 |  |  | 422
|  | CAUSE CODE : |  | 4262 |  |  | - |  | Intercept valves | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830#1 Intercept Valve Maintenance
MC3 | 31 | U1 | 2023-09-02 21:09 |  |  |  |  | 2023-09-03 04:15 |  | 0 | 0 | 7.1 | 7.1 | 2790.3 | 1 |  |  |  | 0 |  |  | 422.5
|  | CAUSE CODE : |  | 1480 |  |  | - |  | Other induced draft fan problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820ID Fan Trip - Glycol Cooling Pump
Mill Creek - MC4
Unit | Event | Type | Start |  |  |  |  | End |  | GAC | NAC | Duration | Equiv Hrs | Equiv MWH | Cont | Work Start | Work End |  | Hours |  |  | Gross Capacity Impact (MW)
MC4 | 60 | U1 | 2014-04-13 16:27 |  |  |  |  | 2014-04-13 18:03 |  | 0 | 0 | 1.6 | 1.6 | 763.2 | 1 |  |  |  | 0 |  |  | 521
|  | CAUSE CODE : |  | 4309 |  |  | - |  | Other turbine instrument and control problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F400Turbine EHC Control Issue - Lost All Feeders
MC4 | 120 | U1 | 2014-06-08 03:25 |  |  |  |  | 2014-06-09 16:15 |  | 0 | 0 | 36.833 | 36.8333 | 17569.5 | 1 |  |  |  | 0 |  |  | 517
|  | CAUSE CODE : |  | 1060 |  |  | - |  | First reheater | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F540Boiler Tube Leak - First Reheater
MC4 | 167 | U1 | 2014-07-17 21:56 |  |  |  |  | 2014-07-17 23:26 |  | 0 | 0 | 1.5 | 1.5 | 715.5 | 1 |  |  |  | 0 |  |  | 517
|  | CAUSE CODE : |  | 0800 |  |  | - |  | Drums and drum internals (single drum only) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F420Low Drum Level
MC4 | 175 | U1 | 2014-07-25 01:43 |  |  |  |  | 2014-07-27 17:10 |  | 0 | 0 | 63.45 | 63.45 | 30265.649 | 1 |  |  |  | 0 |  |  | 517
|  | CAUSE CODE : |  | 1000 |  |  | - |  | Waterwall (Furnace wall) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F540Boiler Tube Leak - Lower Slope Waterwall
MC4 | 177 | U1 | 2014-07-27 17:30 |  |  |  |  | 2014-07-27 19:10 |  | 0 | 0 | 1.667 | 1.6667 | 795 | 1 |  |  |  | 0 |  |  | 517
|  | CAUSE CODE : |  | 0800 |  |  | - |  | Drums and drum internals (single drum only) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Low Drum Level Trip - Boiler Feed Pump Low Pressure Steam Supply Check Valve Stuck
MC4 | 179 | U1 | 2014-07-28 03:04 |  |  |  |  | 2014-07-28 05:13 |  | 0 | 0 | 2.15 | 2.15 | 1025.55 | 1 |  |  |  | 0 |  |  | 517
|  | CAUSE CODE : |  | 0800 |  |  | - |  | Drums and drum internals (single drum only) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F400Low Drum Level Trip
MC4 | 184 | U1 | 2014-07-29 02:24 |  |  |  |  | 2014-07-31 09:57 |  | 0 | 0 | 55.55 | 55.55 | 26497.35 | 1 |  |  |  | 0 |  |  | 517
|  | CAUSE CODE : |  | 1060 |  |  | - |  | First reheater | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F540Boiler Tube Leak - First Reheater
MC4 | 186 | U1 | 2014-07-31 10:13 |  |  |  |  | 2014-07-31 11:37 |  | 0 | 0 | 1.4 | 1.4 | 667.8 | 1 |  |  |  | 0 |  |  | 517
|  | CAUSE CODE : |  | 0800 |  |  | - |  | Drums and drum internals (single drum only) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Low Drum Level Trip - Turbine Driven Boiler Feed Pump Issues
MC4 | 190 | U1 | 2014-08-01 22:04 |  |  |  |  | 2014-08-03 07:43 |  | 0 | 0 | 33.65 | 33.65 | 16051.05 | 1 |  |  |  | 0 |  |  | 517
|  | CAUSE CODE : |  | 1060 |  |  | - |  | First reheater | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F540Boiler Tube Leak - First Reheater
MC4 | 227 | U1 | 2014-09-10 02:54 |  |  |  |  | 2014-09-10 05:39 |  | 0 | 0 | 2.75 | 2.75 | 1311.75 | 1 |  |  |  | 0 |  |  | 521
|  | CAUSE CODE : |  | 0800 |  |  | - |  | Drums and drum internals (single drum only) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F420Low Drum Level Trip - Operator Error
MC4 | 234 | U1 | 2014-09-18 14:35 |  |  |  |  | 2014-09-23 14:46 |  | 0 | 0 | 120.183 | 120.1833 | 57327.45 | 1 |  |  |  | 0 |  |  | 521
|  | CAUSE CODE : |  | 3649 |  |  | - |  | Other AC instrument power problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F430Electrical Wiring - Burnt Wiring in Cable Tray
MC4 | 237 | U1 | 2014-09-24 06:54 |  |  |  |  | 2014-09-24 08:05 |  | 0 | 0 | 1.183 | 1.1833 | 564.45 | 1 |  |  |  | 0 |  |  | 521
|  | CAUSE CODE : |  | 0800 |  |  | - |  | Drums and drum internals (single drum only) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Low Drum Level Trip - Boiler Pressure Swing
MC4 | 239 | U1 | 2014-09-24 09:45 |  |  |  |  | 2014-09-24 11:02 |  | 0 | 0 | 1.283 | 1.2833 | 612.15 | 1 |  |  |  | 0 |  |  | 521
|  | CAUSE CODE : |  | 0800 |  |  | - |  | Drums and drum internals (single drum only) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Low Drum Level Trip
MC4 | 243 | U1 | 2014-12-03 10:19 |  |  |  |  | 2014-12-03 11:00 |  | 0 | 0 | 0.683 | 0.6833 | 332.1 | 1 |  |  |  | 0 |  |  | 525
|  | CAUSE CODE : |  | 0800 |  |  | - |  | Drums and drum internals (single drum only) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Low Drum Level Trip
MC4 | 247 | U1 | 2014-12-06 11:58 |  |  |  |  | 2014-12-06 12:35 |  | 0 | 0 | 0.617 | 0.6167 | 299.7 | 1 |  |  |  | 0 |  |  | 525
|  | CAUSE CODE : |  | 0800 |  |  | - |  | Drums and drum internals (single drum only) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F420Low Drum Level Trip - Operator Error
MC4 | 256 | U1 | 2014-12-09 22:15 |  |  |  |  | 2014-12-10 02:09 |  | 0 | 0 | 3.9 | 3.9 | 1895.4 | 1 |  |  |  | 0 |  |  | 525
|  | CAUSE CODE : |  | 1455 |  |  | - |  | Induced draft fans | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F8204A Induced Draft Fan - Trip
MC4 | 260 | U1 | 2014-12-10 06:39 |  |  |  |  | 2014-12-10 08:39 |  | 0 | 0 | 2 | 2 | 972 | 1 |  |  |  | 0 |  |  | 525
|  | CAUSE CODE : |  | 0800 |  |  | - |  | Drums and drum internals (single drum only) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F420Low Drum Level Trip - Operator Error
MC4 | 262 | U1 | 2014-12-10 19:25 |  |  |  |  | 2014-12-13 22:03 |  | 0 | 0 | 74.633 | 74.6333 | 36271.8 | 1 |  |  |  | 0 |  |  | 525
|  | CAUSE CODE : |  | 3110 |  |  | - |  | Condenser tube leaks | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F540Condenser Tube Leaks
MC4 | 272 | U1 | 2014-12-16 09:12 |  |  |  |  | 2014-12-18 11:49 |  | 0 | 0 | 50.617 | 50.6167 | 24599.7 | 1 |  |  |  | 0 |  |  | 525
|  | CAUSE CODE : |  | 3110 |  |  | - |  | Condenser tube leaks | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F540Condenser Tube Leaks
MC4 | 7 | U1 | 2015-01-15 02:34 |  |  |  |  | 2015-01-15 07:18 |  | 0 | 0 | 4.733 | 4.7333 | 2300.4 | 1 |  |  |  | 0 |  |  | 525
|  | CAUSE CODE : |  | 1480 |  |  | - |  | Other induced draft fan problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Induced Draft Fan Suction Pressure Trip
MC4 | 11 | U1 | 2015-01-16 20:40 |  |  |  |  | 2015-01-17 03:02 |  | 0 | 0 | 6.367 | 6.3667 | 3094.2 | 1 |  |  |  | 0 |  |  | 525
|  | CAUSE CODE : |  | 4299 |  |  | - |  | Other hydraulic system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F540Turbine Left Intercept Valve - EHC Leak
MC4 | 14 | U1 | 2015-01-18 22:43 |  |  |  |  | 2015-01-19 01:41 |  | 0 | 0 | 2.967 | 2.9667 | 1441.8 | 1 |  |  |  | 0 |  |  | 525
|  | CAUSE CODE : |  | 4268 |  |  | - |  | Reheat/intercept valve testing | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Turbine Reheat/Intercept Valve Check - Trip
MC4 | 46 | U1 | 2015-03-25 15:24 |  |  |  |  | 2015-03-25 19:31 |  | 0 | 0 | 4.117 | 4.1167 | 2000.7 | 1 |  |  |  | 0 |  |  | 521
|  | CAUSE CODE : |  | 0800 |  |  | - |  | Drums and drum internals (single drum only) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Low Drum Level Trip
MC4 | 57 | U1 | 2015-04-01 18:22 |  |  |  |  | 2015-04-01 20:30 |  | 0 | 0 | 2.133 | 2.1333 | 1017.6 | 1 |  |  |  | 0 |  |  | 521
|  | CAUSE CODE : |  | 1455 |  |  | - |  | Induced draft fans | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F8204A Induced Draft Fan - Tripped
MC4 | 63 | U1 | 2015-05-14 10:40 |  |  |  |  | 2015-05-14 12:39 |  | 0 | 0 | 1.983 | 1.9833 | 946.05 | 1 |  |  |  | 0 |  |  | 521
|  | CAUSE CODE : |  | 1455 |  |  | - |  | Induced draft fans | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820ID fan sunction pressure trip
MC4 | 65 | U1 | 2015-05-14 13:42 |  |  |  |  | 2015-05-14 14:10 |  | 0 | 0 | 0.467 | 0.4667 | 222.6 | 1 |  |  |  | 0 |  |  | 521
|  | CAUSE CODE : |  | 0800 |  |  | - |  | Drums and drum internals (single drum only) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820High drum level trip
MC4 | 84 | U1 | 2015-08-02 02:27 |  |  |  |  | 2015-08-02 09:10 |  | 0 | 0 | 6.717 | 6.7167 | 3203.85 | 1 |  |  |  | 0 |  |  | 517
|  | CAUSE CODE : |  | 4264 |  |  | - |  | Combined intercept valves | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F540Turbine #2 Reheat/Intercept Valve - EHC Leak
MC4 | 86 | U1 | 2015-08-02 17:26 |  |  |  |  | 2015-08-02 20:09 |  | 0 | 0 | 2.717 | 2.7167 | 1295.85 | 1 |  |  |  | 0 |  |  | 517
|  | CAUSE CODE : |  | 0800 |  |  | - |  | Drums and drum internals (single drum only) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820High Drum Level Trip
MC4 | 89 | U1 | 2015-08-04 02:33 |  |  |  |  | 2015-08-04 04:58 |  | 0 | 0 | 2.417 | 2.4167 | 1152.75 | 1 |  |  |  | 0 |  |  | 517
|  | CAUSE CODE : |  | 0800 |  |  | - |  | Drums and drum internals (single drum only) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820High Drum Level Trip - Feedwater Heater Bypass
MC4 | 102 | U1 | 2015-10-18 00:22 |  |  |  |  | 2015-10-19 14:53 |  | 0 | 0 | 38.517 | 38.5167 | 18719.1 | 1 |  |  |  | 0 |  |  | 521
|  | CAUSE CODE : |  | 1000 |  |  | - |  | Waterwall (Furnace wall) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F540Boiler Tube Leak - Waterwall
MC4 | 11 | U1 | 2016-02-02 13:01 |  |  |  |  | 2016-02-02 16:34 |  | 0 | 0 | 3.55 | 3.55 | 1725.3 | 1 |  |  |  | 0 |  |  | 525
|  | CAUSE CODE : |  | 1470 |  |  | - |  | Induced draft fan motors and drives | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F8204B ID fan trip on high stator temp.
MC4 | 16 | U1 | 2016-02-27 14:37 |  |  |  |  | 2016-02-27 16:18 |  | 0 | 0 | 1.683 | 1.6833 | 818.1 | 1 |  |  |  | 0 |  |  | 525
|  | CAUSE CODE : |  | 0250 |  |  | - |  | Pulverizer feeders | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F8204A and 4B Mill feeders tripped.
MC4 | 18 | U1 | 2016-02-27 21:44 |  |  |  |  | 2016-02-28 00:57 |  | 0 | 0 | 3.217 | 3.2167 | 1563.3 | 1 |  |  |  | 0 |  |  | 525
|  | CAUSE CODE : |  | 1470 |  |  | - |  | Induced draft fan motors and drives | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F8204A ID fan inlet load index trip
MC4 | 23 | U1 | 2016-04-28 10:34 |  |  |  |  | 2016-05-01 23:27 |  | 0 | 0 | 84.883 | 84.8833 | 40913.767 | 1 |  |  |  | 0 |  |  | 521
|  | CAUSE CODE : |  | 1040 |  |  | - |  | First superheater | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F540Boiler tube leak - superheat
MC4 | 31 | U1 | 2016-09-20 09:36 |  |  |  |  | 2016-09-24 10:55 |  | 0 | 0 | 97.317 | 97.3167 | 46906.633 | 1 |  |  |  | 0 |  |  | 521
|  | CAUSE CODE : |  | 1040 |  |  | - |  | First superheater | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Boiler tube leak - superheater
MC4 | 32 | U1 | 2016-09-24 12:09 |  |  |  |  | 2016-09-24 12:39 |  | 0 | 0 | 0.5 | 0.5 | 241 | 1 |  |  |  | 0 |  |  | 521
|  | CAUSE CODE : |  | 0380 |  |  | - |  | Light off (igniter) systems (including fuel supply) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820'Trip - Loss of Fuel
MC4 | 13 | U1 | 2017-02-14 02:13 |  |  |  |  | 2017-02-14 04:11 |  | 0 | 0 | 1.967 | 1.9667 | 955.8 | 1 |  |  |  | 0 |  |  | 525
|  | CAUSE CODE : |  | 4268 |  |  | - |  | Reheat/intercept valve testing | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Trip During Valve Testing (Under Investigation)
MC4 | 16 | U1 | 2017-02-25 18:00 |  |  |  |  | 2017-02-26 20:49 |  | 0 | 0 | 26.817 | 26.8167 | 13032.9 | 1 |  |  |  | 0 |  |  | 525
|  | CAUSE CODE : |  | 0370 |  |  | - |  | Burner instruments and controls (except light off) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Master Fuel Trip (Lost Flame Scanner)
MC4 | 20 | U1 | 2017-03-25 08:50 |  |  |  |  | 2017-03-25 08:55 |  | 0 | 0 | 0.083 | 0.0833 | 40.167 | 1 |  |  |  | 0 |  |  | 521
|  | CAUSE CODE : |  | 4268 |  |  | - |  | Reheat/intercept valve testing | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Trip During Valve Testing (Under Investigation)
MC4 | 24 | U1 | 2017-03-30 14:49 |  |  |  |  | 2017-04-02 08:34 |  | 0 | 0 | 65.75 | 65.75 | 31691.5 | 1 |  |  |  | 0 |  |  | 521
|  | CAUSE CODE : |  | 4810 |  |  | - |  | Generator output breaker | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Generator Lockout Trip (Electrical Ground Indication)
MC4 | 25 | U1 | 2017-04-02 09:22 |  |  |  |  | 2017-04-02 11:06 |  | 0 | 0 | 1.733 | 1.7333 | 835.467 | 1 |  |  |  | 0 |  |  | 521
|  | CAUSE CODE : |  | 0800 |  |  | - |  | Drums and drum internals (single drum only) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Drum Level Trip
MC4 | 29 | U1 | 2017-04-07 00:50 |  |  |  |  | 2017-04-07 03:41 |  | 0 | 0 | 2.85 | 2.85 | 1373.7 | 1 |  |  |  | 0 |  |  | 521
|  | CAUSE CODE : |  | 4268 |  |  | - |  | Reheat/intercept valve testing | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Trip During Valve Testing
MC4 | 32 | U1 | 2017-05-08 01:46 |  |  |  |  | 2017-05-08 03:03 |  | 0 | 0 | 1.283 | 1.2833 | 618.567 | 1 |  |  |  | 0 |  |  | 521
|  | CAUSE CODE : |  | 4266 |  |  | - |  | Main stop valve testing | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Drum Level Trip (During Main Stop Valve Testing)
MC4 | 33 | U1 | 2017-05-12 21:07 |  |  |  |  | 2017-05-12 21:22 |  | 0 | 0 | 0.25 | 0.25 | 120.5 | 1 |  |  |  | 0 |  |  | 521
|  | CAUSE CODE : |  | 4268 |  |  | - |  | Reheat/intercept valve testing | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Trip During Valve Testing
MC4 | 35 | U1 | 2017-05-19 02:11 |  |  |  |  | 2017-05-19 07:58 |  | 0 | 0 | 5.783 | 5.7833 | 2787.567 | 1 |  |  |  | 0 |  |  | 521
|  | CAUSE CODE : |  | 4810 |  |  | - |  | Generator output breaker | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Generator Lockout Trip
MC4 | 40 | U1 | 2017-06-27 12:32 |  |  |  |  | 2017-06-28 14:01 |  | 0 | 0 | 25.483 | 25.4833 | 12155.55 | 1 |  |  |  | 0 |  |  | 517
|  | CAUSE CODE : |  | 3110 |  |  | - |  | Condenser tube leaks | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Condenser Leak
MC4 | 51 | U1 | 2017-11-29 04:47 |  |  |  |  | 2017-11-30 13:16 |  | 0 | 0 | 32.483 | 32.4833 | 15656.967 | 1 |  |  |  | 0 |  |  | 521
|  | CAUSE CODE : |  | 0520 |  |  | - |  | Other main steam valves (including vent and drain valves but not including the turbine stop valves) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F540Steam Leaks (Blowdown Tank & Stop Valve Drain)
MC4 | 53 | U1 | 2017-12-06 14:35 |  |  |  |  | 2017-12-06 17:01 |  | 0 | 0 | 2.433 | 2.4333 | 1182.6 | 1 |  |  |  | 0 |  |  | 525
|  | CAUSE CODE : |  | 3700 |  |  | - |  | Power Station switchyard (non generating unit equipment) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Generator Protective Trip - Switchyard Work
MC4 | 14 | U1 | 2018-01-23 03:45 |  |  |  |  | 2018-01-23 04:24 |  | 0 | 0 | 0.65 | 0.65 | 315.9 | 1 |  |  |  | 0 |  |  | 525
|  | CAUSE CODE : |  | 0800 |  |  | - |  | Drums and drum internals (single drum only) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Low Drum Level Trip
MC4 | 18 | U1 | 2018-02-25 06:50 |  |  |  |  | 2018-02-25 08:50 |  | 0 | 0 | 2 | 2 | 972 | 1 |  |  |  | 0 |  |  | 525
|  | CAUSE CODE : |  | 0800 |  |  | - |  | Drums and drum internals (single drum only) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Drum Level Trip - Low Level
MC4 | 22 | SF | 2018-03-07 02:33 |  |  |  |  | 2018-03-07 07:56 |  | 0 | 0 | 5.383 | 5.3833 | 2594.767 | 1 |  |  |  | 0 |  |  | 521
|  | CAUSE CODE : |  | 8280 |  |  | - |  | Reagent feed piping | [8 empty] | AMP CODE: |  | 12
|  | DESCRIPTION : |  | F120Plugged Limestone Feed (SUF)
MC4 | 29 | U1 | 2018-05-14 19:03 |  |  |  |  | 2018-05-14 21:52 |  | 0 | 0 | 2.817 | 2.8167 | 1357.633 | 1 |  |  |  | 0 |  |  | 521
|  | CAUSE CODE : |  | 1470 |  |  | - |  | Induced draft fan motors and drives | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F8204B ID Fan Motor Stator Temperature Trip
MC4 | 30 | U1 | 2018-05-15 00:12 |  |  |  |  | 2018-05-15 03:27 |  | 0 | 0 | 3.25 | 3.25 | 1566.5 | 1 |  |  |  | 0 |  |  | 521
|  | CAUSE CODE : |  | 3864 |  |  | - |  | Fire protection system instrumentation and controls | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Fire System Deluge Valve Opened - Tripped TDBFP
MC4 | 40 | U1 | 2018-06-07 15:11 |  |  |  |  | 2018-06-07 19:43 |  | 0 | 0 | 4.533 | 4.5333 | 2162.4 | 1 |  |  |  | 0 |  |  | 517
|  | CAUSE CODE : |  | 3499 |  |  | - |  | Other feedwater system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Steam/Feedwater Flow Deviation Trip
MC4 | 48 | U1 | 2018-06-29 14:10 |  |  |  |  | 2018-06-29 15:41 |  | 0 | 0 | 1.517 | 1.5167 | 723.45 | 1 |  |  |  | 0 |  |  | 517
|  | CAUSE CODE : |  | 3211 |  |  | - |  | Circulating water pump motors | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F8204B CTP Tripped
MC4 | 73 | U1 | 2018-09-19 04:27 |  |  |  |  | 2018-09-20 02:00 |  | 0 | 0 | 21.55 | 21.55 | 10387.1 | 1 |  |  |  | 0 |  |  | 521
|  | CAUSE CODE : |  | 4810 |  |  | - |  | Generator output breaker | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Generator Lockout - Surge Protection Capacitor Failure
MC4 | 78 | U1 | 2018-11-25 22:16 |  |  |  |  | 2018-11-28 04:03 |  | 0 | 0 | 53.783 | 53.7833 | 25923.567 | 1 |  |  |  | 0 |  |  | 521
|  | CAUSE CODE : |  | 3415 |  |  | - |  | Feedwater pump/drive lube oil system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820TDBFP Bearing Oil Leak/Fire
MC4 | 3 | U1 | 2019-01-27 07:55 |  |  |  |  | 2019-01-28 12:50 |  | 0 | 0 | 28.917 | 28.9167 | 14053.5 | 1 |  |  |  | 0 |  |  | 525
|  | CAUSE CODE : |  | 1080 |  |  | - |  | Economizer | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Economizer Tube Leak
MC4 | 4 | SF | 2019-01-28 12:50 |  |  |  |  | 2019-01-28 17:05 |  | 0 | 0 | 4.25 | 4.25 | 2065.5 | 1 |  |  |  | 0 |  |  | 525
|  | CAUSE CODE : |  | 3344 |  |  | - |  | Deaerator (including level control) | [8 empty] | AMP CODE: |  | 52
|  | DESCRIPTION : |  | F820Lost Deaerator Level Indication - SUF
MC4 | 16 | U1 | 2019-02-19 13:31 |  |  |  |  | 2019-02-19 15:33 |  | 0 | 0 | 2.033 | 2.0333 | 988.2 | 1 |  |  |  | 0 |  |  | 525
|  | CAUSE CODE : |  | 3634 |  |  | - |  | 400-700 volt protection devices | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Loss of 480 volt MCC
MC4 | 6 | U1 | 2020-03-04 09:37 |  |  |  |  | 2020-03-04 13:57 |  | 0 | 0 | 4.333 | 4.3333 | 2088.667 | 1 |  |  |  | 0 |  |  | 521
|  | CAUSE CODE : |  | 4302 |  |  | - |  | Turbine trip devices (including instruments) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820High Turbine Vibration - False Indication
MC4 | 25 | SF | 2020-12-06 14:20 |  |  |  |  | 2020-12-07 06:43 |  | 0 | 0 | 16.383 | 16.3833 | 7962.3 | 1 |  |  |  | 0 |  |  | 525
|  | CAUSE CODE : |  | 4720 |  |  | - |  | Generator synchronization equipment | [8 empty] | AMP CODE: |  | 52
|  | DESCRIPTION : |  | F520Start Up Failure - Various Issues
MC4 | 26 | U1 | 2020-12-07 08:02 |  |  |  |  | 2020-12-08 07:42 |  | 0 | 0 | 23.667 | 23.6667 | 11502 | 1 |  |  |  | 0 |  |  | 525
|  | CAUSE CODE : |  | 4265 |  |  | - |  | Miscellaneous drain and vent valves | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820MSV Seat Drain Steam Leak
MC4 | 27 | SF | 2020-12-08 07:42 |  |  |  |  | 2020-12-09 04:30 |  | 0 | 0 | 20.8 | 20.8 | 10108.8 | 1 |  |  |  | 0 |  |  | 525
|  | CAUSE CODE : |  | 4265 |  |  | - |  | Miscellaneous drain and vent valves | [8 empty] | AMP CODE: |  | 54
|  | DESCRIPTION : |  | F540MSV Seat Drain Steam Leak
MC4 | 28 | U1 | 2020-12-09 11:48 |  |  |  |  | 2020-12-11 06:34 |  | 0 | 0 | 42.767 | 42.7667 | 20784.6 | 1 |  |  |  | 0 |  |  | 525
|  | CAUSE CODE : |  | 4260 |  |  | - |  | Main stop valves | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830MSV Screen Differential
MC4 | 30 | U1 | 2020-12-13 09:06 |  |  |  |  | 2020-12-13 10:42 |  | 0 | 0 | 1.6 | 1.6 | 777.6 | 1 |  |  |  | 0 |  |  | 525
|  | CAUSE CODE : |  | 0800 |  |  | - |  | Drums and drum internals (single drum only) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Low Boiler Drum Level
MC4 | 3 | U1 | 2021-03-08 09:45 |  |  |  |  | 2021-03-08 12:20 |  | 0 | 0 | 2.583 | 2.5833 | 1243.875 | 1 |  |  |  | 0 |  |  | 521
|  | CAUSE CODE : |  | 1430 |  |  | - |  | Air supply ducts from FD fan | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Secondary Air Duct - High Pressure
MC4 | 5 | U1 | 2021-03-08 22:16 |  |  |  |  | 2021-03-10 04:15 |  | 0 | 0 | 29.983 | 29.9833 | 14436.975 | 1 |  |  |  | 0 |  |  | 521
|  | CAUSE CODE : |  | 3110 |  |  | - |  | Condenser tube leaks | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Condenser Tube Leak
MC4 | 31 | U1 | 2021-05-28 17:55 |  |  |  |  | 2021-05-28 23:12 |  | 0 | 0 | 5.283 | 5.2833 | 2543.925 | 1 |  |  |  | 0 |  |  | 521
|  | CAUSE CODE : |  | 8261 |  |  | - |  | Scrubber booster I.D. fan drive | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F8204A ID Fan Trip - VFD Fault
MC4 | 35 | U1 | 2021-06-04 15:06 |  |  |  |  | 2021-06-04 19:45 |  | 0 | 0 | 4.65 | 4.65 | 2218.05 | 1 |  |  |  | 0 |  |  | 517
|  | CAUSE CODE : |  | 8262 |  |  | - |  | Scrubber booster I.D. fan vibration (fan specific to the scrubber) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F8204A ID Fan Trip - False Indication
MC4 | 40 | U1 | 2021-07-15 13:18 |  |  |  |  | 2021-07-16 01:44 |  | 0 | 0 | 12.433 | 12.4333 | 5930.7 | 1 |  |  |  | 0 |  |  | 517
|  | CAUSE CODE : |  | 9720 |  |  | - |  | Other safety problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Station Service Water Out of Service
MC4 | 42 | U1 | 2021-08-18 05:11 |  |  |  |  | 2021-08-18 06:52 |  | 0 | 0 | 1.683 | 1.6833 | 802.95 | 1 |  |  |  | 0 |  |  | 517
|  | CAUSE CODE : |  | 4611 |  |  | - |  | Hydrogen coolers | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Generator Hydrogen Temp High
MC4 | 43 | U1 | 2021-08-23 03:51 |  |  |  |  | 2021-08-23 06:05 |  | 0 | 0 | 2.233 | 2.2333 | 1065.3 | 1 |  |  |  | 0 |  |  | 517
|  | CAUSE CODE : |  | 4630 |  |  | - |  | Liquid cooling system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Loss of Stator Cooling Flow
MC4 | 49 | U1 | 2021-10-13 15:53 |  |  |  |  | 2021-10-15 09:40 |  | 0 | 0 | 41.783 | 41.7833 | 20118.675 | 1 |  |  |  | 0 |  |  | 521
|  | CAUSE CODE : |  | 1400 |  |  | - |  | Forced draft fans | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830FD Fan Bearing Vibration
MC4 | 61 | U1 | 2021-12-10 08:29 |  |  |  |  | 2021-12-10 10:34 |  | 0 | 0 | 2.083 | 2.0833 | 1012.5 | 1 |  |  |  | 0 |  |  | 525
|  | CAUSE CODE : |  | 1407 |  |  | - |  | Forced draft fan lubrication system | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F8304B FD Fan - Bearing Temperature
MC4 | 2 | U1 | 2023-01-03 09:54 |  |  |  |  | 2023-01-04 06:51 |  | 0 | 0 | 20.95 | 20.95 | 10181.7 | 1 |  |  |  | 0 |  |  | 525
|  | CAUSE CODE : |  | 1080 |  |  | - |  | Economizer | [8 empty] | AMP CODE:
|  | DESCRIPTION : |  | F830Economizer Tube Leak
MC4 | 16 | U1 | 2023-02-26 14:56 |  |  |  |  | 2023-02-26 18:27 |  | 0 | 0 | 3.517 | 3.5167 | 1709.1 | 1 |  |  |  | 0 |  |  | 525
|  | CAUSE CODE : |  | 4040 |  |  | - |  | Bearings | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Turbine Bearing Vibration
MC4 | 24 | U1 | 2023-05-30 15:47 |  |  |  |  | 2023-05-30 17:58 |  | 0 | 0 | 2.183 | 2.1833 | 1051.275 | 1 |  |  |  | 0 |  |  | 521
|  | CAUSE CODE : |  | 4099 |  |  | - |  | Other high pressure turbine problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Turbine Trip
MC4 | 26 | U1 | 2023-05-30 21:05 |  |  |  |  | 2023-05-31 00:02 |  | 0 | 0 | 2.95 | 2.95 | 1420.425 | 1 |  |  |  | 0 |  |  | 521
|  | CAUSE CODE : |  | 0800 |  |  | - |  | Drums and drum internals (single drum only) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Drum Level Trip
MC4 | 33 | SF | 2023-08-15 11:33 |  |  |  |  | 2023-08-15 12:39 |  | 0 | 0 | 1.1 | 1.1 | 524.7 | 1 |  |  |  | 0 |  |  | 517
|  | CAUSE CODE : |  | 4551 |  |  | - |  | Generator bearings | [8 empty] | AMP CODE: |  | 85
|  | DESCRIPTION : |  | F850Startup Failure - Turbine Vibration
Ohio Falls - OF1
Unit | Event | Type | Start |  |  |  |  | End |  | GAC | NAC | Duration | Equiv Hrs | Equiv MWH | Cont | Work Start | Work End |  | Hours |  |  | Gross Capacity Impact (MW)
OF1 | 8 | U1 | 2014-07-21 08:32 |  |  |  |  | 2014-07-21 15:46 |  | 0 | 0 | 7.233 | 7.2333 | 43.4 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9590 |  |  | - |  | Miscellaneous regulatory (this code is primarily intended for use with event contribution code 2 to indicate that a regulatory-related factor contributed to the primary cause of the event) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830FERC diver inspection
OF1 | 9 | U1 | 2014-07-25 09:50 |  |  |  |  | 2014-07-28 13:33 |  | 0 | 0 | 75.717 | 75.7167 | 454.3 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | FE00Low Flow
OF1 | 10 | U1 | 2014-07-28 13:34 |  |  |  |  | 2014-07-28 14:49 |  | 0 | 0 | 1.25 | 1.25 | 7.5 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 3671 |  |  | - |  | 12-15kV circuit breakers | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F82014kv breaker tripped
OF1 | 11 | U1 | 2014-08-31 11:26 |  |  |  |  | 2014-09-04 07:05 |  | 0 | 0 | 91.65 | 91.65 | 708.067 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830LOW RIVER
OF1 | 14 | U1 | 2014-09-20 13:50 |  |  |  |  | 2014-09-22 07:39 |  | 0 | 0 | 41.817 | 41.8167 | 334.533 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low river
OF1 | 15 | U1 | 2014-09-24 06:29 |  |  |  |  | 2014-10-06 07:11 |  | 0 | 0 | 288.7 | 288.7 | 2055.233 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF1 | 16 | U1 | 2014-10-06 14:23 |  |  |  |  | 2014-10-08 12:29 |  | 0 | 0 | 46.1 | 46.1 | 276.6 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7007 |  |  | - |  | Bearings | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Thrust bearing shaft oil pump broken
OF1 | 19 | U1 | 2014-12-06 14:15 |  |  |  |  | 2014-12-12 12:04 |  | 0 | 0 | 141.817 | 141.8167 | 850.9 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830high water
OF1 | 20 | U1 | 2014-12-15 10:13 |  |  |  |  | 2014-12-15 16:27 |  | 0 | 0 | 6.233 | 6.2333 | 37.4 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9720 |  |  | - |  | Other safety problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Divers removing plugs in Unit #3, intakes for cooling water.
OF1 | 1 | U1 | 2015-01-15 10:04 |  |  |  |  | 2015-01-15 14:53 |  | 0 | 0 | 4.817 | 4.8167 | 19.267 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9720 |  |  | - |  | Other safety problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Divers in the water doing inspection on Unit 2 ,lower pool.
OF1 | 2 | U1 | 2015-01-27 14:55 |  |  |  |  | 2015-01-27 18:54 |  | 0 | 0 | 3.983 | 3.9833 | 15.933 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9720 |  |  | - |  | Other safety problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Divers transfering lower head gates from Unit 3 to unit 2
OF1 | 3 | U1 | 2015-01-28 10:03 |  |  |  |  | 2015-01-28 15:01 |  | 0 | 0 | 4.967 | 4.9667 | 19.867 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9720 |  |  | - |  | Other safety problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Divers in lower pool installing lower head gates in unit #2
OF1 | 4 | U1 | 2015-01-30 09:37 |  |  |  |  | 2015-01-30 12:55 |  | 0 | 0 | 3.3 | 3.3 | 13.2 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9720 |  |  | - |  | Other safety problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Divers in lower pool sealing lower head gates.
OF1 | 7 | U1 | 2015-02-06 13:12 |  |  |  |  | 2015-02-07 13:19 |  | 0 | 0 | 24.117 | 24.1167 | 144.7 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Flush Drift
OF1 | 11 | U1 | 2015-03-04 11:52 |  |  |  |  | 2015-03-27 13:07 |  | 0 | 0 | 553.25 | 553.25 | 2213 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF1 | 12 | U1 | 2015-04-03 07:07 |  |  |  |  | 2015-04-29 10:31 |  | 0 | 0 | 627.4 | 627.4 | 3764.4 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830HIGH WATER
OF1 | 13 | U1 | 2015-05-23 12:48 |  |  |  |  | 2015-05-26 09:55 |  | 0 | 0 | 69.117 | 69.1167 | 414.7 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF1 | 14 | U1 | 2015-05-27 14:44 |  |  |  |  | 2015-05-28 07:42 |  | 0 | 0 | 16.967 | 16.9667 | 101.8 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Low Flow
OF1 | 15 | U1 | 2015-06-12 08:37 |  |  |  |  | 2015-06-13 08:19 |  | 0 | 0 | 23.7 | 23.7 | 142.2 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low river
OF1 | 18 | U1 | 2015-06-21 06:46 |  |  |  |  | 2015-06-26 12:18 |  | 0 | 0 | 125.533 | 125.5333 | 753.2 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830High water.
OF1 | 19 | U1 | 2015-06-29 13:18 |  |  |  |  | 2015-07-08 08:01 |  | 0 | 0 | 210.717 | 210.7167 | 1616.333 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830HIGHWATER
OF1 | 20 | U1 | 2015-07-10 12:26 |  |  |  |  | 2015-07-22 12:14 |  | 0 | 0 | 287.8 | 287.8 | 2302.4 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF1 | 21 | U1 | 2015-07-25 09:14 |  |  |  |  | 2015-07-26 09:57 |  | 0 | 0 | 24.717 | 24.7167 | 197.733 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Trash
OF1 | 22 | U1 | 2015-07-28 03:00 |  |  |  |  | 2015-07-28 07:51 |  | 0 | 0 | 4.85 | 4.85 | 38.8 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 3812 |  |  | - |  | Service water valves | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Had to replace service water valve.
OF1 | 23 | U1 | 2015-07-31 12:38 |  |  |  |  | 2015-07-31 12:52 |  | 0 | 0 | 0.233 | 0.2333 | 1.867 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Trash in trashracks, stopped up.
OF1 | 24 | U1 | 2015-08-04 09:54 |  |  |  |  | 2015-08-04 10:20 |  | 0 | 0 | 0.433 | 0.4333 | 3.467 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 3974 |  |  | - |  | DCS - logic problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Tailwater sensor in logic lost communication.
OF1 | 25 | U1 | 2015-08-10 07:00 |  |  |  |  | 2015-08-14 15:54 |  | 0 | 0 | 104.9 | 104.9 | 839.2 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Dredge
OF1 | 26 | U1 | 2015-08-15 06:17 |  |  |  |  | 2015-08-16 12:13 |  | 0 | 0 | 29.933 | 29.9333 | 239.466 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Off for low flow
OF1 | 27 | U1 | 2015-08-17 09:10 |  |  |  |  | 2015-08-19 07:31 |  | 0 | 0 | 46.35 | 46.35 | 370.8 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF1 | 28 | U1 | 2015-08-21 06:15 |  |  |  |  | 2015-09-11 07:24 |  | 0 | 0 | 505.15 | 505.15 | 4041.2 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF1 | 29 | U1 | 2015-09-12 01:10 |  |  |  |  | 2015-09-30 07:34 |  | 0 | 0 | 438.4 | 438.4 | 3507.2 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low flow
OF1 | 31 | U1 | 2015-10-07 19:53 |  |  |  |  | 2015-10-09 09:01 |  | 0 | 0 | 37.133 | 37.1333 | 297.066 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Took unit at the request of ACOE.
OF1 | 32 | U1 | 2015-10-11 06:57 |  |  |  |  | 2015-10-20 15:08 |  | 0 | 0 | 224.183 | 224.1833 | 1793.467 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Took unit off line @ 0657 system time at the request of ACOE. Low flow.
OF1 | 33 | U1 | 2015-10-21 13:22 |  |  |  |  | 2015-10-28 08:30 |  | 0 | 0 | 163.133 | 163.1333 | 1305.067 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low flow
OF1 | 35 | U1 | 2015-11-02 04:09 |  |  |  |  | 2015-11-02 08:24 |  | 0 | 0 | 4.25 | 4.25 | 34 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 4650 |  |  | - |  | Other cooling system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Clog strainer basket
OF1 | 37 | U1 | 2015-11-13 17:55 |  |  |  |  | 2015-11-13 18:05 |  | 0 | 0 | 0.167 | 0.1667 | 1.333 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 3974 |  |  | - |  | DCS - logic problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Control problem with unit #2
OF1 | 39 | U1 | 2015-12-04 00:49 |  |  |  |  | 2015-12-08 11:26 |  | 0 | 0 | 106.617 | 106.6167 | 852.934 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF1 | 40 | U1 | 2015-12-24 10:00 |  |  |  |  | 2015-12-31 23:59 |  | 0 | 0 | 181.983 | 181.9833 | 1455.867 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF1 | 1 | U1 | 2016-01-01 |  |  |  |  | 2016-01-05 14:27 |  | 0 | 0 | 110.45 | 110.45 | 552.25 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Highwater
OF1 | 2 | U1 | 2016-02-03 06:26 |  |  |  |  | 2016-02-11 12:51 |  | 0 | 0 | 198.417 | 198.4167 | 992.083 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF1 | 3 | U1 | 2016-02-17 22:31 |  |  |  |  | 2016-03-08 13:29 |  | 0 | 0 | 470.967 | 470.9667 | 2717.8 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Highwater
OF1 | 4 | U1 | 2016-03-12 03:17 |  |  |  |  | 2016-03-21 12:17 |  | 0 | 0 | 225 | 225 | 1575 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Highwater
OF1 | 5 | U1 | 2016-04-13 12:14 |  |  |  |  | 2016-04-18 10:04 |  | 0 | 0 | 117.833 | 117.8333 | 824.834 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830High water
OF1 | 6 | U1 | 2016-05-02 10:17 |  |  |  |  | 2016-05-02 13:18 |  | 0 | 0 | 3.017 | 3.0167 | 21.117 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7053 |  |  | - |  | Governor oil system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Governor system low on oil.
OF1 | 7 | U1 | 2016-05-03 06:09 |  |  |  |  | 2016-05-10 10:23 |  | 0 | 0 | 172.233 | 172.2333 | 1205.633 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820HIGHWATER
OF1 | 8 | U1 | 2016-05-12 09:05 |  |  |  |  | 2016-05-16 10:37 |  | 0 | 0 | 97.533 | 97.5333 | 682.734 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF1 | 9 | U1 | 2016-05-24 09:23 |  |  |  |  | 2016-05-24 12:44 |  | 0 | 0 | 3.35 | 3.35 | 23.45 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Trash at intake, cleaning out.
OF1 | 10 | U1 | 2016-05-25 03:09 |  |  |  |  | 2016-05-25 07:04 |  | 0 | 0 | 3.917 | 3.9167 | 27.417 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830TRASH
OF1 | 12 | U1 | 2016-06-11 22:10 |  |  |  |  | 2016-06-13 07:31 |  | 0 | 0 | 33.35 | 33.35 | 266.8 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF1 | 13 | U1 | 2016-06-15 05:38 |  |  |  |  | 2016-06-16 10:43 |  | 0 | 0 | 29.083 | 29.0833 | 232.666 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830LOW RIVER
OF1 | 14 | U1 | 2016-06-20 11:16 |  |  |  |  | 2016-06-22 06:58 |  | 0 | 0 | 43.7 | 43.7 | 349.6 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF1 | 15 | U1 | 2016-06-26 02:50 |  |  |  |  | 2016-06-28 09:18 |  | 0 | 0 | 54.467 | 54.4667 | 435.733 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820highwater
OF1 | 16 | U1 | 2016-07-09 06:25 |  |  |  |  | 2016-07-09 08:45 |  | 0 | 0 | 2.333 | 2.3333 | 18.667 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Trash
OF1 | 17 | U1 | 2016-07-13 16:57 |  |  |  |  | 2016-07-15 13:59 |  | 0 | 0 | 45.033 | 45.0333 | 360.267 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF1 | 18 | U1 | 2016-07-18 08:31 |  |  |  |  | 2016-07-28 10:39 |  | 0 | 0 | 242.133 | 242.1333 | 1937.067 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF1 | 19 | U1 | 2016-08-05 05:24 |  |  |  |  | 2016-08-06 08:56 |  | 0 | 0 | 27.533 | 27.5333 | 220.267 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF1 | 20 | U1 | 2016-08-07 16:16 |  |  |  |  | 2016-08-11 09:31 |  | 0 | 0 | 89.25 | 89.25 | 714 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF1 | 21 | U1 | 2016-08-11 19:11 |  |  |  |  | 2016-08-14 09:45 |  | 0 | 0 | 62.567 | 62.5667 | 500.533 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830LOW FLOW
OF1 | 22 | U1 | 2016-08-14 14:25 |  |  |  |  | 2016-08-15 10:23 |  | 0 | 0 | 19.967 | 19.9667 | 159.734 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830LOW FLOW
OF1 | 23 | U1 | 2016-08-22 10:07 |  |  |  |  | 2016-08-23 14:09 |  | 0 | 0 | 28.033 | 28.0333 | 224.267 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF1 | 24 | U1 | 2016-08-25 02:15 |  |  |  |  | 2016-08-29 07:15 |  | 0 | 0 | 101 | 101 | 808 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF1 | 25 | U1 | 2016-09-02 13:00 |  |  |  |  | 2016-09-08 09:25 |  | 0 | 0 | 140.417 | 140.4167 | 982.917 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF1 | 26 | U1 | 2016-09-12 00:26 |  |  |  |  | 2016-10-01 08:23 |  | 0 | 0 | 463.95 | 463.95 | 3247.65 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830LOW FLOW
OF1 | 27 | U1 | 2016-10-02 09:08 |  |  |  |  | 2016-10-03 07:25 |  | 0 | 0 | 22.283 | 22.2833 | 155.984 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830LOW FLOW
OF1 | 28 | U1 | 2016-10-04 11:51 |  |  |  |  | 2016-10-20 11:55 |  | 0 | 0 | 384.067 | 384.0667 | 2688.467 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low river
OF1 | 29 | U1 | 2016-10-21 04:23 |  |  |  |  | 2016-10-22 07:41 |  | 0 | 0 | 27.3 | 27.3 | 191.1 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF1 | 30 | U1 | 2016-11-01 15:57 |  |  |  |  | 2016-11-02 13:50 |  | 0 | 0 | 21.883 | 21.8833 | 153.183 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF1 | 31 | U1 | 2016-11-08 07:18 |  |  |  |  | 2016-11-10 08:34 |  | 0 | 0 | 49.267 | 49.2667 | 344.867 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830LOW FLOW
OF1 | 32 | U1 | 2016-11-16 12:03 |  |  |  |  | 2016-11-17 07:39 |  | 0 | 0 | 19.6 | 19.6 | 137.2 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF1 | 33 | U1 | 2016-11-18 13:24 |  |  |  |  | 2016-11-29 07:43 |  | 0 | 0 | 258.317 | 258.3167 | 1808.217 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low river
OF1 | 34 | U1 | 2016-11-30 13:42 |  |  |  |  | 2016-12-02 07:39 |  | 0 | 0 | 41.95 | 41.95 | 230.35 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830LOW FLOW
OF1 | 35 | U1 | 2016-12-19 08:19 |  |  |  |  | 2016-12-26 13:24 |  | 0 | 0 | 173.083 | 173.0833 | 865.417 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830HIGH WATER
OF1 | 36 | U1 | 2016-12-31 08:47 |  |  |  |  | 2017-01-01 |  | 0 | 0 | 15.217 | 15.2167 | 76.083 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF1 | 1 | U1 | 2017-01-01 |  |  |  |  | 2017-01-02 14:02 |  | 0 | 0 | 38.033 | 38.0333 | 190.167 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF1 | 2 | U1 | 2017-01-05 22:05 |  |  |  |  | 2017-01-10 13:50 |  | 0 | 0 | 111.75 | 111.75 | 558.75 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF1 | 3 | U1 | 2017-01-14 15:57 |  |  |  |  | 2017-01-31 14:31 |  | 0 | 0 | 406.567 | 406.5667 | 2032.833 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820HIGH WATER
OF1 | 4 | U1 | 2017-01-31 14:33 |  |  |  |  | 2017-01-31 14:59 |  | 0 | 0 | 0.433 | 0.4333 | 2.167 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820TRASH RACK INTAKE BLOCKAGE
OF1 | 5 | U1 | 2017-02-11 17:38 |  |  |  |  | 2017-02-14 08:10 |  | 0 | 0 | 62.533 | 62.5333 | 312.666 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Highwater
OF1 | 9 | U1 | 2017-02-21 08:41 |  |  |  |  | 2017-02-21 11:36 |  | 0 | 0 | 2.917 | 2.9167 | 14.583 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9320 |  |  | - |  | Other miscellaneous external problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F82086 Generator Lock out
OF1 | 10 | U1 | 2017-03-01 12:47 |  |  |  |  | 2017-03-14 12:06 |  | 0 | 0 | 311.317 | 311.3167 | 2179.217 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820High Water
OF1 | 13 | U1 | 2017-03-24 09:57 |  |  |  |  | 2017-03-24 13:31 |  | 0 | 0 | 3.567 | 3.5667 | 24.967 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Trash
OF1 | 18 | U1 | 2017-04-01 00:54 |  |  |  |  | 2017-04-14 10:14 |  | 0 | 0 | 321.333 | 321.3333 | 2249.333 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830highwater
OF1 | 19 | U1 | 2017-04-29 05:29 |  |  |  |  | 2017-05-18 12:53 |  | 0 | 0 | 463.4 | 463.4 | 3243.8 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820HIGH WATER
OF1 | 20 | U1 | 2017-05-25 22:19 |  |  |  |  | 2017-05-31 10:00 |  | 0 | 0 | 131.683 | 131.6833 | 921.783 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830highwater
OF1 | 21 | U1 | 2017-06-10 14:55 |  |  |  |  | 2017-06-11 09:06 |  | 0 | 0 | 18.183 | 18.1833 | 145.467 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830LOW RIVER CONDITIONS
OF1 | 22 | U1 | 2017-06-11 09:34 |  |  |  |  | 2017-06-11 10:17 |  | 0 | 0 | 0.717 | 0.7167 | 5.733 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 4552 |  |  | - |  | Generator lube oil system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820LOW OIL FLOW
OF1 | 23 | U1 | 2017-06-24 21:48 |  |  |  |  | 2017-06-29 06:56 |  | 0 | 0 | 105.133 | 105.1333 | 841.067 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820HIGH WATER
OF1 | 27 | U1 | 2017-07-22 07:07 |  |  |  |  | 2017-07-23 06:34 |  | 0 | 0 | 23.45 | 23.45 | 187.6 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF1 | 28 | U1 | 2017-07-24 10:38 |  |  |  |  | 2017-07-24 11:15 |  | 0 | 0 | 0.617 | 0.6167 | 4.933 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 4650 |  |  | - |  | Other cooling system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Clogged strainers
OF1 | 30 | U1 | 2017-08-04 21:59 |  |  |  |  | 2017-08-07 10:14 |  | 0 | 0 | 60.25 | 60.25 | 482 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF1 | 31 | U1 | 2017-08-07 15:11 |  |  |  |  | 2017-08-10 07:16 |  | 0 | 0 | 64.083 | 64.0833 | 512.666 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF1 | 32 | U1 | 2017-08-13 01:14 |  |  |  |  | 2017-08-14 08:49 |  | 0 | 0 | 31.583 | 31.5833 | 252.666 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF1 | 33 | U1 | 2017-08-15 06:19 |  |  |  |  | 2017-08-16 09:56 |  | 0 | 0 | 27.617 | 27.6167 | 220.934 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF1 | 34 | U1 | 2017-08-18 11:41 |  |  |  |  | 2017-08-19 08:57 |  | 0 | 0 | 21.267 | 21.2667 | 170.133 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF1 | 35 | U1 | 2017-08-21 09:10 |  |  |  |  | 2017-08-24 07:31 |  | 0 | 0 | 70.35 | 70.35 | 562.8 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF1 | 36 | U1 | 2017-08-25 18:45 |  |  |  |  | 2017-09-02 07:27 |  | 0 | 0 | 180.7 | 180.7 | 1414.15 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF1 | 37 | U1 | 2017-09-03 08:31 |  |  |  |  | 2017-09-06 13:17 |  | 0 | 0 | 76.767 | 76.7667 | 537.366 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF1 | 38 | U1 | 2017-09-09 07:05 |  |  |  |  | 2017-09-13 12:04 |  | 0 | 0 | 100.983 | 100.9833 | 706.884 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF1 | 39 | U1 | 2017-09-14 21:09 |  |  |  |  | 2017-10-04 07:34 |  | 0 | 0 | 466.417 | 466.4167 | 3264.917 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low flow
OF1 | 40 | U1 | 2017-10-06 15:01 |  |  |  |  | 2017-10-09 09:44 |  | 0 | 0 | 66.717 | 66.7167 | 467.016 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF1 | 41 | U1 | 2017-10-15 12:49 |  |  |  |  | 2017-10-15 15:18 |  | 0 | 0 | 2.483 | 2.4833 | 17.383 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 3974 |  |  | - |  | DCS - logic problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Loss of signal from tail water sensor.
OF1 | 42 | U1 | 2017-10-15 15:18 |  |  |  |  | 2017-10-26 08:03 |  | 0 | 0 | 256.75 | 256.75 | 1797.25 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | FR
|  | DESCRIPTION : |  | F830Low Flow
OF1 | 43 | U1 | 2017-11-06 09:40 |  |  |  |  | 2017-11-13 11:49 |  | 0 | 0 | 170.15 | 170.15 | 1191.05 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830High River
OF1 | 44 | U1 | 2017-11-20 10:33 |  |  |  |  | 2017-11-24 08:55 |  | 0 | 0 | 94.367 | 94.3667 | 660.567 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Shutdown for Highwater
OF1 | 45 | U1 | 2017-12-04 13:28 |  |  |  |  | 2017-12-06 08:08 |  | 0 | 0 | 42.667 | 42.6667 | 213.334 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low water flow
OF1 | 46 | U1 | 2017-12-11 15:48 |  |  |  |  | 2017-12-21 13:22 |  | 0 | 0 | 237.567 | 237.5667 | 1187.833 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow ACOE Request shutdown
OF1 | 47 | U1 | 2017-12-25 10:14 |  |  |  |  | 2017-12-28 14:38 |  | 0 | 0 | 76.4 | 76.4 | 382 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830trash
OF1 | 2 | U1 | 2018-01-11 23:31 |  |  |  |  | 2018-01-12 08:27 |  | 0 | 0 | 8.933 | 8.9333 | 44.667 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 7050 |  |  | - |  | Turbine governor | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Low pressure on GPU
OF1 | 3 | U1 | 2018-01-13 21:48 |  |  |  |  | 2018-01-20 13:24 |  | 0 | 0 | 159.6 | 159.6 | 798 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF1 | 4 | U1 | 2018-01-24 07:19 |  |  |  |  | 2018-02-02 11:55 |  | 0 | 0 | 220.6 | 220.6 | 1103 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830highwater
OF1 | 5 | U1 | 2018-02-08 03:17 |  |  |  |  | 2018-03-12 12:13 |  | 0 | 0 | 776.933 | 776.9333 | 4437.1 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Highwater
OF1 | 6 | U1 | 2018-03-19 13:00 |  |  |  |  | 2018-03-20 12:15 |  | 0 | 0 | 23.25 | 23.25 | 162.75 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Trash
OF1 | 7 | U1 | 2018-03-23 12:03 |  |  |  |  | 2018-04-15 13:38 |  | 0 | 0 | 553.583 | 553.5833 | 3875.083 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830highwater
OF1 | 8 | U1 | 2018-04-16 11:46 |  |  |  |  | 2018-05-01 08:00 |  | 0 | 0 | 356.233 | 356.2333 | 2493.633 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF1 | 9 | U1 | 2018-05-04 10:04 |  |  |  |  | 2018-05-04 12:55 |  | 0 | 0 | 2.85 | 2.85 | 19.95 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Trash intakes
OF1 | 10 | U1 | 2018-05-08 05:30 |  |  |  |  | 2018-05-12 10:28 |  | 0 | 0 | 100.967 | 100.9667 | 706.767 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF1 | 11 | U1 | 2018-05-17 09:33 |  |  |  |  | 2018-05-17 13:05 |  | 0 | 0 | 3.533 | 3.5333 | 24.733 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Trash
OF1 | 12 | U1 | 2018-05-19 08:39 |  |  |  |  | 2018-05-28 10:28 |  | 0 | 0 | 217.817 | 217.8167 | 1524.717 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830high water
OF1 | 13 | U1 | 2018-05-31 08:40 |  |  |  |  | 2018-05-31 13:11 |  | 0 | 0 | 4.517 | 4.5167 | 31.617 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830trash
OF1 | 16 | U1 | 2018-06-23 06:39 |  |  |  |  | 2018-06-28 12:29 |  | 0 | 0 | 125.833 | 125.8333 | 1006.667 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF1 | 17 | U1 | 2018-06-29 10:50 |  |  |  |  | 2018-07-03 10:09 |  | 0 | 0 | 95.317 | 95.3167 | 762.533 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Highwater
OF1 | 18 | U1 | 2018-07-11 05:47 |  |  |  |  | 2018-07-16 13:26 |  | 0 | 0 | 127.65 | 127.65 | 1021.2 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF1 | 19 | U1 | 2018-07-16 16:23 |  |  |  |  | 2018-07-21 09:45 |  | 0 | 0 | 113.367 | 113.3667 | 906.933 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low water
OF1 | 21 | U1 | 2018-08-08 15:00 |  |  |  |  | 2018-08-13 06:40 |  | 0 | 0 | 111.667 | 111.6667 | 893.333 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | NF
|  | DESCRIPTION : |  | F830Low Flow
OF1 | 22 | U1 | 2018-08-15 13:46 |  |  |  |  | 2018-08-16 07:50 |  | 0 | 0 | 18.067 | 18.0667 | 144.534 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low flow
OF1 | 23 | U1 | 2018-08-20 07:46 |  |  |  |  | 2018-08-20 15:16 |  | 0 | 0 | 7.5 | 7.5 | 60 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830trash
OF1 | 24 | U1 | 2018-08-26 17:50 |  |  |  |  | 2018-09-17 13:00 |  | 0 | 0 | 523.167 | 523.1667 | 3788.333 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF1 | 25 | U1 | 2018-09-19 00:03 |  |  |  |  | 2018-10-04 13:02 |  | 0 | 0 | 372.983 | 372.9833 | 2610.883 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Highwater
OF1 | 26 | U1 | 2018-10-07 09:01 |  |  |  |  | 2018-10-11 16:55 |  | 0 | 0 | 103.9 | 103.9 | 727.3 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Trash
OF1 | 27 | U1 | 2018-10-11 16:59 |  |  |  |  | 2018-10-12 13:26 |  | 0 | 0 | 20.45 | 20.45 | 143.15 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Trash too great for operation
OF1 | 28 | U1 | 2018-10-13 11:22 |  |  |  |  | 2018-10-14 19:37 |  | 0 | 0 | 32.25 | 32.25 | 225.75 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Trash
OF1 | 31 | U1 | 2018-11-01 12:43 |  |  |  |  | 2018-12-09 17:12 |  | 0 | 0 | 916.483 | 916.4833 | 5996.983 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF1 | 32 | U1 | 2018-12-17 00:21 |  |  |  |  | 2019-01-01 |  | 0 | 0 | 359.65 | 359.65 | 1798.25 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF1 | 1 | U1 | 2019-01-01 |  |  |  |  | 2019-01-15 09:12 |  | 0 | 0 | 345.2 | 345.2 | 1726 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | Shut down for high water.
OF1 | 2 | U1 | 2019-01-16 19:17 |  |  |  |  | 2019-01-17 10:17 |  | 0 | 0 | 15 | 15 | 75 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | Shut down to clean trash racks.
OF1 | 3 | U1 | 2019-01-20 04:00 |  |  |  |  | 2019-01-31 23:59 |  | 0 | 0 | 283.983 | 283.9833 | 1419.917 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | Shut down for high water.
OF1 | 4 | U1 | 2019-02-01 |  |  |  |  | 2019-02-03 15:44 |  | 0 | 0 | 63.733 | 63.7333 | 318.667 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | Shut down for high water.
OF1 | 5 | U1 | 2019-02-04 10:51 |  |  |  |  | 2019-02-04 14:37 |  | 0 | 0 | 3.767 | 3.7667 | 18.833 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | Shut down to clean trash racks.
OF1 | 6 | U1 | 2019-02-06 07:05 |  |  |  |  | 2019-03-08 11:32 |  | 0 | 0 | 724.45 | 724.45 | 3981.316 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF1 | 7 | U1 | 2019-03-08 12:49 |  |  |  |  | 2019-03-22 11:58 |  | 0 | 0 | 335.15 | 335.15 | 2346.05 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF1 | 8 | U1 | 2019-03-23 07:43 |  |  |  |  | 2019-03-26 13:50 |  | 0 | 0 | 78.117 | 78.1167 | 546.816 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Trash
OF1 | 9 | U1 | 2019-03-26 21:39 |  |  |  |  | 2019-03-27 15:27 |  | 0 | 0 | 17.8 | 17.8 | 124.6 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Trash
OF1 | 10 | U1 | 2019-03-28 03:26 |  |  |  |  | 2019-03-28 06:48 |  | 0 | 0 | 3.367 | 3.3667 | 23.567 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7008 |  |  | - |  | Bearing cooling system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820LV Bearing Cooling water flow trip
OF1 | 12 | U1 | 2019-03-31 06:30 |  |  |  |  | 2019-04-02 13:37 |  | 0 | 0 | 55.117 | 55.1167 | 385.817 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Trash in front of unit, tripped unit
OF1 | 13 | U1 | 2019-04-02 23:46 |  |  |  |  | 2019-04-03 12:17 |  | 0 | 0 | 12.517 | 12.5167 | 87.616 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Highwater
OF1 | 14 | U1 | 2019-04-03 22:12 |  |  |  |  | 2019-04-04 11:59 |  | 0 | 0 | 13.783 | 13.7833 | 96.483 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820trash
OF1 | 15 | U1 | 2019-04-04 13:05 |  |  |  |  | 2019-04-04 19:30 |  | 0 | 0 | 6.417 | 6.4167 | 44.917 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830trash
OF1 | 16 | U1 | 2019-04-05 04:37 |  |  |  |  | 2019-04-05 16:26 |  | 0 | 0 | 11.817 | 11.8167 | 82.717 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820trash
OF1 | 17 | U1 | 2019-04-06 07:52 |  |  |  |  | 2019-04-06 16:15 |  | 0 | 0 | 8.383 | 8.3833 | 58.683 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830trash
OF1 | 19 | U1 | 2019-04-13 08:38 |  |  |  |  | 2019-04-13 09:46 |  | 0 | 0 | 1.133 | 1.1333 | 7.933 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830trash
OF1 | 20 | U1 | 2019-04-15 14:49 |  |  |  |  | 2019-05-11 08:54 |  | 0 | 0 | 618.083 | 618.0833 | 4326.583 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Trash
OF1 | 21 | U1 | 2019-05-12 15:32 |  |  |  |  | 2019-05-12 16:45 |  | 0 | 0 | 1.217 | 1.2167 | 8.517 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Run of river
OF1 | 22 | U1 | 2019-05-12 21:50 |  |  |  |  | 2019-05-21 10:29 |  | 0 | 0 | 204.65 | 204.65 | 1432.55 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Trash
OF1 | 23 | U1 | 2019-05-22 08:55 |  |  |  |  | 2019-05-22 13:34 |  | 0 | 0 | 4.65 | 4.65 | 32.55 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830trash
OF1 | 24 | U1 | 2019-05-31 13:12 |  |  |  |  | 2019-06-05 16:21 |  | 0 | 0 | 123.15 | 123.15 | 974.4 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF1 | 25 | U1 | 2019-06-09 13:28 |  |  |  |  | 2019-06-11 14:31 |  | 0 | 0 | 49.05 | 49.05 | 392.4 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF1 | 26 | U1 | 2019-06-16 21:14 |  |  |  |  | 2019-06-28 15:00 |  | 0 | 0 | 281.767 | 281.7667 | 2254.133 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820highwater
OF1 | 27 | U1 | 2019-06-29 08:58 |  |  |  |  | 2019-06-29 13:53 |  | 0 | 0 | 4.917 | 4.9167 | 39.333 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Trash
OF1 | 28 | U1 | 2019-07-01 20:05 |  |  |  |  | 2019-07-02 14:28 |  | 0 | 0 | 18.383 | 18.3833 | 147.066 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Trash
OF1 | 29 | U1 | 2019-07-19 07:26 |  |  |  |  | 2019-07-19 13:51 |  | 0 | 0 | 6.417 | 6.4167 | 51.333 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Drift wood clogging intakes
OF1 | 30 | U1 | 2019-07-22 08:43 |  |  |  |  | 2019-07-22 15:11 |  | 0 | 0 | 6.467 | 6.4667 | 51.733 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Trash buildup
OF1 | 31 | U1 | 2019-07-23 03:45 |  |  |  |  | 2019-07-23 15:50 |  | 0 | 0 | 12.083 | 12.0833 | 96.667 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Trash
OF1 | 32 | U1 | 2019-07-27 08:15 |  |  |  |  | 2019-07-27 13:55 |  | 0 | 0 | 5.667 | 5.6667 | 45.333 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830trash
OF1 | 33 | U1 | 2019-07-28 14:23 |  |  |  |  | 2019-10-08 07:38 |  | 0 | 0 | 1721.25 | 1721.25 | 12874.366 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low water
OF1 | 34 | U1 | 2019-10-09 06:59 |  |  |  |  | 2019-10-30 07:18 |  | 0 | 0 | 504.317 | 504.3167 | 3530.217 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Water, Offline by request from ACOE
OF1 | 36 | U1 | 2019-11-17 04:47 |  |  |  |  | 2019-11-23 10:13 |  | 0 | 0 | 149.433 | 149.4333 | 1046.034 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF1 | 37 | U1 | 2019-12-02 14:59 |  |  |  |  | 2019-12-06 10:57 |  | 0 | 0 | 91.967 | 91.9667 | 459.833 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF1 | 38 | U1 | 2019-12-13 22:22 |  |  |  |  | 2019-12-24 13:50 |  | 0 | 0 | 255.467 | 255.4667 | 1277.334 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Trash and Highwater, due to high water and the amount of trash in front of the uni
OF1 | 39 | U1 | 2019-12-31 07:34 |  |  |  |  | 2019-12-31 23:59 |  | 0 | 0 | 16.417 | 16.4167 | 82.083 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF1 | 1 | U1 | 2020-01-01 |  |  |  |  | 2020-01-18 14:25 |  | 0 | 0 | 422.417 | 422.4167 | 2112.083 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Highwater
OF1 | 2 | U1 | 2020-01-21 09:42 |  |  |  |  | 2020-01-24 10:58 |  | 0 | 0 | 73.267 | 73.2667 | 366.333 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for highwater
OF1 | 3 | U1 | 2020-01-27 06:52 |  |  |  |  | 2020-02-01 14:36 |  | 0 | 0 | 127.733 | 127.7333 | 638.667 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830High River
OF1 | 4 | U1 | 2020-02-07 22:04 |  |  |  |  | 2020-02-24 11:22 |  | 0 | 0 | 397.3 | 397.3 | 1986.5 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Highwater
OF1 | 5 | U1 | 2020-03-02 06:59 |  |  |  |  | 2020-03-10 13:02 |  | 0 | 0 | 198.05 | 198.05 | 1386.35 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Trash
OF1 | 6 | U1 | 2020-03-13 19:11 |  |  |  |  | 2020-04-06 13:13 |  | 0 | 0 | 570.033 | 570.0333 | 3990.234 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830High River
OF1 | 7 | U1 | 2020-04-10 14:54 |  |  |  |  | 2020-04-22 13:28 |  | 0 | 0 | 286.567 | 286.5667 | 2005.967 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF1 | 8 | U1 | 2020-04-26 10:59 |  |  |  |  | 2020-05-12 13:52 |  | 0 | 0 | 386.883 | 386.8833 | 2708.184 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830High River
OF1 | 9 | U1 | 2020-05-19 10:14 |  |  |  |  | 2020-05-30 10:31 |  | 0 | 0 | 264.283 | 264.2833 | 1849.984 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF1 | 10 | U1 | 2020-05-31 18:47 |  |  |  |  | 2020-06-03 07:51 |  | 0 | 0 | 61.067 | 61.0667 | 483.317 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Offline for Trash
OF1 | 11 | U1 | 2020-06-04 09:48 |  |  |  |  | 2020-06-04 12:57 |  | 0 | 0 | 3.15 | 3.15 | 25.2 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 3710 |  |  | - |  | Transmission line (connected to powerhouse switchyard to 1st Substation) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Transformer Outage
OF1 | 12 | U1 | 2020-06-04 14:17 |  |  |  |  | 2020-06-17 12:51 |  | 0 | 0 | 310.567 | 310.5667 | 2484.533 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 3710 |  |  | - |  | Transmission line (connected to powerhouse switchyard to 1st Substation) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Transmission Outage
OF1 | 13 | U1 | 2020-06-26 06:12 |  |  |  |  | 2020-06-26 12:50 |  | 0 | 0 | 6.633 | 6.6333 | 53.067 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9350 |  |  | - |  | Public Safety (water hazard or river rescue) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F590ACOE requested shutdown for safety while they are working on the lower dam.
OF1 | 14 | U1 | 2020-06-28 09:25 |  |  |  |  | 2020-06-29 09:59 |  | 0 | 0 | 24.567 | 24.5667 | 196.534 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9001 |  |  | - |  | Drought | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow, ACOE requested Shutdown
OF1 | 15 | U1 | 2020-07-06 10:17 |  |  |  |  | 2020-07-10 09:26 |  | 0 | 0 | 95.15 | 95.15 | 761.2 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Low Flow (ACOE Request)
OF1 | 16 | U1 | 2020-07-11 09:39 |  |  |  |  | 2020-07-14 10:52 |  | 0 | 0 | 73.217 | 73.2167 | 585.733 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow, ACOE rquest offline
OF1 | 17 | U1 | 2020-07-16 03:43 |  |  |  |  | 2020-07-16 09:39 |  | 0 | 0 | 5.933 | 5.9333 | 47.467 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF1 | 18 | U1 | 2020-07-16 14:50 |  |  |  |  | 2020-07-17 07:59 |  | 0 | 0 | 17.15 | 17.15 | 137.2 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low flow
OF1 | 19 | U1 | 2020-07-17 13:54 |  |  |  |  | 2020-07-20 11:58 |  | 0 | 0 | 70.067 | 70.0667 | 560.533 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low flow.
OF1 | 20 | U1 | 2020-07-21 05:52 |  |  |  |  | 2020-07-22 09:06 |  | 0 | 0 | 27.233 | 27.2333 | 217.867 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Low Flow (ACOE Request)
OF1 | 21 | U1 | 2020-07-23 06:14 |  |  |  |  | 2020-07-24 13:25 |  | 0 | 0 | 31.183 | 31.1833 | 249.466 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Lack of Water (ACOE Requested)
OF1 | 22 | U1 | 2020-07-27 10:22 |  |  |  |  | 2020-07-31 07:21 |  | 0 | 0 | 92.983 | 92.9833 | 743.867 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low flow ACOE
OF1 | 23 | U1 | 2020-08-04 07:08 |  |  |  |  | 2020-08-04 10:15 |  | 0 | 0 | 3.117 | 3.1167 | 24.933 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Trash
OF1 | 24 | U1 | 2020-08-04 19:34 |  |  |  |  | 2020-08-06 06:54 |  | 0 | 0 | 35.333 | 35.3333 | 282.667 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Lack of Water (ACOE Request)
OF1 | 25 | U1 | 2020-08-07 14:40 |  |  |  |  | 2020-08-08 10:41 |  | 0 | 0 | 20.017 | 20.0167 | 160.134 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830lack of water (request by ACOE)
OF1 | 26 | U1 | 2020-08-10 06:38 |  |  |  |  | 2020-08-11 08:43 |  | 0 | 0 | 26.083 | 26.0833 | 208.666 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF1 | 27 | U1 | 2020-08-20 08:11 |  |  |  |  | 2020-09-04 08:25 |  | 0 | 0 | 360.233 | 360.2333 | 2801.45 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Lack of Water (ACOE)
OF1 | 28 | U1 | 2020-09-08 08:15 |  |  |  |  | 2020-09-09 09:48 |  | 0 | 0 | 25.55 | 25.55 | 178.85 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF1 | 29 | U1 | 2020-09-12 18:26 |  |  |  |  | 2020-09-15 06:33 |  | 0 | 0 | 60.117 | 60.1167 | 420.817 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Lack of water.
OF1 | 30 | U1 | 2020-09-15 11:59 |  |  |  |  | 2020-09-15 15:21 |  | 0 | 0 | 3.367 | 3.3667 | 23.567 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for trash.
OF1 | 31 | U1 | 2020-09-16 06:26 |  |  |  |  | 2020-10-03 09:05 |  | 0 | 0 | 410.65 | 410.65 | 2874.55 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for trash.
OF1 | 32 | U1 | 2020-10-03 21:47 |  |  |  |  | 2020-10-29 12:21 |  | 0 | 0 | 614.567 | 614.5667 | 4301.967 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for lack of water.
OF1 | 33 | U1 | 2020-11-01 05:30 |  |  |  |  | 2020-11-02 15:04 |  | 0 | 0 | 33.567 | 33.5667 | 234.967 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820offline for trash
OF1 | 34 | U1 | 2020-11-05 12:53 |  |  |  |  | 2020-11-05 16:46 |  | 0 | 0 | 3.883 | 3.8833 | 27.183 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 3710 |  |  | - |  | Transmission line (connected to powerhouse switchyard to 1st Substation) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Switching Bus
OF1 | 35 | U1 | 2020-11-11 08:15 |  |  |  |  | 2020-11-16 12:00 |  | 0 | 0 | 123.75 | 123.75 | 866.25 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow (ACOE)
OF1 | 38 | U1 | 2020-12-27 10:19 |  |  |  |  | 2021-01-01 |  | 0 | 0 | 109.683 | 109.6833 | 548.417 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Highwater
OF1 | 1 | U1 | 2021-01-01 |  |  |  |  | 2021-01-11 12:04 |  | 0 | 0 | 252.067 | 252.0667 | 3176.04 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for highwater
OF1 | 3 | U1 | 2021-01-27 12:36 |  |  |  |  | 2021-02-05 11:31 |  | 0 | 0 | 214.917 | 214.9167 | 2707.95 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Highwater
OF1 | 4 | U1 | 2021-02-22 13:09 |  |  |  |  | 2021-03-15 07:50 |  | 0 | 0 | 498.683 | 498.6833 | 6283.41 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF1 | 5 | U1 | 2021-03-17 04:50 |  |  |  |  | 2021-03-24 10:08 |  | 0 | 0 | 173.3 | 173.3 | 2183.58 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Trash Differential - Highwater
OF1 | 6 | U1 | 2021-03-29 12:58 |  |  |  |  | 2021-04-06 07:11 |  | 0 | 0 | 186.217 | 186.2167 | 2346.33 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Highwater
OF1 | 7 | U1 | 2021-04-07 07:33 |  |  |  |  | 2021-04-07 07:53 |  | 0 | 0 | 0.333 | 0.3333 | 4.2 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 3972 |  |  | - |  | DCS - hardware problems (including card failure) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Meiners Breaker issue
OF1 | 8 | U1 | 2021-04-07 07:54 |  |  |  |  | 2021-04-07 08:19 |  | 0 | 0 | 0.417 | 0.4167 | 5.25 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 3972 |  |  | - |  | DCS - hardware problems (including card failure) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Meiners Breaker Issue
OF1 | 13 | U1 | 2021-05-27 23:20 |  |  |  |  | 2021-06-04 06:42 |  | 0 | 0 | 175.367 | 175.3667 | 2209.62 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for lack of water.
OF1 | 14 | U1 | 2021-06-06 16:14 |  |  |  |  | 2021-06-07 07:52 |  | 0 | 0 | 15.633 | 15.6333 | 196.98 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Lack of water.
OF1 | 15 | U1 | 2021-06-08 19:01 |  |  |  |  | 2021-06-10 07:12 |  | 0 | 0 | 36.183 | 36.1833 | 455.91 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit1 requested to be taken off by ACOE
OF1 | 16 | U1 | 2021-06-13 07:45 |  |  |  |  | 2021-06-15 13:51 |  | 0 | 0 | 54.1 | 54.1 | 681.66 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit taken offline @ 0745 for trash, Unit ran until 0.0 MW, then shut down
OF1 | 17 | U1 | 2021-06-16 02:02 |  |  |  |  | 2021-06-21 09:23 |  | 0 | 0 | 127.35 | 127.35 | 1604.61 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Offline for trash.
OF1 | 18 | U1 | 2021-06-23 06:43 |  |  |  |  | 2021-06-25 12:48 |  | 0 | 0 | 54.083 | 54.0833 | 681.45 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Excessive trash build up in front of Unit trashracks.
OF1 | 19 | U1 | 2021-06-26 13:56 |  |  |  |  | 2021-06-28 09:19 |  | 0 | 0 | 43.383 | 43.3833 | 546.63 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830ACOE requested, Lack of Water
OF1 | 20 | U1 | 2021-06-29 06:02 |  |  |  |  | 2021-07-01 07:35 |  | 0 | 0 | 49.55 | 49.55 | 624.33 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Lack of Water, Run of River per ACOE
OF1 | 22 | U1 | 2021-07-03 06:32 |  |  |  |  | 2021-07-06 06:41 |  | 0 | 0 | 72.15 | 72.15 | 909.09 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for trash
OF1 | 25 | U1 | 2021-12-08 07:01 |  |  |  |  | 2021-12-10 11:10 |  | 0 | 0 | 52.15 | 52.15 | 657.09 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Run of River - Highwater
OF1 | 26 | U1 | 2021-12-11 01:36 |  |  |  |  | 2021-12-15 08:23 |  | 0 | 0 | 102.783 | 102.7833 | 1295.07 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 4609 |  |  | - |  | Other exciter problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Field Ground Detected
OF1 | 27 | U1 | 2021-12-31 09:45 |  |  |  |  | 2022-01-01 |  | 0 | 0 | 14.25 | 14.25 | 179.55 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830High Water.
OF1 | 1 | U1 | 2022-01-01 |  |  |  |  | 2022-01-16 11:32 |  | 0 | 0 | 371.533 | 371.5333 | 4681.32 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for High Water.
OF1 | 2 | U1 | 2022-01-17 13:39 |  |  |  |  | 2022-01-17 14:56 |  | 0 | 0 | 1.283 | 1.2833 | 16.17 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 4551 |  |  | - |  | Generator bearings | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F780Intermediate Guide Bearing had sudden increase in Temp./ Exceeded normal operation
OF1 | 3 | U1 | 2022-02-04 05:35 |  |  |  |  | 2022-02-14 15:08 |  | 0 | 0 | 249.55 | 249.55 | 3144.33 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for High Water
OF1 | 4 | U1 | 2022-02-17 20:07 |  |  |  |  | 2022-03-21 07:09 |  | 0 | 0 | 755.033 | 755.0333 | 9513.42 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for High Water (Run of River)
OF1 | 5 | U1 | 2022-03-31 10:42 |  |  |  |  | 2022-03-31 11:54 |  | 0 | 0 | 1.2 | 1.2 | 15.12 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Lack of Water (ACOE)
OF1 | 6 | U1 | 2022-04-09 04:23 |  |  |  |  | 2022-04-18 07:51 |  | 0 | 0 | 219.467 | 219.4667 | 2765.28 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for High Water
OF1 | 7 | U1 | 2022-04-22 04:28 |  |  |  |  | 2022-04-25 07:09 |  | 0 | 0 | 74.683 | 74.6833 | 941.01 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Offline for High Water.
OF1 | 8 | U1 | 2022-05-07 08:06 |  |  |  |  | 2022-05-16 09:52 |  | 0 | 0 | 217.767 | 217.7667 | 2743.86 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for High Water.
OF1 | 9 | U1 | 2022-05-25 07:04 |  |  |  |  | 2022-05-25 13:29 |  | 0 | 0 | 6.417 | 6.4167 | 80.85 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for trash.
OF1 | 10 | U1 | 2022-05-29 14:13 |  |  |  |  | 2022-06-01 09:38 |  | 0 | 0 | 67.417 | 67.4167 | 849.45 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Trash.
OF1 | 11 | U1 | 2022-06-08 05:24 |  |  |  |  | 2022-06-09 06:56 |  | 0 | 0 | 25.533 | 25.5333 | 321.72 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Trash
OF1 | 12 | U1 | 2022-06-13 14:52 |  |  |  |  | 2022-06-13 17:16 |  | 0 | 0 | 2.4 | 2.4 | 30.24 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 4740 |  |  | - |  | Emergency generator trip devices | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Emergency Generator Trip, (Condensation from water pipe)
OF1 | 13 | U1 | 2022-06-22 14:15 |  |  |  |  | 2022-06-24 09:31 |  | 0 | 0 | 43.267 | 43.2667 | 545.16 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Lack of Water (Run of River) by the ACOE
OF1 | 14 | U1 | 2022-06-25 09:28 |  |  |  |  | 2022-06-28 08:47 |  | 0 | 0 | 71.317 | 71.3167 | 898.59 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Lack of Water-Run of River per the ACOE
OF1 | 15 | U1 | 2022-06-30 06:38 |  |  |  |  | 2022-07-07 08:41 |  | 0 | 0 | 170.05 | 170.05 | 2142.63 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for lack of water.
OF1 | 16 | U1 | 2022-07-13 12:04 |  |  |  |  | 2022-07-19 07:19 |  | 0 | 0 | 139.25 | 139.25 | 1754.55 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Lack of Water (Run of River) per The ACOE
OF1 | 17 | U1 | 2022-07-22 13:58 |  |  |  |  | 2022-07-25 06:49 |  | 0 | 0 | 64.85 | 64.85 | 817.11 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Lack of Water (Run of River) per the ACOE
OF1 | 19 | U1 | 2022-08-02 06:52 |  |  |  |  | 2022-08-02 13:55 |  | 0 | 0 | 7.05 | 7.05 | 88.83 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Trash
OF1 | 21 | U1 | 2022-08-23 11:00 |  |  |  |  | 2022-08-23 14:18 |  | 0 | 0 | 3.3 | 3.3 | 41.58 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Trash (Run of River)
OF1 | 22 | U1 | 2022-08-28 13:06 |  |  |  |  | 2022-08-29 16:40 |  | 0 | 0 | 27.567 | 27.5667 | 347.34 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Lack of Water.
OF1 | 23 | U1 | 2022-08-29 16:40 |  |  |  |  | 2022-08-30 12:56 |  | 0 | 0 | 20.267 | 20.2667 | 255.36 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 3672 |  |  | - |  | 12-15kV conductors and buses | [8 empty] | AMP CODE: |  | 49
|  | DESCRIPTION : |  | F49014KV Bus A lockout
OF1 | 24 | U1 | 2022-08-30 12:56 |  |  |  |  | 2022-09-04 08:34 |  | 0 | 0 | 115.633 | 115.6333 | 1456.98 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | FR
|  | DESCRIPTION : |  | F830Lack of water
OF1 | 25 | U1 | 2022-09-04 16:00 |  |  |  |  | 2022-09-06 09:26 |  | 0 | 0 | 41.433 | 41.4333 | 522.06 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Lack of Water.
OF1 | 26 | U1 | 2022-09-06 14:14 |  |  |  |  | 2022-09-07 07:27 |  | 0 | 0 | 17.217 | 17.2167 | 216.93 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Trash / Run of River
OF1 | 27 | U1 | 2022-09-13 07:16 |  |  |  |  | 2022-09-14 10:05 |  | 0 | 0 | 26.817 | 26.8167 | 337.89 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Trash
OF1 | 28 | U1 | 2022-09-16 10:58 |  |  |  |  | 2022-09-28 08:00 |  | 0 | 0 | 285.033 | 285.0333 | 3591.42 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Lack of Water
OF1 | 29 | U1 | 2022-09-29 01:08 |  |  |  |  | 2022-09-30 08:46 |  | 0 | 0 | 31.633 | 31.6333 | 398.58 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830lack of water
OF1 | 30 | U1 | 2022-10-07 17:56 |  |  |  |  | 2022-11-12 14:21 |  | 0 | 0 | 860.417 | 860.4167 | 10841.25 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Lack of Water.
OF1 | 31 | U1 | 2022-11-26 01:00 |  |  |  |  | 2022-11-28 07:40 |  | 0 | 0 | 54.667 | 54.6667 | 688.8 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Lack of Water
OF1 | 32 | U1 | 2022-12-11 08:08 |  |  |  |  | 2022-12-12 14:58 |  | 0 | 0 | 30.833 | 30.8333 | 388.5 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830trash
OF1 | 33 | U1 | 2022-12-23 04:32 |  |  |  |  | 2022-12-27 14:40 |  | 0 | 0 | 106.133 | 106.1333 | 1337.28 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9036 |  |  | - |  | "Storms (ice, snow, etc)" | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Army Corps gates not operating due to freezing temperatures. Unit shut down to mai
OF1 | 34 | U1 | 2022-12-27 15:57 |  |  |  |  | 2022-12-29 14:34 |  | 0 | 0 | 46.617 | 46.6167 | 587.37 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Lack of Water
OF1 | 35 | U1 | 2022-12-30 07:14 |  |  |  |  | 2023-01-01 |  | 0 | 0 | 40.767 | 40.7667 | 513.66 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Trash
OF1 | 1 | U1 | 2023-01-01 |  |  |  |  | 2023-01-09 11:09 |  | 0 | 0 | 203.15 | 203.15 | 2559.69 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Trash
OF1 | 2 | U1 | 2023-01-13 04:38 |  |  |  |  | 2023-01-24 08:13 |  | 0 | 0 | 267.583 | 267.5833 | 3371.55 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820trash
OF1 | 4 | U1 | 2023-01-25 14:40 |  |  |  |  | 2023-01-27 14:25 |  | 0 | 0 | 47.75 | 47.75 | 601.65 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | FR
|  | DESCRIPTION : |  | F820Offline for Trash.
OF1 | 5 | U1 | 2023-01-29 04:52 |  |  |  |  | 2023-01-30 07:48 |  | 0 | 0 | 26.933 | 26.9333 | 339.36 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Offline for high water.
OF1 | 6 | U1 | 2023-02-03 12:07 |  |  |  |  | 2023-02-07 11:50 |  | 0 | 0 | 95.717 | 95.7167 | 1206.03 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9320 |  |  | - |  | Other miscellaneous external problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830barge recovery
OF1 | 8 | U1 | 2023-02-17 08:54 |  |  |  |  | 2023-02-24 15:00 |  | 0 | 0 | 174.1 | 174.1 | 2193.66 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Unit offline for High Water
OF1 | 9 | U1 | 2023-03-02 19:48 |  |  |  |  | 2023-03-13 12:39 |  | 0 | 0 | 256.85 | 256.85 | 3236.31 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for High Water
OF1 | 10 | U1 | 2023-03-14 20:51 |  |  |  |  | 2023-03-15 06:47 |  | 0 | 0 | 9.933 | 9.9333 | 125.16 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7009 |  |  | - |  | Bearing oil system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820IGB pad 1 high high temp
OF1 | 11 | U1 | 2023-03-15 06:56 |  |  |  |  | 2023-03-16 09:54 |  | 0 | 0 | 26.967 | 26.9667 | 339.78 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7009 |  |  | - |  | Bearing oil system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820low oil alarm
OF1 | 12 | U1 | 2023-03-16 14:47 |  |  |  |  | 2023-03-20 10:45 |  | 0 | 0 | 91.967 | 91.9667 | 1158.78 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7009 |  |  | - |  | Bearing oil system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820low oil alarm
OF1 | 13 | U1 | 2023-03-24 20:12 |  |  |  |  | 2023-04-11 06:30 |  | 0 | 0 | 418.3 | 418.3 | 5270.58 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Offline for High Water.
OF1 | 14 | U1 | 2023-04-11 06:30 |  |  |  |  | 2023-04-28 13:46 |  | 0 | 0 | 415.267 | 415.2667 | 5232.36 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9320 |  |  | - |  | Other miscellaneous external problems | [8 empty] | AMP CODE: |  | FR
|  | DESCRIPTION : |  | FX00Barge Recovery
OF1 | 15 | U1 | 2023-05-07 06:12 |  |  |  |  | 2023-05-11 12:01 |  | 0 | 0 | 101.817 | 101.8167 | 1282.89 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Trash
OF1 | 16 | U1 | 2023-05-24 17:42 |  |  |  |  | 2023-05-31 13:34 |  | 0 | 0 | 163.867 | 163.8667 | 2064.72 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Lack of Water
OF1 | 17 | U1 | 2023-06-05 07:16 |  |  |  |  | 2023-06-18 07:12 |  | 0 | 0 | 311.933 | 311.9333 | 3930.36 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830lack of water
OF1 | 18 | U1 | 2023-06-19 18:58 |  |  |  |  | 2023-06-26 07:29 |  | 0 | 0 | 156.517 | 156.5167 | 1972.11 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline lack of water.
OF1 | 19 | U1 | 2023-06-26 07:29 |  |  |  |  | 2023-06-26 16:00 |  | 0 | 0 | 8.517 | 8.5167 | 107.31 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | FR
|  | DESCRIPTION : |  | F530MSI sonar.
OF1 | 20 | U1 | 2023-06-26 16:00 |  |  |  |  | 2023-07-02 07:49 |  | 0 | 0 | 135.817 | 135.8167 | 1711.29 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | FR
|  | DESCRIPTION : |  | F830lack of water
OF1 | 21 | U1 | 2023-07-02 22:11 |  |  |  |  | 2023-07-04 07:45 |  | 0 | 0 | 33.567 | 33.5667 | 422.94 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Lack of Water
OF1 | 22 | U1 | 2023-07-07 07:53 |  |  |  |  | 2023-07-07 13:59 |  | 0 | 0 | 6.1 | 6.1 | 76.86 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Trash
OF1 | 23 | U1 | 2023-07-08 07:18 |  |  |  |  | 2023-07-10 07:28 |  | 0 | 0 | 48.167 | 48.1667 | 606.9 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Lack of Water
OF1 | 24 | U1 | 2023-07-12 15:26 |  |  |  |  | 2023-07-17 08:15 |  | 0 | 0 | 112.817 | 112.8167 | 1421.49 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830lack of water
OF1 | 25 | U1 | 2023-07-18 00:50 |  |  |  |  | 2023-07-19 08:39 |  | 0 | 0 | 31.817 | 31.8167 | 400.89 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline lack of water.
OF1 | 26 | U1 | 2023-07-24 19:02 |  |  |  |  | 2023-07-29 08:36 |  | 0 | 0 | 109.567 | 109.5667 | 1380.54 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Lack of Water
OF1 | 27 | U1 | 2023-07-30 21:11 |  |  |  |  | 2023-08-07 09:00 |  | 0 | 0 | 179.817 | 179.8167 | 2265.69 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for lack of water
OF1 | 29 | U1 | 2023-08-17 16:59 |  |  |  |  | 2023-08-26 09:02 |  | 0 | 0 | 208.05 | 208.05 | 2621.43 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for lack of water
OF1 | 30 | U1 | 2023-08-30 12:03 |  |  |  |  | 2023-09-09 05:30 |  | 0 | 0 | 233.45 | 233.45 | 2941.47 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830lack of water
OF1 | 33 | U1 | 2023-10-02 13:09 |  |  |  |  | 2023-10-12 07:46 |  | 0 | 0 | 234.617 | 234.6167 | 2956.17 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | FR
|  | DESCRIPTION : |  | F830Offline lack of water.
OF1 | 34 | U1 | 2023-10-12 14:55 |  |  |  |  | 2023-10-25 08:14 |  | 0 | 0 | 305.317 | 305.3167 | 3846.99 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830lack of water
OF1 | 35 | U1 | 2023-10-26 06:05 |  |  |  |  | 2023-11-02 07:20 |  | 0 | 0 | 169.25 | 169.25 | 2132.55 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline lack of water.
OF1 | 36 | U1 | 2023-11-02 12:33 |  |  |  |  | 2023-11-22 08:11 |  | 0 | 0 | 475.633 | 475.6333 | 5992.98 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830lack of water
OF1 | 37 | U1 | 2023-11-27 16:47 |  |  |  |  | 2023-11-30 08:40 |  | 0 | 0 | 63.883 | 63.8833 | 804.93 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830lack of water
OF1 | 38 | U1 | 2023-12-03 09:57 |  |  |  |  | 2023-12-05 07:18 |  | 0 | 0 | 45.35 | 45.35 | 571.41 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830lack of water
Ohio Falls - OF2
Unit | Event | Type | Start |  |  |  |  | End |  | GAC | NAC | Duration | Equiv Hrs | Equiv MWH | Cont | Work Start | Work End |  | Hours |  |  | Gross Capacity Impact (MW)
OF2 | 1 | U1 | 2014-01-01 |  |  |  |  | 2015-01-01 |  | 0 | 0 | 8760 | 8760 | 43824 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 7007 |  |  | - |  | Bearings | [8 empty] | AMP CODE: |  | 93
|  | DESCRIPTION : |  | F930Lower Guide Bearing Problem
OF2 | 1 | U1 | 2015-01-01 |  |  |  |  | 2015-11-13 19:12 |  | 0 | 0 | 7603.2 | 7603.2 | 41913.6 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 7007 |  |  | - |  | Bearings | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F930The lower turbine guide bearing and inner head cover failure caused Unit 2 to go o
OF2 | 2 | U1 | 2015-11-13 19:35 |  |  |  |  | 2015-11-14 08:26 |  | 0 | 0 | 12.85 | 12.85 | 102.8 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7200 |  |  | - |  | Major overhaul (use for non-specific overhaul only; see page B-CCGT-2) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Continued testing #2
OF2 | 3 | U1 | 2015-11-14 10:20 |  |  |  |  | 2015-11-14 10:33 |  | 0 | 0 | 0.217 | 0.2167 | 1.733 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7200 |  |  | - |  | Major overhaul (use for non-specific overhaul only; see page B-CCGT-2) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Continued testing #2
OF2 | 4 | U1 | 2015-11-14 10:39 |  |  |  |  | 2015-11-14 10:53 |  | 0 | 0 | 0.233 | 0.2333 | 1.867 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7200 |  |  | - |  | Major overhaul (use for non-specific overhaul only; see page B-CCGT-2) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Continued testing Unit #2
OF2 | 5 | U1 | 2015-11-14 13:04 |  |  |  |  | 2015-11-14 14:26 |  | 0 | 0 | 1.367 | 1.3667 | 10.933 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7200 |  |  | - |  | Major overhaul (use for non-specific overhaul only; see page B-CCGT-2) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Continued Testing Unit #2
OF2 | 7 | U1 | 2015-12-04 00:22 |  |  |  |  | 2015-12-08 10:38 |  | 0 | 0 | 106.267 | 106.2667 | 850.134 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF2 | 9 | U1 | 2015-12-24 09:59 |  |  |  |  | 2015-12-31 23:59 |  | 0 | 0 | 182 | 182 | 1456 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF2 | 1 | U1 | 2016-01-01 |  |  |  |  | 2016-01-05 14:14 |  | 0 | 0 | 110.233 | 110.2333 | 551.167 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820highwater
OF2 | 2 | U1 | 2016-02-03 06:29 |  |  |  |  | 2016-02-11 11:02 |  | 0 | 0 | 196.55 | 196.55 | 982.75 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF2 | 3 | U1 | 2016-02-17 22:31 |  |  |  |  | 2016-03-08 13:49 |  | 0 | 0 | 471.3 | 471.3 | 2720.134 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Highwater
OF2 | 4 | U1 | 2016-03-14 05:32 |  |  |  |  | 2016-03-21 12:33 |  | 0 | 0 | 175.017 | 175.0167 | 1225.117 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF2 | 5 | U1 | 2016-04-15 10:33 |  |  |  |  | 2016-04-18 09:37 |  | 0 | 0 | 71.067 | 71.0667 | 497.467 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830HIGHWATER
OF2 | 6 | U1 | 2016-05-02 10:07 |  |  |  |  | 2016-05-02 10:58 |  | 0 | 0 | 0.85 | 0.85 | 5.95 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Trash
OF2 | 7 | U1 | 2016-05-03 06:07 |  |  |  |  | 2016-05-10 10:05 |  | 0 | 0 | 171.967 | 171.9667 | 1203.766 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820HIGHWATER
OF2 | 8 | U1 | 2016-05-12 13:01 |  |  |  |  | 2016-05-16 10:24 |  | 0 | 0 | 93.383 | 93.3833 | 653.683 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830highwater
OF2 | 9 | U1 | 2016-05-24 09:22 |  |  |  |  | 2016-05-24 12:24 |  | 0 | 0 | 3.033 | 3.0333 | 21.233 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Trash at intake, cleaning out.
OF2 | 11 | U1 | 2016-06-15 14:08 |  |  |  |  | 2016-06-16 07:50 |  | 0 | 0 | 17.7 | 17.7 | 141.6 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830LOW RIVER
OF2 | 12 | U1 | 2016-06-20 15:21 |  |  |  |  | 2016-06-21 06:55 |  | 0 | 0 | 15.567 | 15.5667 | 124.533 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF2 | 13 | U1 | 2016-06-26 06:54 |  |  |  |  | 2016-06-28 10:42 |  | 0 | 0 | 51.8 | 51.8 | 414.4 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF2 | 14 | U1 | 2016-07-14 16:58 |  |  |  |  | 2016-07-15 11:44 |  | 0 | 0 | 18.767 | 18.7667 | 150.134 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF2 | 15 | U1 | 2016-07-17 10:02 |  |  |  |  | 2016-07-17 10:47 |  | 0 | 0 | 0.75 | 0.75 | 6 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 4650 |  |  | - |  | Other cooling system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Gen cooling water strainer basket clogged
OF2 | 16 | U1 | 2016-07-17 18:50 |  |  |  |  | 2016-07-26 09:53 |  | 0 | 0 | 207.05 | 207.05 | 1656.4 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF2 | 17 | U1 | 2016-07-27 16:17 |  |  |  |  | 2016-07-28 10:14 |  | 0 | 0 | 17.95 | 17.95 | 143.6 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830L/F
OF2 | 18 | U1 | 2016-08-05 13:26 |  |  |  |  | 2016-08-06 08:29 |  | 0 | 0 | 19.05 | 19.05 | 152.4 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Water
OF2 | 19 | U1 | 2016-08-07 17:30 |  |  |  |  | 2016-08-10 08:57 |  | 0 | 0 | 63.45 | 63.45 | 507.6 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF2 | 20 | U1 | 2016-08-11 14:25 |  |  |  |  | 2016-08-14 09:26 |  | 0 | 0 | 67.017 | 67.0167 | 536.134 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830LOW FLOW
OF2 | 21 | U1 | 2016-08-14 15:53 |  |  |  |  | 2016-08-15 09:10 |  | 0 | 0 | 17.283 | 17.2833 | 138.266 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830LOW FLOW
OF2 | 24 | U1 | 2016-08-25 06:04 |  |  |  |  | 2016-08-29 06:56 |  | 0 | 0 | 96.867 | 96.8667 | 774.934 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF2 | 22 | U1 | 2016-09-06 20:04 |  |  |  |  | 2016-09-08 07:04 |  | 0 | 0 | 35 | 35 | 245 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830LOW FLOW
OF2 | 23 | U1 | 2016-09-12 03:02 |  |  |  |  | 2016-09-19 13:18 |  | 0 | 0 | 178.267 | 178.2667 | 1247.867 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830LOW FLOW
OF2 | 25 | U1 | 2016-09-23 08:15 |  |  |  |  | 2016-10-01 07:30 |  | 0 | 0 | 191.25 | 191.25 | 1338.75 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF2 | 26 | U1 | 2016-10-02 10:56 |  |  |  |  | 2016-10-03 06:53 |  | 0 | 0 | 19.95 | 19.95 | 139.65 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF2 | 27 | U1 | 2016-10-04 14:10 |  |  |  |  | 2016-10-17 07:10 |  | 0 | 0 | 305 | 305 | 2135 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF2 | 28 | U1 | 2016-10-18 14:00 |  |  |  |  | 2016-10-20 08:38 |  | 0 | 0 | 42.633 | 42.6333 | 298.433 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF2 | 29 | U1 | 2016-10-22 09:30 |  |  |  |  | 2016-10-22 11:59 |  | 0 | 0 | 2.483 | 2.4833 | 17.383 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 3975 |  |  | - |  | DCS - upgrades | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Changing out I/O box on Generator Floor
OF2 | 30 | U1 | 2016-11-16 09:04 |  |  |  |  | 2016-11-17 10:18 |  | 0 | 0 | 25.233 | 25.2333 | 176.633 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF2 | 31 | U1 | 2016-11-18 10:42 |  |  |  |  | 2016-11-22 07:49 |  | 0 | 0 | 93.117 | 93.1167 | 651.817 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF2 | 32 | U1 | 2016-11-22 15:02 |  |  |  |  | 2016-11-29 07:34 |  | 0 | 0 | 160.533 | 160.5333 | 1123.734 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830LOW FLOW
OF2 | 33 | U1 | 2016-11-30 14:13 |  |  |  |  | 2016-12-02 07:50 |  | 0 | 0 | 41.617 | 41.6167 | 227.65 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830LOW FLOW
OF2 | 34 | U1 | 2016-12-02 12:13 |  |  |  |  | 2016-12-02 12:56 |  | 0 | 0 | 0.717 | 0.7167 | 3.583 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 7140 |  |  | - |  | Wicket gate assembly | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Wicketgate valve driver card failure
OF2 | 35 | U1 | 2016-12-20 01:34 |  |  |  |  | 2016-12-26 13:00 |  | 0 | 0 | 155.433 | 155.4333 | 777.167 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820HIGH WATER
OF2 | 36 | U1 | 2016-12-31 09:36 |  |  |  |  | 2017-01-01 |  | 0 | 0 | 14.4 | 14.4 | 72 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF2 | 1 | U1 | 2017-01-01 |  |  |  |  | 2017-01-02 13:49 |  | 0 | 0 | 37.817 | 37.8167 | 189.083 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF2 | 2 | U1 | 2017-01-06 12:47 |  |  |  |  | 2017-01-10 13:30 |  | 0 | 0 | 96.717 | 96.7167 | 483.583 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF2 | 3 | U1 | 2017-01-14 23:24 |  |  |  |  | 2017-01-31 14:17 |  | 0 | 0 | 398.883 | 398.8833 | 1994.417 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820HIGH WATER
OF2 | 6 | U1 | 2017-02-21 08:41 |  |  |  |  | 2017-02-21 11:23 |  | 0 | 0 | 2.7 | 2.7 | 13.5 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9320 |  |  | - |  | Other miscellaneous external problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F82086 Generator Lock out
OF2 | 7 | U1 | 2017-03-01 19:36 |  |  |  |  | 2017-03-14 11:48 |  | 0 | 0 | 304.2 | 304.2 | 2129.4 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Highwater
OF2 | 12 | U1 | 2017-04-01 00:43 |  |  |  |  | 2017-04-14 09:31 |  | 0 | 0 | 320.8 | 320.8 | 2245.6 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820highwater
OF2 | 13 | U1 | 2017-04-29 05:28 |  |  |  |  | 2017-05-18 12:07 |  | 0 | 0 | 462.65 | 462.65 | 3238.55 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820HIGH WATER
OF2 | 14 | U1 | 2017-05-25 22:26 |  |  |  |  | 2017-05-31 09:19 |  | 0 | 0 | 130.883 | 130.8833 | 916.184 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Highwater
OF2 | 15 | U1 | 2017-06-24 21:47 |  |  |  |  | 2017-06-29 07:14 |  | 0 | 0 | 105.45 | 105.45 | 843.6 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Highwater
OF2 | 19 | U1 | 2017-08-04 21:57 |  |  |  |  | 2017-08-07 09:12 |  | 0 | 0 | 59.25 | 59.25 | 474 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF2 | 20 | U1 | 2017-08-07 17:06 |  |  |  |  | 2017-08-08 14:03 |  | 0 | 0 | 20.95 | 20.95 | 167.6 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF2 | 21 | U1 | 2017-08-13 09:53 |  |  |  |  | 2017-08-14 07:29 |  | 0 | 0 | 21.6 | 21.6 | 172.8 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF2 | 22 | U1 | 2017-08-15 07:46 |  |  |  |  | 2017-08-16 09:00 |  | 0 | 0 | 25.233 | 25.2333 | 201.867 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF2 | 23 | U1 | 2017-08-18 13:46 |  |  |  |  | 2017-08-19 07:36 |  | 0 | 0 | 17.833 | 17.8333 | 142.667 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF2 | 24 | U1 | 2017-08-21 15:02 |  |  |  |  | 2017-08-22 07:15 |  | 0 | 0 | 16.217 | 16.2167 | 129.733 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF2 | 25 | U1 | 2017-08-26 17:58 |  |  |  |  | 2017-09-02 06:32 |  | 0 | 0 | 156.567 | 156.5667 | 1222 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low flow
OF2 | 26 | U1 | 2017-09-03 09:01 |  |  |  |  | 2017-09-06 06:53 |  | 0 | 0 | 69.867 | 69.8667 | 489.066 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF2 | 27 | U1 | 2017-09-10 19:45 |  |  |  |  | 2017-09-12 07:14 |  | 0 | 0 | 35.483 | 35.4833 | 248.383 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF2 | 28 | U1 | 2017-09-14 21:25 |  |  |  |  | 2017-09-17 08:40 |  | 0 | 0 | 59.25 | 59.25 | 414.75 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low flow
OF2 | 30 | U1 | 2017-09-20 06:57 |  |  |  |  | 2017-09-22 06:54 |  | 0 | 0 | 47.95 | 47.95 | 335.65 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF2 | 31 | U1 | 2017-09-23 13:55 |  |  |  |  | 2017-10-09 09:28 |  | 0 | 0 | 379.55 | 379.55 | 2656.85 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF2 | 32 | U1 | 2017-10-15 12:50 |  |  |  |  | 2017-10-15 15:18 |  | 0 | 0 | 2.467 | 2.4667 | 17.267 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 3653 |  |  | - |  | DC protection devices | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Loss of signal from tail water sensor.
OF2 | 33 | U1 | 2017-10-15 15:18 |  |  |  |  | 2017-10-26 07:28 |  | 0 | 0 | 256.167 | 256.1667 | 1793.167 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | FR
|  | DESCRIPTION : |  | F830Low Flow
OF2 | 34 | U1 | 2017-10-26 07:28 |  |  |  |  | 2017-10-26 08:50 |  | 0 | 0 | 1.367 | 1.3667 | 9.567 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | FR
|  | DESCRIPTION : |  | F820Cavitation limiter not operating properly
OF2 | 35 | U1 | 2017-11-06 12:13 |  |  |  |  | 2017-11-13 11:59 |  | 0 | 0 | 167.767 | 167.7667 | 1174.366 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820High River
OF2 | 36 | U1 | 2017-11-21 00:43 |  |  |  |  | 2017-11-21 08:22 |  | 0 | 0 | 7.65 | 7.65 | 53.55 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7009 |  |  | - |  | Bearing oil system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Intermediate Bearing tripped on Pad 1 for temp exceeding 158 F
OF2 | 37 | U1 | 2017-11-21 21:10 |  |  |  |  | 2017-11-24 09:42 |  | 0 | 0 | 60.533 | 60.5333 | 423.733 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Unit tripped off due to high water and trash buildup
OF2 | 38 | U1 | 2017-12-11 21:21 |  |  |  |  | 2017-12-13 07:36 |  | 0 | 0 | 34.25 | 34.25 | 171.25 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830ACOE requested unit to be turned off due to low flow.
OF2 | 39 | U1 | 2017-12-13 23:40 |  |  |  |  | 2017-12-23 11:54 |  | 0 | 0 | 228.233 | 228.2333 | 1141.167 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline due to low water
OF2 | 40 | U1 | 2017-12-26 07:42 |  |  |  |  | 2017-12-28 14:28 |  | 0 | 0 | 54.767 | 54.7667 | 273.833 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF2 | 1 | U1 | 2018-01-03 08:56 |  |  |  |  | 2018-01-11 15:24 |  | 0 | 0 | 198.467 | 198.4667 | 992.333 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Run of river
OF2 | 2 | U1 | 2018-01-13 21:49 |  |  |  |  | 2018-01-20 13:11 |  | 0 | 0 | 159.367 | 159.3667 | 796.834 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF2 | 3 | U1 | 2018-01-20 14:02 |  |  |  |  | 2018-01-20 14:28 |  | 0 | 0 | 0.433 | 0.4333 | 2.167 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 4750 |  |  | - |  | Other generator controls and metering problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820speed box
OF2 | 4 | U1 | 2018-01-24 08:36 |  |  |  |  | 2018-02-02 11:23 |  | 0 | 0 | 218.783 | 218.7833 | 1093.917 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830highwater
OF2 | 5 | U1 | 2018-02-08 20:08 |  |  |  |  | 2018-03-12 10:51 |  | 0 | 0 | 758.717 | 758.7167 | 4343.283 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF2 | 6 | U1 | 2018-03-23 12:00 |  |  |  |  | 2018-04-15 12:50 |  | 0 | 0 | 552.833 | 552.8333 | 3869.833 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830highwater
OF2 | 7 | U1 | 2018-04-16 11:50 |  |  |  |  | 2018-05-01 07:38 |  | 0 | 0 | 355.8 | 355.8 | 2490.6 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF2 | 8 | U1 | 2018-05-08 06:55 |  |  |  |  | 2018-05-12 10:09 |  | 0 | 0 | 99.233 | 99.2333 | 694.633 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF2 | 9 | U1 | 2018-05-19 20:45 |  |  |  |  | 2018-05-28 09:51 |  | 0 | 0 | 205.1 | 205.1 | 1435.7 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830high water
OF2 | 12 | U1 | 2018-06-24 06:45 |  |  |  |  | 2018-06-28 13:20 |  | 0 | 0 | 102.583 | 102.5833 | 820.667 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF2 | 13 | U1 | 2018-06-29 22:09 |  |  |  |  | 2018-07-02 12:21 |  | 0 | 0 | 62.2 | 62.2 | 497.6 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Highwater
OF2 | 15 | U1 | 2018-07-11 09:59 |  |  |  |  | 2018-07-13 06:39 |  | 0 | 0 | 44.667 | 44.6667 | 357.333 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF2 | 16 | U1 | 2018-07-14 04:15 |  |  |  |  | 2018-07-16 12:47 |  | 0 | 0 | 56.533 | 56.5333 | 452.267 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low flow
OF2 | 17 | U1 | 2018-07-16 17:44 |  |  |  |  | 2018-07-18 09:07 |  | 0 | 0 | 39.383 | 39.3833 | 315.066 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Water
OF2 | 18 | U1 | 2018-07-20 09:49 |  |  |  |  | 2018-07-21 09:01 |  | 0 | 0 | 23.2 | 23.2 | 185.6 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Water
OF2 | 20 | U1 | 2018-08-08 15:00 |  |  |  |  | 2018-08-09 13:41 |  | 0 | 0 | 22.683 | 22.6833 | 181.467 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | FR
|  | DESCRIPTION : |  | F830Low Flow
OF2 | 21 | U1 | 2018-08-20 08:20 |  |  |  |  | 2018-08-20 15:03 |  | 0 | 0 | 6.717 | 6.7167 | 53.733 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830trash
OF2 | 22 | U1 | 2018-08-29 09:02 |  |  |  |  | 2018-09-17 12:34 |  | 0 | 0 | 459.533 | 459.5333 | 3279.7 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low water flow
OF2 | 23 | U1 | 2018-09-19 16:21 |  |  |  |  | 2018-09-24 10:33 |  | 0 | 0 | 114.2 | 114.2 | 799.4 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F830Highwater
OF2 | 24 | U1 | 2018-09-24 20:24 |  |  |  |  | 2018-10-04 12:43 |  | 0 | 0 | 232.317 | 232.3167 | 1626.217 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830high water
OF2 | 25 | U1 | 2018-10-07 09:03 |  |  |  |  | 2018-10-11 17:12 |  | 0 | 0 | 104.15 | 104.15 | 729.05 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Trash
OF2 | 26 | U1 | 2018-10-11 17:15 |  |  |  |  | 2018-10-13 16:46 |  | 0 | 0 | 47.517 | 47.5167 | 332.617 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Trash
OF2 | 27 | U1 | 2018-10-14 18:43 |  |  |  |  | 2018-10-14 19:27 |  | 0 | 0 | 0.733 | 0.7333 | 5.133 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for trash and to move barge
OF2 | 29 | U1 | 2018-11-01 09:53 |  |  |  |  | 2018-12-09 17:12 |  | 0 | 0 | 919.317 | 919.3167 | 6016.817 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF2 | 30 | U1 | 2018-12-17 00:17 |  |  |  |  | 2019-01-01 |  | 0 | 0 | 359.717 | 359.7167 | 1798.583 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Highwater
OF2 | 1 | U1 | 2019-01-01 |  |  |  |  | 2019-01-16 20:28 |  | 0 | 0 | 380.467 | 380.4667 | 1902.333 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Highwater
OF2 | 2 | U1 | 2019-01-20 03:55 |  |  |  |  | 2019-01-31 23:59 |  | 0 | 0 | 284.067 | 284.0667 | 1420.334 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820high water
OF2 | 3 | U1 | 2019-02-01 |  |  |  |  | 2019-02-03 14:53 |  | 0 | 0 | 62.883 | 62.8833 | 314.417 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Highwater
OF2 | 4 | U1 | 2019-02-04 11:03 |  |  |  |  | 2019-02-04 14:52 |  | 0 | 0 | 3.817 | 3.8167 | 19.083 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Trash buildup
OF2 | 5 | U1 | 2019-02-06 14:01 |  |  |  |  | 2019-03-08 11:40 |  | 0 | 0 | 717.65 | 717.65 | 3947.584 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF2 | 6 | U1 | 2019-03-08 20:16 |  |  |  |  | 2019-03-22 13:39 |  | 0 | 0 | 329.383 | 329.3833 | 2305.683 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Highwater--Motoring
OF2 | 7 | U1 | 2019-03-26 20:38 |  |  |  |  | 2019-03-27 09:37 |  | 0 | 0 | 12.983 | 12.9833 | 90.884 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Trash
OF2 | 9 | U1 | 2019-04-01 04:30 |  |  |  |  | 2019-04-02 14:19 |  | 0 | 0 | 33.817 | 33.8167 | 236.717 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Trash
OF2 | 10 | U1 | 2019-04-03 22:11 |  |  |  |  | 2019-04-04 13:02 |  | 0 | 0 | 14.85 | 14.85 | 103.95 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F830trash
OF2 | 12 | U1 | 2019-04-17 12:05 |  |  |  |  | 2019-05-11 08:43 |  | 0 | 0 | 572.633 | 572.6333 | 4008.434 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Trash
OF2 | 13 | U1 | 2019-05-13 02:47 |  |  |  |  | 2019-05-21 10:20 |  | 0 | 0 | 199.55 | 199.55 | 1396.85 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Trash
OF2 | 14 | U1 | 2019-06-01 06:03 |  |  |  |  | 2019-06-05 16:14 |  | 0 | 0 | 106.183 | 106.1833 | 849.467 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF2 | 15 | U1 | 2019-06-10 11:44 |  |  |  |  | 2019-06-11 14:47 |  | 0 | 0 | 27.05 | 27.05 | 216.4 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF2 | 16 | U1 | 2019-06-16 22:32 |  |  |  |  | 2019-06-28 13:32 |  | 0 | 0 | 279 | 279 | 2232 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820highwater
OF2 | 17 | U1 | 2019-06-29 10:38 |  |  |  |  | 2019-06-29 13:26 |  | 0 | 0 | 2.8 | 2.8 | 22.4 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Trash
OF2 | 18 | U1 | 2019-07-01 21:01 |  |  |  |  | 2019-07-02 13:58 |  | 0 | 0 | 16.95 | 16.95 | 135.6 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820trash
OF2 | 19 | U1 | 2019-07-23 03:44 |  |  |  |  | 2019-07-23 15:35 |  | 0 | 0 | 11.85 | 11.85 | 94.8 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820trash
OF2 | 20 | U1 | 2019-07-28 16:17 |  |  |  |  | 2019-08-09 07:31 |  | 0 | 0 | 279.233 | 279.2333 | 2233.866 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low water
OF2 | 21 | U1 | 2019-08-11 09:31 |  |  |  |  | 2019-10-08 07:22 |  | 0 | 0 | 1389.85 | 1389.85 | 10223.434 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF2 | 22 | U1 | 2019-10-09 10:58 |  |  |  |  | 2019-10-29 06:28 |  | 0 | 0 | 475.5 | 475.5 | 3328.5 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow Offline per ACOE Request
OF2 | 24 | U1 | 2019-11-17 18:46 |  |  |  |  | 2019-11-20 13:51 |  | 0 | 0 | 67.083 | 67.0833 | 469.583 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF2 | 25 | U1 | 2019-12-03 00:54 |  |  |  |  | 2019-12-06 10:04 |  | 0 | 0 | 81.167 | 81.1667 | 405.833 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820highwater
OF2 | 26 | U1 | 2019-12-13 11:12 |  |  |  |  | 2019-12-13 11:35 |  | 0 | 0 | 0.383 | 0.3833 | 1.917 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 7141 |  |  | - |  | Wicket gate operating mechanism or positioner | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Tripped first out on "Wicket Gate Valve Driver Card Failure"
OF2 | 27 | U1 | 2019-12-14 11:54 |  |  |  |  | 2019-12-24 13:29 |  | 0 | 0 | 241.583 | 241.5833 | 1207.917 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830highwater
OF2 | 28 | U1 | 2019-12-31 09:59 |  |  |  |  | 2019-12-31 23:59 |  | 0 | 0 | 14 | 14 | 70 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF2 | 1 | U1 | 2020-01-01 |  |  |  |  | 2020-01-18 14:09 |  | 0 | 0 | 422.15 | 422.15 | 2110.75 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Highwater
OF2 | 2 | U1 | 2020-01-27 07:35 |  |  |  |  | 2020-02-01 13:16 |  | 0 | 0 | 125.683 | 125.6833 | 628.416 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830High River
OF2 | 3 | U1 | 2020-02-08 09:19 |  |  |  |  | 2020-02-24 11:02 |  | 0 | 0 | 385.717 | 385.7167 | 1928.584 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Highwater
OF2 | 4 | U1 | 2020-03-05 14:18 |  |  |  |  | 2020-03-10 12:37 |  | 0 | 0 | 118.317 | 118.3167 | 828.217 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Trash
OF2 | 5 | U1 | 2020-03-14 18:41 |  |  |  |  | 2020-04-06 12:58 |  | 0 | 0 | 546.283 | 546.2833 | 3823.984 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF2 | 6 | U1 | 2020-04-13 13:18 |  |  |  |  | 2020-04-22 13:11 |  | 0 | 0 | 215.883 | 215.8833 | 1511.183 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Highwater & Trash
OF2 | 7 | U1 | 2020-04-28 07:28 |  |  |  |  | 2020-05-12 13:21 |  | 0 | 0 | 341.883 | 341.8833 | 2393.183 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Highwater
OF2 | 8 | U1 | 2020-05-20 07:10 |  |  |  |  | 2020-05-30 09:10 |  | 0 | 0 | 242 | 242 | 1694 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF2 | 9 | U1 | 2020-06-04 12:59 |  |  |  |  | 2020-06-08 07:17 |  | 0 | 0 | 90.3 | 90.3 | 722.4 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 3710 |  |  | - |  | Transmission line (connected to powerhouse switchyard to 1st Substation) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Transformer Outage
OF2 | 10 | U1 | 2020-06-10 09:42 |  |  |  |  | 2020-06-10 17:19 |  | 0 | 0 | 7.617 | 7.6167 | 60.933 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for trash
OF2 | 11 | U1 | 2020-06-10 17:19 |  |  |  |  | 2020-06-17 12:32 |  | 0 | 0 | 163.217 | 163.2167 | 1305.734 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 3710 |  |  | - |  | Transmission line (connected to powerhouse switchyard to 1st Substation) | [8 empty] | AMP CODE: |  | X0
|  | DESCRIPTION : |  | F830Transmission Outage
OF2 | 12 | U1 | 2020-06-26 06:14 |  |  |  |  | 2020-06-26 12:37 |  | 0 | 0 | 6.383 | 6.3833 | 51.067 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9350 |  |  | - |  | Public Safety (water hazard or river rescue) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F590ACOE requested shutdown for safety while they are working on the lower dam.
OF2 | 13 | U1 | 2020-06-28 12:17 |  |  |  |  | 2020-06-29 09:35 |  | 0 | 0 | 21.3 | 21.3 | 170.4 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9001 |  |  | - |  | Drought | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Low Flow, ACOE Request
OF2 | 14 | U1 | 2020-07-08 15:13 |  |  |  |  | 2020-07-10 10:42 |  | 0 | 0 | 43.483 | 43.4833 | 347.867 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Lack of Water (ACOE Offline Request)
OF2 | 15 | U1 | 2020-07-11 10:27 |  |  |  |  | 2020-07-16 13:43 |  | 0 | 0 | 123.267 | 123.2667 | 986.133 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow, ACOE offline request
OF2 | 16 | U1 | 2020-07-17 14:07 |  |  |  |  | 2020-07-20 13:40 |  | 0 | 0 | 71.55 | 71.55 | 572.4 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low flow,
OF2 | 17 | U1 | 2020-07-21 08:58 |  |  |  |  | 2020-07-22 09:56 |  | 0 | 0 | 24.967 | 24.9667 | 199.734 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Lack of Water (ACOE REquested)
OF2 | 18 | U1 | 2020-07-22 17:40 |  |  |  |  | 2020-07-22 20:06 |  | 0 | 0 | 2.433 | 2.4333 | 19.467 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 4730 |  |  | - |  | Generator current and potential transformers | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Unknown trip, after troubleshooting we could not find the cause. Cleared the trip
OF2 | 19 | U1 | 2020-07-23 08:39 |  |  |  |  | 2020-07-25 08:16 |  | 0 | 0 | 47.617 | 47.6167 | 380.933 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Lack of water (ACOE Requested)
OF2 | 20 | U1 | 2020-07-25 15:48 |  |  |  |  | 2020-07-25 21:32 |  | 0 | 0 | 5.733 | 5.7333 | 45.867 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 4730 |  |  | - |  | Generator current and potential transformers | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Generator offline for unknown reason, related to Code 40G LOF on GPS sysetm, came
OF2 | 21 | U1 | 2020-07-25 21:33 |  |  |  |  | 2020-07-31 07:21 |  | 0 | 0 | 129.8 | 129.8 | 1038.4 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Lack of Water (ACOE Requested)
OF2 | 22 | U1 | 2020-07-31 07:21 |  |  |  |  | 2020-08-04 10:06 |  | 0 | 0 | 98.75 | 98.75 | 790 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 3710 |  |  | - |  | Transmission line (connected to powerhouse switchyard to 1st Substation) | [8 empty] | AMP CODE: |  | X0
|  | DESCRIPTION : |  | F830trans line
OF2 | 23 | U1 | 2020-08-10 08:22 |  |  |  |  | 2020-08-11 08:32 |  | 0 | 0 | 24.167 | 24.1667 | 193.334 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low River
OF2 | 24 | U1 | 2020-08-24 13:23 |  |  |  |  | 2020-09-03 15:52 |  | 0 | 0 | 242.483 | 242.4833 | 1876 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF2 | 25 | U1 | 2020-09-08 05:07 |  |  |  |  | 2020-09-09 09:37 |  | 0 | 0 | 28.5 | 28.5 | 199.5 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Lack of water.
OF2 | 26 | U1 | 2020-09-13 16:20 |  |  |  |  | 2020-09-14 13:37 |  | 0 | 0 | 21.283 | 21.2833 | 148.984 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF2 | 27 | U1 | 2020-09-15 12:01 |  |  |  |  | 2020-09-15 15:08 |  | 0 | 0 | 3.117 | 3.1167 | 21.817 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for trash.
OF2 | 29 | U1 | 2020-09-16 14:00 |  |  |  |  | 2020-10-29 12:21 |  | 0 | 0 | 1030.35 | 1030.35 | 7212.45 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | X0
|  | DESCRIPTION : |  | F830MSI M/O completed. Remained offline for lack of water.
OF2 | 31 | U1 | 2020-11-13 07:48 |  |  |  |  | 2020-11-16 12:00 |  | 0 | 0 | 76.2 | 76.2 | 533.4 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Trash in front of Intake switched to another unit for better output
OF2 | 34 | U1 | 2020-12-19 16:33 |  |  |  |  | 2020-12-20 09:37 |  | 0 | 0 | 17.067 | 17.0667 | 85.333 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 4750 |  |  | - |  | Other generator controls and metering problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820VCA 3 card
OF2 | 36 | U1 | 2020-12-27 22:36 |  |  |  |  | 2021-01-01 |  | 0 | 0 | 97.4 | 97.4 | 487 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF2 | 1 | U1 | 2021-01-01 |  |  |  |  | 2021-01-11 12:01 |  | 0 | 0 | 252.017 | 252.0167 | 3175.41 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for highwater
OF2 | 3 | U1 | 2021-01-27 20:26 |  |  |  |  | 2021-02-05 11:15 |  | 0 | 0 | 206.817 | 206.8167 | 2605.89 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Offline for highwater
OF2 | 4 | U1 | 2021-02-24 07:29 |  |  |  |  | 2021-03-15 07:55 |  | 0 | 0 | 456.433 | 456.4333 | 5751.06 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF2 | 5 | U1 | 2021-03-20 00:59 |  |  |  |  | 2021-03-24 09:56 |  | 0 | 0 | 104.95 | 104.95 | 1322.37 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820high water
OF2 | 6 | U1 | 2021-03-31 02:12 |  |  |  |  | 2021-04-05 13:04 |  | 0 | 0 | 130.867 | 130.8667 | 1648.92 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Offline for Highwater
OF2 | 21 | U1 | 2021-05-17 16:13 |  |  |  |  | 2021-05-18 07:19 |  | 0 | 0 | 15.1 | 15.1 | 190.26 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 3979 |  |  | - |  | Other DCS problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Issue with DCS Upgrade logic
OF2 | 24 | U1 | 2021-06-15 07:49 |  |  |  |  | 2021-06-15 13:39 |  | 0 | 0 | 5.833 | 5.8333 | 73.5 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for trash.
OF2 | 25 | U1 | 2021-06-19 19:36 |  |  |  |  | 2021-06-21 09:10 |  | 0 | 0 | 37.567 | 37.5667 | 473.34 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for trash.
OF2 | 26 | U1 | 2021-06-26 13:35 |  |  |  |  | 2021-06-28 09:39 |  | 0 | 0 | 44.067 | 44.0667 | 555.24 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830ACOE requested, Lack of Water
OF2 | 28 | U1 | 2021-06-29 09:00 |  |  |  |  | 2021-07-01 07:35 |  | 0 | 0 | 46.583 | 46.5833 | 586.95 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | FR
|  | DESCRIPTION : |  | F830Unit offline for Lack of Water, Run of River per ACOE
OF2 | 31 | U1 | 2021-07-09 06:30 |  |  |  |  | 2021-07-13 09:57 |  | 0 | 0 | 99.45 | 99.45 | 1253.07 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | FR
|  | DESCRIPTION : |  | F830Unit offline for run of river lack of water.
OF2 | 33 | U1 | 2021-07-30 07:51 |  |  |  |  | 2021-07-30 14:24 |  | 0 | 0 | 6.55 | 6.55 | 82.53 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Lack of Water, offline per ACOE request
OF2 | 34 | U1 | 2021-08-04 05:55 |  |  |  |  | 2021-08-13 10:28 |  | 0 | 0 | 220.55 | 220.55 | 2778.93 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Lack of Water
OF2 | 41 | U1 | 2021-08-18 06:30 |  |  |  |  | 2021-08-18 07:53 |  | 0 | 0 | 1.383 | 1.3833 | 17.43 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | FR
|  | DESCRIPTION : |  | F830Run of River
OF2 | 42 | U1 | 2021-09-03 10:41 |  |  |  |  | 2021-09-06 07:37 |  | 0 | 0 | 68.933 | 68.9333 | 868.56 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for High Water
OF2 | 44 | U1 | 2021-10-02 15:56 |  |  |  |  | 2021-10-04 07:40 |  | 0 | 0 | 39.733 | 39.7333 | 500.64 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Lack of Water (ACOE)
OF2 | 45 | U1 | 2021-10-05 10:01 |  |  |  |  | 2021-10-08 06:30 |  | 0 | 0 | 68.483 | 68.4833 | 862.89 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Lack of Water (ACOE)
OF2 | 46 | U1 | 2021-11-01 23:18 |  |  |  |  | 2021-11-02 07:03 |  | 0 | 0 | 7.75 | 7.75 | 97.65 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 4551 |  |  | - |  | Generator bearings | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F780Bearings-IGB increase in temperature/exceed operational limits.
OF2 | 50 | U1 | 2021-12-07 15:18 |  |  |  |  | 2021-12-10 10:59 |  | 0 | 0 | 67.683 | 67.6833 | 852.81 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Run of River - Highwater
OF2 | 51 | U1 | 2021-12-12 20:55 |  |  |  |  | 2021-12-15 08:31 |  | 0 | 0 | 59.6 | 59.6 | 750.96 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Run of RIver - Highwater
OF2 | 53 | U1 | 2021-12-31 08:42 |  |  |  |  | 2022-01-01 |  | 0 | 0 | 15.3 | 15.3 | 192.78 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830High Water.
OF2 | 1 | U1 | 2022-01-01 |  |  |  |  | 2022-01-16 11:45 |  | 0 | 0 | 371.75 | 371.75 | 4684.05 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for High Water.
OF2 | 2 | U1 | 2022-02-04 05:43 |  |  |  |  | 2022-02-14 14:04 |  | 0 | 0 | 248.35 | 248.35 | 3129.21 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Offline for High Water
OF2 | 3 | U1 | 2022-02-17 07:14 |  |  |  |  | 2022-03-21 07:16 |  | 0 | 0 | 768.033 | 768.0333 | 9677.22 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Trash / Highwater (Run of River)
OF2 | 6 | U1 | 2022-04-10 05:29 |  |  |  |  | 2022-04-18 07:44 |  | 0 | 0 | 194.25 | 194.25 | 2447.55 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for High Water
OF2 | 7 | U1 | 2022-05-07 13:48 |  |  |  |  | 2022-05-16 09:45 |  | 0 | 0 | 211.95 | 211.95 | 2670.57 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for High Water.
OF2 | 8 | U1 | 2022-05-23 10:10 |  |  |  |  | 2022-05-23 10:30 |  | 0 | 0 | 0.333 | 0.3333 | 4.2 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7053 |  |  | - |  | Governor oil system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Governor Oil Pressure Lo.
OF2 | 9 | U1 | 2022-05-30 07:58 |  |  |  |  | 2022-06-01 09:33 |  | 0 | 0 | 49.583 | 49.5833 | 624.75 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for high water.
OF2 | 10 | U1 | 2022-06-03 06:43 |  |  |  |  | 2022-06-03 09:28 |  | 0 | 0 | 2.75 | 2.75 | 34.65 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 4609 |  |  | - |  | Other exciter problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Offline for Exciter problems.
OF2 | 11 | U1 | 2022-06-25 13:55 |  |  |  |  | 2022-06-28 08:40 |  | 0 | 0 | 66.75 | 66.75 | 841.05 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Lack of Water-Run of River per the ACOE
OF2 | 12 | U1 | 2022-07-01 01:15 |  |  |  |  | 2022-07-07 07:38 |  | 0 | 0 | 150.383 | 150.3833 | 1894.83 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for lack of water.
OF2 | 13 | U1 | 2022-07-13 12:40 |  |  |  |  | 2022-07-19 07:34 |  | 0 | 0 | 138.9 | 138.9 | 1750.14 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Lack of Water (Run of River) per The ACOE
OF2 | 14 | U1 | 2022-07-22 16:13 |  |  |  |  | 2022-07-25 06:49 |  | 0 | 0 | 62.6 | 62.6 | 788.76 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Lack of Water (Run of River) per the ACOE
OF2 | 16 | U1 | 2022-08-02 06:51 |  |  |  |  | 2022-08-02 13:49 |  | 0 | 0 | 6.967 | 6.9667 | 87.78 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Trash
OF2 | 18 | U1 | 2022-08-23 11:00 |  |  |  |  | 2022-08-23 13:53 |  | 0 | 0 | 2.883 | 2.8833 | 36.33 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Trash (Run of River)
OF2 | 19 | U1 | 2022-08-28 08:02 |  |  |  |  | 2022-08-29 16:40 |  | 0 | 0 | 32.633 | 32.6333 | 411.18 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Lack of Water per The ACOE
OF2 | 20 | U1 | 2022-08-29 16:40 |  |  |  |  | 2022-08-30 12:56 |  | 0 | 0 | 20.267 | 20.2667 | 255.36 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 3672 |  |  | - |  | 12-15kV conductors and buses | [8 empty] | AMP CODE: |  | 49
|  | DESCRIPTION : |  | F49014KV Bus A Lockout
OF2 | 21 | U1 | 2022-08-30 12:56 |  |  |  |  | 2022-09-04 08:24 |  | 0 | 0 | 115.467 | 115.4667 | 1454.88 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | FR
|  | DESCRIPTION : |  | F830Lack of water.
OF2 | 22 | U1 | 2022-09-04 17:52 |  |  |  |  | 2022-09-06 09:20 |  | 0 | 0 | 39.467 | 39.4667 | 497.28 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Lack of Water.
OF2 | 23 | U1 | 2022-09-06 13:09 |  |  |  |  | 2022-09-07 07:20 |  | 0 | 0 | 18.183 | 18.1833 | 229.11 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Trash / Run of River
OF2 | 24 | U1 | 2022-09-13 06:19 |  |  |  |  | 2022-09-14 06:52 |  | 0 | 0 | 24.55 | 24.55 | 309.33 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Trash
OF2 | 25 | U1 | 2022-09-18 15:56 |  |  |  |  | 2022-09-28 07:57 |  | 0 | 0 | 232.017 | 232.0167 | 2923.41 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Lack of Water
OF2 | 26 | U1 | 2022-09-28 18:52 |  |  |  |  | 2022-09-30 10:11 |  | 0 | 0 | 39.317 | 39.3167 | 495.39 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830lack of water
OF2 | 27 | U1 | 2022-10-07 23:08 |  |  |  |  | 2022-11-12 14:16 |  | 0 | 0 | 855.133 | 855.1333 | 10774.68 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Lack of Water.
OF2 | 28 | U1 | 2022-11-27 09:46 |  |  |  |  | 2022-11-28 07:46 |  | 0 | 0 | 22 | 22 | 277.2 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Lack of Water
OF2 | 29 | U1 | 2022-12-11 08:10 |  |  |  |  | 2022-12-12 08:20 |  | 0 | 0 | 24.167 | 24.1667 | 304.5 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830trash
OF2 | 30 | U1 | 2022-12-28 14:31 |  |  |  |  | 2022-12-29 13:46 |  | 0 | 0 | 23.25 | 23.25 | 292.95 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for lack of water
OF2 | 1 | U1 | 2023-01-03 16:34 |  |  |  |  | 2023-01-09 10:18 |  | 0 | 0 | 137.733 | 137.7333 | 1735.44 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Offline for trash.
OF2 | 2 | U1 | 2023-01-13 23:03 |  |  |  |  | 2023-01-24 08:13 |  | 0 | 0 | 249.167 | 249.1667 | 3139.5 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830trash
OF2 | 4 | U1 | 2023-01-25 14:40 |  |  |  |  | 2023-01-27 11:56 |  | 0 | 0 | 45.267 | 45.2667 | 570.36 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | FR
|  | DESCRIPTION : |  | F820Offline for Trash.
OF2 | 5 | U1 | 2023-01-29 04:51 |  |  |  |  | 2023-01-29 14:55 |  | 0 | 0 | 10.067 | 10.0667 | 126.84 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Offline for high water.
OF2 | 6 | U1 | 2023-02-03 12:08 |  |  |  |  | 2023-02-07 11:51 |  | 0 | 0 | 95.717 | 95.7167 | 1206.03 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9320 |  |  | - |  | Other miscellaneous external problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830barge recovery
OF2 | 8 | U1 | 2023-02-17 08:45 |  |  |  |  | 2023-02-24 14:54 |  | 0 | 0 | 174.15 | 174.15 | 2194.29 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for High Water
OF2 | 9 | U1 | 2023-03-03 07:08 |  |  |  |  | 2023-03-13 11:07 |  | 0 | 0 | 243.983 | 243.9833 | 3074.19 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for High Water
OF2 | 10 | U1 | 2023-03-24 20:10 |  |  |  |  | 2023-04-11 06:30 |  | 0 | 0 | 418.333 | 418.3333 | 5271 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Offline for High Water.
OF2 | 11 | U1 | 2023-04-11 06:30 |  |  |  |  | 2023-04-28 13:36 |  | 0 | 0 | 415.1 | 415.1 | 5230.26 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9320 |  |  | - |  | Other miscellaneous external problems | [8 empty] | AMP CODE: |  | FR
|  | DESCRIPTION : |  | FX00Barge Recovery
OF2 | 12 | U1 | 2023-05-25 08:27 |  |  |  |  | 2023-05-26 12:01 |  | 0 | 0 | 27.567 | 27.5667 | 347.34 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Lack of Water
OF2 | 13 | U1 | 2023-05-29 15:51 |  |  |  |  | 2023-05-31 13:24 |  | 0 | 0 | 45.55 | 45.55 | 573.93 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Lack of Water.
OF2 | 14 | U1 | 2023-06-12 14:05 |  |  |  |  | 2023-06-18 07:09 |  | 0 | 0 | 137.067 | 137.0667 | 1727.04 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Trash
OF2 | 15 | U1 | 2023-06-19 21:00 |  |  |  |  | 2023-06-25 09:00 |  | 0 | 0 | 132 | 132 | 1663.2 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline lack of water.
OF2 | 16 | U1 | 2023-06-26 07:29 |  |  |  |  | 2023-06-26 16:00 |  | 0 | 0 | 8.517 | 8.5167 | 107.31 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for MSI sonar.
OF2 | 17 | U1 | 2023-06-26 16:00 |  |  |  |  | 2023-07-02 07:41 |  | 0 | 0 | 135.683 | 135.6833 | 1709.61 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | FR
|  | DESCRIPTION : |  | F830lack of water
OF2 | 18 | U1 | 2023-07-07 07:53 |  |  |  |  | 2023-07-07 13:59 |  | 0 | 0 | 6.1 | 6.1 | 76.86 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Trash
OF2 | 19 | U1 | 2023-07-08 09:27 |  |  |  |  | 2023-07-10 07:34 |  | 0 | 0 | 46.117 | 46.1167 | 581.07 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for lack of water
OF2 | 20 | U1 | 2023-07-14 04:58 |  |  |  |  | 2023-07-16 08:26 |  | 0 | 0 | 51.467 | 51.4667 | 648.48 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830lack of water
OF2 | 21 | U1 | 2023-07-30 19:22 |  |  |  |  | 2023-08-07 09:00 |  | 0 | 0 | 181.633 | 181.6333 | 2288.58 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for lack of water
OF2 | 23 | U1 | 2023-08-13 22:14 |  |  |  |  | 2023-08-14 07:46 |  | 0 | 0 | 9.533 | 9.5333 | 120.12 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7007 |  |  | - |  | Bearings | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Unit offline for Turbine Bearing Flow Trip
OF2 | 24 | U1 | 2023-08-17 19:03 |  |  |  |  | 2023-08-26 07:02 |  | 0 | 0 | 203.983 | 203.9833 | 2570.19 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for lack of water
OF2 | 25 | U1 | 2023-08-30 20:35 |  |  |  |  | 2023-09-01 14:13 |  | 0 | 0 | 41.633 | 41.6333 | 524.58 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830lack of water
OF2 | 26 | U1 | 2023-09-02 13:00 |  |  |  |  | 2023-09-09 05:30 |  | 0 | 0 | 160.5 | 160.5 | 2022.3 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Lack of water
OF2 | 28 | U1 | 2023-09-23 06:24 |  |  |  |  | 2023-10-25 08:21 |  | 0 | 0 | 769.95 | 769.95 | 9701.37 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | FR
|  | DESCRIPTION : |  | F830lack of water
OF2 | 29 | U1 | 2023-10-27 04:14 |  |  |  |  | 2023-11-01 13:49 |  | 0 | 0 | 129.583 | 129.5833 | 1632.75 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline lack of water.
OF2 | 30 | U1 | 2023-11-03 15:45 |  |  |  |  | 2023-11-22 08:03 |  | 0 | 0 | 448.3 | 448.3 | 5648.58 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830lack of water
OF2 | 31 | U1 | 2023-11-25 05:28 |  |  |  |  | 2023-11-26 08:48 |  | 0 | 0 | 27.333 | 27.3333 | 344.4 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7053 |  |  | - |  | Governor oil system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Unit offline for Gov Oil Pressure Low
Ohio Falls - OF3
Unit | Event | Type | Start |  |  |  |  | End |  | GAC | NAC | Duration | Equiv Hrs | Equiv MWH | Cont | Work Start | Work End |  | Hours |  |  | Gross Capacity Impact (MW)
OF3 | 1 | U1 | 2014-01-01 |  |  |  |  | 2014-01-05 14:37 |  | 0 | 0 | 110.617 | 110.6167 | 442.467 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820High water
OF3 | 2 | U1 | 2014-01-12 11:57 |  |  |  |  | 2014-01-20 14:03 |  | 0 | 0 | 194.1 | 194.1 | 776.4 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF3 | 3 | U1 | 2014-02-05 10:35 |  |  |  |  | 2014-02-12 16:14 |  | 0 | 0 | 173.65 | 173.65 | 694.6 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Highwater
OF3 | 4 | U1 | 2014-02-13 05:03 |  |  |  |  | 2014-02-13 11:30 |  | 0 | 0 | 6.45 | 6.45 | 25.8 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 4650 |  |  | - |  | Other cooling system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Upper generator guide bearing temp pad 2
OF3 | 5 | U1 | 2014-02-20 13:59 |  |  |  |  | 2014-03-03 10:38 |  | 0 | 0 | 260.65 | 260.65 | 1042.6 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF3 | 6 | U1 | 2014-03-10 06:46 |  |  |  |  | 2014-03-11 07:56 |  | 0 | 0 | 25.167 | 25.1667 | 100.666 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Trash isuses.
OF3 | 7 | U1 | 2014-03-15 06:09 |  |  |  |  | 2014-03-18 09:39 |  | 0 | 0 | 75.5 | 75.5 | 302 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830High water.
OF3 | 9 | U1 | 2014-04-01 11:38 |  |  |  |  | 2014-04-14 12:24 |  | 0 | 0 | 312.767 | 312.7667 | 1876.6 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF3 | 10 | U1 | 2014-04-16 09:12 |  |  |  |  | 2014-04-16 12:28 |  | 0 | 0 | 3.267 | 3.2667 | 19.6 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 4550 |  |  | - |  | Generator bearings and lube oil system (including thrust bearings on hydro units) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Upper Guide Bearing Temperature.
OF3 | 11 | U1 | 2014-04-22 14:33 |  |  |  |  | 2014-04-22 15:26 |  | 0 | 0 | 0.883 | 0.8833 | 5.3 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7200 |  |  | - |  | Major overhaul (use for non-specific overhaul only; see page B-CCGT-2) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F000Moving heavy loads over gen. , due to rehab of unit 5.
OF3 | 12 | U1 | 2014-04-30 06:14 |  |  |  |  | 2014-05-07 07:17 |  | 0 | 0 | 169.05 | 169.05 | 1014.3 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF3 | 13 | U1 | 2014-05-15 23:09 |  |  |  |  | 2014-05-25 07:40 |  | 0 | 0 | 224.517 | 224.5167 | 1347.1 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Highwater
OF3 | 14 | U1 | 2014-06-04 10:02 |  |  |  |  | 2014-06-05 07:31 |  | 0 | 0 | 21.483 | 21.4833 | 128.9 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830LOW RIVER
OF3 | 15 | U1 | 2014-07-02 14:14 |  |  |  |  | 2014-07-02 15:52 |  | 0 | 0 | 1.633 | 1.6333 | 9.8 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Trash-ran rake rack
OF3 | 16 | U1 | 2014-07-16 10:44 |  |  |  |  | 2014-07-16 13:40 |  | 0 | 0 | 2.933 | 2.9333 | 17.6 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Dredge
OF3 | 17 | U1 | 2014-07-21 08:35 |  |  |  |  | 2014-07-21 15:19 |  | 0 | 0 | 6.733 | 6.7333 | 40.4 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9590 |  |  | - |  | Miscellaneous regulatory (this code is primarily intended for use with event contribution code 2 to indicate that a regulatory-related factor contributed to the primary cause of the event) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830FERC inspection divers
OF3 | 18 | U1 | 2014-07-22 07:29 |  |  |  |  | 2014-07-22 13:25 |  | 0 | 0 | 5.933 | 5.9333 | 35.6 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9590 |  |  | - |  | Miscellaneous regulatory (this code is primarily intended for use with event contribution code 2 to indicate that a regulatory-related factor contributed to the primary cause of the event) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Ferc diver inspection
OF3 | 19 | U1 | 2014-07-25 09:26 |  |  |  |  | 2014-07-28 10:22 |  | 0 | 0 | 72.933 | 72.9333 | 437.6 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF3 | 20 | U1 | 2014-07-28 22:41 |  |  |  |  | 2014-07-29 11:36 |  | 0 | 0 | 12.917 | 12.9167 | 77.5 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low flow
OF3 | 21 | U1 | 2014-08-02 09:19 |  |  |  |  | 2014-08-02 12:58 |  | 0 | 0 | 3.65 | 3.65 | 21.9 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7111 |  |  | - |  | Intake tunnel | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Divers installing balloons in tunnel to isolate river water from coming in so we c
OF3 | 22 | U1 | 2014-08-02 12:58 |  |  |  |  | 2014-08-05 06:40 |  | 0 | 0 | 65.7 | 65.7 | 394.2 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | NF
|  | DESCRIPTION : |  | FE00low flow
OF3 | 23 | U1 | 2014-08-07 21:29 |  |  |  |  | 2014-08-12 07:00 |  | 0 | 0 | 105.517 | 105.5167 | 633.1 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830LOW RIVER
OF3 | 24 | U1 | 2014-08-25 09:37 |  |  |  |  | 2014-08-25 12:22 |  | 0 | 0 | 2.75 | 2.75 | 16.5 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Took unit off to dredge trash.
OF3 | 25 | U1 | 2014-08-30 23:29 |  |  |  |  | 2014-09-02 12:06 |  | 0 | 0 | 60.617 | 60.6167 | 363.7 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830LOW RIVER
OF3 | 31 | U1 | 2014-09-13 09:41 |  |  |  |  | 2014-09-15 06:56 |  | 0 | 0 | 45.25 | 45.25 | 271.5 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF3 | 32 | U1 | 2014-09-20 00:13 |  |  |  |  | 2014-09-29 06:00 |  | 0 | 0 | 221.783 | 221.7833 | 1330.7 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830LOW RIVER
OF3 | 3 | U1 | 2015-03-04 11:51 |  |  |  |  | 2015-03-27 08:02 |  | 0 | 0 | 548.183 | 548.1833 | 2192.733 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF3 | 4 | U1 | 2015-04-03 10:01 |  |  |  |  | 2015-04-29 07:57 |  | 0 | 0 | 621.933 | 621.9333 | 3731.6 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF3 | 5 | U1 | 2015-05-27 16:32 |  |  |  |  | 2015-05-28 07:18 |  | 0 | 0 | 14.767 | 14.7667 | 88.6 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Low Flow
OF3 | 7 | U1 | 2015-06-19 05:03 |  |  |  |  | 2015-06-19 09:16 |  | 0 | 0 | 4.217 | 4.2167 | 25.3 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7040 |  |  | - |  | Turbine overhaul | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Took this unit off for contractors taking intricate readings on unit 2 Gen re-hab.
OF3 | 8 | U1 | 2015-06-21 06:43 |  |  |  |  | 2015-06-26 12:38 |  | 0 | 0 | 125.917 | 125.9167 | 755.5 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830High water.
OF3 | 9 | U1 | 2015-06-30 12:09 |  |  |  |  | 2015-07-07 12:35 |  | 0 | 0 | 168.433 | 168.4333 | 1323.767 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF3 | 10 | U1 | 2015-07-11 10:14 |  |  |  |  | 2015-07-22 10:32 |  | 0 | 0 | 264.3 | 264.3 | 2114.4 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF3 | 11 | U1 | 2015-07-25 09:17 |  |  |  |  | 2015-07-26 09:41 |  | 0 | 0 | 24.4 | 24.4 | 195.2 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Trash
OF3 | 12 | U1 | 2015-07-28 03:02 |  |  |  |  | 2015-07-28 07:40 |  | 0 | 0 | 4.633 | 4.6333 | 37.067 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 3812 |  |  | - |  | Service water valves | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Had to replace service water valve.
OF3 | 13 | U1 | 2015-07-31 05:00 |  |  |  |  | 2015-07-31 07:59 |  | 0 | 0 | 2.983 | 2.9833 | 23.867 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7040 |  |  | - |  | Turbine overhaul | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit #3 running causing too much vibration for Voith Hydro to take their wire read
OF3 | 14 | U1 | 2015-08-10 06:56 |  |  |  |  | 2015-08-10 11:00 |  | 0 | 0 | 4.067 | 4.0667 | 32.533 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Dredge
OF3 | 15 | U1 | 2015-08-10 11:41 |  |  |  |  | 2015-08-12 12:28 |  | 0 | 0 | 48.783 | 48.7833 | 390.266 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low flow
OF3 | 16 | U1 | 2015-08-13 07:50 |  |  |  |  | 2015-08-14 15:22 |  | 0 | 0 | 31.533 | 31.5333 | 252.266 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9720 |  |  | - |  | Other safety problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Divers in lower pool to replace de-watering pump in unit 2.
OF3 | 17 | U1 | 2015-08-15 08:34 |  |  |  |  | 2015-08-16 11:09 |  | 0 | 0 | 26.583 | 26.5833 | 212.667 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low flow
OF3 | 18 | U1 | 2015-08-17 11:53 |  |  |  |  | 2015-08-19 10:42 |  | 0 | 0 | 46.817 | 46.8167 | 374.533 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF3 | 19 | U1 | 2015-08-21 09:45 |  |  |  |  | 2015-08-26 12:31 |  | 0 | 0 | 122.767 | 122.7667 | 982.133 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830LOW FLOW
OF3 | 20 | U1 | 2015-08-26 17:58 |  |  |  |  | 2015-09-04 12:27 |  | 0 | 0 | 210.483 | 210.4833 | 1683.867 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830LOW FLOW
OF3 | 21 | U1 | 2015-09-04 20:15 |  |  |  |  | 2015-09-09 07:59 |  | 0 | 0 | 107.733 | 107.7333 | 861.867 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low river
OF3 | 22 | U1 | 2015-09-09 20:39 |  |  |  |  | 2015-09-11 06:50 |  | 0 | 0 | 34.183 | 34.1833 | 273.467 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low flow
OF3 | 23 | U1 | 2015-09-12 02:13 |  |  |  |  | 2015-09-14 10:11 |  | 0 | 0 | 55.967 | 55.9667 | 447.734 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low flow
OF3 | 24 | U1 | 2015-09-15 14:12 |  |  |  |  | 2015-09-18 07:09 |  | 0 | 0 | 64.95 | 64.95 | 519.6 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF3 | 25 | U1 | 2015-09-19 20:17 |  |  |  |  | 2015-09-23 10:44 |  | 0 | 0 | 86.45 | 86.45 | 691.6 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF3 | 27 | U1 | 2015-10-11 12:46 |  |  |  |  | 2015-10-12 07:53 |  | 0 | 0 | 19.117 | 19.1167 | 152.934 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Took unit off at the request of ACOE due to low flow.
OF3 | 28 | U1 | 2015-10-16 02:14 |  |  |  |  | 2015-10-23 08:08 |  | 0 | 0 | 173.9 | 173.9 | 1391.2 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF3 | 29 | U1 | 2015-10-26 14:17 |  |  |  |  | 2015-10-28 08:30 |  | 0 | 0 | 42.217 | 42.2167 | 337.733 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF3 | 31 | U1 | 2015-11-01 07:21 |  |  |  |  | 2015-11-01 14:05 |  | 0 | 0 | 6.733 | 6.7333 | 53.867 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9720 |  |  | - |  | Other safety problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Divers in lower river removing stop logs. Had to take unit off for divers safety.
OF3 | 32 | U1 | 2015-11-02 |  |  |  |  | 2015-11-08 10:41 |  | 0 | 0 | 154.683 | 154.6833 | 1237.467 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9720 |  |  | - |  | Other safety problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Divers had to go into Unit #2 to dredge around the bottom trash rack in order to g
OF3 | 33 | U1 | 2015-11-11 19:08 |  |  |  |  | 2015-11-11 19:51 |  | 0 | 0 | 0.717 | 0.7167 | 5.733 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9720 |  |  | - |  | Other safety problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Critical lift over unit.
OF3 | 35 | U1 | 2015-12-03 23:19 |  |  |  |  | 2015-12-08 09:47 |  | 0 | 0 | 106.467 | 106.4667 | 851.734 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF3 | 36 | U1 | 2015-12-24 09:25 |  |  |  |  | 2015-12-31 23:59 |  | 0 | 0 | 182.567 | 182.5667 | 1460.534 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF3 | 1 | U1 | 2016-01-01 |  |  |  |  | 2016-01-05 14:02 |  | 0 | 0 | 110.033 | 110.0333 | 550.167 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820highwater
OF3 | 2 | U1 | 2016-01-19 10:21 |  |  |  |  | 2016-01-19 11:21 |  | 0 | 0 | 1 | 1 | 5 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 4650 |  |  | - |  | Other cooling system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Turbine Guide Brg water supply stopped up.
OF3 | 3 | U1 | 2016-01-22 09:03 |  |  |  |  | 2016-01-22 10:42 |  | 0 | 0 | 1.65 | 1.65 | 8.25 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 4650 |  |  | - |  | Other cooling system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Turbine Guide Brg cooling water stopped up
OF3 | 4 | U1 | 2016-02-03 06:11 |  |  |  |  | 2016-02-11 10:24 |  | 0 | 0 | 196.217 | 196.2167 | 981.083 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Highwater
OF3 | 5 | U1 | 2016-02-17 22:24 |  |  |  |  | 2016-03-08 11:27 |  | 0 | 0 | 469.05 | 469.05 | 2704.15 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Highwater
OF3 | 6 | U1 | 2016-03-14 06:20 |  |  |  |  | 2016-03-21 09:45 |  | 0 | 0 | 171.417 | 171.4167 | 1199.917 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830highwater
OF3 | 7 | U1 | 2016-04-06 19:26 |  |  |  |  | 2016-04-07 07:10 |  | 0 | 0 | 11.733 | 11.7333 | 82.134 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 4650 |  |  | - |  | Other cooling system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Pit screen clogged
OF3 | 8 | U1 | 2016-04-15 11:57 |  |  |  |  | 2016-04-18 09:13 |  | 0 | 0 | 69.267 | 69.2667 | 484.867 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830HIGHWATER
OF3 | 9 | U1 | 2016-05-02 09:50 |  |  |  |  | 2016-05-02 12:56 |  | 0 | 0 | 3.1 | 3.1 | 21.7 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7190 |  |  | - |  | Dewatering and rewatering equipment | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Divers replacing Level Indicator to our Dewatering Pumps.
OF3 | 10 | U1 | 2016-05-03 06:16 |  |  |  |  | 2016-05-10 09:21 |  | 0 | 0 | 171.083 | 171.0833 | 1197.583 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830HIGHWATER
OF3 | 11 | U1 | 2016-05-12 13:04 |  |  |  |  | 2016-05-16 09:48 |  | 0 | 0 | 92.733 | 92.7333 | 649.133 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830highwater
OF3 | 12 | U1 | 2016-05-24 07:30 |  |  |  |  | 2016-05-24 10:47 |  | 0 | 0 | 3.283 | 3.2833 | 22.983 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7190 |  |  | - |  | Dewatering and rewatering equipment | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Diver in water installing Level Probe at Unit #4
OF3 | 14 | U1 | 2016-06-15 11:10 |  |  |  |  | 2016-06-16 09:49 |  | 0 | 0 | 22.65 | 22.65 | 181.2 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830LOW RIVER
OF3 | 15 | U1 | 2016-06-26 06:49 |  |  |  |  | 2016-06-28 10:19 |  | 0 | 0 | 51.5 | 51.5 | 412 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF3 | 16 | U1 | 2016-07-13 21:16 |  |  |  |  | 2016-07-15 09:28 |  | 0 | 0 | 36.2 | 36.2 | 289.6 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF3 | 17 | U1 | 2016-07-17 11:22 |  |  |  |  | 2016-07-17 11:56 |  | 0 | 0 | 0.567 | 0.5667 | 4.533 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 4650 |  |  | - |  | Other cooling system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Gen cooling water strainer clogged
OF3 | 18 | U1 | 2016-07-18 02:05 |  |  |  |  | 2016-07-21 09:26 |  | 0 | 0 | 79.35 | 79.35 | 634.8 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low River
OF3 | 19 | U1 | 2016-07-21 14:56 |  |  |  |  | 2016-07-26 12:50 |  | 0 | 0 | 117.9 | 117.9 | 943.2 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF3 | 20 | U1 | 2016-08-05 04:07 |  |  |  |  | 2016-08-06 07:44 |  | 0 | 0 | 27.617 | 27.6167 | 220.934 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF3 | 21 | U1 | 2016-08-07 18:26 |  |  |  |  | 2016-08-09 07:14 |  | 0 | 0 | 36.8 | 36.8 | 294.4 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF3 | 22 | U1 | 2016-08-11 09:33 |  |  |  |  | 2016-08-13 10:58 |  | 0 | 0 | 49.417 | 49.4167 | 395.333 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830LOW FLOW
OF3 | 23 | U1 | 2016-08-14 18:13 |  |  |  |  | 2016-08-15 07:42 |  | 0 | 0 | 13.483 | 13.4833 | 107.867 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830LOW FLOW
OF3 | 24 | U1 | 2016-08-25 07:54 |  |  |  |  | 2016-08-29 07:50 |  | 0 | 0 | 95.933 | 95.9333 | 767.467 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF3 | 25 | U1 | 2016-09-03 13:09 |  |  |  |  | 2016-09-06 07:08 |  | 0 | 0 | 65.983 | 65.9833 | 461.883 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF3 | 26 | U1 | 2016-09-06 17:01 |  |  |  |  | 2016-09-08 07:43 |  | 0 | 0 | 38.7 | 38.7 | 270.9 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830LOW FLOW
OF3 | 27 | U1 | 2016-09-12 03:02 |  |  |  |  | 2016-09-14 06:46 |  | 0 | 0 | 51.733 | 51.7333 | 362.134 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830LOW FLOW
OF3 | 28 | U1 | 2016-09-14 18:06 |  |  |  |  | 2016-09-17 06:47 |  | 0 | 0 | 60.683 | 60.6833 | 424.783 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF3 | 29 | U1 | 2016-09-17 16:37 |  |  |  |  | 2016-09-19 06:52 |  | 0 | 0 | 38.25 | 38.25 | 267.75 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF3 | 30 | U1 | 2016-09-22 19:38 |  |  |  |  | 2016-09-30 07:16 |  | 0 | 0 | 179.633 | 179.6333 | 1257.434 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF3 | 31 | U1 | 2016-10-04 16:08 |  |  |  |  | 2016-10-10 09:22 |  | 0 | 0 | 137.233 | 137.2333 | 960.634 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF3 | 32 | U1 | 2016-10-12 10:34 |  |  |  |  | 2016-10-14 08:13 |  | 0 | 0 | 45.65 | 45.65 | 319.55 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF3 | 33 | U1 | 2016-10-14 14:11 |  |  |  |  | 2016-10-15 07:26 |  | 0 | 0 | 17.25 | 17.25 | 120.75 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830LOW FLOW
OF3 | 34 | U1 | 2016-10-18 11:32 |  |  |  |  | 2016-10-20 12:12 |  | 0 | 0 | 48.667 | 48.6667 | 340.667 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF3 | 35 | U1 | 2016-10-21 02:14 |  |  |  |  | 2016-10-22 07:18 |  | 0 | 0 | 29.067 | 29.0667 | 203.467 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF3 | 36 | U1 | 2016-11-01 14:14 |  |  |  |  | 2016-11-03 09:09 |  | 0 | 0 | 42.917 | 42.9167 | 300.417 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF3 | 37 | U1 | 2016-11-07 11:14 |  |  |  |  | 2016-11-10 08:50 |  | 0 | 0 | 69.6 | 69.6 | 487.2 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830LOW FLOW
OF3 | 38 | U1 | 2016-11-15 15:27 |  |  |  |  | 2016-11-17 10:53 |  | 0 | 0 | 43.433 | 43.4333 | 304.033 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF3 | 39 | U1 | 2016-11-18 10:10 |  |  |  |  | 2016-11-21 08:19 |  | 0 | 0 | 70.15 | 70.15 | 491.05 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF3 | 40 | U1 | 2016-11-27 12:48 |  |  |  |  | 2016-11-29 07:55 |  | 0 | 0 | 43.117 | 43.1167 | 301.817 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF3 | 43 | U1 | 2016-12-19 17:47 |  |  |  |  | 2016-12-26 11:18 |  | 0 | 0 | 161.517 | 161.5167 | 807.583 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820HIGH WATER
OF3 | 44 | U1 | 2016-12-31 09:28 |  |  |  |  | 2017-01-01 |  | 0 | 0 | 14.533 | 14.5333 | 72.667 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF3 | 1 | U1 | 2017-01-01 |  |  |  |  | 2017-01-02 11:26 |  | 0 | 0 | 35.433 | 35.4333 | 177.167 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF3 | 2 | U1 | 2017-01-07 00:31 |  |  |  |  | 2017-01-10 12:55 |  | 0 | 0 | 84.4 | 84.4 | 422 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF3 | 3 | U1 | 2017-01-15 06:53 |  |  |  |  | 2017-01-31 13:09 |  | 0 | 0 | 390.267 | 390.2667 | 1951.333 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830HIGH WATER
OF3 | 6 | U1 | 2017-02-21 08:41 |  |  |  |  | 2017-02-21 11:09 |  | 0 | 0 | 2.467 | 2.4667 | 12.333 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9320 |  |  | - |  | Other miscellaneous external problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F82086 Genetator Lock out
OF3 | 7 | U1 | 2017-03-01 19:36 |  |  |  |  | 2017-03-14 10:20 |  | 0 | 0 | 302.733 | 302.7333 | 2119.133 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Highwater
OF3 | 13 | U1 | 2017-04-01 00:42 |  |  |  |  | 2017-04-14 08:06 |  | 0 | 0 | 319.4 | 319.4 | 2235.8 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820highwater
OF3 | 14 | U1 | 2017-04-29 05:28 |  |  |  |  | 2017-05-18 12:00 |  | 0 | 0 | 462.533 | 462.5333 | 3237.733 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820HIGH WATER
OF3 | 15 | U1 | 2017-05-25 22:25 |  |  |  |  | 2017-05-31 07:53 |  | 0 | 0 | 129.467 | 129.4667 | 906.266 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Highwater
OF3 | 16 | U1 | 2017-06-24 21:46 |  |  |  |  | 2017-06-29 08:55 |  | 0 | 0 | 107.15 | 107.15 | 857.2 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Highwater
OF3 | 17 | U1 | 2017-07-07 13:36 |  |  |  |  | 2017-07-07 14:11 |  | 0 | 0 | 0.583 | 0.5833 | 4.667 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 4650 |  |  | - |  | Other cooling system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820L. V. strainer clogged.
OF3 | 21 | U1 | 2017-08-05 20:57 |  |  |  |  | 2017-08-07 07:46 |  | 0 | 0 | 34.817 | 34.8167 | 278.533 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF3 | 22 | U1 | 2017-08-13 07:36 |  |  |  |  | 2017-08-14 07:15 |  | 0 | 0 | 23.65 | 23.65 | 189.2 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF3 | 23 | U1 | 2017-08-15 10:34 |  |  |  |  | 2017-08-16 07:10 |  | 0 | 0 | 20.6 | 20.6 | 164.8 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF3 | 24 | U1 | 2017-08-18 14:51 |  |  |  |  | 2017-08-19 07:22 |  | 0 | 0 | 16.517 | 16.5167 | 132.133 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF3 | 25 | U1 | 2017-08-28 04:40 |  |  |  |  | 2017-08-30 10:23 |  | 0 | 0 | 53.717 | 53.7167 | 429.734 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low flow
OF3 | 26 | U1 | 2017-08-31 04:50 |  |  |  |  | 2017-09-01 14:17 |  | 0 | 0 | 33.45 | 33.45 | 253.316 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830LOW FLOW
OF3 | 27 | U1 | 2017-09-03 07:34 |  |  |  |  | 2017-09-04 10:29 |  | 0 | 0 | 26.917 | 26.9167 | 188.416 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF3 | 28 | U1 | 2017-09-04 18:38 |  |  |  |  | 2017-09-05 07:21 |  | 0 | 0 | 12.717 | 12.7167 | 89.017 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF3 | 29 | U1 | 2017-09-10 22:31 |  |  |  |  | 2017-09-12 06:56 |  | 0 | 0 | 32.417 | 32.4167 | 226.916 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF3 | 30 | U1 | 2017-09-15 09:20 |  |  |  |  | 2017-09-17 08:24 |  | 0 | 0 | 47.067 | 47.0667 | 329.467 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low flow
OF3 | 32 | U1 | 2017-09-20 09:49 |  |  |  |  | 2017-09-22 07:10 |  | 0 | 0 | 45.35 | 45.35 | 317.45 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF3 | 33 | U1 | 2017-09-23 10:53 |  |  |  |  | 2017-10-09 09:03 |  | 0 | 0 | 382.167 | 382.1667 | 2675.167 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF3 | 34 | U1 | 2017-10-17 13:46 |  |  |  |  | 2017-10-19 08:49 |  | 0 | 0 | 43.05 | 43.05 | 301.35 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low river
OF3 | 35 | U1 | 2017-10-21 11:37 |  |  |  |  | 2017-10-25 13:12 |  | 0 | 0 | 97.583 | 97.5833 | 683.083 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF3 | 36 | U1 | 2017-11-06 12:09 |  |  |  |  | 2017-11-13 13:37 |  | 0 | 0 | 169.467 | 169.4667 | 1186.267 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830High River
OF3 | 37 | U1 | 2017-11-21 21:09 |  |  |  |  | 2017-11-24 08:21 |  | 0 | 0 | 59.2 | 59.2 | 414.4 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Unit tripped off due to high water and trash buildup
OF3 | 38 | U1 | 2017-11-28 20:05 |  |  |  |  | 2017-11-29 08:30 |  | 0 | 0 | 12.417 | 12.4167 | 86.917 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 4650 |  |  | - |  | Other cooling system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Cool water strainer baskets clogged
OF3 | 39 | U1 | 2017-12-18 18:59 |  |  |  |  | 2017-12-23 12:35 |  | 0 | 0 | 113.6 | 113.6 | 795.2 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low river
OF3 | 40 | U1 | 2017-12-26 07:48 |  |  |  |  | 2017-12-28 09:48 |  | 0 | 0 | 50 | 50 | 350 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830highwater
OF3 | 41 | U1 | 2017-12-29 10:26 |  |  |  |  | 2017-12-29 10:43 |  | 0 | 0 | 0.283 | 0.2833 | 1.983 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 3672 |  |  | - |  | 12-15kV conductors and buses | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830changed from bus B to bus A
OF3 | 1 | U1 | 2018-01-03 11:02 |  |  |  |  | 2018-01-05 10:03 |  | 0 | 0 | 47.017 | 47.0167 | 235.083 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Run of river
OF3 | 2 | U1 | 2018-01-10 14:46 |  |  |  |  | 2018-01-11 14:56 |  | 0 | 0 | 24.167 | 24.1667 | 120.834 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF3 | 3 | U1 | 2018-01-14 04:20 |  |  |  |  | 2018-01-20 12:44 |  | 0 | 0 | 152.4 | 152.4 | 762 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF3 | 4 | U1 | 2018-01-24 08:34 |  |  |  |  | 2018-02-01 13:00 |  | 0 | 0 | 196.433 | 196.4333 | 982.167 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830highwater
OF3 | 5 | U1 | 2018-02-08 20:11 |  |  |  |  | 2018-03-12 10:29 |  | 0 | 0 | 758.3 | 758.3 | 4340.466 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830High River
OF3 | 6 | U1 | 2018-03-23 12:54 |  |  |  |  | 2018-04-15 11:26 |  | 0 | 0 | 550.533 | 550.5333 | 3853.733 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830highwater
OF3 | 7 | U1 | 2018-04-17 03:19 |  |  |  |  | 2018-04-30 13:42 |  | 0 | 0 | 322.383 | 322.3833 | 2256.683 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820highwater
OF3 | 8 | U1 | 2018-05-08 06:53 |  |  |  |  | 2018-05-12 09:51 |  | 0 | 0 | 98.967 | 98.9667 | 692.767 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF3 | 9 | U1 | 2018-05-21 06:59 |  |  |  |  | 2018-05-21 13:46 |  | 0 | 0 | 6.783 | 6.7833 | 47.483 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater / Trash
OF3 | 10 | U1 | 2018-05-21 22:55 |  |  |  |  | 2018-05-28 09:27 |  | 0 | 0 | 154.533 | 154.5333 | 1081.733 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Trash and Highwater
OF3 | 13 | U1 | 2018-06-09 15:50 |  |  |  |  | 2018-06-09 16:56 |  | 0 | 0 | 1.1 | 1.1 | 8.8 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7053 |  |  | - |  | Governor oil system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820GPU Accumulator trip
OF3 | 14 | U1 | 2018-06-09 18:29 |  |  |  |  | 2018-06-10 07:57 |  | 0 | 0 | 13.467 | 13.4667 | 107.733 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7053 |  |  | - |  | Governor oil system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820GPU Accumulator trip
OF3 | 16 | U1 | 2018-06-25 00:40 |  |  |  |  | 2018-06-27 12:22 |  | 0 | 0 | 59.7 | 59.7 | 477.6 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Highwater
OF3 | 18 | U1 | 2018-07-11 07:16 |  |  |  |  | 2018-07-19 07:12 |  | 0 | 0 | 191.933 | 191.9333 | 1535.467 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF3 | 19 | U1 | 2018-07-20 13:07 |  |  |  |  | 2018-08-01 07:00 |  | 0 | 0 | 281.883 | 281.8833 | 2255.067 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low flow
OF3 | 22 | U1 | 2018-08-20 08:22 |  |  |  |  | 2018-08-20 14:44 |  | 0 | 0 | 6.367 | 6.3667 | 50.933 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830trash
OF3 | 23 | U1 | 2018-08-29 11:52 |  |  |  |  | 2018-08-30 06:53 |  | 0 | 0 | 19.017 | 19.0167 | 152.134 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low water flow
OF3 | 24 | U1 | 2018-09-09 03:59 |  |  |  |  | 2018-09-17 11:12 |  | 0 | 0 | 199.217 | 199.2167 | 1394.517 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Highwater
OF3 | 25 | U1 | 2018-09-19 16:30 |  |  |  |  | 2018-09-24 10:22 |  | 0 | 0 | 113.867 | 113.8667 | 797.067 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF3 | 26 | U1 | 2018-09-24 22:07 |  |  |  |  | 2018-10-04 10:00 |  | 0 | 0 | 227.883 | 227.8833 | 1595.183 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820high water
OF3 | 27 | U1 | 2018-10-10 08:01 |  |  |  |  | 2018-10-11 07:27 |  | 0 | 0 | 23.433 | 23.4333 | 164.033 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Trash in front of facility Intakes
OF3 | 28 | U1 | 2018-10-11 11:43 |  |  |  |  | 2018-10-11 13:01 |  | 0 | 0 | 1.3 | 1.3 | 9.1 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for trash removal
OF3 | 29 | U1 | 2018-10-12 13:16 |  |  |  |  | 2018-10-13 11:53 |  | 0 | 0 | 22.617 | 22.6167 | 158.316 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Trash
OF3 | 30 | U1 | 2018-10-14 18:44 |  |  |  |  | 2018-10-14 19:12 |  | 0 | 0 | 0.467 | 0.4667 | 3.267 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for trash and Brage removal
OF3 | 31 | U1 | 2018-10-21 17:18 |  |  |  |  | 2018-10-21 18:06 |  | 0 | 0 | 0.8 | 0.8 | 5.6 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 3814 |  |  | - |  | Service water system fouling | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Clogged L. V. bearing strainer .
OF3 | 33 | U1 | 2018-11-02 05:29 |  |  |  |  | 2018-12-09 15:38 |  | 0 | 0 | 898.15 | 898.15 | 5871.784 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF3 | 34 | U1 | 2018-12-17 13:41 |  |  |  |  | 2019-01-01 |  | 0 | 0 | 346.317 | 346.3167 | 1731.583 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830high water
OF3 | 1 | U1 | 2019-01-01 |  |  |  |  | 2019-01-15 13:34 |  | 0 | 0 | 349.567 | 349.5667 | 1747.833 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Highwater
OF3 | 2 | U1 | 2019-01-20 16:35 |  |  |  |  | 2019-01-31 23:59 |  | 0 | 0 | 271.4 | 271.4 | 1357 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830high water
OF3 | 3 | U1 | 2019-02-01 |  |  |  |  | 2019-02-03 14:04 |  | 0 | 0 | 62.067 | 62.0667 | 310.333 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF3 | 4 | U1 | 2019-02-07 07:40 |  |  |  |  | 2019-03-08 11:13 |  | 0 | 0 | 699.55 | 699.55 | 3856.184 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830highwater
OF3 | 5 | U1 | 2019-03-10 12:32 |  |  |  |  | 2019-03-19 12:35 |  | 0 | 0 | 216.05 | 216.05 | 1512.35 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF3 | 6 | U1 | 2019-03-27 03:07 |  |  |  |  | 2019-03-27 10:04 |  | 0 | 0 | 6.95 | 6.95 | 48.65 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820trash
OF3 | 9 | U1 | 2019-04-19 11:32 |  |  |  |  | 2019-05-10 07:33 |  | 0 | 0 | 500.017 | 500.0167 | 3500.117 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF3 | 10 | U1 | 2019-05-14 06:08 |  |  |  |  | 2019-05-14 10:06 |  | 0 | 0 | 3.967 | 3.9667 | 27.767 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Trash
OF3 | 11 | U1 | 2019-05-15 11:46 |  |  |  |  | 2019-05-20 09:49 |  | 0 | 0 | 118.05 | 118.05 | 826.35 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Trash
OF3 | 12 | U1 | 2019-06-01 06:04 |  |  |  |  | 2019-06-04 12:28 |  | 0 | 0 | 78.4 | 78.4 | 627.2 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF3 | 13 | U1 | 2019-06-17 00:18 |  |  |  |  | 2019-06-28 12:46 |  | 0 | 0 | 276.467 | 276.4667 | 2211.733 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820highwater
OF3 | 14 | U1 | 2019-07-23 06:38 |  |  |  |  | 2019-07-23 15:06 |  | 0 | 0 | 8.467 | 8.4667 | 67.733 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830trash
OF3 | 15 | U1 | 2019-07-29 17:22 |  |  |  |  | 2019-07-30 07:39 |  | 0 | 0 | 14.283 | 14.2833 | 114.267 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low water
OF3 | 16 | U1 | 2019-07-31 06:18 |  |  |  |  | 2019-08-01 10:16 |  | 0 | 0 | 27.967 | 27.9667 | 223.733 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low water
OF3 | 17 | U1 | 2019-08-02 15:00 |  |  |  |  | 2019-08-09 07:00 |  | 0 | 0 | 160 | 160 | 1280 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF3 | 18 | U1 | 2019-08-11 14:37 |  |  |  |  | 2019-08-14 10:24 |  | 0 | 0 | 67.783 | 67.7833 | 542.267 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF3 | 19 | U1 | 2019-08-15 12:20 |  |  |  |  | 2019-10-08 07:00 |  | 0 | 0 | 1290.667 | 1290.6667 | 9430.333 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low flow
OF3 | 20 | U1 | 2019-10-09 16:15 |  |  |  |  | 2019-10-11 08:52 |  | 0 | 0 | 40.617 | 40.6167 | 284.317 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow Offline per ACOE Request
OF3 | 21 | U1 | 2019-10-11 22:02 |  |  |  |  | 2019-10-28 09:52 |  | 0 | 0 | 395.833 | 395.8333 | 2770.834 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Water, Offline per request of ACOE
OF3 | 23 | U1 | 2019-12-03 01:31 |  |  |  |  | 2019-12-06 09:53 |  | 0 | 0 | 80.367 | 80.3667 | 401.834 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820highwater
OF3 | 24 | U1 | 2019-12-14 12:02 |  |  |  |  | 2019-12-24 13:11 |  | 0 | 0 | 241.15 | 241.15 | 1205.75 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830highwater
OF3 | 25 | U1 | 2019-12-31 11:45 |  |  |  |  | 2019-12-31 23:59 |  | 0 | 0 | 12.233 | 12.2333 | 61.167 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Highwater
OF3 | 1 | U1 | 2020-01-01 |  |  |  |  | 2020-01-10 14:52 |  | 0 | 0 | 230.867 | 230.8667 | 1154.333 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Highwater
OF3 | 2 | U1 | 2020-01-14 09:56 |  |  |  |  | 2020-01-18 13:48 |  | 0 | 0 | 99.867 | 99.8667 | 499.333 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830High River
OF3 | 3 | U1 | 2020-01-27 18:41 |  |  |  |  | 2020-02-01 12:59 |  | 0 | 0 | 114.3 | 114.3 | 571.5 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830highwater
OF3 | 4 | U1 | 2020-02-08 12:28 |  |  |  |  | 2020-02-24 10:38 |  | 0 | 0 | 382.167 | 382.1667 | 1910.834 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Highwater
OF3 | 5 | U1 | 2020-03-05 15:09 |  |  |  |  | 2020-03-10 12:08 |  | 0 | 0 | 116.983 | 116.9833 | 818.883 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Trash
OF3 | 6 | U1 | 2020-03-15 10:05 |  |  |  |  | 2020-04-06 12:12 |  | 0 | 0 | 530.117 | 530.1167 | 3710.817 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF3 | 7 | U1 | 2020-04-13 22:29 |  |  |  |  | 2020-04-22 10:06 |  | 0 | 0 | 203.617 | 203.6167 | 1425.317 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for highwater
OF3 | 8 | U1 | 2020-04-28 14:12 |  |  |  |  | 2020-05-12 12:39 |  | 0 | 0 | 334.45 | 334.45 | 2341.15 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Highwater
OF3 | 9 | U1 | 2020-05-20 08:35 |  |  |  |  | 2020-05-30 07:45 |  | 0 | 0 | 239.167 | 239.1667 | 1674.167 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF3 | 10 | U1 | 2020-06-10 09:46 |  |  |  |  | 2020-06-10 17:19 |  | 0 | 0 | 7.55 | 7.55 | 60.4 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for trash
OF3 | 11 | U1 | 2020-06-10 17:19 |  |  |  |  | 2020-06-17 12:45 |  | 0 | 0 | 163.433 | 163.4333 | 1307.467 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 3710 |  |  | - |  | Transmission line (connected to powerhouse switchyard to 1st Substation) | [8 empty] | AMP CODE: |  | X0
|  | DESCRIPTION : |  | F830Transmission Outage
OF3 | 12 | U1 | 2020-06-26 06:17 |  |  |  |  | 2020-06-26 12:23 |  | 0 | 0 | 6.1 | 6.1 | 48.8 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9350 |  |  | - |  | Public Safety (water hazard or river rescue) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F590ACOE requested shutdown for safety while they are working on the lower dam.
OF3 | 14 | U1 | 2020-07-05 04:48 |  |  |  |  | 2020-07-31 07:21 |  | 0 | 0 | 626.55 | 626.55 | 5012.4 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830lack of water
OF3 | 15 | U1 | 2020-07-31 07:21 |  |  |  |  | 2020-08-04 19:34 |  | 0 | 0 | 108.217 | 108.2167 | 865.733 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 3710 |  |  | - |  | Transmission line (connected to powerhouse switchyard to 1st Substation) | [8 empty] | AMP CODE: |  | X0
|  | DESCRIPTION : |  | F830trans line
OF3 | 16 | U1 | 2020-08-04 19:34 |  |  |  |  | 2020-08-16 10:01 |  | 0 | 0 | 278.45 | 278.45 | 2227.6 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | X0
|  | DESCRIPTION : |  | F830Lack of Water (ACOE Request)
OF3 | 19 | U1 | 2020-10-23 10:00 |  |  |  |  | 2020-10-29 11:22 |  | 0 | 0 | 145.367 | 145.3667 | 1017.567 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | X0
|  | DESCRIPTION : |  | F830Low river
OF3 | 20 | U1 | 2020-11-02 08:27 |  |  |  |  | 2020-11-02 14:28 |  | 0 | 0 | 6.017 | 6.0167 | 42.117 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 3710 |  |  | - |  | Transmission line (connected to powerhouse switchyard to 1st Substation) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Transformer Outage
OF3 | 21 | U1 | 2020-11-05 12:59 |  |  |  |  | 2020-11-05 16:08 |  | 0 | 0 | 3.15 | 3.15 | 22.05 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 3710 |  |  | - |  | Transmission line (connected to powerhouse switchyard to 1st Substation) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Switching Bus
OF3 | 22 | U1 | 2020-11-13 07:50 |  |  |  |  | 2020-11-13 08:39 |  | 0 | 0 | 0.817 | 0.8167 | 5.717 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Trash build up, repositioned unit intake to distribute trash for better efficiency
OF3 | 24 | U1 | 2020-12-16 11:01 |  |  |  |  | 2020-12-16 17:00 |  | 0 | 0 | 5.983 | 5.9833 | 29.917 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9350 |  |  | - |  | Public Safety (water hazard or river rescue) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Diesel fuel in upper pool
OF3 | 25 | U1 | 2020-12-27 21:09 |  |  |  |  | 2021-01-01 |  | 0 | 0 | 98.85 | 98.85 | 494.25 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF3 | 1 | U1 | 2021-01-01 |  |  |  |  | 2021-01-11 11:50 |  | 0 | 0 | 251.833 | 251.8333 | 3173.1 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for highwater
OF3 | 3 | U1 | 2021-01-27 20:17 |  |  |  |  | 2021-02-05 11:01 |  | 0 | 0 | 206.733 | 206.7333 | 2604.84 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Offline for highwater
OF3 | 4 | U1 | 2021-02-24 19:21 |  |  |  |  | 2021-03-12 11:51 |  | 0 | 0 | 376.5 | 376.5 | 4743.9 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF3 | 5 | U1 | 2021-03-20 06:04 |  |  |  |  | 2021-03-24 07:59 |  | 0 | 0 | 97.917 | 97.9167 | 1233.75 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830high water
OF3 | 6 | U1 | 2021-03-31 06:13 |  |  |  |  | 2021-04-05 09:26 |  | 0 | 0 | 123.217 | 123.2167 | 1552.53 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Highwater
OF3 | 14 | U1 | 2021-06-15 07:51 |  |  |  |  | 2021-06-15 13:27 |  | 0 | 0 | 5.6 | 5.6 | 70.56 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for trash.
OF3 | 15 | U1 | 2021-06-16 17:31 |  |  |  |  | 2021-06-17 07:29 |  | 0 | 0 | 13.967 | 13.9667 | 175.98 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7053 |  |  | - |  | Governor oil system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Unit tripped offline for Gov. Accum Piston A Lower.
OF3 | 16 | U1 | 2021-06-20 02:50 |  |  |  |  | 2021-06-21 08:54 |  | 0 | 0 | 30.067 | 30.0667 | 378.84 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for trash.
OF3 | 18 | U1 | 2021-06-27 10:16 |  |  |  |  | 2021-06-28 09:39 |  | 0 | 0 | 23.383 | 23.3833 | 294.63 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830ACOE requested, Lack of Water
OF3 | 20 | U1 | 2021-06-29 09:00 |  |  |  |  | 2021-07-01 07:35 |  | 0 | 0 | 46.583 | 46.5833 | 586.95 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | FR
|  | DESCRIPTION : |  | F830Unit offline for Lack of Water, Run of River per ACOE
OF3 | 23 | U1 | 2021-07-09 06:30 |  |  |  |  | 2021-07-13 09:37 |  | 0 | 0 | 99.117 | 99.1167 | 1248.87 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | FR
|  | DESCRIPTION : |  | F830Unit offline for run of river lack of water.
OF3 | 24 | U1 | 2021-07-20 10:47 |  |  |  |  | 2021-07-20 11:08 |  | 0 | 0 | 0.35 | 0.35 | 4.41 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 4609 |  |  | - |  | Other exciter problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Field Ground Detected.
OF3 | 25 | U1 | 2021-08-04 08:26 |  |  |  |  | 2021-08-13 10:20 |  | 0 | 0 | 217.9 | 217.9 | 2745.54 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Lack of Water
OF3 | 28 | U1 | 2021-08-18 06:30 |  |  |  |  | 2021-08-18 07:53 |  | 0 | 0 | 1.383 | 1.3833 | 17.43 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | FR
|  | DESCRIPTION : |  | F830Run of River
OF3 | 30 | U1 | 2021-09-03 10:40 |  |  |  |  | 2021-09-06 07:30 |  | 0 | 0 | 68.833 | 68.8333 | 867.3 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for High Water
OF3 | 31 | U1 | 2021-09-14 18:05 |  |  |  |  | 2021-09-18 08:22 |  | 0 | 0 | 86.283 | 86.2833 | 1087.17 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Lack of Water (ACOE)
OF3 | 32 | U1 | 2021-09-18 23:15 |  |  |  |  | 2021-09-24 13:26 |  | 0 | 0 | 134.183 | 134.1833 | 1690.71 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Lack of Water
OF3 | 33 | U1 | 2021-10-03 11:30 |  |  |  |  | 2021-10-04 06:48 |  | 0 | 0 | 19.3 | 19.3 | 243.18 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 3979 |  |  | - |  | Other DCS problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Remote Connection to Cane Run 7 Lost, Unable to leave unit online unattended
OF3 | 34 | U1 | 2021-10-04 06:58 |  |  |  |  | 2021-10-04 07:06 |  | 0 | 0 | 0.133 | 0.1333 | 1.68 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9900 |  |  | - |  | Operator error | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Tripped Unit Manually due to operator error with DCS System.
OF3 | 35 | U1 | 2021-10-12 15:09 |  |  |  |  | 2021-10-14 07:07 |  | 0 | 0 | 39.967 | 39.9667 | 503.58 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Lack of Water (ACOE)
OF3 | 39 | U1 | 2021-12-13 04:19 |  |  |  |  | 2021-12-15 08:53 |  | 0 | 0 | 52.567 | 52.5667 | 662.34 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Run of RIver - Highwater
OF3 | 40 | U1 | 2021-12-31 08:39 |  |  |  |  | 2022-01-01 |  | 0 | 0 | 15.35 | 15.35 | 193.41 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820High Water.
OF3 | 1 | U1 | 2022-01-01 |  |  |  |  | 2022-01-16 13:01 |  | 0 | 0 | 373.017 | 373.0167 | 4700.01 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Offline for High Water.
OF3 | 2 | U1 | 2022-01-31 09:49 |  |  |  |  | 2022-02-01 10:52 |  | 0 | 0 | 25.05 | 25.05 | 315.63 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Trash (Run of River)
OF3 | 4 | U1 | 2022-02-04 11:51 |  |  |  |  | 2022-02-14 13:58 |  | 0 | 0 | 242.117 | 242.1167 | 3050.67 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | FR
|  | DESCRIPTION : |  | F830Offline for High Water
OF3 | 5 | U1 | 2022-02-16 08:06 |  |  |  |  | 2022-03-21 07:22 |  | 0 | 0 | 791.267 | 791.2667 | 9969.96 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Trash / Highwater (Run of River)
OF3 | 8 | U1 | 2022-04-10 06:34 |  |  |  |  | 2022-04-18 07:35 |  | 0 | 0 | 193.017 | 193.0167 | 2432.01 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for High Water
OF3 | 9 | U1 | 2022-05-07 13:48 |  |  |  |  | 2022-05-16 09:36 |  | 0 | 0 | 211.8 | 211.8 | 2668.68 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for High Water.
OF3 | 10 | U1 | 2022-05-30 07:09 |  |  |  |  | 2022-06-01 07:45 |  | 0 | 0 | 48.6 | 48.6 | 612.36 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for high water.
OF3 | 11 | U1 | 2022-06-22 17:30 |  |  |  |  | 2022-06-24 06:56 |  | 0 | 0 | 37.433 | 37.4333 | 471.66 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Lack of Water (Run of River) by the ACOE
OF3 | 12 | U1 | 2022-06-25 03:56 |  |  |  |  | 2022-06-28 07:24 |  | 0 | 0 | 75.467 | 75.4667 | 950.88 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Lack of Water-Run of River per the ACOE
OF3 | 13 | U1 | 2022-07-01 05:31 |  |  |  |  | 2022-07-05 12:49 |  | 0 | 0 | 103.3 | 103.3 | 1301.58 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for lack of water.
OF3 | 14 | U1 | 2022-07-06 10:48 |  |  |  |  | 2022-07-07 07:34 |  | 0 | 0 | 20.767 | 20.7667 | 261.66 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline lack of water.
OF3 | 15 | U1 | 2022-07-16 13:59 |  |  |  |  | 2022-07-19 06:54 |  | 0 | 0 | 64.917 | 64.9167 | 817.95 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Run of River (Lack of Water) per the ACOE
OF3 | 17 | U1 | 2022-08-02 06:49 |  |  |  |  | 2022-08-02 13:42 |  | 0 | 0 | 6.883 | 6.8833 | 86.73 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Trash
OF3 | 19 | U1 | 2022-08-19 14:17 |  |  |  |  | 2022-08-23 07:32 |  | 0 | 0 | 89.25 | 89.25 | 1124.55 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7053 |  |  | - |  | Governor oil system | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830G.P.U. pressure issue
OF3 | 20 | U1 | 2022-08-23 10:57 |  |  |  |  | 2022-08-23 13:51 |  | 0 | 0 | 2.9 | 2.9 | 36.54 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Trash (Run of River)
OF3 | 21 | U1 | 2022-08-26 22:15 |  |  |  |  | 2022-08-29 14:17 |  | 0 | 0 | 64.033 | 64.0333 | 806.82 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Lack of Water
OF3 | 22 | U1 | 2022-08-29 16:40 |  |  |  |  | 2022-08-30 12:56 |  | 0 | 0 | 20.267 | 20.2667 | 255.36 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 3672 |  |  | - |  | 12-15kV conductors and buses | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F49014KV Bus A Lockout
OF3 | 23 | U1 | 2022-09-02 06:22 |  |  |  |  | 2022-09-04 08:09 |  | 0 | 0 | 49.783 | 49.7833 | 627.27 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Lack of Water
OF3 | 24 | U1 | 2022-09-04 17:53 |  |  |  |  | 2022-09-06 09:15 |  | 0 | 0 | 39.367 | 39.3667 | 496.02 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Lack of Water.
OF3 | 25 | U1 | 2022-09-06 13:01 |  |  |  |  | 2022-09-07 07:16 |  | 0 | 0 | 18.25 | 18.25 | 229.95 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Trash / Run of River
OF3 | 26 | U1 | 2022-09-13 05:02 |  |  |  |  | 2022-09-13 14:19 |  | 0 | 0 | 9.283 | 9.2833 | 116.97 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Trash
OF3 | 27 | U1 | 2022-09-18 08:01 |  |  |  |  | 2022-09-23 10:48 |  | 0 | 0 | 122.783 | 122.7833 | 1547.07 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Lack of Water
OF3 | 28 | U1 | 2022-09-25 10:30 |  |  |  |  | 2022-09-28 06:58 |  | 0 | 0 | 68.467 | 68.4667 | 862.68 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for low water.
OF3 | 29 | U1 | 2022-09-28 18:53 |  |  |  |  | 2022-09-30 12:47 |  | 0 | 0 | 41.9 | 41.9 | 527.94 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830lack of water
OF3 | 30 | U1 | 2022-10-08 04:53 |  |  |  |  | 2022-10-12 07:01 |  | 0 | 0 | 98.133 | 98.1333 | 1236.48 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Lack of Water.
OF3 | 31 | U1 | 2022-10-12 16:54 |  |  |  |  | 2022-11-12 14:13 |  | 0 | 0 | 741.317 | 741.3167 | 9340.59 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Lack of Water
OF3 | 32 | U1 | 2022-11-27 11:57 |  |  |  |  | 2022-11-28 07:50 |  | 0 | 0 | 19.883 | 19.8833 | 250.53 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Lack of Water
OF3 | 33 | U1 | 2022-12-11 08:13 |  |  |  |  | 2022-12-12 08:27 |  | 0 | 0 | 24.233 | 24.2333 | 305.34 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830trash
OF3 | 34 | U1 | 2022-12-23 16:49 |  |  |  |  | 2022-12-27 13:39 |  | 0 | 0 | 92.833 | 92.8333 | 1169.7 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9036 |  |  | - |  | "Storms (ice, snow, etc)" | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Army Corps gates not operating due to freezing temperatures. Unit shut down to mai
OF3 | 35 | U1 | 2022-12-29 15:10 |  |  |  |  | 2022-12-29 16:20 |  | 0 | 0 | 1.167 | 1.1667 | 14.7 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 7053 |  |  | - |  | Governor oil system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Governor Accumulator Piston A Lower Trip
OF3 | 1 | U1 | 2023-01-03 13:51 |  |  |  |  | 2023-01-09 12:16 |  | 0 | 0 | 142.417 | 142.4167 | 1794.45 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Offline for trash.
OF3 | 2 | U1 | 2023-01-13 23:00 |  |  |  |  | 2023-01-27 11:58 |  | 0 | 0 | 324.967 | 324.9667 | 4094.58 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830trash
OF3 | 3 | U1 | 2023-01-29 04:49 |  |  |  |  | 2023-01-29 14:55 |  | 0 | 0 | 10.1 | 10.1 | 127.26 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Offline for high water.
OF3 | 4 | U1 | 2023-01-30 14:47 |  |  |  |  | 2023-01-31 10:19 |  | 0 | 0 | 19.533 | 19.5333 | 246.12 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830trash
OF3 | 5 | U1 | 2023-02-03 12:09 |  |  |  |  | 2023-02-07 11:13 |  | 0 | 0 | 95.067 | 95.0667 | 1197.84 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9320 |  |  | - |  | Other miscellaneous external problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830barge recovery
OF3 | 7 | U1 | 2023-02-17 08:31 |  |  |  |  | 2023-02-24 13:19 |  | 0 | 0 | 172.8 | 172.8 | 2177.28 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for High Water
OF3 | 8 | U1 | 2023-03-02 20:00 |  |  |  |  | 2023-03-13 11:29 |  | 0 | 0 | 255.483 | 255.4833 | 3219.09 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for High Water
OF3 | 9 | U1 | 2023-03-24 20:02 |  |  |  |  | 2023-04-11 06:30 |  | 0 | 0 | 418.467 | 418.4667 | 5272.68 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for High Water.
OF3 | 10 | U1 | 2023-04-11 06:30 |  |  |  |  | 2023-04-28 13:22 |  | 0 | 0 | 414.867 | 414.8667 | 5227.32 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9320 |  |  | - |  | Other miscellaneous external problems | [8 empty] | AMP CODE: |  | FR
|  | DESCRIPTION : |  | FX00Barge Recovery
OF3 | 11 | U1 | 2023-05-24 16:23 |  |  |  |  | 2023-05-31 07:00 |  | 0 | 0 | 158.617 | 158.6167 | 1998.57 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Lack of Water
OF3 | 12 | U1 | 2023-06-08 10:21 |  |  |  |  | 2023-06-17 07:11 |  | 0 | 0 | 212.833 | 212.8333 | 2681.7 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830lack of water
OF3 | 13 | U1 | 2023-06-20 04:41 |  |  |  |  | 2023-06-21 06:18 |  | 0 | 0 | 25.617 | 25.6167 | 322.77 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline lack of water.
OF3 | 14 | U1 | 2023-06-21 23:02 |  |  |  |  | 2023-06-22 13:48 |  | 0 | 0 | 14.767 | 14.7667 | 186.06 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline lack of water.
OF3 | 15 | U1 | 2023-06-23 12:57 |  |  |  |  | 2023-06-25 07:05 |  | 0 | 0 | 42.133 | 42.1333 | 530.88 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline lack of water.
OF3 | 16 | U1 | 2023-06-26 07:29 |  |  |  |  | 2023-06-26 16:00 |  | 0 | 0 | 8.517 | 8.5167 | 107.31 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for MSI sonar.
OF3 | 17 | U1 | 2023-06-26 16:00 |  |  |  |  | 2023-07-02 07:34 |  | 0 | 0 | 135.567 | 135.5667 | 1708.14 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | FR
|  | DESCRIPTION : |  | F830lack of water
OF3 | 18 | U1 | 2023-07-07 07:53 |  |  |  |  | 2023-07-07 13:31 |  | 0 | 0 | 5.633 | 5.6333 | 70.98 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Trash
OF3 | 19 | U1 | 2023-07-08 12:37 |  |  |  |  | 2023-07-16 08:18 |  | 0 | 0 | 187.683 | 187.6833 | 2364.81 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for lack of water
OF3 | 20 | U1 | 2023-07-24 08:55 |  |  |  |  | 2023-07-25 06:45 |  | 0 | 0 | 21.833 | 21.8333 | 275.1 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for lack of water
OF3 | 21 | U1 | 2023-07-31 07:00 |  |  |  |  | 2023-08-07 09:00 |  | 0 | 0 | 170 | 170 | 2142 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline lack of water.
OF3 | 23 | U1 | 2023-08-17 21:57 |  |  |  |  | 2023-08-26 07:02 |  | 0 | 0 | 201.083 | 201.0833 | 2533.65 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for lack of water
OF3 | 24 | U1 | 2023-09-02 15:01 |  |  |  |  | 2023-09-09 05:30 |  | 0 | 0 | 158.483 | 158.4833 | 1996.89 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Lack of water
OF3 | 26 | U1 | 2023-09-23 06:24 |  |  |  |  | 2023-11-01 12:05 |  | 0 | 0 | 941.683 | 941.6833 | 11865.21 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | FR
|  | DESCRIPTION : |  | F830lack of water
OF3 | 27 | U1 | 2023-11-05 06:12 |  |  |  |  | 2023-11-21 08:23 |  | 0 | 0 | 386.183 | 386.1833 | 4865.91 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830lack of water
OF3 | 28 | U1 | 2023-12-03 14:15 |  |  |  |  | 2023-12-05 07:10 |  | 0 | 0 | 40.917 | 40.9167 | 515.55 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830lack of water
OF3 | 29 | U1 | 2023-12-30 01:28 |  |  |  |  | 2023-12-30 08:13 |  | 0 | 0 | 6.75 | 6.75 | 85.05 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 7007 |  |  | - |  | Bearings | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Turbine Bearing Flow Trip (Strainer)
Ohio Falls - OF4
Unit | Event | Type | Start |  |  |  |  | End |  | GAC | NAC | Duration | Equiv Hrs | Equiv MWH | Cont | Work Start | Work End |  | Hours |  |  | Gross Capacity Impact (MW)
OF4 | 1 | U1 | 2014-01-01 |  |  |  |  | 2014-01-05 13:19 |  | 0 | 0 | 109.317 | 109.3167 | 437.267 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830High water.
OF4 | 2 | U1 | 2014-01-12 11:58 |  |  |  |  | 2014-01-20 13:17 |  | 0 | 0 | 193.317 | 193.3167 | 773.266 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF4 | 3 | U1 | 2014-02-05 10:15 |  |  |  |  | 2014-02-12 14:40 |  | 0 | 0 | 172.417 | 172.4167 | 689.667 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF4 | 4 | U1 | 2014-02-20 14:04 |  |  |  |  | 2014-03-03 13:36 |  | 0 | 0 | 263.533 | 263.5333 | 1054.133 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF4 | 5 | U1 | 2014-03-10 07:05 |  |  |  |  | 2014-03-11 10:04 |  | 0 | 0 | 26.983 | 26.9833 | 107.934 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Trash isuses.
OF4 | 6 | U1 | 2014-03-15 08:36 |  |  |  |  | 2014-03-18 12:37 |  | 0 | 0 | 76.017 | 76.0167 | 304.067 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830High water.
OF4 | 7 | U1 | 2014-04-03 06:33 |  |  |  |  | 2014-04-14 12:44 |  | 0 | 0 | 270.183 | 270.1833 | 1621.1 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF4 | 8 | U1 | 2014-04-22 14:30 |  |  |  |  | 2014-04-22 15:52 |  | 0 | 0 | 1.367 | 1.3667 | 8.2 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7200 |  |  | - |  | Major overhaul (use for non-specific overhaul only; see page B-CCGT-2) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Moving heavy load over gen. Due to rehab on gen. 5
OF4 | 9 | U1 | 2014-04-22 23:05 |  |  |  |  | 2014-04-23 07:09 |  | 0 | 0 | 8.067 | 8.0667 | 48.4 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 4560 |  |  | - |  | Generator vibration (excluding vibration due to failed bearing and other components) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Speed probes detected over speed of unit, causing vibration.
OF4 | 10 | U1 | 2014-04-23 21:51 |  |  |  |  | 2014-04-24 07:16 |  | 0 | 0 | 9.417 | 9.4167 | 56.5 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 3644 |  |  | - |  | AC Protection devices | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F82086 lockout relay.
OF4 | 11 | U1 | 2014-04-24 08:26 |  |  |  |  | 2014-04-24 09:54 |  | 0 | 0 | 1.467 | 1.4667 | 8.8 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 3644 |  |  | - |  | AC Protection devices | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F82086 lockout relay
OF4 | 12 | U1 | 2014-04-30 12:41 |  |  |  |  | 2014-05-07 10:18 |  | 0 | 0 | 165.617 | 165.6167 | 993.7 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF4 | 14 | U1 | 2014-05-16 13:20 |  |  |  |  | 2014-05-25 09:35 |  | 0 | 0 | 212.25 | 212.25 | 1273.5 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF4 | 15 | U1 | 2014-05-28 08:35 |  |  |  |  | 2014-05-28 16:54 |  | 0 | 0 | 8.317 | 8.3167 | 49.9 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7190 |  |  | - |  | Dewatering and rewatering equipment | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Divers in water setting up dewatering pumps,too much turbulance with units running
OF4 | 16 | U1 | 2014-05-29 10:47 |  |  |  |  | 2014-05-29 15:08 |  | 0 | 0 | 4.35 | 4.35 | 26.1 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7190 |  |  | - |  | Dewatering and rewatering equipment | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Divers in the water,too much turbulance
OF4 | 17 | U1 | 2014-05-30 07:32 |  |  |  |  | 2014-05-30 14:39 |  | 0 | 0 | 7.117 | 7.1167 | 42.7 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7190 |  |  | - |  | Dewatering and rewatering equipment | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Divers in the water, too much turbulance from units running
OF4 | 18 | U1 | 2014-06-04 12:29 |  |  |  |  | 2014-06-05 06:58 |  | 0 | 0 | 18.483 | 18.4833 | 110.9 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830LOW RIVER
OF4 | 19 | U1 | 2014-07-09 10:37 |  |  |  |  | 2014-07-10 07:06 |  | 0 | 0 | 20.483 | 20.4833 | 122.9 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830USACE had us take Unit off for low river conditions.
OF4 | 20 | U1 | 2014-07-11 06:16 |  |  |  |  | 2014-07-14 07:25 |  | 0 | 0 | 73.15 | 73.15 | 438.9 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830USACE HAD US TAKE A UNIT OFF DUE TO LOW RIVER CONDITIONS.
OF4 | 21 | U1 | 2014-07-22 07:40 |  |  |  |  | 2014-07-22 13:22 |  | 0 | 0 | 5.7 | 5.7 | 34.2 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9590 |  |  | - |  | Miscellaneous regulatory (this code is primarily intended for use with event contribution code 2 to indicate that a regulatory-related factor contributed to the primary cause of the event) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Ferc diver inspection
OF4 | 22 | U1 | 2014-07-23 18:22 |  |  |  |  | 2014-07-24 07:42 |  | 0 | 0 | 13.333 | 13.3333 | 80 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF4 | 23 | U1 | 2014-07-25 09:03 |  |  |  |  | 2014-07-28 11:05 |  | 0 | 0 | 74.033 | 74.0333 | 444.2 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF4 | 24 | U1 | 2014-08-04 04:15 |  |  |  |  | 2014-08-05 07:40 |  | 0 | 0 | 27.417 | 27.4167 | 164.5 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830L/F
OF4 | 26 | U1 | 2014-08-18 14:20 |  |  |  |  | 2014-08-19 09:21 |  | 0 | 0 | 19.017 | 19.0167 | 114.1 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830LOW FLOW
OF4 | 27 | U1 | 2014-08-31 09:25 |  |  |  |  | 2014-09-02 10:39 |  | 0 | 0 | 49.233 | 49.2333 | 295.4 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830LOW RIVER
OF4 | 28 | U1 | 2014-09-10 10:33 |  |  |  |  | 2014-09-11 06:51 |  | 0 | 0 | 20.3 | 20.3 | 121.8 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF4 | 29 | U1 | 2014-09-16 13:41 |  |  |  |  | 2014-09-23 06:47 |  | 0 | 0 | 161.1 | 161.1 | 966.6 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF4 | 30 | U1 | 2014-09-23 13:59 |  |  |  |  | 2014-10-01 10:45 |  | 0 | 0 | 188.767 | 188.7667 | 1111.1 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF4 | 31 | U1 | 2014-10-02 14:21 |  |  |  |  | 2014-10-06 07:27 |  | 0 | 0 | 89.1 | 89.1 | 356.4 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low flow
OF4 | 33 | U1 | 2014-10-09 11:54 |  |  |  |  | 2014-10-10 07:43 |  | 0 | 0 | 19.817 | 19.8167 | 79.267 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low river
OF4 | 39 | U1 | 2014-12-04 07:39 |  |  |  |  | 2014-12-04 08:25 |  | 0 | 0 | 0.767 | 0.7667 | 3.067 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 4730 |  |  | - |  | Generator current and potential transformers | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Had to tie in the currents for 480V upgrade on Unit 7.
OF4 | 40 | U1 | 2014-12-06 09:33 |  |  |  |  | 2014-12-06 10:15 |  | 0 | 0 | 0.7 | 0.7 | 2.8 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9720 |  |  | - |  | Other safety problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Voith moving Runner assy over Units 4 and 5 to install in Unit 3
OF4 | 41 | U1 | 2014-12-07 08:56 |  |  |  |  | 2014-12-12 11:03 |  | 0 | 0 | 122.117 | 122.1167 | 488.467 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830HIGH WATER
OF4 | 42 | U1 | 2014-12-15 10:38 |  |  |  |  | 2014-12-15 16:46 |  | 0 | 0 | 6.133 | 6.1333 | 24.533 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9720 |  |  | - |  | Other safety problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Divers removing plugs in Unit #3 , intakes for cooling water.
OF4 | 1 | U1 | 2015-01-26 10:13 |  |  |  |  | 2015-01-26 12:55 |  | 0 | 0 | 2.7 | 2.7 | 10.8 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9720 |  |  | - |  | Other safety problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Divers in lower pool for unit#3 head gates
OF4 | 2 | U1 | 2015-01-27 13:21 |  |  |  |  | 2015-01-27 15:42 |  | 0 | 0 | 2.35 | 2.35 | 9.4 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9720 |  |  | - |  | Other safety problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Divers installing lower head gates from unit #3 to unit #2
OF4 | 3 | U1 | 2015-02-06 13:24 |  |  |  |  | 2015-02-07 13:04 |  | 0 | 0 | 23.667 | 23.6667 | 94.667 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Drift flush
OF4 | 4 | U1 | 2015-02-11 12:53 |  |  |  |  | 2015-02-11 14:46 |  | 0 | 0 | 1.883 | 1.8833 | 7.533 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9720 |  |  | - |  | Other safety problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Divers in upper pool to inspect # 3 trash rack slots. Need unit off for safety.
OF4 | 5 | U1 | 2015-02-12 08:56 |  |  |  |  | 2015-02-12 14:42 |  | 0 | 0 | 5.767 | 5.7667 | 23.067 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9720 |  |  | - |  | Other safety problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Divers inspecting Unit 3 trash racks.
OF4 | 6 | U1 | 2015-02-12 14:51 |  |  |  |  | 2015-02-12 15:07 |  | 0 | 0 | 0.267 | 0.2667 | 1.067 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 4740 |  |  | - |  | Emergency generator trip devices | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F83086 trip, relay problem
OF4 | 7 | U1 | 2015-03-04 11:38 |  |  |  |  | 2015-03-30 11:46 |  | 0 | 0 | 624.133 | 624.1333 | 2496.534 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF4 | 8 | U1 | 2015-04-03 07:35 |  |  |  |  | 2015-04-30 13:56 |  | 0 | 0 | 654.35 | 654.35 | 3926.1 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF4 | 10 | U1 | 2015-06-12 05:49 |  |  |  |  | 2015-06-13 09:23 |  | 0 | 0 | 27.567 | 27.5667 | 165.4 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low river
OF4 | 12 | U1 | 2015-06-19 05:08 |  |  |  |  | 2015-06-19 09:57 |  | 0 | 0 | 4.817 | 4.8167 | 28.9 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7040 |  |  | - |  | Turbine overhaul | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Took this unit off for contractors taking intricate readings on unit 2 Gen re-hab.
OF4 | 13 | U1 | 2015-06-21 06:27 |  |  |  |  | 2015-07-07 13:21 |  | 0 | 0 | 390.9 | 390.9 | 2345.4 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830High water
OF4 | 14 | U1 | 2015-07-11 10:53 |  |  |  |  | 2015-07-23 09:50 |  | 0 | 0 | 286.95 | 286.95 | 1721.7 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF4 | 15 | U1 | 2015-07-23 11:02 |  |  |  |  | 2015-07-23 12:09 |  | 0 | 0 | 1.117 | 1.1167 | 6.7 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 3653 |  |  | - |  | DC protection devices | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820overspeed protection device
OF4 | 16 | U1 | 2015-07-25 09:22 |  |  |  |  | 2015-07-26 09:19 |  | 0 | 0 | 23.95 | 23.95 | 143.7 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Trash
OF4 | 17 | U1 | 2015-07-28 03:07 |  |  |  |  | 2015-07-28 09:15 |  | 0 | 0 | 6.133 | 6.1333 | 36.8 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 3812 |  |  | - |  | Service water valves | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Had to replace service water valve.
OF4 | 18 | U1 | 2015-08-03 06:11 |  |  |  |  | 2015-08-03 09:30 |  | 0 | 0 | 3.317 | 3.3167 | 19.9 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 3829 |  |  | - |  | Other closed cooling water system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820 A phase on windings got hot and tripped @ 0611, not enough cooling water. On @ 0
OF4 | 19 | U1 | 2015-08-03 09:46 |  |  |  |  | 2015-08-03 10:22 |  | 0 | 0 | 0.6 | 0.6 | 3.6 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 4650 |  |  | - |  | Other cooling system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820L. V. bearing water got clogged with debris .
OF4 | 20 | U1 | 2015-08-05 23:35 |  |  |  |  | 2015-08-06 07:13 |  | 0 | 0 | 7.633 | 7.6333 | 45.8 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 3653 |  |  | - |  | DC protection devices | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F82086 lockout relay
OF4 | 21 | U1 | 2015-08-06 07:13 |  |  |  |  | 2015-08-06 13:01 |  | 0 | 0 | 5.8 | 5.8 | 34.8 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | 84
|  | DESCRIPTION : |  | F830Repairs to Unit 4 were completed on 08-06-15 @ 07:13 and Unit was released to Load
OF4 | 22 | U1 | 2015-08-06 14:06 |  |  |  |  | 2015-08-07 09:54 |  | 0 | 0 | 19.8 | 19.8 | 118.8 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 3653 |  |  | - |  | DC protection devices | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F82086 lockout relay
OF4 | 23 | U1 | 2015-08-07 17:18 |  |  |  |  | 2015-08-10 09:03 |  | 0 | 0 | 63.75 | 63.75 | 382.5 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 3653 |  |  | - |  | DC protection devices | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F82086 lockout relay
OF4 | 24 | U1 | 2015-08-10 18:59 |  |  |  |  | 2015-08-12 08:00 |  | 0 | 0 | 37.017 | 37.0167 | 222.1 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low flow
OF4 | 25 | U1 | 2015-08-15 12:30 |  |  |  |  | 2015-10-01 14:13 |  | 0 | 0 | 1129.717 | 1129.7167 | 6778.3 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low flow
OF4 | 26 | U1 | 2015-10-07 19:58 |  |  |  |  | 2015-10-19 07:30 |  | 0 | 0 | 275.533 | 275.5333 | 1653.2 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Took unit off at the request of ACOE. Low flow.
OF4 | 7 | U1 | 2016-12-20 01:32 |  |  |  |  | 2016-12-26 11:05 |  | 0 | 0 | 153.55 | 153.55 | 614.2 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820HIGH WATER
OF4 | 8 | U1 | 2016-12-31 09:17 |  |  |  |  | 2017-01-01 |  | 0 | 0 | 14.717 | 14.7167 | 58.867 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF4 | 1 | U1 | 2017-01-01 |  |  |  |  | 2017-01-02 11:12 |  | 0 | 0 | 35.2 | 35.2 | 140.8 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF4 | 2 | U1 | 2017-01-07 00:34 |  |  |  |  | 2017-01-10 12:44 |  | 0 | 0 | 84.167 | 84.1667 | 336.666 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF4 | 3 | U1 | 2017-01-15 10:03 |  |  |  |  | 2017-01-31 12:52 |  | 0 | 0 | 386.817 | 386.8167 | 1547.267 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830HIGH WATER
OF4 | 4 | U1 | 2017-02-15 00:26 |  |  |  |  | 2017-02-15 08:13 |  | 0 | 0 | 7.783 | 7.7833 | 31.133 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 7141 |  |  | - |  | Wicket gate operating mechanism or positioner | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Speed probe PT
OF4 | 6 | U1 | 2017-03-01 18:42 |  |  |  |  | 2017-03-14 10:05 |  | 0 | 0 | 303.383 | 303.3833 | 1516.917 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Highwater
OF4 | 11 | U1 | 2017-03-31 09:47 |  |  |  |  | 2017-03-31 12:13 |  | 0 | 0 | 2.433 | 2.4333 | 12.167 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Trash
OF4 | 12 | U1 | 2017-04-01 00:37 |  |  |  |  | 2017-04-13 18:00 |  | 0 | 0 | 305.383 | 305.3833 | 1526.917 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820highwater
OF4 | 13 | U1 | 2017-04-29 05:27 |  |  |  |  | 2017-05-18 10:09 |  | 0 | 0 | 460.7 | 460.7 | 3139.8 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820HIGH WATER
OF4 | 14 | U1 | 2017-05-25 22:20 |  |  |  |  | 2017-05-31 07:02 |  | 0 | 0 | 128.7 | 128.7 | 900.9 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF4 | 15 | U1 | 2017-06-01 14:01 |  |  |  |  | 2017-06-01 14:31 |  | 0 | 0 | 0.5 | 0.5 | 4 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7052 |  |  | - |  | "Other turbine control problems (Report specific wicket gate controls, etc., using the code for the appropriate equipment item.)" | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820wicket gate valve driver card failure.
OF4 | 16 | U1 | 2017-06-10 18:51 |  |  |  |  | 2017-06-11 06:48 |  | 0 | 0 | 11.95 | 11.95 | 95.6 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830LOW RIVER CONDITIONS
OF4 | 17 | U1 | 2017-06-24 21:45 |  |  |  |  | 2017-06-29 09:13 |  | 0 | 0 | 107.467 | 107.4667 | 859.733 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Highwater
OF4 | 21 | U1 | 2017-08-05 22:01 |  |  |  |  | 2017-08-07 06:56 |  | 0 | 0 | 32.917 | 32.9167 | 197.5 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF4 | 22 | U1 | 2017-08-08 00:43 |  |  |  |  | 2017-08-08 07:40 |  | 0 | 0 | 6.95 | 6.95 | 41.7 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 3653 |  |  | - |  | DC protection devices | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Speed Box Overspeed Trip
OF4 | 23 | U1 | 2017-08-08 10:33 |  |  |  |  | 2017-08-08 12:03 |  | 0 | 0 | 1.5 | 1.5 | 9 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 3653 |  |  | - |  | DC protection devices | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Speed Box Overspeed Trop
OF4 | 24 | U1 | 2017-08-08 13:35 |  |  |  |  | 2017-08-08 17:44 |  | 0 | 0 | 4.15 | 4.15 | 24.9 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 3653 |  |  | - |  | DC protection devices | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820OVERSPEED BOX TRIP
OF4 | 25 | U1 | 2017-08-08 18:00 |  |  |  |  | 2017-08-10 06:37 |  | 0 | 0 | 36.617 | 36.6167 | 219.7 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF4 | 26 | U1 | 2017-08-13 01:16 |  |  |  |  | 2017-08-14 06:52 |  | 0 | 0 | 29.6 | 29.6 | 177.6 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF4 | 27 | U1 | 2017-08-15 15:12 |  |  |  |  | 2017-08-16 06:32 |  | 0 | 0 | 15.333 | 15.3333 | 92 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low River
OF4 | 28 | U1 | 2017-08-21 13:57 |  |  |  |  | 2017-08-22 06:46 |  | 0 | 0 | 16.817 | 16.8167 | 100.9 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF4 | 29 | U1 | 2017-08-26 11:09 |  |  |  |  | 2017-08-30 06:30 |  | 0 | 0 | 91.35 | 91.35 | 548.1 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low flow
OF4 | 30 | U1 | 2017-08-31 09:19 |  |  |  |  | 2017-09-01 13:12 |  | 0 | 0 | 27.883 | 27.8833 | 180.5 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830LOW FLOW
OF4 | 31 | U1 | 2017-09-03 09:30 |  |  |  |  | 2017-09-04 10:13 |  | 0 | 0 | 24.717 | 24.7167 | 173.017 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF4 | 32 | U1 | 2017-09-11 01:07 |  |  |  |  | 2017-09-18 07:54 |  | 0 | 0 | 174.783 | 174.7833 | 1223.483 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF4 | 34 | U1 | 2017-09-20 10:49 |  |  |  |  | 2017-09-22 07:25 |  | 0 | 0 | 44.6 | 44.6 | 312.2 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF4 | 35 | U1 | 2017-09-23 07:58 |  |  |  |  | 2017-09-25 07:53 |  | 0 | 0 | 47.917 | 47.9167 | 335.416 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF4 | 36 | U1 | 2017-09-25 23:58 |  |  |  |  | 2017-09-30 10:21 |  | 0 | 0 | 106.383 | 106.3833 | 744.683 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF4 | 37 | U1 | 2017-10-01 10:57 |  |  |  |  | 2017-10-09 07:15 |  | 0 | 0 | 188.3 | 188.3 | 1318.1 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF4 | 38 | U1 | 2017-10-17 08:52 |  |  |  |  | 2017-10-19 06:44 |  | 0 | 0 | 45.867 | 45.8667 | 321.066 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low River
OF4 | 39 | U1 | 2017-10-20 10:08 |  |  |  |  | 2017-10-25 12:50 |  | 0 | 0 | 122.7 | 122.7 | 858.9 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF4 | 40 | U1 | 2017-11-06 12:01 |  |  |  |  | 2017-11-13 13:48 |  | 0 | 0 | 169.783 | 169.7833 | 848.917 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820High River
OF4 | 41 | U1 | 2017-11-21 19:13 |  |  |  |  | 2017-11-24 08:10 |  | 0 | 0 | 60.95 | 60.95 | 304.75 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for highwater and trash
OF4 | 42 | U1 | 2017-12-20 11:29 |  |  |  |  | 2017-12-23 13:51 |  | 0 | 0 | 74.367 | 74.3667 | 520.567 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF4 | 43 | U1 | 2017-12-26 07:28 |  |  |  |  | 2017-12-28 10:00 |  | 0 | 0 | 50.533 | 50.5333 | 353.733 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820highwater
OF4 | 44 | U1 | 2017-12-29 10:02 |  |  |  |  | 2017-12-29 10:18 |  | 0 | 0 | 0.267 | 0.2667 | 1.867 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 3672 |  |  | - |  | 12-15kV conductors and buses | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Changed from bus B to bus A
OF4 | 1 | U1 | 2018-01-10 10:58 |  |  |  |  | 2018-01-11 13:47 |  | 0 | 0 | 26.817 | 26.8167 | 134.084 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF4 | 2 | U1 | 2018-01-14 04:15 |  |  |  |  | 2018-01-20 12:55 |  | 0 | 0 | 152.667 | 152.6667 | 763.333 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF4 | 3 | U1 | 2018-01-24 08:22 |  |  |  |  | 2018-02-01 13:07 |  | 0 | 0 | 196.75 | 196.75 | 970.634 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830highwater
OF4 | 4 | U1 | 2018-02-08 15:46 |  |  |  |  | 2018-03-12 09:04 |  | 0 | 0 | 761.3 | 761.3 | 3318.266 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830High river
OF4 | 5 | U1 | 2018-03-23 10:37 |  |  |  |  | 2018-04-15 10:56 |  | 0 | 0 | 552.317 | 552.3167 | 2761.584 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830highwater
OF4 | 6 | U1 | 2018-04-16 21:55 |  |  |  |  | 2018-04-30 14:01 |  | 0 | 0 | 328.1 | 328.1 | 1640.5 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820highwater
OF4 | 7 | U1 | 2018-05-08 05:28 |  |  |  |  | 2018-05-12 09:31 |  | 0 | 0 | 100.05 | 100.05 | 700.35 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF4 | 8 | U1 | 2018-05-21 07:00 |  |  |  |  | 2018-05-21 13:59 |  | 0 | 0 | 6.983 | 6.9833 | 48.883 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater / Trash
OF4 | 9 | U1 | 2018-05-21 22:08 |  |  |  |  | 2018-05-28 07:26 |  | 0 | 0 | 153.3 | 153.3 | 1073.1 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Trash and Highwater
OF4 | 13 | U1 | 2018-06-24 11:01 |  |  |  |  | 2018-06-27 11:57 |  | 0 | 0 | 72.933 | 72.9333 | 583.467 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Highwater
OF4 | 14 | U1 | 2018-06-29 18:09 |  |  |  |  | 2018-07-02 09:00 |  | 0 | 0 | 62.85 | 62.85 | 436.8 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Highwater
OF4 | 16 | U1 | 2018-07-11 13:28 |  |  |  |  | 2018-07-13 06:56 |  | 0 | 0 | 41.467 | 41.4667 | 248.8 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF4 | 17 | U1 | 2018-07-14 05:22 |  |  |  |  | 2018-07-19 07:26 |  | 0 | 0 | 122.067 | 122.0667 | 732.4 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low flow
OF4 | 20 | U1 | 2018-08-20 08:39 |  |  |  |  | 2018-08-20 14:13 |  | 0 | 0 | 5.567 | 5.5667 | 33.4 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830trash
OF4 | 21 | U1 | 2018-08-29 11:54 |  |  |  |  | 2018-09-01 08:18 |  | 0 | 0 | 68.4 | 68.4 | 418.7 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low water flow
OF4 | 22 | U1 | 2018-09-06 10:19 |  |  |  |  | 2018-09-08 13:52 |  | 0 | 0 | 51.55 | 51.55 | 360.85 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF4 | 23 | U1 | 2018-09-09 02:48 |  |  |  |  | 2018-09-17 10:31 |  | 0 | 0 | 199.717 | 199.7167 | 1398.017 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Highwater
OF4 | 24 | U1 | 2018-09-19 16:35 |  |  |  |  | 2018-09-24 10:10 |  | 0 | 0 | 113.583 | 113.5833 | 795.084 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF4 | 25 | U1 | 2018-09-24 22:16 |  |  |  |  | 2018-10-04 09:29 |  | 0 | 0 | 227.217 | 227.2167 | 1590.516 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F830high water
OF4 | 26 | U1 | 2018-10-10 08:05 |  |  |  |  | 2018-10-10 18:11 |  | 0 | 0 | 10.1 | 10.1 | 70.7 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Trash in front of facility Intakes
OF4 | 27 | U1 | 2018-10-13 08:36 |  |  |  |  | 2018-10-13 11:39 |  | 0 | 0 | 3.05 | 3.05 | 21.35 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offine for Trash
OF4 | 28 | U1 | 2018-10-13 14:53 |  |  |  |  | 2018-10-13 16:38 |  | 0 | 0 | 1.75 | 1.75 | 12.25 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for trash
OF4 | 29 | U1 | 2018-10-19 11:03 |  |  |  |  | 2018-10-19 13:37 |  | 0 | 0 | 2.567 | 2.5667 | 17.967 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Trash Buildup
OF4 | 34 | U1 | 2018-11-02 00:30 |  |  |  |  | 2018-12-09 07:56 |  | 0 | 0 | 895.433 | 895.4333 | 4477.167 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater, taken off by C/R motoring.
OF4 | 35 | U1 | 2018-12-09 08:11 |  |  |  |  | 2018-12-09 12:58 |  | 0 | 0 | 4.783 | 4.7833 | 23.917 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 7009 |  |  | - |  | Bearing oil system | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Oil temp, shut down due to poor flow of oil because of cold temps.
OF4 | 36 | U1 | 2018-12-17 13:35 |  |  |  |  | 2019-01-01 |  | 0 | 0 | 346.417 | 346.4167 | 1732.083 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830high water
OF4 | 1 | U1 | 2019-01-01 |  |  |  |  | 2019-01-15 08:56 |  | 0 | 0 | 344.933 | 344.9333 | 1724.667 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830High water.
OF4 | 2 | U1 | 2019-01-20 16:36 |  |  |  |  | 2019-01-31 23:59 |  | 0 | 0 | 271.383 | 271.3833 | 1356.917 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830highwater
OF4 | 3 | U1 | 2019-02-01 |  |  |  |  | 2019-02-03 13:03 |  | 0 | 0 | 61.05 | 61.05 | 305.25 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF4 | 4 | U1 | 2019-02-07 07:49 |  |  |  |  | 2019-03-07 13:46 |  | 0 | 0 | 677.95 | 677.95 | 3705.284 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830highwater
OF4 | 5 | U1 | 2019-03-10 12:38 |  |  |  |  | 2019-03-19 12:13 |  | 0 | 0 | 215.583 | 215.5833 | 1509.084 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF4 | 6 | U1 | 2019-03-27 09:45 |  |  |  |  | 2019-03-27 10:57 |  | 0 | 0 | 1.2 | 1.2 | 8.4 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Trash
OF4 | 9 | U1 | 2019-04-19 11:35 |  |  |  |  | 2019-05-10 07:22 |  | 0 | 0 | 499.783 | 499.7833 | 3498.484 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF4 | 10 | U1 | 2019-05-15 06:27 |  |  |  |  | 2019-05-20 09:38 |  | 0 | 0 | 123.183 | 123.1833 | 862.283 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Trash
OF4 | 11 | U1 | 2019-06-03 05:58 |  |  |  |  | 2019-06-04 12:07 |  | 0 | 0 | 30.15 | 30.15 | 241.2 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820high water
OF4 | 13 | U1 | 2019-06-17 06:25 |  |  |  |  | 2019-06-28 11:58 |  | 0 | 0 | 269.55 | 269.55 | 2156.4 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830highwater
OF4 | 14 | U1 | 2019-07-23 06:48 |  |  |  |  | 2019-07-23 14:36 |  | 0 | 0 | 7.8 | 7.8 | 46.8 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830trash
OF4 | 15 | U1 | 2019-07-31 10:01 |  |  |  |  | 2019-08-01 09:21 |  | 0 | 0 | 23.333 | 23.3333 | 158.7 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low water
OF4 | 16 | U1 | 2019-08-02 20:32 |  |  |  |  | 2019-08-08 06:53 |  | 0 | 0 | 130.35 | 130.35 | 1042.8 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF4 | 17 | U1 | 2019-08-11 21:47 |  |  |  |  | 2019-08-14 09:07 |  | 0 | 0 | 59.333 | 59.3333 | 474.666 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF4 | 18 | U1 | 2019-08-15 17:10 |  |  |  |  | 2019-08-23 09:19 |  | 0 | 0 | 184.15 | 184.15 | 1473.2 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low river
OF4 | 19 | U1 | 2019-08-23 20:09 |  |  |  |  | 2019-08-25 09:36 |  | 0 | 0 | 37.45 | 37.45 | 299.6 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF4 | 20 | U1 | 2019-08-28 06:54 |  |  |  |  | 2019-08-31 07:20 |  | 0 | 0 | 72.433 | 72.4333 | 579.467 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for low flow, alternated with unit 6 due to dredging
OF4 | 21 | U1 | 2019-08-31 20:44 |  |  |  |  | 2019-09-03 10:45 |  | 0 | 0 | 62.017 | 62.0167 | 437.383 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow, ACOE Request shut down
OF4 | 22 | U1 | 2019-09-05 11:03 |  |  |  |  | 2019-09-20 07:11 |  | 0 | 0 | 356.133 | 356.1333 | 2492.933 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF4 | 23 | U1 | 2019-09-20 09:58 |  |  |  |  | 2019-10-08 06:43 |  | 0 | 0 | 428.75 | 428.75 | 3001.25 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline per ACOE Request Low FLow
OF4 | 24 | U1 | 2019-10-09 21:52 |  |  |  |  | 2019-10-11 06:55 |  | 0 | 0 | 33.05 | 33.05 | 231.35 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow Offline per ACOE Request
OF4 | 25 | U1 | 2019-10-12 01:53 |  |  |  |  | 2019-10-24 10:40 |  | 0 | 0 | 296.783 | 296.7833 | 2077.484 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Water, Offline per request of ACOE
OF4 | 26 | U1 | 2019-10-28 10:28 |  |  |  |  | 2019-10-28 11:01 |  | 0 | 0 | 0.55 | 0.55 | 3.85 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 3999 |  |  | - |  | Other miscellaneous balance of plant problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Transferred Unit 4 from Bus B back to Bus A for balanceing
OF4 | 28 | U1 | 2019-11-12 10:59 |  |  |  |  | 2019-11-13 14:15 |  | 0 | 0 | 27.267 | 27.2667 | 190.867 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF4 | 29 | U1 | 2019-12-03 05:05 |  |  |  |  | 2019-12-05 14:24 |  | 0 | 0 | 57.317 | 57.3167 | 286.583 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820highwater
OF4 | 30 | U1 | 2019-12-14 12:25 |  |  |  |  | 2019-12-24 12:55 |  | 0 | 0 | 240.5 | 240.5 | 1202.5 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830highwater
OF4 | 31 | U1 | 2019-12-26 12:05 |  |  |  |  | 2019-12-26 16:08 |  | 0 | 0 | 4.05 | 4.05 | 20.25 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 7141 |  |  | - |  | Wicket gate operating mechanism or positioner | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820GPU PISTON A FAILURE
OF4 | 32 | U1 | 2019-12-31 11:28 |  |  |  |  | 2019-12-31 23:59 |  | 0 | 0 | 12.517 | 12.5167 | 62.583 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Highwater
OF4 | 1 | U1 | 2020-01-01 |  |  |  |  | 2020-01-10 14:34 |  | 0 | 0 | 230.567 | 230.5667 | 1152.833 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Highwater
OF4 | 2 | U1 | 2020-01-14 10:06 |  |  |  |  | 2020-01-18 13:36 |  | 0 | 0 | 99.5 | 99.5 | 497.5 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830High River
OF4 | 3 | U1 | 2020-01-27 18:49 |  |  |  |  | 2020-02-01 13:34 |  | 0 | 0 | 114.75 | 114.75 | 573.75 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF4 | 4 | U1 | 2020-02-08 12:30 |  |  |  |  | 2020-02-24 10:21 |  | 0 | 0 | 381.85 | 381.85 | 1909.25 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Highwater
OF4 | 5 | U1 | 2020-03-05 15:07 |  |  |  |  | 2020-03-10 11:58 |  | 0 | 0 | 116.85 | 116.85 | 817.95 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Trash
OF4 | 6 | U1 | 2020-03-15 10:11 |  |  |  |  | 2020-04-06 11:57 |  | 0 | 0 | 529.767 | 529.7667 | 3708.367 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF4 | 7 | U1 | 2020-04-13 22:13 |  |  |  |  | 2020-04-22 09:51 |  | 0 | 0 | 203.633 | 203.6333 | 1425.433 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for highwater
OF4 | 8 | U1 | 2020-04-28 14:10 |  |  |  |  | 2020-05-12 12:24 |  | 0 | 0 | 334.233 | 334.2333 | 2339.633 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Highwater
OF4 | 9 | U1 | 2020-05-20 08:39 |  |  |  |  | 2020-05-30 07:25 |  | 0 | 0 | 238.767 | 238.7667 | 1671.367 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF4 | 10 | U1 | 2020-06-10 09:49 |  |  |  |  | 2020-06-10 17:19 |  | 0 | 0 | 7.5 | 7.5 | 60 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for trash
OF4 | 11 | U1 | 2020-06-10 17:19 |  |  |  |  | 2020-06-17 12:46 |  | 0 | 0 | 163.45 | 163.45 | 1307.6 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 3710 |  |  | - |  | Transmission line (connected to powerhouse switchyard to 1st Substation) | [8 empty] | AMP CODE: |  | X0
|  | DESCRIPTION : |  | F830Transmission Outage
OF4 | 14 | U1 | 2020-06-28 07:12 |  |  |  |  | 2020-06-29 09:59 |  | 0 | 0 | 26.783 | 26.7833 | 214.267 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9001 |  |  | - |  | Drought | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow, ACOE requested shutdown
OF4 | 16 | U1 | 2020-08-28 06:00 |  |  |  |  | 2020-09-03 11:16 |  | 0 | 0 | 149.267 | 149.2667 | 1134.867 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | X0
|  | DESCRIPTION : |  | F830low flow
OF4 | 17 | U1 | 2020-09-11 07:00 |  |  |  |  | 2020-09-15 13:55 |  | 0 | 0 | 102.917 | 102.9167 | 720.417 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Lack of water.
OF4 | 18 | U1 | 2020-09-17 14:58 |  |  |  |  | 2020-09-19 09:33 |  | 0 | 0 | 42.583 | 42.5833 | 298.083 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Lack of water.
OF4 | 19 | U1 | 2020-09-21 19:41 |  |  |  |  | 2020-10-03 08:38 |  | 0 | 0 | 276.95 | 276.95 | 1938.65 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Lack of water.
OF4 | 20 | U1 | 2020-10-04 12:13 |  |  |  |  | 2020-10-29 10:02 |  | 0 | 0 | 597.817 | 597.8167 | 4184.716 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Lack of water.
OF4 | 23 | U1 | 2020-11-09 13:10 |  |  |  |  | 2020-11-13 08:10 |  | 0 | 0 | 91 | 91 | 637 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow (ACOE)
OF4 | 25 | U1 | 2020-12-16 11:03 |  |  |  |  | 2020-12-16 16:46 |  | 0 | 0 | 5.717 | 5.7167 | 28.583 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9350 |  |  | - |  | Public Safety (water hazard or river rescue) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Diesel fuel in upper pool
OF4 | 26 | U1 | 2020-12-27 21:04 |  |  |  |  | 2021-01-01 |  | 0 | 0 | 98.933 | 98.9333 | 494.667 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Highwater
OF4 | 1 | U1 | 2021-01-01 |  |  |  |  | 2021-01-11 11:44 |  | 0 | 0 | 251.733 | 251.7333 | 3171.84 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for highwater
OF4 | 2 | U1 | 2021-01-27 20:12 |  |  |  |  | 2021-02-05 10:54 |  | 0 | 0 | 206.7 | 206.7 | 2604.42 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Offline for highwater
OF4 | 3 | U1 | 2021-02-08 04:08 |  |  |  |  | 2021-02-11 14:56 |  | 0 | 0 | 82.8 | 82.8 | 1043.28 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 4550 |  |  | - |  | Generator bearings and lube oil system (including thrust bearings on hydro units) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820The unit gear pump failed. We replaced the gear ring on shaft and the gear pump.
OF4 | 4 | U1 | 2021-02-24 21:07 |  |  |  |  | 2021-03-12 11:58 |  | 0 | 0 | 374.85 | 374.85 | 4723.11 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF4 | 5 | U1 | 2021-03-20 07:01 |  |  |  |  | 2021-03-24 07:55 |  | 0 | 0 | 96.9 | 96.9 | 1220.94 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830high water
OF4 | 6 | U1 | 2021-03-31 02:19 |  |  |  |  | 2021-04-05 09:09 |  | 0 | 0 | 126.833 | 126.8333 | 1598.1 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Highwater
OF4 | 10 | U1 | 2021-05-22 17:55 |  |  |  |  | 2021-05-25 06:40 |  | 0 | 0 | 60.75 | 60.75 | 765.45 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830lack of water ACOE
OF4 | 12 | U1 | 2021-06-15 07:53 |  |  |  |  | 2021-06-15 13:18 |  | 0 | 0 | 5.417 | 5.4167 | 68.25 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for trash.
OF4 | 13 | U1 | 2021-06-20 02:49 |  |  |  |  | 2021-06-21 08:48 |  | 0 | 0 | 29.983 | 29.9833 | 377.79 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for trash.
OF4 | 15 | U1 | 2021-06-27 16:23 |  |  |  |  | 2021-06-28 07:33 |  | 0 | 0 | 15.167 | 15.1667 | 191.1 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830ACOE requested, Lack of Water
OF4 | 16 | U1 | 2021-06-29 11:51 |  |  |  |  | 2021-07-01 07:35 |  | 0 | 0 | 43.733 | 43.7333 | 551.04 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Lack of Water, Run of River per ACOE
OF4 | 19 | U1 | 2021-07-09 06:30 |  |  |  |  | 2021-07-13 09:48 |  | 0 | 0 | 99.3 | 99.3 | 1251.18 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | FR
|  | DESCRIPTION : |  | F830Unit offline for run of river lack of water.
OF4 | 20 | U1 | 2021-08-04 10:52 |  |  |  |  | 2021-08-11 07:18 |  | 0 | 0 | 164.433 | 164.4333 | 2071.86 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Lack of Water
OF4 | 21 | U1 | 2021-08-12 00:55 |  |  |  |  | 2021-08-13 13:02 |  | 0 | 0 | 36.117 | 36.1167 | 455.07 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Lack of Water (ACOE)
OF4 | 22 | U1 | 2021-08-16 06:58 |  |  |  |  | 2021-08-17 09:39 |  | 0 | 0 | 26.683 | 26.6833 | 336.21 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Lack of Water (ACOE)
OF4 | 25 | U1 | 2021-09-03 10:39 |  |  |  |  | 2021-09-06 08:08 |  | 0 | 0 | 69.483 | 69.4833 | 875.49 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for High Water
OF4 | 26 | U1 | 2021-09-11 13:14 |  |  |  |  | 2021-09-18 08:19 |  | 0 | 0 | 163.083 | 163.0833 | 2054.85 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Lack of water.
OF4 | 27 | U1 | 2021-09-19 11:29 |  |  |  |  | 2021-09-22 12:01 |  | 0 | 0 | 72.533 | 72.5333 | 913.92 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Lack of Water.
OF4 | 28 | U1 | 2021-09-22 16:09 |  |  |  |  | 2021-09-24 13:32 |  | 0 | 0 | 45.383 | 45.3833 | 571.83 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Lack of Water
OF4 | 29 | U1 | 2021-10-02 14:19 |  |  |  |  | 2021-10-04 07:11 |  | 0 | 0 | 40.867 | 40.8667 | 514.92 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Lack of Water (ACOE)
OF4 | 30 | U1 | 2021-10-05 06:03 |  |  |  |  | 2021-10-07 11:43 |  | 0 | 0 | 53.667 | 53.6667 | 676.2 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Lack of Water (ACOE)
OF4 | 31 | U1 | 2021-10-14 17:48 |  |  |  |  | 2021-10-18 08:00 |  | 0 | 0 | 86.2 | 86.2 | 1086.12 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Lack of Water(ACOE)
OF4 | 34 | U1 | 2021-12-31 08:38 |  |  |  |  | 2022-01-01 |  | 0 | 0 | 15.367 | 15.3667 | 193.62 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820High Water.
OF4 | 1 | U1 | 2022-01-01 |  |  |  |  | 2022-01-16 13:57 |  | 0 | 0 | 373.95 | 373.95 | 4711.77 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Offline for High Water.
OF4 | 2 | U1 | 2022-02-04 05:40 |  |  |  |  | 2022-02-14 10:51 |  | 0 | 0 | 245.183 | 245.1833 | 3089.31 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for High Water
OF4 | 3 | U1 | 2022-02-15 20:39 |  |  |  |  | 2022-03-21 07:34 |  | 0 | 0 | 802.917 | 802.9167 | 10116.75 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Trash / Highwater (Run of River)
OF4 | 6 | U1 | 2022-04-10 07:01 |  |  |  |  | 2022-04-18 07:29 |  | 0 | 0 | 192.467 | 192.4667 | 2425.08 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for High Water
OF4 | 7 | U1 | 2022-05-07 16:32 |  |  |  |  | 2022-05-16 09:30 |  | 0 | 0 | 208.967 | 208.9667 | 2632.98 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Offline for High Water.
OF4 | 8 | U1 | 2022-05-30 08:55 |  |  |  |  | 2022-06-01 07:37 |  | 0 | 0 | 46.7 | 46.7 | 588.42 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for high water.
OF4 | 9 | U1 | 2022-06-25 06:44 |  |  |  |  | 2022-06-27 07:04 |  | 0 | 0 | 48.333 | 48.3333 | 609 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Lack of Water-Run of River per the ACOE
OF4 | 10 | U1 | 2022-06-30 20:08 |  |  |  |  | 2022-07-05 12:35 |  | 0 | 0 | 112.45 | 112.45 | 1416.87 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for lack of water.
OF4 | 11 | U1 | 2022-07-06 13:52 |  |  |  |  | 2022-07-07 06:49 |  | 0 | 0 | 16.95 | 16.95 | 213.57 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for lack of water.
OF4 | 12 | U1 | 2022-07-16 15:43 |  |  |  |  | 2022-07-18 10:43 |  | 0 | 0 | 43 | 43 | 541.8 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Run of River (Lack of Water) per the ACOE
OF4 | 14 | U1 | 2022-08-02 06:05 |  |  |  |  | 2022-08-02 13:32 |  | 0 | 0 | 7.45 | 7.45 | 93.87 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Trash
OF4 | 15 | U1 | 2022-08-17 06:59 |  |  |  |  | 2022-08-22 09:13 |  | 0 | 0 | 122.233 | 122.2333 | 1540.14 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Trash - Run of River
OF4 | 16 | U1 | 2022-08-23 10:57 |  |  |  |  | 2022-08-23 13:48 |  | 0 | 0 | 2.85 | 2.85 | 35.91 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Trash (Run of River)
OF4 | 17 | U1 | 2022-08-26 06:02 |  |  |  |  | 2022-08-29 12:39 |  | 0 | 0 | 78.617 | 78.6167 | 990.57 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Lack of Water per The ACOE
OF4 | 18 | U1 | 2022-08-29 16:40 |  |  |  |  | 2022-08-30 12:46 |  | 0 | 0 | 20.1 | 20.1 | 253.26 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 3672 |  |  | - |  | 12-15kV conductors and buses | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F49014KV Bus A lockout
OF4 | 19 | U1 | 2022-09-06 07:17 |  |  |  |  | 2022-09-06 09:11 |  | 0 | 0 | 1.9 | 1.9 | 23.94 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830trash
OF4 | 20 | U1 | 2022-09-06 12:57 |  |  |  |  | 2022-09-07 07:01 |  | 0 | 0 | 18.067 | 18.0667 | 227.64 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F820trash
OF4 | 21 | U1 | 2022-09-13 04:19 |  |  |  |  | 2022-09-13 14:22 |  | 0 | 0 | 10.05 | 10.05 | 126.63 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Unit offline for Trash
OF4 | 22 | U1 | 2022-09-16 13:51 |  |  |  |  | 2022-09-23 10:14 |  | 0 | 0 | 164.383 | 164.3833 | 2071.23 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Lack of Water
OF4 | 23 | U1 | 2022-09-25 13:47 |  |  |  |  | 2022-09-30 14:02 |  | 0 | 0 | 120.25 | 120.25 | 1515.15 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for low water.
OF4 | 24 | U1 | 2022-10-11 12:56 |  |  |  |  | 2022-10-14 09:03 |  | 0 | 0 | 68.117 | 68.1167 | 858.27 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Lack of Water
OF4 | 25 | U1 | 2022-10-14 13:09 |  |  |  |  | 2022-11-09 07:43 |  | 0 | 0 | 618.567 | 618.5667 | 7793.94 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Lack of Water
OF4 | 26 | U1 | 2022-11-10 00:50 |  |  |  |  | 2022-11-12 14:08 |  | 0 | 0 | 61.3 | 61.3 | 772.38 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Lack of Water
OF4 | 27 | U1 | 2022-12-02 11:50 |  |  |  |  | 2022-12-12 14:21 |  | 0 | 0 | 242.517 | 242.5167 | 3055.71 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Excessive Trash
OF4 | 28 | U1 | 2022-12-23 15:20 |  |  |  |  | 2022-12-27 10:39 |  | 0 | 0 | 91.317 | 91.3167 | 1150.59 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9036 |  |  | - |  | "Storms (ice, snow, etc)" | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Army Corps gates not operating due to freezing temperatures. Unit shut down to mai
OF4 | 1 | U1 | 2023-01-03 17:26 |  |  |  |  | 2023-01-09 11:15 |  | 0 | 0 | 137.817 | 137.8167 | 1736.49 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Offline for trash.
OF4 | 2 | U1 | 2023-01-13 08:10 |  |  |  |  | 2023-01-27 10:39 |  | 0 | 0 | 338.483 | 338.4833 | 4264.89 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830trash
OF4 | 3 | U1 | 2023-01-29 05:04 |  |  |  |  | 2023-01-29 14:53 |  | 0 | 0 | 9.817 | 9.8167 | 123.69 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for high water.
OF4 | 4 | U1 | 2023-01-30 11:35 |  |  |  |  | 2023-01-31 11:15 |  | 0 | 0 | 23.667 | 23.6667 | 298.2 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830trash
OF4 | 5 | U1 | 2023-02-03 12:10 |  |  |  |  | 2023-02-07 09:40 |  | 0 | 0 | 93.5 | 93.5 | 1178.1 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9320 |  |  | - |  | Other miscellaneous external problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830barge recovery
OF4 | 7 | U1 | 2023-02-17 08:22 |  |  |  |  | 2023-02-24 13:29 |  | 0 | 0 | 173.117 | 173.1167 | 2181.27 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for High Water
OF4 | 8 | U1 | 2023-03-03 07:56 |  |  |  |  | 2023-03-13 09:56 |  | 0 | 0 | 242 | 242 | 3049.2 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for High Water
OF4 | 9 | U1 | 2023-03-17 10:01 |  |  |  |  | 2023-03-17 10:25 |  | 0 | 0 | 0.4 | 0.4 | 5.04 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7201 |  |  | - |  | Inspection | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830inspect slinger spring
OF4 | 10 | U1 | 2023-03-24 19:58 |  |  |  |  | 2023-04-11 06:30 |  | 0 | 0 | 418.533 | 418.5333 | 5273.52 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Offline for High Water.
OF4 | 11 | U1 | 2023-04-11 06:30 |  |  |  |  | 2023-04-28 13:10 |  | 0 | 0 | 414.667 | 414.6667 | 5224.8 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9320 |  |  | - |  | Other miscellaneous external problems | [8 empty] | AMP CODE: |  | FR
|  | DESCRIPTION : |  | FX00Barge Recovery
OF4 | 12 | U1 | 2023-05-24 13:13 |  |  |  |  | 2023-05-31 06:51 |  | 0 | 0 | 161.633 | 161.6333 | 2036.58 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Lack of Water
OF4 | 13 | U1 | 2023-06-06 18:43 |  |  |  |  | 2023-06-16 07:25 |  | 0 | 0 | 228.7 | 228.7 | 2881.62 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830lack of water
OF4 | 14 | U1 | 2023-06-19 16:19 |  |  |  |  | 2023-06-26 07:29 |  | 0 | 0 | 159.167 | 159.1667 | 2005.5 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline lack of water.
OF4 | 15 | U1 | 2023-06-26 07:29 |  |  |  |  | 2023-06-26 16:00 |  | 0 | 0 | 8.517 | 8.5167 | 107.31 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | FR
|  | DESCRIPTION : |  | F530MSI sonar.
OF4 | 16 | U1 | 2023-06-26 16:00 |  |  |  |  | 2023-06-27 07:08 |  | 0 | 0 | 15.133 | 15.1333 | 190.68 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE:
|  | DESCRIPTION : |  | F830lack of water
OF4 | 17 | U1 | 2023-06-28 12:38 |  |  |  |  | 2023-07-02 07:23 |  | 0 | 0 | 90.75 | 90.75 | 1143.45 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830lack of water
OF4 | 18 | U1 | 2023-07-07 07:49 |  |  |  |  | 2023-07-07 13:30 |  | 0 | 0 | 5.683 | 5.6833 | 71.61 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Trash
OF4 | 19 | U1 | 2023-07-11 14:04 |  |  |  |  | 2023-07-17 08:14 |  | 0 | 0 | 138.167 | 138.1667 | 1740.9 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830lack of water
OF4 | 20 | U1 | 2023-07-24 04:34 |  |  |  |  | 2023-07-29 07:44 |  | 0 | 0 | 123.167 | 123.1667 | 1551.9 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Lack of water
OF4 | 22 | U1 | 2023-08-03 03:03 |  |  |  |  | 2023-08-07 09:00 |  | 0 | 0 | 101.95 | 101.95 | 1284.57 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline lack of water.
OF4 | 24 | U1 | 2023-08-21 09:15 |  |  |  |  | 2023-08-25 10:09 |  | 0 | 0 | 96.9 | 96.9 | 1220.94 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline lack of water.
OF4 | 25 | U1 | 2023-09-02 16:36 |  |  |  |  | 2023-09-09 05:30 |  | 0 | 0 | 156.9 | 156.9 | 1976.94 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Lack of water
OF4 | 27 | U1 | 2023-09-23 06:24 |  |  |  |  | 2023-10-08 09:35 |  | 0 | 0 | 363.183 | 363.1833 | 4576.11 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | FR
|  | DESCRIPTION : |  | F830lack of water
OF4 | 28 | U1 | 2023-10-08 15:33 |  |  |  |  | 2023-11-01 10:24 |  | 0 | 0 | 570.85 | 570.85 | 7192.71 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline lack of water.
OF4 | 29 | U1 | 2023-11-06 13:15 |  |  |  |  | 2023-11-21 08:09 |  | 0 | 0 | 354.9 | 354.9 | 4471.74 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830lack of water
OF4 | 30 | U1 | 2023-12-25 12:15 |  |  |  |  | 2023-12-27 14:24 |  | 0 | 0 | 50.15 | 50.15 | 631.89 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830lack of water
Ohio Falls - OF5
Unit | Event | Type | Start |  |  |  |  | End |  | GAC | NAC | Duration | Equiv Hrs | Equiv MWH | Cont | Work Start | Work End |  | Hours |  |  | Gross Capacity Impact (MW)
OF5 | 1 | U1 | 2014-01-01 |  |  |  |  | 2014-10-22 09:12 |  | 0 | 0 | 7065.2 | 7065.2 | 50041.6 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 7011 |  |  | - |  | Other runner problems | [8 empty] | AMP CODE: |  | 30
|  | DESCRIPTION : |  | F300Damaged runner.
OF5 | 2 | U1 | 2014-10-23 02:19 |  |  |  |  | 2014-10-23 09:41 |  | 0 | 0 | 7.367 | 7.3667 | 58.933 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7053 |  |  | - |  | Governor oil system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Governor oil level probe failed, had to repair.
OF5 | 3 | U1 | 2014-11-03 17:52 |  |  |  |  | 2014-11-04 15:18 |  | 0 | 0 | 21.433 | 21.4333 | 171.467 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7053 |  |  | - |  | Governor oil system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820GPU Accum. Piston A Lower Limit Trip
OF5 | 4 | U1 | 2014-11-11 10:23 |  |  |  |  | 2014-11-11 11:26 |  | 0 | 0 | 1.05 | 1.05 | 8.4 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 3684 |  |  | - |  | Other voltage protection devices | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Unit 5 tripped when rewiring for upgrade on unit 6.
OF5 | 5 | U1 | 2014-12-06 09:31 |  |  |  |  | 2014-12-06 10:29 |  | 0 | 0 | 0.967 | 0.9667 | 5.8 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9720 |  |  | - |  | Other safety problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Voith moving Runner assy over Units 4 and 5 to install on Unit 3
OF5 | 6 | U1 | 2014-12-07 08:49 |  |  |  |  | 2014-12-12 12:11 |  | 0 | 0 | 123.367 | 123.3667 | 740.2 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830HIGH WATER
OF5 | 1 | U1 | 2015-02-06 13:27 |  |  |  |  | 2015-02-07 15:04 |  | 0 | 0 | 25.617 | 25.6167 | 128.083 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Trash flush
OF5 | 2 | U1 | 2015-03-04 11:56 |  |  |  |  | 2015-03-27 09:47 |  | 0 | 0 | 549.85 | 549.85 | 2749.25 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF5 | 3 | U1 | 2015-04-03 10:04 |  |  |  |  | 2015-04-27 13:56 |  | 0 | 0 | 579.867 | 579.8667 | 4638.934 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF5 | 4 | U1 | 2015-06-02 05:18 |  |  |  |  | 2015-06-02 07:04 |  | 0 | 0 | 1.767 | 1.7667 | 14.133 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7008 |  |  | - |  | Bearing cooling system | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830LV bearing intake screens clogged
OF5 | 5 | U1 | 2015-06-12 13:32 |  |  |  |  | 2015-06-13 07:33 |  | 0 | 0 | 18.017 | 18.0167 | 144.133 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low river
OF5 | 6 | U1 | 2015-06-19 18:22 |  |  |  |  | 2015-06-20 08:41 |  | 0 | 0 | 14.317 | 14.3167 | 114.534 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Debris blocking trash racks causing high differential.
OF5 | 7 | U1 | 2015-06-21 06:09 |  |  |  |  | 2015-06-26 13:05 |  | 0 | 0 | 126.933 | 126.9333 | 1015.467 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830High water.
OF5 | 8 | U1 | 2015-06-30 12:12 |  |  |  |  | 2015-07-07 09:25 |  | 0 | 0 | 165.217 | 165.2167 | 1321.733 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF5 | 9 | U1 | 2015-07-11 10:35 |  |  |  |  | 2015-07-22 09:45 |  | 0 | 0 | 263.167 | 263.1667 | 2105.333 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF5 | 10 | U1 | 2015-07-25 09:27 |  |  |  |  | 2015-07-26 08:26 |  | 0 | 0 | 22.983 | 22.9833 | 183.867 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Trash
OF5 | 11 | U1 | 2015-07-28 03:16 |  |  |  |  | 2015-07-28 06:40 |  | 0 | 0 | 3.4 | 3.4 | 27.2 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 3812 |  |  | - |  | Service water valves | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Had to replace service water valve.
OF5 | 12 | U1 | 2015-08-05 23:47 |  |  |  |  | 2015-08-06 07:12 |  | 0 | 0 | 7.417 | 7.4167 | 59.333 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 3973 |  |  | - |  | DCS - internal and termination wiring | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F82024 V control wire to control cabinet was loose.
OF5 | 13 | U1 | 2015-08-07 10:41 |  |  |  |  | 2015-08-07 11:08 |  | 0 | 0 | 0.45 | 0.45 | 3.6 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 4710 |  |  | - |  | Generator metering devices | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Speed probe failed
OF5 | 14 | U1 | 2015-08-10 06:54 |  |  |  |  | 2015-08-10 10:27 |  | 0 | 0 | 3.55 | 3.55 | 28.4 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Dredge
OF5 | 15 | U1 | 2015-08-10 17:59 |  |  |  |  | 2015-08-12 07:25 |  | 0 | 0 | 37.433 | 37.4333 | 299.466 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low flow
OF5 | 16 | U1 | 2015-08-13 14:25 |  |  |  |  | 2015-08-14 09:38 |  | 0 | 0 | 19.217 | 19.2167 | 153.734 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low flow
OF5 | 17 | U1 | 2015-08-15 08:37 |  |  |  |  | 2015-08-16 10:15 |  | 0 | 0 | 25.633 | 25.6333 | 205.067 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low flow
OF5 | 18 | U1 | 2015-08-17 19:17 |  |  |  |  | 2015-08-19 06:58 |  | 0 | 0 | 35.683 | 35.6833 | 285.466 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF5 | 19 | U1 | 2015-08-21 11:55 |  |  |  |  | 2015-08-22 09:40 |  | 0 | 0 | 21.75 | 21.75 | 174 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF5 | 20 | U1 | 2015-08-25 01:54 |  |  |  |  | 2015-08-26 09:28 |  | 0 | 0 | 31.567 | 31.5667 | 252.533 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF5 | 21 | U1 | 2015-08-26 17:56 |  |  |  |  | 2015-08-28 10:11 |  | 0 | 0 | 40.25 | 40.25 | 322 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830LOW FLOW
OF5 | 22 | U1 | 2015-08-29 09:41 |  |  |  |  | 2015-09-01 06:39 |  | 0 | 0 | 68.967 | 68.9667 | 551.733 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF5 | 23 | U1 | 2015-09-01 19:50 |  |  |  |  | 2015-09-03 13:55 |  | 0 | 0 | 42.083 | 42.0833 | 336.666 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low river
OF5 | 24 | U1 | 2015-09-07 09:01 |  |  |  |  | 2015-09-09 06:36 |  | 0 | 0 | 45.583 | 45.5833 | 364.667 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low flow
OF5 | 25 | U1 | 2015-09-12 03:44 |  |  |  |  | 2015-09-14 09:53 |  | 0 | 0 | 54.15 | 54.15 | 433.2 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low flow
OF5 | 26 | U1 | 2015-09-22 18:43 |  |  |  |  | 2015-09-29 07:08 |  | 0 | 0 | 156.417 | 156.4167 | 1251.334 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830LOW FLOW
OF5 | 28 | U1 | 2015-10-05 07:01 |  |  |  |  | 2015-10-05 07:44 |  | 0 | 0 | 0.717 | 0.7167 | 5.733 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 3644 |  |  | - |  | AC Protection devices | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820tripped cause unknown
OF5 | 29 | U1 | 2015-10-05 16:04 |  |  |  |  | 2015-10-05 16:41 |  | 0 | 0 | 0.617 | 0.6167 | 4.933 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 3644 |  |  | - |  | AC Protection devices | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820I&E to trouble shoot cause.
OF5 | 30 | U1 | 2015-10-05 19:35 |  |  |  |  | 2015-10-06 07:49 |  | 0 | 0 | 12.233 | 12.2333 | 97.866 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 4650 |  |  | - |  | Other cooling system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Cooling wtr. pmp. elec. overload.
OF5 | 31 | U1 | 2015-10-09 08:45 |  |  |  |  | 2015-10-12 14:24 |  | 0 | 0 | 77.65 | 77.65 | 621.2 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 3644 |  |  | - |  | AC Protection devices | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820AC protection device took unit off. Being investigated.
OF5 | 32 | U1 | 2015-10-12 14:24 |  |  |  |  | 2015-10-27 10:53 |  | 0 | 0 | 356.483 | 356.4833 | 2851.867 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | NF
|  | DESCRIPTION : |  | F830Low Flow
OF5 | 33 | U1 | 2015-11-01 09:28 |  |  |  |  | 2015-11-01 13:40 |  | 0 | 0 | 4.2 | 4.2 | 33.6 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9720 |  |  | - |  | Other safety problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Divers installing stop logs in # 4 in lower pool. Unit off due to safety for diver
OF5 | 34 | U1 | 2015-11-06 13:10 |  |  |  |  | 2015-11-07 15:46 |  | 0 | 0 | 26.6 | 26.6 | 212.8 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9720 |  |  | - |  | Other safety problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Divers in the water to seal tail gates on unit 4 for dewatering on unit for re-hab
OF5 | 35 | U1 | 2015-11-08 09:34 |  |  |  |  | 2015-11-08 10:53 |  | 0 | 0 | 1.317 | 1.3167 | 10.533 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9720 |  |  | - |  | Other safety problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Off for divers sealing lower head gates on unit4
OF5 | 36 | U1 | 2015-11-11 22:55 |  |  |  |  | 2015-11-12 08:40 |  | 0 | 0 | 9.75 | 9.75 | 78 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 4650 |  |  | - |  | Other cooling system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Cooling water clogged in pit at strainer.
OF5 | 38 | U1 | 2015-11-24 18:52 |  |  |  |  | 2015-11-25 08:21 |  | 0 | 0 | 13.483 | 13.4833 | 107.867 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7008 |  |  | - |  | Bearing cooling system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Strainer basket to L.V. bearing clogged.
OF5 | 39 | U1 | 2015-11-27 03:52 |  |  |  |  | 2015-11-29 11:38 |  | 0 | 0 | 55.767 | 55.7667 | 446.134 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low river conditions
OF5 | 41 | U1 | 2015-12-03 23:17 |  |  |  |  | 2015-12-07 11:38 |  | 0 | 0 | 84.35 | 84.35 | 674.8 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF5 | 42 | U1 | 2015-12-10 13:34 |  |  |  |  | 2015-12-10 13:58 |  | 0 | 0 | 0.4 | 0.4 | 3.2 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 3642 |  |  | - |  | AC Conductors and buses | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Changed from "A" bus to "B" bus.
OF5 | 43 | U1 | 2015-12-24 09:56 |  |  |  |  | 2015-12-31 23:59 |  | 0 | 0 | 182.05 | 182.05 | 1456.4 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF5 | 1 | U1 | 2016-01-01 |  |  |  |  | 2016-01-05 12:00 |  | 0 | 0 | 108 | 108 | 540 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820highwater
OF5 | 2 | U1 | 2016-01-19 10:18 |  |  |  |  | 2016-01-19 11:59 |  | 0 | 0 | 1.683 | 1.6833 | 8.417 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 4650 |  |  | - |  | Other cooling system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820TURBINE GUIDE BRG WATER SUPPLY STOPPED UP
OF5 | 3 | U1 | 2016-01-19 19:53 |  |  |  |  | 2016-01-20 09:53 |  | 0 | 0 | 14 | 14 | 70 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 4650 |  |  | - |  | Other cooling system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Turbine Guide Bearing cooling water flow stopped up.
OF5 | 4 | U1 | 2016-02-03 06:31 |  |  |  |  | 2016-02-10 11:40 |  | 0 | 0 | 173.15 | 173.15 | 865.75 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF5 | 5 | U1 | 2016-02-10 12:28 |  |  |  |  | 2016-02-10 14:37 |  | 0 | 0 | 2.15 | 2.15 | 10.75 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 4609 |  |  | - |  | Other exciter problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Bad digital input card
OF5 | 6 | U1 | 2016-02-10 16:12 |  |  |  |  | 2016-02-11 10:43 |  | 0 | 0 | 18.517 | 18.5167 | 92.583 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 4609 |  |  | - |  | Other exciter problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Exciter feed opened, troubleshooting problem
OF5 | 7 | U1 | 2016-02-13 02:35 |  |  |  |  | 2016-02-13 09:35 |  | 0 | 0 | 7 | 7 | 35 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 4609 |  |  | - |  | Other exciter problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Exciter feed opened
OF5 | 8 | U1 | 2016-02-18 01:17 |  |  |  |  | 2016-03-08 11:02 |  | 0 | 0 | 465.75 | 465.75 | 2686.816 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Highwater
OF5 | 9 | U1 | 2016-03-14 06:23 |  |  |  |  | 2016-03-21 09:32 |  | 0 | 0 | 171.15 | 171.15 | 1198.05 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830highwater
OF5 | 10 | U1 | 2016-04-15 11:39 |  |  |  |  | 2016-04-18 07:51 |  | 0 | 0 | 68.2 | 68.2 | 477.4 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830HIGHWATER
OF5 | 11 | U1 | 2016-05-02 09:52 |  |  |  |  | 2016-05-02 12:32 |  | 0 | 0 | 2.667 | 2.6667 | 18.667 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7190 |  |  | - |  | Dewatering and rewatering equipment | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Divers replacing Level Indicator to the Dewatering Pumps.
OF5 | 12 | U1 | 2016-05-03 06:06 |  |  |  |  | 2016-05-10 09:05 |  | 0 | 0 | 170.983 | 170.9833 | 1196.883 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820HIGHWATER
OF5 | 13 | U1 | 2016-05-12 16:52 |  |  |  |  | 2016-05-16 07:49 |  | 0 | 0 | 86.95 | 86.95 | 608.65 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830highwater
OF5 | 14 | U1 | 2016-05-24 07:32 |  |  |  |  | 2016-05-24 10:21 |  | 0 | 0 | 2.817 | 2.8167 | 19.717 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7190 |  |  | - |  | Dewatering and rewatering equipment | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Divers in water replacing Level Probe at Unit #4.
OF5 | 15 | U1 | 2016-06-03 05:35 |  |  |  |  | 2016-06-03 07:06 |  | 0 | 0 | 1.517 | 1.5167 | 12.133 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 4650 |  |  | - |  | Other cooling system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820air cooler pump clogged.
OF5 | 17 | U1 | 2016-06-05 15:24 |  |  |  |  | 2016-06-05 16:46 |  | 0 | 0 | 1.367 | 1.3667 | 10.933 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 4650 |  |  | - |  | Other cooling system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820L. V bearing strainer clogged
OF5 | 18 | U1 | 2016-06-08 07:07 |  |  |  |  | 2016-06-08 07:33 |  | 0 | 0 | 0.433 | 0.4333 | 3.467 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 4650 |  |  | - |  | Other cooling system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820LV strainer in pit clogged
OF5 | 19 | U1 | 2016-06-08 11:15 |  |  |  |  | 2016-06-08 12:22 |  | 0 | 0 | 1.117 | 1.1167 | 8.933 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 4650 |  |  | - |  | Other cooling system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820LV strainer clogged in pit
OF5 | 20 | U1 | 2016-06-08 16:56 |  |  |  |  | 2016-06-08 19:02 |  | 0 | 0 | 2.1 | 2.1 | 16.8 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 4650 |  |  | - |  | Other cooling system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820LV strainer clogged in pit
OF5 | 21 | U1 | 2016-06-09 01:11 |  |  |  |  | 2016-06-09 07:57 |  | 0 | 0 | 6.767 | 6.7667 | 54.133 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 4650 |  |  | - |  | Other cooling system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820LV strainer clogged in pit
OF5 | 22 | U1 | 2016-06-09 19:21 |  |  |  |  | 2016-06-10 05:40 |  | 0 | 0 | 10.317 | 10.3167 | 82.533 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 4650 |  |  | - |  | Other cooling system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820LV strainer in pit clogged
OF5 | 23 | U1 | 2016-06-11 05:15 |  |  |  |  | 2016-06-11 06:31 |  | 0 | 0 | 1.267 | 1.2667 | 10.133 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 4650 |  |  | - |  | Other cooling system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820LV strainer in pit clogged
OF5 | 24 | U1 | 2016-06-12 08:15 |  |  |  |  | 2016-06-13 06:36 |  | 0 | 0 | 22.35 | 22.35 | 178.8 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF5 | 25 | U1 | 2016-06-14 19:11 |  |  |  |  | 2016-06-18 07:40 |  | 0 | 0 | 84.483 | 84.4833 | 675.866 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830LOW RIVER
OF5 | 26 | U1 | 2016-06-26 06:57 |  |  |  |  | 2016-06-28 09:52 |  | 0 | 0 | 50.917 | 50.9167 | 407.333 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF5 | 27 | U1 | 2016-07-15 01:13 |  |  |  |  | 2016-07-15 08:42 |  | 0 | 0 | 7.483 | 7.4833 | 59.867 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Low River
OF5 | 28 | U1 | 2016-07-19 20:58 |  |  |  |  | 2016-07-21 07:41 |  | 0 | 0 | 34.717 | 34.7167 | 277.734 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF5 | 29 | U1 | 2016-07-22 14:40 |  |  |  |  | 2016-07-23 10:29 |  | 0 | 0 | 19.817 | 19.8167 | 158.534 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF5 | 30 | U1 | 2016-07-24 17:58 |  |  |  |  | 2016-07-26 07:06 |  | 0 | 0 | 37.133 | 37.1333 | 297.067 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF5 | 31 | U1 | 2016-08-07 19:25 |  |  |  |  | 2016-08-08 07:26 |  | 0 | 0 | 12.017 | 12.0167 | 96.134 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF5 | 32 | U1 | 2016-08-11 19:12 |  |  |  |  | 2016-08-13 08:05 |  | 0 | 0 | 36.883 | 36.8833 | 295.067 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830LOW FLOW
OF5 | 33 | U1 | 2016-08-14 19:03 |  |  |  |  | 2016-08-15 06:50 |  | 0 | 0 | 11.783 | 11.7833 | 94.267 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830LOW FLOW
OF5 | 34 | U1 | 2016-08-28 15:52 |  |  |  |  | 2016-09-09 12:21 |  | 0 | 0 | 284.483 | 284.4833 | 2071.517 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF5 | 35 | U1 | 2016-09-15 06:31 |  |  |  |  | 2016-09-17 06:26 |  | 0 | 0 | 47.917 | 47.9167 | 335.416 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF5 | 36 | U1 | 2016-09-17 18:10 |  |  |  |  | 2016-09-22 06:51 |  | 0 | 0 | 108.683 | 108.6833 | 760.783 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low River
OF5 | 37 | U1 | 2016-09-22 22:56 |  |  |  |  | 2016-09-27 07:05 |  | 0 | 0 | 104.15 | 104.15 | 729.05 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF5 | 38 | U1 | 2016-09-27 16:57 |  |  |  |  | 2016-09-29 06:52 |  | 0 | 0 | 37.917 | 37.9167 | 265.417 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830LOW FLOW
OF5 | 39 | U1 | 2016-10-06 23:57 |  |  |  |  | 2016-10-09 09:13 |  | 0 | 0 | 57.267 | 57.2667 | 400.867 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF5 | 40 | U1 | 2016-10-12 13:52 |  |  |  |  | 2016-10-13 12:17 |  | 0 | 0 | 22.417 | 22.4167 | 156.916 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830LOW FLOW
OF5 | 42 | U1 | 2016-10-14 13:12 |  |  |  |  | 2016-10-15 07:41 |  | 0 | 0 | 18.483 | 18.4833 | 129.383 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830LOW FLOW
OF5 | 43 | U1 | 2016-10-18 07:57 |  |  |  |  | 2016-10-20 12:36 |  | 0 | 0 | 52.65 | 52.65 | 368.55 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF5 | 44 | U1 | 2016-10-21 02:17 |  |  |  |  | 2016-10-22 07:02 |  | 0 | 0 | 28.75 | 28.75 | 201.25 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF5 | 45 | U1 | 2016-10-29 11:36 |  |  |  |  | 2016-10-30 08:52 |  | 0 | 0 | 21.267 | 21.2667 | 148.867 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low River
OF5 | 46 | U1 | 2016-11-01 12:45 |  |  |  |  | 2016-11-03 09:26 |  | 0 | 0 | 44.683 | 44.6833 | 312.783 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF5 | 47 | U1 | 2016-11-08 10:42 |  |  |  |  | 2016-11-18 10:07 |  | 0 | 0 | 239.417 | 239.4167 | 1675.917 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830LOW FLOW
OF5 | 48 | U1 | 2016-11-20 11:41 |  |  |  |  | 2016-11-21 08:29 |  | 0 | 0 | 20.8 | 20.8 | 145.6 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF5 | 49 | U1 | 2016-11-22 16:50 |  |  |  |  | 2016-11-23 08:52 |  | 0 | 0 | 16.033 | 16.0333 | 112.234 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF5 | 50 | U1 | 2016-11-26 22:31 |  |  |  |  | 2016-11-29 08:06 |  | 0 | 0 | 57.583 | 57.5833 | 403.083 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF5 | 51 | U1 | 2016-11-30 14:42 |  |  |  |  | 2016-12-02 07:57 |  | 0 | 0 | 41.25 | 41.25 | 224.85 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830LOW FLOW
OF5 | 54 | U1 | 2016-12-20 00:53 |  |  |  |  | 2016-12-26 09:11 |  | 0 | 0 | 152.3 | 152.3 | 761.5 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820HIGH WATER
OF5 | 55 | U1 | 2016-12-31 09:00 |  |  |  |  | 2017-01-01 |  | 0 | 0 | 15 | 15 | 75 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Highwater
OF5 | 1 | U1 | 2017-01-01 |  |  |  |  | 2017-01-02 09:05 |  | 0 | 0 | 33.083 | 33.0833 | 165.417 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Highwater
OF5 | 2 | U1 | 2017-01-06 14:19 |  |  |  |  | 2017-01-10 10:28 |  | 0 | 0 | 92.15 | 92.15 | 460.75 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF5 | 3 | U1 | 2017-01-15 06:55 |  |  |  |  | 2017-01-31 11:31 |  | 0 | 0 | 388.6 | 388.6 | 1943 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830HIGH WATER
OF5 | 5 | U1 | 2017-02-21 08:41 |  |  |  |  | 2017-02-21 10:54 |  | 0 | 0 | 2.217 | 2.2167 | 11.083 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9320 |  |  | - |  | Other miscellaneous external problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F82086 Generator Lock out
OF5 | 6 | U1 | 2017-03-01 19:41 |  |  |  |  | 2017-03-09 11:20 |  | 0 | 0 | 183.65 | 183.65 | 1285.55 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF5 | 7 | U1 | 2017-03-11 18:25 |  |  |  |  | 2017-03-14 08:54 |  | 0 | 0 | 62.483 | 62.4833 | 437.383 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830High water
OF5 | 8 | U1 | 2017-03-31 01:36 |  |  |  |  | 2017-03-31 11:59 |  | 0 | 0 | 10.383 | 10.3833 | 72.683 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Trash
OF5 | 9 | U1 | 2017-04-01 00:35 |  |  |  |  | 2017-04-13 15:57 |  | 0 | 0 | 303.367 | 303.3667 | 2123.567 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820highwater
OF5 | 10 | U1 | 2017-04-29 05:26 |  |  |  |  | 2017-05-18 09:52 |  | 0 | 0 | 460.433 | 460.4333 | 3223.034 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820HIGH WATER
OF5 | 11 | U1 | 2017-05-25 09:46 |  |  |  |  | 2017-05-25 10:09 |  | 0 | 0 | 0.383 | 0.3833 | 2.683 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Trash rack differential high
OF5 | 12 | U1 | 2017-05-25 22:13 |  |  |  |  | 2017-05-31 11:58 |  | 0 | 0 | 133.75 | 133.75 | 936.25 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Highwater
OF5 | 14 | U1 | 2017-06-10 13:55 |  |  |  |  | 2017-06-11 07:40 |  | 0 | 0 | 17.75 | 17.75 | 142 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830LOW RIVER CONDITIONS
OF5 | 15 | U1 | 2017-06-24 20:41 |  |  |  |  | 2017-06-29 10:21 |  | 0 | 0 | 109.667 | 109.6667 | 877.333 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Highwater
OF5 | 17 | U1 | 2017-07-24 09:13 |  |  |  |  | 2017-07-24 10:29 |  | 0 | 0 | 1.267 | 1.2667 | 10.133 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 4650 |  |  | - |  | Other cooling system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Clogged strainers
OF5 | 20 | U1 | 2017-08-04 15:05 |  |  |  |  | 2017-08-04 16:46 |  | 0 | 0 | 1.683 | 1.6833 | 13.467 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 4730 |  |  | - |  | Generator current and potential transformers | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Readings were eratic
OF5 | 21 | U1 | 2017-08-15 11:35 |  |  |  |  | 2017-08-16 07:10 |  | 0 | 0 | 19.583 | 19.5833 | 156.666 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF5 | 22 | U1 | 2017-08-21 12:52 |  |  |  |  | 2017-08-24 06:46 |  | 0 | 0 | 65.9 | 65.9 | 527.2 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF5 | 23 | U1 | 2017-08-27 20:49 |  |  |  |  | 2017-08-30 06:43 |  | 0 | 0 | 57.9 | 57.9 | 463.2 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low flow
OF5 | 24 | U1 | 2017-08-31 15:12 |  |  |  |  | 2017-09-01 12:32 |  | 0 | 0 | 21.333 | 21.3333 | 158.133 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF5 | 25 | U1 | 2017-09-03 10:00 |  |  |  |  | 2017-09-04 09:53 |  | 0 | 0 | 23.883 | 23.8833 | 167.183 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF5 | 26 | U1 | 2017-09-14 19:53 |  |  |  |  | 2017-09-18 10:59 |  | 0 | 0 | 87.1 | 87.1 | 609.7 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low flow
OF5 | 27 | U1 | 2017-09-18 13:10 |  |  |  |  | 2017-09-19 08:08 |  | 0 | 0 | 18.967 | 18.9667 | 132.766 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830LOW FLOW
OF5 | 28 | U1 | 2017-09-20 08:28 |  |  |  |  | 2017-09-30 08:41 |  | 0 | 0 | 240.217 | 240.2167 | 1681.516 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF5 | 29 | U1 | 2017-10-01 17:07 |  |  |  |  | 2017-10-05 07:12 |  | 0 | 0 | 86.083 | 86.0833 | 602.583 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low flow
OF5 | 30 | U1 | 2017-10-17 06:22 |  |  |  |  | 2017-10-19 09:56 |  | 0 | 0 | 51.567 | 51.5667 | 360.966 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF5 | 31 | U1 | 2017-10-22 12:23 |  |  |  |  | 2017-10-26 06:52 |  | 0 | 0 | 90.483 | 90.4833 | 633.384 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF5 | 32 | U1 | 2017-11-06 11:54 |  |  |  |  | 2017-11-13 14:53 |  | 0 | 0 | 170.983 | 170.9833 | 1196.883 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820High River
OF5 | 33 | U1 | 2017-11-21 17:19 |  |  |  |  | 2017-11-25 08:05 |  | 0 | 0 | 86.767 | 86.7667 | 607.366 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Shut down for high water
OF5 | 34 | U1 | 2017-12-26 07:22 |  |  |  |  | 2017-12-27 11:56 |  | 0 | 0 | 28.567 | 28.5667 | 142.834 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830highwater
OF5 | 1 | U1 | 2018-01-08 14:42 |  |  |  |  | 2018-01-09 08:30 |  | 0 | 0 | 17.8 | 17.8 | 89 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low River
OF5 | 2 | U1 | 2018-01-10 12:36 |  |  |  |  | 2018-01-11 13:36 |  | 0 | 0 | 25 | 25 | 125 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF5 | 3 | U1 | 2018-01-14 04:12 |  |  |  |  | 2018-01-20 09:55 |  | 0 | 0 | 149.717 | 149.7167 | 748.583 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF5 | 4 | U1 | 2018-01-24 07:17 |  |  |  |  | 2018-01-30 10:48 |  | 0 | 0 | 147.517 | 147.5167 | 737.583 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830highwater
OF5 | 7 | U1 | 2018-02-08 20:13 |  |  |  |  | 2018-03-12 08:53 |  | 0 | 0 | 756.667 | 756.6667 | 4329.1 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830High river
OF5 | 8 | U1 | 2018-03-23 12:51 |  |  |  |  | 2018-04-15 09:10 |  | 0 | 0 | 548.317 | 548.3167 | 3838.217 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830highwater
OF5 | 9 | U1 | 2018-04-17 05:41 |  |  |  |  | 2018-04-30 12:46 |  | 0 | 0 | 319.083 | 319.0833 | 2233.584 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830highwater
OF5 | 11 | U1 | 2018-05-08 14:01 |  |  |  |  | 2018-05-12 07:55 |  | 0 | 0 | 89.9 | 89.9 | 629.3 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF5 | 12 | U1 | 2018-05-21 06:43 |  |  |  |  | 2018-05-28 07:02 |  | 0 | 0 | 168.317 | 168.3167 | 1178.216 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater / Trash
OF5 | 13 | U1 | 2018-06-01 16:03 |  |  |  |  | 2018-06-01 16:55 |  | 0 | 0 | 0.867 | 0.8667 | 6.933 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 3820 |  |  | - |  | Closed cooling water pumps and motors | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F830Strainer basket clogged on bearing water.
OF5 | 15 | U1 | 2018-06-17 19:23 |  |  |  |  | 2018-06-18 09:05 |  | 0 | 0 | 13.7 | 13.7 | 109.6 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7053 |  |  | - |  | Governor oil system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820GPU Accumulator Piston A Lower Limit Trip
OF5 | 16 | U1 | 2018-06-25 02:48 |  |  |  |  | 2018-06-27 09:24 |  | 0 | 0 | 54.6 | 54.6 | 436.8 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Highwater
OF5 | 18 | U1 | 2018-07-14 03:17 |  |  |  |  | 2018-07-16 07:22 |  | 0 | 0 | 52.083 | 52.0833 | 416.666 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low flow
OF5 | 19 | U1 | 2018-07-16 12:48 |  |  |  |  | 2018-07-17 14:01 |  | 0 | 0 | 25.217 | 25.2167 | 201.733 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Water
OF5 | 20 | U1 | 2018-07-20 11:14 |  |  |  |  | 2018-07-21 06:59 |  | 0 | 0 | 19.75 | 19.75 | 158 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Water
OF5 | 23 | U1 | 2018-08-14 09:54 |  |  |  |  | 2018-08-16 09:10 |  | 0 | 0 | 47.267 | 47.2667 | 378.133 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low flow
OF5 | 24 | U1 | 2018-08-20 08:41 |  |  |  |  | 2018-08-20 14:01 |  | 0 | 0 | 5.333 | 5.3333 | 42.667 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830trash
OF5 | 25 | U1 | 2018-08-22 11:59 |  |  |  |  | 2018-08-22 13:27 |  | 0 | 0 | 1.467 | 1.4667 | 11.733 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9720 |  |  | - |  | Other safety problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Crane Safety
OF5 | 26 | U1 | 2018-09-06 12:19 |  |  |  |  | 2018-09-08 13:38 |  | 0 | 0 | 49.317 | 49.3167 | 345.216 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF5 | 27 | U1 | 2018-09-09 06:00 |  |  |  |  | 2018-09-17 09:26 |  | 0 | 0 | 195.433 | 195.4333 | 1368.033 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF5 | 28 | U1 | 2018-09-20 06:05 |  |  |  |  | 2018-09-24 09:57 |  | 0 | 0 | 99.867 | 99.8667 | 699.067 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF5 | 29 | U1 | 2018-09-24 23:58 |  |  |  |  | 2018-10-04 09:06 |  | 0 | 0 | 225.133 | 225.1333 | 1575.933 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820high water
OF5 | 30 | U1 | 2018-10-10 09:10 |  |  |  |  | 2018-10-10 17:42 |  | 0 | 0 | 8.533 | 8.5333 | 59.733 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Trash in front of facility Intakes
OF5 | 31 | U1 | 2018-10-13 14:55 |  |  |  |  | 2018-10-13 17:55 |  | 0 | 0 | 3 | 3 | 21 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for trash
OF5 | 37 | U1 | 2018-11-02 00:22 |  |  |  |  | 2018-12-09 10:25 |  | 0 | 0 | 898.05 | 898.05 | 5881.516 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Highwater
OF5 | 38 | U1 | 2018-12-17 13:26 |  |  |  |  | 2019-01-01 |  | 0 | 0 | 346.567 | 346.5667 | 1732.833 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830high water
OF5 | 1 | U1 | 2019-01-01 |  |  |  |  | 2019-01-15 08:39 |  | 0 | 0 | 344.65 | 344.65 | 1723.25 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Highwater
OF5 | 2 | U1 | 2019-01-20 17:02 |  |  |  |  | 2019-01-31 23:59 |  | 0 | 0 | 270.95 | 270.95 | 1354.75 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830high water
OF5 | 3 | U1 | 2019-02-01 |  |  |  |  | 2019-02-03 10:16 |  | 0 | 0 | 58.267 | 58.2667 | 291.333 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF5 | 4 | U1 | 2019-02-07 07:56 |  |  |  |  | 2019-03-07 13:10 |  | 0 | 0 | 677.233 | 677.2333 | 3700.5 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830highwater
OF5 | 5 | U1 | 2019-03-10 13:26 |  |  |  |  | 2019-03-18 13:16 |  | 0 | 0 | 191.833 | 191.8333 | 1342.834 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF5 | 8 | U1 | 2019-04-15 12:10 |  |  |  |  | 2019-04-15 14:47 |  | 0 | 0 | 2.617 | 2.6167 | 18.317 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 3710 |  |  | - |  | Transmission line (connected to powerhouse switchyard to 1st Substation) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Line 6608 Protection Relaying
OF5 | 9 | U1 | 2019-04-20 08:35 |  |  |  |  | 2019-05-03 10:25 |  | 0 | 0 | 313.833 | 313.8333 | 2196.834 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF5 | 10 | U1 | 2019-05-03 10:41 |  |  |  |  | 2019-05-29 07:37 |  | 0 | 0 | 620.933 | 620.9333 | 4346.534 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7140 |  |  | - |  | Wicket gate assembly | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Debris in wicket gates
OF5 | 13 | U1 | 2019-06-11 04:43 |  |  |  |  | 2019-06-11 07:12 |  | 0 | 0 | 2.483 | 2.4833 | 19.867 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 4750 |  |  | - |  | Other generator controls and metering problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820speed box fault
OF5 | 14 | U1 | 2019-06-17 13:18 |  |  |  |  | 2019-06-28 10:08 |  | 0 | 0 | 260.833 | 260.8333 | 2086.667 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830high water
OF5 | 15 | U1 | 2019-07-23 07:03 |  |  |  |  | 2019-07-23 14:15 |  | 0 | 0 | 7.2 | 7.2 | 57.6 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830trash
OF5 | 16 | U1 | 2019-08-06 20:19 |  |  |  |  | 2019-08-08 09:33 |  | 0 | 0 | 37.233 | 37.2333 | 297.867 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF5 | 17 | U1 | 2019-08-11 12:40 |  |  |  |  | 2019-08-14 08:48 |  | 0 | 0 | 68.133 | 68.1333 | 545.067 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF5 | 18 | U1 | 2019-08-17 22:49 |  |  |  |  | 2019-08-21 10:38 |  | 0 | 0 | 83.817 | 83.8167 | 670.534 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low river
OF5 | 19 | U1 | 2019-08-22 17:50 |  |  |  |  | 2019-08-23 07:15 |  | 0 | 0 | 13.417 | 13.4167 | 107.333 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF5 | 20 | U1 | 2019-08-24 21:48 |  |  |  |  | 2019-08-25 07:39 |  | 0 | 0 | 9.85 | 9.85 | 78.8 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9720 |  |  | - |  | Other safety problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830river rescue
OF5 | 21 | U1 | 2019-08-26 11:05 |  |  |  |  | 2019-08-29 07:16 |  | 0 | 0 | 68.183 | 68.1833 | 545.466 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Low Flow per ACOE request
OF5 | 22 | U1 | 2019-08-30 09:41 |  |  |  |  | 2019-08-30 10:18 |  | 0 | 0 | 0.617 | 0.6167 | 4.933 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9720 |  |  | - |  | Other safety problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Shut down for Tug/Dredging positioning
OF5 | 23 | U1 | 2019-08-30 15:32 |  |  |  |  | 2019-08-30 16:30 |  | 0 | 0 | 0.967 | 0.9667 | 7.733 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9720 |  |  | - |  | Other safety problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Reposition of tug for dredging
OF5 | 24 | U1 | 2019-08-31 21:46 |  |  |  |  | 2019-09-03 06:56 |  | 0 | 0 | 57.167 | 57.1667 | 402.4 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow, ACOE Request shut down
OF5 | 25 | U1 | 2019-09-06 07:29 |  |  |  |  | 2019-09-17 10:52 |  | 0 | 0 | 267.383 | 267.3833 | 1871.684 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low flow
OF5 | 26 | U1 | 2019-09-18 01:13 |  |  |  |  | 2019-09-19 15:23 |  | 0 | 0 | 38.167 | 38.1667 | 267.166 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low FLow, Requested shut down from ACOE
OF5 | 27 | U1 | 2019-09-20 11:58 |  |  |  |  | 2019-10-02 07:24 |  | 0 | 0 | 283.433 | 283.4333 | 1984.033 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline per ACOE Request Low FLow
OF5 | 28 | U1 | 2019-10-02 18:10 |  |  |  |  | 2019-10-08 06:34 |  | 0 | 0 | 132.4 | 132.4 | 926.8 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low river
OF5 | 29 | U1 | 2019-10-09 17:59 |  |  |  |  | 2019-10-11 06:48 |  | 0 | 0 | 36.817 | 36.8167 | 257.717 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low flow, Offline by request from ACOE
OF5 | 30 | U1 | 2019-10-12 01:55 |  |  |  |  | 2019-10-18 07:01 |  | 0 | 0 | 149.1 | 149.1 | 1043.7 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Water, Offline per request of ACOE
OF5 | 31 | U1 | 2019-10-18 22:13 |  |  |  |  | 2019-10-21 06:55 |  | 0 | 0 | 56.7 | 56.7 | 396.9 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low flow
OF5 | 32 | U1 | 2019-10-22 09:26 |  |  |  |  | 2019-10-23 11:55 |  | 0 | 0 | 26.483 | 26.4833 | 185.384 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low river
OF5 | 34 | U1 | 2019-12-03 05:03 |  |  |  |  | 2019-12-05 14:18 |  | 0 | 0 | 57.25 | 57.25 | 286.25 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820highwater
OF5 | 35 | U1 | 2019-12-14 12:59 |  |  |  |  | 2019-12-24 10:45 |  | 0 | 0 | 237.767 | 237.7667 | 1188.833 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830highwater
OF5 | 36 | U1 | 2019-12-31 11:21 |  |  |  |  | 2019-12-31 23:59 |  | 0 | 0 | 12.633 | 12.6333 | 63.167 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Highwater
OF5 | 1 | U1 | 2020-01-01 |  |  |  |  | 2020-01-10 11:53 |  | 0 | 0 | 227.883 | 227.8833 | 1139.417 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Highwater
OF5 | 2 | U1 | 2020-01-14 09:58 |  |  |  |  | 2020-01-18 11:28 |  | 0 | 0 | 97.5 | 97.5 | 487.5 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830High River
OF5 | 3 | U1 | 2020-01-27 18:53 |  |  |  |  | 2020-02-01 11:01 |  | 0 | 0 | 112.133 | 112.1333 | 560.666 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF5 | 4 | U1 | 2020-02-08 12:15 |  |  |  |  | 2020-02-24 14:14 |  | 0 | 0 | 385.983 | 385.9833 | 1929.917 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Highwater
OF5 | 5 | U1 | 2020-03-05 15:05 |  |  |  |  | 2020-03-10 10:21 |  | 0 | 0 | 115.267 | 115.2667 | 806.867 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Trash
OF5 | 6 | U1 | 2020-03-15 10:17 |  |  |  |  | 2020-04-06 10:11 |  | 0 | 0 | 527.9 | 527.9 | 3695.3 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF5 | 7 | U1 | 2020-04-08 17:50 |  |  |  |  | 2020-04-09 10:59 |  | 0 | 0 | 17.15 | 17.15 | 120.05 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 3670 |  |  | - |  | 12-15kV transformers | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Bad P T fuse
OF5 | 8 | U1 | 2020-04-13 22:14 |  |  |  |  | 2020-04-21 13:22 |  | 0 | 0 | 183.133 | 183.1333 | 1281.934 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Highwater
OF5 | 9 | U1 | 2020-04-28 14:08 |  |  |  |  | 2020-05-11 13:50 |  | 0 | 0 | 311.7 | 311.7 | 2181.9 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Highwater
OF5 | 10 | U1 | 2020-05-20 08:47 |  |  |  |  | 2020-05-30 08:49 |  | 0 | 0 | 240.033 | 240.0333 | 1680.234 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF5 | 11 | U1 | 2020-06-10 09:52 |  |  |  |  | 2020-06-10 17:19 |  | 0 | 0 | 7.45 | 7.45 | 59.6 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for trash
OF5 | 12 | U1 | 2020-06-16 12:14 |  |  |  |  | 2020-06-16 14:02 |  | 0 | 0 | 1.8 | 1.8 | 14.4 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 3710 |  |  | - |  | Transmission line (connected to powerhouse switchyard to 1st Substation) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Transmission Outage
OF5 | 13 | U1 | 2020-06-17 08:58 |  |  |  |  | 2020-06-17 09:29 |  | 0 | 0 | 0.517 | 0.5167 | 4.133 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 3710 |  |  | - |  | Transmission line (connected to powerhouse switchyard to 1st Substation) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Transmission Outage
OF5 | 14 | U1 | 2020-06-26 06:21 |  |  |  |  | 2020-06-26 12:10 |  | 0 | 0 | 5.817 | 5.8167 | 46.533 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9350 |  |  | - |  | Public Safety (water hazard or river rescue) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F590ACOE requested shutdown for safety while they are working on the lower dam.
OF5 | 15 | U1 | 2020-07-08 23:52 |  |  |  |  | 2020-07-10 06:53 |  | 0 | 0 | 31.017 | 31.0167 | 248.134 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Lack of Water (ACOE Offline request)
OF5 | 16 | U1 | 2020-07-16 09:44 |  |  |  |  | 2020-07-23 08:54 |  | 0 | 0 | 167.167 | 167.1667 | 1337.333 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF5 | 17 | U1 | 2020-07-29 15:16 |  |  |  |  | 2020-07-30 11:58 |  | 0 | 0 | 20.7 | 20.7 | 165.6 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830lack of water ACOE
OF5 | 18 | U1 | 2020-08-04 07:12 |  |  |  |  | 2020-08-04 19:34 |  | 0 | 0 | 12.367 | 12.3667 | 98.933 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Trash
OF5 | 19 | U1 | 2020-08-04 19:34 |  |  |  |  | 2020-08-07 15:37 |  | 0 | 0 | 68.05 | 68.05 | 544.4 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | X0
|  | DESCRIPTION : |  | F830Lack of Water (ACOE Request)
OF5 | 20 | U1 | 2020-08-10 10:42 |  |  |  |  | 2020-08-16 09:24 |  | 0 | 0 | 142.7 | 142.7 | 1141.6 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF5 | 22 | U1 | 2020-08-21 07:40 |  |  |  |  | 2020-08-24 11:51 |  | 0 | 0 | 76.183 | 76.1833 | 609.467 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | X0
|  | DESCRIPTION : |  | F830Offline for Lack of Water (ACOE)
OF5 | 23 | U1 | 2020-08-28 13:59 |  |  |  |  | 2020-08-29 08:51 |  | 0 | 0 | 18.867 | 18.8667 | 150.933 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF5 | 24 | U1 | 2020-09-15 07:32 |  |  |  |  | 2020-09-15 08:05 |  | 0 | 0 | 0.55 | 0.55 | 3.85 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 4650 |  |  | - |  | Other cooling system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F120LV Strainer basket plugged.
OF5 | 25 | U1 | 2020-09-15 12:04 |  |  |  |  | 2020-09-15 14:45 |  | 0 | 0 | 2.683 | 2.6833 | 18.783 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for trash.
OF5 | 26 | U1 | 2020-09-17 18:04 |  |  |  |  | 2020-09-18 06:42 |  | 0 | 0 | 12.633 | 12.6333 | 88.433 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Lack of water.
OF5 | 27 | U1 | 2020-09-18 20:48 |  |  |  |  | 2020-09-19 08:40 |  | 0 | 0 | 11.867 | 11.8667 | 83.067 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Lack of water.
OF5 | 28 | U1 | 2020-09-24 11:18 |  |  |  |  | 2020-10-03 08:13 |  | 0 | 0 | 212.917 | 212.9167 | 1490.417 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF5 | 29 | U1 | 2020-10-04 15:25 |  |  |  |  | 2020-10-23 07:35 |  | 0 | 0 | 448.167 | 448.1667 | 3137.166 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Lack of water.
OF5 | 30 | U1 | 2020-10-24 21:16 |  |  |  |  | 2020-10-27 06:50 |  | 0 | 0 | 57.567 | 57.5667 | 402.966 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low flow
OF5 | 32 | U1 | 2020-11-08 23:00 |  |  |  |  | 2020-11-12 07:56 |  | 0 | 0 | 80.933 | 80.9333 | 566.533 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow (ACOE)
OF5 | 34 | U1 | 2020-12-14 00:19 |  |  |  |  | 2020-12-14 08:01 |  | 0 | 0 | 7.7 | 7.7 | 38.5 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 7050 |  |  | - |  | Turbine governor | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820GPU oil pressure
OF5 | 36 | U1 | 2020-12-16 11:05 |  |  |  |  | 2020-12-16 16:38 |  | 0 | 0 | 5.55 | 5.55 | 27.75 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9350 |  |  | - |  | Public Safety (water hazard or river rescue) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Diesel fuel in upper pool
OF5 | 37 | U1 | 2020-12-27 20:57 |  |  |  |  | 2021-01-01 |  | 0 | 0 | 99.05 | 99.05 | 495.25 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Highwater
OF5 | 1 | U1 | 2021-01-01 |  |  |  |  | 2021-01-11 10:43 |  | 0 | 0 | 250.717 | 250.7167 | 3159.03 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for highwater
OF5 | 2 | U1 | 2021-01-27 20:11 |  |  |  |  | 2021-02-05 10:42 |  | 0 | 0 | 206.517 | 206.5167 | 2602.11 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Offline for highwater
OF5 | 3 | U1 | 2021-02-24 21:02 |  |  |  |  | 2021-03-12 10:13 |  | 0 | 0 | 373.183 | 373.1833 | 4702.11 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Highwater
OF5 | 4 | U1 | 2021-03-20 08:25 |  |  |  |  | 2021-03-24 07:26 |  | 0 | 0 | 95.017 | 95.0167 | 1197.21 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830high water
OF5 | 5 | U1 | 2021-03-25 04:19 |  |  |  |  | 2021-03-25 06:53 |  | 0 | 0 | 2.567 | 2.5667 | 32.34 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7009 |  |  | - |  | Bearing oil system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Bearing Oil System. Thrust Pad 1 High temp trip. (No flow)
OF5 | 10 | U1 | 2021-05-22 17:56 |  |  |  |  | 2021-05-25 07:03 |  | 0 | 0 | 61.117 | 61.1167 | 770.07 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830lack of water ACOE
OF5 | 12 | U1 | 2021-06-15 07:54 |  |  |  |  | 2021-06-15 13:09 |  | 0 | 0 | 5.25 | 5.25 | 66.15 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for trash.
OF5 | 13 | U1 | 2021-06-20 02:48 |  |  |  |  | 2021-06-21 07:52 |  | 0 | 0 | 29.067 | 29.0667 | 366.24 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for trash.
OF5 | 14 | U1 | 2021-06-23 06:24 |  |  |  |  | 2021-06-23 06:53 |  | 0 | 0 | 0.483 | 0.4833 | 6.09 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 4650 |  |  | - |  | Other cooling system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Lower Turbine Guide Bearing (LV Bearing) water supply duplex strainer clogged with
OF5 | 15 | U1 | 2021-06-27 15:02 |  |  |  |  | 2021-06-28 07:22 |  | 0 | 0 | 16.333 | 16.3333 | 205.8 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830ACOE requested, Lack of Water
OF5 | 16 | U1 | 2021-06-29 07:31 |  |  |  |  | 2021-07-01 07:35 |  | 0 | 0 | 48.067 | 48.0667 | 605.64 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Lack of Water, Run of River per ACOE
OF5 | 19 | U1 | 2021-07-09 14:50 |  |  |  |  | 2021-07-13 09:23 |  | 0 | 0 | 90.55 | 90.55 | 1140.93 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | FR
|  | DESCRIPTION : |  | F830Offline for trash.
OF5 | 20 | U1 | 2021-08-06 08:55 |  |  |  |  | 2021-08-11 07:04 |  | 0 | 0 | 118.15 | 118.15 | 1488.69 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Lack of Water
OF5 | 21 | U1 | 2021-08-12 02:53 |  |  |  |  | 2021-08-13 07:01 |  | 0 | 0 | 28.133 | 28.1333 | 354.48 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Lack of Water (ACOE)
OF5 | 24 | U1 | 2021-09-01 10:23 |  |  |  |  | 2021-09-01 10:43 |  | 0 | 0 | 0.333 | 0.3333 | 4.2 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 4650 |  |  | - |  | Other cooling system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Turbine Guide Bearing Strainer Clogged/Trip
OF5 | 25 | U1 | 2021-09-03 10:38 |  |  |  |  | 2021-09-06 07:01 |  | 0 | 0 | 68.383 | 68.3833 | 861.63 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for High Water
OF5 | 26 | U1 | 2021-09-11 07:09 |  |  |  |  | 2021-09-16 06:53 |  | 0 | 0 | 119.733 | 119.7333 | 1508.64 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Lack of water.
OF5 | 27 | U1 | 2021-09-16 19:00 |  |  |  |  | 2021-09-18 08:05 |  | 0 | 0 | 37.083 | 37.0833 | 467.25 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Lack of Water
OF5 | 28 | U1 | 2021-09-19 13:07 |  |  |  |  | 2021-09-21 06:42 |  | 0 | 0 | 41.583 | 41.5833 | 523.95 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Lack of Water.
OF5 | 29 | U1 | 2021-09-22 19:16 |  |  |  |  | 2021-09-24 13:35 |  | 0 | 0 | 42.317 | 42.3167 | 533.19 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Lack of Water
OF5 | 30 | U1 | 2021-10-01 08:58 |  |  |  |  | 2021-10-04 07:45 |  | 0 | 0 | 70.783 | 70.7833 | 891.87 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Lack of Water (ACOE)
OF5 | 31 | U1 | 2021-10-14 16:51 |  |  |  |  | 2021-10-25 09:35 |  | 0 | 0 | 256.733 | 256.7333 | 3234.84 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Lack of Water(ACOE)
OF5 | 34 | U1 | 2021-12-12 21:00 |  |  |  |  | 2021-12-15 08:15 |  | 0 | 0 | 59.25 | 59.25 | 746.55 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Run of RIver - Highwater
OF5 | 36 | U1 | 2021-12-31 07:21 |  |  |  |  | 2022-01-01 |  | 0 | 0 | 16.65 | 16.65 | 209.79 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830High Water.
OF5 | 1 | U1 | 2022-01-01 |  |  |  |  | 2022-01-16 13:58 |  | 0 | 0 | 373.967 | 373.9667 | 4711.98 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for High Water.
OF5 | 2 | U1 | 2022-02-03 19:14 |  |  |  |  | 2022-02-14 11:34 |  | 0 | 0 | 256.333 | 256.3333 | 3229.8 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for High Water
OF5 | 3 | U1 | 2022-02-15 13:54 |  |  |  |  | 2022-03-21 07:33 |  | 0 | 0 | 809.65 | 809.65 | 10201.59 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Trash/ Highwater (Run of River)
OF5 | 6 | U1 | 2022-04-10 07:43 |  |  |  |  | 2022-04-18 07:22 |  | 0 | 0 | 191.65 | 191.65 | 2414.79 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for High Water
OF5 | 7 | U1 | 2022-05-07 16:37 |  |  |  |  | 2022-05-16 09:21 |  | 0 | 0 | 208.733 | 208.7333 | 2630.04 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for High Water.
OF5 | 8 | U1 | 2022-05-30 10:18 |  |  |  |  | 2022-06-01 07:23 |  | 0 | 0 | 45.083 | 45.0833 | 568.05 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for high water.
OF5 | 9 | U1 | 2022-06-25 14:54 |  |  |  |  | 2022-06-27 06:58 |  | 0 | 0 | 40.067 | 40.0667 | 504.84 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Lack of Water-Run of River per the ACOE
OF5 | 10 | U1 | 2022-07-01 04:15 |  |  |  |  | 2022-07-05 12:29 |  | 0 | 0 | 104.233 | 104.2333 | 1313.34 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for lack of water.
OF5 | 11 | U1 | 2022-07-16 22:42 |  |  |  |  | 2022-07-17 08:38 |  | 0 | 0 | 9.933 | 9.9333 | 125.16 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 3979 |  |  | - |  | Other DCS problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830There was a Company wide Internet outage, Cane Run lost connectivity with our Plan
OF5 | 12 | U1 | 2022-07-17 14:45 |  |  |  |  | 2022-07-18 07:38 |  | 0 | 0 | 16.883 | 16.8833 | 212.73 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Lack of Water (Run of River) per the ACOE
OF5 | 14 | U1 | 2022-08-02 06:48 |  |  |  |  | 2022-08-02 13:23 |  | 0 | 0 | 6.583 | 6.5833 | 82.95 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Trash
OF5 | 15 | U1 | 2022-08-20 15:01 |  |  |  |  | 2022-08-22 12:24 |  | 0 | 0 | 45.383 | 45.3833 | 571.83 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830lack of water
OF5 | 16 | U1 | 2022-08-23 10:53 |  |  |  |  | 2022-08-23 13:41 |  | 0 | 0 | 2.8 | 2.8 | 35.28 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Trash (Run of River)
OF5 | 17 | U1 | 2022-08-28 17:01 |  |  |  |  | 2022-08-29 10:55 |  | 0 | 0 | 17.9 | 17.9 | 225.54 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Lack of Water per The ACOE
OF5 | 18 | U1 | 2022-09-06 07:17 |  |  |  |  | 2022-09-06 09:00 |  | 0 | 0 | 1.717 | 1.7167 | 21.63 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830trash
OF5 | 19 | U1 | 2022-09-06 12:49 |  |  |  |  | 2022-09-07 07:10 |  | 0 | 0 | 18.35 | 18.35 | 231.21 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820trash
OF5 | 20 | U1 | 2022-09-13 04:13 |  |  |  |  | 2022-09-13 14:04 |  | 0 | 0 | 9.85 | 9.85 | 124.11 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Unit offline for Trash
OF5 | 21 | U1 | 2022-09-14 09:55 |  |  |  |  | 2022-09-23 10:40 |  | 0 | 0 | 216.75 | 216.75 | 2731.05 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Lack of Water
OF5 | 22 | U1 | 2022-09-25 15:44 |  |  |  |  | 2022-10-02 10:00 |  | 0 | 0 | 162.267 | 162.2667 | 2044.56 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for low water.
OF5 | 24 | U1 | 2022-10-06 01:51 |  |  |  |  | 2022-10-06 06:53 |  | 0 | 0 | 5.033 | 5.0333 | 63.42 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7008 |  |  | - |  | Bearing cooling system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Offline for Turbine Bearing Flow
OF5 | 25 | U1 | 2022-10-12 18:21 |  |  |  |  | 2022-10-14 09:00 |  | 0 | 0 | 38.65 | 38.65 | 486.99 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Lack of Water
OF5 | 26 | U1 | 2022-10-14 14:46 |  |  |  |  | 2022-10-22 06:21 |  | 0 | 0 | 183.583 | 183.5833 | 2313.15 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Lack of Water
OF5 | 27 | U1 | 2022-10-29 09:58 |  |  |  |  | 2022-11-06 08:29 |  | 0 | 0 | 190.517 | 190.5167 | 2400.51 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Lack of Water
OF5 | 28 | U1 | 2022-11-07 09:51 |  |  |  |  | 2022-11-09 07:35 |  | 0 | 0 | 45.733 | 45.7333 | 576.24 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830lack of water
OF5 | 29 | U1 | 2022-11-10 09:01 |  |  |  |  | 2022-11-12 14:05 |  | 0 | 0 | 53.067 | 53.0667 | 668.64 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Lack of Water
OF5 | 30 | U1 | 2022-12-11 08:15 |  |  |  |  | 2022-12-12 14:53 |  | 0 | 0 | 30.633 | 30.6333 | 385.98 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830trash
OF5 | 1 | U1 | 2023-01-03 18:00 |  |  |  |  | 2023-01-09 13:18 |  | 0 | 0 | 139.3 | 139.3 | 1755.18 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Offline for trash.
OF5 | 2 | U1 | 2023-01-14 12:32 |  |  |  |  | 2023-01-27 13:48 |  | 0 | 0 | 313.267 | 313.2667 | 3947.16 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820trash
OF5 | 3 | U1 | 2023-01-29 13:26 |  |  |  |  | 2023-01-29 15:00 |  | 0 | 0 | 1.567 | 1.5667 | 19.74 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9320 |  |  | - |  | Other miscellaneous external problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for barge recovery.
OF5 | 4 | U1 | 2023-02-02 19:34 |  |  |  |  | 2023-02-03 12:07 |  | 0 | 0 | 16.55 | 16.55 | 208.53 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820trash
OF5 | 5 | U1 | 2023-02-03 12:07 |  |  |  |  | 2023-02-07 11:12 |  | 0 | 0 | 95.083 | 95.0833 | 1198.05 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9320 |  |  | - |  | Other miscellaneous external problems | [8 empty] | AMP CODE:
|  | DESCRIPTION : |  | FX00barge recovery
OF5 | 7 | U1 | 2023-02-18 04:15 |  |  |  |  | 2023-02-24 10:09 |  | 0 | 0 | 149.9 | 149.9 | 1888.74 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for High Water
OF5 | 8 | U1 | 2023-03-03 13:18 |  |  |  |  | 2023-03-13 10:24 |  | 0 | 0 | 237.1 | 237.1 | 2987.46 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for High Water
OF5 | 9 | U1 | 2023-03-25 02:03 |  |  |  |  | 2023-04-11 06:30 |  | 0 | 0 | 412.45 | 412.45 | 5196.87 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Offline for High Water.
OF5 | 10 | U1 | 2023-04-11 06:30 |  |  |  |  | 2023-04-28 12:50 |  | 0 | 0 | 414.333 | 414.3333 | 5220.6 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9320 |  |  | - |  | Other miscellaneous external problems | [8 empty] | AMP CODE: |  | FR
|  | DESCRIPTION : |  | FX00Barge Recovery
OF5 | 11 | U1 | 2023-05-27 10:09 |  |  |  |  | 2023-06-14 12:45 |  | 0 | 0 | 434.6 | 434.6 | 5475.96 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Lack of Water
OF5 | 12 | U1 | 2023-06-20 07:19 |  |  |  |  | 2023-06-26 07:29 |  | 0 | 0 | 144.167 | 144.1667 | 1816.5 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline lack of water.
OF5 | 13 | U1 | 2023-06-26 07:29 |  |  |  |  | 2023-06-26 16:06 |  | 0 | 0 | 8.617 | 8.6167 | 108.57 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | FR
|  | DESCRIPTION : |  | F530MSI sonar.
OF5 | 14 | U1 | 2023-07-01 05:24 |  |  |  |  | 2023-07-02 07:15 |  | 0 | 0 | 25.85 | 25.85 | 325.71 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830lack of water
OF5 | 15 | U1 | 2023-07-07 07:49 |  |  |  |  | 2023-07-07 12:45 |  | 0 | 0 | 4.933 | 4.9333 | 62.16 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Trash
OF5 | 16 | U1 | 2023-07-17 21:33 |  |  |  |  | 2023-07-19 06:46 |  | 0 | 0 | 33.217 | 33.2167 | 418.53 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline lack of water.
OF5 | 17 | U1 | 2023-07-31 10:58 |  |  |  |  | 2023-08-01 09:09 |  | 0 | 0 | 22.183 | 22.1833 | 279.51 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline lack of water.
OF5 | 18 | U1 | 2023-08-03 06:49 |  |  |  |  | 2023-08-07 09:50 |  | 0 | 0 | 99.017 | 99.0167 | 1247.61 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for lack of water.
OF5 | 20 | U1 | 2023-08-13 08:12 |  |  |  |  | 2023-08-13 09:05 |  | 0 | 0 | 0.883 | 0.8833 | 11.13 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE:
|  | DESCRIPTION : |  | F830lack of water
OF5 | 21 | U1 | 2023-08-21 09:16 |  |  |  |  | 2023-08-25 09:01 |  | 0 | 0 | 95.75 | 95.75 | 1206.45 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline lack of water.
OF5 | 22 | U1 | 2023-09-02 18:03 |  |  |  |  | 2023-09-07 12:48 |  | 0 | 0 | 114.75 | 114.75 | 1445.85 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Lack of water
OF5 | 23 | U1 | 2023-09-08 13:07 |  |  |  |  | 2023-09-09 05:30 |  | 0 | 0 | 16.383 | 16.3833 | 206.43 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for lack of water
OF5 | 25 | U1 | 2023-09-23 06:24 |  |  |  |  | 2023-09-26 10:51 |  | 0 | 0 | 76.45 | 76.45 | 963.27 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | FR
|  | DESCRIPTION : |  | F830lack of water
OF5 | 26 | U1 | 2023-09-27 08:36 |  |  |  |  | 2023-09-29 07:38 |  | 0 | 0 | 47.033 | 47.0333 | 592.62 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for lack of water
OF5 | 27 | U1 | 2023-09-30 01:58 |  |  |  |  | 2023-11-01 08:52 |  | 0 | 0 | 774.9 | 774.9 | 9763.74 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for lack of water
OF5 | 28 | U1 | 2023-11-07 02:02 |  |  |  |  | 2023-11-20 10:39 |  | 0 | 0 | 320.617 | 320.6167 | 4039.77 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830lack of water
OF5 | 29 | U1 | 2023-12-20 08:02 |  |  |  |  | 2023-12-21 11:02 |  | 0 | 0 | 27 | 27 | 340.2 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 3670 |  |  | - |  | 12-15kV transformers | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830carded TR-2 for MAC construction to replace catwalk for relay room
Ohio Falls - OF6
Unit | Event | Type | Start |  |  |  |  | End |  | GAC | NAC | Duration | Equiv Hrs | Equiv MWH | Cont | Work Start | Work End |  | Hours |  |  | Gross Capacity Impact (MW)
OF6 | 1 | U1 | 2014-01-01 |  |  |  |  | 2014-01-05 13:39 |  | 0 | 0 | 109.65 | 109.65 | 548.25 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830High water
OF6 | 2 | U1 | 2014-01-12 12:05 |  |  |  |  | 2014-01-20 13:40 |  | 0 | 0 | 193.583 | 193.5833 | 967.916 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF6 | 3 | U1 | 2014-02-05 14:01 |  |  |  |  | 2014-02-12 13:45 |  | 0 | 0 | 167.733 | 167.7333 | 838.667 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF6 | 4 | U1 | 2014-02-20 14:07 |  |  |  |  | 2014-03-03 10:59 |  | 0 | 0 | 260.867 | 260.8667 | 1304.334 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF6 | 5 | U1 | 2014-03-10 06:53 |  |  |  |  | 2014-03-11 09:45 |  | 0 | 0 | 26.867 | 26.8667 | 134.333 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Trash isuses.
OF6 | 6 | U1 | 2014-03-15 07:37 |  |  |  |  | 2014-03-18 09:22 |  | 0 | 0 | 73.75 | 73.75 | 368.75 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830High water.
OF6 | 8 | U1 | 2014-04-03 07:11 |  |  |  |  | 2014-04-14 14:20 |  | 0 | 0 | 271.15 | 271.15 | 2169.2 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF6 | 9 | U1 | 2014-04-22 07:17 |  |  |  |  | 2014-04-22 09:05 |  | 0 | 0 | 1.8 | 1.8 | 14.4 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7008 |  |  | - |  | Bearing cooling system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Water to turbine guide bearing strainer stopped up with debris.
OF6 | 10 | U1 | 2014-04-30 13:37 |  |  |  |  | 2014-05-07 08:55 |  | 0 | 0 | 163.3 | 163.3 | 1306.4 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF6 | 13 | U1 | 2014-05-16 13:09 |  |  |  |  | 2014-05-25 09:28 |  | 0 | 0 | 212.317 | 212.3167 | 1698.533 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830highwater
OF6 | 14 | U1 | 2014-05-28 08:37 |  |  |  |  | 2014-05-28 16:38 |  | 0 | 0 | 8.017 | 8.0167 | 64.133 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7190 |  |  | - |  | Dewatering and rewatering equipment | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Diver in water moving dewatering pumps,too much turbulance with units running.
OF6 | 15 | U1 | 2014-05-29 10:50 |  |  |  |  | 2014-05-29 14:52 |  | 0 | 0 | 4.033 | 4.0333 | 32.267 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7190 |  |  | - |  | Dewatering and rewatering equipment | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Divers in the water, too much turbulance
OF6 | 16 | U1 | 2014-05-30 07:28 |  |  |  |  | 2014-05-30 14:50 |  | 0 | 0 | 7.367 | 7.3667 | 58.933 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7190 |  |  | - |  | Dewatering and rewatering equipment | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Divers in the water, too much turbulance from units running
OF6 | 17 | U1 | 2014-06-04 11:28 |  |  |  |  | 2014-06-05 06:41 |  | 0 | 0 | 19.217 | 19.2167 | 153.734 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830LOW RIVER
OF6 | 18 | U1 | 2014-07-13 11:53 |  |  |  |  | 2014-07-14 06:51 |  | 0 | 0 | 18.967 | 18.9667 | 151.733 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low flow
OF6 | 19 | U1 | 2014-07-22 13:31 |  |  |  |  | 2014-07-22 15:00 |  | 0 | 0 | 1.483 | 1.4833 | 11.867 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9590 |  |  | - |  | Miscellaneous regulatory (this code is primarily intended for use with event contribution code 2 to indicate that a regulatory-related factor contributed to the primary cause of the event) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Ferc diver inspection
OF6 | 20 | U1 | 2014-07-22 15:00 |  |  |  |  | 2014-07-25 09:45 |  | 0 | 0 | 66.75 | 66.75 | 534 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | NF
|  | DESCRIPTION : |  | FE00Low Flow
OF6 | 21 | U1 | 2014-07-26 06:31 |  |  |  |  | 2014-07-27 08:49 |  | 0 | 0 | 26.3 | 26.3 | 210.4 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | FE00Low Flow
OF6 | 22 | U1 | 2014-07-29 00:13 |  |  |  |  | 2014-07-30 06:34 |  | 0 | 0 | 30.35 | 30.35 | 242.8 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low flow
OF6 | 23 | U1 | 2014-08-25 00:42 |  |  |  |  | 2014-08-25 14:50 |  | 0 | 0 | 14.133 | 14.1333 | 113.067 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7009 |  |  | - |  | Bearing oil system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Intermediate bearing oil slinger spring broke.
OF6 | 24 | U1 | 2014-09-01 09:31 |  |  |  |  | 2014-09-02 07:18 |  | 0 | 0 | 21.783 | 21.7833 | 174.267 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Trash
OF6 | 25 | U1 | 2014-09-07 04:07 |  |  |  |  | 2014-09-07 06:50 |  | 0 | 0 | 2.717 | 2.7167 | 21.733 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7008 |  |  | - |  | Bearing cooling system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Unit trip, Turbine Bearing Cooling Water Flow trip.
OF6 | 26 | U1 | 2014-09-07 06:50 |  |  |  |  | 2014-09-08 06:46 |  | 0 | 0 | 23.933 | 23.9333 | 191.466 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | NF
|  | DESCRIPTION : |  | FE00Low Flow
OF6 | 27 | U1 | 2014-09-20 20:00 |  |  |  |  | 2014-09-22 07:15 |  | 0 | 0 | 35.25 | 35.25 | 282 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low river
OF6 | 28 | U1 | 2014-09-24 14:14 |  |  |  |  | 2014-09-26 06:50 |  | 0 | 0 | 40.6 | 40.6 | 324.8 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF6 | 30 | U1 | 2014-11-13 15:12 |  |  |  |  | 2014-11-14 11:52 |  | 0 | 0 | 20.667 | 20.6667 | 124 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7141 |  |  | - |  | Wicket gate operating mechanism or positioner | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830repair broken link
OF6 | 31 | U1 | 2014-12-07 08:51 |  |  |  |  | 2014-12-12 11:22 |  | 0 | 0 | 122.517 | 122.5167 | 612.583 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830HIGH WATER
OF6 | 1 | U1 | 2015-01-16 13:58 |  |  |  |  | 2015-01-16 14:37 |  | 0 | 0 | 0.65 | 0.65 | 3.25 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 4555 |  |  | - |  | Bearing cooling system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Intake water screen stopped up.
OF6 | 2 | U1 | 2015-01-18 16:30 |  |  |  |  | 2015-01-19 09:56 |  | 0 | 0 | 17.433 | 17.4333 | 87.167 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 7050 |  |  | - |  | Turbine governor | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Gen. pressure unit malfunction. Low oil pressure.
OF6 | 3 | U1 | 2015-02-06 13:31 |  |  |  |  | 2015-02-07 13:27 |  | 0 | 0 | 23.933 | 23.9333 | 119.667 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Trash flush
OF6 | 4 | U1 | 2015-02-19 21:28 |  |  |  |  | 2015-02-19 22:53 |  | 0 | 0 | 1.417 | 1.4167 | 7.083 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 4560 |  |  | - |  | Generator vibration (excluding vibration due to failed bearing and other components) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Think big slabs of ice got into intakes and caused sever vibration to generator by
OF6 | 5 | U1 | 2015-02-20 00:10 |  |  |  |  | 2015-02-20 04:07 |  | 0 | 0 | 3.95 | 3.95 | 19.75 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 7008 |  |  | - |  | Bearing cooling system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Thrust bearing oil temp high. Tripped.
OF6 | 6 | U1 | 2015-03-04 11:56 |  |  |  |  | 2015-03-27 11:52 |  | 0 | 0 | 551.933 | 551.9333 | 2759.666 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF6 | 7 | U1 | 2015-04-03 10:08 |  |  |  |  | 2015-04-28 12:48 |  | 0 | 0 | 602.667 | 602.6667 | 4821.333 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF6 | 8 | U1 | 2015-04-29 13:45 |  |  |  |  | 2015-04-29 14:14 |  | 0 | 0 | 0.483 | 0.4833 | 3.867 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 4740 |  |  | - |  | Emergency generator trip devices | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820#11 Turbine Pit Water Level High High Trip
OF6 | 9 | U1 | 2015-05-05 08:16 |  |  |  |  | 2015-05-05 12:43 |  | 0 | 0 | 4.45 | 4.45 | 35.6 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 4650 |  |  | - |  | Other cooling system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Clogged strainer to turbine cooling water system.
OF6 | 10 | U1 | 2015-06-01 15:33 |  |  |  |  | 2015-06-11 16:10 |  | 0 | 0 | 240.617 | 240.6167 | 1924.933 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7141 |  |  | - |  | Wicket gate operating mechanism or positioner | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Servo cylinder has broke away from speed ring
OF6 | 11 | U1 | 2015-06-21 05:50 |  |  |  |  | 2015-06-26 13:24 |  | 0 | 0 | 127.567 | 127.5667 | 1020.533 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830High water.
OF6 | 12 | U1 | 2015-06-27 07:33 |  |  |  |  | 2015-06-27 09:51 |  | 0 | 0 | 2.3 | 2.3 | 18.4 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 4740 |  |  | - |  | Emergency generator trip devices | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820High water in Pit (trip)
OF6 | 13 | U1 | 2015-06-30 12:15 |  |  |  |  | 2015-07-07 07:29 |  | 0 | 0 | 163.233 | 163.2333 | 1305.867 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF6 | 14 | U1 | 2015-07-09 20:31 |  |  |  |  | 2015-07-10 07:19 |  | 0 | 0 | 10.8 | 10.8 | 86.4 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 3973 |  |  | - |  | DCS - internal and termination wiring | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Loose wire on gate wicket circuit, lost communication causing wicket gates to shu
OF6 | 15 | U1 | 2015-07-12 08:37 |  |  |  |  | 2015-07-22 13:06 |  | 0 | 0 | 244.483 | 244.4833 | 1955.867 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF6 | 16 | U1 | 2015-07-25 09:33 |  |  |  |  | 2015-07-26 08:03 |  | 0 | 0 | 22.5 | 22.5 | 180 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Trash
OF6 | 17 | U1 | 2015-07-28 03:18 |  |  |  |  | 2015-07-28 06:24 |  | 0 | 0 | 3.1 | 3.1 | 24.8 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 3812 |  |  | - |  | Service water valves | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Had to replace service water valve.
OF6 | 18 | U1 | 2015-08-10 06:50 |  |  |  |  | 2015-08-10 10:05 |  | 0 | 0 | 3.25 | 3.25 | 26 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Dredge
OF6 | 19 | U1 | 2015-08-10 14:58 |  |  |  |  | 2015-08-11 13:03 |  | 0 | 0 | 22.083 | 22.0833 | 176.667 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low flow
OF6 | 20 | U1 | 2015-08-13 14:28 |  |  |  |  | 2015-08-14 06:28 |  | 0 | 0 | 16 | 16 | 128 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low flow
OF6 | 21 | U1 | 2015-08-15 12:21 |  |  |  |  | 2015-08-19 07:12 |  | 0 | 0 | 90.85 | 90.85 | 726.8 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low flow
OF6 | 22 | U1 | 2015-08-21 07:31 |  |  |  |  | 2015-08-26 12:02 |  | 0 | 0 | 124.517 | 124.5167 | 996.134 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF6 | 23 | U1 | 2015-08-26 18:06 |  |  |  |  | 2015-08-28 08:45 |  | 0 | 0 | 38.65 | 38.65 | 309.2 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830LOW FLOW
OF6 | 24 | U1 | 2015-08-29 08:10 |  |  |  |  | 2015-09-04 10:30 |  | 0 | 0 | 146.333 | 146.3333 | 1170.667 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF6 | 25 | U1 | 2015-09-05 16:14 |  |  |  |  | 2015-09-11 10:48 |  | 0 | 0 | 138.567 | 138.5667 | 1108.533 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low river
OF6 | 26 | U1 | 2015-09-12 05:00 |  |  |  |  | 2015-09-14 07:40 |  | 0 | 0 | 50.667 | 50.6667 | 405.333 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low flow
OF6 | 28 | U1 | 2015-09-17 12:33 |  |  |  |  | 2015-09-22 09:19 |  | 0 | 0 | 116.767 | 116.7667 | 934.133 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF6 | 29 | U1 | 2015-09-22 18:46 |  |  |  |  | 2015-09-29 06:42 |  | 0 | 0 | 155.933 | 155.9333 | 1247.467 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830LOW FLOW
OF6 | 31 | U1 | 2015-10-16 09:18 |  |  |  |  | 2015-10-20 11:54 |  | 0 | 0 | 98.6 | 98.6 | 788.8 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830LOW FLOW
OF6 | 32 | U1 | 2015-10-20 14:10 |  |  |  |  | 2015-10-21 10:13 |  | 0 | 0 | 20.05 | 20.05 | 160.4 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7140 |  |  | - |  | Wicket gate assembly | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820BROKEN WICKET GATE LINK
OF6 | 33 | U1 | 2015-10-31 04:51 |  |  |  |  | 2015-10-31 07:01 |  | 0 | 0 | 2.167 | 2.1667 | 17.333 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 4650 |  |  | - |  | Other cooling system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Coolwater strainer blocked.
OF6 | 34 | U1 | 2015-11-11 20:25 |  |  |  |  | 2015-11-12 08:24 |  | 0 | 0 | 11.983 | 11.9833 | 95.867 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 4650 |  |  | - |  | Other cooling system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820cooling water to pit clogged at strainer.
OF6 | 36 | U1 | 2015-11-17 15:20 |  |  |  |  | 2015-11-17 16:19 |  | 0 | 0 | 0.983 | 0.9833 | 7.867 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7009 |  |  | - |  | Bearing oil system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Intermediate bearing had low oil flow. False indication. I&E corrected problem.
OF6 | 37 | U1 | 2015-11-18 00:42 |  |  |  |  | 2015-11-18 09:01 |  | 0 | 0 | 8.317 | 8.3167 | 66.533 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7053 |  |  | - |  | Governor oil system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820GPU oil pressure high trip. I&E corrected problem.
OF6 | 39 | U1 | 2015-12-03 22:01 |  |  |  |  | 2015-12-07 14:03 |  | 0 | 0 | 88.033 | 88.0333 | 704.267 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF6 | 40 | U1 | 2015-12-11 12:58 |  |  |  |  | 2015-12-11 13:29 |  | 0 | 0 | 0.517 | 0.5167 | 4.133 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 3642 |  |  | - |  | AC Conductors and buses | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Took Unit off of "A" bus and put it back on the "B" bus
OF6 | 41 | U1 | 2015-12-24 09:47 |  |  |  |  | 2015-12-31 23:59 |  | 0 | 0 | 182.2 | 182.2 | 1457.6 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF6 | 1 | U1 | 2016-01-01 |  |  |  |  | 2016-01-05 10:25 |  | 0 | 0 | 106.417 | 106.4167 | 532.083 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820highwater
OF6 | 2 | U1 | 2016-01-06 06:20 |  |  |  |  | 2016-01-06 08:55 |  | 0 | 0 | 2.583 | 2.5833 | 12.917 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 4650 |  |  | - |  | Other cooling system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Cooling water intakes clogged
OF6 | 3 | U1 | 2016-01-19 10:18 |  |  |  |  | 2016-01-19 14:43 |  | 0 | 0 | 4.417 | 4.4167 | 22.083 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 4650 |  |  | - |  | Other cooling system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Turbine guide brg cooling water stopped up.
OF6 | 4 | U1 | 2016-01-20 10:22 |  |  |  |  | 2016-01-20 10:46 |  | 0 | 0 | 0.4 | 0.4 | 2 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 4650 |  |  | - |  | Other cooling system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Turbine Guide Bearing cooling water stopped up.
OF6 | 5 | U1 | 2016-02-03 06:09 |  |  |  |  | 2016-02-10 10:33 |  | 0 | 0 | 172.4 | 172.4 | 862 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Highwater
OF6 | 6 | U1 | 2016-02-18 01:16 |  |  |  |  | 2016-03-08 09:08 |  | 0 | 0 | 463.867 | 463.8667 | 2673.6 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Highwater
OF6 | 7 | U1 | 2016-03-14 08:17 |  |  |  |  | 2016-03-21 07:38 |  | 0 | 0 | 167.35 | 167.35 | 1171.45 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830highwater
OF6 | 8 | U1 | 2016-03-27 16:35 |  |  |  |  | 2016-03-28 07:37 |  | 0 | 0 | 15.033 | 15.0333 | 105.234 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 4650 |  |  | - |  | Other cooling system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820L V strainer basket clogged.
OF6 | 9 | U1 | 2016-04-15 12:34 |  |  |  |  | 2016-04-18 07:29 |  | 0 | 0 | 66.917 | 66.9167 | 468.416 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830HIGHWATER
OF6 | 10 | U1 | 2016-04-19 16:14 |  |  |  |  | 2016-04-19 18:15 |  | 0 | 0 | 2.017 | 2.0167 | 14.117 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 4650 |  |  | - |  | Other cooling system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820L V bearing water clogged with debris.
OF6 | 11 | U1 | 2016-05-03 06:04 |  |  |  |  | 2016-05-10 07:40 |  | 0 | 0 | 169.6 | 169.6 | 1187.2 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820HIGHWATER
OF6 | 12 | U1 | 2016-05-12 15:53 |  |  |  |  | 2016-05-16 07:36 |  | 0 | 0 | 87.717 | 87.7167 | 614.017 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820highwater
OF6 | 13 | U1 | 2016-05-30 07:46 |  |  |  |  | 2016-05-30 08:40 |  | 0 | 0 | 0.9 | 0.9 | 6.3 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 4650 |  |  | - |  | Other cooling system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820L.V. strainer basket clogged
OF6 | 15 | U1 | 2016-06-04 12:15 |  |  |  |  | 2016-06-04 12:48 |  | 0 | 0 | 0.55 | 0.55 | 4.4 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 4650 |  |  | - |  | Other cooling system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Clogged strainer basket
OF6 | 16 | U1 | 2016-06-09 01:06 |  |  |  |  | 2016-06-09 07:00 |  | 0 | 0 | 5.9 | 5.9 | 47.2 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 4650 |  |  | - |  | Other cooling system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820LV strainer clogged in pit
OF6 | 17 | U1 | 2016-06-15 19:05 |  |  |  |  | 2016-06-18 08:22 |  | 0 | 0 | 61.283 | 61.2833 | 490.266 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830LOW RIVER
OF6 | 18 | U1 | 2016-06-18 08:26 |  |  |  |  | 2016-06-18 08:59 |  | 0 | 0 | 0.55 | 0.55 | 4.4 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7141 |  |  | - |  | Wicket gate operating mechanism or positioner | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820GATE POSITION ERROR
OF6 | 19 | U1 | 2016-06-20 16:17 |  |  |  |  | 2016-06-22 13:51 |  | 0 | 0 | 45.567 | 45.5667 | 364.533 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Low River
OF6 | 20 | U1 | 2016-06-26 07:02 |  |  |  |  | 2016-06-28 07:43 |  | 0 | 0 | 48.683 | 48.6833 | 389.466 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF6 | 21 | U1 | 2016-07-03 15:26 |  |  |  |  | 2016-07-03 16:53 |  | 0 | 0 | 1.45 | 1.45 | 11.6 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 4750 |  |  | - |  | Other generator controls and metering problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Speed Box Overspeed Trip
OF6 | 22 | U1 | 2016-07-20 04:39 |  |  |  |  | 2016-07-21 07:01 |  | 0 | 0 | 26.367 | 26.3667 | 210.933 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF6 | 23 | U1 | 2016-07-22 16:52 |  |  |  |  | 2016-07-23 09:47 |  | 0 | 0 | 16.917 | 16.9167 | 135.334 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF6 | 24 | U1 | 2016-07-24 19:00 |  |  |  |  | 2016-07-29 08:43 |  | 0 | 0 | 109.717 | 109.7167 | 877.733 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF6 | 25 | U1 | 2016-08-11 13:02 |  |  |  |  | 2016-08-14 07:13 |  | 0 | 0 | 66.183 | 66.1833 | 529.466 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830LOW FLOW
OF6 | 26 | U1 | 2016-08-14 20:05 |  |  |  |  | 2016-08-15 12:00 |  | 0 | 0 | 15.917 | 15.9167 | 127.333 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830LOW FLOW
OF6 | 27 | U1 | 2016-08-28 17:56 |  |  |  |  | 2016-09-10 06:36 |  | 0 | 0 | 300.667 | 300.6667 | 2182.733 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF6 | 28 | U1 | 2016-09-11 21:06 |  |  |  |  | 2016-09-12 07:10 |  | 0 | 0 | 10.067 | 10.0667 | 70.467 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 3653 |  |  | - |  | DC protection devices | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F82086-Lockout
OF6 | 30 | U1 | 2016-09-15 11:00 |  |  |  |  | 2016-09-19 07:44 |  | 0 | 0 | 92.733 | 92.7333 | 649.133 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | FR
|  | DESCRIPTION : |  | F820Low Flow
OF6 | 31 | U1 | 2016-09-23 06:16 |  |  |  |  | 2016-09-29 07:16 |  | 0 | 0 | 145 | 145 | 1015 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF6 | 32 | U1 | 2016-10-06 23:59 |  |  |  |  | 2016-10-07 07:17 |  | 0 | 0 | 7.3 | 7.3 | 51.1 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF6 | 34 | U1 | 2016-10-14 11:27 |  |  |  |  | 2016-10-20 07:02 |  | 0 | 0 | 139.583 | 139.5833 | 977.083 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low flow
OF6 | 35 | U1 | 2016-10-21 07:01 |  |  |  |  | 2016-10-22 06:47 |  | 0 | 0 | 23.767 | 23.7667 | 166.366 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF6 | 36 | U1 | 2016-11-12 13:00 |  |  |  |  | 2016-11-18 10:37 |  | 0 | 0 | 141.617 | 141.6167 | 991.317 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830LOW FLOW
OF6 | 37 | U1 | 2016-11-20 10:16 |  |  |  |  | 2016-11-21 08:06 |  | 0 | 0 | 21.833 | 21.8333 | 152.833 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF6 | 38 | U1 | 2016-12-19 23:19 |  |  |  |  | 2016-12-26 08:59 |  | 0 | 0 | 153.667 | 153.6667 | 768.334 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820HIGH WATER
OF6 | 39 | U1 | 2016-12-31 08:58 |  |  |  |  | 2017-01-01 |  | 0 | 0 | 15.033 | 15.0333 | 75.167 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF6 | 1 | U1 | 2017-01-01 |  |  |  |  | 2017-01-02 08:56 |  | 0 | 0 | 32.933 | 32.9333 | 164.667 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF6 | 2 | U1 | 2017-01-07 00:56 |  |  |  |  | 2017-01-10 10:13 |  | 0 | 0 | 81.283 | 81.2833 | 406.416 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF6 | 3 | U1 | 2017-01-15 10:05 |  |  |  |  | 2017-01-31 10:10 |  | 0 | 0 | 384.083 | 384.0833 | 1920.416 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830HIGH WATER
OF6 | 5 | U1 | 2017-03-01 19:42 |  |  |  |  | 2017-03-09 11:07 |  | 0 | 0 | 183.417 | 183.4167 | 1283.917 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF6 | 6 | U1 | 2017-03-11 18:28 |  |  |  |  | 2017-03-14 07:44 |  | 0 | 0 | 61.267 | 61.2667 | 428.866 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Off for High water
OF6 | 7 | U1 | 2017-04-01 00:31 |  |  |  |  | 2017-04-13 16:23 |  | 0 | 0 | 303.867 | 303.8667 | 2127.066 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820highwater
OF6 | 8 | U1 | 2017-04-29 05:25 |  |  |  |  | 2017-05-18 07:16 |  | 0 | 0 | 457.85 | 457.85 | 3204.95 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820HIGH WATER
OF6 | 9 | U1 | 2017-05-25 22:19 |  |  |  |  | 2017-05-31 12:15 |  | 0 | 0 | 133.933 | 133.9333 | 937.533 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF6 | 10 | U1 | 2017-06-04 05:13 |  |  |  |  | 2017-06-04 07:10 |  | 0 | 0 | 1.95 | 1.95 | 15.6 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 4650 |  |  | - |  | Other cooling system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820LV Bearing strainer basket clogged
OF6 | 11 | U1 | 2017-06-10 12:55 |  |  |  |  | 2017-06-12 09:10 |  | 0 | 0 | 44.25 | 44.25 | 354 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830LOW RIVER CONDITIONS
OF6 | 12 | U1 | 2017-06-16 01:12 |  |  |  |  | 2017-06-16 07:00 |  | 0 | 0 | 5.8 | 5.8 | 46.4 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 4650 |  |  | - |  | Other cooling system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820L.V. strainer baskets clogged.
OF6 | 13 | U1 | 2017-06-25 00:20 |  |  |  |  | 2017-06-29 13:27 |  | 0 | 0 | 109.117 | 109.1167 | 872.933 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Highwater
OF6 | 18 | U1 | 2017-08-21 10:55 |  |  |  |  | 2017-08-24 07:08 |  | 0 | 0 | 68.217 | 68.2167 | 545.734 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF6 | 19 | U1 | 2017-08-28 04:35 |  |  |  |  | 2017-08-30 10:41 |  | 0 | 0 | 54.1 | 54.1 | 432.8 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low flow
OF6 | 20 | U1 | 2017-08-31 21:56 |  |  |  |  | 2017-09-01 12:14 |  | 0 | 0 | 14.3 | 14.3 | 102.166 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF6 | 21 | U1 | 2017-09-03 08:01 |  |  |  |  | 2017-09-04 09:28 |  | 0 | 0 | 25.45 | 25.45 | 178.15 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF6 | 22 | U1 | 2017-09-11 00:23 |  |  |  |  | 2017-09-13 06:58 |  | 0 | 0 | 54.583 | 54.5833 | 382.084 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF6 | 23 | U1 | 2017-09-15 07:29 |  |  |  |  | 2017-09-25 07:32 |  | 0 | 0 | 240.05 | 240.05 | 1680.35 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low flow
OF6 | 24 | U1 | 2017-09-25 21:58 |  |  |  |  | 2017-09-30 08:59 |  | 0 | 0 | 107.017 | 107.0167 | 749.116 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF6 | 25 | U1 | 2017-10-01 14:22 |  |  |  |  | 2017-10-09 07:00 |  | 0 | 0 | 184.633 | 184.6333 | 1292.433 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low flow
OF6 | 26 | U1 | 2017-10-15 12:51 |  |  |  |  | 2017-10-15 15:18 |  | 0 | 0 | 2.45 | 2.45 | 17.15 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 3974 |  |  | - |  | DCS - logic problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Loss of signal from tail water sensor.
OF6 | 27 | U1 | 2017-10-15 15:18 |  |  |  |  | 2017-10-19 06:45 |  | 0 | 0 | 87.45 | 87.45 | 612.15 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | FR
|  | DESCRIPTION : |  | F830Low Flow
OF6 | 29 | U1 | 2017-11-06 11:53 |  |  |  |  | 2017-11-14 08:02 |  | 0 | 0 | 188.15 | 188.15 | 1317.05 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820High River
OF6 | 36 | U1 | 2017-11-22 10:56 |  |  |  |  | 2017-11-25 08:20 |  | 0 | 0 | 69.4 | 69.4 | 485.8 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for highwater and trash
OF6 | 38 | U1 | 2017-12-26 11:03 |  |  |  |  | 2017-12-27 11:47 |  | 0 | 0 | 24.733 | 24.7333 | 173.133 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830highwater
OF6 | 2 | U1 | 2018-01-11 07:33 |  |  |  |  | 2018-01-11 13:23 |  | 0 | 0 | 5.833 | 5.8333 | 29.167 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Trash Buildup
OF6 | 3 | U1 | 2018-01-14 04:20 |  |  |  |  | 2018-01-20 10:22 |  | 0 | 0 | 150.033 | 150.0333 | 750.166 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF6 | 4 | U1 | 2018-01-24 15:04 |  |  |  |  | 2018-01-29 14:09 |  | 0 | 0 | 119.083 | 119.0833 | 595.417 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830highwater
OF6 | 6 | U1 | 2018-02-08 23:59 |  |  |  |  | 2018-03-11 10:40 |  | 0 | 0 | 730.683 | 730.6833 | 4154.75 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830High river
OF6 | 10 | U1 | 2018-03-24 12:58 |  |  |  |  | 2018-03-27 09:06 |  | 0 | 0 | 68.133 | 68.1333 | 476.933 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830highwater
OF6 | 11 | U1 | 2018-03-28 06:20 |  |  |  |  | 2018-04-15 09:25 |  | 0 | 0 | 435.083 | 435.0833 | 3045.584 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F830Highwater
OF6 | 12 | U1 | 2018-04-17 05:45 |  |  |  |  | 2018-04-30 12:23 |  | 0 | 0 | 318.633 | 318.6333 | 2230.433 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830highwater
OF6 | 14 | U1 | 2018-05-08 14:05 |  |  |  |  | 2018-05-12 07:32 |  | 0 | 0 | 89.45 | 89.45 | 626.15 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF6 | 17 | U1 | 2018-05-21 07:06 |  |  |  |  | 2018-05-22 09:35 |  | 0 | 0 | 26.483 | 26.4833 | 185.383 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater / Trash
OF6 | 18 | U1 | 2018-05-25 06:04 |  |  |  |  | 2018-05-27 15:10 |  | 0 | 0 | 57.1 | 57.1 | 399.7 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater & Trash build-up
OF6 | 20 | U1 | 2018-06-07 08:43 |  |  |  |  | 2018-06-07 19:44 |  | 0 | 0 | 11.017 | 11.0167 | 88.133 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7190 |  |  | - |  | Dewatering and rewatering equipment | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F590Barge crane blocked unit to pick up gate rack on shore.
OF6 | 23 | U1 | 2018-06-25 07:09 |  |  |  |  | 2018-06-27 07:43 |  | 0 | 0 | 48.567 | 48.5667 | 388.533 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF6 | 25 | U1 | 2018-07-14 07:11 |  |  |  |  | 2018-07-16 07:04 |  | 0 | 0 | 47.883 | 47.8833 | 383.066 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low flow
OF6 | 26 | U1 | 2018-07-16 13:27 |  |  |  |  | 2018-07-17 12:54 |  | 0 | 0 | 23.45 | 23.45 | 187.6 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Water
OF6 | 27 | U1 | 2018-07-28 00:47 |  |  |  |  | 2018-07-28 09:06 |  | 0 | 0 | 8.317 | 8.3167 | 66.533 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 3814 |  |  | - |  | Service water system fouling | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820lower guide bearing water strainer baskets clogged.
OF6 | 28 | U1 | 2018-07-29 00:25 |  |  |  |  | 2018-07-29 09:09 |  | 0 | 0 | 8.733 | 8.7333 | 69.867 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 3814 |  |  | - |  | Service water system fouling | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Lower guide bearing strainer blocked
OF6 | 31 | U1 | 2018-08-20 08:44 |  |  |  |  | 2018-08-20 13:48 |  | 0 | 0 | 5.067 | 5.0667 | 40.533 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830trash
OF6 | 32 | U1 | 2018-08-22 12:02 |  |  |  |  | 2018-08-22 13:13 |  | 0 | 0 | 1.183 | 1.1833 | 9.467 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9720 |  |  | - |  | Other safety problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Crane safety
OF6 | 33 | U1 | 2018-08-22 13:52 |  |  |  |  | 2018-08-22 14:32 |  | 0 | 0 | 0.667 | 0.6667 | 5.333 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 3814 |  |  | - |  | Service water system fouling | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F830Strainer blocked
OF6 | 34 | U1 | 2018-09-08 13:57 |  |  |  |  | 2018-09-08 14:20 |  | 0 | 0 | 0.383 | 0.3833 | 2.683 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 3814 |  |  | - |  | Service water system fouling | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F830Strainer blocked
OF6 | 35 | U1 | 2018-09-09 08:56 |  |  |  |  | 2018-09-17 10:14 |  | 0 | 0 | 193.3 | 193.3 | 1353.1 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830highwater
OF6 | 36 | U1 | 2018-09-20 09:43 |  |  |  |  | 2018-09-24 09:49 |  | 0 | 0 | 96.1 | 96.1 | 672.7 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF6 | 37 | U1 | 2018-09-25 05:36 |  |  |  |  | 2018-10-04 08:00 |  | 0 | 0 | 218.4 | 218.4 | 1528.8 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830high water
OF6 | 38 | U1 | 2018-10-10 09:12 |  |  |  |  | 2018-10-10 17:20 |  | 0 | 0 | 8.133 | 8.1333 | 56.933 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Trash in front of facility Intakes
OF6 | 40 | U1 | 2018-11-02 00:19 |  |  |  |  | 2018-12-09 11:18 |  | 0 | 0 | 898.983 | 898.9833 | 5886.283 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Highwater
OF6 | 41 | U1 | 2018-12-17 14:33 |  |  |  |  | 2019-01-01 |  | 0 | 0 | 345.45 | 345.45 | 1727.25 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830high water
OF6 | 1 | U1 | 2019-01-01 |  |  |  |  | 2019-01-14 16:39 |  | 0 | 0 | 328.65 | 328.65 | 1643.25 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Highwater
OF6 | 2 | U1 | 2019-01-20 17:05 |  |  |  |  | 2019-01-31 23:59 |  | 0 | 0 | 270.9 | 270.9 | 1354.5 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830high water
OF6 | 3 | U1 | 2019-02-01 |  |  |  |  | 2019-02-03 10:04 |  | 0 | 0 | 58.067 | 58.0667 | 290.333 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF6 | 4 | U1 | 2019-02-07 08:04 |  |  |  |  | 2019-03-06 14:52 |  | 0 | 0 | 654.8 | 654.8 | 3543.734 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830highwater
OF6 | 5 | U1 | 2019-03-10 13:40 |  |  |  |  | 2019-03-18 12:49 |  | 0 | 0 | 191.15 | 191.15 | 1338.05 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF6 | 7 | U1 | 2019-04-12 01:43 |  |  |  |  | 2019-04-12 07:13 |  | 0 | 0 | 5.5 | 5.5 | 38.5 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7053 |  |  | - |  | Governor oil system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820GPU oil level low trip
OF6 | 9 | U1 | 2019-04-15 12:13 |  |  |  |  | 2019-04-15 14:26 |  | 0 | 0 | 2.217 | 2.2167 | 15.517 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 3710 |  |  | - |  | Transmission line (connected to powerhouse switchyard to 1st Substation) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Line 6608 Protection Relaying
OF6 | 10 | U1 | 2019-04-20 08:40 |  |  |  |  | 2019-05-03 09:54 |  | 0 | 0 | 313.233 | 313.2333 | 2192.633 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF6 | 11 | U1 | 2019-05-07 15:59 |  |  |  |  | 2019-05-10 07:10 |  | 0 | 0 | 63.183 | 63.1833 | 442.284 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Water on the headworks, highwater
OF6 | 12 | U1 | 2019-05-27 21:12 |  |  |  |  | 2019-05-28 06:24 |  | 0 | 0 | 9.2 | 9.2 | 64.4 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7008 |  |  | - |  | Bearing cooling system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820L. V. bearing strainer clogged
OF6 | 14 | U1 | 2019-06-17 15:10 |  |  |  |  | 2019-06-28 09:20 |  | 0 | 0 | 258.167 | 258.1667 | 2065.334 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820high water
OF6 | 15 | U1 | 2019-07-23 07:18 |  |  |  |  | 2019-07-23 13:58 |  | 0 | 0 | 6.667 | 6.6667 | 53.333 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830trash
OF6 | 16 | U1 | 2019-08-10 11:00 |  |  |  |  | 2019-08-14 06:57 |  | 0 | 0 | 91.95 | 91.95 | 735.6 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF6 | 17 | U1 | 2019-08-18 22:35 |  |  |  |  | 2019-08-21 10:18 |  | 0 | 0 | 59.717 | 59.7167 | 477.733 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low flow
OF6 | 18 | U1 | 2019-08-24 21:50 |  |  |  |  | 2019-08-25 07:22 |  | 0 | 0 | 9.533 | 9.5333 | 76.266 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9720 |  |  | - |  | Other safety problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830river rescue
OF6 | 19 | U1 | 2019-08-26 08:46 |  |  |  |  | 2019-08-28 06:54 |  | 0 | 0 | 46.133 | 46.1333 | 369.067 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Low Flow per ACOE request
OF6 | 20 | U1 | 2019-08-30 09:44 |  |  |  |  | 2019-08-30 10:04 |  | 0 | 0 | 0.333 | 0.3333 | 2.667 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9720 |  |  | - |  | Other safety problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Shut down for Tug/Dredging positioning
OF6 | 21 | U1 | 2019-08-30 15:34 |  |  |  |  | 2019-08-30 16:21 |  | 0 | 0 | 0.783 | 0.7833 | 6.267 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9720 |  |  | - |  | Other safety problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Reposition of tug for dredging
OF6 | 22 | U1 | 2019-09-06 10:25 |  |  |  |  | 2019-09-10 16:39 |  | 0 | 0 | 102.233 | 102.2333 | 715.633 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low flow
OF6 | 23 | U1 | 2019-09-12 08:22 |  |  |  |  | 2019-10-07 06:58 |  | 0 | 0 | 598.6 | 598.6 | 4190.2 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low river
OF6 | 24 | U1 | 2019-10-09 13:51 |  |  |  |  | 2019-10-21 12:42 |  | 0 | 0 | 286.85 | 286.85 | 2007.95 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low flow, Offline by request from ACOE
OF6 | 25 | U1 | 2019-10-22 06:01 |  |  |  |  | 2019-10-23 09:30 |  | 0 | 0 | 27.483 | 27.4833 | 192.383 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low river
OF6 | 27 | U1 | 2019-11-13 22:18 |  |  |  |  | 2019-11-14 08:04 |  | 0 | 0 | 9.767 | 9.7667 | 68.367 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 4750 |  |  | - |  | Other generator controls and metering problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Speed Box Fault
OF6 | 28 | U1 | 2019-11-21 13:40 |  |  |  |  | 2019-11-25 11:15 |  | 0 | 0 | 93.583 | 93.5833 | 655.083 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low flow
OF6 | 29 | U1 | 2019-12-03 08:44 |  |  |  |  | 2019-12-05 13:57 |  | 0 | 0 | 53.217 | 53.2167 | 266.083 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830highwater
OF6 | 30 | U1 | 2019-12-06 06:35 |  |  |  |  | 2019-12-06 13:18 |  | 0 | 0 | 6.717 | 6.7167 | 33.583 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820trash
OF6 | 31 | U1 | 2019-12-14 13:11 |  |  |  |  | 2019-12-14 13:42 |  | 0 | 0 | 0.517 | 0.5167 | 2.583 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Trash caused Trip
OF6 | 32 | U2 | 2019-12-14 14:32 |  |  |  |  | 2019-12-17 16:33 |  | 0 | 0 | 74.017 | 74.0167 | 370.083 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 7052 |  |  | - |  | "Other turbine control problems (Report specific wicket gate controls, etc., using the code for the appropriate equipment item.)" | [8 empty] | AMP CODE: |  | 66
|  | DESCRIPTION : |  | F690GPU oil pressure low trip, appears that motor and / or pump may have failed.
OF6 | 33 | U1 | 2019-12-17 16:33 |  |  |  |  | 2019-12-24 10:34 |  | 0 | 0 | 162.017 | 162.0167 | 810.083 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | FR
|  | DESCRIPTION : |  | F830highwater
OF6 | 34 | U1 | 2019-12-31 12:52 |  |  |  |  | 2019-12-31 23:59 |  | 0 | 0 | 11.117 | 11.1167 | 55.583 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Highwater
OF6 | 1 | U1 | 2020-01-01 |  |  |  |  | 2020-01-10 11:43 |  | 0 | 0 | 227.717 | 227.7167 | 1138.583 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Highwater
OF6 | 2 | U1 | 2020-01-15 14:45 |  |  |  |  | 2020-01-18 11:19 |  | 0 | 0 | 68.567 | 68.5667 | 342.833 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830High River
OF6 | 3 | U1 | 2020-01-28 15:13 |  |  |  |  | 2020-02-01 10:39 |  | 0 | 0 | 91.433 | 91.4333 | 457.167 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF6 | 4 | U1 | 2020-02-08 22:23 |  |  |  |  | 2020-02-24 13:53 |  | 0 | 0 | 375.5 | 375.5 | 1877.5 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Highwater
OF6 | 5 | U1 | 2020-03-05 21:30 |  |  |  |  | 2020-03-10 10:06 |  | 0 | 0 | 108.6 | 108.6 | 760.2 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Highwater
OF6 | 6 | U1 | 2020-03-10 22:41 |  |  |  |  | 2020-03-11 09:29 |  | 0 | 0 | 10.8 | 10.8 | 75.6 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 3824 |  |  | - |  | Closed cooling water system fouling | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820cool water pump clogged
OF6 | 7 | U1 | 2020-03-15 10:23 |  |  |  |  | 2020-04-06 09:56 |  | 0 | 0 | 527.55 | 527.55 | 3692.85 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF6 | 8 | U1 | 2020-04-08 17:50 |  |  |  |  | 2020-04-09 10:42 |  | 0 | 0 | 16.867 | 16.8667 | 118.067 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 3670 |  |  | - |  | 12-15kV transformers | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Bad P T fuse
OF6 | 9 | U1 | 2020-04-15 09:43 |  |  |  |  | 2020-04-21 13:10 |  | 0 | 0 | 147.45 | 147.45 | 1032.15 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Highwater
OF6 | 10 | U1 | 2020-04-29 10:20 |  |  |  |  | 2020-05-11 13:32 |  | 0 | 0 | 291.2 | 291.2 | 2038.4 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Highwater
OF6 | 11 | U1 | 2020-05-20 08:51 |  |  |  |  | 2020-05-29 13:45 |  | 0 | 0 | 220.9 | 220.9 | 1546.3 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF6 | 12 | U1 | 2020-06-10 09:54 |  |  |  |  | 2020-06-10 17:05 |  | 0 | 0 | 7.183 | 7.1833 | 57.467 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for trash
OF6 | 13 | U1 | 2020-06-16 12:17 |  |  |  |  | 2020-06-16 13:51 |  | 0 | 0 | 1.567 | 1.5667 | 12.533 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 3710 |  |  | - |  | Transmission line (connected to powerhouse switchyard to 1st Substation) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Transmission Outage
OF6 | 14 | U1 | 2020-06-17 09:33 |  |  |  |  | 2020-06-17 09:56 |  | 0 | 0 | 0.383 | 0.3833 | 3.067 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 3710 |  |  | - |  | Transmission line (connected to powerhouse switchyard to 1st Substation) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Transmission Outage
OF6 | 15 | U1 | 2020-06-26 06:23 |  |  |  |  | 2020-06-26 10:56 |  | 0 | 0 | 4.55 | 4.55 | 36.4 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9350 |  |  | - |  | Public Safety (water hazard or river rescue) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F590ACOE requested shutdown for safety while they are working on the lower dam.
OF6 | 16 | U1 | 2020-06-26 14:16 |  |  |  |  | 2020-06-26 15:16 |  | 0 | 0 | 1 | 1 | 8 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 4650 |  |  | - |  | Other cooling system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F120Lower Guide Bearing cooling water flow blocked by Zebra Muscles in strainer basket
OF6 | 17 | U1 | 2020-06-26 15:21 |  |  |  |  | 2020-06-26 15:35 |  | 0 | 0 | 0.233 | 0.2333 | 1.867 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7050 |  |  | - |  | Turbine governor | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F820Wicket Gate Control will not exceed 52%, during operation procedures, with Control
OF6 | 18 | U1 | 2020-06-28 01:35 |  |  |  |  | 2020-06-29 07:56 |  | 0 | 0 | 30.35 | 30.35 | 242.8 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9001 |  |  | - |  | Drought | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow, ACOE requested shutdown
OF6 | 19 | U1 | 2020-06-30 08:00 |  |  |  |  | 2020-06-30 10:25 |  | 0 | 0 | 2.417 | 2.4167 | 19.333 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9350 |  |  | - |  | Public Safety (water hazard or river rescue) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830ACOE request on lower dam
OF6 | 20 | U1 | 2020-07-04 14:49 |  |  |  |  | 2020-07-20 13:22 |  | 0 | 0 | 382.55 | 382.55 | 3060.4 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830lack of water
OF6 | 21 | U1 | 2020-07-20 13:27 |  |  |  |  | 2020-07-31 07:21 |  | 0 | 0 | 257.9 | 257.9 | 2063.2 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Low Water (ACOE Request) Alternated to another Unit for better MW Out
OF6 | 22 | U1 | 2020-07-31 07:21 |  |  |  |  | 2020-08-04 19:34 |  | 0 | 0 | 108.217 | 108.2167 | 865.733 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 3710 |  |  | - |  | Transmission line (connected to powerhouse switchyard to 1st Substation) | [8 empty] | AMP CODE: |  | X0
|  | DESCRIPTION : |  | F830trans line
OF6 | 23 | U1 | 2020-08-04 19:34 |  |  |  |  | 2020-08-17 06:45 |  | 0 | 0 | 299.183 | 299.1833 | 2393.467 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | X0
|  | DESCRIPTION : |  | F830Lack of Water (ACOE Request)
OF6 | 24 | U1 | 2020-08-20 05:53 |  |  |  |  | 2020-08-24 12:07 |  | 0 | 0 | 102.233 | 102.2333 | 817.866 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Lack of Water (ACOE)
OF6 | 25 | U1 | 2020-09-15 12:06 |  |  |  |  | 2020-09-15 14:31 |  | 0 | 0 | 2.417 | 2.4167 | 16.917 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for trash.
OF6 | 26 | U1 | 2020-09-24 17:10 |  |  |  |  | 2020-09-29 10:36 |  | 0 | 0 | 113.433 | 113.4333 | 794.033 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low river
OF6 | 27 | U1 | 2020-09-30 13:57 |  |  |  |  | 2020-10-03 08:02 |  | 0 | 0 | 66.083 | 66.0833 | 462.583 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Lack of water.
OF6 | 28 | U1 | 2020-10-16 07:23 |  |  |  |  | 2020-10-17 12:16 |  | 0 | 0 | 28.883 | 28.8833 | 202.184 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF6 | 31 | U1 | 2020-11-09 13:10 |  |  |  |  | 2020-11-11 12:52 |  | 0 | 0 | 47.7 | 47.7 | 333.9 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | X0
|  | DESCRIPTION : |  | F830Low Flow (ACOE)
OF6 | 34 | U1 | 2020-12-16 11:07 |  |  |  |  | 2020-12-16 16:26 |  | 0 | 0 | 5.317 | 5.3167 | 26.583 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9350 |  |  | - |  | Public Safety (water hazard or river rescue) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Diesel fuel in upper pool
OF6 | 35 | U1 | 2020-12-27 20:56 |  |  |  |  | 2021-01-01 |  | 0 | 0 | 99.067 | 99.0667 | 495.333 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF6 | 1 | U1 | 2021-01-01 |  |  |  |  | 2021-01-11 10:39 |  | 0 | 0 | 250.65 | 250.65 | 3158.19 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for highwater
OF6 | 2 | U1 | 2021-01-27 19:54 |  |  |  |  | 2021-02-05 10:32 |  | 0 | 0 | 206.633 | 206.6333 | 2603.58 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Offline for highwater
OF6 | 3 | U1 | 2021-02-07 12:33 |  |  |  |  | 2021-02-07 15:41 |  | 0 | 0 | 3.133 | 3.1333 | 39.48 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 4650 |  |  | - |  | Other cooling system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820L V strainer baskets
OF6 | 5 | U1 | 2021-02-24 21:08 |  |  |  |  | 2021-03-12 09:54 |  | 0 | 0 | 372.767 | 372.7667 | 4696.86 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF6 | 6 | U1 | 2021-03-20 08:26 |  |  |  |  | 2021-03-24 09:27 |  | 0 | 0 | 97.017 | 97.0167 | 1222.41 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830high water
OF6 | 7 | U1 | 2021-04-01 06:24 |  |  |  |  | 2021-04-05 12:56 |  | 0 | 0 | 102.533 | 102.5333 | 1291.92 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Highwater
OF6 | 12 | U1 | 2021-05-27 14:10 |  |  |  |  | 2021-05-28 07:14 |  | 0 | 0 | 17.067 | 17.0667 | 215.04 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | FR
|  | DESCRIPTION : |  | F830Offline for lack of water.
OF6 | 13 | U1 | 2021-06-06 15:01 |  |  |  |  | 2021-06-07 07:25 |  | 0 | 0 | 16.4 | 16.4 | 206.64 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Lack of water.
OF6 | 14 | U1 | 2021-06-15 07:56 |  |  |  |  | 2021-06-15 12:59 |  | 0 | 0 | 5.05 | 5.05 | 63.63 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for trash.
OF6 | 15 | U1 | 2021-06-20 02:45 |  |  |  |  | 2021-06-21 07:42 |  | 0 | 0 | 28.95 | 28.95 | 364.77 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for trash.
OF6 | 17 | U1 | 2021-06-27 13:26 |  |  |  |  | 2021-06-28 09:39 |  | 0 | 0 | 20.217 | 20.2167 | 254.73 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830ACOE requested, Lack of Water
OF6 | 19 | U1 | 2021-06-29 09:00 |  |  |  |  | 2021-07-01 07:35 |  | 0 | 0 | 46.583 | 46.5833 | 586.95 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | FR
|  | DESCRIPTION : |  | F830Unit offline for Lack of Water, Run of River per ACOE
OF6 | 22 | U1 | 2021-07-09 14:50 |  |  |  |  | 2021-07-13 08:54 |  | 0 | 0 | 90.067 | 90.0667 | 1134.84 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | FR
|  | DESCRIPTION : |  | F830Offline for trash.
OF6 | 23 | U1 | 2021-08-06 12:03 |  |  |  |  | 2021-08-07 07:45 |  | 0 | 0 | 19.7 | 19.7 | 248.22 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Lack of Water
OF6 | 24 | U1 | 2021-08-09 22:17 |  |  |  |  | 2021-08-11 06:52 |  | 0 | 0 | 32.583 | 32.5833 | 410.55 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Lack of Water (ACOE)
OF6 | 25 | U1 | 2021-08-12 00:56 |  |  |  |  | 2021-08-17 06:40 |  | 0 | 0 | 125.733 | 125.7333 | 1584.24 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Lack of Water (ACOE)
OF6 | 27 | U1 | 2021-09-03 10:35 |  |  |  |  | 2021-09-06 06:57 |  | 0 | 0 | 68.367 | 68.3667 | 861.42 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for High Water
OF6 | 28 | U1 | 2021-09-19 22:19 |  |  |  |  | 2021-09-21 06:47 |  | 0 | 0 | 32.467 | 32.4667 | 409.08 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Lack of Water.
OF6 | 29 | U1 | 2021-09-22 17:14 |  |  |  |  | 2021-09-24 13:45 |  | 0 | 0 | 44.517 | 44.5167 | 560.91 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Lack of Water
OF6 | 30 | U1 | 2021-10-01 01:52 |  |  |  |  | 2021-10-02 09:18 |  | 0 | 0 | 31.433 | 31.4333 | 396.06 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Lack of Water (ACOE)
OF6 | 31 | U1 | 2021-10-02 12:51 |  |  |  |  | 2021-10-04 08:47 |  | 0 | 0 | 43.933 | 43.9333 | 553.56 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Lack of Water (ACOE)
OF6 | 32 | U1 | 2021-10-12 20:45 |  |  |  |  | 2021-10-17 07:28 |  | 0 | 0 | 106.717 | 106.7167 | 1344.63 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Lack of Water (ACOE)
OF6 | 33 | U1 | 2021-10-22 14:56 |  |  |  |  | 2021-10-25 09:39 |  | 0 | 0 | 66.717 | 66.7167 | 840.63 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Lack of water.
OF6 | 34 | U1 | 2021-12-06 14:51 |  |  |  |  | 2021-12-07 14:43 |  | 0 | 0 | 23.867 | 23.8667 | 300.72 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Run of River - Trash build up at intake
OF6 | 36 | U1 | 2021-12-12 20:57 |  |  |  |  | 2021-12-15 08:15 |  | 0 | 0 | 59.3 | 59.3 | 747.18 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Run of RIver - Highwater
OF6 | 1 | U1 | 2022-01-01 18:10 |  |  |  |  | 2022-01-16 12:55 |  | 0 | 0 | 354.75 | 354.75 | 4469.85 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for High Water.
OF6 | 3 | U1 | 2022-02-02 14:47 |  |  |  |  | 2022-02-03 10:46 |  | 0 | 0 | 19.983 | 19.9833 | 251.79 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | FR
|  | DESCRIPTION : |  | F830Unit offline for Highwater, Run of River
OF6 | 4 | U1 | 2022-02-04 07:15 |  |  |  |  | 2022-02-14 15:08 |  | 0 | 0 | 247.883 | 247.8833 | 3123.33 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for High Water
OF6 | 6 | U1 | 2022-02-18 07:25 |  |  |  |  | 2022-03-21 07:08 |  | 0 | 0 | 743.717 | 743.7167 | 9370.83 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | FR
|  | DESCRIPTION : |  | F830Unit offline for High Water (Run of River)
OF6 | 10 | U1 | 2022-04-10 20:38 |  |  |  |  | 2022-04-18 07:16 |  | 0 | 0 | 178.633 | 178.6333 | 2250.78 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for High Water
OF6 | 11 | U1 | 2022-05-07 21:24 |  |  |  |  | 2022-05-16 09:14 |  | 0 | 0 | 203.833 | 203.8333 | 2568.3 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for High Water.
OF6 | 12 | U1 | 2022-05-30 20:19 |  |  |  |  | 2022-06-01 07:18 |  | 0 | 0 | 34.983 | 34.9833 | 440.79 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for high water.
OF6 | 13 | U1 | 2022-06-25 16:21 |  |  |  |  | 2022-06-28 07:39 |  | 0 | 0 | 63.3 | 63.3 | 797.58 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Lack of Water-Run of River per the ACOE
OF6 | 14 | U1 | 2022-07-01 06:17 |  |  |  |  | 2022-07-01 06:40 |  | 0 | 0 | 0.383 | 0.3833 | 4.83 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9900 |  |  | - |  | Operator error | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F420Local/Remote key turned.
OF6 | 16 | U1 | 2022-07-06 00:44 |  |  |  |  | 2022-07-06 07:09 |  | 0 | 0 | 6.417 | 6.4167 | 80.85 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7008 |  |  | - |  | Bearing cooling system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Offline for Turbine Bearing Flow.
OF6 | 17 | U1 | 2022-07-06 07:09 |  |  |  |  | 2022-07-07 06:45 |  | 0 | 0 | 23.6 | 23.6 | 297.36 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | FR
|  | DESCRIPTION : |  | F830Offline for lack of water.
OF6 | 18 | U1 | 2022-07-16 22:44 |  |  |  |  | 2022-07-17 08:35 |  | 0 | 0 | 9.85 | 9.85 | 124.11 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 3979 |  |  | - |  | Other DCS problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830There was a Company wide Internet outage, Cane Run lost connectivity with our Plan
OF6 | 20 | U1 | 2022-08-02 06:46 |  |  |  |  | 2022-08-02 13:20 |  | 0 | 0 | 6.567 | 6.5667 | 82.74 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F830Unit offline for Trash
OF6 | 21 | U1 | 2022-08-20 17:03 |  |  |  |  | 2022-08-22 12:30 |  | 0 | 0 | 43.45 | 43.45 | 547.47 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830lack of water
OF6 | 22 | U1 | 2022-08-23 10:52 |  |  |  |  | 2022-08-23 13:47 |  | 0 | 0 | 2.917 | 2.9167 | 36.75 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Trash (Run of River)
OF6 | 23 | U1 | 2022-08-28 22:15 |  |  |  |  | 2022-08-29 08:02 |  | 0 | 0 | 9.783 | 9.7833 | 123.27 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Lack of Water per The ACOE
OF6 | 24 | U1 | 2022-09-06 07:18 |  |  |  |  | 2022-09-06 08:56 |  | 0 | 0 | 1.633 | 1.6333 | 20.58 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830trash
OF6 | 25 | U1 | 2022-09-06 12:54 |  |  |  |  | 2022-09-07 06:54 |  | 0 | 0 | 18 | 18 | 226.8 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830trash
OF6 | 26 | U1 | 2022-09-13 03:30 |  |  |  |  | 2022-09-13 14:06 |  | 0 | 0 | 10.6 | 10.6 | 133.56 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Trash
OF6 | 27 | U1 | 2022-09-21 18:10 |  |  |  |  | 2022-10-01 06:28 |  | 0 | 0 | 228.3 | 228.3 | 2876.58 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Lack of Water.
OF6 | 28 | U1 | 2022-10-12 21:50 |  |  |  |  | 2022-10-14 06:44 |  | 0 | 0 | 32.9 | 32.9 | 414.54 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Lack of Water
OF6 | 29 | U1 | 2022-10-15 01:08 |  |  |  |  | 2022-10-16 06:49 |  | 0 | 0 | 29.683 | 29.6833 | 374.01 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Lack of Water
OF6 | 30 | U1 | 2022-10-17 23:56 |  |  |  |  | 2022-10-22 06:16 |  | 0 | 0 | 102.333 | 102.3333 | 1289.4 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Lack of Water
OF6 | 31 | U1 | 2022-10-23 15:12 |  |  |  |  | 2022-10-25 09:11 |  | 0 | 0 | 41.983 | 41.9833 | 528.99 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Lack of Water
OF6 | 32 | U1 | 2022-10-29 10:31 |  |  |  |  | 2022-11-01 06:36 |  | 0 | 0 | 68.083 | 68.0833 | 857.85 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Lack of Water
OF6 | 33 | U1 | 2022-11-02 08:50 |  |  |  |  | 2022-11-06 08:20 |  | 0 | 0 | 95.5 | 95.5 | 1203.3 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for lack of water.
OF6 | 34 | U1 | 2022-11-07 12:52 |  |  |  |  | 2022-11-09 07:31 |  | 0 | 0 | 42.65 | 42.65 | 537.39 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830lack of water
OF6 | 35 | U1 | 2022-11-27 00:21 |  |  |  |  | 2022-11-28 07:54 |  | 0 | 0 | 31.55 | 31.55 | 397.53 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Lack of Water
OF6 | 36 | U1 | 2022-12-11 08:19 |  |  |  |  | 2022-12-12 11:59 |  | 0 | 0 | 27.667 | 27.6667 | 348.6 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830trash
OF6 | 1 | U1 | 2023-01-03 17:59 |  |  |  |  | 2023-01-09 13:02 |  | 0 | 0 | 139.05 | 139.05 | 1752.03 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Offline for trash.
OF6 | 2 | U1 | 2023-01-14 18:12 |  |  |  |  | 2023-01-27 10:26 |  | 0 | 0 | 304.233 | 304.2333 | 3833.34 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830trash
OF6 | 3 | U1 | 2023-01-29 13:26 |  |  |  |  | 2023-01-30 07:52 |  | 0 | 0 | 18.433 | 18.4333 | 232.26 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9320 |  |  | - |  | Other miscellaneous external problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for barge recovery.
OF6 | 4 | U1 | 2023-02-03 12:11 |  |  |  |  | 2023-02-07 09:41 |  | 0 | 0 | 93.5 | 93.5 | 1178.1 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9320 |  |  | - |  | Other miscellaneous external problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830barge recovery
OF6 | 6 | U1 | 2023-02-18 04:18 |  |  |  |  | 2023-02-24 10:02 |  | 0 | 0 | 149.733 | 149.7333 | 1886.64 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for High Water
OF6 | 7 | U1 | 2023-03-03 18:57 |  |  |  |  | 2023-03-13 09:00 |  | 0 | 0 | 230.05 | 230.05 | 2898.63 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for High Water
OF6 | 8 | U1 | 2023-03-25 02:19 |  |  |  |  | 2023-04-11 06:30 |  | 0 | 0 | 412.183 | 412.1833 | 5193.51 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for High Water.
OF6 | 9 | U1 | 2023-04-11 06:30 |  |  |  |  | 2023-04-28 12:35 |  | 0 | 0 | 414.083 | 414.0833 | 5217.45 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9320 |  |  | - |  | Other miscellaneous external problems | [8 empty] | AMP CODE: |  | FR
|  | DESCRIPTION : |  | FX00Barge Recovery
OF6 | 10 | U1 | 2023-06-08 03:12 |  |  |  |  | 2023-06-13 11:49 |  | 0 | 0 | 128.617 | 128.6167 | 1620.57 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830lack of water
OF6 | 11 | U1 | 2023-06-13 14:39 |  |  |  |  | 2023-06-14 06:45 |  | 0 | 0 | 16.1 | 16.1 | 202.86 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for lack of water
OF6 | 12 | U1 | 2023-06-23 13:51 |  |  |  |  | 2023-06-26 07:29 |  | 0 | 0 | 65.633 | 65.6333 | 826.98 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline lack of water.
OF6 | 13 | U1 | 2023-06-26 07:29 |  |  |  |  | 2023-06-26 16:10 |  | 0 | 0 | 8.683 | 8.6833 | 109.41 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | FR
|  | DESCRIPTION : |  | F530MSI sonar.
OF6 | 14 | U1 | 2023-07-07 07:44 |  |  |  |  | 2023-07-07 12:40 |  | 0 | 0 | 4.933 | 4.9333 | 62.16 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Trash
OF6 | 15 | U1 | 2023-07-31 08:56 |  |  |  |  | 2023-08-07 09:50 |  | 0 | 0 | 168.9 | 168.9 | 2128.14 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline lack of water.
OF6 | 17 | U1 | 2023-08-13 08:12 |  |  |  |  | 2023-08-13 09:11 |  | 0 | 0 | 0.983 | 0.9833 | 12.39 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE:
|  | DESCRIPTION : |  | F830lack of water
OF6 | 18 | U1 | 2023-08-21 14:17 |  |  |  |  | 2023-08-23 10:08 |  | 0 | 0 | 43.85 | 43.85 | 552.51 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for lack of water.
OF6 | 19 | U1 | 2023-08-23 17:13 |  |  |  |  | 2023-08-25 07:28 |  | 0 | 0 | 38.25 | 38.25 | 481.95 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for lack of water.
OF6 | 20 | U1 | 2023-08-25 16:36 |  |  |  |  | 2023-08-26 08:15 |  | 0 | 0 | 15.65 | 15.65 | 197.19 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 4620 |  |  | - |  | Air cooling system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Offline for Cooler Temp from Tripped Cooling Water Pump.
OF6 | 21 | U1 | 2023-09-02 20:08 |  |  |  |  | 2023-09-07 09:40 |  | 0 | 0 | 109.533 | 109.5333 | 1380.12 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Lack of water
OF6 | 23 | U1 | 2023-09-23 06:24 |  |  |  |  | 2023-09-26 09:04 |  | 0 | 0 | 74.667 | 74.6667 | 940.8 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | FR
|  | DESCRIPTION : |  | F830lack of water
OF6 | 24 | U1 | 2023-09-28 16:39 |  |  |  |  | 2023-09-29 12:01 |  | 0 | 0 | 19.367 | 19.3667 | 244.02 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for lack of water
OF6 | 25 | U1 | 2023-09-30 05:26 |  |  |  |  | 2023-10-05 09:38 |  | 0 | 0 | 124.2 | 124.2 | 1564.92 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for lack of water
OF6 | 26 | U1 | 2023-10-05 23:11 |  |  |  |  | 2023-10-08 08:36 |  | 0 | 0 | 57.417 | 57.4167 | 723.45 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline lack of water.
OF6 | 27 | U1 | 2023-10-08 18:55 |  |  |  |  | 2023-10-18 07:17 |  | 0 | 0 | 228.367 | 228.3667 | 2877.42 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline lack of water.
OF6 | 28 | U1 | 2023-10-20 06:47 |  |  |  |  | 2023-10-23 08:43 |  | 0 | 0 | 73.933 | 73.9333 | 931.56 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for lack of water
OF6 | 29 | U1 | 2023-10-26 08:22 |  |  |  |  | 2023-10-31 09:00 |  | 0 | 0 | 120.633 | 120.6333 | 1519.98 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline lack of water.
OF6 | 30 | U1 | 2023-11-08 12:51 |  |  |  |  | 2023-11-10 07:23 |  | 0 | 0 | 42.533 | 42.5333 | 535.92 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830lack of water
OF6 | 31 | U1 | 2023-11-11 21:22 |  |  |  |  | 2023-11-19 09:16 |  | 0 | 0 | 179.9 | 179.9 | 2266.74 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830lack of water
OF6 | 32 | U1 | 2023-11-30 08:34 |  |  |  |  | 2023-12-04 06:30 |  | 0 | 0 | 93.933 | 93.9333 | 1183.56 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830lack of water
OF6 | 34 | U1 | 2023-12-08 13:06 |  |  |  |  | 2023-12-11 08:02 |  | 0 | 0 | 66.933 | 66.9333 | 843.36 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830lack of water
OF6 | 35 | U1 | 2023-12-20 08:03 |  |  |  |  | 2023-12-21 11:06 |  | 0 | 0 | 27.05 | 27.05 | 340.83 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 3670 |  |  | - |  | 12-15kV transformers | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830carded TR-2 for MAC construction to replace catwalk for relay room
Ohio Falls - OF7
Unit | Event | Type | Start |  |  |  |  | End |  | GAC | NAC | Duration | Equiv Hrs | Equiv MWH | Cont | Work Start | Work End |  | Hours |  |  | Gross Capacity Impact (MW)
OF7 | 2 | U1 | 2014-01-27 11:38 |  |  |  |  | 2014-01-27 12:19 |  | 0 | 0 | 0.683 | 0.6833 | 4.1 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 7008 |  |  | - |  | Bearing cooling system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Turbine Guide Bearing Strainer Basket stopped up.
OF7 | 3 | U1 | 2014-01-27 14:06 |  |  |  |  | 2014-01-28 09:49 |  | 0 | 0 | 19.717 | 19.7167 | 118.3 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 3644 |  |  | - |  | AC Protection devices | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Field Ground Protection Trip
OF7 | 4 | U1 | 2014-02-05 14:04 |  |  |  |  | 2014-02-11 10:19 |  | 0 | 0 | 140.25 | 140.25 | 701.25 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF7 | 5 | U1 | 2014-02-12 16:54 |  |  |  |  | 2014-02-13 08:53 |  | 0 | 0 | 15.983 | 15.9833 | 79.917 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 7008 |  |  | - |  | Bearing cooling system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Turbine bearing cooling h2o flow trip.
OF7 | 6 | U1 | 2014-02-20 14:15 |  |  |  |  | 2014-03-03 10:19 |  | 0 | 0 | 260.067 | 260.0667 | 1300.333 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF7 | 7 | U1 | 2014-03-07 23:34 |  |  |  |  | 2014-03-08 09:12 |  | 0 | 0 | 9.633 | 9.6333 | 48.167 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7008 |  |  | - |  | Bearing cooling system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Turbine cooling water strainer blocked with river debris.
OF7 | 8 | U1 | 2014-03-10 06:58 |  |  |  |  | 2014-03-11 08:10 |  | 0 | 0 | 25.2 | 25.2 | 126 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F820Trash isuses.
OF7 | 9 | U1 | 2014-03-15 06:59 |  |  |  |  | 2014-03-18 09:15 |  | 0 | 0 | 74.267 | 74.2667 | 371.333 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830High water.
OF7 | 10 | U1 | 2014-04-03 07:09 |  |  |  |  | 2014-04-14 14:32 |  | 0 | 0 | 271.383 | 271.3833 | 2171.067 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF7 | 11 | U1 | 2014-04-28 11:26 |  |  |  |  | 2014-04-28 12:22 |  | 0 | 0 | 0.933 | 0.9333 | 7.467 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7008 |  |  | - |  | Bearing cooling system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820L.V. screens clogged
OF7 | 12 | U1 | 2014-04-30 13:41 |  |  |  |  | 2014-05-07 09:16 |  | 0 | 0 | 163.583 | 163.5833 | 1308.666 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF7 | 13 | U1 | 2014-05-16 13:12 |  |  |  |  | 2014-05-25 07:53 |  | 0 | 0 | 210.683 | 210.6833 | 1685.467 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830highwater
OF7 | 14 | U1 | 2014-06-04 14:35 |  |  |  |  | 2014-06-04 16:57 |  | 0 | 0 | 2.367 | 2.3667 | 18.933 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830LOW RIVER
OF7 | 15 | U1 | 2014-07-13 07:21 |  |  |  |  | 2014-07-14 12:55 |  | 0 | 0 | 29.567 | 29.5667 | 236.533 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830USACE HAD US TAKE UNIT OFF FOR LOW FLOW
OF7 | 16 | U1 | 2014-07-22 13:35 |  |  |  |  | 2014-07-22 15:20 |  | 0 | 0 | 1.75 | 1.75 | 14 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9590 |  |  | - |  | Miscellaneous regulatory (this code is primarily intended for use with event contribution code 2 to indicate that a regulatory-related factor contributed to the primary cause of the event) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Ferc diver inspection
OF7 | 17 | U1 | 2014-07-24 07:50 |  |  |  |  | 2014-07-24 15:22 |  | 0 | 0 | 7.533 | 7.5333 | 60.267 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9590 |  |  | - |  | Miscellaneous regulatory (this code is primarily intended for use with event contribution code 2 to indicate that a regulatory-related factor contributed to the primary cause of the event) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830FERC divers inspection
OF7 | 18 | U1 | 2014-07-24 15:22 |  |  |  |  | 2014-07-25 09:21 |  | 0 | 0 | 17.983 | 17.9833 | 143.867 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | FR
|  | DESCRIPTION : |  | F830Low Flow
OF7 | 19 | U1 | 2014-07-26 04:10 |  |  |  |  | 2014-07-27 08:37 |  | 0 | 0 | 28.45 | 28.45 | 227.6 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | FE00Low Flow
OF7 | 20 | U1 | 2014-07-29 00:10 |  |  |  |  | 2014-07-30 06:52 |  | 0 | 0 | 30.7 | 30.7 | 245.6 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low flow
OF7 | 21 | U1 | 2014-09-01 09:35 |  |  |  |  | 2014-09-02 07:07 |  | 0 | 0 | 21.533 | 21.5333 | 172.266 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Trash
OF7 | 22 | U1 | 2014-09-24 10:17 |  |  |  |  | 2014-09-26 06:42 |  | 0 | 0 | 44.417 | 44.4167 | 355.333 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF7 | 23 | U1 | 2014-09-29 18:27 |  |  |  |  | 2014-10-01 07:37 |  | 0 | 0 | 37.167 | 37.1667 | 282.1 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF7 | 3 | U1 | 2015-03-04 11:58 |  |  |  |  | 2015-03-27 10:07 |  | 0 | 0 | 550.15 | 550.15 | 2750.75 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF7 | 4 | U1 | 2015-04-01 17:06 |  |  |  |  | 2015-04-02 07:28 |  | 0 | 0 | 14.367 | 14.3667 | 114.933 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 4620 |  |  | - |  | Air cooling system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Gen. Cooling water strainer stopped up with debris
OF7 | 5 | U1 | 2015-04-03 10:13 |  |  |  |  | 2015-04-27 13:07 |  | 0 | 0 | 578.9 | 578.9 | 4631.2 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF7 | 6 | U1 | 2015-05-04 21:51 |  |  |  |  | 2015-05-05 09:11 |  | 0 | 0 | 11.333 | 11.3333 | 90.667 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 4650 |  |  | - |  | Other cooling system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Clogged strainer to turbine brg cooling water
OF7 | 7 | U1 | 2015-05-09 20:20 |  |  |  |  | 2015-05-10 11:00 |  | 0 | 0 | 14.667 | 14.6667 | 117.333 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 4650 |  |  | - |  | Other cooling system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Turbine strainer basket and Generator cooling wtr pump stopped up.
OF7 | 9 | U1 | 2015-05-19 00:10 |  |  |  |  | 2015-05-19 07:44 |  | 0 | 0 | 7.567 | 7.5667 | 60.533 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 4650 |  |  | - |  | Other cooling system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Turbine guide cooling water strainer basket clogged
OF7 | 8 | U1 | 2015-05-19 09:17 |  |  |  |  | 2015-05-19 10:30 |  | 0 | 0 | 1.217 | 1.2167 | 9.733 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 4650 |  |  | - |  | Other cooling system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Cooling water pump clogged
OF7 | 10 | U1 | 2015-06-12 16:25 |  |  |  |  | 2015-06-13 10:50 |  | 0 | 0 | 18.417 | 18.4167 | 147.334 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF7 | 11 | U1 | 2015-06-21 05:46 |  |  |  |  | 2015-06-26 13:42 |  | 0 | 0 | 127.933 | 127.9333 | 1023.467 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830High water
OF7 | 12 | U1 | 2015-06-30 12:16 |  |  |  |  | 2015-07-07 06:52 |  | 0 | 0 | 162.6 | 162.6 | 1300.8 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF7 | 13 | U1 | 2015-07-12 08:33 |  |  |  |  | 2015-07-22 09:01 |  | 0 | 0 | 240.467 | 240.4667 | 1923.733 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF7 | 14 | U1 | 2015-07-25 09:38 |  |  |  |  | 2015-07-26 07:51 |  | 0 | 0 | 22.217 | 22.2167 | 177.733 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Trash
OF7 | 15 | U1 | 2015-07-28 03:19 |  |  |  |  | 2015-07-28 06:04 |  | 0 | 0 | 2.75 | 2.75 | 22 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 3812 |  |  | - |  | Service water valves | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Had to replace service water valve.
OF7 | 16 | U1 | 2015-07-31 16:27 |  |  |  |  | 2015-07-31 18:02 |  | 0 | 0 | 1.583 | 1.5833 | 12.667 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 4650 |  |  | - |  | Other cooling system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Turbine LV brg strainer basket stopped up.
OF7 | 17 | U1 | 2015-08-07 04:23 |  |  |  |  | 2015-08-07 05:47 |  | 0 | 0 | 1.4 | 1.4 | 11.2 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 4650 |  |  | - |  | Other cooling system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Cooling water strainer blocked
OF7 | 18 | U1 | 2015-08-09 17:10 |  |  |  |  | 2015-08-10 09:31 |  | 0 | 0 | 16.35 | 16.35 | 130.8 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 4650 |  |  | - |  | Other cooling system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Strainer blocked
OF7 | 19 | U1 | 2015-08-10 18:53 |  |  |  |  | 2015-08-11 12:22 |  | 0 | 0 | 17.483 | 17.4833 | 139.866 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low flow
OF7 | 20 | U1 | 2015-08-13 17:27 |  |  |  |  | 2015-08-14 06:49 |  | 0 | 0 | 13.367 | 13.3667 | 106.933 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low flow
OF7 | 21 | U1 | 2015-08-15 09:57 |  |  |  |  | 2015-08-16 10:00 |  | 0 | 0 | 24.05 | 24.05 | 192.4 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low flow
OF7 | 22 | U1 | 2015-08-21 12:40 |  |  |  |  | 2015-08-22 09:24 |  | 0 | 0 | 20.733 | 20.7333 | 165.867 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF7 | 23 | U1 | 2015-08-25 05:57 |  |  |  |  | 2015-08-26 07:18 |  | 0 | 0 | 25.35 | 25.35 | 202.8 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF7 | 24 | U1 | 2015-08-26 18:07 |  |  |  |  | 2015-08-28 06:52 |  | 0 | 0 | 36.75 | 36.75 | 294 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830LOW FLOW
OF7 | 25 | U1 | 2015-08-29 09:44 |  |  |  |  | 2015-08-31 07:29 |  | 0 | 0 | 45.75 | 45.75 | 366 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF7 | 26 | U1 | 2015-09-02 02:49 |  |  |  |  | 2015-09-03 13:08 |  | 0 | 0 | 34.317 | 34.3167 | 274.534 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low river
OF7 | 27 | U1 | 2015-09-07 11:01 |  |  |  |  | 2015-09-08 12:07 |  | 0 | 0 | 25.1 | 25.1 | 200.8 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low flow
OF7 | 28 | U1 | 2015-09-12 09:50 |  |  |  |  | 2015-09-14 07:40 |  | 0 | 0 | 45.833 | 45.8333 | 366.666 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low flow
OF7 | 30 | U1 | 2015-09-17 13:08 |  |  |  |  | 2015-09-30 07:05 |  | 0 | 0 | 305.95 | 305.95 | 2447.6 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF7 | 32 | U1 | 2015-10-16 07:15 |  |  |  |  | 2015-10-19 07:11 |  | 0 | 0 | 71.933 | 71.9333 | 575.467 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF7 | 33 | U1 | 2015-10-25 02:05 |  |  |  |  | 2015-10-26 14:15 |  | 0 | 0 | 36.167 | 36.1667 | 289.333 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830LOW FLOW
OF7 | 34 | U1 | 2015-11-11 12:55 |  |  |  |  | 2015-11-12 14:42 |  | 0 | 0 | 25.783 | 25.7833 | 206.267 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 3975 |  |  | - |  | DCS - upgrades | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Upgrade program to match other units.
OF7 | 35 | U1 | 2015-11-12 14:52 |  |  |  |  | 2015-11-12 15:41 |  | 0 | 0 | 0.817 | 0.8167 | 6.533 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 3975 |  |  | - |  | DCS - upgrades | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820While upgrading program to match other units, Unit tripped due to Intermediate bea
OF7 | 36 | U1 | 2015-11-16 09:07 |  |  |  |  | 2015-11-16 09:50 |  | 0 | 0 | 0.717 | 0.7167 | 5.733 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 4740 |  |  | - |  | Emergency generator trip devices | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F82086 trip accidently initiated while software was being loaded in to unit by contrat
OF7 | 38 | U1 | 2015-11-25 11:32 |  |  |  |  | 2015-11-25 12:20 |  | 0 | 0 | 0.8 | 0.8 | 6.4 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7008 |  |  | - |  | Bearing cooling system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Cool water strainer clogged.
OF7 | 39 | U1 | 2015-12-03 21:51 |  |  |  |  | 2015-12-07 14:20 |  | 0 | 0 | 88.483 | 88.4833 | 707.867 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF7 | 40 | U1 | 2015-12-11 13:35 |  |  |  |  | 2015-12-11 13:49 |  | 0 | 0 | 0.233 | 0.2333 | 1.867 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 3642 |  |  | - |  | AC Conductors and buses | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Took Unit off the "A" Bus and put it on the "B" Bus
OF7 | 41 | U1 | 2015-12-24 09:52 |  |  |  |  | 2015-12-31 23:59 |  | 0 | 0 | 182.117 | 182.1167 | 1456.934 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF7 | 1 | U1 | 2016-01-01 |  |  |  |  | 2016-01-05 11:24 |  | 0 | 0 | 107.4 | 107.4 | 537 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820highwater
OF7 | 3 | U1 | 2016-01-19 10:18 |  |  |  |  | 2016-01-19 13:51 |  | 0 | 0 | 3.55 | 3.55 | 17.75 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 4650 |  |  | - |  | Other cooling system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Turbine Guide Brg cooling water supply stopped up.
OF7 | 4 | U1 | 2016-02-03 06:46 |  |  |  |  | 2016-02-10 08:40 |  | 0 | 0 | 169.9 | 169.9 | 849.5 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Highwater
OF7 | 5 | U1 | 2016-02-18 01:13 |  |  |  |  | 2016-03-08 08:46 |  | 0 | 0 | 463.55 | 463.55 | 2671.284 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Highwater
OF7 | 6 | U1 | 2016-03-14 08:15 |  |  |  |  | 2016-03-21 07:15 |  | 0 | 0 | 167 | 167 | 1169 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830highwater
OF7 | 7 | U1 | 2016-04-15 12:06 |  |  |  |  | 2016-04-18 07:02 |  | 0 | 0 | 66.933 | 66.9333 | 468.533 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830HIGHWATER
OF7 | 8 | U1 | 2016-05-03 07:36 |  |  |  |  | 2016-05-10 07:07 |  | 0 | 0 | 167.517 | 167.5167 | 1172.617 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830HIGHWATER
OF7 | 9 | U1 | 2016-05-12 15:40 |  |  |  |  | 2016-05-16 07:10 |  | 0 | 0 | 87.5 | 87.5 | 612.5 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Highwater
OF7 | 11 | U1 | 2016-06-13 20:14 |  |  |  |  | 2016-06-14 14:26 |  | 0 | 0 | 18.2 | 18.2 | 145.6 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7050 |  |  | - |  | Turbine governor | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Governor Pressure Unit not circulating properly,too much pressure and over heating
OF7 | 12 | U1 | 2016-06-26 06:46 |  |  |  |  | 2016-06-28 07:16 |  | 0 | 0 | 48.5 | 48.5 | 388 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF7 | 13 | U1 | 2016-07-20 08:00 |  |  |  |  | 2016-07-21 06:34 |  | 0 | 0 | 22.567 | 22.5667 | 180.533 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF7 | 14 | U1 | 2016-07-22 18:00 |  |  |  |  | 2016-07-23 09:30 |  | 0 | 0 | 15.5 | 15.5 | 124 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF7 | 15 | U1 | 2016-07-24 19:29 |  |  |  |  | 2016-07-26 06:45 |  | 0 | 0 | 35.267 | 35.2667 | 282.133 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF7 | 16 | U1 | 2016-08-12 07:46 |  |  |  |  | 2016-08-14 07:35 |  | 0 | 0 | 47.817 | 47.8167 | 382.534 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830LOW FLOW
OF7 | 17 | U1 | 2016-08-14 20:03 |  |  |  |  | 2016-08-15 13:26 |  | 0 | 0 | 17.383 | 17.3833 | 139.067 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830LOW FLOW
OF7 | 18 | U1 | 2016-08-28 17:09 |  |  |  |  | 2016-08-30 06:56 |  | 0 | 0 | 37.783 | 37.7833 | 302.267 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF7 | 19 | U1 | 2016-09-03 06:54 |  |  |  |  | 2016-09-10 06:47 |  | 0 | 0 | 167.883 | 167.8833 | 1175.183 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF7 | 20 | U1 | 2016-09-15 14:54 |  |  |  |  | 2016-10-01 07:47 |  | 0 | 0 | 376.883 | 376.8833 | 2638.183 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF7 | 21 | U1 | 2016-10-06 22:25 |  |  |  |  | 2016-10-09 07:44 |  | 0 | 0 | 57.317 | 57.3167 | 401.216 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F820Low River
OF7 | 24 | U1 | 2016-10-21 10:03 |  |  |  |  | 2016-10-22 06:28 |  | 0 | 0 | 20.417 | 20.4167 | 142.917 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF7 | 25 | U1 | 2016-11-20 08:28 |  |  |  |  | 2016-11-21 07:50 |  | 0 | 0 | 23.367 | 23.3667 | 163.566 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF7 | 29 | U1 | 2016-12-15 18:44 |  |  |  |  | 2016-12-16 07:57 |  | 0 | 0 | 13.217 | 13.2167 | 66.083 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 4750 |  |  | - |  | Other generator controls and metering problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Speed Probe PT
OF7 | 32 | U1 | 2016-12-20 01:36 |  |  |  |  | 2016-12-26 08:41 |  | 0 | 0 | 151.083 | 151.0833 | 755.417 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820HIGH WATER
OF7 | 33 | U1 | 2016-12-31 08:39 |  |  |  |  | 2017-01-01 |  | 0 | 0 | 15.35 | 15.35 | 76.75 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Highwater
OF7 | 1 | U1 | 2017-01-01 |  |  |  |  | 2017-01-02 08:39 |  | 0 | 0 | 32.65 | 32.65 | 163.25 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Highwater
OF7 | 2 | U1 | 2017-01-08 06:26 |  |  |  |  | 2017-01-10 08:46 |  | 0 | 0 | 50.333 | 50.3333 | 251.666 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Highwater
OF7 | 3 | U1 | 2017-01-15 10:08 |  |  |  |  | 2017-01-31 08:48 |  | 0 | 0 | 382.667 | 382.6667 | 1913.333 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830HIGH WATER
OF7 | 5 | U1 | 2017-02-21 08:47 |  |  |  |  | 2017-02-21 10:39 |  | 0 | 0 | 1.867 | 1.8667 | 9.333 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 4650 |  |  | - |  | Other cooling system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Turbine Guide Brg cooling water strainer stopped up
OF7 | 6 | U1 | 2017-03-01 19:42 |  |  |  |  | 2017-03-09 10:52 |  | 0 | 0 | 183.167 | 183.1667 | 1282.167 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF7 | 7 | U1 | 2017-03-11 18:32 |  |  |  |  | 2017-03-14 07:28 |  | 0 | 0 | 60.933 | 60.9333 | 426.534 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F830Off for high water
OF7 | 8 | U1 | 2017-04-01 00:29 |  |  |  |  | 2017-04-13 15:13 |  | 0 | 0 | 302.733 | 302.7333 | 2119.134 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820highwater
OF7 | 9 | U1 | 2017-04-29 05:24 |  |  |  |  | 2017-05-18 06:56 |  | 0 | 0 | 457.533 | 457.5333 | 3202.733 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820HIGH WATER
OF7 | 10 | U1 | 2017-05-26 03:47 |  |  |  |  | 2017-06-01 06:28 |  | 0 | 0 | 146.683 | 146.6833 | 1033.25 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Highwater
OF7 | 11 | U1 | 2017-06-01 06:28 |  |  |  |  | 2017-06-14 07:20 |  | 0 | 0 | 312.867 | 312.8667 | 2502.934 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7141 |  |  | - |  | Wicket gate operating mechanism or positioner | [8 empty] | AMP CODE: |  | NF
|  | DESCRIPTION : |  | F820Links broke in pit
OF7 | 12 | U1 | 2017-06-14 07:20 |  |  |  |  | 2017-06-15 09:56 |  | 0 | 0 | 26.6 | 26.6 | 212.8 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | FR
|  | DESCRIPTION : |  | F830Low River
OF7 | 13 | U1 | 2017-06-25 00:18 |  |  |  |  | 2017-06-29 13:39 |  | 0 | 0 | 109.35 | 109.35 | 874.8 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Highwater
OF7 | 19 | U1 | 2017-08-15 12:43 |  |  |  |  | 2017-08-17 09:22 |  | 0 | 0 | 44.65 | 44.65 | 357.2 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF7 | 20 | U1 | 2017-09-03 10:31 |  |  |  |  | 2017-10-12 07:54 |  | 0 | 0 | 933.383 | 933.3833 | 6533.683 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF7 | 5 | U1 | 2018-11-27 14:56 |  |  |  |  | 2018-12-09 09:00 |  | 0 | 0 | 282.067 | 282.0667 | 1572.467 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF7 | 6 | U1 | 2018-12-12 14:54 |  |  |  |  | 2018-12-12 15:34 |  | 0 | 0 | 0.667 | 0.6667 | 3.333 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 3814 |  |  | - |  | Service water system fouling | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Strainer basket to L. V. bearing clogged
OF7 | 7 | U1 | 2018-12-17 14:35 |  |  |  |  | 2019-01-01 |  | 0 | 0 | 345.417 | 345.4167 | 1727.083 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830highwater
OF7 | 1 | U1 | 2019-01-01 |  |  |  |  | 2019-01-14 15:53 |  | 0 | 0 | 327.883 | 327.8833 | 1639.417 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Highwater
OF7 | 2 | U1 | 2019-01-20 17:20 |  |  |  |  | 2019-01-31 23:59 |  | 0 | 0 | 270.65 | 270.65 | 1353.25 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830high water
OF7 | 3 | U1 | 2019-02-01 |  |  |  |  | 2019-02-03 12:14 |  | 0 | 0 | 60.233 | 60.2333 | 301.167 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF7 | 4 | U1 | 2019-02-07 08:10 |  |  |  |  | 2019-03-06 10:56 |  | 0 | 0 | 650.767 | 650.7667 | 3515.7 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830highwater
OF7 | 5 | U1 | 2019-03-10 14:12 |  |  |  |  | 2019-03-18 12:15 |  | 0 | 0 | 190.05 | 190.05 | 1330.35 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF7 | 7 | U1 | 2019-03-30 14:29 |  |  |  |  | 2019-03-30 15:32 |  | 0 | 0 | 1.05 | 1.05 | 7.35 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7008 |  |  | - |  | Bearing cooling system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Low Water flow
OF7 | 8 | U1 | 2019-03-31 01:42 |  |  |  |  | 2019-03-31 06:36 |  | 0 | 0 | 4.9 | 4.9 | 34.3 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7008 |  |  | - |  | Bearing cooling system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Low water flow
OF7 | 9 | U1 | 2019-04-12 10:59 |  |  |  |  | 2019-04-12 14:35 |  | 0 | 0 | 3.6 | 3.6 | 25.2 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830trash
OF7 | 10 | U1 | 2019-04-15 12:18 |  |  |  |  | 2019-04-15 14:07 |  | 0 | 0 | 1.817 | 1.8167 | 12.717 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 3710 |  |  | - |  | Transmission line (connected to powerhouse switchyard to 1st Substation) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Line 6608 Protection Relaying loss
OF7 | 11 | U1 | 2019-04-20 08:45 |  |  |  |  | 2019-05-03 09:19 |  | 0 | 0 | 312.567 | 312.5667 | 2187.967 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830highwater
OF7 | 12 | U1 | 2019-05-07 15:57 |  |  |  |  | 2019-05-10 06:48 |  | 0 | 0 | 62.85 | 62.85 | 439.95 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Water on the headworks, highwater
OF7 | 13 | U1 | 2019-06-17 15:19 |  |  |  |  | 2019-06-28 08:00 |  | 0 | 0 | 256.683 | 256.6833 | 2053.467 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830high water
OF7 | 14 | U1 | 2019-07-23 07:27 |  |  |  |  | 2019-07-23 13:36 |  | 0 | 0 | 6.15 | 6.15 | 49.2 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830trash
OF7 | 15 | U1 | 2019-08-07 02:21 |  |  |  |  | 2019-08-08 07:28 |  | 0 | 0 | 29.117 | 29.1167 | 232.933 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF7 | 16 | U1 | 2019-08-20 06:17 |  |  |  |  | 2019-08-21 09:44 |  | 0 | 0 | 27.45 | 27.45 | 219.6 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF7 | 17 | U1 | 2019-08-24 21:52 |  |  |  |  | 2019-08-25 07:04 |  | 0 | 0 | 9.2 | 9.2 | 73.6 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9720 |  |  | - |  | Other safety problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830river rescue
OF7 | 18 | U1 | 2019-08-26 14:09 |  |  |  |  | 2019-08-27 14:42 |  | 0 | 0 | 24.55 | 24.55 | 196.4 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Low Flow per ACOE Request
OF7 | 19 | U1 | 2019-09-06 14:43 |  |  |  |  | 2019-09-07 14:38 |  | 0 | 0 | 23.917 | 23.9167 | 167.416 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low flow
OF7 | 20 | U1 | 2019-09-09 13:27 |  |  |  |  | 2019-09-10 16:31 |  | 0 | 0 | 27.067 | 27.0667 | 189.467 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low river
OF7 | 21 | U1 | 2019-09-11 21:58 |  |  |  |  | 2019-09-16 06:52 |  | 0 | 0 | 104.9 | 104.9 | 734.3 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low river
OF7 | 22 | U1 | 2019-09-18 02:26 |  |  |  |  | 2019-09-19 13:33 |  | 0 | 0 | 35.117 | 35.1167 | 245.817 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830ACOE requested shutdown for low flow
OF7 | 23 | U1 | 2019-09-20 06:34 |  |  |  |  | 2019-10-01 14:17 |  | 0 | 0 | 271.717 | 271.7167 | 1902.016 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline per ACOE Request Low FLow, switched to unit 4
OF7 | 24 | U1 | 2019-10-02 15:55 |  |  |  |  | 2019-10-07 07:15 |  | 0 | 0 | 111.333 | 111.3333 | 779.333 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low river
OF7 | 25 | U1 | 2019-10-09 19:45 |  |  |  |  | 2019-10-14 07:40 |  | 0 | 0 | 107.917 | 107.9167 | 755.417 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low flow, Offline by request from ACOE
OF7 | 26 | U1 | 2019-10-15 00:34 |  |  |  |  | 2019-10-17 07:11 |  | 0 | 0 | 54.617 | 54.6167 | 382.316 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low flow
OF7 | 27 | U1 | 2019-10-22 11:57 |  |  |  |  | 2019-10-23 08:06 |  | 0 | 0 | 20.15 | 20.15 | 141.05 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low river
OF7 | 29 | U1 | 2019-11-18 14:19 |  |  |  |  | 2019-11-25 08:49 |  | 0 | 0 | 162.5 | 162.5 | 1137.5 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF7 | 30 | U1 | 2019-12-03 08:41 |  |  |  |  | 2019-12-05 11:22 |  | 0 | 0 | 50.683 | 50.6833 | 253.416 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830highwater
OF7 | 31 | U1 | 2019-12-14 13:18 |  |  |  |  | 2019-12-24 10:14 |  | 0 | 0 | 236.933 | 236.9333 | 1184.667 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830highwater
OF7 | 32 | U1 | 2019-12-31 12:50 |  |  |  |  | 2019-12-31 23:59 |  | 0 | 0 | 11.15 | 11.15 | 55.75 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Highwater
OF7 | 1 | U1 | 2020-01-01 |  |  |  |  | 2020-01-10 10:09 |  | 0 | 0 | 226.15 | 226.15 | 1130.75 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Highwater
OF7 | 2 | U1 | 2020-01-16 08:30 |  |  |  |  | 2020-01-18 10:09 |  | 0 | 0 | 49.65 | 49.65 | 248.25 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830High River
OF7 | 3 | U1 | 2020-01-29 07:41 |  |  |  |  | 2020-02-01 10:21 |  | 0 | 0 | 74.667 | 74.6667 | 373.333 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830High River
OF7 | 4 | U1 | 2020-02-09 08:42 |  |  |  |  | 2020-02-24 13:34 |  | 0 | 0 | 364.867 | 364.8667 | 1824.333 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Highwater
OF7 | 5 | U1 | 2020-03-06 06:48 |  |  |  |  | 2020-03-10 09:24 |  | 0 | 0 | 98.6 | 98.6 | 690.2 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Highwater
OF7 | 6 | U1 | 2020-03-15 10:31 |  |  |  |  | 2020-04-06 09:02 |  | 0 | 0 | 526.517 | 526.5167 | 3685.616 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF7 | 7 | U1 | 2020-04-07 05:57 |  |  |  |  | 2020-04-07 10:28 |  | 0 | 0 | 4.517 | 4.5167 | 31.617 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 3824 |  |  | - |  | Closed cooling water system fouling | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Cool water pump clogged. Temp got hot tripped gen.
OF7 | 8 | U1 | 2020-04-08 17:50 |  |  |  |  | 2020-04-09 10:21 |  | 0 | 0 | 16.517 | 16.5167 | 115.617 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 3670 |  |  | - |  | 12-15kV transformers | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Bad P T fuse
OF7 | 9 | U1 | 2020-04-16 05:51 |  |  |  |  | 2020-04-21 09:12 |  | 0 | 0 | 123.35 | 123.35 | 863.45 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Highwater
OF7 | 10 | U1 | 2020-04-29 10:23 |  |  |  |  | 2020-05-11 13:11 |  | 0 | 0 | 290.8 | 290.8 | 2035.6 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Highwater
OF7 | 11 | U1 | 2020-05-20 08:56 |  |  |  |  | 2020-05-29 13:06 |  | 0 | 0 | 220.167 | 220.1667 | 1541.167 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF7 | 12 | U1 | 2020-06-10 10:00 |  |  |  |  | 2020-06-10 16:42 |  | 0 | 0 | 6.7 | 6.7 | 53.6 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for trash
OF7 | 13 | U1 | 2020-06-16 12:21 |  |  |  |  | 2020-06-16 13:40 |  | 0 | 0 | 1.317 | 1.3167 | 10.533 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 3710 |  |  | - |  | Transmission line (connected to powerhouse switchyard to 1st Substation) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Transmission Outage
OF7 | 14 | U1 | 2020-06-17 10:03 |  |  |  |  | 2020-06-17 10:28 |  | 0 | 0 | 0.417 | 0.4167 | 3.333 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 3710 |  |  | - |  | Transmission line (connected to powerhouse switchyard to 1st Substation) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Transmission Outage
OF7 | 15 | U1 | 2020-06-26 06:26 |  |  |  |  | 2020-06-26 12:00 |  | 0 | 0 | 5.567 | 5.5667 | 44.533 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9350 |  |  | - |  | Public Safety (water hazard or river rescue) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F590ACOE requested shutdown for safety while they are working on the lower dam.
OF7 | 16 | U1 | 2020-06-30 08:07 |  |  |  |  | 2020-06-30 10:15 |  | 0 | 0 | 2.133 | 2.1333 | 17.067 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9350 |  |  | - |  | Public Safety (water hazard or river rescue) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830ACOE request on lower dam
OF7 | 17 | U1 | 2020-07-09 07:34 |  |  |  |  | 2020-07-10 06:30 |  | 0 | 0 | 22.933 | 22.9333 | 183.467 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Lack of Water (ACOE Offline request)
OF7 | 18 | U1 | 2020-07-16 13:47 |  |  |  |  | 2020-07-17 14:14 |  | 0 | 0 | 24.45 | 24.45 | 195.6 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF7 | 19 | U1 | 2020-07-19 11:54 |  |  |  |  | 2020-07-20 07:08 |  | 0 | 0 | 19.233 | 19.2333 | 153.867 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830ACOE Requested Lack of Water
OF7 | 20 | U1 | 2020-07-21 12:05 |  |  |  |  | 2020-07-22 06:09 |  | 0 | 0 | 18.067 | 18.0667 | 144.533 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for low flow.
OF7 | 21 | U1 | 2020-07-29 16:47 |  |  |  |  | 2020-07-31 06:55 |  | 0 | 0 | 38.133 | 38.1333 | 305.066 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830lack of water ACOE
OF7 | 22 | U1 | 2020-08-04 07:16 |  |  |  |  | 2020-08-04 09:18 |  | 0 | 0 | 2.033 | 2.0333 | 16.267 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Trash
OF7 | 23 | U1 | 2020-08-11 08:35 |  |  |  |  | 2020-08-16 10:26 |  | 0 | 0 | 121.85 | 121.85 | 974.8 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF7 | 24 | U1 | 2020-08-24 11:55 |  |  |  |  | 2020-08-29 08:30 |  | 0 | 0 | 116.583 | 116.5833 | 932.667 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF7 | 25 | U1 | 2020-09-15 12:07 |  |  |  |  | 2020-09-15 14:16 |  | 0 | 0 | 2.15 | 2.15 | 15.05 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for trash.
OF7 | 26 | U1 | 2020-09-18 22:43 |  |  |  |  | 2020-09-29 06:51 |  | 0 | 0 | 248.133 | 248.1333 | 1736.933 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Run of river.
OF7 | 27 | U1 | 2020-09-30 15:58 |  |  |  |  | 2020-10-03 07:53 |  | 0 | 0 | 63.917 | 63.9167 | 447.416 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F820Lack of water.
OF7 | 28 | U1 | 2020-10-04 19:22 |  |  |  |  | 2020-10-13 09:31 |  | 0 | 0 | 206.15 | 206.15 | 1443.05 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Lack of water.
OF7 | 29 | U1 | 2020-10-16 09:09 |  |  |  |  | 2020-10-17 11:18 |  | 0 | 0 | 26.15 | 26.15 | 183.05 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF7 | 30 | U1 | 2020-10-24 21:49 |  |  |  |  | 2020-10-26 07:08 |  | 0 | 0 | 33.317 | 33.3167 | 233.216 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low flow
OF7 | 33 | U1 | 2020-12-27 20:33 |  |  |  |  | 2021-01-01 |  | 0 | 0 | 99.45 | 99.45 | 497.25 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF7 | 1 | U1 | 2021-01-01 |  |  |  |  | 2021-01-11 10:25 |  | 0 | 0 | 250.417 | 250.4167 | 3155.25 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for highwater
OF7 | 2 | U1 | 2021-01-11 21:47 |  |  |  |  | 2021-01-12 09:44 |  | 0 | 0 | 11.95 | 11.95 | 150.57 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 4650 |  |  | - |  | Other cooling system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820L. V. bearing water strainer basket clogged
OF7 | 4 | U1 | 2021-02-04 07:23 |  |  |  |  | 2021-02-05 10:24 |  | 0 | 0 | 27.017 | 27.0167 | 340.41 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | FR
|  | DESCRIPTION : |  | F830HIGHWATER
OF7 | 5 | U1 | 2021-02-07 13:26 |  |  |  |  | 2021-02-07 15:29 |  | 0 | 0 | 2.05 | 2.05 | 25.83 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 4650 |  |  | - |  | Other cooling system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820L V strainer baskets
OF7 | 7 | U1 | 2021-02-24 21:08 |  |  |  |  | 2021-03-12 10:28 |  | 0 | 0 | 373.333 | 373.3333 | 4704 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF7 | 8 | U1 | 2021-03-20 08:07 |  |  |  |  | 2021-03-24 07:18 |  | 0 | 0 | 95.183 | 95.1833 | 1199.31 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830high water
OF7 | 9 | U1 | 2021-04-01 06:26 |  |  |  |  | 2021-04-05 08:23 |  | 0 | 0 | 97.95 | 97.95 | 1234.17 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Highwater
OF7 | 15 | U1 | 2021-05-27 14:10 |  |  |  |  | 2021-06-01 07:31 |  | 0 | 0 | 113.35 | 113.35 | 1428.21 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | FR
|  | DESCRIPTION : |  | F830Offline for lack of water.
OF7 | 16 | U1 | 2021-06-15 07:57 |  |  |  |  | 2021-06-15 12:49 |  | 0 | 0 | 4.867 | 4.8667 | 61.32 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for trash.
OF7 | 17 | U1 | 2021-06-19 23:37 |  |  |  |  | 2021-06-21 07:35 |  | 0 | 0 | 31.967 | 31.9667 | 402.78 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Offline for trash.
OF7 | 18 | U1 | 2021-06-29 17:07 |  |  |  |  | 2021-06-30 13:51 |  | 0 | 0 | 20.733 | 20.7333 | 261.24 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit taken offline due to Lack of Water per ACOE
OF7 | 20 | U1 | 2021-07-09 14:50 |  |  |  |  | 2021-07-13 09:02 |  | 0 | 0 | 90.2 | 90.2 | 1136.52 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | FR
|  | DESCRIPTION : |  | F830Offline for trash.
OF7 | 21 | U1 | 2021-08-06 09:52 |  |  |  |  | 2021-08-07 07:52 |  | 0 | 0 | 22 | 22 | 277.2 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Lack of Water
OF7 | 22 | U1 | 2021-08-10 06:30 |  |  |  |  | 2021-08-11 06:44 |  | 0 | 0 | 24.233 | 24.2333 | 305.34 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Lack of Water (ACOE)
OF7 | 23 | U1 | 2021-08-12 02:54 |  |  |  |  | 2021-08-13 06:46 |  | 0 | 0 | 27.867 | 27.8667 | 351.12 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Lack of Water (ACOE)
OF7 | 25 | U1 | 2021-09-03 01:24 |  |  |  |  | 2021-09-06 06:51 |  | 0 | 0 | 77.45 | 77.45 | 975.87 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830offline for High Water
OF7 | 27 | U1 | 2021-09-30 22:24 |  |  |  |  | 2021-10-04 08:40 |  | 0 | 0 | 82.267 | 82.2667 | 1036.56 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Lack of Water (ACOE)
OF7 | 28 | U1 | 2021-10-12 17:17 |  |  |  |  | 2021-10-14 07:12 |  | 0 | 0 | 37.917 | 37.9167 | 477.75 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Lack of Water (ACOE)
OF7 | 29 | U1 | 2021-10-21 19:52 |  |  |  |  | 2021-10-25 09:44 |  | 0 | 0 | 85.867 | 85.8667 | 1081.92 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Lack of water.
OF7 | 30 | U1 | 2021-12-07 07:43 |  |  |  |  | 2021-12-07 14:18 |  | 0 | 0 | 6.583 | 6.5833 | 82.95 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Run of River - Trash build up at intake
OF7 | 31 | U1 | 2021-12-09 07:04 |  |  |  |  | 2021-12-10 07:50 |  | 0 | 0 | 24.767 | 24.7667 | 312.06 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Run of River - Highwater
OF7 | 32 | U1 | 2021-12-10 07:50 |  |  |  |  | 2021-12-10 15:02 |  | 0 | 0 | 7.2 | 7.2 | 90.72 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 7003 |  |  | - |  | Lube oil system (use code 7007 to report bearing failures due to lube oil problems) | [8 empty] | AMP CODE: |  | 56
|  | DESCRIPTION : |  | F560Bearing Lube Oil System Overflow
OF7 | 33 | U1 | 2021-12-13 04:18 |  |  |  |  | 2021-12-15 09:06 |  | 0 | 0 | 52.8 | 52.8 | 665.28 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Run of River - Highwater
OF7 | 35 | U1 | 2021-12-22 14:45 |  |  |  |  | 2021-12-22 15:17 |  | 0 | 0 | 0.533 | 0.5333 | 6.72 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 7053 |  |  | - |  | Governor oil system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Gov Oil Pressure Bad
OF7 | 36 | U1 | 2021-12-23 04:05 |  |  |  |  | 2021-12-23 11:07 |  | 0 | 0 | 7.033 | 7.0333 | 88.62 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 7053 |  |  | - |  | Governor oil system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Gov Oil Pressure Bad.
OF7 | 37 | U1 | 2021-12-23 15:58 |  |  |  |  | 2021-12-30 14:19 |  | 0 | 0 | 166.35 | 166.35 | 2096.01 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 7053 |  |  | - |  | Governor oil system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Gov Oil Pressure Bad.
OF7 | 1 | U1 | 2022-01-01 18:54 |  |  |  |  | 2022-01-16 13:58 |  | 0 | 0 | 355.067 | 355.0667 | 4473.84 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for High Water.
OF7 | 2 | U1 | 2022-01-16 14:03 |  |  |  |  | 2022-01-16 14:11 |  | 0 | 0 | 0.133 | 0.1333 | 1.68 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 7053 |  |  | - |  | Governor oil system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Gov Oil Pressure
OF7 | 3 | U1 | 2022-01-16 21:46 |  |  |  |  | 2022-01-17 08:11 |  | 0 | 0 | 10.417 | 10.4167 | 131.25 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 7053 |  |  | - |  | Governor oil system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Gov Oil Pressure
OF7 | 4 | U1 | 2022-01-18 01:08 |  |  |  |  | 2022-01-18 08:24 |  | 0 | 0 | 7.267 | 7.2667 | 91.56 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 7053 |  |  | - |  | Governor oil system | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Governor Oil Pressure Bad Quality, GPU Trip
OF7 | 6 | U1 | 2022-02-04 10:31 |  |  |  |  | 2022-02-14 15:08 |  | 0 | 0 | 244.617 | 244.6167 | 3082.17 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for High Water
OF7 | 8 | U1 | 2022-02-18 07:25 |  |  |  |  | 2022-03-21 07:08 |  | 0 | 0 | 743.717 | 743.7167 | 9370.83 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | FR
|  | DESCRIPTION : |  | F830Unit offline for High Water (Run of River)
OF7 | 12 | U1 | 2022-04-15 01:57 |  |  |  |  | 2022-04-18 07:10 |  | 0 | 0 | 77.217 | 77.2167 | 972.93 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Unit offline for High Water.
OF7 | 14 | U1 | 2022-05-08 17:02 |  |  |  |  | 2022-05-16 09:00 |  | 0 | 0 | 183.967 | 183.9667 | 2317.98 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for High Water.
OF7 | 15 | U1 | 2022-05-31 07:09 |  |  |  |  | 2022-06-01 07:01 |  | 0 | 0 | 23.867 | 23.8667 | 300.72 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for trash.
OF7 | 16 | U1 | 2022-06-30 13:16 |  |  |  |  | 2022-07-05 12:16 |  | 0 | 0 | 119 | 119 | 1499.4 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for lack of water.
OF7 | 17 | U1 | 2022-07-16 22:48 |  |  |  |  | 2022-07-17 08:28 |  | 0 | 0 | 9.667 | 9.6667 | 121.8 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 3979 |  |  | - |  | Other DCS problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830There was a Company wide Internet outage, Cane Run lost connectivity with our Plan
OF7 | 19 | U1 | 2022-08-02 06:45 |  |  |  |  | 2022-08-02 13:14 |  | 0 | 0 | 6.483 | 6.4833 | 81.69 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Trash
OF7 | 20 | U1 | 2022-08-23 10:35 |  |  |  |  | 2022-08-23 13:37 |  | 0 | 0 | 3.033 | 3.0333 | 38.22 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Trash (Run of River)
OF7 | 21 | U1 | 2022-09-06 07:20 |  |  |  |  | 2022-09-06 08:51 |  | 0 | 0 | 1.517 | 1.5167 | 19.11 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830trash
OF7 | 22 | U1 | 2022-09-06 12:56 |  |  |  |  | 2022-09-07 06:43 |  | 0 | 0 | 17.783 | 17.7833 | 224.07 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820trash
OF7 | 23 | U1 | 2022-09-12 02:02 |  |  |  |  | 2022-09-13 13:21 |  | 0 | 0 | 35.317 | 35.3167 | 444.99 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Lack of Water per The ACOE
OF7 | 24 | U1 | 2022-09-25 07:31 |  |  |  |  | 2022-09-28 06:54 |  | 0 | 0 | 71.383 | 71.3833 | 899.43 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for low water.
OF7 | 25 | U1 | 2022-09-28 18:32 |  |  |  |  | 2022-10-01 06:22 |  | 0 | 0 | 59.833 | 59.8333 | 753.9 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830lack of water
OF7 | 26 | U1 | 2022-10-07 04:57 |  |  |  |  | 2022-11-01 06:33 |  | 0 | 0 | 601.6 | 601.6 | 7580.16 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Lack of Water.
OF7 | 27 | U1 | 2022-11-07 20:08 |  |  |  |  | 2022-11-09 07:27 |  | 0 | 0 | 35.317 | 35.3167 | 444.99 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Lack of Water
OF7 | 28 | U1 | 2022-12-11 08:22 |  |  |  |  | 2022-12-12 09:46 |  | 0 | 0 | 25.4 | 25.4 | 320.04 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830trash
OF7 | 1 | U1 | 2023-01-03 19:01 |  |  |  |  | 2023-01-09 15:07 |  | 0 | 0 | 140.1 | 140.1 | 1765.26 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for trash.
OF7 | 2 | U1 | 2023-01-14 23:02 |  |  |  |  | 2023-01-27 10:19 |  | 0 | 0 | 299.283 | 299.2833 | 3770.97 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830trash
OF7 | 3 | U1 | 2023-01-29 13:27 |  |  |  |  | 2023-01-30 08:34 |  | 0 | 0 | 19.117 | 19.1167 | 240.87 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9320 |  |  | - |  | Other miscellaneous external problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for barge recovery.
OF7 | 4 | U1 | 2023-02-03 12:12 |  |  |  |  | 2023-02-07 09:06 |  | 0 | 0 | 92.9 | 92.9 | 1170.54 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9320 |  |  | - |  | Other miscellaneous external problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830barge recovery
OF7 | 6 | U1 | 2023-02-18 04:17 |  |  |  |  | 2023-02-24 08:32 |  | 0 | 0 | 148.25 | 148.25 | 1867.95 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for High Water
OF7 | 7 | U1 | 2023-03-03 19:55 |  |  |  |  | 2023-03-13 07:59 |  | 0 | 0 | 228.067 | 228.0667 | 2873.64 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for High Water
OF7 | 8 | U1 | 2023-03-25 02:15 |  |  |  |  | 2023-04-11 06:30 |  | 0 | 0 | 412.25 | 412.25 | 5194.35 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for High Water.
OF7 | 9 | U1 | 2023-04-11 06:30 |  |  |  |  | 2023-04-28 12:14 |  | 0 | 0 | 413.733 | 413.7333 | 5213.04 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9320 |  |  | - |  | Other miscellaneous external problems | [8 empty] | AMP CODE: |  | FR
|  | DESCRIPTION : |  | FX00Barge Recovery
OF7 | 10 | U1 | 2023-06-07 08:54 |  |  |  |  | 2023-06-13 08:50 |  | 0 | 0 | 143.933 | 143.9333 | 1813.56 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830lack of water
OF7 | 11 | U1 | 2023-06-26 07:28 |  |  |  |  | 2023-06-26 16:02 |  | 0 | 0 | 8.567 | 8.5667 | 107.94 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for MSI sonar.
OF7 | 12 | U1 | 2023-07-07 07:43 |  |  |  |  | 2023-07-07 12:30 |  | 0 | 0 | 4.783 | 4.7833 | 60.27 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Trash
OF7 | 13 | U1 | 2023-07-26 15:00 |  |  |  |  | 2023-07-29 07:33 |  | 0 | 0 | 64.55 | 64.55 | 813.33 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Lack of Water
OF7 | 15 | U1 | 2023-08-05 09:30 |  |  |  |  | 2023-08-07 09:50 |  | 0 | 0 | 48.333 | 48.3333 | 609 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline lack of water.
OF7 | 17 | U1 | 2023-08-13 08:12 |  |  |  |  | 2023-08-13 09:19 |  | 0 | 0 | 1.117 | 1.1167 | 14.07 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE:
|  | DESCRIPTION : |  | F830lack of water
OF7 | 18 | U1 | 2023-08-21 15:07 |  |  |  |  | 2023-08-23 07:56 |  | 0 | 0 | 40.817 | 40.8167 | 514.29 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for lack of water.
OF7 | 19 | U1 | 2023-09-05 06:33 |  |  |  |  | 2023-09-09 05:30 |  | 0 | 0 | 94.95 | 94.95 | 1196.37 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830lack of water
OF7 | 21 | U1 | 2023-09-23 06:24 |  |  |  |  | 2023-10-02 07:35 |  | 0 | 0 | 217.183 | 217.1833 | 2736.51 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | FR
|  | DESCRIPTION : |  | F830lack of water
OF7 | 22 | U1 | 2023-10-02 18:05 |  |  |  |  | 2023-10-08 07:48 |  | 0 | 0 | 133.717 | 133.7167 | 1684.83 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline lack of water.
OF7 | 23 | U1 | 2023-10-08 20:56 |  |  |  |  | 2023-10-10 06:54 |  | 0 | 0 | 33.967 | 33.9667 | 427.98 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline lack of water.
OF7 | 24 | U1 | 2023-10-10 22:25 |  |  |  |  | 2023-10-17 13:45 |  | 0 | 0 | 159.333 | 159.3333 | 2007.6 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830lack of water
OF7 | 25 | U1 | 2023-10-20 11:30 |  |  |  |  | 2023-10-23 07:07 |  | 0 | 0 | 67.617 | 67.6167 | 851.97 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for lack of water
OF7 | 26 | U1 | 2023-10-26 11:22 |  |  |  |  | 2023-10-31 06:23 |  | 0 | 0 | 115.017 | 115.0167 | 1449.21 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline lack of water.
OF7 | 27 | U1 | 2023-11-15 13:20 |  |  |  |  | 2023-11-19 09:11 |  | 0 | 0 | 91.85 | 91.85 | 1157.31 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Lack of Water
OF7 | 28 | U1 | 2023-12-17 22:18 |  |  |  |  | 2023-12-20 08:01 |  | 0 | 0 | 57.717 | 57.7167 | 727.23 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Lack of Water
OF7 | 29 | U1 | 2023-12-20 08:01 |  |  |  |  | 2023-12-21 11:02 |  | 0 | 0 | 27.017 | 27.0167 | 340.41 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 3670 |  |  | - |  | 12-15kV transformers | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830carded TR-2 for MAC construction to replace catwalk for relay room
OF7 | 30 | U1 | 2023-12-21 11:02 |  |  |  |  | 2023-12-21 12:46 |  | 0 | 0 | 1.733 | 1.7333 | 21.84 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830lack of water
OF7 | 31 | U1 | 2023-12-26 15:58 |  |  |  |  | 2023-12-28 08:15 |  | 0 | 0 | 40.283 | 40.2833 | 507.57 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for lack of water
Ohio Falls - OF8
Unit | Event | Type | Start |  |  |  |  | End |  | GAC | NAC | Duration | Equiv Hrs | Equiv MWH | Cont | Work Start | Work End |  | Hours |  |  | Gross Capacity Impact (MW)
OF8 | 2 | U1 | 2014-02-05 09:52 |  |  |  |  | 2014-02-11 11:00 |  | 0 | 0 | 145.133 | 145.1333 | 580.533 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF8 | 3 | U1 | 2014-02-11 11:00 |  |  |  |  | 2014-02-11 11:46 |  | 0 | 0 | 0.767 | 0.7667 | 3.067 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 3651 |  |  | - |  | DC circuit breakers | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Blown Fuse on DC
OF8 | 4 | U1 | 2014-02-20 14:25 |  |  |  |  | 2014-03-03 13:24 |  | 0 | 0 | 262.983 | 262.9833 | 1051.933 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF8 | 5 | U1 | 2014-03-10 07:12 |  |  |  |  | 2014-03-11 10:27 |  | 0 | 0 | 27.25 | 27.25 | 109 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F820Trash isuses.
OF8 | 6 | U1 | 2014-03-15 09:04 |  |  |  |  | 2014-03-18 10:20 |  | 0 | 0 | 73.267 | 73.2667 | 293.066 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830High water.
OF8 | 7 | U1 | 2014-04-03 06:56 |  |  |  |  | 2014-04-15 12:28 |  | 0 | 0 | 293.533 | 293.5333 | 1761.2 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF8 | 8 | U1 | 2014-04-30 13:53 |  |  |  |  | 2014-05-07 12:07 |  | 0 | 0 | 166.233 | 166.2333 | 997.4 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF8 | 9 | U1 | 2014-05-16 13:25 |  |  |  |  | 2014-05-25 10:14 |  | 0 | 0 | 212.817 | 212.8167 | 1276.9 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830highwater
OF8 | 10 | U1 | 2014-05-31 20:21 |  |  |  |  | 2014-06-01 06:34 |  | 0 | 0 | 10.217 | 10.2167 | 61.3 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 4620 |  |  | - |  | Air cooling system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Tripped on high temp.
OF8 | 11 | U1 | 2014-06-01 16:45 |  |  |  |  | 2014-06-02 07:08 |  | 0 | 0 | 14.383 | 14.3833 | 86.3 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 4620 |  |  | - |  | Air cooling system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820C phase temp hot. Not enough cooling water
OF8 | 12 | U1 | 2014-06-02 21:27 |  |  |  |  | 2014-06-03 06:35 |  | 0 | 0 | 9.133 | 9.1333 | 54.8 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 4620 |  |  | - |  | Air cooling system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Gen cooling water. temp. on C phase hot.
OF8 | 13 | U1 | 2014-06-03 10:27 |  |  |  |  | 2014-06-03 11:20 |  | 0 | 0 | 0.883 | 0.8833 | 5.3 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 4520 |  |  | - |  | "Stator windings, bushings, and terminals" | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Rolled RTD temp probes that monitors temp on stator.
OF8 | 14 | U1 | 2014-06-03 19:43 |  |  |  |  | 2014-06-04 06:55 |  | 0 | 0 | 11.2 | 11.2 | 67.2 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 4520 |  |  | - |  | "Stator windings, bushings, and terminals" | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820RTD temp probe on B phase trip.
OF8 | 15 | U1 | 2014-06-04 06:55 |  |  |  |  | 2014-06-04 10:54 |  | 0 | 0 | 3.983 | 3.9833 | 23.9 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | E0
|  | DESCRIPTION : |  | FE00Low river
OF8 | 17 | U1 | 2014-06-12 19:58 |  |  |  |  | 2014-06-13 12:40 |  | 0 | 0 | 16.7 | 16.7 | 100.2 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 4520 |  |  | - |  | "Stator windings, bushings, and terminals" | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Unit trip c phase hot
OF8 | 18 | U1 | 2014-06-16 13:26 |  |  |  |  | 2014-06-19 07:50 |  | 0 | 0 | 66.4 | 66.4 | 398.4 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 4520 |  |  | - |  | "Stator windings, bushings, and terminals" | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830"C" Phase running too hot,had to take off before it tripped off.
OF8 | 19 | U1 | 2014-07-24 08:12 |  |  |  |  | 2014-07-24 15:22 |  | 0 | 0 | 7.167 | 7.1667 | 43 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9590 |  |  | - |  | Miscellaneous regulatory (this code is primarily intended for use with event contribution code 2 to indicate that a regulatory-related factor contributed to the primary cause of the event) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Ferc divers inspection
OF8 | 20 | U1 | 2014-07-24 15:22 |  |  |  |  | 2014-07-25 08:56 |  | 0 | 0 | 17.567 | 17.5667 | 105.4 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | FR
|  | DESCRIPTION : |  | FE00Low Flow
OF8 | 21 | U1 | 2014-07-26 09:18 |  |  |  |  | 2014-07-27 09:10 |  | 0 | 0 | 23.867 | 23.8667 | 143.2 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | FE00Low Flow
OF8 | 23 | U1 | 2014-09-30 07:06 |  |  |  |  | 2014-10-06 13:18 |  | 0 | 0 | 150.2 | 150.2 | 767.9 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | NF
|  | DESCRIPTION : |  | FE00Low Flow
OF8 | 26 | U1 | 2014-12-04 07:42 |  |  |  |  | 2014-12-04 08:37 |  | 0 | 0 | 0.917 | 0.9167 | 5.5 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 4730 |  |  | - |  | Generator current and potential transformers | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Had to tie in Currents for 480V upgrade on Unit 7.
OF8 | 27 | U1 | 2014-12-07 09:04 |  |  |  |  | 2014-12-12 10:37 |  | 0 | 0 | 121.55 | 121.55 | 729.3 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830HIGH WATER
OF8 | 1 | U1 | 2015-02-06 13:36 |  |  |  |  | 2015-02-07 14:49 |  | 0 | 0 | 25.217 | 25.2167 | 151.3 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Trash flush
OF8 | 2 | U1 | 2015-03-04 11:25 |  |  |  |  | 2015-03-30 10:45 |  | 0 | 0 | 623.333 | 623.3333 | 2493.333 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF8 | 3 | U1 | 2015-04-03 07:24 |  |  |  |  | 2015-04-30 13:29 |  | 0 | 0 | 654.083 | 654.0833 | 3924.5 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF8 | 4 | U1 | 2015-05-27 10:15 |  |  |  |  | 2015-06-02 07:18 |  | 0 | 0 | 141.05 | 141.05 | 846.3 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF8 | 5 | U1 | 2015-06-12 07:06 |  |  |  |  | 2015-06-13 09:43 |  | 0 | 0 | 26.617 | 26.6167 | 159.7 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low river
OF8 | 6 | U1 | 2015-06-21 06:12 |  |  |  |  | 2015-07-08 07:30 |  | 0 | 0 | 409.3 | 409.3 | 2455.8 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830High water.
OF8 | 7 | U1 | 2015-07-10 12:52 |  |  |  |  | 2015-07-23 10:25 |  | 0 | 0 | 309.55 | 309.55 | 1857.3 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF8 | 8 | U1 | 2015-07-25 06:42 |  |  |  |  | 2015-07-28 11:11 |  | 0 | 0 | 76.483 | 76.4833 | 458.9 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Lv bearing clogged and cool water pump stopped up.
OF8 | 9 | U1 | 2015-08-09 21:27 |  |  |  |  | 2015-08-11 14:55 |  | 0 | 0 | 41.467 | 41.4667 | 248.8 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low flow
OF8 | 10 | U1 | 2015-08-13 17:33 |  |  |  |  | 2015-08-14 10:07 |  | 0 | 0 | 16.567 | 16.5667 | 99.4 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low flow
OF8 | 11 | U1 | 2015-08-15 06:26 |  |  |  |  | 2015-10-01 13:54 |  | 0 | 0 | 1135.467 | 1135.4667 | 6812.8 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830off low flow
OF8 | 12 | U1 | 2015-10-07 20:02 |  |  |  |  | 2015-10-20 07:59 |  | 0 | 0 | 299.95 | 299.95 | 1799.7 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Took unit off at the request of ACOE. Low flow.
OF8 | 13 | U1 | 2015-10-20 11:57 |  |  |  |  | 2015-10-27 13:31 |  | 0 | 0 | 169.567 | 169.5667 | 1017.4 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830LOW FLOW
OF8 | 14 | U1 | 2015-11-13 06:57 |  |  |  |  | 2015-11-13 10:33 |  | 0 | 0 | 3.6 | 3.6 | 21.6 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7053 |  |  | - |  | Governor oil system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Trip Pressure Tank Oil Level Low. Solenoid air valve stuck. Problem corrected.
OF8 | 15 | U1 | 2015-11-20 06:29 |  |  |  |  | 2015-11-20 11:15 |  | 0 | 0 | 4.767 | 4.7667 | 28.6 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 4650 |  |  | - |  | Other cooling system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Turbine guide bearing strainer blocked and high temp. on stator windings.
OF8 | 16 | U1 | 2015-11-21 08:00 |  |  |  |  | 2015-11-21 09:30 |  | 0 | 0 | 1.5 | 1.5 | 9 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 4650 |  |  | - |  | Other cooling system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Turbine Guide Bearing Cooling Water Strainer Blocked
OF8 | 18 | U1 | 2015-12-03 13:07 |  |  |  |  | 2015-12-09 10:02 |  | 0 | 0 | 140.917 | 140.9167 | 845.5 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF8 | 19 | U1 | 2015-12-15 02:24 |  |  |  |  | 2015-12-15 09:01 |  | 0 | 0 | 6.617 | 6.6167 | 39.7 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 7053 |  |  | - |  | Governor oil system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Governor oil pressure tank had a selenoid malfuction. Replaced.
OF8 | 20 | U1 | 2015-12-24 09:39 |  |  |  |  | 2015-12-31 23:59 |  | 0 | 0 | 182.333 | 182.3333 | 1094 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF8 | 1 | U1 | 2016-01-01 |  |  |  |  | 2016-01-06 14:01 |  | 0 | 0 | 134.017 | 134.0167 | 670.083 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830highwater
OF8 | 2 | U1 | 2016-01-17 11:42 |  |  |  |  | 2016-01-19 15:55 |  | 0 | 0 | 52.217 | 52.2167 | 261.083 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Screens outside going to L.V. Bearing blocked
OF8 | 3 | U1 | 2016-02-03 07:14 |  |  |  |  | 2016-02-13 11:32 |  | 0 | 0 | 244.3 | 244.3 | 977.2 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF8 | 4 | U1 | 2016-02-17 03:11 |  |  |  |  | 2016-02-19 09:43 |  | 0 | 0 | 54.533 | 54.5333 | 218.134 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 7053 |  |  | - |  | Governor oil system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Low oil pressure
OF8 | 5 | U1 | 2016-02-19 09:43 |  |  |  |  | 2016-03-09 13:49 |  | 0 | 0 | 460.1 | 460.1 | 2046.216 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | NF
|  | DESCRIPTION : |  | F400Unit 8 was repaired, but can not be placed in service due to highwater river cond
OF8 | 6 | U1 | 2016-03-11 13:56 |  |  |  |  | 2016-03-22 10:46 |  | 0 | 0 | 260.833 | 260.8333 | 1304.166 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF8 | 7 | U1 | 2016-03-27 23:07 |  |  |  |  | 2016-03-28 12:07 |  | 0 | 0 | 13 | 13 | 65 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7053 |  |  | - |  | Governor oil system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Low oil pressure on gov tank.
OF8 | 8 | U1 | 2016-04-15 09:22 |  |  |  |  | 2016-04-18 11:15 |  | 0 | 0 | 73.883 | 73.8833 | 369.417 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830HIGHWATER
OF8 | 9 | U1 | 2016-05-03 07:30 |  |  |  |  | 2016-05-10 12:53 |  | 0 | 0 | 173.383 | 173.3833 | 866.917 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830HIGHWATER
OF8 | 10 | U1 | 2016-05-11 12:07 |  |  |  |  | 2016-05-17 07:53 |  | 0 | 0 | 139.767 | 139.7667 | 698.834 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF8 | 12 | U1 | 2016-06-25 04:09 |  |  |  |  | 2016-06-29 09:12 |  | 0 | 0 | 101.05 | 101.05 | 606.3 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Highwater
OF8 | 13 | U1 | 2016-07-20 06:48 |  |  |  |  | 2016-07-28 11:59 |  | 0 | 0 | 197.183 | 197.1833 | 1577.467 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF8 | 14 | U1 | 2016-08-12 10:53 |  |  |  |  | 2016-08-14 08:58 |  | 0 | 0 | 46.083 | 46.0833 | 276.5 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830LOW FLOW
OF8 | 15 | U1 | 2016-08-14 21:01 |  |  |  |  | 2016-08-16 10:17 |  | 0 | 0 | 37.267 | 37.2667 | 223.6 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830LOW FLOW
OF8 | 16 | U1 | 2016-08-20 08:18 |  |  |  |  | 2016-08-24 06:24 |  | 0 | 0 | 94.1 | 94.1 | 564.6 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF8 | 17 | U1 | 2016-08-28 14:31 |  |  |  |  | 2016-08-30 06:39 |  | 0 | 0 | 40.133 | 40.1333 | 240.8 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF8 | 18 | U1 | 2016-08-31 14:24 |  |  |  |  | 2016-10-01 09:04 |  | 0 | 0 | 738.667 | 738.6667 | 3721.067 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF8 | 19 | U1 | 2016-10-08 08:13 |  |  |  |  | 2016-10-10 08:01 |  | 0 | 0 | 47.8 | 47.8 | 334.6 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low river flow
OF8 | 22 | U1 | 2016-10-21 06:05 |  |  |  |  | 2016-10-22 12:25 |  | 0 | 0 | 30.333 | 30.3333 | 212.334 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF8 | 23 | U1 | 2016-11-16 13:02 |  |  |  |  | 2016-11-17 08:17 |  | 0 | 0 | 19.25 | 19.25 | 134.75 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF8 | 24 | U1 | 2016-11-19 17:52 |  |  |  |  | 2016-11-21 08:33 |  | 0 | 0 | 38.683 | 38.6833 | 270.783 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF8 | 7 | U1 | 2017-11-22 10:54 |  |  |  |  | 2017-11-25 08:32 |  | 0 | 0 | 69.633 | 69.6333 | 487.433 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for highwater and trash
OF8 | 9 | U1 | 2017-12-26 15:01 |  |  |  |  | 2017-12-27 14:18 |  | 0 | 0 | 23.283 | 23.2833 | 162.983 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830highwater
OF8 | 1 | U1 | 2018-01-03 12:27 |  |  |  |  | 2018-01-04 13:53 |  | 0 | 0 | 25.433 | 25.4333 | 127.167 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Run of river
OF8 | 2 | U1 | 2018-01-11 07:35 |  |  |  |  | 2018-01-11 13:02 |  | 0 | 0 | 5.45 | 5.45 | 27.25 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Trash Buildup
OF8 | 3 | U1 | 2018-01-14 04:19 |  |  |  |  | 2018-01-20 10:08 |  | 0 | 0 | 149.817 | 149.8167 | 749.084 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF8 | 4 | U1 | 2018-01-24 15:01 |  |  |  |  | 2018-01-29 13:33 |  | 0 | 0 | 118.533 | 118.5333 | 592.667 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830highwater
OF8 | 6 | U1 | 2018-02-09 08:08 |  |  |  |  | 2018-03-11 12:14 |  | 0 | 0 | 724.1 | 724.1 | 3148.634 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830High river
OF8 | 10 | U1 | 2018-03-24 13:01 |  |  |  |  | 2018-03-27 08:55 |  | 0 | 0 | 67.9 | 67.9 | 339.5 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830highwater
OF8 | 11 | U1 | 2018-03-28 06:24 |  |  |  |  | 2018-04-15 08:32 |  | 0 | 0 | 434.133 | 434.1333 | 2170.667 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F830Highwater
OF8 | 12 | U1 | 2018-04-17 05:50 |  |  |  |  | 2018-04-30 12:02 |  | 0 | 0 | 318.2 | 318.2 | 1591 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830highwater
OF8 | 14 | U1 | 2018-05-08 14:10 |  |  |  |  | 2018-05-12 07:12 |  | 0 | 0 | 89.033 | 89.0333 | 445.167 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF8 | 17 | U1 | 2018-05-21 07:11 |  |  |  |  | 2018-05-22 09:18 |  | 0 | 0 | 26.117 | 26.1167 | 130.583 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater / Trash
OF8 | 19 | U1 | 2018-06-07 08:46 |  |  |  |  | 2018-06-07 20:01 |  | 0 | 0 | 11.25 | 11.25 | 90 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7190 |  |  | - |  | Dewatering and rewatering equipment | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F590Barge crane needed unit off to work on unit 7
OF8 | 21 | U1 | 2018-06-25 09:10 |  |  |  |  | 2018-06-27 07:07 |  | 0 | 0 | 45.95 | 45.95 | 367.6 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF8 | 23 | U1 | 2018-07-14 13:50 |  |  |  |  | 2018-07-16 06:54 |  | 0 | 0 | 41.067 | 41.0667 | 328.533 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low flow
OF8 | 24 | U1 | 2018-07-16 15:00 |  |  |  |  | 2018-07-17 11:46 |  | 0 | 0 | 20.767 | 20.7667 | 166.133 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Water
OF8 | 27 | U1 | 2018-08-20 08:47 |  |  |  |  | 2018-08-20 13:34 |  | 0 | 0 | 4.783 | 4.7833 | 28.7 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830trash
OF8 | 28 | U1 | 2018-08-22 12:05 |  |  |  |  | 2018-08-22 12:58 |  | 0 | 0 | 0.883 | 0.8833 | 5.3 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9720 |  |  | - |  | Other safety problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Crane safety
OF8 | 29 | U1 | 2018-09-09 09:01 |  |  |  |  | 2018-09-17 15:00 |  | 0 | 0 | 197.983 | 197.9833 | 1385.883 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830highwater
OF8 | 30 | U1 | 2018-09-20 09:45 |  |  |  |  | 2018-09-24 09:36 |  | 0 | 0 | 95.85 | 95.85 | 670.95 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF8 | 31 | U1 | 2018-09-25 07:12 |  |  |  |  | 2018-10-04 07:35 |  | 0 | 0 | 216.383 | 216.3833 | 1514.683 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830high water
OF8 | 32 | U1 | 2018-10-10 09:00 |  |  |  |  | 2018-10-10 16:51 |  | 0 | 0 | 7.85 | 7.85 | 54.95 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Trash in front of facility Intakes
OF8 | 34 | U1 | 2018-10-27 16:42 |  |  |  |  | 2018-10-28 11:23 |  | 0 | 0 | 18.683 | 18.6833 | 130.783 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 4650 |  |  | - |  | Other cooling system problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F780gpu high temperature
OF8 | 35 | U1 | 2018-11-02 10:24 |  |  |  |  | 2018-11-30 23:59 |  | 0 | 0 | 685.583 | 685.5833 | 4799.083 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF8 | 36 | U1 | 2018-12-17 14:28 |  |  |  |  | 2019-01-01 |  | 0 | 0 | 345.533 | 345.5333 | 1727.667 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830high water
OF8 | 1 | U1 | 2019-01-01 |  |  |  |  | 2019-01-16 14:54 |  | 0 | 0 | 374.9 | 374.9 | 1874.5 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Highwater
OF8 | 2 | U1 | 2019-01-20 17:22 |  |  |  |  | 2019-01-31 23:59 |  | 0 | 0 | 270.617 | 270.6167 | 1353.084 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830high water
OF8 | 3 | U1 | 2019-02-01 |  |  |  |  | 2019-02-03 10:51 |  | 0 | 0 | 58.85 | 58.85 | 294.25 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF8 | 4 | U1 | 2019-02-03 22:27 |  |  |  |  | 2019-02-04 09:13 |  | 0 | 0 | 10.767 | 10.7667 | 53.833 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 4550 |  |  | - |  | Generator bearings and lube oil system (including thrust bearings on hydro units) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Upper guide bearing had high temp and tripped, found needle flow bearing stopped.
OF8 | 5 | U1 | 2019-02-07 08:16 |  |  |  |  | 2019-03-06 13:16 |  | 0 | 0 | 653 | 653 | 3531.534 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830highwater
OF8 | 6 | U1 | 2019-03-10 14:15 |  |  |  |  | 2019-03-22 09:41 |  | 0 | 0 | 283.433 | 283.4333 | 1984.033 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF8 | 8 | U1 | 2019-04-12 11:01 |  |  |  |  | 2019-04-12 15:06 |  | 0 | 0 | 4.083 | 4.0833 | 28.583 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830trash
OF8 | 9 | U1 | 2019-04-14 04:34 |  |  |  |  | 2019-04-14 10:13 |  | 0 | 0 | 5.65 | 5.65 | 39.55 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7009 |  |  | - |  | Bearing oil system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820bearing oil temp to hot
OF8 | 10 | U1 | 2019-04-15 12:21 |  |  |  |  | 2019-04-15 13:48 |  | 0 | 0 | 1.45 | 1.45 | 10.15 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 3710 |  |  | - |  | Transmission line (connected to powerhouse switchyard to 1st Substation) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830line 6608 protection relay
OF8 | 11 | U1 | 2019-04-20 08:32 |  |  |  |  | 2019-05-03 09:03 |  | 0 | 0 | 312.517 | 312.5167 | 2187.617 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830highwater
OF8 | 12 | U1 | 2019-05-07 15:55 |  |  |  |  | 2019-05-10 06:27 |  | 0 | 0 | 62.533 | 62.5333 | 437.733 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Water on the headworks, highwater
OF8 | 13 | U1 | 2019-05-17 06:00 |  |  |  |  | 2019-05-17 06:56 |  | 0 | 0 | 0.933 | 0.9333 | 6.533 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 3972 |  |  | - |  | DCS - hardware problems (including card failure) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820wicket gate driver card
OF8 | 14 | U1 | 2019-06-17 15:21 |  |  |  |  | 2019-06-28 07:32 |  | 0 | 0 | 256.183 | 256.1833 | 2049.467 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830high water
OF8 | 15 | U1 | 2019-07-11 20:06 |  |  |  |  | 2019-07-12 07:06 |  | 0 | 0 | 11 | 11 | 88 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 4550 |  |  | - |  | Generator bearings and lube oil system (including thrust bearings on hydro units) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Temp. spike Intermediate bearing pad #1
OF8 | 16 | U1 | 2019-07-16 21:51 |  |  |  |  | 2019-07-17 07:31 |  | 0 | 0 | 9.667 | 9.6667 | 77.333 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7008 |  |  | - |  | Bearing cooling system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Strainer basket clogged
OF8 | 17 | U1 | 2019-07-22 12:58 |  |  |  |  | 2019-07-22 15:26 |  | 0 | 0 | 2.467 | 2.4667 | 19.733 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 4550 |  |  | - |  | Generator bearings and lube oil system (including thrust bearings on hydro units) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Intermediate guide bearing trtip
OF8 | 18 | U1 | 2019-07-23 07:35 |  |  |  |  | 2019-07-23 13:19 |  | 0 | 0 | 5.733 | 5.7333 | 45.867 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830trash
OF8 | 19 | U1 | 2019-08-06 17:44 |  |  |  |  | 2019-08-08 07:45 |  | 0 | 0 | 38.017 | 38.0167 | 304.133 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF8 | 20 | U1 | 2019-08-21 06:56 |  |  |  |  | 2019-08-21 09:23 |  | 0 | 0 | 2.45 | 2.45 | 19.6 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River Conditions
OF8 | 21 | U1 | 2019-08-24 21:54 |  |  |  |  | 2019-08-25 06:49 |  | 0 | 0 | 8.917 | 8.9167 | 71.333 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9720 |  |  | - |  | Other safety problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830river rescue
OF8 | 22 | U1 | 2019-09-06 12:15 |  |  |  |  | 2019-09-07 12:07 |  | 0 | 0 | 23.867 | 23.8667 | 167.067 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low flow
OF8 | 23 | U1 | 2019-09-09 12:59 |  |  |  |  | 2019-09-10 16:09 |  | 0 | 0 | 27.167 | 27.1667 | 190.167 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF8 | 24 | U1 | 2019-09-12 04:15 |  |  |  |  | 2019-09-13 12:57 |  | 0 | 0 | 32.7 | 32.7 | 228.9 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low river
OF8 | 25 | U1 | 2019-09-18 02:28 |  |  |  |  | 2019-09-18 10:59 |  | 0 | 0 | 8.517 | 8.5167 | 59.617 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830ACOE requested shutdown for low flow
OF8 | 26 | U1 | 2019-09-20 15:58 |  |  |  |  | 2019-09-22 08:28 |  | 0 | 0 | 40.5 | 40.5 | 283.5 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline per ACOE Request Low FLow
OF8 | 27 | U1 | 2019-09-23 09:15 |  |  |  |  | 2019-09-25 07:02 |  | 0 | 0 | 45.783 | 45.7833 | 320.483 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF8 | 28 | U1 | 2019-09-26 06:50 |  |  |  |  | 2019-09-30 08:00 |  | 0 | 0 | 97.167 | 97.1667 | 680.167 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low flow
OF8 | 29 | U1 | 2019-09-30 16:05 |  |  |  |  | 2019-10-01 13:06 |  | 0 | 0 | 21.017 | 21.0167 | 147.117 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF8 | 30 | U1 | 2019-10-02 20:13 |  |  |  |  | 2019-10-04 07:34 |  | 0 | 0 | 35.35 | 35.35 | 247.45 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low river
OF8 | 31 | U1 | 2019-10-10 00:41 |  |  |  |  | 2019-10-14 07:21 |  | 0 | 0 | 102.667 | 102.6667 | 718.667 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low flow, Offline by request from ACOE
OF8 | 32 | U1 | 2019-10-15 02:58 |  |  |  |  | 2019-10-17 06:50 |  | 0 | 0 | 51.867 | 51.8667 | 363.066 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low flow
OF8 | 33 | U1 | 2019-10-22 13:53 |  |  |  |  | 2019-10-23 06:56 |  | 0 | 0 | 17.05 | 17.05 | 119.35 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low river
OF8 | 35 | U1 | 2019-11-18 09:22 |  |  |  |  | 2019-11-23 11:13 |  | 0 | 0 | 121.85 | 121.85 | 852.95 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low Flow
OF8 | 36 | U1 | 2019-12-03 08:10 |  |  |  |  | 2019-12-05 11:09 |  | 0 | 0 | 50.983 | 50.9833 | 254.917 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830highwater
OF8 | 37 | U1 | 2019-12-14 13:20 |  |  |  |  | 2019-12-24 10:03 |  | 0 | 0 | 236.717 | 236.7167 | 1183.583 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830highwater
OF8 | 38 | U1 | 2019-12-31 12:47 |  |  |  |  | 2019-12-31 23:59 |  | 0 | 0 | 11.2 | 11.2 | 56 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Highwater
OF8 | 1 | U1 | 2020-01-01 |  |  |  |  | 2020-01-10 09:48 |  | 0 | 0 | 225.8 | 225.8 | 1129 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Highwater
OF8 | 2 | U1 | 2020-01-17 09:55 |  |  |  |  | 2020-01-18 09:05 |  | 0 | 0 | 23.167 | 23.1667 | 115.834 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830High River
OF8 | 3 | U1 | 2020-01-29 08:39 |  |  |  |  | 2020-02-01 10:08 |  | 0 | 0 | 73.483 | 73.4833 | 367.417 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830High River
OF8 | 4 | U1 | 2020-02-09 08:44 |  |  |  |  | 2020-02-24 13:17 |  | 0 | 0 | 364.55 | 364.55 | 1822.75 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Highwater
OF8 | 5 | U1 | 2020-03-06 06:50 |  |  |  |  | 2020-03-10 09:14 |  | 0 | 0 | 98.4 | 98.4 | 688.8 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Highwater
OF8 | 6 | U1 | 2020-03-15 10:35 |  |  |  |  | 2020-04-06 08:51 |  | 0 | 0 | 526.267 | 526.2667 | 3683.867 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Highwater
OF8 | 7 | U1 | 2020-04-08 17:50 |  |  |  |  | 2020-04-09 09:59 |  | 0 | 0 | 16.15 | 16.15 | 113.05 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 3670 |  |  | - |  | 12-15kV transformers | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Bad P T fuse
OF8 | 8 | U1 | 2020-04-16 05:53 |  |  |  |  | 2020-04-21 09:02 |  | 0 | 0 | 123.15 | 123.15 | 862.05 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for highwater
OF8 | 9 | U1 | 2020-04-29 10:25 |  |  |  |  | 2020-05-11 12:44 |  | 0 | 0 | 290.317 | 290.3167 | 2032.216 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Highwater
OF8 | 10 | U1 | 2020-05-20 09:01 |  |  |  |  | 2020-05-29 12:34 |  | 0 | 0 | 219.55 | 219.55 | 1536.85 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830highwater
OF8 | 11 | U1 | 2020-06-03 13:41 |  |  |  |  | 2020-06-10 16:36 |  | 0 | 0 | 170.917 | 170.9167 | 1367.333 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 3710 |  |  | - |  | Transmission line (connected to powerhouse switchyard to 1st Substation) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Transformer Outage
OF8 | 12 | U1 | 2020-06-16 12:23 |  |  |  |  | 2020-06-16 13:31 |  | 0 | 0 | 1.133 | 1.1333 | 9.067 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 3710 |  |  | - |  | Transmission line (connected to powerhouse switchyard to 1st Substation) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Transmission Outage
OF8 | 13 | U1 | 2020-06-17 10:30 |  |  |  |  | 2020-06-17 11:04 |  | 0 | 0 | 0.567 | 0.5667 | 4.533 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 3710 |  |  | - |  | Transmission line (connected to powerhouse switchyard to 1st Substation) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Transmission Outage
OF8 | 14 | U1 | 2020-06-26 06:27 |  |  |  |  | 2020-06-26 10:20 |  | 0 | 0 | 3.883 | 3.8833 | 31.067 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9350 |  |  | - |  | Public Safety (water hazard or river rescue) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F590ACOE requested shutdown for safety while they are working on the lower dam.
OF8 | 15 | U1 | 2020-06-30 08:12 |  |  |  |  | 2020-06-30 10:00 |  | 0 | 0 | 1.8 | 1.8 | 14.4 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9350 |  |  | - |  | Public Safety (water hazard or river rescue) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830ACOE request on lower dam
OF8 | 16 | U1 | 2020-07-17 07:49 |  |  |  |  | 2020-07-17 14:04 |  | 0 | 0 | 6.25 | 6.25 | 50 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low flow.
OF8 | 17 | U1 | 2020-07-22 09:32 |  |  |  |  | 2020-07-22 12:09 |  | 0 | 0 | 2.617 | 2.6167 | 20.933 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9350 |  |  | - |  | Public Safety (water hazard or river rescue) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Louisville Fire Department requested Unit Shutdown, due to a boat in the water for
OF8 | 18 | U1 | 2020-08-04 07:44 |  |  |  |  | 2020-08-04 09:09 |  | 0 | 0 | 1.417 | 1.4167 | 11.333 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Trash
OF8 | 19 | U1 | 2020-08-11 08:46 |  |  |  |  | 2020-08-16 09:03 |  | 0 | 0 | 120.283 | 120.2833 | 962.267 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF8 | 20 | U1 | 2020-08-24 12:11 |  |  |  |  | 2020-08-27 07:19 |  | 0 | 0 | 67.133 | 67.1333 | 537.066 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF8 | 21 | U1 | 2020-09-12 21:16 |  |  |  |  | 2020-09-14 11:51 |  | 0 | 0 | 38.583 | 38.5833 | 270.083 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Lack of water.
OF8 | 22 | U1 | 2020-09-15 12:09 |  |  |  |  | 2020-09-15 14:05 |  | 0 | 0 | 1.933 | 1.9333 | 13.533 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for trash.
OF8 | 23 | U1 | 2020-09-24 20:41 |  |  |  |  | 2020-09-29 06:36 |  | 0 | 0 | 105.917 | 105.9167 | 741.417 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830low river
OF8 | 24 | U1 | 2020-10-05 02:17 |  |  |  |  | 2020-10-08 10:16 |  | 0 | 0 | 79.983 | 79.9833 | 559.884 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Lack of water.
OF8 | 25 | U1 | 2020-10-09 16:59 |  |  |  |  | 2020-10-13 06:41 |  | 0 | 0 | 85.7 | 85.7 | 599.9 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF8 | 26 | U1 | 2020-10-16 12:23 |  |  |  |  | 2020-10-17 10:32 |  | 0 | 0 | 22.15 | 22.15 | 155.05 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF8 | 28 | U1 | 2020-11-08 19:00 |  |  |  |  | 2020-11-11 08:27 |  | 0 | 0 | 61.45 | 61.45 | 430.15 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Low River
OF8 | 31 | U1 | 2020-12-16 11:10 |  |  |  |  | 2020-12-16 16:16 |  | 0 | 0 | 5.1 | 5.1 | 25.5 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9350 |  |  | - |  | Public Safety (water hazard or river rescue) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Diesel fuel in upper pool
OF8 | 32 | U1 | 2020-12-27 02:43 |  |  |  |  | 2020-12-27 09:47 |  | 0 | 0 | 7.067 | 7.0667 | 35.333 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 4551 |  |  | - |  | Generator bearings | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F780Intermediate guide bearing spiked 20 degrees on pad 2 and caused the unit to trip
OF8 | 33 | U1 | 2020-12-27 10:24 |  |  |  |  | 2020-12-27 11:58 |  | 0 | 0 | 1.567 | 1.5667 | 7.833 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 4551 |  |  | - |  | Generator bearings | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F780Bearing Temp Spiked, troubleshooting taking place at this time.
OF8 | 34 | U1 | 2020-12-27 12:12 |  |  |  |  | 2021-01-01 |  | 0 | 0 | 107.8 | 107.8 | 539 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Highwater
OF8 | 1 | U1 | 2021-01-01 |  |  |  |  | 2021-01-11 12:05 |  | 0 | 0 | 252.083 | 252.0833 | 3176.25 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for highwater
OF8 | 3 | U1 | 2021-01-21 09:00 |  |  |  |  | 2022-01-01 |  | 0 | 0 | 8271 | 8271 | 104214.6 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 7141 |  |  | - |  | Wicket gate operating mechanism or positioner | [8 empty] | AMP CODE: |  | 28
|  | DESCRIPTION : |  | F280Wicket Gate servo mount is cracked at base, Indiana Side in Unit #8 Pit.
OF8 | 1 | U1 | 2022-01-01 |  |  |  |  | 2022-01-31 15:56 |  | 0 | 0 | 735.933 | 735.9333 | 9272.76 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 7141 |  |  | - |  | Wicket gate operating mechanism or positioner | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F280Wicket Gate servo mount is crasked at base. Indiana Side in Unit #8 Pit.
OF8 | 2 | U1 | 2022-02-04 11:51 |  |  |  |  | 2022-02-14 15:08 |  | 0 | 0 | 243.283 | 243.2833 | 3065.37 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Offline for High Water
OF8 | 4 | U1 | 2022-02-18 07:25 |  |  |  |  | 2022-03-21 07:08 |  | 0 | 0 | 743.717 | 743.7167 | 9370.83 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | FR
|  | DESCRIPTION : |  | F830Unit offline for High Water (Run of River)
OF8 | 7 | U1 | 2022-04-15 11:48 |  |  |  |  | 2022-04-18 07:05 |  | 0 | 0 | 67.283 | 67.2833 | 847.77 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for High Water.
OF8 | 9 | U1 | 2022-05-08 17:04 |  |  |  |  | 2022-05-16 08:54 |  | 0 | 0 | 183.833 | 183.8333 | 2316.3 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9010 |  |  | - |  | "Fire including wildfires, not related to a specific component" | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for High Water.
OF8 | 10 | U1 | 2022-05-31 07:04 |  |  |  |  | 2022-06-01 06:55 |  | 0 | 0 | 23.85 | 23.85 | 300.51 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for trash.
OF8 | 11 | U1 | 2022-06-13 20:16 |  |  |  |  | 2022-06-14 07:41 |  | 0 | 0 | 11.417 | 11.4167 | 143.85 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7053 |  |  | - |  | Governor oil system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Gov. Oil Level
OF8 | 13 | U1 | 2022-07-16 22:49 |  |  |  |  | 2022-07-17 08:25 |  | 0 | 0 | 9.6 | 9.6 | 120.96 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 3979 |  |  | - |  | Other DCS problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830There was a Company wide Internet outage, Cane Run lost connectivity with our Plan
OF8 | 15 | U1 | 2022-08-02 03:21 |  |  |  |  | 2022-08-02 13:10 |  | 0 | 0 | 9.817 | 9.8167 | 123.69 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Unit offline for Trash
OF8 | 16 | U1 | 2022-08-23 10:33 |  |  |  |  | 2022-08-23 13:36 |  | 0 | 0 | 3.05 | 3.05 | 38.43 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Trash (Run of River)
OF8 | 17 | U1 | 2022-09-06 07:21 |  |  |  |  | 2022-09-06 08:47 |  | 0 | 0 | 1.433 | 1.4333 | 18.06 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830trash
OF8 | 18 | U1 | 2022-09-06 12:59 |  |  |  |  | 2022-09-07 06:38 |  | 0 | 0 | 17.65 | 17.65 | 222.39 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830trash
OF8 | 19 | U1 | 2022-09-08 12:17 |  |  |  |  | 2022-09-08 12:25 |  | 0 | 0 | 0.133 | 0.1333 | 1.68 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9900 |  |  | - |  | Operator error | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830operator error
OF8 | 20 | U1 | 2022-09-11 06:06 |  |  |  |  | 2022-09-15 14:00 |  | 0 | 0 | 103.9 | 103.9 | 1309.14 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830trash was at 13.8'
OF8 | 21 | U1 | 2022-09-15 14:00 |  |  |  |  | 2022-09-23 13:18 |  | 0 | 0 | 191.3 | 191.3 | 2410.38 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 7007 |  |  | - |  | Bearings | [8 empty] | AMP CODE:
|  | DESCRIPTION : |  | F830Unit offline due to Bearing Issue (Rod and Wrench)
OF8 | 22 | U1 | 2022-09-23 13:18 |  |  |  |  | 2022-10-03 09:22 |  | 0 | 0 | 236.067 | 236.0667 | 2974.44 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | FR
|  | DESCRIPTION : |  | F830Offline for Run of River
OF8 | 23 | U1 | 2022-10-15 10:19 |  |  |  |  | 2022-10-16 06:51 |  | 0 | 0 | 20.533 | 20.5333 | 258.72 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Lack of Water
OF8 | 24 | U1 | 2022-10-23 08:11 |  |  |  |  | 2022-10-28 10:51 |  | 0 | 0 | 122.667 | 122.6667 | 1545.6 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Lack of Water
OF8 | 25 | U1 | 2022-10-29 11:00 |  |  |  |  | 2022-10-31 11:44 |  | 0 | 0 | 48.733 | 48.7333 | 614.04 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Lack of Water
OF8 | 26 | U1 | 2022-11-02 14:38 |  |  |  |  | 2022-11-06 08:26 |  | 0 | 0 | 89.8 | 89.8 | 1131.48 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for Lack of Water.
OF8 | 27 | U1 | 2022-12-11 08:28 |  |  |  |  | 2022-12-12 09:41 |  | 0 | 0 | 25.217 | 25.2167 | 317.73 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830trash
OF8 | 1 | U1 | 2023-01-03 19:01 |  |  |  |  | 2023-01-09 15:11 |  | 0 | 0 | 140.167 | 140.1667 | 1766.1 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for trash.
OF8 | 2 | U1 | 2023-01-14 23:02 |  |  |  |  | 2023-01-27 10:10 |  | 0 | 0 | 299.133 | 299.1333 | 3769.08 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830trash
OF8 | 3 | U1 | 2023-01-29 13:28 |  |  |  |  | 2023-01-30 08:34 |  | 0 | 0 | 19.1 | 19.1 | 240.66 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9320 |  |  | - |  | Other miscellaneous external problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for barge recovery.
OF8 | 4 | U1 | 2023-02-03 12:13 |  |  |  |  | 2023-02-07 09:05 |  | 0 | 0 | 92.867 | 92.8667 | 1170.12 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9320 |  |  | - |  | Other miscellaneous external problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830barge recovery
OF8 | 6 | U1 | 2023-02-18 04:12 |  |  |  |  | 2023-02-24 08:19 |  | 0 | 0 | 148.117 | 148.1167 | 1866.27 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for High Water
OF8 | 7 | U1 | 2023-03-03 19:56 |  |  |  |  | 2023-03-13 08:03 |  | 0 | 0 | 228.117 | 228.1167 | 2874.27 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for High Water
OF8 | 8 | U1 | 2023-03-25 00:39 |  |  |  |  | 2023-04-11 06:30 |  | 0 | 0 | 413.85 | 413.85 | 5214.51 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9000 |  |  | - |  | Flood | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Offline for High Water.
OF8 | 9 | U1 | 2023-04-11 06:30 |  |  |  |  | 2023-04-28 12:01 |  | 0 | 0 | 413.517 | 413.5167 | 5210.31 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9320 |  |  | - |  | Other miscellaneous external problems | [8 empty] | AMP CODE: |  | FR
|  | DESCRIPTION : |  | FX00Barge Recovery
OF8 | 10 | U1 | 2023-05-29 10:47 |  |  |  |  | 2023-06-13 07:19 |  | 0 | 0 | 356.533 | 356.5333 | 4492.32 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Lack of Water.
OF8 | 11 | U1 | 2023-06-26 07:28 |  |  |  |  | 2023-06-26 16:00 |  | 0 | 0 | 8.533 | 8.5333 | 107.52 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for MSI sonar.
OF8 | 12 | U1 | 2023-07-07 04:30 |  |  |  |  | 2023-07-07 12:30 |  | 0 | 0 | 8 | 8 | 100.8 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 7110 |  |  | - |  | Intake channel or flume (including trash racks) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Trash
OF8 | 13 | U1 | 2023-07-24 13:33 |  |  |  |  | 2023-07-27 13:18 |  | 0 | 0 | 71.75 | 71.75 | 904.05 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for lack of water
OF8 | 16 | U1 | 2023-08-13 08:12 |  |  |  |  | 2023-08-14 07:40 |  | 0 | 0 | 23.467 | 23.4667 | 295.68 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | FR
|  | DESCRIPTION : |  | F830lack of water
OF8 | 17 | U1 | 2023-08-21 11:37 |  |  |  |  | 2023-08-23 09:09 |  | 0 | 0 | 45.533 | 45.5333 | 573.72 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline lack of water.
OF8 | 18 | U1 | 2023-08-23 22:57 |  |  |  |  | 2023-08-25 06:48 |  | 0 | 0 | 31.85 | 31.85 | 401.31 | 1 |  |  |  | 0 |  |  | 8
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for lack of water.
OF8 | 20 | U1 | 2023-09-23 06:24 |  |  |  |  | 2023-09-26 06:51 |  | 0 | 0 | 72.45 | 72.45 | 912.87 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | FR
|  | DESCRIPTION : |  | F830lack of water
OF8 | 21 | U1 | 2023-09-30 14:09 |  |  |  |  | 2023-10-02 07:26 |  | 0 | 0 | 41.283 | 41.2833 | 520.17 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for lack of water
OF8 | 22 | U1 | 2023-10-03 03:54 |  |  |  |  | 2023-10-05 08:00 |  | 0 | 0 | 52.1 | 52.1 | 656.46 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline lack of water.
OF8 | 23 | U1 | 2023-10-06 06:22 |  |  |  |  | 2023-10-08 06:34 |  | 0 | 0 | 48.2 | 48.2 | 607.32 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline for lack of water.
OF8 | 24 | U1 | 2023-10-08 22:56 |  |  |  |  | 2023-10-10 06:50 |  | 0 | 0 | 31.9 | 31.9 | 401.94 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline lack of water.
OF8 | 25 | U1 | 2023-10-11 01:59 |  |  |  |  | 2023-10-17 13:43 |  | 0 | 0 | 155.733 | 155.7333 | 1962.24 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830lack of water
OF8 | 26 | U1 | 2023-10-21 15:04 |  |  |  |  | 2023-10-23 07:09 |  | 0 | 0 | 40.083 | 40.0833 | 505.05 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Lack of Water
OF8 | 27 | U1 | 2023-10-26 13:50 |  |  |  |  | 2023-10-28 08:19 |  | 0 | 0 | 42.483 | 42.4833 | 535.29 | 1 |  |  |  | 0 |  |  | 6.5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Offline lack of water.
OF8 | 28 | U1 | 2023-12-17 19:49 |  |  |  |  | 2023-12-20 08:01 |  | 0 | 0 | 60.2 | 60.2 | 758.52 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit offline for Lack of Water
OF8 | 29 | U1 | 2023-12-20 08:01 |  |  |  |  | 2023-12-21 11:02 |  | 0 | 0 | 27.017 | 27.0167 | 340.41 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 3670 |  |  | - |  | 12-15kV transformers | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F830carded TR-2 for MAC construction to replace catwalk for relay room
OF8 | 30 | U1 | 2023-12-21 11:02 |  |  |  |  | 2023-12-28 09:52 |  | 0 | 0 | 166.833 | 166.8333 | 2102.1 | 1 |  |  |  | 0 |  |  | 5
|  | CAUSE CODE : |  | 9135 |  |  | - |  | Lack of water | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830lack of water
Paddy's Run - PR12
Unit | Event | Type | Start |  |  |  |  | End |  | GAC | NAC | Duration | Equiv Hrs | Equiv MWH | Cont | Work Start | Work End |  | Hours |  |  | Gross Capacity Impact (MW)
PR12 | 2 | U1 | 2014-01-30 07:00 |  |  |  |  | 2014-01-31 09:20 |  | 0 | 0 | 26.333 | 26.3333 | 737.333 | 1 |  |  |  | 0 |  |  | 28
|  | CAUSE CODE : |  | 9130 |  |  | - |  | "Lack of fuel (water from rivers or lakes, coal mines, gas lines, etc) where the operator is not in control of contracts, supply lines, or delivery of fuels" | [8 empty] | AMP CODE: |  | NF
|  | DESCRIPTION : |  | FX00Fuel supply not available.
PR12 | 4 | U1 | 2014-02-19 10:25 |  |  |  |  | 2014-03-06 13:33 |  | 0 | 0 | 363.133 | 363.1333 | 10167.733 | 1 |  |  |  | 0 |  |  | 28
|  | CAUSE CODE : |  | 5170 |  |  | - |  | Cooling water system | [8 empty] | AMP CODE: |  | 69
|  | DESCRIPTION : |  | F690Fire pump that supplies cooling water locked up. Both the pump and motor were reb
PR12 | 6 | U1 | 2014-03-11 11:34 |  |  |  |  | 2014-03-12 10:22 |  | 0 | 0 | 22.8 | 22.8 | 638.4 | 1 |  |  |  | 0 |  |  | 25.5
|  | CAUSE CODE : |  | 5250 |  |  | - |  | Other controls and instrumentation problems | [8 empty] | AMP CODE: |  | 52
|  | DESCRIPTION : |  | F520The Active Speed Probe is having erratic readings.
PR12 | 11 | U1 | 2014-10-30 09:39 |  |  |  |  | 2014-10-30 10:14 |  | 0 | 0 | 0.583 | 0.5833 | 16.333 | 1 |  |  |  | 0 |  |  | 25.5
|  | CAUSE CODE : |  | 5108 |  |  | - |  | High engine exhaust temperature | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F750Exhaust gas temperature was high.
PR12 | 13 | U1 | 2014-11-14 08:15 |  |  |  |  | 2014-11-14 10:00 |  | 0 | 0 | 1.75 | 1.75 | 49 | 1 |  |  |  | 0 |  |  | 25.5
|  | CAUSE CODE : |  | 9130 |  |  | - |  | "Lack of fuel (water from rivers or lakes, coal mines, gas lines, etc) where the operator is not in control of contracts, supply lines, or delivery of fuels" | [8 empty] | AMP CODE: |  | X0
|  | DESCRIPTION : |  | FX00Gas supply unavailable.
PR12 | 15 | U1 | 2014-11-18 11:08 |  |  |  |  | 2014-11-18 11:26 |  | 0 | 0 | 0.3 | 0.3 | 8.4 | 1 |  |  |  | 0 |  |  | 25.5
|  | CAUSE CODE : |  | 5079 |  |  | - |  | Other combustor problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F780Two of the combustor thermocouples went out of range at the same time making unit
PR12 | 2 | U1 | 2015-01-07 04:00 |  |  |  |  | 2015-01-08 16:00 |  | 0 | 0 | 36 | 36 | 1008 | 1 |  |  |  | 0 |  |  | 28
|  | CAUSE CODE : |  | 9130 |  |  | - |  | "Lack of fuel (water from rivers or lakes, coal mines, gas lines, etc) where the operator is not in control of contracts, supply lines, or delivery of fuels" | [8 empty] | AMP CODE: |  | FR
|  | DESCRIPTION : |  | FX00Insufficient gas pressure.
PR12 | 4 | U1 | 2015-01-09 16:00 |  |  |  |  | 2015-01-10 22:15 |  | 0 | 0 | 30.25 | 30.25 | 847 | 1 |  |  |  | 0 |  |  | 28
|  | CAUSE CODE : |  | 9130 |  |  | - |  | "Lack of fuel (water from rivers or lakes, coal mines, gas lines, etc) where the operator is not in control of contracts, supply lines, or delivery of fuels" | [8 empty] | AMP CODE: |  | FR
|  | DESCRIPTION : |  | FX00Insufficient gas pressure.
PR12 | 6 | U1 | 2015-02-12 20:00 |  |  |  |  | 2015-02-13 10:00 |  | 0 | 0 | 14 | 14 | 392 | 1 |  |  |  | 0 |  |  | 28
|  | CAUSE CODE : |  | 9290 |  |  | - |  | Other fuel quality problems (OMC) | [8 empty] | AMP CODE: |  | 66
|  | DESCRIPTION : |  | F660Gas Pressure Problems.
PR12 | 8 | U1 | 2015-02-14 20:00 |  |  |  |  | 2015-02-21 20:10 |  | 0 | 0 | 168.167 | 168.1667 | 4708.667 | 1 |  |  |  | 0 |  |  | 28
|  | CAUSE CODE : |  | 9290 |  |  | - |  | Other fuel quality problems (OMC) | [8 empty] | AMP CODE: |  | 66
|  | DESCRIPTION : |  | F660Gas pressure problems.
PR12 | 10 | U1 | 2015-02-22 22:00 |  |  |  |  | 2015-02-24 12:00 |  | 0 | 0 | 38 | 38 | 1064 | 1 |  |  |  | 0 |  |  | 28
|  | CAUSE CODE : |  | 9290 |  |  | - |  | Other fuel quality problems (OMC) | [8 empty] | AMP CODE: |  | 66
|  | DESCRIPTION : |  | F660Gas pressure problems.
PR12 | 12 | U1 | 2015-02-26 22:00 |  |  |  |  | 2015-02-28 12:18 |  | 0 | 0 | 38.3 | 38.3 | 1072.4 | 1 |  |  |  | 0 |  |  | 28
|  | CAUSE CODE : |  | 9290 |  |  | - |  | Other fuel quality problems (OMC) | [8 empty] | AMP CODE: |  | 66
|  | DESCRIPTION : |  | F660Gas pressure problems.
PR12 | 14 | U1 | 2015-03-05 04:00 |  |  |  |  | 2015-03-06 16:08 |  | 0 | 0 | 36.133 | 36.1333 | 1011.733 | 1 |  |  |  | 0 |  |  | 25.5
|  | CAUSE CODE : |  | 9290 |  |  | - |  | Other fuel quality problems (OMC) | [8 empty] | AMP CODE: |  | 66
|  | DESCRIPTION : |  | F660Gas pressure problems.
PR12 | 16 | SF | 2015-03-11 12:18 |  |  |  |  | 2015-03-11 14:11 |  | 0 | 0 | 1.883 | 1.8833 | 52.733 | 1 |  |  |  | 0 |  |  | 25.5
|  | CAUSE CODE : |  | 5079 |  |  | - |  | Other combustor problems | [8 empty] | AMP CODE: |  | 52
|  | DESCRIPTION : |  | F520Thermocouple wiring was shorted together and causing false indication.
PR12 | 17 | U1 | 2015-03-11 14:15 |  |  |  |  | 2015-03-12 10:11 |  | 0 | 0 | 19.933 | 19.9333 | 558.133 | 1 |  |  |  | 0 |  |  | 25.5
|  | CAUSE CODE : |  | 5079 |  |  | - |  | Other combustor problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F520Thermocouple wiring was shorted together and causing false indication.
PR12 | 19 | U1 | 2015-05-15 11:56 |  |  |  |  | 2015-05-15 12:36 |  | 0 | 0 | 0.667 | 0.6667 | 15.333 | 1 |  |  |  | 0 |  |  | 25.5
|  | CAUSE CODE : |  | 5079 |  |  | - |  | Other combustor problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F740Combustor temperature went high due to loading of the turbine.
PR12 | 20 | U1 | 2015-05-15 13:53 |  |  |  |  | 2015-06-16 13:17 |  | 0 | 0 | 767.4 | 767.4 | 17650.2 | 1 |  |  |  | 0 |  |  | 25.5
|  | CAUSE CODE : |  | 5079 |  |  | - |  | Other combustor problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F780One of the combustor thermocouples well broke inside of the turbine and let all th
|  | CAUSE CODE: |  |  |  | 4640 | - |  | Seal oil system and seals | [8 empty] | AMP CODE: |  |  | 54
|  | DESCRIPTION: |  |  | F540The seal oil system pressure switch for the main pump failed and caused us to use
|  | CAUSE CODE: |  |  |  | 5210 | - |  | Intercoolers | [8 empty] | AMP CODE: |  |  | 54
|  | DESCRIPTION: |  |  | F540There was 2 broken bolts on the exhaust bearing cap causing a small oil leak which
PR12 | 21 | U1 | 2015-06-16 13:21 |  |  |  |  | 2015-06-16 13:57 |  | 0 | 0 | 0.6 | 0.6 | 13.8 | 1 |  |  |  | 0 |  |  | 23
|  | CAUSE CODE : |  | 5079 |  |  | - |  | Other combustor problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F410Thermocouple issue with wiring.
PR12 | 23 | U1 | 2015-07-16 09:58 |  |  |  |  | 2015-07-16 11:22 |  | 0 | 0 | 1.4 | 1.4 | 32.2 | 1 |  |  |  | 0 |  |  | 23
|  | CAUSE CODE : |  | 5048 |  |  | - |  | Gas fuel system including controls and instrumentation | [8 empty] | AMP CODE: |  | 09
|  | DESCRIPTION : |  | F090Incoming Gas Regulator was not working properly. Gas Department Calibrated Regula
PR12 | 1 | U1 | 2016-01-11 |  |  |  |  | 2016-01-11 13:20 |  | 0 | 0 | 13.333 | 13.3333 | 373.333 | 1 |  |  |  | 0 |  |  | 28
|  | CAUSE CODE : |  | 9131 |  |  | - |  | Lack of fuel (interruptible supply of fuel part of fuel contract) | [8 empty] | AMP CODE: |  | 66
|  | DESCRIPTION : |  | F660Lack of fuel supply from gas department.
PR12 | 3 | U1 | 2016-01-13 |  |  |  |  | 2016-01-13 11:52 |  | 0 | 0 | 11.867 | 11.8667 | 332.267 | 1 |  |  |  | 0 |  |  | 28
|  | CAUSE CODE : |  | 9131 |  |  | - |  | Lack of fuel (interruptible supply of fuel part of fuel contract) | [8 empty] | AMP CODE: |  | 66
|  | DESCRIPTION : |  | F660Low gas pressure from Gas Department
PR12 | 5 | U1 | 2016-01-18 |  |  |  |  | 2016-01-20 10:00 |  | 0 | 0 | 58 | 58 | 1624 | 1 |  |  |  | 0 |  |  | 28
|  | CAUSE CODE : |  | 9131 |  |  | - |  | Lack of fuel (interruptible supply of fuel part of fuel contract) | [8 empty] | AMP CODE: |  | 66
|  | DESCRIPTION : |  | F660Low gas pressure for gas department
PR12 | 7 | U1 | 2016-01-24 |  |  |  |  | 2016-01-24 17:00 |  | 0 | 0 | 17 | 17 | 476 | 1 |  |  |  | 0 |  |  | 28
|  | CAUSE CODE : |  | 9131 |  |  | - |  | Lack of fuel (interruptible supply of fuel part of fuel contract) | [8 empty] | AMP CODE: |  | 66
|  | DESCRIPTION : |  | F660Low gas pressure from Gas Department.
PR12 | 11 | U1 | 2016-02-09 07:30 |  |  |  |  | 2016-02-11 17:00 |  | 0 | 0 | 57.5 | 57.5 | 1610 | 1 |  |  |  | 0 |  |  | 28
|  | CAUSE CODE : |  | 9131 |  |  | - |  | Lack of fuel (interruptible supply of fuel part of fuel contract) | [8 empty] | AMP CODE: |  | 66
|  | DESCRIPTION : |  | F660Low Gas Pressure from Gas Dept.
PR12 | 13 | U1 | 2016-02-13 01:00 |  |  |  |  | 2016-02-15 10:13 |  | 0 | 0 | 57.217 | 57.2167 | 1602.067 | 1 |  |  |  | 0 |  |  | 28
|  | CAUSE CODE : |  | 9131 |  |  | - |  | Lack of fuel (interruptible supply of fuel part of fuel contract) | [8 empty] | AMP CODE: |  | 66
|  | DESCRIPTION : |  | F660Low gas Pressure from Gas Department
PR12 | 24 | U1 | 2016-06-14 13:08 |  |  |  |  | 2016-06-14 16:17 |  | 0 | 0 | 3.15 | 3.15 | 72.45 | 1 |  |  |  | 0 |  |  | 23
|  | CAUSE CODE : |  | 3864 |  |  | - |  | Fire protection system instrumentation and controls | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Unit Tripped due to Fire Pump being called upon for use in Switchyard which was a
PR12 | 32 | U1 | 2016-08-03 08:00 |  |  |  |  | 2016-08-03 13:59 |  | 0 | 0 | 5.983 | 5.9833 | 137.617 | 1 |  |  |  | 0 |  |  | 23
|  | CAUSE CODE : |  | 3619 |  |  | - |  | Other switchyard equipment - external (OMC) | [8 empty] | AMP CODE: |  | 93
|  | DESCRIPTION : |  | F930Emergency outage on 14KV bus due to faulty disconncets. Substation Maint. swapped
PR12 | 40 | U1 | 2016-12-13 15:05 |  |  |  |  | 2016-12-14 15:03 |  | 0 | 0 | 23.967 | 23.9667 | 671.067 | 1 |  |  |  | 0 |  |  | 28
|  | CAUSE CODE : |  | 5447 |  |  | - |  | Gas fuel system including controls and instrumentation | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F460Flameout during testing of new gas line due to dirty gas during startup.
PR12 | 3 | U1 | 2018-01-24 22:26 |  |  |  |  | 2018-01-25 08:31 |  | 0 | 0 | 10.083 | 10.0833 | 282.334 | 1 |  |  |  | 0 |  |  | 28
|  | CAUSE CODE : |  | 3821 |  |  | - |  | Closed cooling water piping | [8 empty] | AMP CODE: |  | 54
|  | DESCRIPTION : |  | F540Fire Pump Piping leaking. Had to turn off pump which made unit unavailabe while r
PR12 | 8 | U1 | 2018-05-30 10:54 |  |  |  |  | 2018-05-30 12:30 |  | 0 | 0 | 1.6 | 1.6 | 41.6 | 1 |  |  |  | 0 |  |  | 25.5
|  | CAUSE CODE : |  | 3611 |  |  | - |  | Switchyard circuit breakers - external (OMC) | [8 empty] | AMP CODE: |  | 70
|  | DESCRIPTION : |  | F700Switchyard PT Failure which tripped out the entire 14KV bus at Paddys Run.
PR12 | 10 | SF | 2018-06-07 10:00 |  |  |  |  | 2018-07-06 12:38 |  | 0 | 0 | 698.633 | 698.6333 | 16068.567 | 1 |  |  |  | 0 |  |  | 23
|  | CAUSE CODE : |  | 4810 |  |  | - |  | Generator output breaker | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Generator circuit breaker coil malfunction prevented synchronization
PR12 | 6 | U1 | 2019-09-11 05:55 |  |  |  |  | 2019-09-11 12:04 |  | 0 | 0 | 6.15 | 6.15 | 159.9 | 1 |  |  |  | 0 |  |  | 25.5
|  | CAUSE CODE : |  | 3600 |  |  | - |  | Switchyard transformers and associated cooling systems - external (OMC) | [8 empty] | AMP CODE: |  | 70
|  | DESCRIPTION : |  | F700Transformer 3 locked out and killed 14kv bus. Trip was due to faulty wiring to t
PR12 | 10 | SF | 2019-12-27 11:56 |  |  |  |  | 2019-12-27 16:04 |  | 0 | 0 | 4.133 | 4.1333 | 115.733 | 1 |  |  |  | 0 |  |  | 28
|  | CAUSE CODE : |  | 5530 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 57
|  | DESCRIPTION : |  | F340Torque converter fluid low, lost hydraulic pressure/torque. Subsequent restarts no
PR12 | 9 | U1 | 2020-10-30 09:24 |  |  |  |  | 2020-11-03 10:43 |  | 0 | 0 | 97.317 | 97.3167 | 2530.233 | 1 |  |  |  | 0 |  |  | 25.5
|  | CAUSE CODE : |  | 5206 |  |  | - |  | Clutch | [8 empty] | AMP CODE: |  | 06
|  | DESCRIPTION : |  | F060Starting diesel failure.
PR12 | 7 | U1 | 2021-07-15 16:19 |  |  |  |  | 2021-07-16 05:00 |  | 0 | 0 | 12.683 | 12.6833 | 291.717 | 1 |  |  |  | 0 |  |  | 23
|  | CAUSE CODE : |  | 4570 |  |  | - |  | Generator casing | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F500Generator cooling issues.
PR12 | 9 | U1 | 2021-07-19 12:00 |  |  |  |  | 2021-07-19 14:38 |  | 0 | 0 | 2.633 | 2.6333 | 60.567 | 1 |  |  |  | 0 |  |  | 23
|  | CAUSE CODE : |  | 4619 |  |  | - |  | Other hydrogen system problems | [8 empty] | AMP CODE: |  | 84
|  | DESCRIPTION : |  | F500Hydrogen supply issues
PR12 | 11 | U1 | 2021-07-20 10:30 |  |  |  |  | 2021-07-26 07:03 |  | 0 | 0 | 140.55 | 140.55 | 3232.65 | 1 |  |  |  | 0 |  |  | 23
|  | CAUSE CODE : |  | 4570 |  |  | - |  | Generator casing | [8 empty] | AMP CODE: |  | 84
|  | DESCRIPTION : |  | F500Leaking H2 from generator coolers
PR12 | 4 | U1 | 2022-05-17 05:42 |  |  |  |  | 2022-05-17 07:15 |  | 0 | 0 | 1.55 | 1.55 | 40.3 | 1 |  |  |  | 0 |  |  | 25.5
|  | CAUSE CODE : |  | 3671 |  |  | - |  | 12-15kV circuit breakers | [8 empty] | AMP CODE:
|  | DESCRIPTION : |  | F82014kv breaker failure killed aux power to unit.
PR12 | 10 | U1 | 2022-12-29 21:55 |  |  |  |  | 2022-12-30 11:38 |  | 0 | 0 | 13.717 | 13.7167 | 384.066 | 1 |  |  |  | 0 |  |  | 28
|  | CAUSE CODE : |  | 3872 |  |  | - |  | Fuel Gas Compressor Valves | [8 empty] | AMP CODE: |  | FR
|  | DESCRIPTION : |  | F130Loss of gas psi. Slam shut valve tripped.
PR12 | 6 | SF | 2023-06-06 08:27 |  |  |  |  | 2023-07-28 13:30 |  | 0 | 0 | 1253.05 | 1253.05 | 28820.15 | 1 |  |  |  | 0 |  |  | 23
|  | CAUSE CODE : |  | 5606 |  |  | - |  | Clutch | [8 empty] | AMP CODE: |  | 06
|  | DESCRIPTION : |  | F060Torque converter failure.
PR12 | 8 | U1 | 2023-12-07 10:30 |  |  |  |  | 2024-01-01 |  | 0 | 0 | 589.5 | 589.5 | 16506 | 1 |  |  |  | 0 |  |  | 28
|  | CAUSE CODE : |  | 5150 |  |  | - |  | Turning gear and motor | [8 empty] | AMP CODE: |  | 06
|  | DESCRIPTION : |  | F060Starting diesel failure
Paddy's Run - PR13
Unit | Event | Type | Start |  |  |  |  | End |  | GAC | NAC | Duration | Equiv Hrs | Equiv MWH | Cont | Work Start | Work End |  | Hours |  |  | Gross Capacity Impact (MW)
PR13 | 2 | U1 | 2014-01-30 07:00 |  |  |  |  | 2014-01-31 09:20 |  | 0 | 0 | 26.333 | 26.3333 | 4608.333 | 1 |  |  |  | 0 |  |  | 176
|  | CAUSE CODE : |  | 9130 |  |  | - |  | "Lack of fuel (water from rivers or lakes, coal mines, gas lines, etc) where the operator is not in control of contracts, supply lines, or delivery of fuels" | [8 empty] | AMP CODE: |  | NF
|  | DESCRIPTION : |  | FX00Fuel supply not available.
PR13 | 5 | U1 | 2014-03-03 08:25 |  |  |  |  | 2014-03-06 13:33 |  | 0 | 0 | 77.133 | 77.1333 | 13498.333 | 1 |  |  |  | 0 |  |  | 162
|  | CAUSE CODE : |  | 3860 |  |  | - |  | Fire protection system pumps | [8 empty] | AMP CODE: |  | 69
|  | DESCRIPTION : |  | F690GSU and aux transformer fire pump is seized up. Both the pump and motor were rebu
PR13 | 11 | SF | 2014-03-25 05:45 |  |  |  |  | 2014-03-25 06:24 |  | 0 | 0 | 0.65 | 0.65 | 113.75 | 1 |  |  |  | 0 |  |  | 162
|  | CAUSE CODE : |  | 4610 |  |  | - |  | Hydrogen cooling system piping and valves | [8 empty] | AMP CODE: |  | 48
|  | DESCRIPTION : |  | F480Hydrogen fill valve was frozen and would not open when needed.
PR13 | 13 | U1 | 2014-04-03 07:18 |  |  |  |  | 2014-04-03 08:38 |  | 0 | 0 | 1.333 | 1.3333 | 196 | 1 |  |  |  | 0 |  |  | 162
|  | CAUSE CODE : |  | 9997 |  |  | - |  | NERC Reliability Standard Requirement | [8 empty] | AMP CODE: |  | 52
|  | DESCRIPTION : |  | F520Sec A is having a bus outage and that is the only spot we get bus voltage informat
PR13 | 19 | U1 | 2014-04-08 10:29 |  |  |  |  | 2014-04-08 11:48 |  | 0 | 0 | 1.317 | 1.3167 | 193.55 | 1 |  |  |  | 0 |  |  | 162
|  | CAUSE CODE : |  | 3872 |  |  | - |  | Fuel Gas Compressor Valves | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F600The solenoid valve for the gas compressor discharged block valve failed. It is en
PR13 | 42 | SF | 2014-05-13 11:32 |  |  |  |  | 2014-05-13 12:47 |  | 0 | 0 | 1.25 | 1.25 | 183.75 | 1 |  |  |  | 0 |  |  | 162
|  | CAUSE CODE : |  | 3621 |  |  | - |  | Unit auxiliaries transformer | [8 empty] | AMP CODE: |  | 52
|  | DESCRIPTION : |  | F520Transformer fault lockout due to relay false indication.
PR13 | 52 | U1 | 2014-06-17 17:50 |  |  |  |  | 2014-06-17 18:36 |  | 0 | 0 | 0.767 | 0.7667 | 112.7 | 1 |  |  |  | 0 |  |  | 148
|  | CAUSE CODE : |  | 5029 |  |  | - |  | Other low pressure problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Trip due to low gas pressure supply. Cleared alarms, reset and restarted unit.
PR13 | 55 | U1 | 2014-06-19 05:33 |  |  |  |  | 2014-06-19 06:39 |  | 0 | 0 | 1.1 | 1.1 | 161.7 | 1 |  |  |  | 0 |  |  | 148
|  | CAUSE CODE : |  | 3899 |  |  | - |  | Other miscellaneous auxiliary system problems | [8 empty] | AMP CODE: |  | 40
|  | DESCRIPTION : |  | F400No ready to start light due to glycol pump tripped out. Reset trip making unit av
PR13 | 57 | U1 | 2014-06-19 21:01 |  |  |  |  | 2014-06-19 21:16 |  | 0 | 0 | 0.25 | 0.25 | 36.75 | 1 |  |  |  | 0 |  |  | 148
|  | CAUSE CODE : |  | 5029 |  |  | - |  | Other low pressure problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Unit trip due to low gas pressure.
PR13 | 81 | U1 | 2014-09-29 19:05 |  |  |  |  | 2014-09-29 22:48 |  | 0 | 0 | 3.717 | 3.7167 | 546.35 | 1 |  |  |  | 0 |  |  | 162
|  | CAUSE CODE : |  | 3621 |  |  | - |  | Unit auxiliaries transformer | [8 empty] | AMP CODE: |  | 70
|  | DESCRIPTION : |  | F820Auxilliary transformer lock out. Closed in backup feed making unit available.
PR13 | 83 | U1 | 2014-09-29 22:48 |  |  |  |  | 2014-09-30 17:54 |  | 0 | 0 | 19.1 | 19.1 | 2807.7 | 1 |  |  |  | 0 |  |  | 162
|  | CAUSE CODE : |  | 3621 |  |  | - |  | Unit auxiliaries transformer | [8 empty] | AMP CODE: |  | 70
|  | DESCRIPTION : |  | F820Auxilliary transformer lockout & backup feed not large enough causing loss of elec
PR13 | 91 | U1 | 2014-11-13 19:52 |  |  |  |  | 2014-11-13 20:24 |  | 0 | 0 | 0.533 | 0.5333 | 93.333 | 1 |  |  |  | 0 |  |  | 162
|  | CAUSE CODE : |  | 5049 |  |  | - |  | Other fuel system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | FX00High gas prressure trip due to gas supply from outside the unit.
PR13 | 93 | U1 | 2014-11-14 07:23 |  |  |  |  | 2014-11-14 10:00 |  | 0 | 0 | 2.617 | 2.6167 | 457.917 | 1 |  |  |  | 0 |  |  | 162
|  | CAUSE CODE : |  | 9130 |  |  | - |  | "Lack of fuel (water from rivers or lakes, coal mines, gas lines, etc) where the operator is not in control of contracts, supply lines, or delivery of fuels" | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | FX00Gas supply unavailable.
PR13 | 2 | U1 | 2015-01-07 04:00 |  |  |  |  | 2015-01-08 16:00 |  | 0 | 0 | 36 | 36 | 6300 | 1 |  |  |  | 0 |  |  | 176
|  | CAUSE CODE : |  | 9130 |  |  | - |  | "Lack of fuel (water from rivers or lakes, coal mines, gas lines, etc) where the operator is not in control of contracts, supply lines, or delivery of fuels" | [8 empty] | AMP CODE: |  | FR
|  | DESCRIPTION : |  | FX00Insufficient gas pressure.
PR13 | 4 | U1 | 2015-01-09 16:00 |  |  |  |  | 2015-01-10 22:15 |  | 0 | 0 | 30.25 | 30.25 | 5293.75 | 1 |  |  |  | 0 |  |  | 176
|  | CAUSE CODE : |  | 9130 |  |  | - |  | "Lack of fuel (water from rivers or lakes, coal mines, gas lines, etc) where the operator is not in control of contracts, supply lines, or delivery of fuels" | [8 empty] | AMP CODE: |  | FR
|  | DESCRIPTION : |  | FX00Insufficient gas pressure.
PR13 | 6 | SF | 2015-01-28 10:00 |  |  |  |  | 2015-01-28 14:22 |  | 0 | 0 | 4.367 | 4.3667 | 764.167 | 1 |  |  |  | 0 |  |  | 176
|  | CAUSE CODE : |  | 4535 |  |  | - |  | "Stator, General" | [8 empty] | AMP CODE: |  | 78
|  | DESCRIPTION : |  | F780The unit's cold gas temp dropped below 32 degrees which is the trip point.
PR13 | 8 | U1 | 2015-02-12 20:00 |  |  |  |  | 2015-02-13 10:00 |  | 0 | 0 | 14 | 14 | 2450 | 1 |  |  |  | 0 |  |  | 176
|  | CAUSE CODE : |  | 9290 |  |  | - |  | Other fuel quality problems (OMC) | [8 empty] | AMP CODE: |  | 66
|  | DESCRIPTION : |  | F660Gas pressure problems.
PR13 | 10 | U1 | 2015-02-14 20:00 |  |  |  |  | 2015-02-21 |  | 0 | 0 | 148 | 148 | 25900 | 1 |  |  |  | 0 |  |  | 176
|  | CAUSE CODE : |  | 9290 |  |  | - |  | Other fuel quality problems (OMC) | [8 empty] | AMP CODE: |  | 66
|  | DESCRIPTION : |  | F660Gas pressure problems.
PR13 | 16 | U1 | 2015-03-23 03:58 |  |  |  |  | 2015-03-23 06:28 |  | 0 | 0 | 2.5 | 2.5 | 437.5 | 1 |  |  |  | 0 |  |  | 162
|  | CAUSE CODE : |  | 5246 |  |  | - |  | Gas Turbine Control System - hardware problems (including card failure) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F520The I/O rack back plane failed causing numerious false readings once unit was on l
PR13 | 25 | U1 | 2015-03-30 09:50 |  |  |  |  | 2015-03-30 10:14 |  | 0 | 0 | 0.4 | 0.4 | 70 | 1 |  |  |  | 0 |  |  | 162
|  | CAUSE CODE : |  | 9290 |  |  | - |  | Other fuel quality problems (OMC) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F660High gas pressure.
PR13 | 27 | U1 | 2015-03-30 10:17 |  |  |  |  | 2015-03-30 10:55 |  | 0 | 0 | 0.633 | 0.6333 | 110.833 | 1 |  |  |  | 0 |  |  | 162
|  | CAUSE CODE : |  | 5017 |  |  | - |  | Low pressure compressor bleed valves | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F720Valve issue.
PR13 | 45 | U1 | 2015-04-06 06:27 |  |  |  |  | 2015-04-06 06:43 |  | 0 | 0 | 0.267 | 0.2667 | 39.2 | 1 |  |  |  | 0 |  |  | 162
|  | CAUSE CODE : |  | 4620 |  |  | - |  | Air cooling system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Air control valves timed out shortly after unit came on line.
PR13 | 54 | U1 | 2015-04-09 06:56 |  |  |  |  | 2015-04-09 10:42 |  | 0 | 0 | 3.767 | 3.7667 | 553.7 | 1 |  |  |  | 0 |  |  | 162
|  | CAUSE CODE : |  | 5017 |  |  | - |  | Low pressure compressor bleed valves | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F720Compressor blowoff valve problems.
PR13 | 57 | U1 | 2015-04-09 12:18 |  |  |  |  | 2015-04-09 13:16 |  | 0 | 0 | 0.967 | 0.9667 | 142.1 | 1 |  |  |  | 0 |  |  | 162
|  | CAUSE CODE : |  | 5041 |  |  | - |  | Fuel piping and valves | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F660Gas valve problems.
PR13 | 96 | U1 | 2015-05-16 13:18 |  |  |  |  | 2015-05-16 13:42 |  | 0 | 0 | 0.4 | 0.4 | 58.8 | 1 |  |  |  | 0 |  |  | 162
|  | CAUSE CODE : |  | 9290 |  |  | - |  | Other fuel quality problems (OMC) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F660High gas pressure.
PR13 | 153 | SF | 2015-10-23 07:02 |  |  |  |  | 2015-10-23 07:23 |  | 0 | 0 | 0.35 | 0.35 | 61.25 | 1 |  |  |  | 0 |  |  | 162
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 33
|  | DESCRIPTION : |  | F330SFC disconnect did not open in allowed time period which caused SFC Lockout and Tr
PR13 | 155 | SF | 2015-10-24 07:27 |  |  |  |  | 2015-10-24 07:39 |  | 0 | 0 | 0.2 | 0.2 | 35 | 1 |  |  |  | 0 |  |  | 162
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 33
|  | DESCRIPTION : |  | F330SFC disconnect did not open in allowed time period Causing and SFC Lockout and uni
PR13 | 156 | U1 | 2015-10-24 07:42 |  |  |  |  | 2015-10-24 08:57 |  | 0 | 0 | 1.25 | 1.25 | 218.75 | 1 |  |  |  | 0 |  |  | 162
|  | CAUSE CODE : |  | 5016 |  |  | - |  | High pressure compressor bleed valves | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Compressor Blowoff valve 1.2 had a false reading and caused the unit to unload and
PR13 | 161 | SF | 2015-10-26 05:16 |  |  |  |  | 2015-10-26 06:09 |  | 0 | 0 | 0.883 | 0.8833 | 154.583 | 1 |  |  |  | 0 |  |  | 162
|  | CAUSE CODE : |  | 3661 |  |  | - |  | 4000-7000 volt circuit breakers | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340Excitation Breaker Failed to close. Misalignment of the breaker arms caused the b
PR13 | 163 | U1 | 2015-10-28 19:19 |  |  |  |  | 2015-10-29 07:45 |  | 0 | 0 | 12.433 | 12.4333 | 2175.833 | 1 |  |  |  | 0 |  |  | 162
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820SFC tripped and found bad indication in the SES Breaker.
PR13 | 164 | U1 | 2015-10-29 08:00 |  |  |  |  | 2015-10-29 08:49 |  | 0 | 0 | 0.817 | 0.8167 | 142.917 | 1 |  |  |  | 0 |  |  | 162
|  | CAUSE CODE : |  | 3870 |  |  | - |  | Fuel Gas Compressor and Motors | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Low LP seal pressure on the Gas Compressor. Adjust valves to proper level.
PR13 | 166 | SF | 2015-10-31 06:00 |  |  |  |  | 2015-10-31 08:37 |  | 0 | 0 | 2.617 | 2.6167 | 457.917 | 1 |  |  |  | 0 |  |  | 162
|  | CAUSE CODE : |  | 4609 |  |  | - |  | Other exciter problems | [8 empty] | AMP CODE: |  | 52
|  | DESCRIPTION : |  | F520Field Breaker was given false indication on breaker position.
PR13 | 167 | U1 | 2015-10-31 08:40 |  |  |  |  | 2015-10-31 09:12 |  | 0 | 0 | 0.533 | 0.5333 | 93.333 | 1 |  |  |  | 0 |  |  | 162
|  | CAUSE CODE : |  | 5016 |  |  | - |  | High pressure compressor bleed valves | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Blow off valve 3.0 showing improper indication.
PR13 | 171 | U1 | 2015-11-02 05:48 |  |  |  |  | 2015-11-02 06:15 |  | 0 | 0 | 0.45 | 0.45 | 78.75 | 1 |  |  |  | 0 |  |  | 162
|  | CAUSE CODE : |  | 3972 |  |  | - |  | DCS - hardware problems (including card failure) | [8 empty] | AMP CODE: |  | 60
|  | DESCRIPTION : |  | F600DCS AI card failed. Replaced Card.
PR13 | 175 | U1 | 2015-11-03 20:55 |  |  |  |  | 2015-11-03 21:16 |  | 0 | 0 | 0.35 | 0.35 | 61.25 | 1 |  |  |  | 0 |  |  | 162
|  | CAUSE CODE : |  | 5049 |  |  | - |  | Other fuel system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Gas pressure spiked while unit was unloading and being removed offline.
PR13 | 178 | U1 | 2015-11-05 21:44 |  |  |  |  | 2015-11-05 21:55 |  | 0 | 0 | 0.183 | 0.1833 | 32.083 | 1 |  |  |  | 0 |  |  | 162
|  | CAUSE CODE : |  | 3870 |  |  | - |  | Fuel Gas Compressor and Motors | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Gas compressor tripped on High Vibration during unload.
PR13 | 180 | U1 | 2015-11-06 21:19 |  |  |  |  | 2015-11-06 21:30 |  | 0 | 0 | 0.183 | 0.1833 | 32.083 | 1 |  |  |  | 0 |  |  | 162
|  | CAUSE CODE : |  | 3870 |  |  | - |  | Fuel Gas Compressor and Motors | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Gas Compressor tripped on High Vibration
PR13 | 185 | U1 | 2015-11-11 07:26 |  |  |  |  | 2015-11-17 15:50 |  | 0 | 0 | 152.4 | 152.4 | 26670 | 1 |  |  |  | 0 |  |  | 162
|  | CAUSE CODE : |  | 5447 |  |  | - |  | Gas fuel system including controls and instrumentation | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Gas compressor trip due to vibration and we had a gas line rupture. Staying on ou
PR13 | 186 | U1 | 2015-11-17 16:30 |  |  |  |  | 2015-11-19 12:16 |  | 0 | 0 | 43.767 | 43.7667 | 7659.167 | 1 |  |  |  | 0 |  |  | 162
|  | CAUSE CODE : |  | 5447 |  |  | - |  | Gas fuel system including controls and instrumentation | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820On line test for service guy to see the exact issue we are having with the compres
PR13 | 187 | U1 | 2015-11-19 13:06 |  |  |  |  | 2015-11-20 11:03 |  | 0 | 0 | 21.95 | 21.95 | 3841.25 | 1 |  |  |  | 0 |  |  | 162
|  | CAUSE CODE : |  | 5447 |  |  | - |  | Gas fuel system including controls and instrumentation | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Replace a PLC card and tried operation again. On line test and Failed coming offl
PR13 | 188 | U1 | 2015-11-20 11:22 |  |  |  |  | 2015-11-20 12:00 |  | 0 | 0 | 0.633 | 0.6333 | 110.833 | 1 |  |  |  | 0 |  |  | 162
|  | CAUSE CODE : |  | 5447 |  |  | - |  | Gas fuel system including controls and instrumentation | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Replace another PLC card. Online test and still tripping while coming offline.
PR13 | 190 | U1 | 2015-11-23 03:03 |  |  |  |  | 2015-11-25 14:40 |  | 0 | 0 | 59.617 | 59.6167 | 10432.917 | 1 |  |  |  | 0 |  |  | 162
|  | CAUSE CODE : |  | 5447 |  |  | - |  | Gas fuel system including controls and instrumentation | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Gas compressor tripped due to high Vibration while unit was at full Load. Investi
PR13 | 1 | U1 | 2016-01-11 |  |  |  |  | 2016-01-11 13:20 |  | 0 | 0 | 13.333 | 13.3333 | 2333.333 | 1 |  |  |  | 0 |  |  | 176
|  | CAUSE CODE : |  | 9131 |  |  | - |  | Lack of fuel (interruptible supply of fuel part of fuel contract) | [8 empty] | AMP CODE: |  | 66
|  | DESCRIPTION : |  | F660Lack of Gas Pressure from Gas department.
PR13 | 3 | U1 | 2016-01-13 |  |  |  |  | 2016-01-13 11:52 |  | 0 | 0 | 11.867 | 11.8667 | 2076.667 | 1 |  |  |  | 0 |  |  | 176
|  | CAUSE CODE : |  | 9131 |  |  | - |  | Lack of fuel (interruptible supply of fuel part of fuel contract) | [8 empty] | AMP CODE: |  | 66
|  | DESCRIPTION : |  | F660No gas pressure from Gas Department
PR13 | 5 | U1 | 2016-01-18 |  |  |  |  | 2016-01-20 10:00 |  | 0 | 0 | 58 | 58 | 10150 | 1 |  |  |  | 0 |  |  | 176
|  | CAUSE CODE : |  | 9131 |  |  | - |  | Lack of fuel (interruptible supply of fuel part of fuel contract) | [8 empty] | AMP CODE: |  | 66
|  | DESCRIPTION : |  | F660Low gas pressure from Gas Department.
PR13 | 7 | U1 | 2016-01-24 |  |  |  |  | 2016-01-24 17:00 |  | 0 | 0 | 17 | 17 | 2975 | 1 |  |  |  | 0 |  |  | 176
|  | CAUSE CODE : |  | 9131 |  |  | - |  | Lack of fuel (interruptible supply of fuel part of fuel contract) | [8 empty] | AMP CODE: |  | 66
|  | DESCRIPTION : |  | F660Low gas pressure from Gas Department.
PR13 | 11 | U1 | 2016-02-09 07:30 |  |  |  |  | 2016-02-11 17:00 |  | 0 | 0 | 57.5 | 57.5 | 10062.5 | 1 |  |  |  | 0 |  |  | 176
|  | CAUSE CODE : |  | 9131 |  |  | - |  | Lack of fuel (interruptible supply of fuel part of fuel contract) | [8 empty] | AMP CODE: |  | 66
|  | DESCRIPTION : |  | F660Low Gas Pressure from Gas Dept.
PR13 | 13 | U1 | 2016-02-13 01:00 |  |  |  |  | 2016-02-15 10:13 |  | 0 | 0 | 57.217 | 57.2167 | 10012.917 | 1 |  |  |  | 0 |  |  | 176
|  | CAUSE CODE : |  | 9131 |  |  | - |  | Lack of fuel (interruptible supply of fuel part of fuel contract) | [8 empty] | AMP CODE: |  | 66
|  | DESCRIPTION : |  | F660Low Gas pressure from Gas Department.
PR13 | 20 | SF | 2016-03-09 06:55 |  |  |  |  | 2016-04-21 12:55 |  | 0 | 0 | 1038 | 1038 | 167118 | 1 |  |  |  | 0 |  |  | 162
|  | CAUSE CODE : |  | 5120 |  |  | - |  | Hydraulic oil system | [8 empty] | AMP CODE: |  | 52
|  | DESCRIPTION : |  | F520Hydarulic System Pressure Switch Failure.
PR13 | 62 | SF | 2016-07-13 11:36 |  |  |  |  | 2016-07-13 16:28 |  | 0 | 0 | 4.867 | 4.8667 | 715.4 | 1 |  |  |  | 0 |  |  | 148
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 33
|  | DESCRIPTION : |  | F330SFC disconnect failed to operate due to busted sheer pin.
PR13 | 77 | U1 | 2016-08-11 10:53 |  |  |  |  | 2016-08-11 11:06 |  | 0 | 0 | 0.217 | 0.2167 | 31.85 | 1 |  |  |  | 0 |  |  | 148
|  | CAUSE CODE : |  | 5016 |  |  | - |  | High pressure compressor bleed valves | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Compressor blowoff valve 2 didnt not show full closed indication.
PR13 | 115 | U1 | 2016-11-30 13:57 |  |  |  |  | 2016-12-01 02:15 |  | 0 | 0 | 12.3 | 12.3 | 2011.8 | 1 |  |  |  | 0 |  |  | 162
|  | CAUSE CODE : |  | 3612 |  |  | - |  | Switchyard system protection devices - external (OMC) | [8 empty] | AMP CODE: |  | 70
|  | DESCRIPTION : |  | F700Shorted PT on the 14KV aux for the Unit.
PR13 | 117 | SF | 2016-12-02 05:34 |  |  |  |  | 2016-12-02 09:43 |  | 0 | 0 | 4.15 | 4.15 | 726.25 | 1 |  |  |  | 0 |  |  | 176
|  | CAUSE CODE : |  | 3970 |  |  | - |  | Distributive Control System (DCS) - process computer | [8 empty] | AMP CODE: |  | 40
|  | DESCRIPTION : |  | F400Unit shutting down during startup for unexplained reasons.
PR13 | 1 | U1 | 2017-01-03 08:50 |  |  |  |  | 2017-01-04 16:38 |  | 0 | 0 | 31.8 | 31.8 | 5565 | 1 |  |  |  | 0 |  |  | 176
|  | CAUSE CODE : |  | 4640 |  |  | - |  | Seal oil system and seals | [8 empty] | AMP CODE: |  | 66
|  | DESCRIPTION : |  | F660Seal Oil Vacuum Pump Failure.
PR13 | 3 | U1 | 2017-01-05 10:45 |  |  |  |  | 2017-01-05 12:57 |  | 0 | 0 | 2.2 | 2.2 | 385 | 1 |  |  |  | 0 |  |  | 176
|  | CAUSE CODE : |  | 4610 |  |  | - |  | Hydrogen cooling system piping and valves | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Units Cold Gas Temp reached below minimum temp and tripped the unit. We adjusted
PR13 | 9 | U1 | 2017-01-26 13:19 |  |  |  |  | 2017-01-26 14:22 |  | 0 | 0 | 1.05 | 1.05 | 183.75 | 1 |  |  |  | 0 |  |  | 176
|  | CAUSE CODE : |  | 5447 |  |  | - |  | Gas fuel system including controls and instrumentation | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F780Incoming gas temp was low cause combustion dynamics issues.
PR13 | 12 | U1 | 2017-01-28 05:47 |  |  |  |  | 2017-01-28 10:09 |  | 0 | 0 | 4.367 | 4.3667 | 764.167 | 1 |  |  |  | 0 |  |  | 176
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 06
|  | DESCRIPTION : |  | F060SFC disconnect motor broke. Swapped with spare.
PR13 | 21 | U1 | 2017-04-12 12:16 |  |  |  |  | 2017-04-12 13:34 |  | 0 | 0 | 1.3 | 1.3 | 209.3 | 1 |  |  |  | 0 |  |  | 162
|  | CAUSE CODE : |  | 5449 |  |  | - |  | Other fuel system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Incoming gas line tempature low causing combustion issues.
PR13 | 60 | U1 | 2017-09-21 12:26 |  |  |  |  | 2017-09-21 13:34 |  | 0 | 0 | 1.133 | 1.1333 | 182.467 | 1 |  |  |  | 0 |  |  | 162
|  | CAUSE CODE : |  | 5108 |  |  | - |  | High engine exhaust temperature | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Turbine Exhaust temp unload and trip due to faulty readings on Thermocouple #115.
PR13 | 63 | U1 | 2017-09-27 13:20 |  |  |  |  | 2017-09-27 14:28 |  | 0 | 0 | 1.133 | 1.1333 | 182.467 | 1 |  |  |  | 0 |  |  | 162
|  | CAUSE CODE : |  | 3972 |  |  | - |  | DCS - hardware problems (including card failure) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Lost CPA22 Cabinet DA row of control cards. Back Plan failure. Replaced back pla
PR13 | 66 | U1 | 2017-10-23 08:42 |  |  |  |  | 2017-10-23 09:56 |  | 0 | 0 | 1.233 | 1.2333 | 198.567 | 1 |  |  |  | 0 |  |  | 162
|  | CAUSE CODE : |  | 5479 |  |  | - |  | Other combustor problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Exhaust temps spread.
PR13 | 68 | U1 | 2017-10-25 05:03 |  |  |  |  | 2017-10-26 13:24 |  | 0 | 0 | 32.35 | 32.35 | 5208.35 | 1 |  |  |  | 0 |  |  | 162
|  | CAUSE CODE : |  | 4619 |  |  | - |  | Other hydrogen system problems | [8 empty] | AMP CODE: |  | 52
|  | DESCRIPTION : |  | F520Hydrogen Purity meter failed. Showing bad Hydrogen, ended up being bad readings o
PR13 | 88 | SF | 2017-12-27 05:33 |  |  |  |  | 2017-12-27 05:44 |  | 0 | 0 | 0.183 | 0.1833 | 32.083 | 1 |  |  |  | 0 |  |  | 176
|  | CAUSE CODE : |  | 4570 |  |  | - |  | Generator casing | [8 empty] | AMP CODE: |  | 66
|  | DESCRIPTION : |  | F660Generator Hydrogen Pressure dropped below limits on startup.
PR13 | 39 | U1 | 2018-06-20 06:18 |  |  |  |  | 2018-06-20 09:42 |  | 0 | 0 | 3.4 | 3.4 | 499.8 | 1 |  |  |  | 0 |  |  | 148
|  | CAUSE CODE : |  | 4640 |  |  | - |  | Seal oil system and seals | [8 empty] | AMP CODE: |  | 66
|  | DESCRIPTION : |  | F660Seal Oil Vacuum Pump Failure.
PR13 | 12 | U1 | 2019-04-04 18:51 |  |  |  |  | 2019-04-04 21:53 |  | 0 | 0 | 3.033 | 3.0333 | 488.367 | 1 |  |  |  | 0 |  |  | 162
|  | CAUSE CODE : |  | 3611 |  |  | - |  | Switchyard circuit breakers - external (OMC) | [8 empty] | AMP CODE: |  | 70
|  | DESCRIPTION : |  | F700Substations had a Transformer Fire which tripped the Aux Feed for PR13. After ins
PR13 | 14 | U1 | 2019-04-11 06:00 |  |  |  |  | 2019-04-11 07:00 |  | 0 | 0 | 1 | 1 | 161 | 1 |  |  |  | 0 |  |  | 162
|  | CAUSE CODE : |  | 3972 |  |  | - |  | DCS - hardware problems (including card failure) | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Reset Faulty rack and cleared all alarms and communitcations failures.
PR13 | 23 | U1 | 2019-05-28 17:00 |  |  |  |  | 2019-06-10 07:32 |  | 0 | 0 | 302.533 | 302.5333 | 45578.4 | 1 |  |  |  | 0 |  |  | 162
|  | CAUSE CODE : |  | 4551 |  |  | - |  | Generator bearings | [8 empty] | AMP CODE: |  | 93
|  | DESCRIPTION : |  | F930During Reassembly of the unit we had to roll out bearings for troubleshooting purp
PR13 | 25 | U1 | 2019-06-13 13:02 |  |  |  |  | 2019-06-14 08:56 |  | 0 | 0 | 19.9 | 19.9 | 2925.3 | 1 |  |  |  | 0 |  |  | 148
|  | CAUSE CODE : |  | 3624 |  |  | - |  | Auxiliary generator voltage supply system | [8 empty] | AMP CODE: |  | 09
|  | DESCRIPTION : |  | F090Bus Voltage Telemetry Off.
PR13 | 36 | U1 | 2019-07-28 15:04 |  |  |  |  | 2019-07-28 15:49 |  | 0 | 0 | 0.75 | 0.75 | 110.25 | 1 |  |  |  | 0 |  |  | 148
|  | CAUSE CODE : |  | 4611 |  |  | - |  | Hydrogen coolers | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F520Generator Cold Gas Temp Thermocouples reading became irratic. Swapped to spare.
PR13 | 47 | SF | 2019-09-13 11:29 |  |  |  |  | 2019-09-13 14:41 |  | 0 | 0 | 3.2 | 3.2 | 515.2 | 1 |  |  |  | 0 |  |  | 162
|  | CAUSE CODE : |  | 3661 |  |  | - |  | 4000-7000 volt circuit breakers | [8 empty] | AMP CODE: |  | 06
|  | DESCRIPTION : |  | F060Excitation Breaker Aux Contact Broken Linkage.
PR13 | 65 | SF | 2019-11-08 04:28 |  |  |  |  | 2019-11-08 12:15 |  | 0 | 0 | 7.783 | 7.7833 | 1253.117 | 1 |  |  |  | 0 |  |  | 162
|  | CAUSE CODE : |  | 5016 |  |  | - |  | High pressure compressor bleed valves | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340Compressor blowoof (bleed) valve 13MBA44AA051 Blowoff valve #3 solenoid valve fail
PR13 | 23 | SF | 2020-07-08 10:55 |  |  |  |  | 2020-07-09 08:59 |  | 0 | 0 | 22.067 | 22.0667 | 3243.8 | 1 |  |  |  | 0 |  |  | 148
|  | CAUSE CODE : |  | 3974 |  |  | - |  | DCS - logic problems | [8 empty] | AMP CODE: |  | 66
|  | DESCRIPTION : |  | F610Recalibrated compressor inlet pressure switches. Compressor Surge protection DCS p
PR13 | 43 | U1 | 2020-12-01 12:15 |  |  |  |  | 2020-12-01 14:04 |  | 0 | 0 | 1.817 | 1.8167 | 317.917 | 1 |  |  |  | 0 |  |  | 176
|  | CAUSE CODE : |  | 4620 |  |  | - |  | Air cooling system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Cooling Air Valve #3 failure
PR13 | 48 | U1 | 2020-12-20 18:07 |  |  |  |  | 2020-12-21 22:57 |  | 0 | 0 | 28.833 | 28.8333 | 5045.833 | 1 |  |  |  | 0 |  |  | 176
|  | CAUSE CODE : |  | 4511 |  |  | - |  | "Rotor, General" | [8 empty] | AMP CODE: |  | 69
|  | DESCRIPTION : |  | F840Investigating turning gear issues.
PR13 | 4 | SF | 2021-01-29 05:40 |  |  |  |  | 2021-01-29 15:14 |  | 0 | 0 | 9.567 | 9.5667 | 1674.167 | 1 |  |  |  | 0 |  |  | 176
|  | CAUSE CODE : |  | 3644 |  |  | - |  | AC Protection devices | [8 empty] | AMP CODE: |  | 09
|  | DESCRIPTION : |  | F090Trouble with Pilot Gas control valve
PR13 | 42 | U1 | 2021-11-03 13:34 |  |  |  |  | 2021-11-03 14:15 |  | 0 | 0 | 0.683 | 0.6833 | 110.017 | 1 |  |  |  | 0 |  |  | 162
|  | CAUSE CODE : |  | 5016 |  |  | - |  | High pressure compressor bleed valves | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F820Compressor blow off valve operated online. Bad limit switches. Changed switches
PR13 | 55 | U1 | 2021-12-05 13:23 |  |  |  |  | 2021-12-12 13:30 |  | 0 | 0 | 168.117 | 168.1167 | 29420.417 | 1 |  |  |  | 0 |  |  | 176
|  | CAUSE CODE : |  | 3644 |  |  | - |  | AC Protection devices | [8 empty] | AMP CODE: |  | 84
|  | DESCRIPTION : |  | F490Possible bad PT fuses
PR13 | 7 | U1 | 2022-01-17 06:57 |  |  |  |  | 2022-01-17 14:08 |  | 0 | 0 | 7.183 | 7.1833 | 1257.083 | 1 |  |  |  | 0 |  |  | 176
|  | CAUSE CODE : |  | 3842 |  |  | - |  | Service air valves | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F400Serviced Cooling Air Valves
PR13 | 21 | U1 | 2022-04-13 22:45 |  |  |  |  | 2022-04-16 19:49 |  | 0 | 0 | 69.067 | 69.0667 | 11119.733 | 1 |  |  |  | 0 |  |  | 162
|  | CAUSE CODE : |  | 3641 |  |  | - |  | AC Circuit breakers | [8 empty] | AMP CODE:
|  | DESCRIPTION : |  | F490138KV Circuit breaker faulted in Paddys Run switchyard
PR13 | 23 | U1 | 2022-04-18 06:28 |  |  |  |  | 2022-04-18 09:40 |  | 0 | 0 | 3.2 | 3.2 | 515.2 | 1 |  |  |  | 0 |  |  | 162
|  | CAUSE CODE : |  | 5150 |  |  | - |  | Turning gear and motor | [8 empty] | AMP CODE:
|  | DESCRIPTION : |  | F690Turning gear not operating correctly
PR13 | 25 | SF | 2022-04-20 06:51 |  |  |  |  | 2022-04-20 08:12 |  | 0 | 0 | 1.35 | 1.35 | 217.35 | 1 |  |  |  | 0 |  |  | 162
|  | CAUSE CODE : |  | 3979 |  |  | - |  | Other DCS problems | [8 empty] | AMP CODE: |  | 49
|  | DESCRIPTION : |  | F820ADDFEM controller fault
PR13 | 27 | U1 | 2022-05-02 05:38 |  |  |  |  | 2022-05-02 08:21 |  | 0 | 0 | 2.717 | 2.7167 | 437.383 | 1 |  |  |  | 0 |  |  | 162
|  | CAUSE CODE : |  | 5150 |  |  | - |  | Turning gear and motor | [8 empty] | AMP CODE:
|  | DESCRIPTION : |  | F84069Kv disturbance tripped station power.
PR13 | 33 | U1 | 2022-05-17 05:42 |  |  |  |  | 2022-05-17 09:50 |  | 0 | 0 | 4.133 | 4.1333 | 665.467 | 1 |  |  |  | 0 |  |  | 162
|  | CAUSE CODE : |  | 3671 |  |  | - |  | 12-15kV circuit breakers | [8 empty] | AMP CODE: |  | 06
|  | DESCRIPTION : |  | F82014kv breaker failure killed aux power to unit.
PR13 | 50 | SF | 2022-06-20 07:22 |  |  |  |  | 2022-06-20 07:37 |  | 0 | 0 | 0.25 | 0.25 | 36.75 | 1 |  |  |  | 0 |  |  | 148
|  | CAUSE CODE : |  | 3661 |  |  | - |  | 4000-7000 volt circuit breakers | [8 empty] | AMP CODE: |  | 59
|  | DESCRIPTION : |  | F840Exciter breaker linkage needed repair
PR13 | 85 | U1 | 2022-12-03 03:06 |  |  |  |  | 2022-12-03 15:54 |  | 0 | 0 | 12.8 | 12.8 | 2240 | 1 |  |  |  | 0 |  |  | 176
|  | CAUSE CODE : |  | 5150 |  |  | - |  | Turning gear and motor | [8 empty] | AMP CODE:
|  | DESCRIPTION : |  | F840Lost AC power and Turning Gear
PR13 | 89 | U1 | 2022-12-23 06:36 |  |  |  |  | 2022-12-23 07:13 |  | 0 | 0 | 0.617 | 0.6167 | 107.917 | 1 |  |  |  | 0 |  |  | 176
|  | CAUSE CODE : |  | 3822 |  |  | - |  | Closed cooling water valves | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Gen cold gas temp got too low.
PR13 | 15 | U1 | 2023-06-24 00:09 |  |  |  |  | 2023-06-25 08:18 |  | 0 | 0 | 32.15 | 32.15 | 4726.05 | 1 |  |  |  | 0 |  |  | 148
|  | CAUSE CODE : |  | 3670 |  |  | - |  | 12-15kV transformers | [8 empty] | AMP CODE:
|  | DESCRIPTION : |  | F490Lost plant14kv. TG issues
PR13 | 30 | SF | 2023-10-03 11:04 |  |  |  |  | 2023-10-03 11:15 |  | 0 | 0 | 0.183 | 0.1833 | 29.517 | 1 |  |  |  | 0 |  |  | 162
|  | CAUSE CODE : |  | 5049 |  |  | - |  | Other fuel system problems | [8 empty] | AMP CODE: |  | 46
|  | DESCRIPTION : |  | F460Flame out during start up
PR13 | 39 | U1 | 2023-12-17 13:54 |  |  |  |  | 2023-12-19 12:57 |  | 0 | 0 | 47.05 | 47.05 | 8233.75 | 1 |  |  |  | 0 |  |  | 176
|  | CAUSE CODE : |  | 3631 |  |  | - |  | 400-700 volt circuit breakers | [8 empty] | AMP CODE: |  | 64
|  | DESCRIPTION : |  | F640Main Lube Oil Pump wont reset.
PR13 | 41 | U1 | 2023-12-20 14:00 |  |  |  |  | 2023-12-31 11:25 |  | 0 | 0 | 261.417 | 261.4167 | 45747.917 | 1 |  |  |  | 0 |  |  | 176
|  | CAUSE CODE : |  | 4810 |  |  | - |  | Generator output breaker | [8 empty] | AMP CODE: |  | 03
|  | DESCRIPTION : |  | F030Possible Gen Brk Arc Flash
Trimble County - TC1
Unit | Event | Type | Start |  |  |  |  | End |  | GAC | NAC | Duration | Equiv Hrs | Equiv MWH | Cont | Work Start | Work End |  | Hours |  |  | Gross Capacity Impact (MW)
TC1 | 12 | U1 | 2014-01-11 21:03 |  |  |  |  | 2014-01-12 07:57 |  | 0 | 0 | 10.9 | 10.9 | 5566.303 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 9900 |  |  | - |  | Operator error | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820During load drop, operator error in valve closing caused the TDBFP main extraction
TC1 | 15 | U1 | 2014-01-14 10:39 |  |  |  |  | 2014-01-16 22:16 |  | 0 | 0 | 59.617 | 59.6167 | 30444.444 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 3344 |  |  | - |  | Deaerator (including level control) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F540Leak in the deaerator heater head was discovered. Unit was taken offline to repai
TC1 | 32 | U1 | 2014-03-06 01:06 |  |  |  |  | 2014-03-06 12:48 |  | 0 | 0 | 11.7 | 11.7 | 5974.839 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 1471 |  |  | - |  | Induced draft fan motors - variable speed | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820The VFD on the 1B ID fan sent a false alarm due to a low-low cooling supply alarm
TC1 | 82 | U1 | 2014-06-12 00:32 |  |  |  |  | 2014-06-12 01:21 |  | 0 | 0 | 0.817 | 0.8167 | 417.047 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 1457 |  |  | - |  | Induced draft fan lubrication systems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820During a lube oil pump swap for the 1A ID Fan, the second lube oil pump failed to
TC1 | 90 | U1 | 2014-06-17 22:12 |  |  |  |  | 2014-06-19 04:24 |  | 0 | 0 | 30.2 | 30.2 | 15422.234 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 0530 |  |  | - |  | Other main steam system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820A thermowell on the TC1 Main Steam line failed at a weld and caused a steam leak o
TC1 | 95 | U1 | 2014-07-08 00:08 |  |  |  |  | 2014-07-08 04:12 |  | 0 | 0 | 4.067 | 4.0667 | 2076.725 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 4267 |  |  | - |  | Control valve testing | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820During the control valve testing and while changing out a servo filter, the unit w
TC1 | 96 | U1 | 2014-07-08 05:41 |  |  |  |  | 2014-07-08 06:22 |  | 0 | 0 | 0.683 | 0.6833 | 348.958 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 3412 |  |  | - |  | Feedwater pump drive - steam turbine | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820While ramping the unit from the initial forced outage, one of the turbine driven b
TC1 | 122 | U1 | 2014-10-07 18:30 |  |  |  |  | 2014-10-10 13:24 |  | 0 | 0 | 66.9 | 66.9 | 34163.823 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 0400 |  |  | - |  | Burner wind box fires | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | FR00TC1 was taken offline due to a fire at the A3 burner windbox area. Severe damager
TC1 | 125 | U1 | 2014-10-30 06:00 |  |  |  |  | 2014-10-30 07:49 |  | 0 | 0 | 1.817 | 1.8167 | 927.717 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 3410 |  |  | - |  | Feedwater pump | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820TC1 tripped due to a feedwater and steam flow mismatch which resulted because of a
TC1 | 128 | U1 | 2014-11-01 22:45 |  |  |  |  | 2014-11-02 12:03 |  | 0 | 0 | 13.3 | 13.3 | 6791.912 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 4261 |  |  | - |  | Control valves | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F400The unit was taken offline to work on the #3 control valve which was found to have
TC1 | 131 | U1 | 2014-11-08 02:00 |  |  |  |  | 2014-11-08 04:54 |  | 0 | 0 | 2.9 | 2.9 | 1480.943 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 3412 |  |  | - |  | Feedwater pump drive - steam turbine | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820The 1B TDBFP malfunctioned during the emergency governor test.
TC1 | 134 | U1 | 2014-11-17 01:40 |  |  |  |  | 2014-11-17 15:28 |  | 0 | 0 | 13.8 | 13.8 | 7047.246 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 1455 |  |  | - |  | Induced draft fans | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Unit 1 went on a forced outage after the 1B ID fan tripped. The trip on the ID fa
TC1 | 135 | U1 | 2014-11-18 01:07 |  |  |  |  | 2014-11-18 03:03 |  | 0 | 0 | 1.933 | 1.9333 | 987.295 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 1400 |  |  | - |  | Forced draft fans | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F870TC1 is believe to have tripped due to the 1B FD fan having a power supply issue to
TC1 | 137 | U1 | 2014-11-22 05:09 |  |  |  |  | 2014-11-22 21:51 |  | 0 | 0 | 16.7 | 16.7 | 8528.189 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 0740 |  |  | - |  | Boiler recirculation pumps | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820TC1 MFT due to the BCP suction valves showing closed which was due to a DCS proces
TC1 | 139 | U1 | 2014-11-23 04:19 |  |  |  |  | 2014-11-24 12:03 |  | 0 | 0 | 31.733 | 31.7333 | 16205.262 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 0400 |  |  | - |  | Burner wind box fires | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | FR00Following the burner fire the decision was made to remove the unit from service wh
TC1 | 67 | U1 | 2015-05-02 00:54 |  |  |  |  | 2015-05-02 04:14 |  | 0 | 0 | 3.333 | 3.3333 | 1702.233 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 1740 |  |  | - |  | Boiler drum gage glasses / level indicator | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F420During maintenance on the the intercept control valves, both control valves were s
TC1 | 83 | U1 | 2015-06-30 09:32 |  |  |  |  | 2015-07-01 01:48 |  | 0 | 0 | 16.267 | 16.2667 | 8306.899 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 3330 |  |  | - |  | Condensate valves | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F400Unit come off on a forced outage due to erratic operation of the condensate contro
TC1 | 84 | U1 | 2015-07-01 03:04 |  |  |  |  | 2015-07-01 03:51 |  | 0 | 0 | 0.783 | 0.7833 | 400.025 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 0380 |  |  | - |  | Light off (igniter) systems (including fuel supply) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F460Unit MFT due to oil igniter flameout.
TC1 | 85 | U1 | 2015-07-01 04:56 |  |  |  |  | 2015-07-01 05:43 |  | 0 | 0 | 0.783 | 0.7833 | 400.025 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 0380 |  |  | - |  | Light off (igniter) systems (including fuel supply) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F460Unit MFT due to oil igniter flameout.
TC1 | 87 | U1 | 2015-07-01 20:06 |  |  |  |  | 2015-07-03 12:15 |  | 0 | 0 | 40.15 | 40.15 | 20503.401 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 3110 |  |  | - |  | Condenser tube leaks | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Condenser tube leak caused the unit to enter into a forced outage.
TC1 | 94 | U1 | 2015-08-20 00:10 |  |  |  |  | 2015-08-21 02:11 |  | 0 | 0 | 26.017 | 26.0167 | 13285.932 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 4260 |  |  | - |  | Main stop valves | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830During a Main Stop Valve test the #2 Main Stop Valve successfully closed but would
TC1 | 111 | U1 | 2015-12-13 11:55 |  |  |  |  | 2015-12-18 11:55 |  | 0 | 0 | 120 | 120 | 61280.4 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 1090 |  |  | - |  | Other boiler tube leaks | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit was taken offline due to a set of boiler tube leaks.
TC1 | 112 | U1 | 2015-12-18 11:55 |  |  |  |  | 2015-12-19 03:22 |  | 0 | 0 | 15.45 | 15.45 | 7889.852 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 8650 |  |  | - |  | "Baghouse systems, general" | [8 empty] | AMP CODE: |  | 59
|  | DESCRIPTION : |  | F590Fires out to coat the new TC1 Baghouse bags.
TC1 | 44 | U1 | 2016-03-24 08:06 |  |  |  |  | 2016-03-24 15:19 |  | 0 | 0 | 7.217 | 7.2167 | 3685.335 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 1455 |  |  | - |  | Induced draft fans | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820ID Fans tripped causing TC1 to MFT.
TC1 | 45 | SF | 2016-03-24 15:19 |  |  |  |  | 2016-03-27 20:48 |  | 0 | 0 | 77.483 | 77.4833 | 39568.414 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 0520 |  |  | - |  | Other main steam valves (including vent and drain valves but not including the turbine stop valves) | [8 empty] | AMP CODE: |  | 06
|  | DESCRIPTION : |  | F060Main Steam Non-Return/Superheat Stop valve component failed and the valve has been
TC1 | 74 | U1 | 2016-06-20 07:28 |  |  |  |  | 2016-06-21 23:03 |  | 0 | 0 | 39.583 | 39.5833 | 19527.645 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 1471 |  |  | - |  | Induced draft fan motors - variable speed | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F5401A ID Fan tripped due to a VFD transformer coolant leak.
TC1 | 75 | U1 | 2016-06-26 15:49 |  |  |  |  | 2016-06-26 20:55 |  | 0 | 0 | 5.1 | 5.1 | 2515.983 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 1488 |  |  | - |  | Air heater (regenerative) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F780Water from a hydroveyor gasket leak caused the MCC suppling power to the Air Heate
TC1 | 87 | U1 | 2016-09-01 22:38 |  |  |  |  | 2016-09-02 06:32 |  | 0 | 0 | 7.9 | 7.9 | 3897.307 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 3681 |  |  | - |  | Other voltage circuit breakers | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F330A 120 VAC limit switch shorted and the circuit breaker remained closed. The distri
TC1 | 89 | U1 | 2016-09-07 16:20 |  |  |  |  | 2016-09-07 19:58 |  | 0 | 0 | 3.633 | 3.6333 | 1792.432 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 3681 |  |  | - |  | Other voltage circuit breakers | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F330A 120 VAC limit switch shorted and the circuit breaker remained closed. The distri
TC1 | 93 | U1 | 2016-09-14 10:53 |  |  |  |  | 2016-09-14 12:39 |  | 0 | 0 | 1.767 | 1.7667 | 871.55 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 1475 |  |  | - |  | Induced draft fan controls | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | FP00Due to issues controlling a coal feeder rate, the airflow to the boiler increased,
TC1 | 106 | U1 | 2016-11-03 04:46 |  |  |  |  | 2016-11-03 17:59 |  | 0 | 0 | 13.217 | 13.2167 | 6520.178 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 3979 |  |  | - |  | Other DCS problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F340A DCS Controller failed and rebooted while its backup was also out of service. The
TC1 | 113 | U1 | 2016-11-26 06:03 |  |  |  |  | 2016-11-26 15:44 |  | 0 | 0 | 9.683 | 9.6833 | 4777.079 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 1475 |  |  | - |  | Induced draft fan controls | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F600A DCS card failed, resulting in a loss of I/O control of the ID fan system. The ca
TC1 | 7 | U1 | 2017-01-26 19:00 |  |  |  |  | 2017-01-26 23:27 |  | 0 | 0 | 4.45 | 4.45 | 2193.85 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 1750 |  |  | - |  | Burner management system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F490When placing a start on the AB oil guns, a ground fault went back to the Burner Ma
TC1 | 29 | U1 | 2017-04-16 21:04 |  |  |  |  | 2017-04-18 12:48 |  | 0 | 0 | 39.733 | 39.7333 | 19588.533 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 1000 |  |  | - |  | Waterwall (Furnace wall) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F540The unit was taken offline and placed on a Forced Outage for repairs on a leaking
TC1 | 34 | U1 | 2017-04-27 17:56 |  |  |  |  | 2017-04-30 11:29 |  | 0 | 0 | 65.55 | 65.55 | 32316.151 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 1000 |  |  | - |  | Waterwall (Furnace wall) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F540The unit was placed on a Forced Outage for repairs to an identified tube leak.
TC1 | 97 | U1 | 2017-11-28 18:00 |  |  |  |  | 2017-11-28 19:58 |  | 0 | 0 | 1.967 | 1.9667 | 969.567 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 3344 |  |  | - |  | Deaerator (including level control) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F660The unit was placed on an Unplanned Outage due to low tank level in the deaerator.
TC1 | 99 | U2 | 2017-11-28 21:06 |  |  |  |  | 2017-11-30 07:47 |  | 0 | 0 | 34.683 | 34.6833 | 17098.883 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 4040 |  |  | - |  | Bearings | [8 empty] | AMP CODE: |  | 85
|  | DESCRIPTION : |  | F850The LP bearing vibrations were not with-in normal limits so the unit was returned
TC1 | 100 | U2 | 2017-11-30 18:04 |  |  |  |  | 2017-12-02 22:23 |  | 0 | 0 | 52.317 | 52.3167 | 25792.116 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 4260 |  |  | - |  | Main stop valves | [8 empty] | AMP CODE: |  | 66
|  | DESCRIPTION : |  | F660The unit was taken offline to address high differential pressure across the screen
TC1 | 101 | U1 | 2017-12-02 22:23 |  |  |  |  | 2017-12-03 19:57 |  | 0 | 0 | 21.567 | 21.5667 | 10632.368 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 0710 |  |  | - |  | Blowdown system piping | [8 empty] | AMP CODE: |  | 54
|  | DESCRIPTION : |  | F540The unit was placed on an Unplanned Outage after the main header for the blowdown
TC1 | 6 | U1 | 2018-01-31 22:03 |  |  |  |  | 2018-02-01 05:08 |  | 0 | 0 | 7.083 | 7.0833 | 3492.083 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 4470 |  |  | - |  | Differential expansion | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F780As the unit was coming down for the Incremental Heat Rate test, the differential e
TC1 | 17 | U1 | 2018-03-07 03:01 |  |  |  |  | 2018-03-07 15:03 |  | 0 | 0 | 12.033 | 12.0333 | 5932.434 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 1400 |  |  | - |  | Forced draft fans | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F660TC1 tripped on furnace pressure after a clinker caused boiler to pressurize.
TC1 | 23 | U1 | 2018-05-01 18:31 |  |  |  |  | 2018-05-04 00:25 |  | 0 | 0 | 53.9 | 53.9 | 26572.7 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 4261 |  |  | - |  | Control valves | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F720The unit was brought offline for the replacement of the actuator on the MS Control
TC1 | 25 | U1 | 2018-05-06 00:28 |  |  |  |  | 2018-05-06 07:33 |  | 0 | 0 | 7.083 | 7.0833 | 3492.083 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 3618 |  |  | - |  | Other switchyard equipment - external (not OMC) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F340When syncing the unit, 511 Line MOD was not operational. This caused a situation w
TC1 | 34 | U3 | 2018-09-12 22:40 |  |  |  |  | 2018-09-14 16:03 |  | 0 | 0 | 41.383 | 41.3833 | 20401.982 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 3110 |  |  | - |  | Condenser tube leaks | [8 empty] | AMP CODE: |  | A0
|  | DESCRIPTION : |  | FA00The unit was taken offline to identify and plug the condenser tube leak which was
TC1 | 35 | U1 | 2018-10-05 11:17 |  |  |  |  | 2018-10-05 13:53 |  | 0 | 0 | 2.6 | 2.6 | 1281.8 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 3618 |  |  | - |  | Other switchyard equipment - external (not OMC) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F790Relay testing of a138kV bus resulted in a loss of power feed to the Trimble County
TC1 | 40 | SF | 2018-11-14 11:00 |  |  |  |  | 2018-11-14 21:53 |  | 0 | 0 | 10.883 | 10.8833 | 5365.483 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 4609 |  |  | - |  | Other exciter problems | [8 empty] | AMP CODE: |  | 59
|  | DESCRIPTION : |  | F590The unit experienced a startup failure when the excitation equipment and transmiss
TC1 | 9 | U1 | 2019-04-02 09:19 |  |  |  |  | 2019-04-03 09:33 |  | 0 | 0 | 24.233 | 24.2333 | 11947.033 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 8817 |  |  | - |  | SCR NOx Control system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F520The unit tripped when troubleshooting a loss of power at reactant prep and DCS dro
TC1 | 11 | U1 | 2019-06-05 22:56 |  |  |  |  | 2019-06-06 01:26 |  | 0 | 0 | 2.5 | 2.5 | 1232.5 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 9900 |  |  | - |  | Operator error | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | FP00The unit experienced a Forced Outage when an incorrect value was entered as a MW s
TC1 | 12 | U1 | 2019-06-08 10:57 |  |  |  |  | 2019-06-12 04:43 |  | 0 | 0 | 89.767 | 89.7667 | 44254.967 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 1035 |  |  | - |  | Platen superheater | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F540The unit was taken offline for repairs to tubes in the superheat vertical platens,
TC1 | 14 | U1 | 2019-06-23 22:24 |  |  |  |  | 2019-06-23 23:06 |  | 0 | 0 | 0.7 | 0.7 | 345.1 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 1700 |  |  | - |  | "Feedwater controls (report local controls - feedwater pump, feedwater regulator valve, etc., - with component or system)" | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F660Feedwater and Steam flow differential increased during a feedwater pump swap, caus
TC1 | 22 | U1 | 2019-11-17 21:29 |  |  |  |  | 2019-11-18 00:24 |  | 0 | 0 | 2.917 | 2.9167 | 1437.917 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 0680 |  |  | - |  | Feedwater valves (not feedwater regulating valve) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F340There were issues with the A turbine driven boiler feed pump recirculation valve.
TC1 | 26 | U1 | 2019-11-24 10:03 |  |  |  |  | 2019-11-25 07:40 |  | 0 | 0 | 21.617 | 21.6167 | 10657.017 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 1035 |  |  | - |  | Platen superheater | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F540The unit was placed into an immediate forced outage due to a boiler tube leak in a
TC1 | 37 | U1 | 2019-12-18 12:36 |  |  |  |  | 2019-12-18 22:18 |  | 0 | 0 | 9.7 | 9.7 | 4782.1 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 4750 |  |  | - |  | Other generator controls and metering problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | FV00The unit tripped due to vibration-caused lack of contact in a fuse on a generator
TC1 | 38 | U1 | 2019-12-18 22:27 |  |  |  |  | 2019-12-18 23:15 |  | 0 | 0 | 0.8 | 0.8 | 394.4 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 9900 |  |  | - |  | Operator error | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | FP00The unit experienced an MFT when gas guns were retracted prior to having its subse
TC1 | 6 | U1 | 2020-04-24 10:15 |  |  |  |  | 2020-04-24 11:51 |  | 0 | 0 | 1.6 | 1.6 | 788.8 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 1799 |  |  | - |  | Other boiler instrumentation and control problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F660The unit experienced a Forced Outage due to an upset in boiler pressure after a la
TC1 | 11 | U1 | 2020-06-08 22:14 |  |  |  |  | 2020-06-09 00:58 |  | 0 | 0 | 2.733 | 2.7333 | 1347.534 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 0260 |  |  | - |  | Primary air fan | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Due to an electrical fault the B phase cable melted and broke in half in the 1B Pr
TC1 | 16 | U1 | 2020-06-29 00:56 |  |  |  |  | 2020-06-30 15:00 |  | 0 | 0 | 38.067 | 38.0667 | 18766.867 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 1000 |  |  | - |  | Waterwall (Furnace wall) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F540The unit was placed into an immediate forced outage due to a tube leak in the TC1
TC1 | 18 | U1 | 2020-07-01 21:15 |  |  |  |  | 2020-07-03 09:14 |  | 0 | 0 | 35.983 | 35.9833 | 17739.784 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 3499 |  |  | - |  | Other feedwater system problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | FA00The unit went into a forced outage due to high levels of silica in the feedwater.
TC1 | 21 | U1 | 2020-07-16 08:41 |  |  |  |  | 2020-07-16 15:04 |  | 0 | 0 | 6.383 | 6.3833 | 3146.983 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 3669 |  |  | - |  | Other 4000-7000 volt problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820The unit went into a forced outage due to a lockout relay shorting and tripping on
TC1 | 16 | U1 | 2021-03-25 16:00 |  |  |  |  | 2021-03-26 15:34 |  | 0 | 0 | 23.567 | 23.5667 | 11618.367 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 4730 |  |  | - |  | Generator current and potential transformers | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F310The unit became unavailable on a Forced Outage after the Generator B side Current
TC1 | 24 | U1 | 2021-07-27 15:57 |  |  |  |  | 2021-07-27 18:19 |  | 0 | 0 | 2.367 | 2.3667 | 1166.767 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 1710 |  |  | - |  | "Combustion/steam condition controls (report local controls - burners, pulverizers, etc., - with component or system)" | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F660The unit tripped due to overpressurization in the boiler, as fan controls chased a
TC1 | 26 | U1 | 2021-07-30 01:37 |  |  |  |  | 2021-07-31 11:21 |  | 0 | 0 | 33.733 | 33.7333 | 16630.533 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 3110 |  |  | - |  | Condenser tube leaks | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | FA00The unit was placed on a Forced Outage for repairs to a condenser tube leak.
TC1 | 29 | U1 | 2021-10-31 16:35 |  |  |  |  | 2021-11-02 19:46 |  | 0 | 0 | 51.183 | 51.1833 | 25233.384 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 3620 |  |  | - |  | Main transformer | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F540The unit was taken offline due to a GSU Transformer oil leak.
TC1 | 30 | U1 | 2021-11-02 21:49 |  |  |  |  | 2021-11-02 23:59 |  | 0 | 0 | 2.167 | 2.1667 | 1068.167 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 3610 |  |  | - |  | Switchyard circuit breakers - external (not OMC) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F630A relay issue on the 4511 tie breaker caused the breaker to open, causing a unit t
TC1 | 3 | U1 | 2022-02-17 14:09 |  |  |  |  | 2022-02-17 16:29 |  | 0 | 0 | 2.333 | 2.3333 | 1150.333 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 3210 |  |  | - |  | Circulating water pumps | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | FP00The TC1 Cooling Tower Pumps tripped after receiving a false signal of low basin le
TC1 | 11 | U1 | 2022-07-24 01:30 |  |  |  |  | 2022-07-26 21:29 |  | 0 | 0 | 67.983 | 67.9833 | 33515.783 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 0890 |  |  | - |  | Bottom ash systems (wet or dry) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F690The unit was placed on a forced outage due to issues with the primary submerged ch
TC1 | 14 | U1 | 2022-07-31 08:04 |  |  |  |  | 2022-07-31 10:27 |  | 0 | 0 | 2.383 | 2.3833 | 1174.983 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 1475 |  |  | - |  | Induced draft fan controls | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | FP00While troubleshooting the 1B ID Fan, the 1A ID Fan was tripped causing a forced un
TC1 | 18 | U1 | 2022-08-31 10:55 |  |  |  |  | 2022-08-31 11:35 |  | 0 | 0 | 0.667 | 0.6667 | 328.667 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 1475 |  |  | - |  | Induced draft fan controls | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | FP00While attempting to isolate the SDRS inverter for repair, the power feeding the ID
TC1 | 22 | SF | 2022-10-22 02:19 |  |  |  |  | 2022-10-22 13:06 |  | 0 | 0 | 10.783 | 10.7833 | 5316.184 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 4293 |  |  | - |  | Hydraulic system pipes and valves | [8 empty] | AMP CODE: |  | 54
|  | DESCRIPTION : |  | F540The unit experienced a start-up failure due to an EHC leak that was addressed.
TC1 | 25 | U1 | 2022-12-22 15:35 |  |  |  |  | 2022-12-30 02:19 |  | 0 | 0 | 178.733 | 178.7333 | 88115.534 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 0897 |  |  | - |  | Bottom ash rotary (drag chain type) conveyor and motor | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F340The unit was placed on a forced outage due to issues with the primary submerged ch
TC1 | 3 | SF | 2023-02-01 21:13 |  |  |  |  | 2023-02-02 23:00 |  | 0 | 0 | 25.783 | 25.7833 | 12711.183 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 1430 |  |  | - |  | Air supply ducts from FD fan | [8 empty] | AMP CODE: |  | 54
|  | DESCRIPTION : |  | F540The 1B water coil air heater (WCAH) developed a leak between the tube sheet and th
TC1 | 4 | SF | 2023-02-02 23:00 |  |  |  |  | 2023-02-03 09:06 |  | 0 | 0 | 10.1 | 10.1 | 4979.3 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 3700 |  |  | - |  | Power Station switchyard (non generating unit equipment) | [8 empty] | AMP CODE: |  | X0
|  | DESCRIPTION : |  | FX00While trying to come online, the 511 MOD bus wouldn't operate. Substation group w
TC1 | 17 | U1 | 2023-11-11 15:01 |  |  |  |  | 2023-11-12 14:29 |  | 0 | 0 | 23.467 | 23.4667 | 11569.068 | 1 |  |  |  | 0 |  |  | 530
|  | CAUSE CODE : |  | 3120 |  |  | - |  | Tube sheets | [8 empty] | AMP CODE: |  | 12
|  | DESCRIPTION : |  | F120The unit was placed on a forced outage due to debris blocking the condenser tube s
Trimble County - TC10
Unit | Event | Type | Start |  |  |  |  | End |  | GAC | NAC | Duration | Equiv Hrs | Equiv MWH | Cont | Work Start | Work End |  | Hours |  |  | Gross Capacity Impact (MW)
TC10 | 2 | U1 | 2014-01-03 05:21 |  |  |  |  | 2014-01-03 07:03 |  | 0 | 0 | 1.7 | 1.7 | 299.2 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5016 |  |  | - |  | High pressure compressor bleed valves | [8 empty] | AMP CODE: |  | 48
|  | DESCRIPTION : |  | F480Forced outage due to compressor bleed valve frozen shut.
TC10 | 13 | SF | 2014-01-22 00:45 |  |  |  |  | 2014-01-22 04:02 |  | 0 | 0 | 3.283 | 3.2833 | 577.867 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5079 |  |  | - |  | Other combustor problems | [8 empty] | AMP CODE: |  | 46
|  | DESCRIPTION : |  | F460Failed to ignite during startup.
TC10 | 25 | U1 | 2014-02-26 02:38 |  |  |  |  | 2014-02-26 03:45 |  | 0 | 0 | 1.117 | 1.1167 | 196.533 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 33
|  | DESCRIPTION : |  | F330Forced outage due to 89SS failing to open.
TC10 | 29 | U1 | 2014-03-08 08:03 |  |  |  |  | 2014-03-08 08:50 |  | 0 | 0 | 0.783 | 0.7833 | 137.867 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 33
|  | DESCRIPTION : |  | F330Forced outage due to 89SS failing to disengage.
TC10 | 33 | U1 | 2014-03-16 18:25 |  |  |  |  | 2014-03-16 20:27 |  | 0 | 0 | 2.033 | 2.0333 | 357.867 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 33
|  | DESCRIPTION : |  | F330Forced outage due to 89SS failing to disengage.
TC10 | 37 | U1 | 2014-03-18 06:09 |  |  |  |  | 2014-03-18 06:19 |  | 0 | 0 | 0.167 | 0.1667 | 29.333 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 3631 |  |  | - |  | 400-700 volt circuit breakers | [8 empty] | AMP CODE: |  | 63
|  | DESCRIPTION : |  | F630Forced outage due to TC9 MCC #2 feed breaker opening. Control power to TC9/10 LCI
TC10 | 41 | U1 | 2014-03-20 08:30 |  |  |  |  | 2014-03-20 09:03 |  | 0 | 0 | 0.55 | 0.55 | 96.8 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 33
|  | DESCRIPTION : |  | F330Forced outage due to issue with 89SS.
TC10 | 56 | SF | 2014-04-06 06:35 |  |  |  |  | 2014-04-06 06:45 |  | 0 | 0 | 0.167 | 0.1667 | 26.167 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340Failure to start due 89SS not engaging.
TC10 | 59 | SF | 2014-04-09 05:08 |  |  |  |  | 2014-04-09 06:21 |  | 0 | 0 | 1.217 | 1.2167 | 191.017 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F34089SS on TC9 failed to engage, TC10 made unavailable to repair TC9.
TC10 | 64 | U1 | 2014-04-10 16:41 |  |  |  |  | 2014-04-10 19:32 |  | 0 | 0 | 2.85 | 2.85 | 447.45 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F34089ND on TC10 failed to engage. TC9 and TC10 made unavailable for repairs.
TC10 | 66 | U1 | 2014-04-11 17:01 |  |  |  |  | 2014-04-11 22:55 |  | 0 | 0 | 5.9 | 5.9 | 926.3 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F34089SS on TC10 over travel.
TC10 | 69 | SF | 2014-04-21 09:29 |  |  |  |  | 2014-04-21 09:46 |  | 0 | 0 | 0.283 | 0.2833 | 44.483 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F34089SS VFD setting too low to make it work.
TC10 | 78 | SF | 2014-04-28 06:18 |  |  |  |  | 2014-04-28 12:59 |  | 0 | 0 | 6.683 | 6.6833 | 1049.283 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F34089SS failed to disengage, Adjustments made to linkage.
TC10 | 80 | U1 | 2014-04-29 06:12 |  |  |  |  | 2014-04-29 06:34 |  | 0 | 0 | 0.367 | 0.3667 | 57.567 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F34089SS motor VFD overload on TC9. Prevented TC10 to be "ready to start".
TC10 | 84 | SF | 2014-05-02 05:25 |  |  |  |  | 2014-05-02 14:18 |  | 0 | 0 | 8.883 | 8.8833 | 1394.683 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F34089SS on TC9 failed to engage. Troubleshooting required TC10 to be unavailable due
TC10 | 86 | U1 | 2014-05-04 02:23 |  |  |  |  | 2014-05-04 04:00 |  | 0 | 0 | 1.617 | 1.6167 | 253.817 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340LCI coolant level low, this makes the unit not ready to start.
TC10 | 88 | U1 | 2014-05-07 10:27 |  |  |  |  | 2014-05-07 10:32 |  | 0 | 0 | 0.083 | 0.0833 | 13.083 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F34089SS failed to open. Reset overload in VFD for motor drive.
TC10 | 90 | U1 | 2014-05-12 15:28 |  |  |  |  | 2014-05-12 17:40 |  | 0 | 0 | 2.2 | 2.2 | 345.4 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5042 |  |  | - |  | Fuel nozzles/vanes | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Fuel gas pressure oscillation due to fuel gas control valves not regulating pressu
TC10 | 92 | U1 | 2014-05-12 19:37 |  |  |  |  | 2014-05-12 19:48 |  | 0 | 0 | 0.183 | 0.1833 | 28.783 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340TC10 89SS failed to open.
TC10 | 95 | U1 | 2014-05-13 13:02 |  |  |  |  | 2014-05-13 15:20 |  | 0 | 0 | 2.3 | 2.3 | 361.1 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5041 |  |  | - |  | Fuel piping and valves | [8 empty] | AMP CODE: |  | FR
|  | DESCRIPTION : |  | F660Fuel gas pressure oscillation due to fuel gas control valves not controlling press
TC10 | 102 | U1 | 2014-05-20 11:17 |  |  |  |  | 2014-05-20 11:26 |  | 0 | 0 | 0.15 | 0.15 | 23.55 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340Unit failed to start because the LCI had a fault in the system, fault reset, LCI w
TC10 | 104 | U1 | 2014-05-20 11:29 |  |  |  |  | 2014-05-20 12:58 |  | 0 | 0 | 1.483 | 1.4833 | 232.883 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340Unit failed to start due to 89MD not engaging. 89MD had a blown fuse. Fuse replace
TC10 | 109 | U1 | 2014-05-22 15:28 |  |  |  |  | 2014-05-22 20:02 |  | 0 | 0 | 4.567 | 4.5667 | 716.967 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5108 |  |  | - |  | High engine exhaust temperature | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Unit trip due to high exhaust area temperature.
TC10 | 113 | U1 | 2014-05-26 20:17 |  |  |  |  | 2014-05-27 01:47 |  | 0 | 0 | 5.5 | 5.5 | 863.5 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340Unit failed to start because the 89MD on the LCI blew a fuse, caused fault code on
TC10 | 117 | U1 | 2014-05-30 23:15 |  |  |  |  | 2014-05-31 00:12 |  | 0 | 0 | 0.95 | 0.95 | 149.15 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340Unit failed to start because the 89MD on the LCI blew a fuse, caused fault code on
TC10 | 119 | U1 | 2014-06-07 15:02 |  |  |  |  | 2014-06-07 15:47 |  | 0 | 0 | 0.75 | 0.75 | 117.75 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5041 |  |  | - |  | Fuel piping and valves | [8 empty] | AMP CODE: |  | 69
|  | DESCRIPTION : |  | F690Forced outage while in reserve due to gas valve failure. Valve was repaired and un
TC10 | 122 | U1 | 2014-06-07 18:30 |  |  |  |  | 2014-06-07 20:26 |  | 0 | 0 | 1.933 | 1.9333 | 303.533 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5299 |  |  | - |  | Other miscellaneous gas turbine problems | [8 empty] | AMP CODE: |  | 70
|  | DESCRIPTION : |  | F70089MD fuse blown causing forced outage while unit in reserve. Unit returned to res
TC10 | 126 | U1 | 2014-06-12 18:15 |  |  |  |  | 2014-06-12 18:43 |  | 0 | 0 | 0.467 | 0.4667 | 73.267 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 70
|  | DESCRIPTION : |  | F70089ND fuse blew causing unit to become unavailable. Fuse replaced and unit returne
TC10 | 128 | U1 | 2014-06-12 19:16 |  |  |  |  | 2014-06-12 20:20 |  | 0 | 0 | 1.067 | 1.0667 | 167.467 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 70
|  | DESCRIPTION : |  | F700Starting device tripped causing unit to become unavailable. I/E repaired and unit
TC10 | 131 | U1 | 2014-06-14 20:00 |  |  |  |  | 2014-06-14 21:27 |  | 0 | 0 | 1.45 | 1.45 | 227.65 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F34089SS switch would not close, I/E notified and repaired to return unit to reserve s
TC10 | 134 | U1 | 2014-06-20 20:13 |  |  |  |  | 2014-06-20 23:28 |  | 0 | 0 | 3.25 | 3.25 | 510.25 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Unit was made unavailable due to 89MD switch issues. Issues resolved and unit ret
TC10 | 155 | U1 | 2014-07-21 23:24 |  |  |  |  | 2014-07-22 00:43 |  | 0 | 0 | 1.317 | 1.3167 | 206.717 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 3996 |  |  | - |  | Air conditioning systems - rooms and areas | [8 empty] | AMP CODE: |  | 49
|  | DESCRIPTION : |  | F490The in service air conditioning unit in the EX2000 compartment went to ground, bac
TC10 | 165 | U1 | 2014-08-09 20:20 |  |  |  |  | 2014-08-09 21:35 |  | 0 | 0 | 1.25 | 1.25 | 196.25 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 3634 |  |  | - |  | 400-700 volt protection devices | [8 empty] | AMP CODE: |  | 49
|  | DESCRIPTION : |  | F490TC10 was made unavailable because of problems on TC9's MCC #2, where the control p
TC10 | 187 | SF | 2014-10-07 01:26 |  |  |  |  | 2014-10-07 02:05 |  | 0 | 0 | 0.65 | 0.65 | 114.4 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 3661 |  |  | - |  | 4000-7000 volt circuit breakers | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F3404KV excitation transformer breaker did not engage properly, causing a failure to s
TC10 | 204 | U1 | 2014-11-15 15:03 |  |  |  |  | 2014-11-15 16:09 |  | 0 | 0 | 1.1 | 1.1 | 193.6 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5049 |  |  | - |  | Other fuel system problems | [8 empty] | AMP CODE: |  | 66
|  | DESCRIPTION : |  | F660Relief valve on TC9/10 fuel gas heater lifted, and all gas turbines needed to be u
TC10 | 205 | U1 | 2014-11-15 16:09 |  |  |  |  | 2014-11-15 16:36 |  | 0 | 0 | 0.45 | 0.45 | 79.2 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5049 |  |  | - |  | Other fuel system problems | [8 empty] | AMP CODE: |  | 66
|  | DESCRIPTION : |  | F660Relief valve on fuel gas heater for TC9/10 lifted, in order to make it seat and st
TC10 | 207 | SF | 2014-11-17 17:30 |  |  |  |  | 2014-11-17 17:50 |  | 0 | 0 | 0.333 | 0.3333 | 58.667 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340TC10 was given a start signal and it did everything correct up to 1,152 RPM where
TC10 | 218 | U1 | 2014-12-10 15:58 |  |  |  |  | 2014-12-10 17:18 |  | 0 | 0 | 1.333 | 1.3333 | 234.667 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 3653 |  |  | - |  | DC protection devices | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340Loss of DC voltage supply to TC9 BOP Fuel Gas Valves, needed the fuel gas heater v
TC10 | 18 | U1 | 2015-02-21 15:46 |  |  |  |  | 2015-02-21 16:05 |  | 0 | 0 | 0.317 | 0.3167 | 55.733 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 19
|  | DESCRIPTION : |  | F190Low cooling water level on LCI caused a not ready start condition. Liquid level wa
TC10 | 26 | SF | 2015-03-25 15:34 |  |  |  |  | 2015-03-25 16:30 |  | 0 | 0 | 0.933 | 0.9333 | 164.267 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5048 |  |  | - |  | Gas fuel system including controls and instrumentation | [8 empty] | AMP CODE: |  | 66
|  | DESCRIPTION : |  | F660Failure to start for reserve deployment. Reported out as balance of plant fuel gas
TC10 | 33 | U1 | 2015-04-01 22:22 |  |  |  |  | 2015-04-01 23:35 |  | 0 | 0 | 1.217 | 1.2167 | 191.017 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 3631 |  |  | - |  | 400-700 volt circuit breakers | [8 empty] | AMP CODE: |  | 49
|  | DESCRIPTION : |  | F490LCI 9/10 lost power, and TC10 lost starting capability. Reason for loss of power w
TC10 | 36 | U1 | 2015-04-13 11:59 |  |  |  |  | 2015-04-13 16:37 |  | 0 | 0 | 4.633 | 4.6333 | 727.433 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5108 |  |  | - |  | High engine exhaust temperature | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820The Inlet Guide Vanes (IGV) were not tracking properly due to varnish build up in
TC10 | 40 | U1 | 2015-05-04 06:37 |  |  |  |  | 2015-05-04 07:51 |  | 0 | 0 | 1.233 | 1.2333 | 193.633 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340The 89ND on TC9 failed to open, making this unit unavailable due to shared LCI.
TC10 | 49 | U1 | 2015-05-15 22:04 |  |  |  |  | 2015-05-15 23:30 |  | 0 | 0 | 1.433 | 1.4333 | 225.033 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5016 |  |  | - |  | High pressure compressor bleed valves | [8 empty] | AMP CODE: |  | 33
|  | DESCRIPTION : |  | F330Compressor bleed valve limit switches did not disengage, causing a "not ready to s
TC10 | 57 | SF | 2015-05-29 13:06 |  |  |  |  | 2015-05-29 14:36 |  | 0 | 0 | 1.5 | 1.5 | 235.5 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340The 89SS, static start switch, failed to engage on TC10 due to a loose wire on a t
TC10 | 59 | U1 | 2015-05-30 10:31 |  |  |  |  | 2015-05-30 11:03 |  | 0 | 0 | 0.533 | 0.5333 | 83.733 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340TC9 did not start due to a starting device trip, TC10 was made unavailable due the
TC10 | 65 | U1 | 2015-06-06 04:48 |  |  |  |  | 2015-06-06 06:40 |  | 0 | 0 | 1.867 | 1.8667 | 293.067 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5299 |  |  | - |  | Other miscellaneous gas turbine problems | [8 empty] | AMP CODE: |  | 09
|  | DESCRIPTION : |  | F090Unit not ready to start due to a faulty hazardous gas detector at the turbine comp
TC10 | 70 | U1 | 2015-06-07 03:53 |  |  |  |  | 2015-06-07 06:13 |  | 0 | 0 | 2.333 | 2.3333 | 366.333 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340Coolant level in the LCI was low, preventing a ready to start signal. Coolant add
TC10 | 72 | U1 | 2015-06-10 22:42 |  |  |  |  | 2015-06-11 02:25 |  | 0 | 0 | 3.717 | 3.7167 | 583.517 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5109 |  |  | - |  | Other exhaust problems (including high exhaust system temperature not attributable to a specific problem) | [8 empty] | AMP CODE: |  | 12
|  | DESCRIPTION : |  | F120High exhaust duct pressure did not allow unit to be ready for start. Instrument li
TC10 | 75 | U1 | 2015-06-13 14:00 |  |  |  |  | 2015-06-13 21:27 |  | 0 | 0 | 7.45 | 7.45 | 1169.65 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340LCI fault caused a "not ready start" condition.
TC10 | 81 | U1 | 2015-06-15 07:38 |  |  |  |  | 2015-06-15 08:16 |  | 0 | 0 | 0.633 | 0.6333 | 99.433 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 3610 |  |  | - |  | Switchyard circuit breakers - external (not OMC) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340MOD on TC9 failed to close, needed B bus outage to correct situation. B bus affect
TC10 | 90 | U1 | 2015-07-23 21:48 |  |  |  |  | 2015-07-23 23:07 |  | 0 | 0 | 1.317 | 1.3167 | 209.35 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5109 |  |  | - |  | Other exhaust problems (including high exhaust system temperature not attributable to a specific problem) | [8 empty] | AMP CODE: |  | 09
|  | DESCRIPTION : |  | F090Exhaust duct pressure high signal caused a not ready to start condition.
TC10 | 93 | U1 | 2015-07-24 19:22 |  |  |  |  | 2015-07-24 22:58 |  | 0 | 0 | 3.6 | 3.6 | 572.4 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340The static start switch 89SS on TC9 failed to engage, needed to card TC10 in order
TC10 | 98 | U1 | 2015-08-03 15:00 |  |  |  |  | 2015-08-03 16:11 |  | 0 | 0 | 1.183 | 1.1833 | 188.15 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340TC9 89SS switch did not operate, troubleshooting required TC10 to be made unavaila
TC10 | 103 | U1 | 2015-08-13 18:31 |  |  |  |  | 2015-08-13 20:01 |  | 0 | 0 | 1.5 | 1.5 | 238.5 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5049 |  |  | - |  | Other fuel system problems | [8 empty] | AMP CODE: |  | 09
|  | DESCRIPTION : |  | F090Unit has a pre-ignition trip due high hazardous gas detectors on the turbine compa
TC10 | 116 | U1 | 2015-09-25 10:26 |  |  |  |  | 2015-09-25 11:07 |  | 0 | 0 | 0.683 | 0.6833 | 108.65 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5449 |  |  | - |  | Other fuel system problems | [8 empty] | AMP CODE: |  | 09
|  | DESCRIPTION : |  | F090One of the three hazardous gas detectors on the turbine compartment fan, was out o
TC10 | 129 | SF | 2015-11-16 09:52 |  |  |  |  | 2015-11-16 11:53 |  | 0 | 0 | 2.017 | 2.0167 | 360.983 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5050 |  |  | - |  | Ignition system | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340Spark rods were stuck in the retracted position not allowing ignition.
TC10 | 12 | U1 | 2016-01-20 12:18 |  |  |  |  | 2016-01-20 13:01 |  | 0 | 0 | 0.717 | 0.7167 | 128.283 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5048 |  |  | - |  | Gas fuel system including controls and instrumentation | [8 empty] | AMP CODE: |  | 09
|  | DESCRIPTION : |  | F090The Fuel Gas counter kept moving while TC10 was offline so the unit was made unava
TC10 | 20 | U1 | 2016-03-01 08:09 |  |  |  |  | 2016-03-01 08:43 |  | 0 | 0 | 0.567 | 0.5667 | 95.767 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 9131 |  |  | - |  | Lack of fuel (interruptible supply of fuel part of fuel contract) | [8 empty] | AMP CODE: |  | NF
|  | DESCRIPTION : |  | F340A Texas Gas supply valve electro-pneumatic transducer failed, causing the valve to
TC10 | 31 | U1 | 2016-03-16 22:40 |  |  |  |  | 2016-03-17 04:47 |  | 0 | 0 | 6.117 | 6.1167 | 1033.716 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 4609 |  |  | - |  | Other exciter problems | [8 empty] | AMP CODE: |  | 52
|  | DESCRIPTION : |  | F520Unit was made unavailable due to generator exciter problems.
TC10 | 35 | U1 | 2016-03-18 04:28 |  |  |  |  | 2016-03-18 06:25 |  | 0 | 0 | 1.95 | 1.95 | 329.55 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 8656 |  |  | - |  | Controls and instrumentation | [8 empty] | AMP CODE: |  | 52
|  | DESCRIPTION : |  | F520Unit made unavailable due to hazgas monitor problems.
TC10 | 86 | U1 | 2016-07-25 22:40 |  |  |  |  | 2016-07-25 23:08 |  | 0 | 0 | 0.467 | 0.4667 | 74.2 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 8656 |  |  | - |  | Controls and instrumentation | [8 empty] | AMP CODE: |  | 52
|  | DESCRIPTION : |  | F520The unit was made unavailable due to a false indication from a Hazardous Gas monit
TC10 | 149 | U1 | 2016-09-05 17:29 |  |  |  |  | 2016-09-05 17:53 |  | 0 | 0 | 0.4 | 0.4 | 67.6 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5041 |  |  | - |  | Fuel piping and valves | [8 empty] | AMP CODE: |  | 49
|  | DESCRIPTION : |  | F490Unit became unavailable when power was lost at the Gas Valve Controller Panels.
TC10 | 200 | U1 | 2016-10-10 21:14 |  |  |  |  | 2016-10-10 23:30 |  | 0 | 0 | 2.267 | 2.2667 | 383.067 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5240 |  |  | - |  | Fire detection and extinguishing system (including hazardous gas detection system) | [8 empty] | AMP CODE: |  | 52
|  | DESCRIPTION : |  | F520Issues with a faulty Hazardous Gas Monitor sensor kept the unit from running.
TC10 | 221 | SF | 2016-11-02 05:35 |  |  |  |  | 2016-11-02 05:47 |  | 0 | 0 | 0.2 | 0.2 | 33.8 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 4609 |  |  | - |  | Other exciter problems | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340The unit failed to start when a signal failed to send to open the 4kV breaker to t
TC10 | 266 | SF | 2016-12-19 05:05 |  |  |  |  | 2016-12-19 06:41 |  | 0 | 0 | 1.6 | 1.6 | 286.4 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5110 |  |  | - |  | Lube oil system - general | [8 empty] | AMP CODE: |  | 66
|  | DESCRIPTION : |  | F660The unit failed to start when multiple Aux Lube Oil pump pressure switches sensed
TC10 | 273 | U1 | 2016-12-23 11:22 |  |  |  |  | 2016-12-24 07:17 |  | 0 | 0 | 19.917 | 19.9167 | 3565.084 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 3861 |  |  | - |  | Fire protection system piping | [8 empty] | AMP CODE: |  | 54
|  | DESCRIPTION : |  | F540A fire protection system CO2 leak caused the unit to be unavailable until the issu
TC10 | 22 | SF | 2017-05-03 05:24 |  |  |  |  | 2017-05-03 06:57 |  | 0 | 0 | 1.55 | 1.55 | 261.95 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5041 |  |  | - |  | Fuel piping and valves | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340TC10 failed on startup after gas pressure dropped when the monitor valve closed. T
TC10 | 40 | SF | 2017-07-13 11:22 |  |  |  |  | 2017-07-13 11:31 |  | 0 | 0 | 0.15 | 0.15 | 23.85 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 9900 |  |  | - |  | Operator error | [8 empty] | AMP CODE: |  | 42
|  | DESCRIPTION : |  | F420A communications error resulted in a SF for TC10.
TC10 | 42 | U1 | 2017-07-13 20:57 |  |  |  |  | 2017-07-13 21:34 |  | 0 | 0 | 0.617 | 0.6167 | 98.05 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 4609 |  |  | - |  | Other exciter problems | [8 empty] | AMP CODE: |  | 52
|  | DESCRIPTION : |  | F520An exciter communication issue caused the unit to be unavailable. A network switch
TC10 | 49 | SF | 2017-09-24 14:16 |  |  |  |  | 2017-09-24 18:07 |  | 0 | 0 | 3.85 | 3.85 | 650.65 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5016 |  |  | - |  | High pressure compressor bleed valves | [8 empty] | AMP CODE: |  | 63
|  | DESCRIPTION : |  | F630The unit was placed on a Startup Failure once a compressor bleed valve solenoid co
TC10 | 60 | U1 | 2017-10-11 08:24 |  |  |  |  | 2017-10-11 16:19 |  | 0 | 0 | 7.917 | 7.9167 | 1337.917 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 52
|  | DESCRIPTION : |  | F520TC10 was made unavailable due to issues with the common TC9-TC10 LCI.
TC10 | 78 | SF | 2017-12-31 08:29 |  |  |  |  | 2017-12-31 08:40 |  | 0 | 0 | 0.183 | 0.1833 | 32.817 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5016 |  |  | - |  | High pressure compressor bleed valves | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340The unit failed to start when one of the compressor bleed valves did not open duri
TC10 | 34 | U1 | 2018-04-17 04:06 |  |  |  |  | 2018-04-17 05:04 |  | 0 | 0 | 0.967 | 0.9667 | 163.367 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5048 |  |  | - |  | Gas fuel system including controls and instrumentation | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340The unit became unavailable when the common TC9/TC10 fuel gas heater tripped due t
TC10 | 49 | U1 | 2018-06-12 16:47 |  |  |  |  | 2018-06-12 16:50 |  | 0 | 0 | 0.05 | 0.05 | 7.95 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5109 |  |  | - |  | Other exhaust problems (including high exhaust system temperature not attributable to a specific problem) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F340The unit tripped offline due to a failure of an exhaust frame blower pressure swit
TC10 | 50 | U1 | 2018-06-12 16:51 |  |  |  |  | 2018-06-12 16:53 |  | 0 | 0 | 0.033 | 0.0333 | 5.3 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5109 |  |  | - |  | Other exhaust problems (including high exhaust system temperature not attributable to a specific problem) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F340The unit tripped offline due to a failure of an exhaust frame blower pressure swit
TC10 | 51 | U1 | 2018-06-12 16:55 |  |  |  |  | 2018-06-12 18:37 |  | 0 | 0 | 1.7 | 1.7 | 270.3 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5109 |  |  | - |  | Other exhaust problems (including high exhaust system temperature not attributable to a specific problem) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F340The unit tripped offline due to a failure of an exhaust frame blower pressure swit
TC10 | 70 | U1 | 2018-09-07 21:47 |  |  |  |  | 2018-09-08 20:45 |  | 0 | 0 | 22.967 | 22.9667 | 3881.367 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5041 |  |  | - |  | Fuel piping and valves | [8 empty] | AMP CODE: |  | 54
|  | DESCRIPTION : |  | F540The TC10 stop ratio valve was leaking through, and a forced outage was taken to re
TC10 | 100 | SF | 2018-10-15 10:09 |  |  |  |  | 2018-10-15 12:53 |  | 0 | 0 | 2.733 | 2.7333 | 461.933 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 4899 |  |  | - |  | Other miscellaneous generator problems | [8 empty] | AMP CODE: |  | 55
|  | DESCRIPTION : |  | F550The unit was unable to start due a loose wire found on the generator/exciter contr
TC10 | 108 | U1 | 2018-10-29 15:55 |  |  |  |  | 2018-10-29 17:55 |  | 0 | 0 | 2 | 2 | 338 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5245 |  |  | - |  | Gas Turbine Control System - data highway | [8 empty] | AMP CODE: |  | 61
|  | DESCRIPTION : |  | F610The unit was made unavailable due to TC8's turbine controls upgrade. The TC8 upgra
TC10 | 10 | U1 | 2019-01-24 00:17 |  |  |  |  | 2019-01-24 03:02 |  | 0 | 0 | 2.75 | 2.75 | 492.25 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5240 |  |  | - |  | Fire detection and extinguishing system (including hazardous gas detection system) | [8 empty] | AMP CODE: |  | 55
|  | DESCRIPTION : |  | F550The unit was unavailable due to a hazardous gas detection alarm being presenet. Th
TC10 | 75 | U1 | 2019-05-08 12:40 |  |  |  |  | 2019-05-08 14:50 |  | 0 | 0 | 2.167 | 2.1667 | 366.167 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5246 |  |  | - |  | Gas Turbine Control System - hardware problems (including card failure) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340TC10 experienced a Forced Outage due to card failure in the S proceessor. The powe
TC10 | 85 | U1 | 2019-05-30 14:45 |  |  |  |  | 2019-05-30 15:18 |  | 0 | 0 | 0.55 | 0.55 | 92.95 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5048 |  |  | - |  | Gas fuel system including controls and instrumentation | [8 empty] | AMP CODE: |  | 66
|  | DESCRIPTION : |  | F660The unit was placed on outage due to decreased gas pressure caused by a temporary
TC10 | 142 | U1 | 2019-09-04 17:47 |  |  |  |  | 2019-09-04 18:52 |  | 0 | 0 | 1.083 | 1.0833 | 183.083 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 3684 |  |  | - |  | Other voltage protection devices | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340Protection Relay Faulted.
TC10 | 144 | U1 | 2019-09-05 12:58 |  |  |  |  | 2019-09-05 15:13 |  | 0 | 0 | 2.25 | 2.25 | 380.25 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5041 |  |  | - |  | Fuel piping and valves | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Fuel gas monitor valve not regulating fuel correctly. As a result caused the sudde
TC10 | 165 | U1 | 2019-11-17 23:56 |  |  |  |  | 2019-11-18 01:09 |  | 0 | 0 | 1.217 | 1.2167 | 205.617 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 4609 |  |  | - |  | Other exciter problems | [8 empty] | AMP CODE: |  | 59
|  | DESCRIPTION : |  | F590There was a communication fault with the exciter to MKVI. This caused the unit to
TC10 | 87 | U1 | 2020-12-03 13:31 |  |  |  |  | 2020-12-03 13:57 |  | 0 | 0 | 0.433 | 0.4333 | 77.567 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 4630 |  |  | - |  | Liquid cooling system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F490The unit tripped due to the cooling water fan motor going to ground.
TC10 | 6 | SF | 2021-03-02 07:49 |  |  |  |  | 2021-03-02 17:30 |  | 0 | 0 | 9.683 | 9.6833 | 1636.483 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410The unit experienced a startup failure after faulty resistors in a control circuit
TC10 | 11 | U1 | 2021-03-25 17:04 |  |  |  |  | 2021-03-25 17:14 |  | 0 | 0 | 0.167 | 0.1667 | 28.167 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340The unit was placed on a Forced Outage due to problems with the LCI.
TC10 | 16 | U1 | 2021-05-13 07:54 |  |  |  |  | 2021-05-13 12:35 |  | 0 | 0 | 4.683 | 4.6833 | 791.483 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 4609 |  |  | - |  | Other exciter problems | [8 empty] | AMP CODE: |  | 52
|  | DESCRIPTION : |  | F520The unit was made unavailable after an exciter alarm was triggered. Investigation
TC10 | 18 | U1 | 2021-05-20 21:07 |  |  |  |  | 2021-05-21 08:11 |  | 0 | 0 | 11.067 | 11.0667 | 1870.266 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5042 |  |  | - |  | Fuel nozzles/vanes | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340The unit became unavailable when a fuel purge aux stop gas valve failed to operate
TC10 | 20 | U1 | 2021-05-30 19:56 |  |  |  |  | 2021-05-30 20:11 |  | 0 | 0 | 0.25 | 0.25 | 42.25 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 3864 |  |  | - |  | Fire protection system instrumentation and controls | [8 empty] | AMP CODE: |  | 52
|  | DESCRIPTION : |  | F520The unit became unavailable due to a false fire protection alarm.
TC10 | 47 | U1 | 2021-08-13 19:18 |  |  |  |  | 2021-08-13 21:40 |  | 0 | 0 | 2.367 | 2.3667 | 376.3 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5042 |  |  | - |  | Fuel nozzles/vanes | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340The unit became unavailable when a fuel purge aux stop gas valve failed to operate
TC10 | 60 | U1 | 2021-09-14 19:20 |  |  |  |  | 2021-09-14 20:47 |  | 0 | 0 | 1.45 | 1.45 | 245.05 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 4609 |  |  | - |  | Other exciter problems | [8 empty] | AMP CODE: |  | 84
|  | DESCRIPTION : |  | F840Investigation underway, exciter tripped on Reserve state.
TC10 | 70 | SF | 2021-11-02 05:32 |  |  |  |  | 2021-11-02 06:43 |  | 0 | 0 | 1.183 | 1.1833 | 199.983 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 87
|  | DESCRIPTION : |  | F870TC10 failed to start due to load over-voltage on the TC9/TC10 LCI.
TC10 | 94 | U1 | 2022-05-20 02:12 |  |  |  |  | 2022-05-20 05:14 |  | 0 | 0 | 3.033 | 3.0333 | 512.633 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 3670 |  |  | - |  | 12-15kV transformers | [8 empty] | AMP CODE: |  | 49
|  | DESCRIPTION : |  | F490Transformer #7 failed due to lightning strike which also caused LCI for 9 and 10 t
TC10 | 292 | U1 | 2022-11-20 07:30 |  |  |  |  | 2022-11-20 08:12 |  | 0 | 0 | 0.7 | 0.7 | 118.3 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5017 |  |  | - |  | Low pressure compressor bleed valves | [8 empty] | AMP CODE: |  | 72
|  | DESCRIPTION : |  | F720Compressor Bleed Valve failed to operate properly in routine check.
TC10 | 6 | U1 | 2023-03-03 07:33 |  |  |  |  | 2023-03-03 07:41 |  | 0 | 0 | 0.133 | 0.1333 | 22.533 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 9020 |  |  | - |  | Lightning | [8 empty] | AMP CODE: |  | X0
|  | DESCRIPTION : |  | FX00Lightning strike caused a blown fuse on controls for 12" main supply fuel gass ven
TC10 | 77 | SF | 2023-07-31 12:50 |  |  |  |  | 2023-07-31 19:35 |  | 0 | 0 | 6.75 | 6.75 | 1073.25 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5017 |  |  | - |  | Low pressure compressor bleed valves | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340Compressor bleed valve #3 failed to operate at start up.
TC10 | 92 | U1 | 2023-08-11 14:08 |  |  |  |  | 2023-08-11 18:07 |  | 0 | 0 | 3.983 | 3.9833 | 633.35 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5170 |  |  | - |  | Cooling water system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F190Unit tripped on high lube oil header temperature due to 2 failed cooling water pum
TC10 | 130 | U1 | 2023-12-13 10:25 |  |  |  |  | 2023-12-13 16:31 |  | 0 | 0 | 6.1 | 6.1 | 1091.9 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5016 |  |  | - |  | High pressure compressor bleed valves | [8 empty] | AMP CODE: |  | 82
|  | DESCRIPTION : |  | F820Compressor bleed valve failed to operate due to faulty TopWorks (limit switches).
Trimble County - TC2
Unit | Event | Type | Start |  |  |  |  | End |  | GAC | NAC | Duration | Equiv Hrs | Equiv MWH | Cont | Work Start | Work End |  | Hours |  |  | Gross Capacity Impact (MW)
TC2 | 22 | U1 | 2014-05-28 07:35 |  |  |  |  | 2014-05-28 14:15 |  | 0 | 0 | 6.667 | 6.6667 | 4880 | 1 |  |  |  | 0 |  |  | 795
|  | CAUSE CODE : |  | 3499 |  |  | - |  | Other feedwater system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Forced outage due to excessive feedwater flow which caused the unit trip. High fe
TC2 | 23 | U1 | 2014-05-28 20:48 |  |  |  |  | 2014-05-29 08:55 |  | 0 | 0 | 12.117 | 12.1167 | 8869.4 | 1 |  |  |  | 0 |  |  | 795
|  | CAUSE CODE : |  | 4303 |  |  | - |  | Exhaust hood and spray controls | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820TC2 unit trip was from high steam temperature at the turbine due to inadequate sup
TC2 | 25 | U1 | 2014-06-01 13:49 |  |  |  |  | 2014-06-02 03:20 |  | 0 | 0 | 13.517 | 13.5167 | 9894.2 | 1 |  |  |  | 0 |  |  | 781
|  | CAUSE CODE : |  | 3853 |  |  | - |  | Instrument air dryers | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820TC2 tripped offline when the instrument air dryer de-pressurized.
TC2 | 26 | SF | 2014-06-02 03:20 |  |  |  |  | 2014-06-02 20:00 |  | 0 | 0 | 16.667 | 16.6667 | 12200 | 1 |  |  |  | 0 |  |  | 781
|  | CAUSE CODE : |  | 1455 |  |  | - |  | Induced draft fans | [8 empty] | AMP CODE: |  | 85
|  | DESCRIPTION : |  | F850During restart, following the forced outage, the 2A ID Fan OB vibration came in al
TC2 | 41 | U1 | 2014-06-29 00:45 |  |  |  |  | 2014-07-12 04:30 |  | 0 | 0 | 315.75 | 315.75 | 231129 | 1 |  |  |  | 0 |  |  | 781
|  | CAUSE CODE : |  | 4299 |  |  | - |  | Other hydraulic system problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830The unit was taken offline due to EHC system and turbine valve issues.
TC2 | 42 | SF | 2014-07-12 04:30 |  |  |  |  | 2014-07-12 17:37 |  | 0 | 0 | 13.117 | 13.1167 | 9601.4 | 1 |  |  |  | 0 |  |  | 781
|  | CAUSE CODE : |  | 4309 |  |  | - |  | Other turbine instrument and control problems | [8 empty] | AMP CODE: |  | 78
|  | DESCRIPTION : |  | F780Turbine temperature control issues caused the reheat temperature to elevate and re
TC2 | 43 | SF | 2014-07-12 17:37 |  |  |  |  | 2014-07-13 07:12 |  | 0 | 0 | 13.583 | 13.5833 | 9943 | 1 |  |  |  | 0 |  |  | 781
|  | CAUSE CODE : |  | 4309 |  |  | - |  | Other turbine instrument and control problems | [8 empty] | AMP CODE: |  | 40
|  | DESCRIPTION : |  | F400Startup failure due to Mark VI controls on the turbine valves not working properly
TC2 | 49 | U1 | 2014-07-23 12:22 |  |  |  |  | 2014-07-25 13:39 |  | 0 | 0 | 49.283 | 49.2833 | 36075.4 | 1 |  |  |  | 0 |  |  | 781
|  | CAUSE CODE : |  | 3671 |  |  | - |  | 12-15kV circuit breakers | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F82014kV switch gear failed causing unit trip. The failure was from a plugged AC unit
TC2 | 55 | U1 | 2014-08-11 00:48 |  |  |  |  | 2014-08-12 13:15 |  | 0 | 0 | 36.45 | 36.45 | 26681.4 | 1 |  |  |  | 0 |  |  | 781
|  | CAUSE CODE : |  | 4750 |  |  | - |  | Other generator controls and metering problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820During control valve testing, the master trip block in the EHC system had a soleno
TC2 | 64 | U1 | 2014-09-14 13:10 |  |  |  |  | 2014-09-19 10:33 |  | 0 | 0 | 117.383 | 117.3833 | 85924.6 | 1 |  |  |  | 0 |  |  | 795
|  | CAUSE CODE : |  | 1030 |  |  | - |  | "Boiler screen, wing wall, or slag screen (water tubes only)" | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F540Unit on forced outage due to tube leak. Screen tube failure lead to 7 other tube
TC2 | 67 | U1 | 2014-09-22 09:50 |  |  |  |  | 2014-09-23 02:00 |  | 0 | 0 | 16.167 | 16.1667 | 11834 | 1 |  |  |  | 0 |  |  | 795
|  | CAUSE CODE : |  | 3431 |  |  | - |  | Other feedwater valves | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F540Packing leak on feedwater start-up bypass valve required unit to be taken off-line
TC2 | 111 | U1 | 2014-12-06 04:54 |  |  |  |  | 2014-12-07 16:55 |  | 0 | 0 | 36.017 | 36.0167 | 27372.666 | 1 |  |  |  | 0 |  |  | 809
|  | CAUSE CODE : |  | 3441 |  |  | - |  | Other high pressure heater problems (see condensate system for LP and IP heater codes) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F540While attempting to isolate the 8A heater for repair, the 8A heater bypass valve p
TC2 | 112 | SF | 2014-12-07 16:55 |  |  |  |  | 2014-12-07 17:18 |  | 0 | 0 | 0.383 | 0.3833 | 291.333 | 1 |  |  |  | 0 |  |  | 809
|  | CAUSE CODE : |  | 0250 |  |  | - |  | Pulverizer feeders | [8 empty] | AMP CODE: |  | 06
|  | DESCRIPTION : |  | F0602E Coal Mill clean out conveyor issues.
TC2 | 113 | SF | 2014-12-07 17:18 |  |  |  |  | 2014-12-07 23:47 |  | 0 | 0 | 6.483 | 6.4833 | 4927.333 | 1 |  |  |  | 0 |  |  | 809
|  | CAUSE CODE : |  | 3499 |  |  | - |  | Other feedwater system problems | [8 empty] | AMP CODE: |  | 66
|  | DESCRIPTION : |  | F660Feedwater flow limit during mill swap.
TC2 | 115 | U1 | 2014-12-17 13:10 |  |  |  |  | 2014-12-20 16:29 |  | 0 | 0 | 75.317 | 75.3167 | 57240.667 | 1 |  |  |  | 0 |  |  | 809
|  | CAUSE CODE : |  | 1035 |  |  | - |  | Platen superheater | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F540Unit came offline due to a boiler tube leak on the Superheater Platen tube, Elemen
TC2 | 27 | U1 | 2015-04-20 17:45 |  |  |  |  | 2015-04-20 23:17 |  | 0 | 0 | 5.533 | 5.5333 | 4050.4 | 1 |  |  |  | 0 |  |  | 795
|  | CAUSE CODE : |  | 3979 |  |  | - |  | Other DCS problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F400DCS control issues required a manual unit MFT. MW setpoint increased to 180 and w
TC2 | 32 | U1 | 2015-05-03 02:40 |  |  |  |  | 2015-05-04 12:25 |  | 0 | 0 | 33.75 | 33.75 | 24705 | 1 |  |  |  | 0 |  |  | 795
|  | CAUSE CODE : |  | 4261 |  |  | - |  | Control valves | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F540Cold Reheat valve CRH 2-CR-CV-054A has a gasket leak
TC2 | 39 | U1 | 2015-05-07 01:44 |  |  |  |  | 2015-05-07 07:03 |  | 0 | 0 | 5.317 | 5.3167 | 3891.8 | 1 |  |  |  | 0 |  |  | 795
|  | CAUSE CODE : |  | 3416 |  |  | - |  | Other feedwater pump problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820While switching operation from MDBFP's to TDBFP's, the TDBFP's are designed to ram
TC2 | 46 | U1 | 2015-05-14 09:48 |  |  |  |  | 2015-05-15 06:45 |  | 0 | 0 | 20.95 | 20.95 | 15335.399 | 1 |  |  |  | 0 |  |  | 795
|  | CAUSE CODE : |  | 4293 |  |  | - |  | Hydraulic system pipes and valves | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F060A bolt sheared on the 2A control valve hydraulic manifold which resulted in unit t
TC2 | 49 | U1 | 2015-05-17 05:04 |  |  |  |  | 2015-05-17 15:33 |  | 0 | 0 | 10.483 | 10.4833 | 7673.8 | 1 |  |  |  | 0 |  |  | 795
|  | CAUSE CODE : |  | 3431 |  |  | - |  | Other feedwater valves | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F540The 8A HP feedwater heater bypass valve was leaking and we had to remove the unit
TC2 | 50 | SF | 2015-05-17 15:33 |  |  |  |  | 2015-05-18 00:57 |  | 0 | 0 | 9.4 | 9.4 | 6880.8 | 1 |  |  |  | 0 |  |  | 795
|  | CAUSE CODE : |  | 0385 |  |  | - |  | Igniters | [8 empty] | AMP CODE: |  | 46
|  | DESCRIPTION : |  | F460Unit MFT due to loss of D2 oil gun, causing 2D coal mill to trip off. Due to this
TC2 | 77 | U1 | 2015-07-26 08:55 |  |  |  |  | 2015-07-28 14:37 |  | 0 | 0 | 53.7 | 53.7 | 39308.4 | 1 |  |  |  | 0 |  |  | 781
|  | CAUSE CODE : |  | 3441 |  |  | - |  | Other high pressure heater problems (see condensate system for LP and IP heater codes) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820The Economizer Inlet Bypass Valve (191) had corroded terminals on the valve actuat
TC2 | 104 | U1 | 2015-09-21 09:05 |  |  |  |  | 2015-09-23 07:58 |  | 0 | 0 | 46.883 | 46.8833 | 34318.6 | 1 |  |  |  | 0 |  |  | 795
|  | CAUSE CODE : |  | 0520 |  |  | - |  | Other main steam valves (including vent and drain valves but not including the turbine stop valves) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F540Forced outage due to the packing leak in the Non-Return Main Steam MOV.
TC2 | 105 | U1 | 2015-09-23 10:47 |  |  |  |  | 2015-09-23 17:19 |  | 0 | 0 | 6.533 | 6.5333 | 4782.4 | 1 |  |  |  | 0 |  |  | 795
|  | CAUSE CODE : |  | 3974 |  |  | - |  | DCS - logic problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F040While ramping and placing three mills in service, a logic problem caused the mills
TC2 | 106 | U1 | 2015-09-23 17:57 |  |  |  |  | 2015-09-23 22:31 |  | 0 | 0 | 4.567 | 4.5667 | 3342.8 | 1 |  |  |  | 0 |  |  | 795
|  | CAUSE CODE : |  | 0380 |  |  | - |  | Light off (igniter) systems (including fuel supply) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820As unit was firing, oil guns were lost on the A Mill. This caused a trip on the A
TC2 | 107 | U1 | 2015-09-23 23:36 |  |  |  |  | 2015-09-24 03:13 |  | 0 | 0 | 3.617 | 3.6167 | 2647.4 | 1 |  |  |  | 0 |  |  | 795
|  | CAUSE CODE : |  | 3974 |  |  | - |  | DCS - logic problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Despite the Feedwater Storage Vessel being at high level, the unit was calling for
TC2 | 124 | U1 | 2015-11-05 16:17 |  |  |  |  | 2015-11-09 10:16 |  | 0 | 0 | 89.983 | 89.9833 | 68387.334 | 1 |  |  |  | 0 |  |  | 795
|  | CAUSE CODE : |  | 1090 |  |  | - |  | Other boiler tube leaks | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F540Forced outage due to tube leak repair - two (2) tube leaks were found and repaired
TC2 | 127 | U1 | 2015-11-16 21:22 |  |  |  |  | 2015-11-17 06:42 |  | 0 | 0 | 9.333 | 9.3333 | 7093.333 | 1 |  |  |  | 0 |  |  | 795
|  | CAUSE CODE : |  | 3412 |  |  | - |  | Feedwater pump drive - steam turbine | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820The unit lost the 2A TDBFP and then the 2F mill, starting a runback and then tripp
TC2 | 128 | U1 | 2015-11-17 07:13 |  |  |  |  | 2015-11-17 13:04 |  | 0 | 0 | 5.85 | 5.85 | 4446 | 1 |  |  |  | 0 |  |  | 795
|  | CAUSE CODE : |  | 3412 |  |  | - |  | Feedwater pump drive - steam turbine | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Continued problems with the 2A TDBFP - tripped on low flow due to turbine blade is
TC2 | 134 | U1 | 2015-11-30 02:35 |  |  |  |  | 2015-12-01 04:12 |  | 0 | 0 | 25.617 | 25.6167 | 19468.666 | 1 |  |  |  | 0 |  |  | 795
|  | CAUSE CODE : |  | 1400 |  |  | - |  | Forced draft fans | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F8502A Forced Draft fan vibration caused unit to MFT.
TC2 | 138 | U1 | 2015-12-09 03:38 |  |  |  |  | 2015-12-09 20:28 |  | 0 | 0 | 16.833 | 16.8333 | 12793.334 | 1 |  |  |  | 0 |  |  | 809
|  | CAUSE CODE : |  | 1480 |  |  | - |  | Other induced draft fan problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820The Radial Y Vibration probe on the TC 2A ID Fans was reading incorrectly, causing
TC2 | 15 | U1 | 2016-02-06 12:49 |  |  |  |  | 2016-02-09 01:21 |  | 0 | 0 | 60.533 | 60.5333 | 46005.333 | 1 |  |  |  | 0 |  |  | 809
|  | CAUSE CODE : |  | 1000 |  |  | - |  | Waterwall (Furnace wall) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F540Unit was manually taken offline for a boiler tuble leak. The leak was located on t
TC2 | 34 | U1 | 2016-03-16 11:50 |  |  |  |  | 2016-03-18 15:27 |  | 0 | 0 | 51.617 | 51.6167 | 38540.616 | 1 |  |  |  | 0 |  |  | 795
|  | CAUSE CODE : |  | 1000 |  |  | - |  | Waterwall (Furnace wall) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F540Forced outage due to a boiler tube leak.
TC2 | 35 | SF | 2016-03-18 15:27 |  |  |  |  | 2016-03-20 14:17 |  | 0 | 0 | 46.833 | 46.8333 | 34969.045 | 1 |  |  |  | 0 |  |  | 795
|  | CAUSE CODE : |  | 1000 |  |  | - |  | Waterwall (Furnace wall) | [8 empty] | AMP CODE: |  | 54
|  | DESCRIPTION : |  | F540As the boiler was coming back online from an outage due to a tube leak when anothe
TC2 | 38 | U1 | 2016-03-22 06:22 |  |  |  |  | 2016-03-23 09:00 |  | 0 | 0 | 26.633 | 26.6333 | 19886.31 | 1 |  |  |  | 0 |  |  | 795
|  | CAUSE CODE : |  | 1000 |  |  | - |  | Waterwall (Furnace wall) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F540Boiler tube leak caused the unit to be taken offline.
TC2 | 43 | U1 | 2016-05-09 09:45 |  |  |  |  | 2016-05-09 16:18 |  | 0 | 0 | 6.55 | 6.55 | 4890.688 | 1 |  |  |  | 0 |  |  | 795
|  | CAUSE CODE : |  | 4700 |  |  | - |  | Generator voltage control | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F870Generator protection relay trip.
TC2 | 47 | U1 | 2016-05-10 18:31 |  |  |  |  | 2016-05-13 05:10 |  | 0 | 0 | 58.65 | 58.65 | 43792.195 | 1 |  |  |  | 0 |  |  | 795
|  | CAUSE CODE : |  | 0799 |  |  | - |  | Other miscellaneous piping system problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F540Unit taken offline to repair boiler drain leak.
TC2 | 52 | U1 | 2016-05-18 19:23 |  |  |  |  | 2016-05-19 08:26 |  | 0 | 0 | 13.05 | 13.05 | 9744.043 | 1 |  |  |  | 0 |  |  | 795
|  | CAUSE CODE : |  | 4500 |  |  | - |  | Rotor windings (including damper windings and fan blades on hydro units) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F870High vibration levels on Turbine-Generator bearing #9 caused the unit to be taken
TC2 | 53 | U1 | 2016-05-19 11:17 |  |  |  |  | 2016-06-01 |  | 0 | 0 | 300.717 | 300.7167 | 224536.113 | 1 |  |  |  | 0 |  |  | 795
|  | CAUSE CODE : |  | 4500 |  |  | - |  | Rotor windings (including damper windings and fan blades on hydro units) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F870Unit continued to have problems with bearing #9 vibration and tripped on low steam
TC2 | 61 | U1 | 2016-06-01 |  |  |  |  | 2016-07-15 05:45 |  | 0 | 0 | 1061.75 | 1061.75 | 777201 | 1 |  |  |  | 0 |  |  | 781
|  | CAUSE CODE : |  | 4500 |  |  | - |  | Rotor windings (including damper windings and fan blades on hydro units) | [8 empty] | AMP CODE: |  | 87
|  | DESCRIPTION : |  | F870Unit continued to have problems with bearing #9 vibration and tripped on low steam
TC2 | 54 | SF | 2016-07-15 05:45 |  |  |  |  | 2016-07-15 07:59 |  | 0 | 0 | 2.233 | 2.2333 | 1634.8 | 1 |  |  |  | 0 |  |  | 781
|  | CAUSE CODE : |  | 4609 |  |  | - |  | Other exciter problems | [8 empty] | AMP CODE: |  | 42
|  | DESCRIPTION : |  | F420Unit was unable to startup due to missing components, the secondary fuses were not
TC2 | 55 | U1 | 2016-07-15 12:45 |  |  |  |  | 2016-07-15 18:12 |  | 0 | 0 | 5.45 | 5.45 | 3989.4 | 1 |  |  |  | 0 |  |  | 781
|  | CAUSE CODE : |  | 3499 |  |  | - |  | Other feedwater system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F660The unit tripped due to low FW flow.
TC2 | 60 | U1 | 2016-07-18 12:32 |  |  |  |  | 2016-07-19 23:59 |  | 0 | 0 | 35.45 | 35.45 | 25949.401 | 1 |  |  |  | 0 |  |  | 781
|  | CAUSE CODE : |  | 1475 |  |  | - |  | Induced draft fan controls | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F520The unit tripped due to a malfunctioned vibration sensor. The unit stayed offline
TC2 | 63 | U1 | 2016-07-31 07:42 |  |  |  |  | 2016-07-31 18:56 |  | 0 | 0 | 11.233 | 11.2333 | 8222.8 | 1 |  |  |  | 0 |  |  | 781
|  | CAUSE CODE : |  | 1488 |  |  | - |  | Air heater (regenerative) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | FP00The unit came offline due to the loss of the 2A Main Air Heater drive motor during
TC2 | 64 | U1 | 2016-07-31 19:19 |  |  |  |  | 2016-08-01 02:59 |  | 0 | 0 | 7.667 | 7.6667 | 5612 | 1 |  |  |  | 0 |  |  | 781
|  | CAUSE CODE : |  | 3681 |  |  | - |  | Other voltage circuit breakers | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F340When transferring the 14kV 2B bus to the 2B Main Aux main breaker the 14kV 2B main
TC2 | 74 | U1 | 2016-09-11 01:31 |  |  |  |  | 2016-09-11 14:58 |  | 0 | 0 | 13.45 | 13.45 | 10042.711 | 1 |  |  |  | 0 |  |  | 795
|  | CAUSE CODE : |  | 4311 |  |  | - |  | Steam Turbine Control System - hardware problems (including card failure) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F400A problem with the B Main Steam Control Vavle positioning feedback sensor caused a
TC2 | 76 | U1 | 2016-09-27 06:46 |  |  |  |  | 2016-09-27 14:43 |  | 0 | 0 | 7.95 | 7.95 | 5936.026 | 1 |  |  |  | 0 |  |  | 795
|  | CAUSE CODE : |  | 0267 |  |  | - |  | Primary air flow instrumentation | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F160The unit was tripped when a plug on a Primary Air transmitter reference line vibra
TC2 | 89 | U1 | 2016-10-30 08:46 |  |  |  |  | 2016-10-30 21:26 |  | 0 | 0 | 12.667 | 12.6667 | 9457.82 | 1 |  |  |  | 0 |  |  | 795
|  | CAUSE CODE : |  | 4311 |  |  | - |  | Steam Turbine Control System - hardware problems (including card failure) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F860When coming back up to full load from the routine deslag, the third and final LVDT
TC2 | 90 | U1 | 2016-10-30 22:03 |  |  |  |  | 2016-10-31 01:41 |  | 0 | 0 | 3.633 | 3.6333 | 2712.9 | 1 |  |  |  | 0 |  |  | 795
|  | CAUSE CODE : |  | 3431 |  |  | - |  | Other feedwater valves | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F400While coming back online, the Feedwater Discharge valve closed and the unit trippe
TC2 | 91 | U1 | 2016-10-31 02:17 |  |  |  |  | 2016-10-31 09:00 |  | 0 | 0 | 6.717 | 6.7167 | 5015.133 | 1 |  |  |  | 0 |  |  | 795
|  | CAUSE CODE : |  | 3431 |  |  | - |  | Other feedwater valves | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F400Continued issues with feedwater flow as the unit was coming back online. The unit
TC2 | 13 | U1 | 2017-02-14 14:38 |  |  |  |  | 2017-02-17 02:05 |  | 0 | 0 | 59.45 | 59.45 | 45182 | 1 |  |  |  | 0 |  |  | 809
|  | CAUSE CODE : |  | 0890 |  |  | - |  | Bottom ash systems (wet or dry) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F340The unit was placed on a Forced Outage due to the previous event involving the Sub
TC2 | 14 | U1 | 2017-02-21 22:30 |  |  |  |  | 2017-02-25 23:32 |  | 0 | 0 | 97.033 | 97.0333 | 73745.332 | 1 |  |  |  | 0 |  |  | 809
|  | CAUSE CODE : |  | 4605 |  |  | - |  | Exciter transformer | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F540A water leak from the roof of the turbine building ran onto the TC2 Exciter Transf
TC2 | 21 | U1 | 2017-04-26 18:30 |  |  |  |  | 2017-05-03 17:01 |  | 0 | 0 | 166.517 | 166.5167 | 124387.95 | 1 |  |  |  | 0 |  |  | 795
|  | CAUSE CODE : |  | 1090 |  |  | - |  | Other boiler tube leaks | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F540The unit was placed on a Forced Outage for repairs to identified tube leaks.
TC2 | 30 | U1 | 2017-05-31 13:51 |  |  |  |  | 2017-06-04 02:31 |  | 0 | 0 | 84.667 | 84.6667 | 62128.25 | 1 |  |  |  | 0 |  |  | 795
|  | CAUSE CODE : |  | 3410 |  |  | - |  | Feedwater pump | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F520The A TDBFP tripped after receiving incorrect flow feedback from the DCS, tripping
TC2 | 31 | U1 | 2017-06-04 15:46 |  |  |  |  | 2017-06-08 15:18 |  | 0 | 0 | 95.533 | 95.5333 | 69930.401 | 1 |  |  |  | 0 |  |  | 781
|  | CAUSE CODE : |  | 3410 |  |  | - |  | Feedwater pump | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | FV00The unit tripped when it experienced a loss of feedwater flow due to a trip on the
TC2 | 32 | SF | 2017-06-08 15:18 |  |  |  |  | 2017-06-08 17:28 |  | 0 | 0 | 2.167 | 2.1667 | 1586 | 1 |  |  |  | 0 |  |  | 781
|  | CAUSE CODE : |  | 4700 |  |  | - |  | Generator voltage control | [8 empty] | AMP CODE: |  | 87
|  | DESCRIPTION : |  | F870The Generator Differential alarm came in and caused the unit to fail to start.
TC2 | 46 | U2 | 2017-07-30 00:53 |  |  |  |  | 2017-08-03 19:06 |  | 0 | 0 | 114.217 | 114.2167 | 83606.6 | 1 |  |  |  | 0 |  |  | 781
|  | CAUSE CODE : |  | 1000 |  |  | - |  | Waterwall (Furnace wall) | [8 empty] | AMP CODE: |  | 54
|  | DESCRIPTION : |  | F540The unit was placed on a Forced Outage after the boiler experienced a waterwall tu
TC2 | 63 | U3 | 2017-09-22 23:57 |  |  |  |  | 2017-09-23 13:39 |  | 0 | 0 | 13.7 | 13.7 | 10233.9 | 1 |  |  |  | 0 |  |  | 795
|  | CAUSE CODE : |  | 0590 |  |  | - |  | Desuperheater/attemperator valves | [8 empty] | AMP CODE: |  | 54
|  | DESCRIPTION : |  | F540The unit was placed on a Forced Outage due to a leak found in the superheat spray
TC2 | 88 | U1 | 2017-12-10 00:17 |  |  |  |  | 2017-12-13 14:00 |  | 0 | 0 | 85.717 | 85.7167 | 65144.668 | 1 |  |  |  | 0 |  |  | 809
|  | CAUSE CODE : |  | 1000 |  |  | - |  | Waterwall (Furnace wall) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F540The unit was placed on an Unplanned Outage due to multiple waterwall leaks, which
TC2 | 95 | U1 | 2017-12-29 19:31 |  |  |  |  | 2018-01-01 |  | 0 | 0 | 52.483 | 52.4833 | 39887.333 | 1 |  |  |  | 0 |  |  | 809
|  | CAUSE CODE : |  | 1000 |  |  | - |  | Waterwall (Furnace wall) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F540The unit was placed on a Forced Outage for repairs to a tube leak on the left wate
TC2 | 1 | U1 | 2018-01-01 |  |  |  |  | 2018-01-01 11:56 |  | 0 | 0 | 11.933 | 11.9333 | 9069.333 | 1 |  |  |  | 0 |  |  | 809
|  | CAUSE CODE : |  | 1000 |  |  | - |  | Waterwall (Furnace wall) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F540The unit was placed on a Forced Outage for repairs to a tube leak on the left wate
TC2 | 25 | U1 | 2018-05-13 00:19 |  |  |  |  | 2018-05-13 06:35 |  | 0 | 0 | 6.267 | 6.2667 | 4681.2 | 1 |  |  |  | 0 |  |  | 795
|  | CAUSE CODE : |  | 9900 |  |  | - |  | Operator error | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | FP00The unit experienced an MFT after the fuel gas shutoff valve was inadvertently clo
TC2 | 34 | U1 | 2018-05-27 17:29 |  |  |  |  | 2018-05-28 10:16 |  | 0 | 0 | 16.783 | 16.7833 | 12537.15 | 1 |  |  |  | 0 |  |  | 795
|  | CAUSE CODE : |  | 1420 |  |  | - |  | Other forced draft fan problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F540TC2 was taken offline on a Forced Outage basis for repairs to the 2B F/D Fan EHC f
TC2 | 36 | U1 | 2018-05-29 20:05 |  |  |  |  | 2018-05-30 07:10 |  | 0 | 0 | 11.083 | 11.0833 | 8279.25 | 1 |  |  |  | 0 |  |  | 795
|  | CAUSE CODE : |  | 3414 |  |  | - |  | Feedwater pump local controls | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F520TC2 came offline when the MDBFP tripped and caused a loss of feedwater flow. The M
TC2 | 91 | U1 | 2018-11-01 00:42 |  |  |  |  | 2018-11-01 18:24 |  | 0 | 0 | 17.7 | 17.7 | 13221.9 | 1 |  |  |  | 0 |  |  | 795
|  | CAUSE CODE : |  | 3671 |  |  | - |  | 12-15kV circuit breakers | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F340The TC2 14kV B-side main auxiliary breaker tripped during the carding of the TC2 1
TC2 | 92 | U1 | 2018-11-01 23:23 |  |  |  |  | 2018-11-03 04:22 |  | 0 | 0 | 28.983 | 28.9833 | 21650.55 | 1 |  |  |  | 0 |  |  | 795
|  | CAUSE CODE : |  | 1488 |  |  | - |  | Air heater (regenerative) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F340The unit was taken offline when the 2B Air Heater motors failed to operate, due to
TC2 | 102 | U1 | 2018-12-16 21:52 |  |  |  |  | 2018-12-18 16:59 |  | 0 | 0 | 43.117 | 43.1167 | 32768.667 | 1 |  |  |  | 0 |  |  | 809
|  | CAUSE CODE : |  | 1060 |  |  | - |  | First reheater | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F540The unit was taken offline for repairs to a boiler tube leak.
TC2 | 18 | U1 | 2019-01-09 06:10 |  |  |  |  | 2019-01-10 02:27 |  | 0 | 0 | 20.283 | 20.2833 | 15415.334 | 1 |  |  |  | 0 |  |  | 809
|  | CAUSE CODE : |  | 4610 |  |  | - |  | Hydrogen cooling system piping and valves | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F540The unit experienced a forced outage due to a leak that developed on the "2D" gene
TC2 | 95 | U1 | 2019-05-06 |  |  |  |  | 2019-05-10 11:26 |  | 0 | 0 | 107.433 | 107.4333 | 80252.7 | 1 |  |  |  | 0 |  |  | 795
|  | CAUSE CODE : |  | 4551 |  |  | - |  | Generator bearings | [8 empty] | AMP CODE: |  | 92
|  | DESCRIPTION : |  | F920The unit was placed on a forced outage for repairs to Generator Bearing #11, which
TC2 | 96 | SF | 2019-05-10 11:26 |  |  |  |  | 2019-05-10 19:47 |  | 0 | 0 | 8.35 | 8.35 | 6237.45 | 1 |  |  |  | 0 |  |  | 795
|  | CAUSE CODE : |  | 4240 |  |  | - |  | Bearings | [8 empty] | AMP CODE: |  | V0
|  | DESCRIPTION : |  | FV00The unit failed to complete startup due to high vibration levels on Turbine Bearin
TC2 | 97 | SF | 2019-05-10 19:47 |  |  |  |  | 2019-05-12 05:49 |  | 0 | 0 | 34.033 | 34.0333 | 25422.9 | 1 |  |  |  | 0 |  |  | 795
|  | CAUSE CODE : |  | 4240 |  |  | - |  | Bearings | [8 empty] | AMP CODE: |  | V0
|  | DESCRIPTION : |  | FV00The unit failed to complete startup due to high vibration levels on Turbine Bearin
TC2 | 98 | SF | 2019-05-12 05:49 |  |  |  |  | 2019-05-13 12:02 |  | 0 | 0 | 30.217 | 30.2167 | 22571.849 | 1 |  |  |  | 0 |  |  | 795
|  | CAUSE CODE : |  | 4551 |  |  | - |  | Generator bearings | [8 empty] | AMP CODE: |  | V0
|  | DESCRIPTION : |  | FV00The unit failed to complete startup due to high vibration levels on Generator Bear
TC2 | 99 | U1 | 2019-05-13 14:04 |  |  |  |  | 2019-05-14 04:29 |  | 0 | 0 | 14.417 | 14.4167 | 10769.25 | 1 |  |  |  | 0 |  |  | 795
|  | CAUSE CODE : |  | 4551 |  |  | - |  | Generator bearings | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | FV00The unit tripped offline due to vibration levels in Generator Bearing #11. A 2 oz
TC2 | 100 | U1 | 2019-05-14 05:31 |  |  |  |  | 2019-05-14 14:32 |  | 0 | 0 | 9.017 | 9.0167 | 6735.45 | 1 |  |  |  | 0 |  |  | 795
|  | CAUSE CODE : |  | 0370 |  |  | - |  | Burner instruments and controls (except light off) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F340The unit tripped due to issues with the flame scanning equipment on D2 burner.
TC2 | 101 | U1 | 2019-05-14 14:48 |  |  |  |  | 2019-05-14 17:07 |  | 0 | 0 | 2.317 | 2.3167 | 1730.55 | 1 |  |  |  | 0 |  |  | 795
|  | CAUSE CODE : |  | 0370 |  |  | - |  | Burner instruments and controls (except light off) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F340The unit tripped due to issues with the flame scanning equipment on the D1 burner.
TC2 | 102 | SF | 2019-05-14 17:07 |  |  |  |  | 2019-05-16 01:30 |  | 0 | 0 | 32.383 | 32.3833 | 24190.35 | 1 |  |  |  | 0 |  |  | 795
|  | CAUSE CODE : |  | 3402 |  |  | - |  | Startup feedwater pump drives - all types | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340The unit failed to start when the Motor Driven Boiler Feed Pump experienced issues
TC2 | 103 | U1 | 2019-05-16 06:53 |  |  |  |  | 2019-05-16 14:52 |  | 0 | 0 | 7.983 | 7.9833 | 5963.55 | 1 |  |  |  | 0 |  |  | 795
|  | CAUSE CODE : |  | 3402 |  |  | - |  | Startup feedwater pump drives - all types | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F340The unit tripped on low feedwater flow when the Motor Driven Boiler Feed Pump expe
TC2 | 104 | U1 | 2019-05-16 17:05 |  |  |  |  | 2019-05-18 10:13 |  | 0 | 0 | 41.133 | 41.1333 | 30726.6 | 1 |  |  |  | 0 |  |  | 795
|  | CAUSE CODE : |  | 3402 |  |  | - |  | Startup feedwater pump drives - all types | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F340The unit tripped on low feedwater flow when the Motor Driven Boiler Feed Pump expe
TC2 | 112 | U1 | 2019-05-25 18:24 |  |  |  |  | 2019-05-25 22:25 |  | 0 | 0 | 4.017 | 4.0167 | 3000.45 | 1 |  |  |  | 0 |  |  | 795
|  | CAUSE CODE : |  | 1700 |  |  | - |  | "Feedwater controls (report local controls - feedwater pump, feedwater regulator valve, etc., - with component or system)" | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F340The unit tripped due to restricted feedwater flow as it was increasing in load, Th
TC2 | 130 | U1 | 2019-07-13 03:45 |  |  |  |  | 2019-07-13 12:27 |  | 0 | 0 | 8.7 | 8.7 | 6368.4 | 1 |  |  |  | 0 |  |  | 781
|  | CAUSE CODE : |  | 3431 |  |  | - |  | Other feedwater valves | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F660The TC2 B TDBFP Feedwater Control Valve servo went full-open, which caused excessi
TC2 | 135 | U2 | 2019-07-27 16:11 |  |  |  |  | 2019-07-30 19:28 |  | 0 | 0 | 75.283 | 75.2833 | 55107.401 | 1 |  |  |  | 0 |  |  | 781
|  | CAUSE CODE : |  | 1060 |  |  | - |  | First reheater | [8 empty] | AMP CODE: |  | 54
|  | DESCRIPTION : |  | F540The unit was taken offline for repairs to boiler tube leaks in the primary reheate
TC2 | 136 | U1 | 2019-07-30 22:01 |  |  |  |  | 2019-07-31 02:33 |  | 0 | 0 | 4.533 | 4.5333 | 3318.4 | 1 |  |  |  | 0 |  |  | 781
|  | CAUSE CODE : |  | 0380 |  |  | - |  | Light off (igniter) systems (including fuel supply) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F340The unit was taken offline after two mills' flame scanner indication signals were
TC2 | 137 | SF | 2019-07-31 02:33 |  |  |  |  | 2019-07-31 06:33 |  | 0 | 0 | 4 | 4 | 2928 | 1 |  |  |  | 0 |  |  | 781
|  | CAUSE CODE : |  | 4308 |  |  | - |  | Automatic turbine control systems - digital control and monitoring | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340The unit failed to start on a generator lockout due to a turbine speed loop signal
TC2 | 139 | U2 | 2019-08-10 13:00 |  |  |  |  | 2019-08-12 16:49 |  | 0 | 0 | 51.817 | 51.8167 | 37929.801 | 1 |  |  |  | 0 |  |  | 781
|  | CAUSE CODE : |  | 1000 |  |  | - |  | Waterwall (Furnace wall) | [8 empty] | AMP CODE: |  | 54
|  | DESCRIPTION : |  | F540The unit was brought offline for waterwall tube leak repairs, located on the left
TC2 | 140 | SF | 2019-08-12 16:49 |  |  |  |  | 2019-08-12 18:03 |  | 0 | 0 | 1.233 | 1.2333 | 902.8 | 1 |  |  |  | 0 |  |  | 781
|  | CAUSE CODE : |  | 4308 |  |  | - |  | Automatic turbine control systems - digital control and monitoring | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340The unit failed to start on a generator lockout due to a turbine speed loop signal
TC2 | 157 | U1 | 2019-10-16 23:00 |  |  |  |  | 2019-10-18 05:15 |  | 0 | 0 | 30.25 | 30.25 | 22596.75 | 1 |  |  |  | 0 |  |  | 795
|  | CAUSE CODE : |  | 1700 |  |  | - |  | "Feedwater controls (report local controls - feedwater pump, feedwater regulator valve, etc., - with component or system)" | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F660The unit was coming down because of a tube leak in the waterwall. While the unit w
TC2 | 9 | U2 | 2020-01-29 01:14 |  |  |  |  | 2020-01-30 02:14 |  | 0 | 0 | 25 | 25 | 18999.999 | 1 |  |  |  | 0 |  |  | 809
|  | CAUSE CODE : |  | 1090 |  |  | - |  | Other boiler tube leaks | [8 empty] | AMP CODE: |  | 54
|  | DESCRIPTION : |  | F540The unit was taken offline due to a leak in the economizer downcomer drain.
TC2 | 55 | U3 | 2020-09-02 15:51 |  |  |  |  | 2020-09-05 05:08 |  | 0 | 0 | 61.283 | 61.2833 | 45778.65 | 1 |  |  |  | 0 |  |  | 795
|  | CAUSE CODE : |  | 1000 |  |  | - |  | Waterwall (Furnace wall) | [8 empty] | AMP CODE: |  | 54
|  | DESCRIPTION : |  | F540The unit was placed on a Forced Outage due to the discovery of a waterwall leak on
TC2 | 59 | U1 | 2020-10-30 20:04 |  |  |  |  | 2020-10-31 05:07 |  | 0 | 0 | 9.05 | 9.05 | 6760.35 | 1 |  |  |  | 0 |  |  | 795
|  | CAUSE CODE : |  | 3402 |  |  | - |  | Startup feedwater pump drives - all types | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F780The unit tripped due to a lack of feedwater when the motor driven Boiler Feed Pump
TC2 | 60 | U1 | 2020-10-31 06:22 |  |  |  |  | 2020-10-31 10:45 |  | 0 | 0 | 4.383 | 4.3833 | 3274.35 | 1 |  |  |  | 0 |  |  | 795
|  | CAUSE CODE : |  | 3621 |  |  | - |  | Unit auxiliaries transformer | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820The unit failed to transfer properly from reserve auxiliary transformers to the ma
TC2 | 62 | U1 | 2020-11-04 06:40 |  |  |  |  | 2020-11-04 10:06 |  | 0 | 0 | 3.433 | 3.4333 | 2564.7 | 1 |  |  |  | 0 |  |  | 795
|  | CAUSE CODE : |  | 3431 |  |  | - |  | Other feedwater valves | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F340The unit tripped due to low feedwater flow after the Motor Driven Boiler Feed Pump
TC2 | 65 | U1 | 2020-11-05 22:28 |  |  |  |  | 2020-11-06 03:48 |  | 0 | 0 | 5.333 | 5.3333 | 3984 | 1 |  |  |  | 0 |  |  | 795
|  | CAUSE CODE : |  | 4290 |  |  | - |  | Hydraulic system pumps | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F340The unit experienced a Forced Outage when the EHC pressure fell due to the one EHC
TC2 | 66 | U1 | 2020-11-06 03:57 |  |  |  |  | 2020-11-07 08:28 |  | 0 | 0 | 28.517 | 28.5167 | 21301.95 | 1 |  |  |  | 0 |  |  | 795
|  | CAUSE CODE : |  | 4099 |  |  | - |  | Other high pressure turbine problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F780The unit experienced a forced outage when the HP Turbine Exhaust temperature excee
TC2 | 5 | U1 | 2021-01-25 18:30 |  |  |  |  | 2021-01-31 13:07 |  | 0 | 0 | 138.617 | 138.6167 | 105348.667 | 1 |  |  |  | 0 |  |  | 809
|  | CAUSE CODE : |  | 0540 |  |  | - |  | Hot reheat steam piping up to turbine stop valves | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F540The unit was removed from service for repairs to a HRH steam leak.
TC2 | 6 | U1 | 2021-01-31 14:05 |  |  |  |  | 2021-01-31 15:29 |  | 0 | 0 | 1.4 | 1.4 | 1064 | 1 |  |  |  | 0 |  |  | 809
|  | CAUSE CODE : |  | 4499 |  |  | - |  | Other miscellaneous steam turbine problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F750The unit tripped due to high HP Turbine exhaust temperature.
TC2 | 17 | U1 | 2021-04-24 15:30 |  |  |  |  | 2021-04-28 13:15 |  | 0 | 0 | 93.75 | 93.75 | 70031.25 | 1 |  |  |  | 0 |  |  | 795
|  | CAUSE CODE : |  | 1035 |  |  | - |  | Platen superheater | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F540The unit load was taken offline for repairs to a leak in an outlet stub tube on th
TC2 | 77 | U1 | 2021-12-30 03:55 |  |  |  |  | 2021-12-30 09:17 |  | 0 | 0 | 5.367 | 5.3667 | 4078.667 | 1 |  |  |  | 0 |  |  | 809
|  | CAUSE CODE : |  | 0256 |  |  | - |  | Seal air system (air to pulverizers) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | FP00Seal air was inadvertently removed from the TC2 Mill causing an MFT.
TC2 | 12 | U1 | 2022-02-14 16:26 |  |  |  |  | 2022-02-17 10:01 |  | 0 | 0 | 65.583 | 65.5833 | 49843.334 | 1 |  |  |  | 0 |  |  | 809
|  | CAUSE CODE : |  | 1000 |  |  | - |  | Waterwall (Furnace wall) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F540The unit was taken offline to make repairs to a boiler tube leak located on the ri
TC2 | 15 | U1 | 2022-02-25 23:32 |  |  |  |  | 2022-02-25 23:33 |  | 0 | 0 | 0.017 | 0.0167 | 12.667 | 1 |  |  |  | 0 |  |  | 809
|  | CAUSE CODE : |  | 3431 |  |  | - |  | Other feedwater valves | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F520The unit tripped offline when coming down for the TC2 Spring 2022 Outage, due to l
TC2 | 16 | U1 | 2022-04-03 19:44 |  |  |  |  | 2022-04-03 19:45 |  | 0 | 0 | 0.017 | 0.0167 | 12.45 | 1 |  |  |  | 0 |  |  | 795
|  | CAUSE CODE : |  | 3430 |  |  | - |  | Feedwater regulating (boiler level control) valve | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F340The unit tripped offline when coming down for a TC2 Maintenance Outage, due to a b
TC2 | 42 | U1 | 2022-10-20 22:46 |  |  |  |  | 2022-10-23 20:20 |  | 0 | 0 | 69.567 | 69.5667 | 51966.3 | 1 |  |  |  | 0 |  |  | 795
|  | CAUSE CODE : |  | 1000 |  |  | - |  | Waterwall (Furnace wall) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F540Unit was taken offline on forced outage due to tube leaks on front and right walls
TC2 | 7 | U1 | 2023-03-11 01:44 |  |  |  |  | 2023-03-11 03:30 |  | 0 | 0 | 1.767 | 1.7667 | 1319.7 | 1 |  |  |  | 0 |  |  | 795
|  | CAUSE CODE : |  | 3499 |  |  | - |  | Other feedwater system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820The unit was tripped on low feedwater flow while dropping load for the planned out
TC2 | 11 | U1 | 2023-05-15 21:28 |  |  |  |  | 2023-05-16 03:23 |  | 0 | 0 | 5.917 | 5.9167 | 4419.75 | 1 |  |  |  | 0 |  |  | 795
|  | CAUSE CODE : |  | 3499 |  |  | - |  | Other feedwater system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820The unit was tripped on low feedwater flow while coming up on load from the planne
TC2 | 26 | U1 | 2023-10-31 10:29 |  |  |  |  | 2023-10-31 15:14 |  | 0 | 0 | 4.75 | 4.75 | 3548.25 | 1 |  |  |  | 0 |  |  | 795
|  | CAUSE CODE : |  | 3690 |  |  | - |  | "Station Service Power Distribution System, General" | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820The unit tripped due to low inlet main steam temperature caused by power loss to M
TC2 | 27 | U1 | 2023-10-31 16:09 |  |  |  |  | 2023-11-01 19:43 |  | 0 | 0 | 27.567 | 27.5667 | 20592.301 | 1 |  |  |  | 0 |  |  | 795
|  | CAUSE CODE : |  | 3661 |  |  | - |  | 4000-7000 volt circuit breakers | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820The unit tripped due to 7 kV main breaker opening up.
Trimble County - TC5
Unit | Event | Type | Start |  |  |  |  | End |  | GAC | NAC | Duration | Equiv Hrs | Equiv MWH | Cont | Work Start | Work End |  | Hours |  |  | Gross Capacity Impact (MW)
TC5 | 2 | U1 | 2014-01-03 11:04 |  |  |  |  | 2014-01-03 13:20 |  | 0 | 0 | 2.267 | 2.2667 | 398.933 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5240 |  |  | - |  | Fire detection and extinguishing system (including hazardous gas detection system) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F150Unit tripped on fire protection alarm due to condensation within fire protection p
TC5 | 4 | U1 | 2014-01-06 12:15 |  |  |  |  | 2014-01-06 14:08 |  | 0 | 0 | 1.883 | 1.8833 | 331.467 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5246 |  |  | - |  | Gas Turbine Control System - hardware problems (including card failure) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F520Unit tripped on high exhaust temperature differential from a failed control system
TC5 | 6 | U1 | 2014-01-07 01:25 |  |  |  |  | 2014-01-07 05:50 |  | 0 | 0 | 4.417 | 4.4167 | 777.333 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5246 |  |  | - |  | Gas Turbine Control System - hardware problems (including card failure) | [8 empty] | AMP CODE: |  | 52
|  | DESCRIPTION : |  | F520Forced outage due to compressor inlet thermocouple disagreement from a failed cont
TC5 | 12 | U1 | 2014-02-11 06:16 |  |  |  |  | 2014-02-11 08:35 |  | 0 | 0 | 2.317 | 2.3167 | 407.733 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5079 |  |  | - |  | Other combustor problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F460Unit tripped due to flameout.
TC5 | 14 | SF | 2014-02-17 06:28 |  |  |  |  | 2014-02-17 06:40 |  | 0 | 0 | 0.2 | 0.2 | 35.2 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 41
|  | DESCRIPTION : |  | F410Startup failure due to issue with LCI.
TC5 | 16 | U1 | 2014-02-17 10:43 |  |  |  |  | 2014-02-17 11:57 |  | 0 | 0 | 1.233 | 1.2333 | 217.067 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 52
|  | DESCRIPTION : |  | F520Forced outage to change out resistivity probe on the cooling system for the LCI.
TC5 | 18 | SF | 2014-02-17 17:45 |  |  |  |  | 2014-02-17 20:14 |  | 0 | 0 | 2.483 | 2.4833 | 437.067 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 32
|  | DESCRIPTION : |  | F320Startup failure due to low resistivity in the cooling water for the LCI. Changed
TC5 | 23 | SF | 2014-03-02 21:40 |  |  |  |  | 2014-03-03 01:59 |  | 0 | 0 | 4.317 | 4.3167 | 759.734 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5016 |  |  | - |  | High pressure compressor bleed valves | [8 empty] | AMP CODE: |  | 48
|  | DESCRIPTION : |  | F480Startup failure due to issue with compressor bleed valve.
TC5 | 43 | U1 | 2014-03-28 05:45 |  |  |  |  | 2014-03-28 06:14 |  | 0 | 0 | 0.483 | 0.4833 | 85.067 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5049 |  |  | - |  | Other fuel system problems | [8 empty] | AMP CODE: |  | 78
|  | DESCRIPTION : |  | F780Forced outage due to over temperature of the fuel gas heater.
TC5 | 49 | U1 | 2014-04-02 22:30 |  |  |  |  | 2014-04-03 02:13 |  | 0 | 0 | 3.717 | 3.7167 | 583.517 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5246 |  |  | - |  | Gas Turbine Control System - hardware problems (including card failure) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Lightning Strike.
TC5 | 52 | U1 | 2014-04-04 09:17 |  |  |  |  | 2014-04-04 14:32 |  | 0 | 0 | 5.25 | 5.25 | 824.25 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5049 |  |  | - |  | Other fuel system problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Replace Transmitter.
TC5 | 131 | U1 | 2014-08-30 18:20 |  |  |  |  | 2014-08-30 18:35 |  | 0 | 0 | 0.25 | 0.25 | 39.25 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 3649 |  |  | - |  | Other AC instrument power problems | [8 empty] | AMP CODE: |  | 70
|  | DESCRIPTION : |  | F820480 VAC breaker in PEECC #5 tripped killing power to LCI Compartment.
TC5 | 134 | SF | 2014-09-02 11:42 |  |  |  |  | 2014-09-02 12:07 |  | 0 | 0 | 0.417 | 0.4167 | 65.417 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340Unit failed to start due fault on LCI controller. Both the LCI and EX2000 controll
TC5 | 136 | U1 | 2014-09-02 12:18 |  |  |  |  | 2014-09-02 13:20 |  | 0 | 0 | 1.033 | 1.0333 | 162.233 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5190 |  |  | - |  | Other auxiliary system problems | [8 empty] | AMP CODE: |  | 09
|  | DESCRIPTION : |  | F090Unit cranked to partial speed and starting sequence stopped. Upon troubleshooting
TC5 | 140 | SF | 2014-09-04 12:09 |  |  |  |  | 2014-09-04 13:01 |  | 0 | 0 | 0.867 | 0.8667 | 136.067 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340Unit failed to start related to previous events #134 and 136, this time we were ab
TC5 | 142 | SF | 2014-09-04 15:23 |  |  |  |  | 2014-09-04 17:06 |  | 0 | 0 | 1.717 | 1.7167 | 269.517 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340Unit failed to start because trend showed that the EX2000 was not getting enough D
TC5 | 144 | SF | 2014-09-05 08:10 |  |  |  |  | 2014-09-05 08:40 |  | 0 | 0 | 0.5 | 0.5 | 78.5 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340Unit failed to start and this time trend picked up information that puts the LCI b
TC5 | 172 | U1 | 2014-11-15 15:03 |  |  |  |  | 2014-11-15 16:09 |  | 0 | 0 | 1.1 | 1.1 | 193.6 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5043 |  |  | - |  | Fuel filters | [8 empty] | AMP CODE: |  | 66
|  | DESCRIPTION : |  | F660Relief valve on TC9/10 fuel gas heater lifted, and all gas turbines needed to be u
TC5 | 176 | U1 | 2014-11-18 06:11 |  |  |  |  | 2014-11-18 06:42 |  | 0 | 0 | 0.517 | 0.5167 | 90.933 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5049 |  |  | - |  | Other fuel system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Lean blow out due to low ambient temperatures, moved NOx slider to 1.2 and machine
TC5 | 191 | U1 | 2014-12-06 19:06 |  |  |  |  | 2014-12-06 21:28 |  | 0 | 0 | 2.367 | 2.3667 | 416.533 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5108 |  |  | - |  | High engine exhaust temperature | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F750Exhaust thermocouple #1 failed high before reaching mode 6, and this kept the unit
TC5 | 11 | U1 | 2015-02-15 01:03 |  |  |  |  | 2015-02-15 01:33 |  | 0 | 0 | 0.5 | 0.5 | 88 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 3629 |  |  | - |  | Other switchyard or high voltage system problems - external | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820System Disturbance.
TC5 | 12 | U1 | 2015-02-17 06:38 |  |  |  |  | 2015-02-17 08:30 |  | 0 | 0 | 1.867 | 1.8667 | 328.533 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5017 |  |  | - |  | Low pressure compressor bleed valves | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Unit tripped on lean blow out and on the re-start the compressor bleed valves held
TC5 | 13 | SF | 2015-02-17 08:30 |  |  |  |  | 2015-02-17 09:30 |  | 0 | 0 | 1 | 1 | 176 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340Loose wire on 89SS switch caused failure to engage.
TC5 | 14 | U1 | 2015-02-19 01:17 |  |  |  |  | 2015-02-19 02:42 |  | 0 | 0 | 1.417 | 1.4167 | 249.333 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5079 |  |  | - |  | Other combustor problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Unit tripped on lean blow out due to NOx adjustment set too low to maintain flame
TC5 | 15 | SF | 2015-02-19 02:42 |  |  |  |  | 2015-02-19 07:57 |  | 0 | 0 | 5.25 | 5.25 | 924 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340Loose wire problem on 89SS switch caused a not ready to start condition.
TC5 | 16 | U1 | 2015-02-19 09:05 |  |  |  |  | 2015-02-19 12:37 |  | 0 | 0 | 3.533 | 3.5333 | 621.867 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5079 |  |  | - |  | Other combustor problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Unit tripped on lean blow out, extreme cold conditions caused autotune to lean com
TC5 | 17 | U1 | 2015-02-19 22:06 |  |  |  |  | 2015-02-19 23:31 |  | 0 | 0 | 1.417 | 1.4167 | 249.333 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5048 |  |  | - |  | Gas fuel system including controls and instrumentation | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820The autotune program was turned off, and this causes the machine to be susceptible
TC5 | 18 | SF | 2015-02-19 23:31 |  |  |  |  | 2015-02-19 23:49 |  | 0 | 0 | 0.3 | 0.3 | 52.8 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340This was not an excitation issue. The LCI was not reset after the previous start a
TC5 | 19 | U1 | 2015-02-20 14:09 |  |  |  |  | 2015-02-20 14:41 |  | 0 | 0 | 0.533 | 0.5333 | 93.867 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5079 |  |  | - |  | Other combustor problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820This trip is similar to event #17, fuel gas heater not working causing low inlet f
TC5 | 21 | U1 | 2015-02-23 02:07 |  |  |  |  | 2015-02-23 04:38 |  | 0 | 0 | 2.517 | 2.5167 | 442.933 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5079 |  |  | - |  | Other combustor problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Manual shut down signal initiated due high NOx readings caused by low fuel gas inl
TC5 | 30 | U1 | 2015-03-04 19:07 |  |  |  |  | 2015-03-04 23:36 |  | 0 | 0 | 4.483 | 4.4833 | 789.067 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5079 |  |  | - |  | Other combustor problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Fuel gas heater temperature regulator failed, and there was a frozen solenoid vent
TC5 | 42 | SF | 2015-04-12 18:51 |  |  |  |  | 2015-04-12 19:58 |  | 0 | 0 | 1.117 | 1.1167 | 175.317 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340LCI failed to start due to high compartment termperature. Battery changed on therm
TC5 | 56 | U1 | 2015-05-07 21:30 |  |  |  |  | 2015-05-08 00:50 |  | 0 | 0 | 3.333 | 3.3333 | 523.333 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 3610 |  |  | - |  | Switchyard circuit breakers - external (not OMC) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F33052G breaker on TC7 failed to open, immediate action to isolate unit from grid was
TC5 | 72 | U1 | 2015-06-13 10:41 |  |  |  |  | 2015-06-13 15:46 |  | 0 | 0 | 5.083 | 5.0833 | 798.083 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 3611 |  |  | - |  | Switchyard circuit breakers - external (OMC) | [8 empty] | AMP CODE: |  | 03
|  | DESCRIPTION : |  | F030"A" Bus lock out due to TC7 C Phase Main Breaker failure. This forced an outage o
TC5 | 83 | SF | 2015-06-21 12:12 |  |  |  |  | 2015-06-21 17:55 |  | 0 | 0 | 5.717 | 5.7167 | 897.517 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5108 |  |  | - |  | High engine exhaust temperature | [8 empty] | AMP CODE: |  | 75
|  | DESCRIPTION : |  | F750TC5 had exhaust thermocouple #12 already reading low due to an exhaust duct leak,
TC5 | 85 | U1 | 2015-06-22 17:09 |  |  |  |  | 2015-06-22 18:55 |  | 0 | 0 | 1.767 | 1.7667 | 277.367 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5108 |  |  | - |  | High engine exhaust temperature | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Machine was running with one of three exahaust spreads high, a second thermocouple
TC5 | 87 | U1 | 2015-06-25 08:00 |  |  |  |  | 2015-06-25 14:47 |  | 0 | 0 | 6.783 | 6.7833 | 1064.983 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5098 |  |  | - |  | Expansion joints | [8 empty] | AMP CODE: |  | 75
|  | DESCRIPTION : |  | F750The machine has a torn exhaust duct expansion joint, and the temporary patch neede
TC5 | 89 | U1 | 2015-06-25 15:42 |  |  |  |  | 2015-06-26 11:13 |  | 0 | 0 | 19.517 | 19.5167 | 3064.117 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5108 |  |  | - |  | High engine exhaust temperature | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820The expansion joint patch was fixed in an attempt to fix the problem with the exha
TC5 | 92 | SF | 2015-07-06 12:08 |  |  |  |  | 2015-07-06 14:04 |  | 0 | 0 | 1.933 | 1.9333 | 307.4 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340LCI cooling water resistivity did not allow LCI to start. This was not an exciter
TC5 | 97 | U1 | 2015-07-25 15:26 |  |  |  |  | 2015-07-28 00:08 |  | 0 | 0 | 56.7 | 56.7 | 9015.3 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 3610 |  |  | - |  | Switchyard circuit breakers - external (not OMC) | [8 empty] | AMP CODE: |  | 16
|  | DESCRIPTION : |  | F160TC5 main line breaker would not close when trying to sychronize unit, after variou
TC5 | 143 | U1 | 2015-11-06 11:36 |  |  |  |  | 2015-11-06 13:14 |  | 0 | 0 | 1.633 | 1.6333 | 292.367 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5109 |  |  | - |  | Other exhaust problems (including high exhaust system temperature not attributable to a specific problem) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Exhaust thermocouple #16 failed high causing machine to trip. Had to replace wirin
TC5 | 145 | U1 | 2015-11-08 19:14 |  |  |  |  | 2015-11-10 15:10 |  | 0 | 0 | 43.933 | 43.9333 | 7864.066 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 3610 |  |  | - |  | Switchyard circuit breakers - external (not OMC) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Loss of control air in main line breaker due to a faulty air compressor. Machine t
TC5 | 158 | SF | 2015-12-03 06:37 |  |  |  |  | 2015-12-03 07:15 |  | 0 | 0 | 0.633 | 0.6333 | 113.367 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340The neutral disconnect switch (89ND) failed to close at full speed no load (FSNL)
TC5 | 161 | SF | 2015-12-04 05:37 |  |  |  |  | 2015-12-04 06:17 |  | 0 | 0 | 0.667 | 0.6667 | 119.333 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5048 |  |  | - |  | Gas fuel system including controls and instrumentation | [8 empty] | AMP CODE: |  | 09
|  | DESCRIPTION : |  | F090The quaternary gas control valve calibration drifted to point beyond control setti
TC5 | 5 | U1 | 2016-01-17 22:48 |  |  |  |  | 2016-01-17 23:30 |  | 0 | 0 | 0.7 | 0.7 | 125.3 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 9613 |  |  | - |  | NOx stack emissions - gas turbines | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Unit manually taken off line due to high NOx emissions, changing load during opera
TC5 | 6 | U1 | 2016-01-18 05:10 |  |  |  |  | 2016-01-18 06:07 |  | 0 | 0 | 0.95 | 0.95 | 170.05 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5108 |  |  | - |  | High engine exhaust temperature | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Unit tripped on exhaust temperature spread, further investigation revealed two out
TC5 | 7 | U1 | 2016-01-18 06:50 |  |  |  |  | 2016-01-18 08:04 |  | 0 | 0 | 1.233 | 1.2333 | 220.767 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5048 |  |  | - |  | Gas fuel system including controls and instrumentation | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830The vent for the final fuel gas filter separator lifted while machine was online,
TC5 | 15 | SF | 2016-02-16 08:37 |  |  |  |  | 2016-02-16 11:34 |  | 0 | 0 | 2.95 | 2.95 | 528.05 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340The unit tripped off during startup, originally thought to be due to exciter issue
TC5 | 16 | SF | 2016-02-16 11:34 |  |  |  |  | 2016-02-17 15:29 |  | 0 | 0 | 27.917 | 27.9167 | 4997.084 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340Continued Startup Failure from LCI ground fault detection.
TC5 | 18 | U1 | 2016-02-17 17:30 |  |  |  |  | 2016-02-18 01:39 |  | 0 | 0 | 8.15 | 8.15 | 1458.85 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 4860 |  |  | - |  | Generator neutral grounding equipment | [8 empty] | AMP CODE: |  | V0
|  | DESCRIPTION : |  | FV00The 89ND switch closed itself under vibration during operation, which controls a l
TC5 | 23 | U1 | 2016-02-29 08:30 |  |  |  |  | 2016-02-29 12:18 |  | 0 | 0 | 3.8 | 3.8 | 680.2 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5041 |  |  | - |  | Fuel piping and valves | [8 empty] | AMP CODE: |  | 06
|  | DESCRIPTION : |  | F060TC5/6 Gas Heater pressure regulating valve PCV-102 failed, and needed replacement.
TC5 | 25 | U1 | 2016-03-01 08:13 |  |  |  |  | 2016-03-01 08:43 |  | 0 | 0 | 0.5 | 0.5 | 84.5 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 9131 |  |  | - |  | Lack of fuel (interruptible supply of fuel part of fuel contract) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F340A Texas Gas supply valve electro-pneumatic transducer failed, causing the valve to
TC5 | 30 | U1 | 2016-03-08 18:24 |  |  |  |  | 2016-03-08 20:01 |  | 0 | 0 | 1.617 | 1.6167 | 273.217 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 8790 |  |  | - |  | Miscellaneous CEMS problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F700Problem with CEM calibration failure alarm after startup. The alarm was recalibrat
TC5 | 67 | SF | 2016-05-11 12:49 |  |  |  |  | 2016-05-14 14:38 |  | 0 | 0 | 73.817 | 73.8167 | 12475.016 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 4810 |  |  | - |  | Generator output breaker | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340MOD failed to close.
TC5 | 80 | U1 | 2016-06-13 23:49 |  |  |  |  | 2016-06-14 03:47 |  | 0 | 0 | 3.967 | 3.9667 | 630.7 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 8790 |  |  | - |  | Miscellaneous CEMS problems | [8 empty] | AMP CODE: |  | 06
|  | DESCRIPTION : |  | F060A CEMS Monitor was not operating correctly. The unit was unavailable while repairs
TC5 | 90 | SF | 2016-06-25 11:44 |  |  |  |  | 2016-06-25 12:39 |  | 0 | 0 | 0.917 | 0.9167 | 145.75 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 70
|  | DESCRIPTION : |  | F700A blown fuse in the motor heater of the LCI caused multiple alarms on the unit.
TC5 | 93 | SF | 2016-06-26 10:24 |  |  |  |  | 2016-06-26 10:34 |  | 0 | 0 | 0.167 | 0.1667 | 26.5 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340The unit was made unavailable due to continued problems with a problematic LCI fus
TC5 | 95 | SF | 2016-06-26 10:54 |  |  |  |  | 2016-06-27 12:44 |  | 0 | 0 | 25.833 | 25.8333 | 4107.5 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340The underlying cause of the fuse problems was found to be with the 89SS switch lin
TC5 | 145 | U1 | 2016-10-25 10:24 |  |  |  |  | 2016-10-25 12:32 |  | 0 | 0 | 2.133 | 2.1333 | 360.533 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340The LCI Communication system failed, making the unit unavailable for the duration
TC5 | 170 | SF | 2016-12-20 05:25 |  |  |  |  | 2016-12-20 08:45 |  | 0 | 0 | 3.333 | 3.3333 | 596.667 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5016 |  |  | - |  | High pressure compressor bleed valves | [8 empty] | AMP CODE: |  | 72
|  | DESCRIPTION : |  | F720The unit failed to start due to a compressor bleed valve failing to completely ope
TC5 | 1 | SF | 2017-01-06 05:29 |  |  |  |  | 2017-01-06 09:41 |  | 0 | 0 | 4.2 | 4.2 | 751.8 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 4609 |  |  | - |  | Other exciter problems | [8 empty] | AMP CODE: |  | 52
|  | DESCRIPTION : |  | F520An exciter control board was receiving incorrect field current feedback. The contr
TC5 | 6 | U1 | 2017-01-11 15:18 |  |  |  |  | 2017-01-11 17:45 |  | 0 | 0 | 2.45 | 2.45 | 438.55 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 4609 |  |  | - |  | Other exciter problems | [8 empty] | AMP CODE: |  | 52
|  | DESCRIPTION : |  | F520An exciter control board was receiving incorrect field current feedback, resulting
TC5 | 8 | U1 | 2017-01-12 09:39 |  |  |  |  | 2017-01-12 10:30 |  | 0 | 0 | 0.85 | 0.85 | 152.15 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340The LCI Communication system was not operating correctly, making the unit unavaila
TC5 | 10 | U1 | 2017-01-13 07:10 |  |  |  |  | 2017-01-13 07:40 |  | 0 | 0 | 0.5 | 0.5 | 89.5 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340The LCI Communication system was not operating correctly, making the unit unavaila
TC5 | 19 | U1 | 2017-02-02 15:03 |  |  |  |  | 2017-02-03 02:42 |  | 0 | 0 | 11.65 | 11.65 | 2085.35 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 3610 |  |  | - |  | Switchyard circuit breakers - external (not OMC) | [8 empty] | AMP CODE: |  | 66
|  | DESCRIPTION : |  | F660The unit's line breaker air line did not have adequate pressure to close the line,
TC5 | 26 | U1 | 2017-02-21 12:54 |  |  |  |  | 2017-02-21 19:23 |  | 0 | 0 | 6.483 | 6.4833 | 1160.517 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5041 |  |  | - |  | Fuel piping and valves | [8 empty] | AMP CODE: |  | 54
|  | DESCRIPTION : |  | F540A fuel gas leak developed on a strainer inspection cover gasket. The gasket was re
TC5 | 33 | U1 | 2017-03-01 06:31 |  |  |  |  | 2017-03-01 07:26 |  | 0 | 0 | 0.917 | 0.9167 | 154.917 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 40
|  | DESCRIPTION : |  | F400Both TC5 and TC6 Exciters and the shared LCI tripped for unknown reasons during a
TC5 | 43 | SF | 2017-03-22 05:11 |  |  |  |  | 2017-03-22 05:22 |  | 0 | 0 | 0.183 | 0.1833 | 30.983 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 4609 |  |  | - |  | Other exciter problems | [8 empty] | AMP CODE: |  | 40
|  | DESCRIPTION : |  | F400The TC5 generator field current signal exceeded normal tolerances which caused an
TC5 | 62 | U1 | 2017-05-27 19:54 |  |  |  |  | 2017-05-27 20:07 |  | 0 | 0 | 0.217 | 0.2167 | 36.617 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 9020 |  |  | - |  | Lightning | [8 empty] | AMP CODE: |  | 70
|  | DESCRIPTION : |  | F700A lightning strike caused the unit to be unavailable. The unit was unavailable due
TC5 | 64 | U1 | 2017-05-27 21:22 |  |  |  |  | 2017-05-27 23:40 |  | 0 | 0 | 2.3 | 2.3 | 388.7 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340The unit was unavailable due to a TC5/TC6 LCI issue. The breaker for the LCI cooli
TC5 | 84 | SF | 2017-07-19 12:43 |  |  |  |  | 2017-07-19 13:02 |  | 0 | 0 | 0.317 | 0.3167 | 50.35 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5050 |  |  | - |  | Ignition system | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340TC5 has a spark rod which remained retracted during startup. Maintenance placed th
TC5 | 92 | U1 | 2017-07-28 06:11 |  |  |  |  | 2017-07-28 11:23 |  | 0 | 0 | 5.2 | 5.2 | 826.8 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 4609 |  |  | - |  | Other exciter problems | [8 empty] | AMP CODE: |  | 06
|  | DESCRIPTION : |  | F060The unit became unavailable on a Forced Outage when an exciter control board faile
TC5 | 98 | U1 | 2017-08-10 19:53 |  |  |  |  | 2017-08-10 20:58 |  | 0 | 0 | 1.083 | 1.0833 | 172.25 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5041 |  |  | - |  | Fuel piping and valves | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340The TC5 Monitor Valve positioner failed causing the valve to close and make the un
TC5 | 106 | U1 | 2017-09-01 07:12 |  |  |  |  | 2017-09-01 10:56 |  | 0 | 0 | 3.733 | 3.7333 | 630.933 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5041 |  |  | - |  | Fuel piping and valves | [8 empty] | AMP CODE: |  | 63
|  | DESCRIPTION : |  | F630TC5 gas relief valve on final filter leaking through. Small shaving of metal preve
TC5 | 108 | SF | 2017-09-25 12:12 |  |  |  |  | 2017-09-26 03:13 |  | 0 | 0 | 15.017 | 15.0167 | 2537.817 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 3629 |  |  | - |  | Other switchyard or high voltage system problems - external | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340The C phase on the MOD did not close in, creating a Startup Failure for TC5. The i
TC5 | 124 | SF | 2017-11-03 05:40 |  |  |  |  | 2017-11-03 06:02 |  | 0 | 0 | 0.367 | 0.3667 | 61.967 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5050 |  |  | - |  | Ignition system | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340The unit failed to start when the spark rods had issues and did not allow for fuel
TC5 | 137 | SF | 2017-12-07 07:57 |  |  |  |  | 2017-12-07 08:35 |  | 0 | 0 | 0.633 | 0.6333 | 113.367 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5001 |  |  | - |  | Inlet air vanes/nozzles | [8 empty] | AMP CODE: |  | 72
|  | DESCRIPTION : |  | F720The unit failed to start when the inlet guide vanes had issues with positioning on
TC5 | 141 | U1 | 2017-12-12 16:09 |  |  |  |  | 2017-12-12 20:25 |  | 0 | 0 | 4.267 | 4.2667 | 763.733 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5001 |  |  | - |  | Inlet air vanes/nozzles | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340The unit was placed on an Immediate Forced Outage to replace the servo of the inle
TC5 | 144 | U1 | 2017-12-28 15:08 |  |  |  |  | 2017-12-28 16:13 |  | 0 | 0 | 1.083 | 1.0833 | 193.917 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 3631 |  |  | - |  | 400-700 volt circuit breakers | [8 empty] | AMP CODE: |  | 33
|  | DESCRIPTION : |  | F820The unit was placed on a Forced Outage when the 480 V Power Center Breaker feeding
TC5 | 146 | U1 | 2017-12-29 01:47 |  |  |  |  | 2017-12-29 03:51 |  | 0 | 0 | 2.067 | 2.0667 | 369.933 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5048 |  |  | - |  | Gas fuel system including controls and instrumentation | [8 empty] | AMP CODE: |  | 66
|  | DESCRIPTION : |  | F660The unit was placed on a Forced Outage to address a dropping fuel gas pressure sup
TC5 | 148 | SF | 2017-12-30 16:57 |  |  |  |  | 2017-12-30 17:21 |  | 0 | 0 | 0.4 | 0.4 | 71.6 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5041 |  |  | - |  | Fuel piping and valves | [8 empty] | AMP CODE: |  | 13
|  | DESCRIPTION : |  | F130The unit failed to start when fuel gas pressure spiked and caused the fuel gas shu
TC5 | 5 | U1 | 2018-01-03 09:22 |  |  |  |  | 2018-01-03 15:01 |  | 0 | 0 | 5.65 | 5.65 | 1011.35 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 3681 |  |  | - |  | Other voltage circuit breakers | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340One of the three TC6 345 kV main breaker failed to open, causing the Main Switchya
TC5 | 7 | U1 | 2018-01-04 06:33 |  |  |  |  | 2018-01-04 17:07 |  | 0 | 0 | 10.567 | 10.5667 | 1891.433 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 3681 |  |  | - |  | Other voltage circuit breakers | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340TC5 became unavailable when two of the three phases of its 345 kV breaker failed t
TC5 | 10 | U1 | 2018-01-10 11:27 |  |  |  |  | 2018-01-10 11:52 |  | 0 | 0 | 0.417 | 0.4167 | 74.583 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 4619 |  |  | - |  | Other hydrogen system problems | [8 empty] | AMP CODE: |  | 54
|  | DESCRIPTION : |  | F540TC5 became unavailable when an alarm came in for hazardous gas detection. A leak w
TC5 | 12 | U1 | 2018-01-11 06:19 |  |  |  |  | 2018-01-11 07:39 |  | 0 | 0 | 1.333 | 1.3333 | 238.667 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5240 |  |  | - |  | Fire detection and extinguishing system (including hazardous gas detection system) | [8 empty] | AMP CODE: |  | 52
|  | DESCRIPTION : |  | F520TC5 became unavailable when an alarm came in for hazardous gas detection. It was a
TC5 | 18 | U1 | 2018-02-14 06:05 |  |  |  |  | 2018-02-14 06:52 |  | 0 | 0 | 0.783 | 0.7833 | 140.217 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5240 |  |  | - |  | Fire detection and extinguishing system (including hazardous gas detection system) | [8 empty] | AMP CODE: |  | 52
|  | DESCRIPTION : |  | F520The unit was placed on a Forced Outage due to hazardous gas alarms. The hazardous
TC5 | 22 | SF | 2018-03-12 06:00 |  |  |  |  | 2018-03-12 06:10 |  | 0 | 0 | 0.167 | 0.1667 | 28.167 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5050 |  |  | - |  | Ignition system | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340An igniter issue and an ignition exciter issue caused the unit to fail to start.
TC5 | 24 | U1 | 2018-03-14 00:17 |  |  |  |  | 2018-03-14 03:13 |  | 0 | 0 | 2.933 | 2.9333 | 495.733 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5050 |  |  | - |  | Ignition system | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340After the installation and testing of a new ignition exciter, the unit became unav
TC5 | 26 | U1 | 2018-03-23 03:57 |  |  |  |  | 2018-03-23 05:39 |  | 0 | 0 | 1.7 | 1.7 | 287.3 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 9930 |  |  | - |  | Operating procedure error | [8 empty] | AMP CODE: |  | P0
|  | DESCRIPTION : |  | FP00Unit was made unavailable due to inadvertently carding the gas valve for the unit.
TC5 | 53 | U1 | 2018-08-20 10:51 |  |  |  |  | 2018-08-20 11:25 |  | 0 | 0 | 0.567 | 0.5667 | 90.1 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 4899 |  |  | - |  | Other miscellaneous generator problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F420The reverse power relay removed the unit from service when the unit load was not i
TC5 | 99 | SF | 2018-10-16 05:10 |  |  |  |  | 2018-10-16 06:05 |  | 0 | 0 | 0.917 | 0.9167 | 154.917 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 3618 |  |  | - |  | Other switchyard equipment - external (not OMC) | [8 empty] | AMP CODE: |  | 52
|  | DESCRIPTION : |  | F520The unit was unable to synchronize due to a lack of bus potential indication, due
TC5 | 58 | U1 | 2019-05-30 14:45 |  |  |  |  | 2019-05-30 15:18 |  | 0 | 0 | 0.55 | 0.55 | 92.95 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5048 |  |  | - |  | Gas fuel system including controls and instrumentation | [8 empty] | AMP CODE: |  | 66
|  | DESCRIPTION : |  | F660The unit was placed on outage due to decreased gas pressure caused by a temporary
TC5 | 108 | U1 | 2019-08-13 15:16 |  |  |  |  | 2019-08-13 15:31 |  | 0 | 0 | 0.25 | 0.25 | 39.75 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 19
|  | DESCRIPTION : |  | F190The TC5/TC6 LCI was not operating due to issue with cooling water, resulting in th
TC5 | 154 | SF | 2019-10-25 04:47 |  |  |  |  | 2019-10-25 07:31 |  | 0 | 0 | 2.733 | 2.7333 | 461.933 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5041 |  |  | - |  | Fuel piping and valves | [8 empty] | AMP CODE: |  | 72
|  | DESCRIPTION : |  | F720TC5 had a startup failure due to the unit tripping from the fuel gas vent valve (2
TC5 | 165 | SF | 2019-12-02 05:52 |  |  |  |  | 2019-12-02 10:07 |  | 0 | 0 | 4.25 | 4.25 | 760.75 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5001 |  |  | - |  | Inlet air vanes/nozzles | [8 empty] | AMP CODE: |  | 59
|  | DESCRIPTION : |  | F590The unit had a startup failure due to the inlet guide vane not tracking
TC5 | 170 | U1 | 2019-12-05 19:07 |  |  |  |  | 2019-12-07 17:06 |  | 0 | 0 | 45.983 | 45.9833 | 8231.017 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5248 |  |  | - |  | Gas Turbine Control System - logic problems | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340The unit was placed on outage after the turning gear failed to start when the roto
TC5 | 56 | U2 | 2020-06-18 18:00 |  |  |  |  | 2020-06-18 19:45 |  | 0 | 0 | 1.75 | 1.75 | 278.25 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 4650 |  |  | - |  | Other cooling system problems | [8 empty] | AMP CODE: |  | 32
|  | DESCRIPTION : |  | F320Dirty inlet filters on the bearing area blowers for the cooling fan caused the uni
TC5 | 25 | SF | 2021-07-10 15:33 |  |  |  |  | 2021-07-10 15:52 |  | 0 | 0 | 0.317 | 0.3167 | 50.35 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5441 |  |  | - |  | Fuel piping and valves | [8 empty] | AMP CODE: |  | 66
|  | DESCRIPTION : |  | F660The unit Failed to Start due to a loss of gas pressure at the main fuel gas supply
TC5 | 38 | SF | 2021-07-22 13:32 |  |  |  |  | 2021-07-22 13:58 |  | 0 | 0 | 0.433 | 0.4333 | 68.9 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 4609 |  |  | - |  | Other exciter problems | [8 empty] | AMP CODE: |  | 52
|  | DESCRIPTION : |  | F520The unit failed to start when the Exciter controls measured excess current onthe E
TC5 | 59 | U1 | 2021-08-31 22:20 |  |  |  |  | 2021-09-01 |  | 0 | 0 | 1.667 | 1.6667 | 265 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5240 |  |  | - |  | Fire detection and extinguishing system (including hazardous gas detection system) | [8 empty] | AMP CODE: |  | 52
|  | DESCRIPTION : |  | F520TC-5 was placed on a Forced Outage after a hazardous gas alarm presented, which wi
TC5 | 60 | U1 | 2021-09-01 |  |  |  |  | 2021-09-01 01:24 |  | 0 | 0 | 1.4 | 1.4 | 236.6 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5240 |  |  | - |  | Fire detection and extinguishing system (including hazardous gas detection system) | [8 empty] | AMP CODE: |  | 52
|  | DESCRIPTION : |  | F520TC-5 was placed on a Forced Outage after a hazardous gas alarm presented, which wi
TC5 | 6 | U1 | 2022-01-10 16:17 |  |  |  |  | 2022-01-10 16:36 |  | 0 | 0 | 0.317 | 0.3167 | 56.683 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5050 |  |  | - |  | Ignition system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F460The unit tripped when one of the combustion cans experienced a lean condition and
TC5 | 91 | U1 | 2022-08-15 11:16 |  |  |  |  | 2022-08-15 12:08 |  | 0 | 0 | 0.867 | 0.8667 | 137.8 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5091 |  |  | - |  | Low pressure bearings | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F850The unit experienced an automatic shutdown due to high bearing vibration levels.
TC5 | 107 | U1 | 2022-10-13 14:25 |  |  |  |  | 2022-10-13 15:13 |  | 0 | 0 | 0.8 | 0.8 | 135.2 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 3610 |  |  | - |  | Switchyard circuit breakers - external (not OMC) | [8 empty] | AMP CODE: |  | 87
|  | DESCRIPTION : |  | F870Lost 14KV feed to Gas Turbine Site.
TC5 | 116 | U1 | 2022-12-23 13:08 |  |  |  |  | 2022-12-23 13:48 |  | 0 | 0 | 0.667 | 0.6667 | 119.333 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5048 |  |  | - |  | Gas fuel system including controls and instrumentation | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Lean Blow Out (LBO) trip.
TC5 | 117 | U1 | 2022-12-23 13:48 |  |  |  |  | 2022-12-25 11:47 |  | 0 | 0 | 45.983 | 45.9833 | 8231.017 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 9130 |  |  | - |  | "Lack of fuel (water from rivers or lakes, coal mines, gas lines, etc) where the operator is not in control of contracts, supply lines, or delivery of fuels" | [8 empty] | AMP CODE: |  | X0
|  | DESCRIPTION : |  | FX00Low fuel gas supply pressure from transport company to the plant.
TC5 | 3 | U1 | 2023-03-03 07:33 |  |  |  |  | 2023-03-03 07:41 |  | 0 | 0 | 0.133 | 0.1333 | 22.533 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 9020 |  |  | - |  | Lightning | [8 empty] | AMP CODE: |  | X0
|  | DESCRIPTION : |  | FX00Lightning strike caused a blown fuse on controls for 12" main supply fuel gass ven
TC5 | 35 | U1 | 2023-10-10 09:31 |  |  |  |  | 2023-10-10 13:21 |  | 0 | 0 | 3.833 | 3.8333 | 647.833 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5041 |  |  | - |  | Fuel piping and valves | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F660Unit tripped on loss of fuel gas supply pressure due to a faulty solenoid coil on
Trimble County - TC6
Unit | Event | Type | Start |  |  |  |  | End |  | GAC | NAC | Duration | Equiv Hrs | Equiv MWH | Cont | Work Start | Work End |  | Hours |  |  | Gross Capacity Impact (MW)
TC6 | 4 | U1 | 2014-01-06 02:17 |  |  |  |  | 2014-01-06 03:50 |  | 0 | 0 | 1.55 | 1.55 | 272.8 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5079 |  |  | - |  | Other combustor problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F460Unit tripped due to a lean blowout.
TC6 | 6 | U1 | 2014-01-06 13:52 |  |  |  |  | 2014-01-06 14:46 |  | 0 | 0 | 0.9 | 0.9 | 158.4 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5041 |  |  | - |  | Fuel piping and valves | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F480Unit tripped due to a fuel gas valve (worker valve) not controlling properly.
TC6 | 8 | U1 | 2014-01-07 01:25 |  |  |  |  | 2014-01-07 05:49 |  | 0 | 0 | 4.4 | 4.4 | 774.4 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5016 |  |  | - |  | High pressure compressor bleed valves | [8 empty] | AMP CODE: |  | 48
|  | DESCRIPTION : |  | F480Forced outage due to compressor bleed valve frozen closed.
TC6 | 10 | U1 | 2014-01-21 16:35 |  |  |  |  | 2014-01-21 17:24 |  | 0 | 0 | 0.817 | 0.8167 | 143.733 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5048 |  |  | - |  | Gas fuel system including controls and instrumentation | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F480Forced outage due to combustion instrumentation issues.
TC6 | 11 | U1 | 2014-01-21 17:32 |  |  |  |  | 2014-01-21 20:01 |  | 0 | 0 | 2.483 | 2.4833 | 437.067 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5048 |  |  | - |  | Gas fuel system including controls and instrumentation | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F480Forced outage due to combustion instrumentation issues.
TC6 | 12 | U1 | 2014-01-22 00:08 |  |  |  |  | 2014-01-22 04:20 |  | 0 | 0 | 4.2 | 4.2 | 739.2 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5079 |  |  | - |  | Other combustor problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F460Forced outage due to flameout.
TC6 | 13 | SF | 2014-01-22 04:20 |  |  |  |  | 2014-01-22 05:55 |  | 0 | 0 | 1.583 | 1.5833 | 278.667 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5016 |  |  | - |  | High pressure compressor bleed valves | [8 empty] | AMP CODE: |  | 48
|  | DESCRIPTION : |  | F480Startup failure due to frozen compressor bleed valve.
TC6 | 14 | SF | 2014-01-22 05:55 |  |  |  |  | 2014-01-22 06:45 |  | 0 | 0 | 0.833 | 0.8333 | 146.667 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5016 |  |  | - |  | High pressure compressor bleed valves | [8 empty] | AMP CODE: |  | 48
|  | DESCRIPTION : |  | F480Startup failure due to frozen compressor bleed valve.
TC6 | 15 | U1 | 2014-01-23 11:39 |  |  |  |  | 2014-01-23 12:04 |  | 0 | 0 | 0.417 | 0.4167 | 73.333 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5079 |  |  | - |  | Other combustor problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F460Forced outage due to combustion issue.
TC6 | 17 | SF | 2014-01-23 16:56 |  |  |  |  | 2014-01-23 17:21 |  | 0 | 0 | 0.417 | 0.4167 | 73.333 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5041 |  |  | - |  | Fuel piping and valves | [8 empty] | AMP CODE: |  | 48
|  | DESCRIPTION : |  | F480Startup failure due to issue with fuel gas valve.
TC6 | 18 | U1 | 2014-01-23 17:30 |  |  |  |  | 2014-01-23 18:00 |  | 0 | 0 | 0.5 | 0.5 | 88 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5079 |  |  | - |  | Other combustor problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F460Forced outage due to combustion issue.
TC6 | 19 | U1 | 2014-01-23 18:18 |  |  |  |  | 2014-01-23 18:49 |  | 0 | 0 | 0.517 | 0.5167 | 90.933 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5079 |  |  | - |  | Other combustor problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F460Forced outage due to combustion issue.
TC6 | 20 | U1 | 2014-01-24 04:29 |  |  |  |  | 2014-01-24 10:13 |  | 0 | 0 | 5.733 | 5.7333 | 1009.067 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5250 |  |  | - |  | Other controls and instrumentation problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F410Forced outage due to erratic thermocouple signals from T Processor.
TC6 | 22 | SF | 2014-01-24 10:30 |  |  |  |  | 2014-01-24 11:08 |  | 0 | 0 | 0.633 | 0.6333 | 111.467 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5041 |  |  | - |  | Fuel piping and valves | [8 empty] | AMP CODE: |  | 66
|  | DESCRIPTION : |  | F660Startup failure due to issue with fuel gas valve.
TC6 | 25 | U1 | 2014-01-27 11:27 |  |  |  |  | 2014-01-27 14:05 |  | 0 | 0 | 2.633 | 2.6333 | 463.467 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5048 |  |  | - |  | Gas fuel system including controls and instrumentation | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F480Unit tripped due to frozen sensing line to 96GN transmitter.
TC6 | 33 | U1 | 2014-02-11 06:16 |  |  |  |  | 2014-02-11 06:58 |  | 0 | 0 | 0.7 | 0.7 | 123.2 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5079 |  |  | - |  | Other combustor problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F460Unit tripped due to flameout.
TC6 | 34 | U1 | 2014-02-11 08:29 |  |  |  |  | 2014-02-11 09:45 |  | 0 | 0 | 1.267 | 1.2667 | 222.933 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5079 |  |  | - |  | Other combustor problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F460Unit tripped due to flameout.
TC6 | 46 | SF | 2014-03-18 05:26 |  |  |  |  | 2014-03-18 05:50 |  | 0 | 0 | 0.4 | 0.4 | 70.4 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5041 |  |  | - |  | Fuel piping and valves | [8 empty] | AMP CODE: |  | 66
|  | DESCRIPTION : |  | F660Startup failure due to gas valves not controlling properly.
TC6 | 53 | U1 | 2014-03-28 05:45 |  |  |  |  | 2014-03-28 06:14 |  | 0 | 0 | 0.483 | 0.4833 | 85.067 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5049 |  |  | - |  | Other fuel system problems | [8 empty] | AMP CODE: |  | 78
|  | DESCRIPTION : |  | F780Forced outage due to over temperature of fuel gas heater.
TC6 | 57 | U1 | 2014-04-02 22:30 |  |  |  |  | 2014-04-03 02:13 |  | 0 | 0 | 3.717 | 3.7167 | 583.517 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 3972 |  |  | - |  | DCS - hardware problems (including card failure) | [8 empty] | AMP CODE: |  | 70
|  | DESCRIPTION : |  | F830Lightning strike, Control card issue.
TC6 | 66 | U1 | 2014-04-17 00:05 |  |  |  |  | 2014-04-17 02:15 |  | 0 | 0 | 2.167 | 2.1667 | 340.167 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 3872 |  |  | - |  | Fuel Gas Compressor Valves | [8 empty] | AMP CODE: |  | 09
|  | DESCRIPTION : |  | F090Servo valve issue.
TC6 | 93 | SF | 2014-05-26 15:02 |  |  |  |  | 2014-05-26 18:18 |  | 0 | 0 | 3.267 | 3.2667 | 512.867 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5041 |  |  | - |  | Fuel piping and valves | [8 empty] | AMP CODE: |  | 66
|  | DESCRIPTION : |  | F660Unit failed to start on a fuel gas start-up inhibit.
TC6 | 98 | SF | 2014-05-31 16:18 |  |  |  |  | 2014-05-31 16:42 |  | 0 | 0 | 0.4 | 0.4 | 62.8 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5079 |  |  | - |  | Other combustor problems | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340Start up failure due to failure to ignite.
TC6 | 100 | SF | 2014-06-01 15:21 |  |  |  |  | 2014-06-01 21:47 |  | 0 | 0 | 6.433 | 6.4333 | 1010.033 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5079 |  |  | - |  | Other combustor problems | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340Start up failure due to failure to ignite. Spark rod not operating properly.
TC6 | 119 | SF | 2014-07-10 11:13 |  |  |  |  | 2014-07-10 11:14 |  | 0 | 0 | 0.017 | 0.0167 | 2.617 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340Failure to reset LCI 5&6 did not give "ready to start" permissive. Failure was on
TC6 | 121 | U1 | 2014-07-11 15:23 |  |  |  |  | 2014-07-11 15:37 |  | 0 | 0 | 0.233 | 0.2333 | 36.633 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340TC5 started at 13:04 hours, the LCI was not reset. The attempt to start TC6 at 15:
TC6 | 124 | SF | 2014-07-21 11:38 |  |  |  |  | 2014-07-21 11:51 |  | 0 | 0 | 0.217 | 0.2167 | 34.017 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 3872 |  |  | - |  | Fuel Gas Compressor Valves | [8 empty] | AMP CODE: |  | 46
|  | DESCRIPTION : |  | F460Machine unexplicably lost flame on start-up, more investigation needed to find roo
TC6 | 128 | U1 | 2014-07-24 09:00 |  |  |  |  | 2014-07-24 10:08 |  | 0 | 0 | 1.133 | 1.1333 | 177.933 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5246 |  |  | - |  | Gas Turbine Control System - hardware problems (including card failure) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340The EX2000 was not communicating with the MK-IV, rebooting the 120 VAC power to EG
TC6 | 136 | SF | 2014-08-25 12:49 |  |  |  |  | 2014-08-25 13:20 |  | 0 | 0 | 0.517 | 0.5167 | 81.117 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5190 |  |  | - |  | Other auxiliary system problems | [8 empty] | AMP CODE: |  | 09
|  | DESCRIPTION : |  | F090After investigation, it was found that three fan motors rotated to the lag motor,
TC6 | 142 | U1 | 2014-08-30 18:20 |  |  |  |  | 2014-08-30 18:35 |  | 0 | 0 | 0.25 | 0.25 | 39.25 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 3649 |  |  | - |  | Other AC instrument power problems | [8 empty] | AMP CODE: |  | 70
|  | DESCRIPTION : |  | F820480 VAC breaker in PEECC #5 tripped killing power to LCI Compartment. TC5 & TC6 Sh
TC6 | 144 | U1 | 2014-09-02 12:18 |  |  |  |  | 2014-09-02 13:20 |  | 0 | 0 | 1.033 | 1.0333 | 162.233 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340TC6 is forced out because the common LCI with TC5 did not operate properly, TC5 ev
TC6 | 147 | SF | 2014-09-04 12:09 |  |  |  |  | 2014-09-04 12:41 |  | 0 | 0 | 0.533 | 0.5333 | 83.733 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340This was a problem with the common LCI between TC5 and TC6. TC6 was not attempted
TC6 | 149 | SF | 2014-09-05 08:10 |  |  |  |  | 2014-09-05 08:40 |  | 0 | 0 | 0.5 | 0.5 | 78.5 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340This is related to TC5 event #144, the LCI failed to start TC5 and TC6 cannot star
TC6 | 152 | SF | 2014-09-06 10:40 |  |  |  |  | 2014-09-06 13:45 |  | 0 | 0 | 3.083 | 3.0833 | 484.083 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340Unit failed to start due to common LCI, this time a faulty relay was found and rep
TC6 | 159 | U1 | 2014-10-02 07:45 |  |  |  |  | 2014-10-02 09:28 |  | 0 | 0 | 1.717 | 1.7167 | 302.133 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 4619 |  |  | - |  | Other hydrogen system problems | [8 empty] | AMP CODE: |  | 09
|  | DESCRIPTION : |  | F090This was called a forced outage because one of the hydrogen purity cells was not p
TC6 | 161 | U1 | 2014-10-02 14:11 |  |  |  |  | 2014-10-02 14:48 |  | 0 | 0 | 0.617 | 0.6167 | 108.533 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 3972 |  |  | - |  | DCS - hardware problems (including card failure) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340Main fuel gas shut-off valve failed to open after coming back from maintnenance ou
TC6 | 163 | SF | 2014-10-02 15:41 |  |  |  |  | 2014-10-02 19:40 |  | 0 | 0 | 3.983 | 3.9833 | 701.067 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340Initial indication was the static starter fault, but further investigation reveale
TC6 | 169 | SF | 2014-10-27 10:04 |  |  |  |  | 2014-10-27 11:42 |  | 0 | 0 | 1.633 | 1.6333 | 287.467 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 3629 |  |  | - |  | Other switchyard or high voltage system problems - external | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340Testing on generator breaker caused protection relay lockouts on TC6's generator p
TC6 | 179 | U1 | 2014-11-14 06:48 |  |  |  |  | 2014-11-14 07:25 |  | 0 | 0 | 0.617 | 0.6167 | 108.533 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5108 |  |  | - |  | High engine exhaust temperature | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820TC6 tripped on all exhaust thermocouples going high, root cause has not been found
TC6 | 181 | U1 | 2014-11-15 15:03 |  |  |  |  | 2014-11-15 16:09 |  | 0 | 0 | 1.1 | 1.1 | 193.6 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5049 |  |  | - |  | Other fuel system problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F660Relief valve on TC9/10 fuel gas heater lifted, and all gas turbines needed to be u
TC6 | 10 | SF | 2015-02-06 06:10 |  |  |  |  | 2015-02-06 13:13 |  | 0 | 0 | 7.05 | 7.05 | 1240.8 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5001 |  |  | - |  | Inlet air vanes/nozzles | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340Failed servo valve on IGV system did not allow machine to start. Servo replaced an
TC6 | 12 | U1 | 2015-02-10 19:24 |  |  |  |  | 2015-02-10 22:24 |  | 0 | 0 | 3 | 3 | 528 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5401 |  |  | - |  | Inlet air vanes/nozzles | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820IGV controls erractic. Changed IGV hydraulic filter and servo valve. Unit made ava
TC6 | 14 | U1 | 2015-02-11 00:19 |  |  |  |  | 2015-02-11 00:52 |  | 0 | 0 | 0.55 | 0.55 | 96.8 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5401 |  |  | - |  | Inlet air vanes/nozzles | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340IGV control erratic. Ran calibration program on IGV's, and it started controling a
TC6 | 16 | U1 | 2015-02-11 08:00 |  |  |  |  | 2015-02-11 13:24 |  | 0 | 0 | 5.4 | 5.4 | 950.4 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5041 |  |  | - |  | Fuel piping and valves | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830The fuel gas vent valve dowstream of the Stop/Ration Valve was stuck open. Deffect
TC6 | 19 | U1 | 2015-02-15 01:03 |  |  |  |  | 2015-02-15 01:43 |  | 0 | 0 | 0.667 | 0.6667 | 117.333 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 3619 |  |  | - |  | Other switchyard equipment - external (OMC) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820System Disturbance.
TC6 | 20 | SF | 2015-02-15 01:43 |  |  |  |  | 2015-02-15 05:15 |  | 0 | 0 | 3.533 | 3.5333 | 621.867 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5041 |  |  | - |  | Fuel piping and valves | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340Off-base fuel gas valves caused fuel gas pressure fluctuation, re-checked calibrat
TC6 | 21 | U1 | 2015-02-18 22:09 |  |  |  |  | 2015-02-18 22:56 |  | 0 | 0 | 0.783 | 0.7833 | 137.867 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5079 |  |  | - |  | Other combustor problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Voltage fluctuation caused machine to react to load and the reaction caused the ma
TC6 | 22 | U1 | 2015-02-19 01:45 |  |  |  |  | 2015-02-19 03:00 |  | 0 | 0 | 1.25 | 1.25 | 220 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5079 |  |  | - |  | Other combustor problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Autotune NOx setting too low to sustain flame in extreme low temperature. Lean blo
TC6 | 23 | U1 | 2015-02-19 06:34 |  |  |  |  | 2015-02-19 08:15 |  | 0 | 0 | 1.683 | 1.6833 | 296.267 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5079 |  |  | - |  | Other combustor problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Lean blow out event. Thermocouple spread is the first sign of a combustion can blo
TC6 | 24 | U1 | 2015-02-19 22:45 |  |  |  |  | 2015-02-20 00:33 |  | 0 | 0 | 1.8 | 1.8 | 316.8 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5079 |  |  | - |  | Other combustor problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Autotune NOx setting too low to sustain flame in extreme cold temperatures. Lean b
TC6 | 26 | U1 | 2015-02-22 23:55 |  |  |  |  | 2015-02-23 10:02 |  | 0 | 0 | 10.117 | 10.1167 | 1780.534 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5079 |  |  | - |  | Other combustor problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830NOx readings while machine was running were too high, machine taken off line manua
TC6 | 32 | U1 | 2015-02-23 10:49 |  |  |  |  | 2015-02-23 17:01 |  | 0 | 0 | 6.2 | 6.2 | 1091.2 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5079 |  |  | - |  | Other combustor problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Machine taken off line due to high NOx and dynamics. Machine was running with Auto
TC6 | 41 | SF | 2015-03-05 05:43 |  |  |  |  | 2015-03-05 07:43 |  | 0 | 0 | 2 | 2 | 352 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5041 |  |  | - |  | Fuel piping and valves | [8 empty] | AMP CODE: |  | 09
|  | DESCRIPTION : |  | F090Unit tripped at 95% speed due to failed transfer from PM2 to PM1 fuel gas control
TC6 | 49 | U1 | 2015-04-12 18:51 |  |  |  |  | 2015-04-12 19:58 |  | 0 | 0 | 1.117 | 1.1167 | 175.317 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340LCI did not engage while starting TC5, making TC6 unavailable. LCI compartment too
TC6 | 64 | U1 | 2015-05-07 21:30 |  |  |  |  | 2015-05-08 00:50 |  | 0 | 0 | 3.333 | 3.3333 | 523.333 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 3610 |  |  | - |  | Switchyard circuit breakers - external (not OMC) | [8 empty] | AMP CODE: |  | 33
|  | DESCRIPTION : |  | F33052G breaker on TC7 failed to open, the immediate action taken to isolate unit was
TC6 | 72 | U1 | 2015-05-26 14:04 |  |  |  |  | 2015-05-26 14:25 |  | 0 | 0 | 0.35 | 0.35 | 54.95 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 9020 |  |  | - |  | Lightning | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Lightning strike affected operation of the BOP fuel gas control valves causing uni
TC6 | 82 | U1 | 2015-06-13 10:41 |  |  |  |  | 2015-06-13 17:07 |  | 0 | 0 | 6.433 | 6.4333 | 1010.033 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 3612 |  |  | - |  | Switchyard system protection devices - external (OMC) | [8 empty] | AMP CODE: |  | 03
|  | DESCRIPTION : |  | F030"A" Bus lock out due to TC7 C Phase Main Breaker failure. This forced an outage o
TC6 | 93 | U1 | 2015-07-06 12:55 |  |  |  |  | 2015-07-06 14:04 |  | 0 | 0 | 1.15 | 1.15 | 182.85 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340LCI cooling water resistivity did not allow LCI to start.
TC6 | 145 | U1 | 2015-11-09 00:43 |  |  |  |  | 2015-11-09 03:06 |  | 0 | 0 | 2.383 | 2.3833 | 426.617 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5079 |  |  | - |  | Other combustor problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Lean blow out, not enough fuel gas to maintain flame.
TC6 | 148 | U1 | 2015-11-16 02:27 |  |  |  |  | 2015-11-16 05:32 |  | 0 | 0 | 3.083 | 3.0833 | 551.917 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5109 |  |  | - |  | Other exhaust problems (including high exhaust system temperature not attributable to a specific problem) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Trip caused by two adjacent exhaust thermocouples going low.
TC6 | 1 | SF | 2016-01-05 05:44 |  |  |  |  | 2016-01-05 19:44 |  | 0 | 0 | 14 | 14 | 2506 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 33
|  | DESCRIPTION : |  | F330The LCI water conductivity was too high causing the 89ND not to disengage as per M
TC6 | 3 | SF | 2016-01-06 05:43 |  |  |  |  | 2016-01-06 07:59 |  | 0 | 0 | 2.267 | 2.2667 | 405.733 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5001 |  |  | - |  | Inlet air vanes/nozzles | [8 empty] | AMP CODE: |  | 09
|  | DESCRIPTION : |  | F090The minimum value on IGV angle that allows machine to start drifted too low causin
TC6 | 5 | SF | 2016-01-10 18:16 |  |  |  |  | 2016-01-11 05:56 |  | 0 | 0 | 11.667 | 11.6667 | 2088.334 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340The 89ND switch did not engage causing starting sequence to not complete and machi
TC6 | 7 | U1 | 2016-01-12 23:03 |  |  |  |  | 2016-01-13 00:23 |  | 0 | 0 | 1.333 | 1.3333 | 238.667 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5109 |  |  | - |  | Other exhaust problems (including high exhaust system temperature not attributable to a specific problem) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820First reported as an exciter trip, later reported as a thermocouple trip.
TC6 | 9 | U1 | 2016-01-17 19:09 |  |  |  |  | 2016-01-17 20:31 |  | 0 | 0 | 1.367 | 1.3667 | 244.633 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5108 |  |  | - |  | High engine exhaust temperature | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Unit tripped on high exhaust temperature spread, and further investigation reveale
TC6 | 14 | U1 | 2016-01-28 06:31 |  |  |  |  | 2016-01-28 08:34 |  | 0 | 0 | 2.05 | 2.05 | 366.95 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5048 |  |  | - |  | Gas fuel system including controls and instrumentation | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Unit tripped on start-up while transferring from mode 2 to mode 3 combustion, trou
TC6 | 19 | SF | 2016-02-12 16:44 |  |  |  |  | 2016-02-12 18:49 |  | 0 | 0 | 2.083 | 2.0833 | 372.917 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5001 |  |  | - |  | Inlet air vanes/nozzles | [8 empty] | AMP CODE: |  | 12
|  | DESCRIPTION : |  | F120TC6 Inlet Guide Vane's were not able to operate correctly due to varnish in a hydr
TC6 | 23 | U1 | 2016-02-16 11:34 |  |  |  |  | 2016-02-17 15:29 |  | 0 | 0 | 27.917 | 27.9167 | 4997.084 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340Due to TC5's Startup Failure, TC6 was in a Forced Outage state.
TC6 | 25 | U1 | 2016-02-17 17:30 |  |  |  |  | 2016-02-18 01:38 |  | 0 | 0 | 8.133 | 8.1333 | 1455.867 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 4860 |  |  | - |  | Generator neutral grounding equipment | [8 empty] | AMP CODE: |  | V0
|  | DESCRIPTION : |  | FV00The 89ND switch closed itself under vibration during operation, which controls a l
TC6 | 28 | U1 | 2016-02-29 08:30 |  |  |  |  | 2016-02-29 12:18 |  | 0 | 0 | 3.8 | 3.8 | 680.2 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5041 |  |  | - |  | Fuel piping and valves | [8 empty] | AMP CODE: |  | 06
|  | DESCRIPTION : |  | F060TC5/6 Gas Heater pressure regulating valve PCV-102 failed, and needed replacement.
TC6 | 30 | U1 | 2016-03-01 08:09 |  |  |  |  | 2016-03-01 08:43 |  | 0 | 0 | 0.567 | 0.5667 | 95.767 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 9131 |  |  | - |  | Lack of fuel (interruptible supply of fuel part of fuel contract) | [8 empty] | AMP CODE: |  | NF
|  | DESCRIPTION : |  | F340A Texas Gas supply valve electro-pneumatic transducer failed, causing the valve to
TC6 | 48 | SF | 2016-06-14 10:32 |  |  |  |  | 2016-06-14 11:15 |  | 0 | 0 | 0.717 | 0.7167 | 113.95 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5050 |  |  | - |  | Ignition system | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340Pre-ignition failiure due to spark rods not engaging.
TC6 | 51 | SF | 2016-06-21 09:49 |  |  |  |  | 2016-06-21 12:10 |  | 0 | 0 | 2.35 | 2.35 | 373.65 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 4609 |  |  | - |  | Other exciter problems | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340TC6 Exciter failed to operate properly, resulting in a startup failure of the unit
TC6 | 55 | U1 | 2016-06-25 11:44 |  |  |  |  | 2016-06-25 12:39 |  | 0 | 0 | 0.917 | 0.9167 | 145.75 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340Due to problems with the TC5 LCI, the unit was unavailable to start.
TC6 | 57 | U1 | 2016-06-26 10:24 |  |  |  |  | 2016-06-26 10:34 |  | 0 | 0 | 0.167 | 0.1667 | 26.5 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340Due to problems with the TC5 LCI, the unit was unavailable to start.
TC6 | 59 | U1 | 2016-06-26 10:54 |  |  |  |  | 2016-06-26 14:26 |  | 0 | 0 | 3.533 | 3.5333 | 561.8 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340Due to problems with the TC5 LCI 89SS switch linkages, the unit was unavailable to
TC6 | 75 | U1 | 2016-07-18 07:23 |  |  |  |  | 2016-07-18 07:30 |  | 0 | 0 | 0.117 | 0.1167 | 18.55 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 3631 |  |  | - |  | 400-700 volt circuit breakers | [8 empty] | AMP CODE: |  | 59
|  | DESCRIPTION : |  | F590Loss of power to the 480V feed on TC6 due to issues with the breakers.
TC6 | 87 | U1 | 2016-08-17 22:40 |  |  |  |  | 2016-08-18 01:53 |  | 0 | 0 | 3.217 | 3.2167 | 511.45 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5041 |  |  | - |  | Fuel piping and valves | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340The TC6 gas fuel valve solenoid failed and was unavailable until the valve was rep
TC6 | 105 | U1 | 2016-10-25 10:24 |  |  |  |  | 2016-10-25 12:32 |  | 0 | 0 | 2.133 | 2.1333 | 360.533 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340Issues with the LCI Communications system caused the unit to be unavailable for th
TC6 | 112 | U1 | 2016-12-09 05:56 |  |  |  |  | 2016-12-09 08:59 |  | 0 | 0 | 3.05 | 3.05 | 545.95 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5048 |  |  | - |  | Gas fuel system including controls and instrumentation | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F460A tuning issue resulted in a lean fuel mixture, which tripped the unit while comin
TC6 | 113 | U1 | 2016-12-09 09:07 |  |  |  |  | 2016-12-09 16:24 |  | 0 | 0 | 7.283 | 7.2833 | 1303.717 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5048 |  |  | - |  | Gas fuel system including controls and instrumentation | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F460A tuning issue resulted in a lean fuel mixture, which tripped the unit while comin
TC6 | 114 | U1 | 2016-12-09 17:03 |  |  |  |  | 2016-12-09 17:37 |  | 0 | 0 | 0.567 | 0.5667 | 101.433 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5048 |  |  | - |  | Gas fuel system including controls and instrumentation | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F460A tuning issue resulted in a lean fuel mixture, which tripped the unit while comin
TC6 | 121 | SF | 2016-12-19 05:37 |  |  |  |  | 2016-12-19 07:36 |  | 0 | 0 | 1.983 | 1.9833 | 355.017 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340The unit failed to start when the LCI tripped and the 4kV breaker opened.
TC6 | 123 | U1 | 2016-12-20 07:24 |  |  |  |  | 2016-12-20 08:02 |  | 0 | 0 | 0.633 | 0.6333 | 113.367 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5100 |  |  | - |  | Chamber | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F520The unit tripped due to an Exhaust Frame Blower pressure switch not reading correc
TC6 | 1 | U1 | 2017-01-06 05:55 |  |  |  |  | 2017-01-06 06:03 |  | 0 | 0 | 0.133 | 0.1333 | 23.867 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5100 |  |  | - |  | Chamber | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F520The unit tripped due to an Exhaust Frame Blower pressure switch not reading correc
TC6 | 5 | U1 | 2017-01-12 09:39 |  |  |  |  | 2017-01-12 10:30 |  | 0 | 0 | 0.85 | 0.85 | 152.15 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340The LCI Communication system was not operating correctly, making the unit unavaila
TC6 | 7 | U1 | 2017-01-13 07:10 |  |  |  |  | 2017-01-13 07:40 |  | 0 | 0 | 0.5 | 0.5 | 89.5 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340The LCI Communication system was not operating correctly, making the unit unavaila
TC6 | 15 | U1 | 2017-03-01 06:31 |  |  |  |  | 2017-03-01 07:26 |  | 0 | 0 | 0.917 | 0.9167 | 154.917 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 40
|  | DESCRIPTION : |  | F400Both TC5 and TC6 Exciters and the shared LCI tripped for unknown reasons during a
TC6 | 18 | U1 | 2017-03-09 12:55 |  |  |  |  | 2017-03-09 14:30 |  | 0 | 0 | 1.583 | 1.5833 | 267.583 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 4609 |  |  | - |  | Other exciter problems | [8 empty] | AMP CODE: |  | 40
|  | DESCRIPTION : |  | F400An exciter control board was receiving erratic field current feedback. If a start
TC6 | 21 | U1 | 2017-03-14 04:31 |  |  |  |  | 2017-03-14 05:20 |  | 0 | 0 | 0.817 | 0.8167 | 138.017 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5041 |  |  | - |  | Fuel piping and valves | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340TC6 was made unavailable when the worker valve was found fixed in the open positio
TC6 | 34 | U1 | 2017-04-19 06:27 |  |  |  |  | 2017-04-19 07:58 |  | 0 | 0 | 1.517 | 1.5167 | 256.317 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340The LCI Communication system was not operating correctly, making the unit unavaila
TC6 | 36 | U1 | 2017-04-19 13:14 |  |  |  |  | 2017-04-19 14:43 |  | 0 | 0 | 1.483 | 1.4833 | 250.683 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340The LCI Communication system was not operating correctly, making the unit unavaila
TC6 | 50 | U1 | 2017-05-27 19:54 |  |  |  |  | 2017-05-27 20:07 |  | 0 | 0 | 0.217 | 0.2167 | 36.617 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 9020 |  |  | - |  | Lightning | [8 empty] | AMP CODE: |  | 70
|  | DESCRIPTION : |  | F700A lightning strike caused the unit to be unavailable. The unit was unavailable due
TC6 | 52 | U1 | 2017-05-27 21:22 |  |  |  |  | 2017-05-27 23:40 |  | 0 | 0 | 2.3 | 2.3 | 388.7 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340The unit was unavailable due to a TC5/TC6 LCI issue. The breaker for the LCI cooli
TC6 | 73 | U1 | 2017-07-10 21:50 |  |  |  |  | 2017-07-10 22:39 |  | 0 | 0 | 0.817 | 0.8167 | 129.85 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5041 |  |  | - |  | Fuel piping and valves | [8 empty] | AMP CODE: |  | 52
|  | DESCRIPTION : |  | F520Worker valve received a false 'input failed' alarm. The issue was corrected and th
TC6 | 77 | U1 | 2017-07-12 22:34 |  |  |  |  | 2017-07-13 01:36 |  | 0 | 0 | 3.033 | 3.0333 | 482.3 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5041 |  |  | - |  | Fuel piping and valves | [8 empty] | AMP CODE: |  | 52
|  | DESCRIPTION : |  | F520False gas valve servo 'not ready to start' alarm came in, causing the unit to be u
TC6 | 80 | U1 | 2017-07-13 23:00 |  |  |  |  | 2017-07-14 00:06 |  | 0 | 0 | 1.1 | 1.1 | 174.9 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5041 |  |  | - |  | Fuel piping and valves | [8 empty] | AMP CODE: |  | 52
|  | DESCRIPTION : |  | F520False gas valve servo alarm 'not ready to start' came in, making the unit unavaila
TC6 | 124 | SF | 2017-10-17 05:33 |  |  |  |  | 2017-10-17 10:04 |  | 0 | 0 | 4.517 | 4.5167 | 763.317 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5041 |  |  | - |  | Fuel piping and valves | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340TC6 failed to start when the fuel gas liquid separator relief valve lifted and and
TC6 | 142 | SF | 2017-12-08 06:44 |  |  |  |  | 2017-12-08 07:18 |  | 0 | 0 | 0.567 | 0.5667 | 101.433 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5001 |  |  | - |  | Inlet air vanes/nozzles | [8 empty] | AMP CODE: |  | 72
|  | DESCRIPTION : |  | F720The unit failed to start when the inlet guide vanes had issues with positioning on
TC6 | 147 | U1 | 2017-12-28 15:08 |  |  |  |  | 2017-12-28 16:13 |  | 0 | 0 | 1.083 | 1.0833 | 193.917 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 33
|  | DESCRIPTION : |  | F820The unit was placed on a Forced Outage when the TC5 MCC1 tripped due to 480 V powe
TC6 | 3 | U1 | 2018-01-03 09:22 |  |  |  |  | 2018-01-04 20:29 |  | 0 | 0 | 35.117 | 35.1167 | 6285.884 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 3681 |  |  | - |  | Other voltage circuit breakers | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340One of the three TC6 345 kV main breaker failed to open, causing the Main Switchya
TC6 | 6 | U1 | 2018-01-13 14:18 |  |  |  |  | 2018-01-13 15:04 |  | 0 | 0 | 0.767 | 0.7667 | 137.233 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5081 |  |  | - |  | High pressure bearings | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F520TC6 was removed from service when an alarm came in for high temperature on turbine
TC6 | 26 | U1 | 2018-05-03 12:31 |  |  |  |  | 2018-05-03 14:22 |  | 0 | 0 | 1.85 | 1.85 | 312.65 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5246 |  |  | - |  | Gas Turbine Control System - hardware problems (including card failure) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F520TC6 was removed from service due to indications on the generator. When the unit wa
TC6 | 54 | U1 | 2018-07-24 14:05 |  |  |  |  | 2018-07-24 15:35 |  | 0 | 0 | 1.5 | 1.5 | 238.5 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 4609 |  |  | - |  | Other exciter problems | [8 empty] | AMP CODE: |  | 40
|  | DESCRIPTION : |  | F400The unit was made unavailable to replace the relay to the TC6 4kV feeder breaker f
TC6 | 66 | U1 | 2018-08-20 12:13 |  |  |  |  | 2018-08-20 12:14 |  | 0 | 0 | 0.017 | 0.0167 | 2.65 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 4899 |  |  | - |  | Other miscellaneous generator problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F420The reverse power relay removed the unit from service when the unit load was not i
TC6 | 106 | SF | 2018-10-16 05:10 |  |  |  |  | 2018-10-16 06:15 |  | 0 | 0 | 1.083 | 1.0833 | 183.083 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 3618 |  |  | - |  | Other switchyard equipment - external (not OMC) | [8 empty] | AMP CODE: |  | 52
|  | DESCRIPTION : |  | F520The unit was unable to synchronize due to a lack of bus potential indication, due
TC6 | 31 | U1 | 2019-05-30 14:45 |  |  |  |  | 2019-05-30 15:18 |  | 0 | 0 | 0.55 | 0.55 | 92.95 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5048 |  |  | - |  | Gas fuel system including controls and instrumentation | [8 empty] | AMP CODE: |  | 66
|  | DESCRIPTION : |  | F660The unit was placed on outage due to decreased gas pressure caused by a temporary
TC6 | 51 | U1 | 2019-07-30 21:40 |  |  |  |  | 2019-07-31 00:47 |  | 0 | 0 | 3.117 | 3.1167 | 495.55 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5041 |  |  | - |  | Fuel piping and valves | [8 empty] | AMP CODE: |  | 63
|  | DESCRIPTION : |  | F630The unit became unavailable when a gas relief valve lifted and did not reseat duri
TC6 | 55 | U1 | 2019-08-13 15:16 |  |  |  |  | 2019-08-13 15:31 |  | 0 | 0 | 0.25 | 0.25 | 39.75 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 19
|  | DESCRIPTION : |  | F190The TC5/TC6 LCI was not operating due to issue with cooling water, resulting in th
TC6 | 85 | SF | 2019-12-02 05:57 |  |  |  |  | 2019-12-02 14:19 |  | 0 | 0 | 8.367 | 8.3667 | 1497.633 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5001 |  |  | - |  | Inlet air vanes/nozzles | [8 empty] | AMP CODE: |  | 59
|  | DESCRIPTION : |  | F590The unit had a startup failure due to the inlet guide vane not tracking
TC6 | 54 | U1 | 2020-12-26 04:52 |  |  |  |  | 2020-12-26 08:21 |  | 0 | 0 | 3.483 | 3.4833 | 623.517 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 4555 |  |  | - |  | Bearing cooling system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F340The #2 bearing cooling fan would not start due to damper and pressure switch issue
TC6 | 117 | U1 | 2021-12-08 16:44 |  |  |  |  | 2021-12-08 18:24 |  | 0 | 0 | 1.667 | 1.6667 | 298.333 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5450 |  |  | - |  | Ignition system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F460The unit was on a forced outage due to burner can fuel/air ratio becoming too lean
TC6 | 35 | U1 | 2022-04-18 09:41 |  |  |  |  | 2022-04-18 10:18 |  | 0 | 0 | 0.617 | 0.6167 | 104.217 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5079 |  |  | - |  | Other combustor problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F660The unit tripped on post-outage testing due to increase combustion dynamics at bas
TC6 | 88 | U1 | 2022-10-13 14:25 |  |  |  |  | 2022-10-13 15:13 |  | 0 | 0 | 0.8 | 0.8 | 135.2 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 3610 |  |  | - |  | Switchyard circuit breakers - external (not OMC) | [8 empty] | AMP CODE: |  | 87
|  | DESCRIPTION : |  | F870Lost 14KV feed to Gas Turbine Site.
TC6 | 98 | U1 | 2022-11-14 22:19 |  |  |  |  | 2022-11-15 16:04 |  | 0 | 0 | 17.75 | 17.75 | 2999.75 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5017 |  |  | - |  | Low pressure compressor bleed valves | [8 empty] | AMP CODE: |  | 33
|  | DESCRIPTION : |  | F330Compressor bleed valve failed to open during shutdown sequence.
TC6 | 9 | U1 | 2023-03-03 07:33 |  |  |  |  | 2023-03-03 07:41 |  | 0 | 0 | 0.133 | 0.1333 | 22.533 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 9020 |  |  | - |  | Lightning | [8 empty] | AMP CODE: |  | X0
|  | DESCRIPTION : |  | FX00Lightning strike caused a blown fuse on controls for 12" main supply fuel gass ven
Trimble County - TC7
Unit | Event | Type | Start |  |  |  |  | End |  | GAC | NAC | Duration | Equiv Hrs | Equiv MWH | Cont | Work Start | Work End |  | Hours |  |  | Gross Capacity Impact (MW)
TC7 | 2 | U1 | 2014-01-03 05:14 |  |  |  |  | 2014-01-03 06:52 |  | 0 | 0 | 1.633 | 1.6333 | 287.467 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5048 |  |  | - |  | Gas fuel system including controls and instrumentation | [8 empty] | AMP CODE: |  | 52
|  | DESCRIPTION : |  | F520Forced outage due to Hazardous Gas alarm.
TC7 | 4 | U1 | 2014-01-05 14:07 |  |  |  |  | 2014-01-05 15:36 |  | 0 | 0 | 1.483 | 1.4833 | 261.067 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5041 |  |  | - |  | Fuel piping and valves | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F660Forced outage due to fuel gas valve (SRV).
TC7 | 8 | U1 | 2014-02-05 16:03 |  |  |  |  | 2014-02-05 16:08 |  | 0 | 0 | 0.083 | 0.0833 | 14.667 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5160 |  |  | - |  | Cooling and seal air system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F480Unit rolled back to FSNL due to issue with pressure switch on Exhaust Frame Blower
TC7 | 9 | U1 | 2014-02-05 16:09 |  |  |  |  | 2014-02-05 16:17 |  | 0 | 0 | 0.133 | 0.1333 | 23.467 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5160 |  |  | - |  | Cooling and seal air system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F480Unit rolled back to FSNL due to issue with pressure switch on Exhaust Frame Blower
TC7 | 18 | SF | 2014-03-02 21:40 |  |  |  |  | 2014-03-02 21:51 |  | 0 | 0 | 0.183 | 0.1833 | 32.267 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5041 |  |  | - |  | Fuel piping and valves | [8 empty] | AMP CODE: |  | 54
|  | DESCRIPTION : |  | F540Startup failure due to high hazardous gas alarm.
TC7 | 33 | U1 | 2014-04-04 15:28 |  |  |  |  | 2014-04-04 16:20 |  | 0 | 0 | 0.867 | 0.8667 | 136.067 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5255 |  |  | - |  | Computer | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Replace control card.
TC7 | 43 | U1 | 2014-04-28 19:26 |  |  |  |  | 2014-04-29 03:25 |  | 0 | 0 | 7.983 | 7.9833 | 1253.384 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5285 |  |  | - |  | Gas turbine vibration | [8 empty] | AMP CODE: |  | 85
|  | DESCRIPTION : |  | F850Bently Nevada panel bad control card. Prevented "Ready to Start Mode".
TC7 | 62 | U1 | 2014-06-10 18:20 |  |  |  |  | 2014-06-10 21:23 |  | 0 | 0 | 3.05 | 3.05 | 478.85 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5299 |  |  | - |  | Other miscellaneous gas turbine problems | [8 empty] | AMP CODE: |  | 50
|  | DESCRIPTION : |  | F500CT7 made unavailable due to unit hydrogen auto purge. Dump valve did not open on
TC7 | 64 | U1 | 2014-06-14 04:45 |  |  |  |  | 2014-06-14 05:44 |  | 0 | 0 | 0.983 | 0.9833 | 154.383 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5250 |  |  | - |  | Other controls and instrumentation problems | [8 empty] | AMP CODE: |  | 40
|  | DESCRIPTION : |  | F400Hazgas detector read high, detector was reset and unit returned to reserve.
TC7 | 79 | U1 | 2014-07-03 21:27 |  |  |  |  | 2014-07-03 21:47 |  | 0 | 0 | 0.333 | 0.3333 | 52.333 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5041 |  |  | - |  | Fuel piping and valves | [8 empty] | AMP CODE: |  | 09
|  | DESCRIPTION : |  | F090Fuel gas P2 transmitters drifted beyond set point and caused unit to be "not ready
TC7 | 97 | U1 | 2014-08-02 03:33 |  |  |  |  | 2014-08-02 03:50 |  | 0 | 0 | 0.283 | 0.2833 | 44.483 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340Static Start switch 89SS failed to engage.
TC7 | 99 | U1 | 2014-08-02 05:02 |  |  |  |  | 2014-08-02 08:41 |  | 0 | 0 | 3.65 | 3.65 | 573.05 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340Initial signal was that the LCI was not working, further investigation revealed th
TC7 | 101 | U1 | 2014-08-02 19:00 |  |  |  |  | 2014-08-02 19:59 |  | 0 | 0 | 0.983 | 0.9833 | 154.383 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5048 |  |  | - |  | Gas fuel system including controls and instrumentation | [8 empty] | AMP CODE: |  | 09
|  | DESCRIPTION : |  | F090Two of the three P2 pressure transmitters were reading negative. Transmitters were
TC7 | 122 | U1 | 2014-09-25 13:55 |  |  |  |  | 2014-09-25 19:22 |  | 0 | 0 | 5.45 | 5.45 | 855.65 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340Cam limit switch hold down bolts were loose, caused false indication on 89SS trave
TC7 | 124 | U1 | 2014-09-25 19:53 |  |  |  |  | 2014-09-25 21:21 |  | 0 | 0 | 1.467 | 1.4667 | 230.267 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 3661 |  |  | - |  | 4000-7000 volt circuit breakers | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340Lose wires found in the control circuits of the LCI 4KV breaker. Wires were tight
TC7 | 127 | U1 | 2014-10-01 12:45 |  |  |  |  | 2014-10-01 13:15 |  | 0 | 0 | 0.5 | 0.5 | 88 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 3661 |  |  | - |  | 4000-7000 volt circuit breakers | [8 empty] | AMP CODE: |  | P0
|  | DESCRIPTION : |  | F700Improper switching instructions lead to a black out of units 7 & 8 during 4KV outa
TC7 | 129 | SF | 2014-10-02 13:57 |  |  |  |  | 2014-10-02 14:01 |  | 0 | 0 | 0.067 | 0.0667 | 11.733 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 4609 |  |  | - |  | Other exciter problems | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340Communications fault on exciter controller caused failure to start. Faults were in
TC7 | 132 | U1 | 2014-10-03 01:29 |  |  |  |  | 2014-10-03 05:48 |  | 0 | 0 | 4.317 | 4.3167 | 759.733 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 4603 |  |  | - |  | Solid state exciter element | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340Communication fault prevented EX2000 to start, faults cleared by reseting EX2000.
TC7 | 142 | U1 | 2014-10-27 13:08 |  |  |  |  | 2014-10-27 13:25 |  | 0 | 0 | 0.283 | 0.2833 | 49.867 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5048 |  |  | - |  | Gas fuel system including controls and instrumentation | [8 empty] | AMP CODE: |  | 09
|  | DESCRIPTION : |  | F090The interstage pressure transmitters (P2) drifted beyond acceptable point in MKVI
TC7 | 144 | U1 | 2014-10-29 12:51 |  |  |  |  | 2014-10-29 22:11 |  | 0 | 0 | 9.333 | 9.3333 | 1642.667 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 4619 |  |  | - |  | Other hydrogen system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820TC7 was running, hydrogen purity went low due to purge CO2 valve vibrating open an
TC7 | 146 | U1 | 2014-11-12 13:09 |  |  |  |  | 2014-11-12 14:10 |  | 0 | 0 | 1.017 | 1.0167 | 178.933 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 3669 |  |  | - |  | Other 4000-7000 volt problems | [8 empty] | AMP CODE: |  | 70
|  | DESCRIPTION : |  | F7004KV lost power due to contact being "bumped" by personnel working on terminations
TC7 | 148 | U1 | 2014-11-12 20:23 |  |  |  |  | 2014-11-13 06:37 |  | 0 | 0 | 10.233 | 10.2333 | 1801.066 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 4619 |  |  | - |  | Other hydrogen system problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F090The loss of power from event #146 caused the hydrogen panel to start a purge of hy
TC7 | 151 | U1 | 2014-11-15 15:03 |  |  |  |  | 2014-11-15 16:09 |  | 0 | 0 | 1.1 | 1.1 | 193.6 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5049 |  |  | - |  | Other fuel system problems | [8 empty] | AMP CODE: |  | 66
|  | DESCRIPTION : |  | F660Relief valve on TC9/10 fuel gas heater lifted, and all gas turbines needed to be u
TC7 | 170 | U1 | 2014-12-11 17:55 |  |  |  |  | 2014-12-11 19:07 |  | 0 | 0 | 1.2 | 1.2 | 211.2 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340Static Start 89SS switch failed to engage on TC8. Adjustments made to limit switch
TC7 | 11 | U1 | 2015-02-10 20:49 |  |  |  |  | 2015-02-10 22:22 |  | 0 | 0 | 1.55 | 1.55 | 272.8 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5049 |  |  | - |  | Other fuel system problems | [8 empty] | AMP CODE: |  | 78
|  | DESCRIPTION : |  | F780The dew point control fuel gas heater did not operate as expected. Adjustment made
TC7 | 40 | U1 | 2015-04-13 17:33 |  |  |  |  | 2015-04-13 18:36 |  | 0 | 0 | 1.05 | 1.05 | 164.85 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5160 |  |  | - |  | Cooling and seal air system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820High turbine compartment temperature caused turbine run back, until it came off li
TC7 | 48 | U1 | 2015-04-20 13:58 |  |  |  |  | 2015-04-20 14:31 |  | 0 | 0 | 0.55 | 0.55 | 86.35 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5250 |  |  | - |  | Other controls and instrumentation problems | [8 empty] | AMP CODE: |  | 09
|  | DESCRIPTION : |  | F090Hazardous Gas Detector in turbine compartment started reading high, two out of the
TC7 | 50 | U1 | 2015-04-21 08:13 |  |  |  |  | 2015-04-21 12:07 |  | 0 | 0 | 3.9 | 3.9 | 612.3 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 4640 |  |  | - |  | Seal oil system and seals | [8 empty] | AMP CODE: |  | 54
|  | DESCRIPTION : |  | F540Seal oil regulator was leaking at the regulator bonnet, bolts tightened and leak w
TC7 | 52 | U1 | 2015-04-29 04:45 |  |  |  |  | 2015-04-29 20:14 |  | 0 | 0 | 15.483 | 15.4833 | 2430.883 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340The 89SS switch on TC8 failed to open due to a bad contactor, this caused TC7 to b
TC7 | 54 | U1 | 2015-04-29 20:23 |  |  |  |  | 2015-04-29 20:47 |  | 0 | 0 | 0.4 | 0.4 | 62.8 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340TC7 made unavailable due to TC8 89SS not opening, and the LCI not being available
TC7 | 56 | SF | 2015-05-01 03:42 |  |  |  |  | 2015-05-01 04:36 |  | 0 | 0 | 0.9 | 0.9 | 141.3 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340The 89ND switch failed to open. Blown fuse replaced and machine made available. T
TC7 | 62 | U1 | 2015-05-05 05:20 |  |  |  |  | 2015-05-05 12:12 |  | 0 | 0 | 6.867 | 6.8667 | 1078.067 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5299 |  |  | - |  | Other miscellaneous gas turbine problems | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340The pressure switches on the turbine compartment vent fans were not working proper
TC7 | 65 | U1 | 2015-05-07 20:52 |  |  |  |  | 2015-05-08 18:28 |  | 0 | 0 | 21.6 | 21.6 | 3391.2 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 3610 |  |  | - |  | Switchyard circuit breakers - external (not OMC) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830On unit shut down, the 52G breaker on TC7 did not open when given the signal to op
TC7 | 67 | U1 | 2015-05-09 16:09 |  |  |  |  | 2015-05-09 17:50 |  | 0 | 0 | 1.683 | 1.6833 | 264.283 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5048 |  |  | - |  | Gas fuel system including controls and instrumentation | [8 empty] | AMP CODE: |  | 09
|  | DESCRIPTION : |  | F090Drift on the fuel gas pressure transmitters caused the unit to be "not ready to st
TC7 | 71 | U1 | 2015-05-18 22:00 |  |  |  |  | 2015-05-18 22:48 |  | 0 | 0 | 0.8 | 0.8 | 125.6 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340The 89SS, static start switch on TC8 failed to disengage, due to shared LCI, TC7 w
TC7 | 75 | U1 | 2015-05-31 08:27 |  |  |  |  | 2015-05-31 10:46 |  | 0 | 0 | 2.317 | 2.3167 | 363.717 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340The static start switch on TC8 did not engage, repairs to TC8 causes TC7 to be una
TC7 | 83 | U1 | 2015-06-13 10:41 |  |  |  |  | 2015-06-19 14:57 |  | 0 | 0 | 148.267 | 148.2667 | 23277.867 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 3613 |  |  | - |  | Switchyard system protection devices - external (not OMC) | [8 empty] | AMP CODE: |  | 03
|  | DESCRIPTION : |  | F030The C phase on TC7 Main Breaker failed causing a bus lock out on A bus.
TC7 | 85 | U1 | 2015-06-19 17:25 |  |  |  |  | 2015-06-19 21:39 |  | 0 | 0 | 4.233 | 4.2333 | 664.633 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340The 89 Static Start switch, 89SS, failed to engage due to a blown fuse.
TC7 | 87 | SF | 2015-06-24 12:33 |  |  |  |  | 2015-06-24 13:45 |  | 0 | 0 | 1.2 | 1.2 | 188.4 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5246 |  |  | - |  | Gas Turbine Control System - hardware problems (including card failure) | [8 empty] | AMP CODE: |  | 70
|  | DESCRIPTION : |  | F700Unit failed to synchronize, found a burnt relay in the TTUR control card. Changed
TC7 | 88 | U1 | 2015-06-24 14:13 |  |  |  |  | 2015-06-24 14:57 |  | 0 | 0 | 0.733 | 0.7333 | 115.133 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5246 |  |  | - |  | Gas Turbine Control System - hardware problems (including card failure) | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F700Unit was brought offline in order to change the TTUR control card in the MK-VI con
TC7 | 98 | U1 | 2015-07-18 03:40 |  |  |  |  | 2015-07-18 10:37 |  | 0 | 0 | 6.95 | 6.95 | 1105.05 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5037 |  |  | - |  | Inlet bleed heat valve | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340The inlet bleed heat pneumatic solenoid failed causing the IBH valve to go full op
TC7 | 118 | U1 | 2015-08-11 12:47 |  |  |  |  | 2015-08-11 13:57 |  | 0 | 0 | 1.167 | 1.1667 | 185.5 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 4619 |  |  | - |  | Other hydrogen system problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830The hydrogen vent valve opened during unit start up and caused the generator to lo
TC7 | 142 | U1 | 2015-09-09 14:03 |  |  |  |  | 2015-09-09 15:32 |  | 0 | 0 | 1.483 | 1.4833 | 235.85 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 4619 |  |  | - |  | Other hydrogen system problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830Hydrogen purge system vent valve opened due to vibration experienced during normal
TC7 | 152 | U1 | 2015-10-18 16:29 |  |  |  |  | 2015-10-19 13:20 |  | 0 | 0 | 20.85 | 20.85 | 3732.15 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5048 |  |  | - |  | Gas fuel system including controls and instrumentation | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F540Fuel gas leak at the interstage pressure transmitter caused high hazardous gas det
TC7 | 154 | U1 | 2015-10-26 19:13 |  |  |  |  | 2015-10-26 19:35 |  | 0 | 0 | 0.367 | 0.3667 | 65.633 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5001 |  |  | - |  | Inlet air vanes/nozzles | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820There was a signal mismatch on the IGV control, the signal did not match real IGV
TC7 | 156 | U1 | 2015-10-27 02:00 |  |  |  |  | 2015-10-27 04:09 |  | 0 | 0 | 2.15 | 2.15 | 384.85 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5048 |  |  | - |  | Gas fuel system including controls and instrumentation | [8 empty] | AMP CODE: |  | 09
|  | DESCRIPTION : |  | F090The fuel gas transmitters for the interstage fuel gas pressure (P2) drifted beyond
TC7 | 179 | U1 | 2015-12-13 18:54 |  |  |  |  | 2015-12-13 19:03 |  | 0 | 0 | 0.15 | 0.15 | 26.85 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340LCI needed a manual reset to clear fault.
TC7 | 182 | U1 | 2015-12-19 18:16 |  |  |  |  | 2015-12-19 19:46 |  | 0 | 0 | 1.5 | 1.5 | 268.5 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5001 |  |  | - |  | Inlet air vanes/nozzles | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Unit tripped due to IGV signal mismatch, all exhaust spreads went up due to IGV's
TC7 | 1 | U1 | 2016-01-05 05:59 |  |  |  |  | 2016-01-05 11:29 |  | 0 | 0 | 5.5 | 5.5 | 984.5 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5108 |  |  | - |  | High engine exhaust temperature | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Machine tripped on exhaust spread due to IGV's not following control signal causin
TC7 | 8 | U1 | 2016-01-24 12:56 |  |  |  |  | 2016-01-24 14:04 |  | 0 | 0 | 1.133 | 1.1333 | 202.867 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 4619 |  |  | - |  | Other hydrogen system problems | [8 empty] | AMP CODE: |  | 66
|  | DESCRIPTION : |  | F660On the previous run the hydrogen vent valve vibrated open liberating all of the hy
TC7 | 10 | U1 | 2016-01-24 14:10 |  |  |  |  | 2016-01-24 16:13 |  | 0 | 0 | 2.05 | 2.05 | 366.95 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 4619 |  |  | - |  | Other hydrogen system problems | [8 empty] | AMP CODE: |  | 66
|  | DESCRIPTION : |  | F660This outage was to confirm that the generator did not suffer any detrimental effec
TC7 | 15 | U1 | 2016-01-27 20:38 |  |  |  |  | 2016-01-27 21:20 |  | 0 | 0 | 0.7 | 0.7 | 125.3 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 4610 |  |  | - |  | Hydrogen cooling system piping and valves | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F830The hydrogen vent solenoid opened once again and vented hydrogen from generator. S
TC7 | 27 | U1 | 2016-03-01 08:09 |  |  |  |  | 2016-03-01 08:43 |  | 0 | 0 | 0.567 | 0.5667 | 95.767 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 9131 |  |  | - |  | Lack of fuel (interruptible supply of fuel part of fuel contract) | [8 empty] | AMP CODE: |  | NF
|  | DESCRIPTION : |  | F340A Texas Gas supply valve electro-pneumatic transducer failed, causing the valve to
TC7 | 33 | U1 | 2016-03-16 21:56 |  |  |  |  | 2016-03-17 03:31 |  | 0 | 0 | 5.583 | 5.5833 | 943.584 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 9131 |  |  | - |  | Lack of fuel (interruptible supply of fuel part of fuel contract) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F130The gas supply valve closed while unit was coming offline.
TC7 | 39 | U1 | 2016-03-24 06:35 |  |  |  |  | 2016-03-24 07:12 |  | 0 | 0 | 0.617 | 0.6167 | 104.217 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 8656 |  |  | - |  | Controls and instrumentation | [8 empty] | AMP CODE: |  | 52
|  | DESCRIPTION : |  | F520Unit made unavailable due to hazgas monitor problems.
TC7 | 48 | SF | 2016-04-19 06:30 |  |  |  |  | 2016-04-19 06:43 |  | 0 | 0 | 0.217 | 0.2167 | 36.617 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5240 |  |  | - |  | Fire detection and extinguishing system (including hazardous gas detection system) | [8 empty] | AMP CODE: |  | 52
|  | DESCRIPTION : |  | F520Hazard Gas monitors gave a high-high reading, causing a unit startup failure.
TC7 | 64 | U1 | 2016-05-25 13:58 |  |  |  |  | 2016-05-25 15:02 |  | 0 | 0 | 1.067 | 1.0667 | 180.267 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5001 |  |  | - |  | Inlet air vanes/nozzles | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F340TC7 Tripped on Inlet Guide Vane servo problems.
TC7 | 185 | SF | 2016-08-29 12:10 |  |  |  |  | 2016-08-29 12:18 |  | 0 | 0 | 0.133 | 0.1333 | 21.2 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5016 |  |  | - |  | High pressure compressor bleed valves | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340Compressor Bleed Valve #4 experienced a limit switch issue during a startup proced
TC7 | 189 | U1 | 2016-08-31 10:48 |  |  |  |  | 2016-08-31 12:09 |  | 0 | 0 | 1.35 | 1.35 | 214.65 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5016 |  |  | - |  | High pressure compressor bleed valves | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340Compressor Bleed Valve #4 experienced a limit switch failure, resulting in the uni
TC7 | 205 | U1 | 2016-10-13 07:49 |  |  |  |  | 2016-10-13 08:06 |  | 0 | 0 | 0.283 | 0.2833 | 47.883 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 4609 |  |  | - |  | Other exciter problems | [8 empty] | AMP CODE: |  | 52
|  | DESCRIPTION : |  | F520Controls on an Exciter communication board failed. Unit was unavailable during thi
TC7 | 207 | U1 | 2016-10-16 13:03 |  |  |  |  | 2016-10-16 13:18 |  | 0 | 0 | 0.25 | 0.25 | 42.25 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 4609 |  |  | - |  | Other exciter problems | [8 empty] | AMP CODE: |  | 52
|  | DESCRIPTION : |  | F520Communication to the exciter control board failed, resulting in a forced outage un
TC7 | 215 | SF | 2016-10-30 07:16 |  |  |  |  | 2016-10-30 07:31 |  | 0 | 0 | 0.25 | 0.25 | 42.25 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5240 |  |  | - |  | Fire detection and extinguishing system (including hazardous gas detection system) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340Unit failed to start due to high hazardous gas levels being detected when fuel fro
TC7 | 220 | SF | 2016-11-02 05:40 |  |  |  |  | 2016-11-02 05:55 |  | 0 | 0 | 0.25 | 0.25 | 42.25 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5240 |  |  | - |  | Fire detection and extinguishing system (including hazardous gas detection system) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340Unit failed to start due to high hazardous gas levels being detected when fuel fro
TC7 | 224 | U1 | 2016-11-07 11:00 |  |  |  |  | 2016-11-07 15:02 |  | 0 | 0 | 4.033 | 4.0333 | 681.633 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5048 |  |  | - |  | Gas fuel system including controls and instrumentation | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F330Unit tripped on exhaust gas temperature spread indicating loss of combustion can.
TC7 | 236 | U1 | 2016-11-28 14:46 |  |  |  |  | 2016-11-28 20:05 |  | 0 | 0 | 5.317 | 5.3167 | 898.517 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 3610 |  |  | - |  | Switchyard circuit breakers - external (not OMC) | [8 empty] | AMP CODE: |  | 66
|  | DESCRIPTION : |  | F660The hydraulic system responsible for closing a 345kV breaker in the CT Switchyard
TC7 | 1 | U1 | 2017-01-05 01:12 |  |  |  |  | 2017-01-05 07:54 |  | 0 | 0 | 6.7 | 6.7 | 1199.3 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 3610 |  |  | - |  | Switchyard circuit breakers - external (not OMC) | [8 empty] | AMP CODE: |  | 66
|  | DESCRIPTION : |  | F660The hydraulic system responsible for closing a 345kV breaker in the CT Switchyard
TC7 | 3 | U1 | 2017-01-05 18:22 |  |  |  |  | 2017-01-05 21:15 |  | 0 | 0 | 2.883 | 2.8833 | 516.117 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5001 |  |  | - |  | Inlet air vanes/nozzles | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F140The Inlet Guide Vane system was not operating correctly. The hydraulic line filter
TC7 | 4 | U1 | 2017-01-05 21:57 |  |  |  |  | 2017-01-06 01:26 |  | 0 | 0 | 3.483 | 3.4833 | 623.517 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5001 |  |  | - |  | Inlet air vanes/nozzles | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F140The Inlet Guide Vane system was not operating correctly after the filter change. T
TC7 | 38 | U1 | 2017-04-07 05:10 |  |  |  |  | 2017-04-07 12:49 |  | 0 | 0 | 7.65 | 7.65 | 1292.85 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 3690 |  |  | - |  | "Station Service Power Distribution System, General" | [8 empty] | AMP CODE: |  | 40
|  | DESCRIPTION : |  | F400The unit was made unavailable when the feeder breaker to an MCC tripped on ground
TC7 | 40 | U1 | 2017-04-07 22:43 |  |  |  |  | 2017-04-08 08:34 |  | 0 | 0 | 9.85 | 9.85 | 1664.65 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340A relay in the common TC7 and TC8 LCI had failed, causing the unit to be made unav
TC7 | 51 | SF | 2017-04-27 05:46 |  |  |  |  | 2017-04-27 06:15 |  | 0 | 0 | 0.483 | 0.4833 | 81.683 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 52
|  | DESCRIPTION : |  | F520The unit failed to start when an exciter core fan switch gave a false indication,
TC7 | 55 | SF | 2017-04-29 08:39 |  |  |  |  | 2017-04-29 10:35 |  | 0 | 0 | 1.933 | 1.9333 | 326.733 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5048 |  |  | - |  | Gas fuel system including controls and instrumentation | [8 empty] | AMP CODE: |  | 70
|  | DESCRIPTION : |  | F700The unit failed to start when a fuel gas valve controller failed. The controller f
TC7 | 57 | SF | 2017-04-30 08:45 |  |  |  |  | 2017-04-30 09:04 |  | 0 | 0 | 0.317 | 0.3167 | 53.517 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5041 |  |  | - |  | Fuel piping and valves | [8 empty] | AMP CODE: |  | 66
|  | DESCRIPTION : |  | F660Two of the three gas regulating valves were leaking through, which caused a situat
TC7 | 61 | U1 | 2017-05-27 19:54 |  |  |  |  | 2017-05-27 23:40 |  | 0 | 0 | 3.767 | 3.7667 | 636.567 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 9020 |  |  | - |  | Lightning | [8 empty] | AMP CODE: |  | 70
|  | DESCRIPTION : |  | F700A lightning strike caused the unit to be unavailable. The unit was unavailable due
TC7 | 93 | SF | 2017-07-20 10:19 |  |  |  |  | 2017-07-20 10:23 |  | 0 | 0 | 0.067 | 0.0667 | 10.6 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5240 |  |  | - |  | Fire detection and extinguishing system (including hazardous gas detection system) | [8 empty] | AMP CODE: |  | 52
|  | DESCRIPTION : |  | F520TC7 failed to start when the hazardous gas monitor caused a false alarm. The issue
TC7 | 117 | U1 | 2017-08-28 21:57 |  |  |  |  | 2017-08-29 01:17 |  | 0 | 0 | 3.333 | 3.3333 | 530 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5041 |  |  | - |  | Fuel piping and valves | [8 empty] | AMP CODE: |  | 52
|  | DESCRIPTION : |  | F520TC7 became unavailable after a TC7 gas fuel valve closed due to a malfunctioning p
TC7 | 136 | U1 | 2017-10-19 |  |  |  |  | 2017-10-26 14:47 |  | 0 | 0 | 182.783 | 182.7833 | 30890.383 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 4640 |  |  | - |  | Seal oil system and seals | [8 empty] | AMP CODE: |  | 66
|  | DESCRIPTION : |  | F660TC7 was placed on a Forced Outage when excessive seal oil flow did not allow the s
TC7 | 156 | SF | 2017-12-30 16:38 |  |  |  |  | 2017-12-31 06:14 |  | 0 | 0 | 13.6 | 13.6 | 2434.4 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340The unit failed to start when the 89SS switch operated but did not meet its limit
TC7 | 2 | SF | 2018-01-01 03:27 |  |  |  |  | 2018-01-01 12:45 |  | 0 | 0 | 9.3 | 9.3 | 1664.7 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340The unit failed to start when the 89SS switch operated but did not meet its limit
TC7 | 3 | U1 | 2018-01-03 09:22 |  |  |  |  | 2018-01-03 15:01 |  | 0 | 0 | 5.65 | 5.65 | 1011.35 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 3681 |  |  | - |  | Other voltage circuit breakers | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F340One of the three TC6 345 kV main breaker failed to open, causing the Main Switchya
TC7 | 7 | U1 | 2018-01-11 05:35 |  |  |  |  | 2018-01-11 08:18 |  | 0 | 0 | 2.717 | 2.7167 | 486.283 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5240 |  |  | - |  | Fire detection and extinguishing system (including hazardous gas detection system) | [8 empty] | AMP CODE: |  | 52
|  | DESCRIPTION : |  | F520TC7 became unavailable when an alarm came in for hazardous gas detection in the ga
TC7 | 9 | U1 | 2018-01-13 07:41 |  |  |  |  | 2018-01-13 12:36 |  | 0 | 0 | 4.917 | 4.9167 | 880.083 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5100 |  |  | - |  | Chamber | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F520TC7 tripped when alarm came in that neither exhaust fans were running. The switch
TC7 | 14 | U1 | 2018-02-02 09:05 |  |  |  |  | 2018-02-02 09:13 |  | 0 | 0 | 0.133 | 0.1333 | 23.867 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5160 |  |  | - |  | Cooling and seal air system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F700The unit tripped offline when an exhaust frame blower tripped and went to ground.
TC7 | 16 | U1 | 2018-02-15 10:09 |  |  |  |  | 2018-02-15 12:15 |  | 0 | 0 | 2.1 | 2.1 | 375.9 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5041 |  |  | - |  | Fuel piping and valves | [8 empty] | AMP CODE: |  | 52
|  | DESCRIPTION : |  | F520The unit was placed on a Forced Outage for a replacement of the TC7 gas positioner
TC7 | 18 | U1 | 2018-02-15 19:13 |  |  |  |  | 2018-02-15 19:24 |  | 0 | 0 | 0.183 | 0.1833 | 32.817 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5240 |  |  | - |  | Fire detection and extinguishing system (including hazardous gas detection system) | [8 empty] | AMP CODE: |  | 52
|  | DESCRIPTION : |  | F520The unit was placed on a Forced Outage due to problems with the hazardous gas moni
TC7 | 20 | SF | 2018-02-24 17:39 |  |  |  |  | 2018-02-24 18:59 |  | 0 | 0 | 1.333 | 1.3333 | 238.667 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5041 |  |  | - |  | Fuel piping and valves | [8 empty] | AMP CODE: |  | 66
|  | DESCRIPTION : |  | F660Controller to the Gas Monitor Valve failed, causing low gas pressure to unit.
TC7 | 23 | U1 | 2018-02-26 13:35 |  |  |  |  | 2018-02-26 14:12 |  | 0 | 0 | 0.617 | 0.6167 | 110.383 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5240 |  |  | - |  | Fire detection and extinguishing system (including hazardous gas detection system) | [8 empty] | AMP CODE: |  | 52
|  | DESCRIPTION : |  | F520The unit was placed on a Forced Outage due to a false indication of a hazardous ga
TC7 | 100 | SF | 2018-06-17 10:00 |  |  |  |  | 2018-06-17 10:50 |  | 0 | 0 | 0.833 | 0.8333 | 132.5 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 9900 |  |  | - |  | Operator error | [8 empty] | AMP CODE: |  | 87
|  | DESCRIPTION : |  | F870TC7 was started and brought up to speed, but was not synchronized within the speci
TC7 | 198 | U1 | 2018-11-28 18:50 |  |  |  |  | 2018-11-28 21:35 |  | 0 | 0 | 2.75 | 2.75 | 464.75 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5041 |  |  | - |  | Fuel piping and valves | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F130TC7 was forced onto outage due to the gas supply valve closing. The valve closed d
TC7 | 206 | U1 | 2018-12-19 13:57 |  |  |  |  | 2018-12-23 11:00 |  | 0 | 0 | 93.05 | 93.05 | 16655.95 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5150 |  |  | - |  | Turning gear and motor | [8 empty] | AMP CODE: |  | 59
|  | DESCRIPTION : |  | F590The unit was made unavailable for repairs to the TC7 turning gear and gearbox.
TC7 | 14 | U1 | 2019-03-10 21:27 |  |  |  |  | 2019-03-11 02:24 |  | 0 | 0 | 4.95 | 4.95 | 836.55 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5111 |  |  | - |  | Lube oil pumps | [8 empty] | AMP CODE: |  | 49
|  | DESCRIPTION : |  | F490The unit was placed on Forced Outage due to the #1 Aux Lube Oil Pump Motor faultin
TC7 | 54 | U1 | 2019-05-17 12:41 |  |  |  |  | 2019-05-17 13:09 |  | 0 | 0 | 0.467 | 0.4667 | 78.867 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5081 |  |  | - |  | High pressure bearings | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | FV00While working through the hold point to eliminate vibration levels, the unit tripp
TC7 | 68 | U1 | 2019-05-30 14:45 |  |  |  |  | 2019-05-30 15:18 |  | 0 | 0 | 0.55 | 0.55 | 92.95 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5048 |  |  | - |  | Gas fuel system including controls and instrumentation | [8 empty] | AMP CODE: |  | 66
|  | DESCRIPTION : |  | F660The unit was placed on outage due to decreased gas pressure caused by a temporary
TC7 | 25 | U1 | 2021-07-20 15:38 |  |  |  |  | 2021-07-20 18:45 |  | 0 | 0 | 3.117 | 3.1167 | 495.55 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5016 |  |  | - |  | High pressure compressor bleed valves | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F700The unit tripped due to a shorted coil on a solenoid valve that supplies control a
TC7 | 29 | SF | 2021-07-24 11:47 |  |  |  |  | 2021-07-24 12:33 |  | 0 | 0 | 0.767 | 0.7667 | 121.9 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5109 |  |  | - |  | Other exhaust problems (including high exhaust system temperature not attributable to a specific problem) | [8 empty] | AMP CODE: |  | 86
|  | DESCRIPTION : |  | F860The unit failed to start when two adjacent Exhaust thermocopules mechanically fail
TC7 | 50 | U1 | 2021-08-26 14:33 |  |  |  |  | 2021-08-26 21:30 |  | 0 | 0 | 6.95 | 6.95 | 1105.05 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5160 |  |  | - |  | Cooling and seal air system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F700The unit tripped after both exhaust frame blower motors failed, causing the unit t
TC7 | 130 | U1 | 2022-11-12 15:15 |  |  |  |  | 2022-11-14 13:30 |  | 0 | 0 | 46.25 | 46.25 | 7816.25 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5122 |  |  | - |  | Hydraulic oil system piping/valves | [8 empty] | AMP CODE: |  | 59
|  | DESCRIPTION : |  | F540Generator lift oil hoses failed on the collector end (CE) and on the turbine end (
TC7 | 3 | U1 | 2023-03-03 07:33 |  |  |  |  | 2023-03-03 07:41 |  | 0 | 0 | 0.133 | 0.1333 | 22.533 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 9020 |  |  | - |  | Lightning | [8 empty] | AMP CODE: |  | X0
|  | DESCRIPTION : |  | FX00Lightning strike caused a blown fuse on controls for 12" main supply fuel gass ven
TC7 | 11 | SF | 2023-04-04 07:31 |  |  |  |  | 2023-04-04 08:15 |  | 0 | 0 | 0.733 | 0.7333 | 123.933 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5050 |  |  | - |  | Ignition system | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340Spark rods did not fire. Both spark rods failed.
Trimble County - TC8
Unit | Event | Type | Start |  |  |  |  | End |  | GAC | NAC | Duration | Equiv Hrs | Equiv MWH | Cont | Work Start | Work End |  | Hours |  |  | Gross Capacity Impact (MW)
TC8 | 2 | U1 | 2014-01-03 05:21 |  |  |  |  | 2014-01-04 00:26 |  | 0 | 0 | 19.083 | 19.0833 | 3358.667 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 33
|  | DESCRIPTION : |  | F330Forced outage due to issue with 89SS.
TC8 | 5 | SF | 2014-01-05 19:28 |  |  |  |  | 2014-01-06 15:58 |  | 0 | 0 | 20.5 | 20.5 | 3608 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 33
|  | DESCRIPTION : |  | F330Startup failure due to issue with 89SS.
TC8 | 9 | U1 | 2014-01-10 14:00 |  |  |  |  | 2014-01-14 13:28 |  | 0 | 0 | 95.467 | 95.4667 | 16802.133 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 3869 |  |  | - |  | Other fire protection system problems | [8 empty] | AMP CODE: |  | 66
|  | DESCRIPTION : |  | F660Forced outage due to issue with Fire Protection System.
TC8 | 15 | U1 | 2014-01-30 06:34 |  |  |  |  | 2014-01-30 07:49 |  | 0 | 0 | 1.25 | 1.25 | 220 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5041 |  |  | - |  | Fuel piping and valves | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F480Forced outage to reset lifted safety valve that occurred due to fuel gas pressure
TC8 | 103 | U1 | 2014-06-10 18:00 |  |  |  |  | 2014-06-10 20:27 |  | 0 | 0 | 2.45 | 2.45 | 384.65 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5049 |  |  | - |  | Other fuel system problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820CT8 tripped as the unit was being shutdown due to excessive inlet gas pressure. I
TC8 | 111 | U1 | 2014-06-23 09:10 |  |  |  |  | 2014-06-24 12:15 |  | 0 | 0 | 27.083 | 27.0833 | 4252.083 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 3869 |  |  | - |  | Other fire protection system problems | [8 empty] | AMP CODE: |  | 54
|  | DESCRIPTION : |  | F540Fire protection CO2 tank lost all CO2 due to refrigeration unit malfunction. Machi
TC8 | 129 | SF | 2014-07-22 13:10 |  |  |  |  | 2014-07-22 13:45 |  | 0 | 0 | 0.583 | 0.5833 | 91.583 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5041 |  |  | - |  | Fuel piping and valves | [8 empty] | AMP CODE: |  | 66
|  | DESCRIPTION : |  | F660The main fuel gas shut-off valve closed on a high fuel gas pressure spike the day
TC8 | 138 | U1 | 2014-08-02 03:33 |  |  |  |  | 2014-08-02 03:50 |  | 0 | 0 | 0.283 | 0.2833 | 44.483 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340Static Start switch failed to engage.
TC8 | 140 | U1 | 2014-08-02 05:02 |  |  |  |  | 2014-08-02 08:41 |  | 0 | 0 | 3.65 | 3.65 | 573.05 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340Initial signal was that the LCI was not working, further investigation revealed th
TC8 | 162 | U1 | 2014-09-20 11:28 |  |  |  |  | 2014-09-20 19:47 |  | 0 | 0 | 8.317 | 8.3167 | 1305.717 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5240 |  |  | - |  | Fire detection and extinguishing system (including hazardous gas detection system) | [8 empty] | AMP CODE: |  | 54
|  | DESCRIPTION : |  | F540The fire protection CO2 skid was found empty. Refrigeration unit checked and CO2 t
TC8 | 164 | SF | 2014-09-25 13:55 |  |  |  |  | 2014-09-25 19:22 |  | 0 | 0 | 5.45 | 5.45 | 855.65 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340Cam switch hold down bolts were loose, this caused false indication on 89SS travel
TC8 | 166 | U1 | 2014-09-25 19:53 |  |  |  |  | 2014-09-25 21:21 |  | 0 | 0 | 1.467 | 1.4667 | 230.267 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 3661 |  |  | - |  | 4000-7000 volt circuit breakers | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340Lose wire found on control circuit of the LCI 4KV breaker. Wire tightened and mach
TC8 | 168 | U1 | 2014-10-01 12:45 |  |  |  |  | 2014-10-01 13:15 |  | 0 | 0 | 0.5 | 0.5 | 88 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 3661 |  |  | - |  | 4000-7000 volt circuit breakers | [8 empty] | AMP CODE: |  | P0
|  | DESCRIPTION : |  | F700Improper switching instructions on the 4KV outage on TC5 and 6, caused a black out
TC8 | 170 | U1 | 2014-10-01 14:58 |  |  |  |  | 2014-10-01 15:25 |  | 0 | 0 | 0.45 | 0.45 | 79.2 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5041 |  |  | - |  | Fuel piping and valves | [8 empty] | AMP CODE: |  | 33
|  | DESCRIPTION : |  | F330This was not a bad solenoid, it was a high differential across the fuel gas main s
TC8 | 173 | U1 | 2014-10-02 12:48 |  |  |  |  | 2014-10-02 13:30 |  | 0 | 0 | 0.7 | 0.7 | 123.2 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5240 |  |  | - |  | Fire detection and extinguishing system (including hazardous gas detection system) | [8 empty] | AMP CODE: |  | 79
|  | DESCRIPTION : |  | F820Fire protection testing caused the unit to lose turning gear. Once fire protection
TC8 | 184 | U1 | 2014-10-07 18:44 |  |  |  |  | 2014-10-07 19:00 |  | 0 | 0 | 0.267 | 0.2667 | 46.933 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5108 |  |  | - |  | High engine exhaust temperature | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F750The gas valve closing is a result of the high exhaust spread trip from exhaust the
TC8 | 208 | U1 | 2014-11-12 13:09 |  |  |  |  | 2014-11-12 13:58 |  | 0 | 0 | 0.817 | 0.8167 | 143.733 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 3669 |  |  | - |  | Other 4000-7000 volt problems | [8 empty] | AMP CODE: |  | 70
|  | DESCRIPTION : |  | F700The loss of power on TC7 event 146 caused the loss of power to the shared LCI, mak
TC8 | 210 | SF | 2014-11-14 07:00 |  |  |  |  | 2014-11-14 10:47 |  | 0 | 0 | 3.783 | 3.7833 | 665.867 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5041 |  |  | - |  | Fuel piping and valves | [8 empty] | AMP CODE: |  | 48
|  | DESCRIPTION : |  | F480Condensation made its way inside the terminal block for the micro switches in the
TC8 | 212 | U1 | 2014-11-15 15:03 |  |  |  |  | 2014-11-15 16:09 |  | 0 | 0 | 1.1 | 1.1 | 193.6 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5049 |  |  | - |  | Other fuel system problems | [8 empty] | AMP CODE: |  | 66
|  | DESCRIPTION : |  | F660Relief valve on TC9/10 fuel gas heater lifted, and all gas turbines needed to be u
TC8 | 232 | U1 | 2014-12-11 17:55 |  |  |  |  | 2014-12-11 19:07 |  | 0 | 0 | 1.2 | 1.2 | 211.2 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340Static start 89SS switch failed to engage. Adjustments made to limit switches and
TC8 | 237 | U1 | 2014-12-13 14:10 |  |  |  |  | 2014-12-13 21:42 |  | 0 | 0 | 7.533 | 7.5333 | 1325.867 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 3611 |  |  | - |  | Switchyard circuit breakers - external (OMC) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340Generator line breaker failed to operate due to springs not charging. Repairs made
TC8 | 240 | U1 | 2014-12-14 11:36 |  |  |  |  | 2014-12-14 12:53 |  | 0 | 0 | 1.283 | 1.2833 | 225.867 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 3611 |  |  | - |  | Switchyard circuit breakers - external (OMC) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340Generator mail line breaker failed to operate due to springs not charging properly
TC8 | 242 | U1 | 2014-12-15 11:01 |  |  |  |  | 2014-12-15 16:12 |  | 0 | 0 | 5.183 | 5.1833 | 912.267 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5240 |  |  | - |  | Fire detection and extinguishing system (including hazardous gas detection system) | [8 empty] | AMP CODE: |  | 43
|  | DESCRIPTION : |  | F430Fire protection upgrade, difference in wiring between units 5 & 6 and 7 through 10
TC8 | 22 | U1 | 2015-02-10 20:49 |  |  |  |  | 2015-02-10 22:22 |  | 0 | 0 | 1.55 | 1.55 | 272.8 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5049 |  |  | - |  | Other fuel system problems | [8 empty] | AMP CODE: |  | 78
|  | DESCRIPTION : |  | F780The dew point control fuel gas heater was not operating properly, adjustments were
TC8 | 38 | U1 | 2015-04-29 04:45 |  |  |  |  | 2015-04-29 20:14 |  | 0 | 0 | 15.483 | 15.4833 | 2430.883 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340The 89SS switch failed to open due to a defective contactor in the 89SS control bo
TC8 | 40 | U1 | 2015-04-29 20:23 |  |  |  |  | 2015-04-29 20:47 |  | 0 | 0 | 0.4 | 0.4 | 62.8 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340Adjustment needed on the speed of travel for the 89SS switch, it was running up ag
TC8 | 43 | U1 | 2015-05-01 03:42 |  |  |  |  | 2015-05-01 04:36 |  | 0 | 0 | 0.9 | 0.9 | 141.3 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340This outage due to TC7's 89ND problem with a blown fuse, this event makes TC7 and
TC8 | 57 | U1 | 2015-05-18 22:00 |  |  |  |  | 2015-05-18 22:48 |  | 0 | 0 | 0.8 | 0.8 | 125.6 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340The 89SS static start switch failed to engage due to overtravel, when attempting t
TC8 | 65 | U1 | 2015-05-31 08:27 |  |  |  |  | 2015-05-31 10:46 |  | 0 | 0 | 2.317 | 2.3167 | 363.717 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340The static start switch 89SS did not engage on start signal. Repairs made and unit
TC8 | 75 | U1 | 2015-06-09 08:03 |  |  |  |  | 2015-06-09 14:03 |  | 0 | 0 | 6 | 6 | 942 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5048 |  |  | - |  | Gas fuel system including controls and instrumentation | [8 empty] | AMP CODE: |  | 54
|  | DESCRIPTION : |  | F540The final fuel gas filter that was worked on during the previous outage had a fuel
TC8 | 83 | U1 | 2015-06-15 07:38 |  |  |  |  | 2015-06-15 08:16 |  | 0 | 0 | 0.633 | 0.6333 | 99.433 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 3610 |  |  | - |  | Switchyard circuit breakers - external (not OMC) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340MOD on TC9 failed to close, needed B bus outage to correct situation. B bus affect
TC8 | 88 | U1 | 2015-06-19 10:32 |  |  |  |  | 2015-06-19 14:35 |  | 0 | 0 | 4.05 | 4.05 | 635.85 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340The 89SS, static start switch failed to engage.
TC8 | 90 | U1 | 2015-06-19 17:25 |  |  |  |  | 2015-06-19 21:39 |  | 0 | 0 | 4.233 | 4.2333 | 664.633 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340The 89SS, static start switch failed to engage due to a blown fuse.
TC8 | 99 | SF | 2015-07-03 01:25 |  |  |  |  | 2015-07-03 02:30 |  | 0 | 0 | 1.083 | 1.0833 | 172.25 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5108 |  |  | - |  | High engine exhaust temperature | [8 empty] | AMP CODE: |  | 75
|  | DESCRIPTION : |  | F750Exhaust thermocouple failed high causing an immediate unit trip.
TC8 | 102 | U1 | 2015-07-06 12:55 |  |  |  |  | 2015-07-06 13:18 |  | 0 | 0 | 0.383 | 0.3833 | 60.95 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340LCI cooling water resisitivity did not allow LCI to start.
TC8 | 174 | U1 | 2015-12-13 18:54 |  |  |  |  | 2015-12-13 19:03 |  | 0 | 0 | 0.15 | 0.15 | 26.85 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340LCI needed a manual reset to clear fault.
TC8 | 18 | U1 | 2016-03-01 08:09 |  |  |  |  | 2016-03-01 08:43 |  | 0 | 0 | 0.567 | 0.5667 | 95.767 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 9131 |  |  | - |  | Lack of fuel (interruptible supply of fuel part of fuel contract) | [8 empty] | AMP CODE: |  | NF
|  | DESCRIPTION : |  | F340A Texas Gas supply valve electro-pneumatic transducer failed, causing the valve to
TC8 | 22 | U1 | 2016-03-16 22:29 |  |  |  |  | 2016-03-17 04:05 |  | 0 | 0 | 5.6 | 5.6 | 946.4 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 9131 |  |  | - |  | Lack of fuel (interruptible supply of fuel part of fuel contract) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F130Unit outage due to gas valve closure while unit was coming offline.
TC8 | 40 | U1 | 2016-05-24 11:55 |  |  |  |  | 2016-05-25 20:05 |  | 0 | 0 | 32.167 | 32.1667 | 5436.166 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 4619 |  |  | - |  | Other hydrogen system problems | [8 empty] | AMP CODE: |  | 54
|  | DESCRIPTION : |  | F540Unit offline due to Hydrogen leak.
TC8 | 66 | U1 | 2016-08-09 14:28 |  |  |  |  | 2016-08-10 10:01 |  | 0 | 0 | 19.55 | 19.55 | 3108.45 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 3869 |  |  | - |  | Other fire protection system problems | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F660TC8 was taken offline once it was discovered the C02 Fire Protection tank was belo
TC8 | 90 | U1 | 2016-10-13 09:17 |  |  |  |  | 2016-10-13 11:38 |  | 0 | 0 | 2.35 | 2.35 | 397.15 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5048 |  |  | - |  | Gas fuel system including controls and instrumentation | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340A TC8 Gas Valve positioner failed, resulting in a Forced Outage during this timefr
TC8 | 111 | SF | 2016-12-20 05:17 |  |  |  |  | 2016-12-20 07:52 |  | 0 | 0 | 2.583 | 2.5833 | 462.417 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5016 |  |  | - |  | High pressure compressor bleed valves | [8 empty] | AMP CODE: |  | 72
|  | DESCRIPTION : |  | F720The unit failed to start due to a compressor bleed valve failing to completely ope
TC8 | 5 | U1 | 2017-01-05 10:46 |  |  |  |  | 2017-01-05 11:05 |  | 0 | 0 | 0.317 | 0.3167 | 56.683 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5108 |  |  | - |  | High engine exhaust temperature | [8 empty] | AMP CODE: |  | 59
|  | DESCRIPTION : |  | F590Maintenace work on the Engine Exhaust Temperature thermocouples resulted in an out
TC8 | 40 | U1 | 2017-04-07 22:43 |  |  |  |  | 2017-04-08 08:34 |  | 0 | 0 | 9.85 | 9.85 | 1664.65 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340A relay in the common TC7 and TC8 LCI had failed, causing the unit to be made unav
TC8 | 57 | U1 | 2017-05-27 19:54 |  |  |  |  | 2017-05-27 23:40 |  | 0 | 0 | 3.767 | 3.7667 | 636.567 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 9020 |  |  | - |  | Lightning | [8 empty] | AMP CODE: |  | 70
|  | DESCRIPTION : |  | F700A lightning strike caused the unit to be unavailable. The unit was unavailable due
TC8 | 67 | U1 | 2017-06-30 08:00 |  |  |  |  | 2017-06-30 09:41 |  | 0 | 0 | 1.683 | 1.6833 | 267.65 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5041 |  |  | - |  | Fuel piping and valves | [8 empty] | AMP CODE: |  | 13
|  | DESCRIPTION : |  | F130The Fuel Gas Startup valve positioner failed. It was replaced and the unit was ret
TC8 | 69 | U1 | 2017-06-30 09:47 |  |  |  |  | 2017-06-30 12:00 |  | 0 | 0 | 2.217 | 2.2167 | 352.45 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5041 |  |  | - |  | Fuel piping and valves | [8 empty] | AMP CODE: |  | 09
|  | DESCRIPTION : |  | F090The Fuel Gas Startup valve positioner failed to function properly until current ra
TC8 | 80 | SF | 2017-08-09 13:01 |  |  |  |  | 2017-08-09 14:52 |  | 0 | 0 | 1.85 | 1.85 | 294.15 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5081 |  |  | - |  | High pressure bearings | [8 empty] | AMP CODE: |  | 66
|  | DESCRIPTION : |  | F660TC8 was made unavailable after the bearing lift oil pressure switch created an ala
TC8 | 94 | U1 | 2017-08-18 05:30 |  |  |  |  | 2017-08-18 07:40 |  | 0 | 0 | 2.167 | 2.1667 | 344.5 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5037 |  |  | - |  | Inlet bleed heat valve | [8 empty] | AMP CODE: |  | 63
|  | DESCRIPTION : |  | F630The unit was placed on a Forced Outage when a solenoid failed on the inlet bleed h
TC8 | 96 | U1 | 2017-08-18 12:47 |  |  |  |  | 2017-08-18 23:23 |  | 0 | 0 | 10.6 | 10.6 | 1685.4 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 4810 |  |  | - |  | Generator output breaker | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F660The unit was placed on a Forced Outage when a unit line breaker hydraulic pole spr
TC8 | 121 | U1 | 2017-09-25 10:42 |  |  |  |  | 2017-09-25 10:47 |  | 0 | 0 | 0.083 | 0.0833 | 14.083 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5109 |  |  | - |  | Other exhaust problems (including high exhaust system temperature not attributable to a specific problem) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F840limit switch issues with the exhaust blowers caused the unit to become unavailable
TC8 | 130 | U1 | 2017-10-03 11:27 |  |  |  |  | 2017-10-03 16:09 |  | 0 | 0 | 4.7 | 4.7 | 794.3 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 4810 |  |  | - |  | Generator output breaker | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F660The unit was placed on a Forced Outage when a unit line breaker hydraulic pole spr
TC8 | 191 | U1 | 2017-12-30 18:55 |  |  |  |  | 2017-12-30 20:44 |  | 0 | 0 | 1.817 | 1.8167 | 325.183 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5041 |  |  | - |  | Fuel piping and valves | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F340The unit was placed on a Forced Outage after a fuel gas vent valve failed to close
TC8 | 20 | U1 | 2018-02-02 07:08 |  |  |  |  | 2018-02-02 21:32 |  | 0 | 0 | 14.4 | 14.4 | 2577.6 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 4810 |  |  | - |  | Generator output breaker | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F660The hydraulic system to the TC8 Breaker failed, causing the unit to trip offline.
TC8 | 88 | SF | 2018-05-04 05:33 |  |  |  |  | 2018-05-04 06:51 |  | 0 | 0 | 1.3 | 1.3 | 219.7 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5016 |  |  | - |  | High pressure compressor bleed valves | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340TC8 failed to start due to a Compressor Bleed valve actuator failure. The actuator
TC8 | 273 | U1 | 2018-11-13 06:44 |  |  |  |  | 2018-11-13 12:39 |  | 0 | 0 | 5.917 | 5.9167 | 999.917 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5041 |  |  | - |  | Fuel piping and valves | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F340The unit was forced onto an outage due to the fuel gas valve positioner acting err
TC8 | 274 | U1 | 2018-11-13 12:53 |  |  |  |  | 2018-11-14 05:30 |  | 0 | 0 | 16.617 | 16.6167 | 2808.217 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5041 |  |  | - |  | Fuel piping and valves | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F340The unit was forced onto an outage due to the fuel gas valve positioner acting err
TC8 | 12 | SF | 2019-01-20 18:04 |  |  |  |  | 2019-01-20 19:54 |  | 0 | 0 | 1.833 | 1.8333 | 328.167 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5001 |  |  | - |  | Inlet air vanes/nozzles | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340The unit failed to start when the inlet guide vanes did not actuate quickly enough
TC8 | 21 | U1 | 2019-02-13 05:22 |  |  |  |  | 2019-02-13 08:01 |  | 0 | 0 | 2.65 | 2.65 | 474.35 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 9291 |  |  | - |  | Other fuel quality problems (not OMC) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F340The unit became unavailable due to a lean fuel mixture.
TC8 | 33 | U1 | 2019-03-10 21:27 |  |  |  |  | 2019-03-10 22:29 |  | 0 | 0 | 1.033 | 1.0333 | 174.633 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5111 |  |  | - |  | Lube oil pumps | [8 empty] | AMP CODE: |  | 49
|  | DESCRIPTION : |  | F490The unit was placed on Forced Outage due to the #1 Aux Lube Oil Pump Motor faultin
TC8 | 46 | U1 | 2019-05-24 03:24 |  |  |  |  | 2019-05-24 07:12 |  | 0 | 0 | 3.8 | 3.8 | 642.2 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5248 |  |  | - |  | Gas Turbine Control System - logic problems | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340The unit experienced a Forced Outage after an upgrade caused the failure of certai
TC8 | 48 | U1 | 2019-05-30 14:45 |  |  |  |  | 2019-05-30 15:18 |  | 0 | 0 | 0.55 | 0.55 | 92.95 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5048 |  |  | - |  | Gas fuel system including controls and instrumentation | [8 empty] | AMP CODE: |  | 66
|  | DESCRIPTION : |  | F660The unit was placed on outage due to decreased gas pressure caused by a temporary
TC8 | 155 | SF | 2020-11-13 07:10 |  |  |  |  | 2020-11-13 11:32 |  | 0 | 0 | 4.367 | 4.3667 | 737.967 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 3610 |  |  | - |  | Switchyard circuit breakers - external (not OMC) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340The unit was at Full Speed No Load and breaker would not close when attempting to
TC8 | 3 | U1 | 2021-01-26 06:05 |  |  |  |  | 2021-01-26 15:04 |  | 0 | 0 | 8.983 | 8.9833 | 1608.017 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5190 |  |  | - |  | Other auxiliary system problems | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340The unit was made unavailable when a purge credit nitrogen valve failed to operate
TC8 | 63 | SF | 2021-06-08 11:51 |  |  |  |  | 2021-06-08 12:13 |  | 0 | 0 | 0.367 | 0.3667 | 58.3 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 52
|  | DESCRIPTION : |  | F520The unit failed to start when the LCI did not engage due to the generator breaker
TC8 | 81 | U1 | 2021-06-24 14:18 |  |  |  |  | 2021-06-24 15:24 |  | 0 | 0 | 1.1 | 1.1 | 174.9 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5109 |  |  | - |  | Other exhaust problems (including high exhaust system temperature not attributable to a specific problem) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F840The unit tripped offline due to failure of the exhaust frame blower pressures to r
TC8 | 147 | U1 | 2021-09-14 19:20 |  |  |  |  | 2021-09-14 20:02 |  | 0 | 0 | 0.7 | 0.7 | 118.3 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 4609 |  |  | - |  | Other exciter problems | [8 empty] | AMP CODE: |  | 84
|  | DESCRIPTION : |  | F840Investigation underway, exciter tripped on Reserve state.
TC8 | 8 | U1 | 2023-03-03 07:33 |  |  |  |  | 2023-03-03 07:41 |  | 0 | 0 | 0.133 | 0.1333 | 22.533 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 9020 |  |  | - |  | Lightning | [8 empty] | AMP CODE: |  | X0
|  | DESCRIPTION : |  | FX00Lightning strike caused a blown fuse on controls for 12" main supply fuel gass ven
TC8 | 12 | U1 | 2023-03-20 03:16 |  |  |  |  | 2023-03-20 04:39 |  | 0 | 0 | 1.383 | 1.3833 | 233.783 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340LCI blower motor voltage problems, caused LCI not active.
TC8 | 21 | U1 | 2023-06-09 07:53 |  |  |  |  | 2023-06-09 09:48 |  | 0 | 0 | 1.917 | 1.9167 | 304.75 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5240 |  |  | - |  | Fire detection and extinguishing system (including hazardous gas detection system) | [8 empty] | AMP CODE: |  | 09
|  | DESCRIPTION : |  | F090Defective haz. gas detector sensor caused not ready to start condition.
TC8 | 39 | SF | 2023-09-25 16:17 |  |  |  |  | 2023-09-25 21:20 |  | 0 | 0 | 5.05 | 5.05 | 853.45 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5016 |  |  | - |  | High pressure compressor bleed valves | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340Failed to start due to compressor bleed valves not operating, immediate trip.
Trimble County - TC9
Unit | Event | Type | Start |  |  |  |  | End |  | GAC | NAC | Duration | Equiv Hrs | Equiv MWH | Cont | Work Start | Work End |  | Hours |  |  | Gross Capacity Impact (MW)
TC9 | 3 | SF | 2014-01-03 |  |  |  |  | 2014-01-03 20:51 |  | 0 | 0 | 20.85 | 20.85 | 3669.6 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340Startup failure due to issue with 89SS.
TC9 | 7 | U1 | 2014-01-06 02:27 |  |  |  |  | 2014-01-06 02:57 |  | 0 | 0 | 0.5 | 0.5 | 88 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340Forced outage due to issue with 89SS.
TC9 | 15 | U1 | 2014-02-07 12:38 |  |  |  |  | 2014-02-07 15:35 |  | 0 | 0 | 2.95 | 2.95 | 519.2 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5041 |  |  | - |  | Fuel piping and valves | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F480Forced outage to address pressure swings due to worker fuel gas valve.
TC9 | 20 | SF | 2014-02-26 02:38 |  |  |  |  | 2014-02-26 03:45 |  | 0 | 0 | 1.117 | 1.1167 | 196.533 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 33
|  | DESCRIPTION : |  | F330Startup failure due to 89SS on TC10 failing to open.
TC9 | 22 | U1 | 2014-02-26 19:14 |  |  |  |  | 2014-02-26 19:15 |  | 0 | 0 | 0.017 | 0.0167 | 2.933 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5160 |  |  | - |  | Cooling and seal air system | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F660Forced outage from load runback due to issue with Exhaust Frame Blower.
TC9 | 30 | SF | 2014-03-16 18:25 |  |  |  |  | 2014-03-16 20:27 |  | 0 | 0 | 2.033 | 2.0333 | 357.867 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 33
|  | DESCRIPTION : |  | F330Startup failure due to 89SS not disengaging on TC10.
TC9 | 33 | SF | 2014-03-18 05:09 |  |  |  |  | 2014-03-18 06:54 |  | 0 | 0 | 1.75 | 1.75 | 308 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 3631 |  |  | - |  | 400-700 volt circuit breakers | [8 empty] | AMP CODE: |  | 63
|  | DESCRIPTION : |  | F630Startup failure due to TC9 MCC #2 feed breaker opening cutting power to inservice
TC9 | 43 | U1 | 2014-04-03 05:09 |  |  |  |  | 2014-04-03 06:12 |  | 0 | 0 | 1.05 | 1.05 | 164.85 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340Start up failure due to 89SS not engaging.
TC9 | 45 | U1 | 2014-04-03 11:38 |  |  |  |  | 2014-04-03 11:55 |  | 0 | 0 | 0.283 | 0.2833 | 44.483 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5041 |  |  | - |  | Fuel piping and valves | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Lightning strike affected start-up and worker valves.
TC9 | 47 | SF | 2014-04-03 17:50 |  |  |  |  | 2014-04-03 18:45 |  | 0 | 0 | 0.917 | 0.9167 | 143.917 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340Start up failure due to 89SS not engaging.
TC9 | 50 | SF | 2014-04-06 06:20 |  |  |  |  | 2014-04-06 06:45 |  | 0 | 0 | 0.417 | 0.4167 | 65.417 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340Failure to start due to 89SS not engaging.
TC9 | 53 | SF | 2014-04-09 05:08 |  |  |  |  | 2014-04-09 06:21 |  | 0 | 0 | 1.217 | 1.2167 | 191.017 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F34089SS failed to engage.
TC9 | 57 | U1 | 2014-04-10 16:41 |  |  |  |  | 2014-04-10 19:32 |  | 0 | 0 | 2.85 | 2.85 | 447.45 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F34089ND on TC10 failed to engage, both units removed from service to make repairs.
TC9 | 59 | SF | 2014-04-11 17:01 |  |  |  |  | 2014-04-12 04:01 |  | 0 | 0 | 11 | 11 | 1727 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340LCI breaker problem.
TC9 | 61 | SF | 2014-04-21 09:29 |  |  |  |  | 2014-04-21 09:46 |  | 0 | 0 | 0.283 | 0.2833 | 44.483 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F34089SS VFD setting too low to work.
TC9 | 63 | U1 | 2014-04-21 12:32 |  |  |  |  | 2014-04-21 12:37 |  | 0 | 0 | 0.083 | 0.0833 | 13.083 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 3690 |  |  | - |  | "Station Service Power Distribution System, General" | [8 empty] | AMP CODE: |  | 49
|  | DESCRIPTION : |  | F490Electrical glitch caused turbine controls to lose power momentarily (2 seconds).
TC9 | 67 | U1 | 2014-04-25 02:09 |  |  |  |  | 2014-04-25 04:00 |  | 0 | 0 | 1.85 | 1.85 | 290.45 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 3661 |  |  | - |  | 4000-7000 volt circuit breakers | [8 empty] | AMP CODE: |  | 70
|  | DESCRIPTION : |  | F700Lost Motor Control Center.
TC9 | 73 | SF | 2014-04-28 06:12 |  |  |  |  | 2014-04-28 12:59 |  | 0 | 0 | 6.783 | 6.7833 | 1064.983 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F34089SS switch failed to engage. Adjustments made to linkage.
TC9 | 75 | SF | 2014-04-29 06:12 |  |  |  |  | 2014-04-29 06:34 |  | 0 | 0 | 0.367 | 0.3667 | 57.567 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F34089SS motor VFD overload indication. Overload reset.
TC9 | 79 | SF | 2014-05-02 05:25 |  |  |  |  | 2014-05-02 14:18 |  | 0 | 0 | 8.883 | 8.8833 | 1394.683 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F34089SS on TC9 Failed to engage. Adjusted linkage and installed through bolt.
TC9 | 82 | U1 | 2014-05-04 02:23 |  |  |  |  | 2014-05-04 04:00 |  | 0 | 0 | 1.617 | 1.6167 | 253.817 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340LCI coolant level low, causes machine to be not ready to start.
TC9 | 86 | SF | 2014-05-07 10:27 |  |  |  |  | 2014-05-07 10:32 |  | 0 | 0 | 0.083 | 0.0833 | 13.083 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F34089SS in TC10 did not open and did not allow TC9 89SS to close.
TC9 | 93 | SF | 2014-05-14 11:25 |  |  |  |  | 2014-05-14 20:24 |  | 0 | 0 | 8.983 | 8.9833 | 1410.383 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 3631 |  |  | - |  | 400-700 volt circuit breakers | [8 empty] | AMP CODE: |  | 87
|  | DESCRIPTION : |  | F870Feed to 480V MCC1 tripped. Unit not able to continue starting sequence.
TC9 | 99 | U1 | 2014-05-21 20:00 |  |  |  |  | 2014-05-22 12:59 |  | 0 | 0 | 16.983 | 16.9833 | 2666.383 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 3631 |  |  | - |  | 400-700 volt circuit breakers | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Unit trip due to loss of power feed to 480VAC MCC.
TC9 | 101 | SF | 2014-05-22 14:28 |  |  |  |  | 2014-05-22 14:43 |  | 0 | 0 | 0.25 | 0.25 | 39.25 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5041 |  |  | - |  | Fuel piping and valves | [8 empty] | AMP CODE: |  | 66
|  | DESCRIPTION : |  | F660Unit failed to start due to fuel gas line not being packed to proper pressure.
TC9 | 103 | U1 | 2014-05-22 17:24 |  |  |  |  | 2014-05-22 20:36 |  | 0 | 0 | 3.2 | 3.2 | 502.4 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 3631 |  |  | - |  | 400-700 volt circuit breakers | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Unit tripped due to loss of power to 480VAC MCC.
TC9 | 106 | U1 | 2014-05-27 13:50 |  |  |  |  | 2014-05-28 15:10 |  | 0 | 0 | 25.333 | 25.3333 | 3977.334 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5041 |  |  | - |  | Fuel piping and valves | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Unit tripped due fuel gas pressure swings caused by a failing fuel gas worker valv
TC9 | 109 | U1 | 2014-06-07 08:30 |  |  |  |  | 2014-06-07 15:13 |  | 0 | 0 | 6.717 | 6.7167 | 1054.517 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5299 |  |  | - |  | Other miscellaneous gas turbine problems | [8 empty] | AMP CODE: |  | 70
|  | DESCRIPTION : |  | F70089MD fuse blown causing unit to be unavailable until repairs completed.
TC9 | 111 | U1 | 2014-06-14 20:00 |  |  |  |  | 2014-06-14 21:27 |  | 0 | 0 | 1.45 | 1.45 | 227.65 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F34089SS switch would not close, I/E notified and repaired to return unit to reserve s
TC9 | 125 | U1 | 2014-07-02 16:38 |  |  |  |  | 2014-07-02 19:05 |  | 0 | 0 | 2.45 | 2.45 | 384.65 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 3639 |  |  | - |  | Other 400-700 volt problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Unit tripped off line due to loss of MCC1. Initial investigation points to a groun
TC9 | 127 | U1 | 2014-07-03 04:10 |  |  |  |  | 2014-07-05 09:30 |  | 0 | 0 | 53.333 | 53.3333 | 8373.333 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5140 |  |  | - |  | Battery and charger system | [8 empty] | AMP CODE: |  | 49
|  | DESCRIPTION : |  | F490Event 125 was the start to this event, and chasing DC grounds in the unit we found
TC9 | 129 | SF | 2014-07-07 10:22 |  |  |  |  | 2014-07-07 10:59 |  | 0 | 0 | 0.617 | 0.6167 | 96.817 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 4609 |  |  | - |  | Other exciter problems | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340Network switch in the EX2000 cab needed to be rebooted due to power loss affecting
TC9 | 141 | U1 | 2014-07-23 21:24 |  |  |  |  | 2014-07-23 22:06 |  | 0 | 0 | 0.7 | 0.7 | 109.9 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 3631 |  |  | - |  | 400-700 volt circuit breakers | [8 empty] | AMP CODE: |  | 87
|  | DESCRIPTION : |  | F870Loss of power to one of the MCC's caused unit to be "not ready to start".
TC9 | 144 | U1 | 2014-08-04 07:42 |  |  |  |  | 2014-08-05 08:29 |  | 0 | 0 | 24.783 | 24.7833 | 3890.983 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 3869 |  |  | - |  | Other fire protection system problems | [8 empty] | AMP CODE: |  | 66
|  | DESCRIPTION : |  | F660The fire protection CO2 skid lost all of its charge of CO2, the refrigeration unit
TC9 | 146 | U1 | 2014-08-09 20:20 |  |  |  |  | 2014-08-09 21:35 |  | 0 | 0 | 1.25 | 1.25 | 196.25 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 3634 |  |  | - |  | 400-700 volt protection devices | [8 empty] | AMP CODE: |  | 49
|  | DESCRIPTION : |  | F490TC9 MCC2 lost power on a ground fault. Meggering of individual buckets revealed a
TC9 | 150 | U1 | 2014-08-17 23:33 |  |  |  |  | 2014-08-18 05:45 |  | 0 | 0 | 6.2 | 6.2 | 973.4 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5246 |  |  | - |  | Gas Turbine Control System - hardware problems (including card failure) | [8 empty] | AMP CODE: |  | 70
|  | DESCRIPTION : |  | F820Blown fuse on gas turbine control Mark VI. Lost all lube oil and hydraulic pumps a
TC9 | 152 | U1 | 2014-08-18 07:22 |  |  |  |  | 2014-08-18 13:51 |  | 0 | 0 | 6.483 | 6.4833 | 1017.883 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5246 |  |  | - |  | Gas Turbine Control System - hardware problems (including card failure) | [8 empty] | AMP CODE: |  | 49
|  | DESCRIPTION : |  | F490A DC ground on TC9 keeps blowing fuses on the PDM (Power Distribution Module) in t
TC9 | 156 | U1 | 2014-08-19 11:00 |  |  |  |  | 2014-08-19 13:00 |  | 0 | 0 | 2 | 2 | 314 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5111 |  |  | - |  | Lube oil pumps | [8 empty] | AMP CODE: |  | 49
|  | DESCRIPTION : |  | F490Further troubleshooting of the DC ground faults related to events #152 and #154, f
TC9 | 171 | SF | 2014-09-21 13:25 |  |  |  |  | 2014-09-21 19:50 |  | 0 | 0 | 6.417 | 6.4167 | 1007.417 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 3631 |  |  | - |  | 400-700 volt circuit breakers | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340The Motor Operated Disconnects (MOD) did not close when signal was given. Further
TC9 | 183 | SF | 2014-10-06 05:09 |  |  |  |  | 2014-10-06 08:17 |  | 0 | 0 | 3.133 | 3.1333 | 551.467 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340LCI had low water level. Added demin water and unit made available.
TC9 | 189 | U1 | 2014-11-06 13:18 |  |  |  |  | 2014-11-06 17:33 |  | 0 | 0 | 4.25 | 4.25 | 748 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 3631 |  |  | - |  | 400-700 volt circuit breakers | [8 empty] | AMP CODE: |  | 49
|  | DESCRIPTION : |  | F490The hydraulic pump issue was that MCC#2 was tripped and when the pump on MCC#1 tri
TC9 | 192 | U1 | 2014-11-15 15:03 |  |  |  |  | 2014-11-15 16:09 |  | 0 | 0 | 1.1 | 1.1 | 193.6 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5049 |  |  | - |  | Other fuel system problems | [8 empty] | AMP CODE: |  | 66
|  | DESCRIPTION : |  | F660Relief valve on TC9/10 fuel gas heater lifted, and all gas turbines needed to be u
TC9 | 193 | U1 | 2014-11-15 16:09 |  |  |  |  | 2014-11-15 16:36 |  | 0 | 0 | 0.45 | 0.45 | 79.2 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5049 |  |  | - |  | Other fuel system problems | [8 empty] | AMP CODE: |  | 66
|  | DESCRIPTION : |  | F660Relief valve on TC9/10 fuel gas heater lifted, and we needed to isolate fuel gas h
TC9 | 208 | U1 | 2014-12-10 15:58 |  |  |  |  | 2014-12-10 17:24 |  | 0 | 0 | 1.433 | 1.4333 | 252.267 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 3653 |  |  | - |  | DC protection devices | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820Unit tripped due to loss of DC voltage to the BOP Fuel Gas Valves. Problem correct
TC9 | 19 | U1 | 2015-02-21 15:46 |  |  |  |  | 2015-02-21 16:05 |  | 0 | 0 | 0.317 | 0.3167 | 55.733 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 19
|  | DESCRIPTION : |  | F190Low liquid level on the LCI gave a not ready to start condition. Level was normali
TC9 | 44 | SF | 2015-05-04 06:37 |  |  |  |  | 2015-05-04 07:51 |  | 0 | 0 | 1.233 | 1.2333 | 193.633 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340The 89ND on TC9 failed to open when called to open. Problem was a blown control fu
TC9 | 59 | U1 | 2015-05-28 07:50 |  |  |  |  | 2015-05-28 09:00 |  | 0 | 0 | 1.167 | 1.1667 | 183.167 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 3631 |  |  | - |  | 400-700 volt circuit breakers | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340The 88QS-1, seal oil auxiliary pump motor breaker had a bad contact that did not a
TC9 | 61 | U1 | 2015-05-29 13:06 |  |  |  |  | 2015-05-29 14:36 |  | 0 | 0 | 1.5 | 1.5 | 235.5 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340The 89SS, static start switch on TC10 failed to engage. Due to shared LCI's, TC9 i
TC9 | 63 | SF | 2015-05-30 10:31 |  |  |  |  | 2015-05-31 02:33 |  | 0 | 0 | 16.033 | 16.0333 | 2517.233 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340The problem was a loose electrical plug on the EX2000 and not on the LCI. Plug eng
TC9 | 67 | U1 | 2015-06-07 03:53 |  |  |  |  | 2015-06-07 06:13 |  | 0 | 0 | 2.333 | 2.3333 | 366.333 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340LCI coolant level low. Added fluid and unit made available.
TC9 | 74 | U1 | 2015-06-15 06:35 |  |  |  |  | 2015-06-16 10:05 |  | 0 | 0 | 27.5 | 27.5 | 4317.5 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 3610 |  |  | - |  | Switchyard circuit breakers - external (not OMC) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340The MOD's on TC9 failed to operate.
TC9 | 81 | U1 | 2015-06-26 15:56 |  |  |  |  | 2015-06-26 21:18 |  | 0 | 0 | 5.367 | 5.3667 | 842.567 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5037 |  |  | - |  | Inlet bleed heat valve | [8 empty] | AMP CODE: |  | 70
|  | DESCRIPTION : |  | F700The inlet bleed heat valve air solenoid failed causing valve to go to it's fail sa
TC9 | 88 | SF | 2015-07-24 15:18 |  |  |  |  | 2015-07-24 22:58 |  | 0 | 0 | 7.667 | 7.6667 | 1219 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340Static start switch 89SS caused a not ready to start condition.
TC9 | 90 | SF | 2015-07-25 14:59 |  |  |  |  | 2015-07-25 16:53 |  | 0 | 0 | 1.9 | 1.9 | 302.1 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340Static start switch 89SS did not engage, found loose wire and I/E shop repaired sa
TC9 | 96 | SF | 2015-08-03 15:00 |  |  |  |  | 2015-08-03 22:05 |  | 0 | 0 | 7.083 | 7.0833 | 1126.25 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340Broken micro limit switch on the 89SS.
TC9 | 109 | U1 | 2015-08-26 12:37 |  |  |  |  | 2015-08-28 23:10 |  | 0 | 0 | 58.55 | 58.55 | 9309.45 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 4619 |  |  | - |  | Other hydrogen system problems | [8 empty] | AMP CODE: |  | 54
|  | DESCRIPTION : |  | F540Hydrogen leak in the collector cab. Hazardous gas detectors did not allow unit to
TC9 | 113 | U1 | 2015-09-03 17:26 |  |  |  |  | 2015-09-03 19:59 |  | 0 | 0 | 2.55 | 2.55 | 405.45 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 8790 |  |  | - |  | Miscellaneous CEMS problems | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F820The stinger came loose from the junction box on the outside of the stack, gave err
TC9 | 19 | U1 | 2016-03-01 08:09 |  |  |  |  | 2016-03-01 08:43 |  | 0 | 0 | 0.567 | 0.5667 | 95.767 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 9131 |  |  | - |  | Lack of fuel (interruptible supply of fuel part of fuel contract) | [8 empty] | AMP CODE: |  | NF
|  | DESCRIPTION : |  | F340A Texas Gas supply valve electro-pneumatic transducer failed, causing the valve to
TC9 | 27 | SF | 2016-05-10 16:35 |  |  |  |  | 2016-05-10 16:39 |  | 0 | 0 | 0.067 | 0.0667 | 11.267 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5079 |  |  | - |  | Other combustor problems | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340Pre-ignition trip while starting up.
TC9 | 30 | SF | 2016-05-12 11:31 |  |  |  |  | 2016-05-12 11:46 |  | 0 | 0 | 0.25 | 0.25 | 42.25 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5079 |  |  | - |  | Other combustor problems | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340Startup failure due to igniter issues.
TC9 | 2 | SF | 2017-01-06 16:47 |  |  |  |  | 2017-01-06 23:43 |  | 0 | 0 | 6.933 | 6.9333 | 1241.067 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340The 89SS Rotary Positon Sensors were out of position and did not allow the unit to
TC9 | 32 | SF | 2017-04-19 15:46 |  |  |  |  | 2017-04-19 16:36 |  | 0 | 0 | 0.833 | 0.8333 | 140.833 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5240 |  |  | - |  | Fire detection and extinguishing system (including hazardous gas detection system) | [8 empty] | AMP CODE: |  | 52
|  | DESCRIPTION : |  | F520The hazardous gas alarm came in during the startup of the unit, without cause. The
TC9 | 38 | SF | 2017-05-10 11:32 |  |  |  |  | 2017-05-10 12:44 |  | 0 | 0 | 1.2 | 1.2 | 202.8 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5041 |  |  | - |  | Fuel piping and valves | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340TC9 tripped during startup when fuel gas pressure and flow went high due to the wo
TC9 | 69 | U1 | 2017-06-27 07:01 |  |  |  |  | 2017-06-27 09:36 |  | 0 | 0 | 2.583 | 2.5833 | 410.75 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5041 |  |  | - |  | Fuel piping and valves | [8 empty] | AMP CODE: |  | 13
|  | DESCRIPTION : |  | F130The Fuel Gas Startup valve positioner failed. The issue was resolved and the unit
TC9 | 93 | U1 | 2017-10-11 08:50 |  |  |  |  | 2017-10-11 09:27 |  | 0 | 0 | 0.617 | 0.6167 | 104.217 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 52
|  | DESCRIPTION : |  | F520TC9 was made unavailable due to issues with the common TC9-TC10 LCI.
TC9 | 95 | U1 | 2017-10-11 12:45 |  |  |  |  | 2017-10-11 16:19 |  | 0 | 0 | 3.567 | 3.5667 | 602.767 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 52
|  | DESCRIPTION : |  | F520TC9 was made unavailable due to issues with the common TC9-TC10 LCI.
TC9 | 113 | U1 | 2017-11-27 14:53 |  |  |  |  | 2017-11-27 15:39 |  | 0 | 0 | 0.767 | 0.7667 | 129.567 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 4605 |  |  | - |  | Exciter transformer | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340The unit was placed on a Forced Outage due to an exciter transformer relay failure
TC9 | 6 | U1 | 2018-01-13 09:01 |  |  |  |  | 2018-01-13 11:52 |  | 0 | 0 | 2.85 | 2.85 | 510.15 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5109 |  |  | - |  | Other exhaust problems (including high exhaust system temperature not attributable to a specific problem) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F520TC9 tripped when an alarm came in for exhaust pressure. The switch was frozen beca
TC9 | 26 | U1 | 2018-04-17 04:06 |  |  |  |  | 2018-04-17 05:04 |  | 0 | 0 | 0.967 | 0.9667 | 163.367 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5048 |  |  | - |  | Gas fuel system including controls and instrumentation | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F340The unit was taken offline when the common TC9/TC10 fuel gas heater tripped due to
TC9 | 101 | U1 | 2018-10-03 11:32 |  |  |  |  | 2018-10-03 13:06 |  | 0 | 0 | 1.567 | 1.5667 | 264.767 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5111 |  |  | - |  | Lube oil pumps | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F340The #1 Aux Lube Oil pump tripped, causing the the unit to trip.
TC9 | 106 | SF | 2018-10-05 11:17 |  |  |  |  | 2018-10-05 16:50 |  | 0 | 0 | 5.55 | 5.55 | 937.95 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340Loss of communication between Mark VI and LCI causing unit startup failure.
TC9 | 108 | SF | 2018-10-06 10:57 |  |  |  |  | 2018-10-07 15:40 |  | 0 | 0 | 28.717 | 28.7167 | 4853.117 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340Loss of communication between Mark VI and LCI causing unit startup failure.
TC9 | 121 | U1 | 2018-10-29 15:55 |  |  |  |  | 2018-10-29 17:55 |  | 0 | 0 | 2 | 2 | 338 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5245 |  |  | - |  | Gas Turbine Control System - data highway | [8 empty] | AMP CODE: |  | 61
|  | DESCRIPTION : |  | F610The unit was made unavailable due to TC8's turbine controls upgrade. The TC8 upgra
TC9 | 127 | U1 | 2018-11-28 20:00 |  |  |  |  | 2018-12-02 00:22 |  | 0 | 0 | 76.367 | 76.3667 | 13149.633 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5122 |  |  | - |  | Hydraulic oil system piping/valves | [8 empty] | AMP CODE: |  | 06
|  | DESCRIPTION : |  | F060The unit was forced on outage after the hydraulic lift oil pressure was not suffic
TC9 | 17 | U1 | 2019-05-30 14:45 |  |  |  |  | 2019-05-30 15:18 |  | 0 | 0 | 0.55 | 0.55 | 92.95 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5048 |  |  | - |  | Gas fuel system including controls and instrumentation | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | F660The unit was placed on outage due to decreased gas pressure caused by a temporary
TC9 | 47 | SF | 2019-09-14 02:57 |  |  |  |  | 2019-09-14 10:45 |  | 0 | 0 | 7.8 | 7.8 | 1318.2 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5041 |  |  | - |  | Fuel piping and valves | [8 empty] | AMP CODE: |  | 13
|  | DESCRIPTION : |  | F130A start was attempted on the unit but shortly after reaching purge speed the unit
TC9 | 74 | U1 | 2020-09-01 14:50 |  |  |  |  | 2020-09-01 15:26 |  | 0 | 0 | 0.6 | 0.6 | 101.4 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 3864 |  |  | - |  | Fire protection system instrumentation and controls | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F520The unit tripped offline due to a false fire protection alarm.
TC9 | 89 | U1 | 2020-11-24 08:47 |  |  |  |  | 2020-11-24 10:30 |  | 0 | 0 | 1.717 | 1.7167 | 290.117 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5170 |  |  | - |  | Cooling water system | [8 empty] | AMP CODE: |  | 54
|  | DESCRIPTION : |  | F540The unit was placed on a forced outage to repair a mechanical seal on a leaking co
TC9 | 9 | U1 | 2021-03-25 17:04 |  |  |  |  | 2021-03-25 17:14 |  | 0 | 0 | 0.167 | 0.1667 | 28.167 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 5130 |  |  | - |  | Starting system (including motor) | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340The unit was placed on a Forced Outage due to problems with the LCI.
TC9 | 17 | U1 | 2021-06-28 20:49 |  |  |  |  | 2021-06-30 08:14 |  | 0 | 0 | 35.417 | 35.4167 | 5631.25 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 4640 |  |  | - |  | Seal oil system and seals | [8 empty] | AMP CODE: |  | 54
|  | DESCRIPTION : |  | F540TC10 was made unavailable after the generator lost hydrogen pressure due to a lack
TC9 | 42 | U1 | 2021-08-23 12:42 |  |  |  |  | 2021-08-23 13:29 |  | 0 | 0 | 0.783 | 0.7833 | 124.55 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5447 |  |  | - |  | Gas fuel system including controls and instrumentation | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F660The unit tripped from a sudden load rejection lockout after a fuel gas control val
TC9 | 2 | U1 | 2022-01-03 10:20 |  |  |  |  | 2022-01-03 12:02 |  | 0 | 0 | 1.7 | 1.7 | 304.3 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 5247 |  |  | - |  | Gas Turbine Control System - internal and termination wiring | [8 empty] | AMP CODE: |  | 55
|  | DESCRIPTION : |  | F550The unit became unavailable due to loose turbine control wiring.
TC9 | 10 | U1 | 2022-02-20 23:29 |  |  |  |  | 2022-02-21 11:16 |  | 0 | 0 | 11.783 | 11.7833 | 2109.216 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 4740 |  |  | - |  | Emergency generator trip devices | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F520The unit tripped due to a Generator Protection Relay that received a faulty signal
TC9 | 38 | U1 | 2022-05-20 02:12 |  |  |  |  | 2022-05-20 05:14 |  | 0 | 0 | 3.033 | 3.0333 | 512.633 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 3670 |  |  | - |  | 12-15kV transformers | [8 empty] | AMP CODE: |  | 49
|  | DESCRIPTION : |  | F490Lightning strike that caused a failure on our switchyard transformer #7 that also
TC9 | 56 | U1 | 2022-06-18 21:56 |  |  |  |  | 2022-06-19 05:29 |  | 0 | 0 | 7.55 | 7.55 | 1200.45 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 3972 |  |  | - |  | DCS - hardware problems (including card failure) | [8 empty] | AMP CODE: |  | T1
|  | DESCRIPTION : |  | F340The unit tripped due to a DCS card failure that caused the fuel gas shutoff valve
TC9 | 58 | SF | 2022-06-19 11:39 |  |  |  |  | 2022-06-19 13:29 |  | 0 | 0 | 1.833 | 1.8333 | 291.5 | 1 |  |  |  | 0 |  |  | 160
|  | CAUSE CODE : |  | 5016 |  |  | - |  | High pressure compressor bleed valves | [8 empty] | AMP CODE: |  | 34
|  | DESCRIPTION : |  | F340The unit failed to start due to one of the compressor bleed valves became stuck in
TC9 | 143 | U1 | 2022-12-25 08:39 |  |  |  |  | 2022-12-25 11:47 |  | 0 | 0 | 3.133 | 3.1333 | 560.867 | 1 |  |  |  | 0 |  |  | 180
|  | CAUSE CODE : |  | 9130 |  |  | - |  | "Lack of fuel (water from rivers or lakes, coal mines, gas lines, etc) where the operator is not in control of contracts, supply lines, or delivery of fuels" | [8 empty] | AMP CODE: |  | T2
|  | DESCRIPTION : |  | FX00Unit manually shut down. Fuel gas supply pressure from transport company too low
TC9 | 4 | U1 | 2023-03-03 07:33 |  |  |  |  | 2023-03-03 07:41 |  | 0 | 0 | 0.133 | 0.1333 | 22.533 | 1 |  |  |  | 0 |  |  | 170
|  | CAUSE CODE : |  | 9020 |  |  | - |  | Lightning | [8 empty] | AMP CODE: |  | X0
|  | DESCRIPTION : |  | FX00Lightning strike caused a blown fuse on controls for 12" main supply fuel gass ven