## Three-Year EUOR (hidden)
[78 empty] | NINE-YEAR | SEVEN -YEAR | FIVE-YEAR | THREE-YEAR | ONE-YEAR
| Winter | Summer | Avg | Maintenance Outage Hours (FOH) | [9 empty] | Equivalent Maintenance Derate Hours (EMDH) | [9 empty] | Forced Outage Hours (FOH) | [9 empty] | Equivalent Forced Derate Hours (EFDH) | [9 empty] | Service Hours (SH) | [9 empty] | EUOR NUMERATOR | [7 empty] | EUOR DENOMINATOR | [7 empty] | ROLLING THREE YEAR EUOR | [7 empty] | AVERAGE | AVERAGE | AVERAGE | AVERAGE | AVERAGE
Unit | NDC | NDC | NDC | 2000 | 2001 | 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2000 | 2001 | 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2000 | 2001 | 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2000 | 2001 | 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2000 | 2001 | 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2000-02 | 2001-03 | 2002-04 | 2003-05 | 2004-06 | 2005-07 | 2006-08 | 2007-09 | 2000-02 | 2001-03 | 2002-04 | 2003-05 | 2004-06 | 2005-07 | 2006-08 | 2007-09 | 2000-02 | 2001-03 | 2002-04 | 2003-05 | 2004-06 | 2005-07 | 2006-08 | 2007-09 | 2000-08 | 2002-08 | 2004-08 | 2006-08 | 2008
GH 1 | 468 | 475 | 471.5 | 183.97 | 109.35 | 0 | 81.75 | 91.7 | 139.63 | 37.67 | 98.62 | 140.23 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 165 | 191 | 1051 | 233.2 | 222.4 | 88.1 | 387.3 | 177.1 | 282.7 |  | 5 | 13 | 17.3 | 74.8 | 9 | 280.6 | 281.2 | 370.6 | 265 |  | 6884 | 7957 | 7199 | 7840 | 7445.5 | 7985.8 | 7829.7 | 6738.8 | 8361.1 |  | 166896.855 | 147744.525 | 503703.45 | 183767.125 | 152341.65 | 239677.595 | 332959.155 | 304739.88 | 3410345.355 | 3893340.525 | 3889875 | 3845058.925 | 3658651.4 | 3872679.395 | 3892076.905 | 3307346.18 | 4.894% | 3.795% | 12.95% | 4.779% | 4.164% | 6.189% | 8.555% | 9.214% | 6.948% | 7.673% | 7.175% | 8.483% | #DIV/0!
GH 2 | 466 | 484 | 475 | 240.77 | 334.82 | 253.53 | 145.18 | 19.42 | 140.47 | 321.63 | 147.35 | 254.37 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 187 | 38 | 435 | 23.8 | 68.7 | 280.8 | 129.4 | 284.3 | 900.3 |  | 15 | 17 | 78 | 17.6 | 32.2 | 6.6 | 49.5 | 23.7 | 50 |  | 7263 | 7679 | 7533 | 8041.9 | 7965.6 | 7032.8 | 7677.1 | 7918.9 | 6766.7 |  | 210315.75 | 185164.5 | 364101.75 | 88625.5 | 57152 | 203238.25 | 237751.75 | 216291.25 | 3653115.75 | 3824614.5 | 3905226.75 | 3900168 | 3825517 | 3540683.25 | 3860861.75 | 3966511.25 | 5.757% | 4.841% | 9.323% | 2.272% | 1.494% | 5.74% | 6.158% | 5.453% | 6.235% | 6.5% | 6.787% | 8.855% | #DIV/0!
GH 3 | 482 | 480 | 481 | 0 | 254.55 | 117.05 | 353.48 | 177.03 | 76.8 | 34.2 | 369.48 | 572.37 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 124 | 119 | 138 | 233.7 | 99.8 | 126.7 | 52.3 | 741.3 | 162.6 |  | 8 | 20 | 27.3 | 49 | 22.5 | 14.6 | 45.8 | 228.7 | 518.1 |  | 8137 | 7882 | 8112 | 6246.5 | 7604.6 | 7968.7 | 8412.4 | 5769.4 | 8042.6 |  | 63492 | 189297.55 | 135810.35 | 306002.58 | 143977.73 | 104906.1 | 63636.3 | 644289.88 | 3973541 | 3970919.55 | 4024551.05 | 3287000.08 | 3790967.83 | 3930828.2 | 4087970.9 | 3309366.58 | 1.598% | 4.767% | 3.375% | 9.309% | 3.798% | 2.669% | 1.557% | 19.47% | 6.515% | 7.509% | 8.063% | 11.28% | #DIV/0!
GH 4 | 481 | 479 | 480 | 155.38 | 173.6 | 363.73 | 55.72 | 0 | 20.67 | 94.13 | 96.58 | 78.03 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 185 | 145 | 186 | 121.8 | 7.6 | 110.5 | 212.2 | 46.9 | 189.3 |  | 4 | 28 | 21.9 | 30.1 | 18.3 | 16.8 | 20.1 | 14.5 | 105.2 |  | 8413 | 8337 | 5922 | 7568.1 | 8131.1 | 8107.2 | 7860.2 | 8129.9 | 7105.3 |  | 165302.4 | 166368 | 274382.4 | 99657.6 | 12432 | 71025.6 | 156686.4 | 75830.4 | 4201622.4 | 4154688 | 3106430.4 | 3717897.6 | 3906576 | 3954417.6 | 3919934.4 | 3971222.4 | 3.934% | 4.004% | 8.833% | 2.68% | 0.3182% | 1.796% | 3.997% | 1.909% | 3.483% | 3.327% | 2.565% | 3.599% | #DIV/0!
GH Sta | 1897 | 1918 | 1907.5 | 580.12 | 872.32 | 734.31 | 636.13 | 288.15 | 377.57 | 487.63 | 712.03 | 1045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 661 | 493 | 1810 | 612.5 | 398.5 | 606.1 | 781.2 | 1249.6 | 1534.9 | 0 | 32 | 78 | 144.5 | 171.5 | 82 | 318.6 | 396.6 | 637.5 | 938.3 | 0 | 30697 | 31855 | 28766 | 29696.5 | 31146.8 | 31094.5 | 31779.4 | 28557 | 30275.7 | 0 | 606007.005 | 688574.575 | 1277997.95 | 678052.805 | 365903.38 | 618847.545 | 791033.605 | 1241151.41 | 15238624.505 | 15843562.575 | 14926083.2 | 14750124.605 | 15181712.23 | 15298608.445 | 15760843.955 | 14554446.41 | 3.977% | 4.346% | 8.562% | 4.597% | 2.41% | 4.045% | 5.019% | 8.528% | 5.796% | 6.273% | 6.146% | 8.072% | #DIV/0!
EUOR (3-Yr Peer Top Qtr) | [69 empty] | 5.18% | 5.26% | 5.78% | 6.39% | 6.14% | 7.18%
EUOR (3-Yr Peer Avg) | [69 empty] | 8.67% | 8.83% | 9.42% | 10.03% | 10.43% | 11.51%
BR 1 | 102 | 101 | 101.5 | 75.42 | 105.63 | 0 | 71.53 | 52.52 | 96.77 | 74.6 | 16.72 | 242.38 |  | 0 | 0 | 0 | 0 | 0 | 2.17 | 0 | 5.08 | 3 |  | 388 | 94 | 23 | 14.3 | 106.9 | 236.8 | 44.8 | 282 | 297 |  | 68 | 277 | 268.8 | 159.7 | 199.3 | 22 | 122.5 | 100.4 | 987.1 |  | 7984 | 8077 | 8128 | 7970.8 | 7931 | 7897.6 | 7009.6 | 6822.1 | 7534 |  | 53939.13 | 48377.945 | 29617.7 | 24921.295 | 36410.08 | 36310.61 | 24552.85 | 41026.3 | 857413.13 | 840077.945 | 827326.5 | 817747.945 | 821177.63 | 835463.755 | 723593.5 | 722763.23 | 6.291% | 5.759% | 3.58% | 3.048% | 4.434% | 4.346% | 3.393% | 5.676% | 6.2% | 6.252% | 7.484% | 9.746% | #DIV/0!
BR 2 | 169 | 167 | 168 | 148.23 | 90.97 | 116.27 | 49.28 | 102.25 | 35.83 | 24.3 | 44.87 | 195.6 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 |  | 436 | 1694 | 633 | 279.9 | 206 | 124.5 | 51.3 | 33.1 | 281.5 |  | 34 | 50 | 170.8 | 26.8 | 11.5 | 75 | 43 | 127.8 | 19.1 |  | 7130 | 6426 | 6969 | 7510.5 | 7725.5 | 7784 | 8117 | 8210 | 8306.9 |  | 103862.64 | 308274.96 | 154571.76 | 59804.64 | 53718 | 39535.44 | 19924.8 | 34569.36 | 1295990.64 | 1379442.96 | 1296669.36 | 1317066.24 | 1349670 | 1334647.44 | 1376356.8 | 1392378.96 | 8.014% | 22.35% | 11.92% | 4.541% | 3.98% | 2.962% | 1.448% | 2.483% | 7.044% | 4.7% | 3.379% | 3.319% | #DIV/0!
BR 3 | 433 | 429 | 431 | 64.35 | 124.05 | 151.38 | 52.77 | 116.58 | 96.93 | 218.02 | 82.55 | 76.08 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.75 | 0 |  | 4 | 106 | 1504 | 290.1 | 77.2 | 2238.2 | 560.8 | 82.2 | 246.8 |  | 21 | 65 | 25.8 | 22.8 | 9.5 | 37.9 | 43.8 | 142.2 | 273.4 |  | 8265 | 7519 | 7105 | 7625.5 | 7040.3 | 4809.6 | 7411.6 | 7616.1 | 7994.5 |  | 38509.85 | 127166.55 | 724588.58 | 157603.77 | 87613.68 | 1022775.93 | 354549.22 | 135204.7 | 3591673.85 | 3339840.55 | 3775723.78 | 3434367.47 | 3117888.48 | 3079378.63 | 3530071.02 | 3353546.35 | 1.072% | 3.808% | 19.19% | 4.589% | 2.81% | 33.21% | 10.04% | 4.032% | 9.43% | 11.47% | 11.14% | 7.133% | #DIV/0!
BR Sta | 704 | 697 | 700.5 | 288 | 320.65 | 267.65 | 173.58 | 271.35 | 229.53 | 316.92 | 144.14 | 514.06 | 0 | 0 | 0 | 0 | 0 | 0 | 2.17 | 0 | 11.83 | 21 | 0 | 828 | 1894 | 2160 | 584.3 | 390.1 | 2599.5 | 656.9 | 397.3 | 825.3 | 0 | 123 | 392 | 465.4 | 209.3 | 220.3 | 134.9 | 209.3 | 370.4 | 1279.6 | 0 | 23379 | 22022 | 22202 | 23106.8 | 22696.8 | 20491.2 | 22538.2 | 22648.2 | 23835.4 | 0 | 196311.62 | 483819.455 | 908778.04 | 242329.705 | 177741.76 | 1098621.98 | 399026.87 | 210800.36 | 5745077.62 | 5559361.455 | 5899719.64 | 5569181.655 | 5288736.11 | 5249489.825 | 5630021.32 | 5468688.54 | 3.417% | 8.703% | 15.4% | 4.351% | 3.361% | 20.93% | 7.087% | 3.855% | 7.554% | 7.456% | 7.249% | 6.604% | #DIV/0!
EUOR (3-Yr Peer Top Qtr) | [69 empty] | 5.099% | 5.218% | 5.822% | 6.621% | 6.117% | 6.872%
EUOR (3-Yr Peer Avg) | [69 empty] | 8.632% | 8.984% | 9.755% | 11.08% | 11.06% | 12.02%
GR 3 | 71 | 68 | 69.5 | 94.43 | 250.12 | 149.47 | 13.88 | 169.02 | 120.9 | 0 | 59.98 | 93.45 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 138.08 | 1.17 |  | 73 | 147 | 218.9 | 2093.2 | 309.2 | 392.2 | 295 | 234.9 | 407.1 |  | 4 | 0 | 638.5 | 89.3 | 79.7 | 223.8 | 93.1 | 69.1 | 107.4 |  | 7165 | 6797 | 4133 | 5273.3 | 6758.6 | 6938.4 | 4532.9 | 8117.3 | 6984.7 |  | 11914.385 | 27599.84 | 69977.465 | 152648.41 | 38775.44 | 51214.55 | 26972.95 | 34893.17 | 509603.885 | 499991.34 | 312845.215 | 512936.41 | 502958.99 | 517879.25 | 335539.05 | 584646.51 | 2.338% | 5.52% | 22.37% | 29.76% | 7.709% | 9.889% | 8.039% | 5.968% | 10.62% | 12.68% | 7.89% | 7.234% | #DIV/0!
GR 4 | 102 | 95 | 98.5 | 323.05 | 243.37 | 225.9 | 214.22 | 156.9 | 93.92 | 170.13 | 24.25 | 59.78 |  | 0 | 0 | 235.02 | 0 | 0 | 0 | 0 | 27.92 | 0 |  | 517 | 98 | 851 | 1592.5 | 356 | 3678 | 73.5 | 362.1 | 372.6 |  | 5 | 0 | 456.1 | 332.6 | 113.6 | 98.1 | 160.4 | 14.8 | 201.9 |  | 7281 | 7055 | 6657 | 4670.6 | 6625.5 | 4654.9 | 6526.4 | 7545.7 | 7766.5 |  | 83237.425 | 33624.945 | 174149.97 | 210723.02 | 61710.25 | 381196.97 | 39796.955 | 42263.395 | 799923.425 | 728542.445 | 761789.15 | 638016.02 | 703132.4 | 830041.77 | 666847.955 | 781306.925 | 10.41% | 4.615% | 22.86% | 33.03% | 8.776% | 45.93% | 5.968% | 5.409% | 16.21% | 18.74% | 15.5% | 6.408% | #DIV/0!
GR Sta | 173 | 163 | 168 | 417.48 | 493.49 | 375.37 | 228.1 | 325.92 | 214.82 | 170.13 | 84.23 | 153.23 | 0 | 0 | 0 | 235.02 | 0 | 0 | 0 | 0 | 166 | 1.17 | 0 | 590 | 245 | 1069.9 | 3685.7 | 665.2 | 4070.2 | 368.5 | 597 | 779.7 | 0 | 9 | 0 | 1094.6 | 421.9 | 193.3 | 321.9 | 253.5 | 83.9 | 309.3 | 0 | 14446 | 13852 | 10790 | 9943.9 | 13384.1 | 11593.3 | 11059.3 | 15663 | 14751.2 | 0 | 95151.81 | 61224.785 | 244127.435 | 363371.43 | 100485.69 | 432411.52 | 66769.905 | 77156.565 | 1309527.31 | 1228533.785 | 1074634.365 | 1150952.43 | 1206091.39 | 1347921.02 | 1002387.005 | 1365953.435 | 7.266% | 4.984% | 22.72% | 31.57% | 8.332% | 32.08% | 6.661% | 5.649% | 13.55% | 15.87% | 11.85% | 6.8% | #DIV/0!
EUOR (3-Yr Peer Top Qtr) | [69 empty] | 4.97% | 5.15% | 5.89% | 6.99% | 6.08% | 6.38%
EUOR (3-Yr Peer Avg) | [69 empty] | 8.57% | 9.23% | 10.29% | 12.75% | 12.07% | 12.84%
TY 3 | 73 | 71 | 72 | 7.15 | 0 | 6.38 | 45.45 | 559.83 | 13.8 | 1.67 | 108.1 | 48.65 |  | 0 | 0 | 0 | 141.5 | 2.08 | 219.25 | 0 | 0 | 0 |  | 9 | 556 | 1881 | 85.2 | 327.5 | 134.6 | 120.8 | 204.9 | 417.4 |  | 74 | 203 | 716.3 | 405.5 | 178.5 | 155.3 | 97.1 | 82.9 | 218.1 |  | 5956 | 5831 | 5586 | 5418.3 | 4933.7 | 7037.5 | 5216.1 | 7221.6 | 6448.7 |  | 6490.8 | 54648 | 187464.96 | 48790.8 | 76889.52 | 37652.4 | 15809.04 | 28504.8 | 429994.8 | 459864 | 538083.36 | 399524.4 | 419114.16 | 517384.8 | 384377.04 | 542491.2 | 1.51% | 11.88% | 34.84% | 12.21% | 18.35% | 7.277% | 4.113% | 5.254% | 12.07% | 13.47% | 8.814% | 6.568% | #DIV/0!
TY Sta | 73 | 71 | 72 | 7.15 | 0 | 6.38 | 45.45 | 559.83 | 13.8 | 1.67 | 108.1 | 48.65 | 0 | 0 | 0 | 0 | 141.5 | 2.08 | 219.25 | 0 | 0 | 0 | 0 | 9 | 556 | 1881 | 85.2 | 327.5 | 134.6 | 120.8 | 204.9 | 417.4 | 0 | 74 | 203 | 716.3 | 405.5 | 178.5 | 155.3 | 97.1 | 82.9 | 218.1 | 0 | 5956 | 5831 | 5586 | 5418.3 | 4933.7 | 7037.5 | 5216.1 | 7221.6 | 6448.7 | 0 | 6490.8 | 54648 | 187464.96 | 48790.8 | 76889.52 | 37652.4 | 15809.04 | 28504.8 | 429994.8 | 459864 | 538083.36 | 399524.4 | 419114.16 | 517384.8 | 384377.04 | 542491.2 | 1.51% | 11.88% | 34.84% | 12.21% | 18.35% | 7.277% | 4.113% | 5.254% | 12.07% | 13.47% | 8.814% | 6.568% | #DIV/0!
EUOR (3-Yr Peer Top Qtr) | [69 empty] | 4.97% | 5.15% | 5.89% | 6.99% | 6.08% | 6.38%
EUOR (3-Yr Peer Avg) | [69 empty] | 8.57% | 9.23% | 10.29% | 12.75% | 12.07% | 12.84%
CR 4 | 155 | 155 | 155 | 270.18 | 489.73 | 189.97 | 229.77 | 327.73 | 116.05 | 486.7 | 64.05 | 90.7 |  | 0 | 0 | 0 | 0 | 0 | 0 | 158.1 | 137.9 | 126.08 |  | 58 | 87 | 40.3 | 138.8 | 323 | 508.3 | 197.1 | 188.3 | 321.1 |  | 147 | 169 | 56 | 31.7 | 95.9 | 107.4 | 80.6 | 44 | 6.6 |  | 7877 | 7460 | 8082 | 7732.6 | 6807.5 | 7905.4 | 7575.2 | 8268.4 | 7865 |  | 73652.9 | 115588.15 | 44371.85 | 62041.85 | 115727.65 | 113421.25 | 142987.5 | 67308.75 | 1271802.9 | 1245693.15 | 1288401.85 | 1255681.35 | 1156025.65 | 1322111.25 | 1280145 | 1320716.25 | 5.791% | 9.279% | 3.444% | 4.941% | 10.01% | 8.579% | 11.17% | 5.096% | 7.174% | 7.077% | 8.234% | 7.588% | #DIV/0!
CR 5 | 168 | 168 | 168 | 588.58 | 132.93 | 480.3 | 525.19 | 181.43 | 155.25 | 95.88 | 116.53 | 74.67 |  | 0 | 0 | 0 | 0 | 7 | 0 | 52.58 | 39.37 | 91.22 |  | 472 | 173 | 717.6 | 23.5 | 291.6 | 197 | 329.8 | 552.5 | 1063.7 |  | 93 | 168 | 281.7 | 326.4 | 272.3 | 61.2 | 39.8 | 131.4 | 11.5 |  | 6749 | 6982 | 7592.7 | 7407 | 6824.8 | 7841.2 | 8001.9 | 7555.6 | 6371.8 |  | 193801.44 | 79620.24 | 248572.8 | 147015.12 | 126391.44 | 69459.6 | 87034.08 | 141086.4 | 1312009.44 | 1224372.24 | 1476820.8 | 1336555.92 | 1226035.44 | 1376499.6 | 1415833.44 | 1381737.84 | 14.77% | 6.503% | 16.83% | 11% | 10.31% | 5.046% | 6.147% | 10.21% | 10.84% | 10.85% | 9.494% | 10.76% | #DIV/0!
CR 6 | 240 | 240 | 240 | 380.53 | 400.85 | 374.08 | 221.18 | 404.33 | 222.17 | 257.4 | 186.8 | 306.43 |  | 0 | 0 | 0 | 0 | 0 | 209.78 | 665.73 | 151.13 | 289.85 |  | 271 | 449 | 3138.7 | 230.6 | 280 | 412.7 | 187.8 | 944.7 | 815.9 |  | 44 | 158 | 81.1 | 94.6 | 42.9 | 171.5 | 100.5 | 75.9 | 226.7 |  | 7250 | 7188 | 5134.3 | 7721.5 | 7873.8 | 7434.5 | 7778.8 | 6806.6 | 7493.2 |  | 166927.2 | 241884 | 862531.2 | 131131.2 | 174535.2 | 243876 | 290743.2 | 326047.2 | 1896367.2 | 1929084 | 2075299.2 | 1961587.2 | 2053951.2 | 1936648.8 | 1973760 | 1905144 | 8.802% | 12.54% | 41.56% | 6.685% | 8.498% | 12.59% | 14.73% | 17.11% | 15.9% | 17.33% | 14.38% | 16.99% | #DIV/0!
CR Sta | 563 | 563 | 563 | 1239.29 | 1023.51 | 1044.35 | 976.14 | 913.49 | 493.47 | 839.98 | 367.38 | 471.8 | 0 | 0 | 0 | 0 | 0 | 7 | 209.78 | 876.41 | 328.4 | 507.15 | 0 | 801 | 709 | 3896.6 | 392.9 | 894.6 | 1118 | 714.7 | 1685.5 | 2200.7 | 0 | 284 | 495 | 418.8 | 452.7 | 411.1 | 340.1 | 220.9 | 251.3 | 244.8 | 0 | 21876 | 21630 | 20809 | 22861.1 | 21506.1 | 23181.1 | 23355.9 | 22630.6 | 21730 | 0 | 434381.54 | 437092.39 | 1155475.85 | 340188.17 | 416654.29 | 426756.85 | 520764.78 | 534442.35 | 4480179.54 | 4399149.39 | 4840521.85 | 4553824.47 | 4436012.29 | 4635259.65 | 4669738.44 | 4607598.09 | 9.696% | 9.936% | 23.87% | 7.47% | 9.393% | 9.207% | 11.15% | 11.6% | 11.32% | 11.78% | 10.73% | 11.77% | #DIV/0!
EUOR (3-Yr Peer Top Qtr) | [69 empty] | 5.06% | 5.197% | 5.843% | 6.734% | 6.106% | 6.721%
EUOR (3-Yr Peer Avg) | [69 empty] | 8.613% | 9.059% | 9.919% | 11.59% | 11.37% | 12.27%
MC 1 | 303 | 303 | 303 | 219.73 | 344.1 | 206 | 258.77 | 300.55 | 54.58 | 202.65 | 175.78 | 65.23 |  | 0 | 0 | 0 | 0 | 0 | 0 | 187.53 | 0 | 0 |  | 209 | 773 | 696.9 | 77.2 | 235.9 | 258.6 | 414.4 | 239.9 | 418.5 |  | 69 | 184 | 52.1 | 101.7 | 196.4 | 57.7 | 42.9 | 68.9 | 60.3 |  | 7484 | 7280 | 7111.9 | 7778.1 | 7529 | 8372.9 | 7555.8 | 8142.8 | 7609.4 |  | 150812.19 | 394233.3 | 289365 | 132614.01 | 222053.55 | 112376.64 | 256786.44 | 146827.74 | 2397557.19 | 2544321.3 | 2428484.4 | 2458563.21 | 2443831.35 | 2631882.24 | 2476373.55 | 2593219.44 | 6.29% | 15.49% | 11.92% | 5.394% | 9.086% | 4.27% | 10.37% | 5.662% | 8.338% | 7.577% | 7.167% | 7.557% | #DIV/0!
MC 2 | 299 | 301 | 300 | 377.38 | 221.07 | 309.78 | 229.35 | 98.23 | 387.72 | 248.57 | 200.38 | 192.53 |  | 119.47 | 0 | 0 | 0 | 0 | 0 | 0 | 45.3 | 0 |  | 376 | 266 | 760.1 | 326.5 | 313.3 | 337.5 | 210.6 | 167.4 | 326.7 |  | 297 | 110 | 19.9 | 110.8 | 46.9 | 181.8 | 246.3 | 137.1 | 62.3 |  | 8030 | 7219 | 7671.2 | 6882.6 | 8136 | 7281.3 | 8134.1 | 7657.5 | 8159.1 |  | 350955 | 179121 | 326934 | 199995 | 137529 | 272106 | 211641 | 165054 | 2635014 | 2311821 | 2622324 | 2231535 | 2564259 | 2401956 | 2577981 | 2407584 | 13.32% | 7.748% | 12.47% | 8.962% | 5.363% | 11.33% | 8.21% | 6.856% | 9.026% | 8.546% | 7.652% | 7.262% | #DIV/0!
MC 3 | 397 | 391 | 394 | 212.4 | 353.3 | 191.28 | 594.55 | 153.4 | 228.38 | 195.22 | 57.98 | 132.07 |  | 0 | 0 | 0 | 0 | 0 | 0 | 152.64 | 0 | 7.5 |  | 26 | 390 | 514.8 | 277.7 | 176.7 | 468.3 | 449.9 | 271.7 | 232.9 |  | 145 | 219 | 88.5 | 106.2 | 67.3 | 39.4 | 38.9 | 22.6 | 23.2 |  | 7447 | 7931 | 7021.9 | 7887.7 | 6477.3 | 8063.3 | 7750.1 | 7631 | 8194.4 |  | 151059.6 | 379146.2 | 313064.52 | 385509.3 | 156575.6 | 290015.52 | 329644.04 | 138798.32 | 3028047.6 | 3417674.2 | 3044824.12 | 3451420.3 | 2682115.6 | 3451432.12 | 3307716.68 | 3136507.92 | 4.989% | 11.09% | 10.28% | 11.17% | 5.838% | 8.403% | 9.966% | 4.425% | 7.96% | 7.883% | 6.714% | 6.36% | #DIV/0!
MC 4 | 492 | 477 | 484.5 | 100.38 | 277.92 | 375.58 | 360.25 | 344.78 | 113.37 | 189.37 | 190.68 | 168 |  | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 272.12 | 166.65 |  | 735 | 770 | 971.6 | 477.1 | 252.3 | 1421.6 | 363.9 | 261.7 | 391.9 |  | 174 | 212 | 94.8 | 228.3 | 48.6 | 60.5 | 28.5 | 103.8 | 102 |  | 7189 | 6281 | 7169.5 | 7152.1 | 7978.1 | 7003.8 | 6711.2 | 8098.1 | 7586.1 |  | 489044.61 | 610431.24 | 698639.31 | 516307.425 | 312831.96 | 773005.215 | 287197.065 | 401311.35 | 3887812.11 | 3550861.74 | 4126331.46 | 3870888.525 | 4154674.71 | 4137034.065 | 3519635.715 | 4142707.56 | 12.58% | 17.19% | 16.93% | 13.34% | 7.53% | 18.69% | 8.16% | 9.687% | 12.71% | 12.15% | 10.93% | 9.389% | #DIV/0!
MC Sta | 1491 | 1472 | 1481.5 | 909.89 | 1196.39 | 1082.64 | 1442.92 | 896.96 | 784.05 | 835.81 | 624.82 | 557.83 | 0 | 119.47 | 0 | 0 | 0 | 0 | 0 | 351.17 | 317.42 | 174.15 | 0 | 1346 | 2199 | 2943.4 | 1158.5 | 978.2 | 2486 | 1438.8 | 940.7 | 1370 | 0 | 685 | 725 | 255.3 | 547 | 359.2 | 339.4 | 356.6 | 332.4 | 247.8 | 0 | 30150 | 28711 | 28974.5 | 29700.5 | 30120.4 | 30721.3 | 30151.2 | 31529.4 | 31549 | 0 | 1141871.4 | 1562931.74 | 1628002.83 | 1234425.735 | 828990.11 | 1447503.375 | 1085268.545 | 851991.41 | 11948430.9 | 11824678.24 | 12221963.98 | 12012407.035 | 11844880.66 | 12622304.425 | 11881706.945 | 12280018.92 | 9.557% | 13.22% | 13.32% | 10.28% | 6.999% | 11.47% | 9.134% | 6.938% | 9.499% | 9.041% | 8.117% | 7.624% | #DIV/0!
EUOR (3-Yr Peer Top Qtr) | [69 empty] | 5.18% | 5.26% | 5.78% | 6.39% | 6.14% | 7.18%
EUOR (3-Yr Peer Avg) | [69 empty] | 8.67% | 8.83% | 9.42% | 10.03% | 10.43% | 11.51%
TC 1 | 514.6667 | 510.6667 | 512.6667 | 333.15 | 0 | 437.78 | 108.55 | 90.67 | 95.72 | 207.47 | 256.15 | 189.05 |  | 0 | 1.75 | 0 | 1 | 0 | 0 | 0 | 0 | 22.43 |  | 222 | 203 | 439 | 231.7 | 39.2 | 228.1 | 152.2 | 297.4 | 180.7 |  | 18 | 10 | 10.3 | 28.7 | 7.4 | 14.4 | 9.9 | 8.4 | 47.4 |  | 7483 | 7108 | 7883.2 | 7626.2 | 8654.2 | 7731.9 | 8400.3 | 7343.2 | 8414.2 |  | 293834.9 | 110095.1667 | 454776.3467 | 189661.0333 | 70373.7533 | 173394.12 | 189466.22 | 288093.0333 | 4120891.5667 | 3748106 | 4490949.7467 | 4084133.3667 | 4503299.8867 | 4129899.12 | 4490944.62 | 4048400.5 | 7.13% | 2.937% | 10.13% | 4.644% | 1.563% | 4.199% | 4.219% | 7.116% | 5.234% | 5.26% | 4.367% | 5.389% | #DIV/0!
TC Sta | 514.6667 | 510.6667 | 512.6667 | 333.15 | 0 | 437.78 | 108.55 | 90.67 | 95.72 | 207.47 | 256.15 | 189.05 | 0 | 0 | 1.75 | 0 | 1 | 0 | 0 | 0 | 0 | 22.43 | 0 | 222 | 203 | 439 | 231.7 | 39.2 | 228.1 | 152.2 | 297.4 | 180.7 | 0 | 18 | 10 | 10.3 | 28.7 | 7.4 | 14.4 | 9.9 | 8.4 | 47.4 | 0 | 7483 | 7108 | 7883.2 | 7626.2 | 8654.2 | 7731.9 | 8400.3 | 7343.2 | 8414.2 | 0 | 293834.9 | 110095.1667 | 454776.3467 | 189661.0333 | 70373.7533 | 173394.12 | 189466.22 | 288093.0333 | 4120891.5667 | 3748106 | 4490949.7467 | 4084133.3667 | 4503299.8867 | 4129899.12 | 4490944.62 | 4048400.5 | 7.13% | 2.937% | 10.13% | 4.644% | 1.563% | 4.199% | 4.219% | 7.116% | 5.234% | 5.26% | 4.367% | 5.389% | #DIV/0!
EUOR (3-Yr Peer Top Qtr) | [69 empty] | 5.51% | 5.42% | 4.88% | 5.58% | 5.4% | 5.61%
EUOR (3-Yr Peer Avg) | [69 empty] | 8.26% | 8.33% | 8.71% | 9.37% | 9.17% | 8.9%
EON-US | 5415.6667 | 5394.6667 | 5405.1667 | 3775.08 | 3906.36 | 3948.48 | 3610.87 | 3346.37 | 2208.96 | 2859.61 | 2296.85 | 2979.62 | 0 | 119.47 | 1.75 | 235.02 | 142.5 | 9.08 | 431.2 | 1227.58 | 823.65 | 725.9 | 0 | 4457 | 6299 | 14199.9 | 6750.8 | 3693.3 | 11242.5 | 4233.1 | 5372.4 | 7308.7 | 0 | 1225 | 1903 | 3105.2 | 2236.6 | 1451.8 | 1624.6 | 1543.9 | 1766.8 | 3285.3 | 0 | 133987 | 131009 | 125010.7 | 128353.3 | 132442.1 | 131850.8 | 132500.4 | 135593 | 137004.2 | 0 | 2774049.075 | 3398386.1117 | 5856623.4117 | 3096819.6783 | 2037038.5033 | 4235187.79 | 3068138.965 | 3232139.9283 | 43272726.2417 | 43063255.445 | 43991956.1417 | 42520147.9617 | 42879846.7267 | 43800867.285 | 43820019.325 | 42867597.095 | 6.411% | 7.892% | 13.31% | 7.283% | 4.751% | 9.669% | 7.002% | 7.54% | 8.932% | 9.296% | 8.173% | 8.003% | #DIV/0!
EUOR (3-Yr Peer Top Qtr) | [69 empty] | 5.179% | 5.258% | 5.712% | 6.406% | 6.061% | 6.908%
EUOR (3-Yr Peer Avg) | [69 empty] | 8.616% | 8.844% | 9.487% | 10.39% | 10.56% | 11.47%

## Baseload MOR Detail
[15 empty] | 10 yrs (2012-2021) |  |  |  | 7 yrs (2015-2021) |  |  |  | 5 yrs (2017-2021)
[5 empty] | MOR% | [10 empty] | 0.1 | 0.5 | 0.9 |  | 0.1 | 0.5 | 0.9 |  | 0.1 | 0.5 | 0.9
Unit/Station | Winter Capacity | Spring/Fall Capacity | Summer Capacity | Average Capacity | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | Avg | 10th %ile | 50th %ile | 90th %ile | Avg | 10th %ile | 50th %ile | 90th %ile | Avg | 10th %ile | 50th %ile | 90th %ile
BR 3 | 416 | 414 | 412 | 414 | 5.622% | 4.252% | 12.94% | 1.793% | 10.44% | 3.481% | 5.224% | 2.489% | 1.791% | 10.23% | 5.826% | 1.793% | 4.738% | 10.69% | 5.063% | 1.792% | 3.481% | 10.31% | 4.642% | 2.07% | 3.481% | 8.226%
GH 1 | 479 | 477 | 475 | 477 | 3.477% | 0.7576% | 4.251% | 3.075% | 0.669% | 2.977% | 1.019% | 1.374% | 2.469% | 1.439% | 2.151% | 0.7487% | 1.954% | 3.554% | 1.86% | 0.8793% | 1.439% | 3.016% | 1.856% | 1.161% | 1.439% | 2.774%
GH 2 | 486 | 485.5 | 485 | 485.5 | 0.8085% | 1.817% | 2.465% | 0.2366% | 1.204% | 1.463% | 0.3815% | 1.449% | 1.363% | 0.8433% | 1.203% | 0.367% | 1.283% | 1.882% | 0.9915% | 0.3235% | 1.204% | 1.455% | 1.1% | 0.5662% | 1.363% | 1.458%
GH 3 | 476 | 478.5 | 481 | 478.5 | 1.803% | 5.073% | 6.373% | 4.17% | 5.426% | 0.2945% | 1.501% | 0.6173% | 4.674% | 0.02151% | 2.995% | 0.2672% | 2.986% | 5.521% | 2.386% | 0.1853% | 1.501% | 4.975% | 1.422% | 0.1307% | 0.6173% | 3.405%
GH 4 | 478 | 478 | 478 | 478 | 4.174% | 6.501% | 7.756% | 3.334% | 1.607% | 0.0003846% | 0.6328% | 1.017% | 2.467% | 3.276% | 3.076% | 0.5696% | 2.872% | 6.626% | 1.762% | 0.3798% | 1.607% | 3.299% | 1.479% | 0.2534% | 1.017% | 2.952%
MC 1 | 300 | 300 | 300 | 300 | 2.157% | 4.965% | 8.142% | 5.066% | 3.933% | 2.941% | 3.618% | 2.357% | 3.255% | 9.014% | 4.545% | 2.337% | 3.776% | 8.229% | 4.312% | 2.707% | 3.618% | 6.645% | 4.237% | 2.59% | 3.255% | 6.856%
MC 2 | 297 | 297 | 297 | 297 | 2.242% | 4.922% | 11.82% | 4.972% | 1.435% | 1.311% | 4.425% | 2.397% | 13.39% | 6.965% | 5.389% | 1.423% | 4.673% | 11.98% | 4.986% | 1.386% | 4.425% | 9.537% | 5.698% | 1.745% | 4.425% | 10.82%
MC 3 | 394 | 392.5 | 391 | 392.5 | 2.459% | 3.126% | 5.061% | 8.086% | 3.229% | 1.38% | 2.077% | 7.091% | 8.601% | 2.126% | 4.324% | 2.008% | 3.177% | 8.137% | 4.656% | 1.798% | 3.229% | 8.292% | 4.255% | 1.659% | 2.126% | 7.997%
MC 4 | 486 | 481.5 | 477 | 481.5 | 4.104% | 6.278% | 13.42% | 6.082% | 0.02738% | 1.655% | 5.365% | 1.153% | 4.115% | 1.583% | 4.378% | 1.041% | 4.11% | 6.992% | 2.854% | 0.7029% | 1.655% | 5.652% | 2.774% | 1.325% | 1.655% | 4.865%
TC 1@75% | 369.75 | 369.75 | 369.75 | 369.75 | 4.776% | 3.951% | 6.759% | 2.775% | 0.2044% | 1.905% | 2.942% | 4.448% | 0.8799% | 5.168% | 3.381% | 0.8123% | 3.446% | 5.328% | 2.617% | 0.6097% | 2.775% | 4.736% | 3.069% | 1.29% | 2.942% | 4.88%
TC 2@75% | 570 | 559.5 | 549 | 559.5 | 4.31% | 3.908% | 14.16% | 1.026% | 7.292% | 2.981% | 7.72% | 3.5% | 4.211% | 2.432% | 5.154% | 2.292% | 4.059% | 8.363% | 4.166% | 1.87% | 3.5% | 7.463% | 4.169% | 2.652% | 3.5% | 6.316%
GH+MC+TC1 | 3765.75 | 3759.75 | 3753.75 | 3759.75 | 2.907% | 4.107% | 7.15% | 4.068% | 1.923% | 1.486% | 2.282% | 2.272% | 4.227% | 2.913% | 3.333% | 1.879% | 2.91% | 4.519% | 2.739% | 1.748% | 2.282% | 4.132% | 2.636% | 1.8% | 2.282% | 3.701%
CR7 | [7 empty] | 4.369% | 4.363% | 25.17% | 5.92% | 3.06% | 2.775% | 2.607% | 6.894% | 2.708% | 4.363% | 13.62% | 6.894% | 2.708% | 4.363% | 13.62% | 7.906% | 2.674% | 3.06% | 17.47%
Note on B3: Unit ratings as of 12/7/2021

## Baseload EFOR Detail
[15 empty] | 10 yrs (2012-2021) |  |  |  | 7 yrs (2015-2021) |  |  |  | 5 yrs (2017-2021)
[5 empty] | EFOR% | [10 empty] | 0.1 | 0.5 | 0.9 |  | 0.1 | 0.5 | 0.9 |  | 0.1 | 0.5 | 0.9
Unit/Station | Winter Capacity | Spring/Fall Capacity | Summer Capacity | Average Capacity | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | Avg | 10th %ile | 50th %ile | 90th %ile | Avg | 10th %ile | 50th %ile | 90th %ile | Avg | 10th %ile | 50th %ile | 90th %ile
BR 3 | 416 | 414 | 412 | 414 | 3.694% | 14.33% | 8.05% | 3.49% | 9.73% | 3.131% | 12.49% | 6.368% | 3.246% | 3.16% | 6.769% | 3.157% | 5.031% | 12.67% | 5.944% | 3.149% | 3.49% | 10.83% | 5.678% | 3.143% | 3.246% | 10.04%
GH 1 | 479 | 477 | 475 | 477 | 9.539% | 5.117% | 2.37% | 5.91% | 3.951% | 3.089% | 1.537% | 1.564% | 1.196% | 2.411% | 3.668% | 1.503% | 2.75% | 6.273% | 2.808% | 1.401% | 2.411% | 4.734% | 1.959% | 1.333% | 1.564% | 2.818%
GH 2 | 486 | 485.5 | 485 | 485.5 | 2.863% | 1.7% | 0.72% | 2.4% | 1.09% | 1.014% | 1.903% | 0.6805% | 0.6101% | 0.3021% | 1.328% | 0.5793% | 1.052% | 2.446% | 1.143% | 0.4869% | 1.014% | 2.102% | 0.902% | 0.4253% | 0.6805% | 1.547%
GH 3 | 476 | 478.5 | 481 | 478.5 | 2.36% | 3.566% | 1.9% | 3.63% | 4.186% | 2.65% | 4.863% | 0.8724% | 1.125% | 0.9838% | 2.614% | 0.9726% | 2.505% | 4.254% | 2.616% | 0.9392% | 2.65% | 4.457% | 2.099% | 0.9169% | 1.125% | 3.978%
GH 4 | 478 | 478 | 478 | 478 | 1.977% | 6.021% | 2.93% | 2.07% | 4.075% | 3.49% | 1.108% | 0.1022% | 1.974% | 0.5368% | 2.428% | 0.4933% | 2.023% | 4.27% | 1.908% | 0.363% | 1.974% | 3.724% | 1.442% | 0.2761% | 1.108% | 2.883%
MC 1 | 300 | 300 | 300 | 300 | 5.341% | 3.773% | 2.47% | 4.12% | 1.676% | 2.094% | 1.162% | 2.926% | 1.192% | 2.563% | 2.732% | 1.189% | 2.517% | 4.242% | 2.248% | 1.18% | 2.094% | 3.404% | 1.988% | 1.174% | 2.094% | 2.781%
MC 2 | 297 | 297 | 297 | 297 | 7.088% | 6.303% | 6.39% | 4.28% | 1.572% | 2.364% | 2.294% | 1.803% | 0.4486% | 4.181% | 3.672% | 1.46% | 3.273% | 6.46% | 2.42% | 1.123% | 2.294% | 4.221% | 2.218% | 0.9902% | 2.294% | 3.454%
MC 3 | 394 | 392.5 | 391 | 392.5 | 2.706% | 14.32% | 3.22% | 2.79% | 5.78% | 0.6706% | 1.21% | 3.887% | 1.188% | 1.029% | 3.68% | 0.993% | 2.748% | 6.634% | 2.365% | 0.8855% | 1.21% | 4.645% | 1.597% | 0.8139% | 1.188% | 2.816%
MC 4 | 486 | 481.5 | 477 | 481.5 | 21.24% | 10.49% | 10.01% | 1.33% | 2.686% | 2.481% | 2.412% | 0.7467% | 1.687% | 2.846% | 5.594% | 1.272% | 2.583% | 11.57% | 2.027% | 1.097% | 2.412% | 2.75% | 2.035% | 1.123% | 2.412% | 2.7%
TC 1@75% | 369.75 | 369.75 | 369.75 | 369.75 | 3.676% | 2.653% | 4.02% | 4.03% | 2.379% | 3.411% | 1.884% | 3.34% | 1.256% | 2.591% | 2.924% | 1.821% | 2.996% | 4.021% | 2.699% | 1.633% | 2.591% | 3.659% | 2.497% | 1.507% | 2.591% | 3.383%
TC 2@75% | 570 | 559.5 | 549 | 559.5 | 17.7% | 15.57% | 12.66% | 7.62% | 22.95% | 10.97% | 2.729% | 7.524% | 2.027% | 3.013% | 10.28% | 2.658% | 9.296% | 18.22% | 8.12% | 2.448% | 7.524% | 15.76% | 5.253% | 2.308% | 3.013% | 9.592%
GH+MC+TC1 | 3765.75 | 3759.75 | 3753.75 | 3759.75 | 6.482% | 5.987% | 3.723% | 3.31% | 3.132% | 2.381% | 2.095% | 1.616% | 1.219% | 1.8% | 3.175% | 1.576% | 2.757% | 6.037% | 2.222% | 1.457% | 2.095% | 3.203% | 1.822% | 1.378% | 1.8% | 2.267%
CR7 | [7 empty] | 2.88% | 2.936% | 4.228% | 0.7236% | 1.037% | 1.62% | 0.3449% | 1.967% | 0.5721% | 1.62% | 3.453% | 1.967% | 0.5721% | 1.62% | 3.453% | 1.591% | 0.4964% | 1.037% | 3.185%

## PrimaryCT EFORd Detail
[15 empty] | 10 yrs (2012-2021) |  |  |  | 7 yrs (2015-2021) |  |  |  | 5 yrs (2017-2021)
[5 empty] | EFORd% | [10 empty] | 0.1 | 0.5 | 0.9 |  | 0.1 | 0.5 | 0.9 |  | 0.1 | 0.5 | 0.9
Unit/Station | Winter Capacity | Spring/Fall Capacity | Summer Capacity | Average Capacity | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | Avg | 10th %ile | 50th %ile | 90th %ile | Avg | 10th %ile | 50th %ile | 90th %ile | Avg | 10th %ile | 50th %ile | 90th %ile
BR5 | 130 | 120 | 130 | 125 | 23.7% | 12.65% | 6.67% | 3.57% | 8.86% | 20.04% | 14.79% | 2.39% | 15.02% | 14.37% | 12.21% | 3.452% | 13.51% | 20.41% | 11.29% | 3.098% | 14.37% | 17.03% | 13.32% | 7.182% | 14.79% | 18.03%
BR6 | 171 | 157 | 146 | 157.75 | 2.99% | 4.39% | 1.72% | 1.67% | 10.95% | 13.4% | 6.95% | 6.86% | 12.88% | 4.53% | 6.634% | 1.715% | 5.695% | 12.93% | 8.177% | 3.386% | 6.95% | 13.09% | 8.924% | 5.462% | 6.95% | 13.19%
BR7 | 171 | 157 | 146 | 157.75 | 2.54% | 11.53% | 3.56% | 1.53% | 14.29% | 15.35% | 2.08% | 13.28% | 5.63% | 4.27% | 7.406% | 2.025% | 4.95% | 14.4% | 8.061% | 1.86% | 5.63% | 14.71% | 8.122% | 2.956% | 5.63% | 14.52%
BR8 | 128 | 118 | 121 | 121.25 | 15.15% | 27.9% | 2.98% | 16.59% | 5.8% | 6.45% | 4.81% | 15.55% | 8.69% | 10.61% | 11.45% | 4.627% | 9.65% | 17.72% | 9.786% | 5.404% | 8.69% | 15.97% | 9.222% | 5.466% | 8.69% | 13.57%
BR9 | 138 | 118 | 121 | 123.75 | 4.1% | 3.29% | 2.64% | 7.12% | 8.08% | 8.3% | 7.6% | 9.62% | 5.38% | 10.18% | 6.631% | 3.225% | 7.36% | 9.676% | 8.04% | 6.424% | 8.08% | 9.844% | 8.216% | 6.268% | 8.3% | 9.956%
BR10 | 138 | 118 | 121 | 123.75 | 16.42% | 5.7% | 2.51% | 11.31% | 2.01% | 3.55% | 4.6% | 7.66% | 6.67% | 6.88% | 6.731% | 2.46% | 6.185% | 11.82% | 6.097% | 2.934% | 6.67% | 9.12% | 5.872% | 3.97% | 6.67% | 7.348%
BR11 | 128 | 118 | 121 | 121.25 | 8.42% | 37.72% | 3.81% | 8.65% | 4.01% | 15.49% | 14.11% | 0.41% | 5.1% | 3.41% | 10.11% | 3.11% | 6.76% | 17.71% | 7.311% | 2.21% | 5.1% | 14.66% | 7.704% | 1.61% | 5.1% | 14.94%
BR CTs (all) | 1004 | 906 | 906 | 930.5 | 9.922% | 14.14% | 3.361% | 6.762% | 8.089% | 12% | 7.606% | 8.113% | 8.555% | 7.518% | 8.607% | 6.422% | 8.101% | 12.22% | 8.378% | 7.216% | 8.089% | 9.934% | 8.759% | 7.553% | 8.113% | 10.62%
PR13 | 175 | 161 | 147 | 161 | 15.57% | 18.55% | 8.41% | 22.37% | 22.09% | 6.79% | 0.32% | 11.94% | 6.27% | 5.34% | 11.76% | 4.838% | 10.18% | 22.12% | 10.73% | 3.332% | 6.79% | 22.2% | 6.132% | 2.328% | 6.27% | 9.88%
TC5 | 179 | 169 | 159 | 169 | 2.78% | 2.75% | 1.63% | 7.7% | 5.85% | 3.44% | 1.31% | 1.52% | 0.12% | 0.31% | 2.741% | 0.291% | 2.19% | 6.035% | 2.893% | 0.234% | 1.52% | 6.59% | 1.34% | 0.196% | 1.31% | 2.672%
TC6 | 179 | 169 | 159 | 169 | 3.2% | 2.67% | 2.97% | 4.28% | 9.78% | 2.3% | 1.73% | 1.36% | 1.01% | 0.02% | 2.932% | 0.911% | 2.485% | 4.83% | 2.926% | 0.614% | 1.73% | 6.48% | 1.284% | 0.416% | 1.36% | 2.072%
TC7 | 179 | 169 | 159 | 169 | 6.96% | 2.38% | 2.77% | 8.55% | 3.9% | 6.68% | 3.46% | 2.9% | 0% | 0.43% | 3.803% | 0.387% | 3.18% | 7.119% | 3.703% | 0.258% | 3.46% | 7.428% | 2.694% | 0.172% | 2.9% | 5.392%
TC8 | 179 | 169 | 159 | 169 | 10.37% | 6.55% | 14.55% | 5.75% | 8.54% | 2.7% | 1.29% | 1.58% | 0.62% | 0.73% | 5.268% | 0.719% | 4.225% | 10.79% | 3.03% | 0.686% | 1.58% | 6.866% | 1.384% | 0.664% | 1.29% | 2.252%
TC9 | 179 | 169 | 159 | 169 | 3.86% | 4.91% | 8.27% | 5.04% | 0.36% | 1.47% | 4.09% | 0.57% | 0.22% | 0.44% | 2.923% | 0.346% | 2.665% | 5.363% | 1.741% | 0.304% | 0.57% | 4.47% | 1.358% | 0.308% | 0.57% | 3.042%
TC10 | 179 | 169 | 159 | 169 | 6.69% | 14.91% | 6.71% | 6.4% | 2.15% | 5.37% | 5.23% | 1.39% | 0.31% | 3.5% | 5.266% | 1.282% | 5.3% | 7.53% | 3.479% | 0.958% | 3.5% | 5.782% | 3.16% | 0.742% | 3.5% | 5.314%
TC CTs | 1074 | 1014 | 954 | 1014 | 5.643% | 5.695% | 6.15% | 6.287% | 5.097% | 3.66% | 2.852% | 1.553% | 0.38% | 0.905% | 3.822% | 0.8525% | 4.378% | 6.164% | 2.962% | 0.695% | 2.852% | 5.573% | 1.87% | 0.59% | 1.553% | 3.337%

## Summary
Modeled EFOR%/EFORd%
| 10-Year History | 7-Year History | 5-Year History | 2023 BP Assumption
BR3 | 5.031% | 3.49% | 3.246% | 5.8%
GH+MC+TC1 | 2.757% | 2.095% | 1.8% | 3.2%
TC2 | 9.296% | 7.524% | 3.013% | 4.1%
CR7 | 1.62% | 1.62% | 1.037% | 2.2%
BR CTs | 8.101% | 8.089% | 8.113% | 8.1%
TC CTs | 4.378% | 2.852% | 1.553% | 4.9%
PR13 | 10.18% | 6.79% | 6.27% | 8.1%
Modeled MOR%
| 10-Year History | 7-Year History | 5-Year History | 2023 BP Assumption
BR3 | 4.738% | 3.481% | 3.481% | 3.5%
GH+MC+TC1 | 2.91% | 2.282% | 2.282% | 2.3%
TC2 | 4.059% | 3.5% | 3.5% | 3.9%
CR7 | 4.363% | 4.363% | 3.06% | 4.4%
Note on F4: plan for 2023 BP is to wait for additional data before lowering BR3's EFOR further
Note on F5: plan for 2023 BP is to wait for additional data before lowering GH/MC/TC1's EFOR further
Note on F7: plan for 2023 BP is to wait for additional data before lowering CR7's EFOR further
Note on F9: plan for 2023 BP is to wait for additional data before lowering TC CTs' EFOR further