## PSC Q1.44a
BR3
Event # | Event Type | GAC | Cause Code | Description | Start | End | Duration
36 | D1 | 400 | 0310 - Pulverizer Mills | Mills on high tonnage | 2022-12-23 07:17 | 2022-12-23 08:30 | 1.2167
40 | D1 | 390 | 8650 - Baghouse Systems | Baghouse plugging up due to boiler slagging | 2022-12-23 08:30 | 2022-12-23 13:40 | 5.1667
37 | D1 | 380 | 9305 - Ash Disposal Problem | Baghouse issues | 2022-12-23 13:40 | 2022-12-25 01:50 | 36.1667
38 | D1 | 165 | 0920 - Other Slag and Ash Removal Problems | Boiler suspect of pluggage | 2022-12-25 18:18 | 2022-12-25 21:15 | 2.95
39 | U1 | 0 | 0920 - Other Slag and Ash Removal Problems | Boiler pluggage. Unable to keep unit online | 2022-12-25 21:15 | 2023-01-01 | 146.75
BR5
Event # | Event Type | GAC | Cause Code | Description | Start | End
55 | U1 | 0 | 5041 - Fuel Piping and Valves | Fuel valves froze after valve heaters to 11N2 units were blown out | 2022-12-23 01:28 | 2022-12-23 17:22 | 15.9
57 | D1 | 100 | 5113 - Lube Oil Piping and Valves | Pressure switch on U5 lube oil pump failed. | 2022-12-23 18:00 | 2022-12-23 21:00 | 3
BR8
Event # | Event Type | GAC | Cause Code | Description | Start | End
74 | U1 | 0 | 5041 - Fuel Piping and Valves | Fuel valves froze because valves heaters to the 11N2 units kept going out | 2022-12-23 01:30 | 2022-12-23 03:36 | 2.1
75 | U1 | 0 | 5111 - Lube Oil Pumps | Malfunctioning lube oil pump | 2022-12-23 03:36 | 2022-12-23 06:26 | 2.8333
78 | D1 | 100 | 3974 - DCS Logic Problems | Generation limited due to high input temp alarm | 2022-12-23 10:51 | 2022-12-23 15:30 | 4.65
BR9
Event # | Event Type | GAC | Cause Code | Description | Start | End
58 | U1 | 0 | 5041 - Fuel Piping and Valves | Frozen fuel valves due to valves heaters to thet 11N2 units kept going out | 2022-12-23 01:30 | 2022-12-23 03:50 | 2.3333
BR10
Event # | Event Type | GAC | Cause Code | Description | Start | End
59 | U1 | 0 | 5109 - Other exhaust problems (including high exhaust sytem temperature not attributable to a specific problem) | Exhaust diffuser sections have separated. Bolts need to be replaced | 2022-12-03 18:26 | 2023-01-01 | 677.5667
BR11
Event # | Event Type | GAC | Cause Code | Description | Start | End
58 | U1 | 0 | 5041 - Fuel Piping and Valves | Frozen fuel valves due to valves heaters to the 11N2 units kept going out | 2022-12-23 01:30 | 2022-12-23 03:50 | 2.3333
60 | U1 | 0 | 5073 - Flame Scanners | Flame Trip | 2022-12-23 15:39 | 2022-12-23 17:03 | 1.4
DIX 3
Event # | Event Type | GAC | Cause Code | Description | Start | End
36 | U1 | 0 | 3653 - DC Protection Devices | Blown fuse on 125 DC control circuit | 2022-12-14 12:52 | 2022-12-14 14:24 | 1.5333
HA1
Event # | Event Type | GAC | Cause Code | Description | Start | End
5 | U1 | 0 | 3700 - Power Station Switchyard (Non-Generating Unit Equipment) | Substation breaker will not remain closed | 2022-12-23 10:33 | 2022-12-24 14:57 | 28.4
HA2
Event # | Event Type | GAC | Cause Code | Description | Start | End
7 | U1 | 0 | 3700 - Power Station Switchyard (non-generating unit equipment) | Substation breaker will not remain closed | 2022-12-23 10:33 | 2022-12-24 14:57 | 28.4
8 | U1 | 0 | 5110 - Lube Oil System - General | Lube oil temperature too low | 2022-12-24 14:57 | 2022-12-28 10:30 | 91.55
MC2
Event # | Event Type | GAC | Cause Code | Description | Start | End
97 | D1 | 240 | 0310 - Pulverizer Mills | Mill temperature malfunction | 2022-12-26 13:14 | 2022-12-26 19:05 | 5.85
MC4
Event # | Event Type | GAC | Cause Code | Description | Start | End
34 | D1 | 404 | 0095 - Bunker Flow Problems | Coal Silo Tripper Issues - Cold Weather | 2022-12-23 16:34 | 2022-12-23 18:44 | 2.1667
OF1
Event # | Event Type | GAC | Cause Code | Description | Start | End
32 | U1 | 0 | 7110 - Intake Channel or Flume (Including Trash Racks) | Excessive Trash | 2022-12-11 08:08 | 2022-12-12 14:58 | 30.8333
33 | U1 | 0 | 9036 - Storms (Ice, Snow, Etc.) | Army Corps gates not operating due to freezing temperatures. Unit shut down | 2022-12-23 04:32 | 2022-12-27 14:40 | 106.1333
OF2
Event # | Event Type | GAC | Cause Code | Description | Start | End
29 | U1 | 0 | 7110 - Intake Channel or Flume (Including Trash Racks) | Excessive Trash | 2022-12-11 08:10 | 2022-12-12 08:20 | 24.1667
OF3
Event # | Event Type | GAC | Cause Code | Description | Start | End
33 | U1 | 0 | 7110 - Intake Channel or Flume (Including Trash Racks) | Excessive Trash | 2022-12-11 08:13 | 2022-12-12 08:27 | 24.2333
34 | U1 | 0 | 9036 - Storms (Ice, Snow, Etc.) | Army Corps gates not operating due to freezing temperatures. Unit shut down | 2022-12-23 16:49 | 2022-12-27 13:39 | 92.8333
OF4
Event # | Event Type | GAC | Cause Code | Description | Start | End
27 | U1 | 0 | 7110 - Intake Channel or Flume (Including Trash Racks) | Excessive Trash | 2022-12-02 11:50 | 2022-12-12 14:21 | 242.5167
28 | U1 | 0 | 9036 - Storms (Ice, Snow, Etc.) | Army Corps gates not operating due to freezing temperatures. Unit shut down | 2022-12-23 15:20 | 2022-12-27 10:39 | 91.3167
OF5
Event # | Event Type | GAC | Cause Code | Description | Start | End
30 | U1 | 0 | 7110 - Intake Channel or Flume (Including Trash Racks) | Excessive Trash | 2022-12-11 08:15 | 2022-12-12 14:53 | 30.6333
OF6
Event # | Event Type | GAC | Cause Code | Description | Start | End
36 | U1 | 0 | 7110 - Intake Channel or Flume (Including Trash Racks) | Excessive Trash | 2022-12-11 08:19 | 2022-12-12 11:59 | 27.6667
OF7
Event # | Event Type | GAC | Cause Code | Description | Start | End
28 | U1 | 0 | 7110 - Intake Channel or Flume (Including Trash Racks) | Excessive Trash | 2022-12-11 08:22 | 2022-12-12 09:46 | 25.4
OF8
Event # | Event Type | GAC | Cause Code | Description | Start | End
27 | U1 | 0 | 7110 - Intake Channel or Flume (Including Trash Racks) | Excessive Trash | 2022-12-11 08:28 | 2022-12-12 09:41 | 25.2167
PR13
Event # | Event Type | GAC | Cause Code | Description | Start | End
89 | U1 | 0 | 3822 - Closed Cooling Water Valves | Gen cold gas temp got too low | 2022-12-23 06:36 | 2022-12-23 07:13 | 0.61667
TC1
Event # | Event Type | GAC | Cause Code | Description | Start | End
24 | D1 | 452 | 0897 - Bottom Ash Rotary (Drag Chain Type) Conveyor and Motor | The unit was placed on derate in order to troubleshoot issues with the submerged chain conveyor | 2022-12-22 07:03 | 2022-12-22 15:35 | 8.5333
25 | U1 | 0 | 0897 - Bottom Ash Rotary (Drag Chain Type) Conveyor and Motor | The unit was placed on a forced outage due to issues with primary submerged chain conveyor | 2022-12-22 15:35 | 2022-12-30 02:19 | 178.7333
TC2
Event # | Event Type | GAC | Cause Code | Description | Start | End
49 | D1 | 770 | 3344 - Deaerator (including level control) | In order to slow demand to the water coil air heaters from the Deaerator, the unit was placed on derate | 2022-12-23 03:10 | 2022-12-23 15:48 | 12.6333
50 | D1 | 414 | 1760 - Feedwater Instrumentation (not local controls) | The unit was placed on derate due to frozen transmitter that caused the loss of the B TDBFP | 2022-12-23 15:48 | 2022-12-23 17:41 | 1.8833
51 | D1 | 595 | 1760 - Feedwater Instrumentation (not local controls) | The unit was placed on a variable derate due to various cold weather issues encountered trying to start-up the B TDBFP | 2022-12-23 17:41 | 2022-12-23 22:06 | 4.4167
52 | D1 | 770 | 3344 - Deaerator (including level control) | In order to slow demand to the water coil air heaters from the Deaerator, the unit was placed on derate | 2022-12-23 22:06 | 2022-12-24 19:28 | 21.3667
53 | D1 | 647 | 3822 - Closed Cooling Water Valves | The unit was placed on derate in order to address a leaking closed cooling water valve | 2022-12-24 19:28 | 2022-12-24 21:45 | 2.2833
54 | D1 | 772 | 3344 - Deaerator (including level control) | In order to slow demand to the water coil air heaters from the Deaerator, the unit was placed on derate | 2022-12-24 21:45 | 2022-12-27 16:30 | 66.75
TC5
Event # | Event Type | GAC | Cause Code | Description | Start | End
116 | U1 | 0 | 5048 - Gas Fuel System Including Controls and Instrumentation | Lean Blow Out (LBO), and low fuel gas supply pressure | 2022-12-23 13:08 | 2022-12-23 13:48 | 0.66667
117 | U1 | 0 | 9130 - Lack of Fuel | Low fuel gas supply pressure from transport company to the plant | 2022-12-23 13:48 | 2022-12-25 11:47 | 45.9833
TC6
Event # | Event Type | GAC | Cause Code | Description | Start | End
103 | D1 | 99 | 9130 - Lack of Fuel | Low fuel gas supply pressure from transport company to the plant | 2022-12-23 13:48 | 2022-12-25 16:00 | 50.2
TC7
Event # | Event Type | GAC | Cause Code | Description | Start | End
137 | D1 | 86 | 9130 - Lack of Fuel | Low fuel gas supply pressure from transport company to the plant | 2022-12-23 13:48 | 2022-12-25 16:00 | 50.2
TC8
Event # | Event Type | GAC | Cause Code | Description | Start | End
201 | D1 | 92 | 9130 - Lack of Fuel | Low fuel gas supply pressure from transport company to the plant | 2022-12-23 13:48 | 2022-12-25 16:00 | 50.2
TC9
Event # | Event Type | GAC | Cause Code | Description | Start | End
142 | D1 | 84 | 9130 - Lack of Fuel | Low fuel gas supply pressure from transport company to the plant | 2022-12-23 13:48 | 2022-12-25 08:39 | 42.85
143 | U1 | 0 | 9130 - Lack of Fuel | Unit manually shut down. Fuel gas supply pressure from transport company too low | 2022-12-25 08:39 | 2022-12-25 11:47 | 3.1333
TC10
Event # | Event Type | GAC | Cause Code | Description | Start | End
301 | D1 | 88 | 9130 - Lack of Fuel | Low fuel gas supply pressure from transport company to the plant | 2022-12-23 13:48 | 2022-12-25 16:00 | 50.2
CR7
Event # | Event Type | GAC | Cause Code | Description | Start | End
55 | U1 | 0 | 3330 - Condensate Valves | Block trip on loss of condensate pressure when pump suction valve was opened | 2022-12-13 09:18 | 2022-12-13 11:05 | 1.7833
56 | U1 | 0 | 5041 - Fuel Piping and Valves | Block trip when fuel gas regulating station slam-shut valves tripped | 2022-12-13 13:35 | 2022-12-13 14:24 | 0.81667
57 | SF | 0 | 0801 - Hp Drum | CT2 trip during startup due to low HP drum level. Restarted | 2022-12-13 14:24 | 2022-12-13 15:34 | 1.1667
58 | D1 | 348 | 5160 - Cooling and Seal Air System | CT1 trip when RAC temperature control valve did not respond at load drop | 2022-12-21 17:08 | 2022-12-21 20:51 | 3.7167
59 | D1 | 552 | 9130 - Lack of Fuel | Block derate due to low fuel gas pipeline pressure | 2022-12-23 13:47 | 2022-12-24 15:30 | 25.7167
60 | D1 | 656 | 9130 - Lack of Fuel | Block derate due to low fuel gas pipeline pressure | 2022-12-25 00:20 | 2022-12-25 04:06 | 3.7667