## BrownSolar_Heather
Input | Value | Notes | [5 empty] | Other Notes
Start Date | 2024-01-17 | 1st day solar output assumed available after manual snow removal. | [5 empty] | Actual output (kWh) is aggregated on an hourly basis at each inverter in the solar field and added together.
End Date | 2024-01-23 | 1st day after sun melts snow (i.e., 1st day after snowfall that modeled output aligns with actual output). | [5 empty] | Small (<5 kWh) actual output values associated with negative POAI should be considered noise.
Lost MWh | -159.1502 | Difference between actual output and final modeled output over specified date range. | [5 empty] | Modeled output is created using a fourth-degree polynomial regression model that predicts generation output as a function of POA irradiance.
Panels | 44000 | [6 empty] | "Final" modeled = actual ouput in hours with negative POAI.
Time to Clear Panel (min per panel) | 1 | [6 empty] | Analysis assumes manual snow removal is completed two days after snowfall on night of 1/14/2024.
Hourly Rate for Snow Removal Labor | 20
Cost of Snow Removal | 14666.6667
$/MWh | -92.1561
| time | Day | Plane of Array Irradiance (POAI) | Actual Output (kW) | Modeled Output (kW) | Final Modeled Output (kW) | Difference
1 | 2024-01-10 | 2024-01-10 | -0.3213 | 1.1174 | -3.1798 | 1.1174 | 0
2 | 2024-01-10 01:00 | 2024-01-10 | -0.30481 | 1.0903 | -3.0167 | 1.0903 | 0
3 | 2024-01-10 02:00 | 2024-01-10 | -0.3532 | 1.0632 | -3.4955 | 1.0632 | 0
4 | 2024-01-10 03:00 | 2024-01-10 | -0.43547 | 1.0361 | -4.3096 | 1.0361 | 0
5 | 2024-01-10 04:00 | 2024-01-10 | -0.27376 | 1.009 | -2.7094 | 1.009 | 0
6 | 2024-01-10 05:00 | 2024-01-10 | -0.48561 | 0.98195 | -4.8058 | 0.98195 | 0
7 | 2024-01-10 06:00 | 2024-01-10 | -0.33633 | 0.95486 | -3.3285 | 0.95486 | 0
8 | 2024-01-10 07:00 | 2024-01-10 | -0.3641 | 0.92776 | -3.6034 | 0.92776 | 0
9 | 2024-01-10 08:00 | 2024-01-10 | 8.1923 | 51.7686 | 81.2643 | 81.2643 | -29.4956
10 | 2024-01-10 09:00 | 2024-01-10 | 32.9164 | 237.368 | 328.672 | 328.672 | -91.304
11 | 2024-01-10 10:00 | 2024-01-10 | 49.4653 | 373.5017 | 496.0392 | 496.0392 | -122.5374
12 | 2024-01-10 11:00 | 2024-01-10 | 64.9005 | 496.2933 | 653.3822 | 653.3822 | -157.0889
13 | 2024-01-10 12:00 | 2024-01-10 | 82.3063 | 632.3838 | 832.2059 | 832.2059 | -199.822
14 | 2024-01-10 13:00 | 2024-01-10 | 67.9533 | 645.4882 | 684.6404 | 684.6404 | -39.1522
15 | 2024-01-10 14:00 | 2024-01-10 | 77.0547 | 839.4122 | 778.0991 | 778.0991 | 61.3131
16 | 2024-01-10 15:00 | 2024-01-10 | 52.2187 | 557.9525 | 524.0203 | 524.0203 | 33.9322
17 | 2024-01-10 16:00 | 2024-01-10 | 35.3227 | 355.7194 | 352.9216 | 352.9216 | 2.7979
18 | 2024-01-10 17:00 | 2024-01-10 | 8.2527 | 66.9719 | 81.8647 | 81.8647 | -14.8928
19 | 2024-01-10 18:00 | 2024-01-10 | -0.3754 | 2.6943 | -3.7152 | 2.6943 | 0
20 | 2024-01-10 19:00 | 2024-01-10 | -0.92186 | 2.5779 | -9.1219 | 2.5779 | 0
21 | 2024-01-10 20:00 | 2024-01-10 | -1.1375 | 2.4614 | -11.2553 | 2.4614 | 0
22 | 2024-01-10 21:00 | 2024-01-10 | -1.0945 | 2.3449 | -10.83 | 2.3449 | 0
23 | 2024-01-10 22:00 | 2024-01-10 | -1.1937 | 2.2285 | -11.8111 | 2.2285 | 0
24 | 2024-01-10 23:00 | 2024-01-10 | -1.2512 | 2.112 | -12.3794 | 2.112 | 0
25 | 2024-01-11 | 2024-01-11 | -1.5104 | 1.9955 | -14.9434 | 1.9955 | 0
26 | 2024-01-11 01:00 | 2024-01-11 | -1.4945 | 1.8791 | -14.786 | 1.8791 | 0
27 | 2024-01-11 02:00 | 2024-01-11 | -0.99455 | 1.7626 | -9.841 | 1.7626 | 0
28 | 2024-01-11 03:00 | 2024-01-11 | -0.49418 | 1.6461 | -4.8905 | 1.6461 | 0
29 | 2024-01-11 04:00 | 2024-01-11 | -1.2735 | 1.5296 | -12.6002 | 1.5296 | 0
30 | 2024-01-11 05:00 | 2024-01-11 | -1.2612 | 1.4132 | -12.479 | 1.4132 | 0
31 | 2024-01-11 06:00 | 2024-01-11 | -1.0179 | 1.2967 | -10.0718 | 1.2967 | 0
32 | 2024-01-11 07:00 | 2024-01-11 | 0.22237 | 3.1454 | 2.2011 | 2.2011 | 0.94436
33 | 2024-01-11 08:00 | 2024-01-11 | 130.6414 | 789.1086 | 1336.0993 | 1336.0993 | -546.9907
34 | 2024-01-11 09:00 | 2024-01-11 | 376.0787 | 3197.1805 | 4009.7714 | 4009.7714 | -812.591
35 | 2024-01-11 10:00 | 2024-01-11 | 570.5395 | 5903.2228 | 6131.3033 | 6131.3033 | -228.0805
36 | 2024-01-11 11:00 | 2024-01-11 | 703.6869 | 7453.1957 | 7477.424 | 7477.424 | -24.2283
37 | 2024-01-11 12:00 | 2024-01-11 | 766.3178 | 7979.9533 | 8054.4378 | 8054.4378 | -74.4845
38 | 2024-01-11 13:00 | 2024-01-11 | 749.4568 | 7621.7257 | 7903.4865 | 7903.4865 | -281.7608
39 | 2024-01-11 14:00 | 2024-01-11 | 659.6804 | 6444.5885 | 7047.9814 | 7047.9814 | -603.3929
40 | 2024-01-11 15:00 | 2024-01-11 | 503.0151 | 4318.28 | 5406.9419 | 5406.9419 | -1088.6619
41 | 2024-01-11 16:00 | 2024-01-11 | 291.3018 | 1637.6574 | 3072.1636 | 3072.1636 | -1434.5062
42 | 2024-01-11 17:00 | 2024-01-11 | 51.7555 | 151.2228 | 519.3111 | 519.3111 | -368.0882
43 | 2024-01-11 18:00 | 2024-01-11 | -0.99578 | 1.5508 | -9.8532 | 1.5508 | 0
44 | 2024-01-11 19:00 | 2024-01-11 | -1.1925 | 1.4837 | -11.7987 | 1.4837 | 0
45 | 2024-01-11 20:00 | 2024-01-11 | -1.162 | 1.4165 | -11.4971 | 1.4165 | 0
46 | 2024-01-11 21:00 | 2024-01-11 | -1.242 | 1.3494 | -12.2886 | 1.3494 | 0
47 | 2024-01-11 22:00 | 2024-01-11 | -1.288 | 1.2822 | -12.7435 | 1.2822 | 0
48 | 2024-01-11 23:00 | 2024-01-11 | -1.1377 | 1.2151 | -11.2565 | 1.2151 | 0
49 | 2024-01-12 | 2024-01-12 | -1.9279 | 1.1479 | -19.0714 | 1.1479 | 0
50 | 2024-01-12 01:00 | 2024-01-12 | -2.4626 | 1.0808 | -20.57 | 1.0808 | 0
51 | 2024-01-12 02:00 | 2024-01-12 | -0.85397 | 1.0137 | -8.4503 | 1.0137 | 0
52 | 2024-01-12 03:00 | 2024-01-12 | -0.3005 | 0.94651 | -2.9739 | 0.94651 | 0
53 | 2024-01-12 04:00 | 2024-01-12 | -0.54444 | 0.87936 | -5.3879 | 0.87936 | 0
54 | 2024-01-12 05:00 | 2024-01-12 | -0.591 | 0.81222 | -5.8486 | 0.81222 | 0
55 | 2024-01-12 06:00 | 2024-01-12 | -1.231 | 0.74507 | -12.1796 | 0.74507 | 0
56 | 2024-01-12 07:00 | 2024-01-12 | -0.40087 | 0.75097 | -3.9672 | 0.75097 | 0
57 | 2024-01-12 08:00 | 2024-01-12 | 11.6426 | 99.4891 | 115.5972 | 115.5972 | -16.108
58 | 2024-01-12 09:00 | 2024-01-12 | 18.2914 | 187.8942 | 181.9355 | 181.9355 | 5.9588
59 | 2024-01-12 10:00 | 2024-01-12 | 14.4058 | 141.5308 | 143.1389 | 143.1389 | -1.6081
60 | 2024-01-12 11:00 | 2024-01-12 | 18.8258 | 185.4183 | 187.2777 | 187.2777 | -1.8594
61 | 2024-01-12 12:00 | 2024-01-12 | 25.9439 | 267.803 | 258.5761 | 258.5761 | 9.227
62 | 2024-01-12 13:00 | 2024-01-12 | 18.9483 | 164.7086 | 188.5019 | 188.5019 | -23.7933
63 | 2024-01-12 14:00 | 2024-01-12 | 25.7568 | 266.5944 | 256.6983 | 256.6983 | 9.8961
64 | 2024-01-12 15:00 | 2024-01-12 | 161.0395 | 1463.7034 | 1658.0736 | 1658.0736 | -194.3703
65 | 2024-01-12 16:00 | 2024-01-12 | 106.2606 | 736.0568 | 1080.6292 | 1080.6292 | -344.5725
66 | 2024-01-12 17:00 | 2024-01-12 | 2.2626 | 11.817 | 22.4082 | 22.4082 | -10.5912
67 | 2024-01-12 18:00 | 2024-01-12 | -0.64499 | 1.4197 | -6.3827 | 1.4197 | 0
68 | 2024-01-12 19:00 | 2024-01-12 | -0.54107 | 1.3305 | -5.3545 | 1.3305 | 0
69 | 2024-01-12 20:00 | 2024-01-12 | -0.5995 | 1.2413 | -5.9326 | 1.2413 | 0
70 | 2024-01-12 21:00 | 2024-01-12 | -0.4051 | 1.152 | -4.0091 | 1.152 | 0
71 | 2024-01-12 22:00 | 2024-01-12 | 0.30294 | 1.0628 | 2.9987 | 2.9987 | -1.9358
72 | 2024-01-12 23:00 | 2024-01-12 | 0.68005 | 0.97358 | 6.7321 | 6.7321 | -5.7586
73 | 2024-01-13 | 2024-01-13 | 0.22669 | 0.88434 | 2.2439 | 2.2439 | -1.3595
74 | 2024-01-13 01:00 | 2024-01-13 | 0.37535 | 0.79511 | 3.7154 | 3.7154 | -2.9203
75 | 2024-01-13 02:00 | 2024-01-13 | 0.16113 | 0.70588 | 1.5948 | 1.5948 | -0.88897
76 | 2024-01-13 03:00 | 2024-01-13 | 0.030577 | 0.61665 | 0.30264 | 0.30264 | 0.31401
77 | 2024-01-13 04:00 | 2024-01-13 | 0.075025 | 0.52742 | 0.74258 | 0.74258 | -0.21516
78 | 2024-01-13 05:00 | 2024-01-13 | -0.13521 | 0.43819 | -1.3382 | 0.43819 | 0
79 | 2024-01-13 06:00 | 2024-01-13 | -0.20813 | 0.34896 | -2.0599 | 0.34896 | 0
80 | 2024-01-13 07:00 | 2024-01-13 | 0.013341 | 0.29301 | 0.13205 | 0.13205 | 0.16097
81 | 2024-01-13 08:00 | 2024-01-13 | 9.4727 | 68.0397 | 93.9982 | 93.9982 | -25.9585
82 | 2024-01-13 09:00 | 2024-01-13 | 45.669 | 430.234 | 457.5225 | 457.5225 | -27.2886
83 | 2024-01-13 10:00 | 2024-01-13 | 77.4682 | 748.7344 | 782.3547 | 782.3547 | -33.6204
84 | 2024-01-13 11:00 | 2024-01-13 | 110.5289 | 1101.3099 | 1125.1667 | 1125.1667 | -23.8568
85 | 2024-01-13 12:00 | 2024-01-13 | 127.5922 | 1283.8546 | 1304.0096 | 1304.0096 | -20.1549
86 | 2024-01-13 13:00 | 2024-01-13 | 175.623 | 1699.1884 | 1813.8049 | 1813.8049 | -114.6165
87 | 2024-01-13 14:00 | 2024-01-13 | 324.8885 | 3004.8969 | 3442.8875 | 3442.8875 | -437.9906
88 | 2024-01-13 15:00 | 2024-01-13 | 259.3226 | 2300.74 | 2720.9022 | 2720.9022 | -420.1622
89 | 2024-01-13 16:00 | 2024-01-13 | 285.8674 | 1461.2556 | 3012.3358 | 3012.3358 | -1551.0802
90 | 2024-01-13 17:00 | 2024-01-13 | 53.2084 | 167.5293 | 534.0871 | 534.0871 | -366.5578
91 | 2024-01-13 18:00 | 2024-01-13 | -1.0077 | 0.81802 | -9.971 | 0.81802 | 0
92 | 2024-01-13 19:00 | 2024-01-13 | -1.2549 | 0.7854 | -12.4158 | 0.7854 | 0
93 | 2024-01-13 20:00 | 2024-01-13 | -1.2216 | 0.77888 | -12.0867 | 0.77888 | 0
94 | 2024-01-13 21:00 | 2024-01-13 | -1.0547 | 0.77235 | -10.4364 | 0.77235 | 0
95 | 2024-01-13 22:00 | 2024-01-13 | -1.0544 | 0.76582 | -10.4326 | 0.76582 | 0
96 | 2024-01-13 23:00 | 2024-01-13 | -0.56186 | 0.75929 | -5.5602 | 0.75929 | 0
97 | 2024-01-14 | 2024-01-14 | -0.49344 | 0.75276 | -4.8833 | 0.75276 | 0
98 | 2024-01-14 01:00 | 2024-01-14 | -0.34997 | 0.74624 | -3.4636 | 0.74624 | 0
99 | 2024-01-14 02:00 | 2024-01-14 | -0.30177 | 0.73971 | -2.9865 | 0.73971 | 0
100 | 2024-01-14 03:00 | 2024-01-14 | 0.01584 | 0.73318 | 0.15678 | 0.15678 | 0.5764
101 | 2024-01-14 04:00 | 2024-01-14 | 0.021563 | 0.72665 | 0.21342 | 0.21342 | 0.51323
102 | 2024-01-14 05:00 | 2024-01-14 | -0.014682 | 0.72013 | -0.14531 | 0.72013 | 0
103 | 2024-01-14 06:00 | 2024-01-14 | 0.003872 | 0.7136 | 0.038324 | 0.038324 | 0.67527
104 | 2024-01-14 07:00 | 2024-01-14 | 0.94801 | 3.6129 | 9.3854 | 9.3854 | -5.7725
105 | 2024-01-14 08:00 | 2024-01-14 | 130.2395 | 881.4838 | 1331.8676 | 1331.8676 | -450.3838
106 | 2024-01-14 09:00 | 2024-01-14 | 379.6579 | 3462.0467 | 4049.4305 | 4049.4305 | -587.3839
107 | 2024-01-14 10:00 | 2024-01-14 | 586.8206 | 5860.3543 | 6302.6187 | 6302.6187 | -442.2644
108 | 2024-01-14 11:00 | 2024-01-14 | 713.3434 | 7101.1399 | 7569.1776 | 7569.1776 | -468.0376
109 | 2024-01-14 12:00 | 2024-01-14 | 759.8079 | 7438.444 | 7996.5642 | 7996.5642 | -558.1202
110 | 2024-01-14 13:00 | 2024-01-14 | 521.1255 | 5077.0515 | 5603.1118 | 5603.1118 | -526.0603
111 | 2024-01-14 14:00 | 2024-01-14 | 186.885 | 1895.4161 | 1934.5907 | 1934.5907 | -39.1746
112 | 2024-01-14 15:00 | 2024-01-14 | 115.5364 | 1181.3394 | 1177.5208 | 1177.5208 | 3.8186
113 | 2024-01-14 16:00 | 2024-01-14 | 54.7167 | 525.6252 | 549.4383 | 549.4383 | -23.8131
114 | 2024-01-14 17:00 | 2024-01-14 | 7.19 | 56.0551 | 71.3028 | 71.3028 | -15.2477
115 | 2024-01-14 18:00 | 2024-01-14 | -0.0094336 | 2.6314 | -0.09337 | 2.6314 | 0
116 | 2024-01-14 19:00 | 2024-01-14 | -0.0044643 | 2.5513 | -0.044186 | 2.5513 | 0
117 | 2024-01-14 20:00 | 2024-01-14 | 0.0049679 | 2.4711 | 0.04917 | 0.04917 | 2.422
118 | 2024-01-14 21:00 | 2024-01-14 | 0.00075437 | 2.391 | 0.0074665 | 0.0074665 | 2.3835
119 | 2024-01-14 22:00 | 2024-01-14 | 0.0046545 | 2.3109 | 0.046068 | 0.046068 | 2.2648
120 | 2024-01-14 23:00 | 2024-01-14 | -0.0062899 | 2.2307 | -0.062255 | 2.2307 | 0
121 | 2024-01-15 | 2024-01-15 | -0.0021393 | 2.1506 | -0.021173 | 2.1506 | 0
122 | 2024-01-15 01:00 | 2024-01-15 | -0.011135 | 2.0704 | -0.11021 | 2.0704 | 0
123 | 2024-01-15 02:00 | 2024-01-15 | -0.032838 | 1.9903 | -0.32501 | 1.9903 | 0
124 | 2024-01-15 03:00 | 2024-01-15 | -0.0077366 | 1.9102 | -0.076574 | 1.9102 | 0
125 | 2024-01-15 04:00 | 2024-01-15 | -0.0061015 | 1.83 | -0.06039 | 1.83 | 0
126 | 2024-01-15 05:00 | 2024-01-15 | -0.0039623 | 1.7499 | -0.039217 | 1.7499 | 0
127 | 2024-01-15 06:00 | 2024-01-15 | -0.010945 | 1.6698 | -0.10833 | 1.6698 | 0
128 | 2024-01-15 07:00 | 2024-01-15 | 0.34396 | 1.5896 | 3.4047 | 3.4047 | -1.815
129 | 2024-01-15 08:00 | 2024-01-15 | 32.5359 | 9.1368 | 324.8401 | 324.8401 | -315.7033
130 | 2024-01-15 09:00 | 2024-01-15 | 95.3754 | 51.5445 | 967.4154 | 967.4154 | -915.8708
131 | 2024-01-15 10:00 | 2024-01-15 | 179.5068 | 111.53 | 1855.408 | 1855.408 | -1743.878
132 | 2024-01-15 11:00 | 2024-01-15 | 269.556 | 172.1199 | 2833.085 | 2833.085 | -2660.9652
133 | 2024-01-15 12:00 | 2024-01-15 | 303.6967 | 202.7462 | 3208.7979 | 3208.7979 | -3006.0517
134 | 2024-01-15 13:00 | 2024-01-15 | 330.7257 | 218.6922 | 3507.4524 | 3507.4524 | -3288.7603
135 | 2024-01-15 14:00 | 2024-01-15 | 156.8111 | 99.5382 | 1613.0691 | 1613.0691 | -1513.5309
136 | 2024-01-15 15:00 | 2024-01-15 | 89.7792 | 35.2311 | 909.4219 | 909.4219 | -874.1908
137 | 2024-01-15 16:00 | 2024-01-15 | 43.9719 | 8.2403 | 440.3275 | 440.3275 | -432.0872
138 | 2024-01-15 17:00 | 2024-01-15 | 8.4041 | 0.20508 | 83.3705 | 83.3705 | -83.1654
139 | 2024-01-15 18:00 | 2024-01-15 | 0 | 0.33052 | 0 | 0 | 0.33052
140 | 2024-01-15 19:00 | 2024-01-15 | -0.0012573 | 0.47025 | -0.012444 | 0.47025 | 0
141 | 2024-01-15 20:00 | 2024-01-15 | -0.00018856 | 0.60997 | -0.0018663 | 0.60997 | 0
142 | 2024-01-15 21:00 | 2024-01-15 | -0.00069206 | 0.74969 | -0.0068497 | 0.74969 | 0
143 | 2024-01-15 22:00 | 2024-01-15 | -0.002642 | 0.88942 | -0.026149 | 0.88942 | 0
144 | 2024-01-15 23:00 | 2024-01-15 | -0.01019 | 1.0291 | -0.10086 | 1.0291 | 0
145 | 2024-01-16 | 2024-01-16 | -0.019816 | 1.1689 | -0.19613 | 1.1689 | 0
146 | 2024-01-16 01:00 | 2024-01-16 | -0.074918 | 1.3086 | -0.74149 | 1.3086 | 0
147 | 2024-01-16 02:00 | 2024-01-16 | -0.10388 | 1.4483 | -1.0282 | 1.4483 | 0
148 | 2024-01-16 03:00 | 2024-01-16 | -0.052054 | 1.588 | -0.5152 | 1.588 | 0
149 | 2024-01-16 04:00 | 2024-01-16 | -0.15323 | 1.7278 | -1.5166 | 1.7278 | 0
150 | 2024-01-16 05:00 | 2024-01-16 | -0.1883 | 1.8675 | -1.8636 | 1.8675 | 0
151 | 2024-01-16 06:00 | 2024-01-16 | -0.22645 | 2.0072 | -2.2412 | 2.0072 | 0
152 | 2024-01-16 07:00 | 2024-01-16 | 0.42795 | 2.1469 | 4.2362 | 4.2362 | -2.0892
153 | 2024-01-16 08:00 | 2024-01-16 | 44.3844 | 5.7985 | 444.5064 | 444.5064 | -438.7079
154 | 2024-01-16 09:00 | 2024-01-16 | 132.4659 | 39.3816 | 1355.3195 | 1355.3195 | -1315.9379
155 | 2024-01-16 10:00 | 2024-01-16 | 356.9321 | 143.7433 | 3797.6212 | 3797.6212 | -3653.8779
156 | 2024-01-16 11:00 | 2024-01-16 | 731.3176 | 315.3021 | 7737.3682 | 7737.3682 | -7422.0661
157 | 2024-01-16 12:00 | 2024-01-16 | 765.5733 | 352.3552 | 8047.8455 | 8047.8455 | -7695.4903
158 | 2024-01-16 13:00 | 2024-01-16 | 856.5788 | 369.2786 | 8797.6549 | 8797.6549 | -8428.3763
159 | 2024-01-16 14:00 | 2024-01-16 | 358.7971 | 151.517 | 3818.2837 | 3818.2837 | -3666.7668
160 | 2024-01-16 15:00 | 2024-01-16 | 216.8225 | 89.3679 | 2257.7229 | 2257.7229 | -2168.355
161 | 2024-01-16 16:00 | 2024-01-16 | 106.962 | 30.2922 | 1087.9424 | 1087.9424 | -1057.6502
162 | 2024-01-16 17:00 | 2024-01-16 | 21.7281 | 3.2473 | 216.3168 | 216.3168 | -213.0695
163 | 2024-01-16 18:00 | 2024-01-16 | -0.67216 | 1.8986 | -6.6515 | 1.8986 | 0
164 | 2024-01-16 19:00 | 2024-01-16 | -0.91469 | 1.8192 | -9.051 | 1.8192 | 0
165 | 2024-01-16 20:00 | 2024-01-16 | -0.9143 | 1.7398 | -9.0471 | 1.7398 | 0
166 | 2024-01-16 21:00 | 2024-01-16 | -0.97704 | 1.6605 | -9.6678 | 1.6605 | 0
167 | 2024-01-16 22:00 | 2024-01-16 | -0.97097 | 1.5811 | -9.6077 | 1.5811 | 0
168 | 2024-01-16 23:00 | 2024-01-16 | -1.0329 | 1.5018 | -10.2202 | 1.5018 | 0
169 | 2024-01-17 | 2024-01-17 | -1.0162 | 1.4224 | -10.055 | 1.4224 | 0
170 | 2024-01-17 01:00 | 2024-01-17 | -1.087 | 1.343 | -10.7555 | 1.343 | 0
171 | 2024-01-17 02:00 | 2024-01-17 | -1.2638 | 1.2637 | -12.5043 | 1.2637 | 0
172 | 2024-01-17 03:00 | 2024-01-17 | -1.3886 | 1.1843 | -13.7386 | 1.1843 | 0
173 | 2024-01-17 04:00 | 2024-01-17 | -1.1102 | 1.1049 | -10.9849 | 1.1049 | 0
174 | 2024-01-17 05:00 | 2024-01-17 | -1.0465 | 1.0256 | -10.355 | 1.0256 | 0
175 | 2024-01-17 06:00 | 2024-01-17 | -1.2652 | 0.94621 | -12.518 | 0.94621 | 0
176 | 2024-01-17 07:00 | 2024-01-17 | 0.61559 | 0.86685 | 6.0939 | 6.0939 | -5.227
177 | 2024-01-17 08:00 | 2024-01-17 | 184.3479 | 26.6568 | 1907.3412 | 1907.3412 | -1880.6844
178 | 2024-01-17 09:00 | 2024-01-17 | 471.0603 | 139.9105 | 5058.1982 | 5058.1982 | -4918.2877
179 | 2024-01-17 10:00 | 2024-01-17 | 693.0643 | 258.1456 | 7375.4149 | 7375.4149 | -7117.2693
180 | 2024-01-17 11:00 | 2024-01-17 | 767.4601 | 367.362 | 8064.539 | 8064.539 | -7697.177
181 | 2024-01-17 12:00 | 2024-01-17 | 817.4456 | 425.3207 | 8489.7885 | 8489.7885 | -8064.4679
182 | 2024-01-17 13:00 | 2024-01-17 | 799.5358 | 415.4973 | 8341.3201 | 8341.3201 | -7925.8227
183 | 2024-01-17 14:00 | 2024-01-17 | 704.0982 | 347.2477 | 7481.3507 | 7481.3507 | -7134.103
184 | 2024-01-17 15:00 | 2024-01-17 | 538.1112 | 227.5656 | 5785.9342 | 5785.9342 | -5558.3686
185 | 2024-01-17 16:00 | 2024-01-17 | 316.1892 | 86.258 | 3346.7289 | 3346.7289 | -3260.4709
186 | 2024-01-17 17:00 | 2024-01-17 | 69.8641 | 5.1773 | 704.2288 | 704.2288 | -699.0514
187 | 2024-01-17 18:00 | 2024-01-17 | -0.61488 | 0.4337 | -6.0848 | 0.4337 | 0
188 | 2024-01-17 19:00 | 2024-01-17 | -0.99787 | 0.46741 | -9.8738 | 0.46741 | 0
189 | 2024-01-17 20:00 | 2024-01-17 | -0.79934 | 0.50112 | -7.9098 | 0.50112 | 0
190 | 2024-01-17 21:00 | 2024-01-17 | -1.1466 | 0.53484 | -11.3451 | 0.53484 | 0
191 | 2024-01-17 22:00 | 2024-01-17 | -1.0552 | 0.56855 | -10.4411 | 0.56855 | 0
192 | 2024-01-17 23:00 | 2024-01-17 | -0.83257 | 0.60227 | -8.2386 | 0.60227 | 0
193 | 2024-01-18 | 2024-01-18 | -0.86988 | 0.63598 | -8.6077 | 0.63598 | 0
194 | 2024-01-18 01:00 | 2024-01-18 | -0.85224 | 0.66969 | -8.4332 | 0.66969 | 0
195 | 2024-01-18 02:00 | 2024-01-18 | -0.724 | 0.70341 | -7.1644 | 0.70341 | 0
196 | 2024-01-18 03:00 | 2024-01-18 | -0.68652 | 0.73712 | -6.7936 | 0.73712 | 0
197 | 2024-01-18 04:00 | 2024-01-18 | -0.94861 | 0.77084 | -9.3866 | 0.77084 | 0
198 | 2024-01-18 05:00 | 2024-01-18 | -0.64999 | 0.80455 | -6.4322 | 0.80455 | 0
199 | 2024-01-18 06:00 | 2024-01-18 | -0.338 | 0.83827 | -3.345 | 0.83827 | 0
200 | 2024-01-18 07:00 | 2024-01-18 | 0.29443 | 0.87198 | 2.9143 | 2.9143 | -2.0424
201 | 2024-01-18 08:00 | 2024-01-18 | 39.7487 | 9.5695 | 397.6017 | 397.6017 | -388.0321
202 | 2024-01-18 09:00 | 2024-01-18 | 171.0972 | 87.4541 | 1765.3924 | 1765.3924 | -1677.9383
203 | 2024-01-18 10:00 | 2024-01-18 | 169.7362 | 97.1365 | 1750.8475 | 1750.8475 | -1653.711
204 | 2024-01-18 11:00 | 2024-01-18 | 183.2442 | 118.116 | 1895.4935 | 1895.4935 | -1777.3775
205 | 2024-01-18 12:00 | 2024-01-18 | 356.168 | 255.8766 | 3789.1551 | 3789.1551 | -3533.2785
206 | 2024-01-18 13:00 | 2024-01-18 | 251.5702 | 230.5383 | 2636.0727 | 2636.0727 | -2405.5343
207 | 2024-01-18 14:00 | 2024-01-18 | 72.8599 | 48.828 | 734.9748 | 734.9748 | -686.1468
208 | 2024-01-18 15:00 | 2024-01-18 | 74.1642 | 51.7047 | 748.3751 | 748.3751 | -696.6704
209 | 2024-01-18 16:00 | 2024-01-18 | 59.472 | 37.5655 | 597.9111 | 597.9111 | -560.3456
210 | 2024-01-18 17:00 | 2024-01-18 | 9.7512 | 3.9878 | 96.7688 | 96.7688 | -92.781
211 | 2024-01-18 18:00 | 2024-01-18 | 0 | 1.5866 | 0 | 0 | 1.5866
212 | 2024-01-18 19:00 | 2024-01-18 | 0 | 1.5063 | 0 | 0 | 1.5063
213 | 2024-01-18 20:00 | 2024-01-18 | 0 | 1.426 | 0 | 0 | 1.426
214 | 2024-01-18 21:00 | 2024-01-18 | 0 | 1.3458 | 0 | 0 | 1.3458
215 | 2024-01-18 22:00 | 2024-01-18 | 0 | 1.2655 | 0 | 0 | 1.2655
216 | 2024-01-18 23:00 | 2024-01-18 | 0 | 1.1853 | 0 | 0 | 1.1853
217 | 2024-01-19 | 2024-01-19 | 0 | 1.105 | 0 | 0 | 1.105
218 | 2024-01-19 01:00 | 2024-01-19 | 0.0025775 | 1.0247 | 0.025511 | 0.025511 | 0.99922
219 | 2024-01-19 02:00 | 2024-01-19 | 0 | 0.94447 | 0 | 0 | 0.94447
220 | 2024-01-19 03:00 | 2024-01-19 | 0 | 0.86421 | 0 | 0 | 0.86421
221 | 2024-01-19 04:00 | 2024-01-19 | 0 | 0.78395 | 0 | 0 | 0.78395
222 | 2024-01-19 05:00 | 2024-01-19 | -0.0132 | 0.70369 | -0.13065 | 0.70369 | 0
223 | 2024-01-19 06:00 | 2024-01-19 | 0 | 0.62343 | 0 | 0 | 0.62343
224 | 2024-01-19 07:00 | 2024-01-19 | 0.068646 | 0.54316 | 0.67944 | 0.67944 | -0.13627
225 | 2024-01-19 08:00 | 2024-01-19 | 13.062 | 0.75262 | 129.7399 | 129.7399 | -128.9873
226 | 2024-01-19 09:00 | 2024-01-19 | 65.8484 | 31.2296 | 663.0833 | 663.0833 | -631.8537
227 | 2024-01-19 10:00 | 2024-01-19 | 106.7309 | 70.5623 | 1085.5319 | 1085.5319 | -1014.9696
228 | 2024-01-19 11:00 | 2024-01-19 | 72.4996 | 33.6255 | 731.2749 | 731.2749 | -697.6495
229 | 2024-01-19 12:00 | 2024-01-19 | 123.6163 | 90.4726 | 1262.2255 | 1262.2255 | -1171.7529
230 | 2024-01-19 13:00 | 2024-01-19 | 98.9138 | 64.3866 | 1004.1585 | 1004.1585 | -939.7719
231 | 2024-01-19 14:00 | 2024-01-19 | 124.6385 | 84.9297 | 1272.9616 | 1272.9616 | -1188.0319
232 | 2024-01-19 15:00 | 2024-01-19 | 88.8391 | 52.1552 | 899.6933 | 899.6933 | -847.5382
233 | 2024-01-19 16:00 | 2024-01-19 | 48.6033 | 16.2425 | 487.2873 | 487.2873 | -471.0448
234 | 2024-01-19 17:00 | 2024-01-19 | 16.8706 | 4.7286 | 167.7404 | 167.7404 | -163.0118
235 | 2024-01-19 18:00 | 2024-01-19 | -0.51909 | 1.7407 | -5.137 | 1.7407 | 0
236 | 2024-01-19 19:00 | 2024-01-19 | -0.22639 | 1.7096 | -2.2405 | 1.7096 | 0
237 | 2024-01-19 20:00 | 2024-01-19 | -0.2264 | 1.6785 | -2.2407 | 1.6785 | 0
238 | 2024-01-19 21:00 | 2024-01-19 | -0.22641 | 1.6474 | -2.2408 | 1.6474 | 0
239 | 2024-01-19 22:00 | 2024-01-19 | -0.22642 | 1.6163 | -2.2409 | 1.6163 | 0
240 | 2024-01-19 23:00 | 2024-01-19 | -0.22644 | 1.5852 | -2.241 | 1.5852 | 0
241 | 2024-01-20 | 2024-01-20 | -0.15628 | 1.5541 | -1.5467 | 1.5541 | 0
242 | 2024-01-20 01:00 | 2024-01-20 | -0.068971 | 1.523 | -0.68263 | 1.523 | 0
243 | 2024-01-20 02:00 | 2024-01-20 | -0.2245 | 1.492 | -2.2219 | 1.492 | 0
244 | 2024-01-20 03:00 | 2024-01-20 | -0.2409 | 1.4609 | -2.3842 | 1.4609 | 0
245 | 2024-01-20 04:00 | 2024-01-20 | -0.68507 | 1.4298 | -6.7793 | 1.4298 | 0
246 | 2024-01-20 05:00 | 2024-01-20 | -1.0322 | 1.3987 | -10.2133 | 1.3987 | 0
247 | 2024-01-20 06:00 | 2024-01-20 | -1.0134 | 1.3676 | -10.0275 | 1.3676 | 0
248 | 2024-01-20 07:00 | 2024-01-20 | -0.20154 | 1.3365 | -1.9947 | 1.3365 | 0
249 | 2024-01-20 08:00 | 2024-01-20 | 56.8145 | 17.5518 | 570.8085 | 570.8085 | -553.2567
250 | 2024-01-20 09:00 | 2024-01-20 | 171.5116 | 111.9431 | 1769.8215 | 1769.8215 | -1657.8785
251 | 2024-01-20 10:00 | 2024-01-20 | 272.672 | 208.6233 | 2867.2873 | 2867.2873 | -2658.664
252 | 2024-01-20 11:00 | 2024-01-20 | 343.1246 | 294.4916 | 3644.6882 | 3644.6882 | -3350.1966
253 | 2024-01-20 12:00 | 2024-01-20 | 373.0744 | 336.9003 | 3976.4826 | 3976.4826 | -3639.5823
254 | 2024-01-20 13:00 | 2024-01-20 | 339.8865 | 298.4643 | 3608.8365 | 3608.8365 | -3310.3722
255 | 2024-01-20 14:00 | 2024-01-20 | 336.7077 | 263.067 | 3573.6494 | 3573.6494 | -3310.5824
256 | 2024-01-20 15:00 | 2024-01-20 | 320.9244 | 184.4433 | 3399.0591 | 3399.0591 | -3214.6159
257 | 2024-01-20 16:00 | 2024-01-20 | 349.727 | 68.0176 | 3717.8057 | 3717.8057 | -3649.7881
258 | 2024-01-20 17:00 | 2024-01-20 | 113.8524 | 5.4305 | 1159.9021 | 1159.9021 | -1154.4716
259 | 2024-01-20 18:00 | 2024-01-20 | -0.98466 | 1.057 | -9.7431 | 1.057 | 0
260 | 2024-01-20 19:00 | 2024-01-20 | -1.2401 | 1.1258 | -12.2698 | 1.1258 | 0
261 | 2024-01-20 20:00 | 2024-01-20 | -0.92583 | 1.1945 | -9.1612 | 1.1945 | 0
262 | 2024-01-20 21:00 | 2024-01-20 | -0.71424 | 1.2633 | -7.0679 | 1.2633 | 0
263 | 2024-01-20 22:00 | 2024-01-20 | -1.027 | 1.332 | -10.1617 | 1.332 | 0
264 | 2024-01-20 23:00 | 2024-01-20 | -1.1282 | 1.4008 | -11.1632 | 1.4008 | 0
265 | 2024-01-21 | 2024-01-21 | -1.1354 | 1.4696 | -11.2344 | 1.4696 | 0
266 | 2024-01-21 01:00 | 2024-01-21 | -1.4008 | 1.5383 | -13.8596 | 1.5383 | 0
267 | 2024-01-21 02:00 | 2024-01-21 | -1.0981 | 1.6071 | -10.8653 | 1.6071 | 0
268 | 2024-01-21 03:00 | 2024-01-21 | -1.0642 | 1.6774 | -10.5299 | 1.6774 | 0
269 | 2024-01-21 04:00 | 2024-01-21 | -1.1546 | 1.7446 | -11.424 | 1.7446 | 0
270 | 2024-01-21 05:00 | 2024-01-21 | -0.43065 | 1.8133 | -4.2619 | 1.8133 | 0
271 | 2024-01-21 06:00 | 2024-01-21 | -0.34282 | 1.8821 | -3.3928 | 1.8821 | 0
272 | 2024-01-21 07:00 | 2024-01-21 | 0.82862 | 1.9509 | 8.2031 | 8.2031 | -6.2523
273 | 2024-01-21 08:00 | 2024-01-21 | 51.0551 | 18.7907 | 512.1914 | 512.1914 | -493.4007
274 | 2024-01-21 09:00 | 2024-01-21 | 182.6405 | 124.0854 | 1889.0155 | 1889.0155 | -1764.9302
275 | 2024-01-21 10:00 | 2024-01-21 | 278.3329 | 230.0708 | 2929.4743 | 2929.4743 | -2699.4034
276 | 2024-01-21 11:00 | 2024-01-21 | 340.1631 | 321.6356 | 3611.8985 | 3611.8985 | -3290.2629
277 | 2024-01-21 12:00 | 2024-01-21 | 373.9084 | 373.0646 | 3985.7236 | 3985.7236 | -3612.659
278 | 2024-01-21 13:00 | 2024-01-21 | 372.3122 | 388.0241 | 3968.0365 | 3968.0365 | -3580.0124
279 | 2024-01-21 14:00 | 2024-01-21 | 504.6569 | 357.4163 | 5424.774 | 5424.774 | -5067.3577
280 | 2024-01-21 15:00 | 2024-01-21 | 513.4776 | 215.2668 | 5520.4169 | 5520.4169 | -5305.1501
281 | 2024-01-21 16:00 | 2024-01-21 | 173.2762 | 69.2928 | 1788.6916 | 1788.6916 | -1719.3988
282 | 2024-01-21 17:00 | 2024-01-21 | 56.1826 | 15.5316 | 564.3693 | 564.3693 | -548.8377
283 | 2024-01-21 18:00 | 2024-01-21 | -1.6765 | 1.926 | -16.5861 | 1.926 | 0
284 | 2024-01-21 19:00 | 2024-01-21 | -2.2527 | 1.8349 | -20.57 | 1.8349 | 0
285 | 2024-01-21 20:00 | 2024-01-21 | -2.0888 | 1.7439 | -20.57 | 1.7439 | 0
286 | 2024-01-21 21:00 | 2024-01-21 | -1.8014 | 1.6529 | -17.8205 | 1.6529 | 0
287 | 2024-01-21 22:00 | 2024-01-21 | -1.5863 | 1.5619 | -15.6941 | 1.5619 | 0
288 | 2024-01-21 23:00 | 2024-01-21 | -1.2248 | 1.4709 | -12.1183 | 1.4709 | 0
289 | 2024-01-22 | 2024-01-22 | -1.0172 | 1.3798 | -10.0649 | 1.3798 | 0
290 | 2024-01-22 01:00 | 2024-01-22 | -1.0505 | 1.2888 | -10.3949 | 1.2888 | 0
291 | 2024-01-22 02:00 | 2024-01-22 | -1.0068 | 1.1978 | -9.9621 | 1.1978 | 0
292 | 2024-01-22 03:00 | 2024-01-22 | -1.1628 | 1.1068 | -11.505 | 1.1068 | 0
293 | 2024-01-22 04:00 | 2024-01-22 | -0.75145 | 1.0157 | -7.436 | 1.0157 | 0
294 | 2024-01-22 05:00 | 2024-01-22 | -0.76294 | 0.92471 | -7.5497 | 0.92471 | 0
295 | 2024-01-22 06:00 | 2024-01-22 | -0.75349 | 0.83369 | -7.4562 | 0.83369 | 0
296 | 2024-01-22 07:00 | 2024-01-22 | 4.2641 | 1.0454 | 42.253 | 42.253 | -41.2076
297 | 2024-01-22 08:00 | 2024-01-22 | 140.4148 | 54.3976 | 1439.2146 | 1439.2146 | -1384.817
298 | 2024-01-22 09:00 | 2024-01-22 | 196.1577 | 113.9619 | 2034.3667 | 2034.3667 | -1920.4048
299 | 2024-01-22 10:00 | 2024-01-22 | 332.0421 | 220.6813 | 3522.0172 | 3522.0172 | -3301.3359
300 | 2024-01-22 11:00 | 2024-01-22 | 333.814 | 252.2536 | 3541.6243 | 3541.6243 | -3289.3707
301 | 2024-01-22 12:00 | 2024-01-22 | 618.1843 | 670.5136 | 6628.0812 | 6628.0812 | -5957.5676
302 | 2024-01-22 13:00 | 2024-01-22 | 795.9878 | 2107.9612 | 8311.3768 | 8311.3768 | -6203.4156
303 | 2024-01-22 14:00 | 2024-01-22 | 677.0915 | 4302.111 | 7220.0031 | 7220.0031 | -2917.8921
304 | 2024-01-22 15:00 | 2024-01-22 | 532.3714 | 3879.8062 | 5724.2901 | 5724.2901 | -1844.4839
305 | 2024-01-22 16:00 | 2024-01-22 | 313.5521 | 1731.3683 | 3317.5958 | 3317.5958 | -1586.2274
306 | 2024-01-22 17:00 | 2024-01-22 | 56.8019 | 216.8366 | 570.6799 | 570.6799 | -353.8433
307 | 2024-01-22 18:00 | 2024-01-22 | -0.50426 | 1.1302 | -4.9902 | 1.1302 | 0
308 | 2024-01-22 19:00 | 2024-01-22 | -0.49316 | 0.91124 | -4.8805 | 0.91124 | 0
309 | 2024-01-22 20:00 | 2024-01-22 | -0.60025 | 0.91905 | -5.94 | 0.91905 | 0
310 | 2024-01-22 21:00 | 2024-01-22 | -0.56726 | 0.92686 | -5.6137 | 0.92686 | 0
311 | 2024-01-22 22:00 | 2024-01-22 | -0.45099 | 0.93468 | -4.4632 | 0.93468 | 0
312 | 2024-01-22 23:00 | 2024-01-22 | -0.35235 | 0.94249 | -3.487 | 0.94249 | 0
313 | 2024-01-23 | 2024-01-23 | -0.2398 | 0.95031 | -2.3733 | 0.95031 | 0
314 | 2024-01-23 01:00 | 2024-01-23 | -0.23385 | 0.95812 | -2.3145 | 0.95812 | 0
315 | 2024-01-23 02:00 | 2024-01-23 | -0.43231 | 0.96593 | -4.2783 | 0.96593 | 0
316 | 2024-01-23 03:00 | 2024-01-23 | -0.36598 | 0.97375 | -3.622 | 0.97375 | 0
317 | 2024-01-23 04:00 | 2024-01-23 | -0.014704 | 0.98156 | -0.14553 | 0.98156 | 0
318 | 2024-01-23 05:00 | 2024-01-23 | -0.0021995 | 0.98938 | -0.021769 | 0.98938 | 0
319 | 2024-01-23 06:00 | 2024-01-23 | -0.0026397 | 0.99719 | -0.026126 | 0.99719 | 0
320 | 2024-01-23 07:00 | 2024-01-23 | 0.19798 | 1.0065 | 1.9596 | 1.9596 | -0.95311
321 | 2024-01-23 08:00 | 2024-01-23 | 11.9926 | 77.0979 | 119.0837 | 119.0837 | -41.9858
322 | 2024-01-23 09:00 | 2024-01-23 | 34.2581 | 281.0161 | 342.1891 | 342.1891 | -61.173
323 | 2024-01-23 10:00 | 2024-01-23 | 41.0669 | 344.1618 | 410.9285 | 410.9285 | -66.7666
324 | 2024-01-23 11:00 | 2024-01-23 | 96.1134 | 807.7981 | 975.0743 | 975.0743 | -167.2761
325 | 2024-01-23 12:00 | 2024-01-23 | 72.996 | 634.057 | 736.3727 | 736.3727 | -102.3157
326 | 2024-01-23 13:00 | 2024-01-23 | 65.1979 | 565.6695 | 656.4261 | 656.4261 | -90.7565
327 | 2024-01-23 14:00 | 2024-01-23 | 64.4873 | 561.9935 | 649.1555 | 649.1555 | -87.162
328 | 2024-01-23 15:00 | 2024-01-23 | 25.9988 | 210.4592 | 259.1272 | 259.1272 | -48.668
329 | 2024-01-23 16:00 | 2024-01-23 | 46.5632 | 388.5192 | 466.5887 | 466.5887 | -78.0695
330 | 2024-01-23 17:00 | 2024-01-23 | 14.7419 | 106.0798 | 146.4911 | 146.4911 | -40.4114
331 | 2024-01-23 18:00 | 2024-01-23 | 0.17608 | 0.61256 | 1.7428 | 1.7428 | -1.1303
332 | 2024-01-23 19:00 | 2024-01-23 | -0.1812 | 0.64455 | -1.7934 | 0.64455 | 0
333 | 2024-01-23 20:00 | 2024-01-23 | -0.25952 | 0.67654 | -2.5684 | 0.67654 | 0
334 | 2024-01-23 21:00 | 2024-01-23 | -0.18161 | 0.70853 | -1.7974 | 0.70853 | 0
335 | 2024-01-23 22:00 | 2024-01-23 | -0.1545 | 0.74051 | -1.5291 | 0.74051 | 0
336 | 2024-01-23 23:00 | 2024-01-23 | -0.047708 | 0.7725 | -0.47219 | 0.7725 | 0
337 | 2024-01-24 | 2024-01-24 | -0.14118 | 0.80449 | -1.3973 | 0.80449 | 0
338 | 2024-01-24 01:00 | 2024-01-24 | -0.18038 | 0.83647 | -1.7853 | 0.83647 | 0
339 | 2024-01-24 02:00 | 2024-01-24 | -0.23708 | 0.86846 | -2.3464 | 0.86846 | 0
340 | 2024-01-24 03:00 | 2024-01-24 | -0.25498 | 0.90045 | -2.5235 | 0.90045 | 0
341 | 2024-01-24 04:00 | 2024-01-24 | -0.17498 | 0.93244 | -1.7318 | 0.93244 | 0
342 | 2024-01-24 05:00 | 2024-01-24 | -0.18346 | 0.96442 | -1.8157 | 0.96442 | 0
343 | 2024-01-24 06:00 | 2024-01-24 | -0.024557 | 0.99641 | -0.24305 | 0.99641 | 0
344 | 2024-01-24 07:00 | 2024-01-24 | 0.02126 | 1.0284 | 0.21042 | 0.21042 | 0.81798
345 | 2024-01-24 08:00 | 2024-01-24 | 3.454 | 2.2489 | 34.2184 | 34.2184 | -31.9695
346 | 2024-01-24 09:00 | 2024-01-24 | 12.6685 | 78.4934 | 125.818 | 125.818 | -47.3246
347 | 2024-01-24 10:00 | 2024-01-24 | 42.6205 | 353.881 | 426.6463 | 426.6463 | -72.7652
348 | 2024-01-24 11:00 | 2024-01-24 | 47.3212 | 357.6875 | 474.2766 | 474.2766 | -116.5892
349 | 2024-01-24 12:00 | 2024-01-24 | 44.8423 | 334.2292 | 449.1446 | 449.1446 | -114.9155
350 | 2024-01-24 13:00 | 2024-01-24 | 79.4013 | 605.9958 | 802.26 | 802.26 | -196.2642
351 | 2024-01-24 14:00 | 2024-01-24 | 62.3704 | 461.8104 | 627.5111 | 627.5111 | -165.7007
352 | 2024-01-24 15:00 | 2024-01-24 | 33.1089 | 235.484 | 330.6111 | 330.6111 | -95.1271
353 | 2024-01-24 16:00 | 2024-01-24 | 14.403 | 95.4873 | 143.1111 | 143.1111 | -47.6238
354 | 2024-01-24 17:00 | 2024-01-24 | 3.8178 | 15.8389 | 37.8263 | 37.8263 | -21.9874
355 | 2024-01-24 18:00 | 2024-01-24 | -0.089616 | 3.1141 | -0.88696 | 3.1141 | 0
356 | 2024-01-24 19:00 | 2024-01-24 | -0.16204 | 3.0086 | -1.6037 | 3.0086 | 0
357 | 2024-01-24 20:00 | 2024-01-24 | -0.17561 | 2.9031 | -1.738 | 2.9031 | 0
358 | 2024-01-24 21:00 | 2024-01-24 | 0.16129 | 2.7976 | 1.5965 | 1.5965 | 1.2011
359 | 2024-01-24 22:00 | 2024-01-24 | -0.10395 | 2.692 | -1.0288 | 2.692 | 0
360 | 2024-01-24 23:00 | 2024-01-24 | 0.10458 | 2.5865 | 1.0351 | 1.0351 | 1.5514
Formulas:
Notes = INT([Value])