## Indices
System Values (Excluding MEDs)
| SAIDI | SAIFI | CAIFI | CAIDI | # of customers | duration of outages (mins) | # of customer interruptions
2016 | 65.6017 | 0.6811 | N/A2 | 96.3173 | 29689 | 1947648.8713 | 20221.1779
2017 | 121.105 | 1.1 | N/A2 | 110.0955 | 29752 | 3603115.96 | 32727.2
2018 | 122.816 | 1.212 | N/A2 | 101.3333 | 29752 | 3654021.632 | 36059.424
2019 | 137.356 | 1.562 | N/A2 | 87.936 | 30044 | 4126723.664 | 46928.728
2020 | 93.058 | 1.185 | N/A2 | 78.53 | 30337 | 2823100.546 | 35949.345
2021 | 130.653 | 1.416 | N/A2 | 92.2691 | 30417 | 3974072.301 | 43070.472
2022 | 134.37 | 1.611 | N/A2 | 83.4078 | 30506 | 4099091.22 | 49145.166
2023 | 153.59 | 1.656 | N/A2 | 92.7476 | 30586 | 4697703.74 | 50650.416
2024 YTD1 | 246.551 | 0.817 | N/A2 | 301.8033 | 30687 | 7565907 | 25069
1MEDs are not excluded for the 2024 YTD indices.
2NISC, our OMS vendor, does not provide this metric. We've requested it moving forward.

## 2024 YTD Circuit Details
JACKSON PURCHASE ENERGY CORP.
Rev: 202306200609
| 2024-05-29 | 10:19 | [5 empty] | ANNUAL RELIABILITY REPORT
2024
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | BURNA | [5 empty] | 100 | Contractor - Planned |  | 2 | 66.67 | 2 | 210.6 | 67.76
| Feeder Name: | Hampton | [5 empty] | 300 | Equipment Failure |  | 1 | 33.33 | 1 | 100.2 | 32.24
| Feeder Number: | 214
| Feeder Location | 14214-Hampton
| Customer Count | 85
| Circuit 5 Year Average (SAIDI |  |  |  | 94.5166
| Reporting Year (SAIDI |  | 2.4676
| Circuit 5 Year Average (SAIFI |  |  |  | 0.3499
| Reporting Year (SAIFI |  | 0.0235
| Total Circuit Length: |  |  |  |  | 11.8
| Date of Last Circuit Trim: |  |  |  |  | 2019
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | BURNA | [5 empty] | 100 | Contractor - Planned |  | 7 | 50 | 12 | 1386 | 6.69
| Feeder Name: | Salem | [5 empty] | 300 | Equipment Failure |  | 1 | 7.14 | 2 | 279.6 | 1.35
[8 empty] | 420 | ROW |  | 2 | 14.29 | 38 | 17485.2 | 84.44
| Feeder Number: | 244
[8 empty] | 500 | Lightning |  | 1 | 7.14 | 1 | 53.4 | 0.26
| Feeder Location | 14244-Salem | [5 empty] | 700 | Member/Public Caused |  | 1 | 7.14 | 1 | 50.4 | 0.24
| Customer Count | 325 | [5 empty] | 810 | Load |  | 1 | 7.14 | 1 | 99 | 0.48
| Circuit 5 Year Average (SAIDI |  |  |  | 129.9194 |  |  | 999 | Cause unknown |  | 1 | 7.14 | 17 | 1353 | 6.53
| Reporting Year (SAIDI |  | 53.8641
| Circuit 5 Year Average (SAIFI |  |  |  | 0.5958
| Reporting Year (SAIFI |  | 0.1171
| Total Circuit Length: |  |  |  |  | 52.9
| Date of Last Circuit Trim: |  |  |  |  | 2019
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | BURNA | [5 empty] | 300 | Equipment Failure |  | 3 | 21.43 | 6 | 645 | 1.15
| Feeder Name: | Smithland | [5 empty] | 420 | ROW |  | 4 | 28.57 | 386 | 27830.4 | 49.43
[8 empty] | 500 | Lightning |  | 4 | 28.57 | 51 | 7125 | 12.65
| Feeder Number: | 254
[8 empty] | 710 | Motor Vehicle |  | 1 | 7.14 | 2 | 693.6 | 1.23
| Feeder Location | 14254-Smithland | [5 empty] | 999 | Cause unknown |  | 2 | 14.29 | 83 | 20014.2 | 35.54
| Customer Count | 350
| Circuit 5 Year Average (SAIDI |  |  |  | 255.6176
| Reporting Year (SAIDI |  | 79.5221
| Circuit 5 Year Average (SAIFI |  |  |  | 2.1116
| Reporting Year (SAIFI |  | 1.103
| Total Circuit Length: |  |  |  |  | 69.7
| Date of Last Circuit Trim: |  |  |  |  | 2019
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | CALVERT CITY | [5 empty] | 110 | JPEC - Planned |  | 1 | 14.29 | 46 | 4314 | 13.47
| Feeder Name: | Hwy 95 | [5 empty] | 420 | ROW |  | 4 | 57.14 | 67 | 27492 | 85.84
[8 empty] | 690 | Animal |  | 2 | 28.57 | 4 | 220.2 | 0.69
| Feeder Number: | 214
| Feeder Location | 43214-Hwy 95
| Customer Count | 250
| Circuit 5 Year Average (SAIDI |  |  |  | 75.9075
| Reporting Year (SAIDI |  | 109.9535
| Circuit 5 Year Average (SAIFI |  |  |  | 0.5407
| Reporting Year (SAIFI |  | 0.268
| Total Circuit Length: |  |  |  |  | 18.9
| Date of Last Circuit Trim: |  |  |  |  | 2017
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | CALVERT CITY | [5 empty] | 100 | Contractor - Planned |  | 1 | 6.67 | 6 | 499.8 | 0.23
| Feeder Name: | Calvert Heights | [5 empty] | 300 | Equipment Failure |  | 1 | 6.67 | 36 | 2095.8 | 0.94
[8 empty] | 420 | ROW |  | 3 | 20 | 48 | 2658 | 1.2
| Feeder Number: | 224
[8 empty] | 500 | Lightning |  | 1 | 6.67 | 665 | 209308.8 | 94.3
| Feeder Location | 43224-Calvert Height | [5 empty] | 690 | Animal |  | 6 | 40 | 53 | 3253.2 | 1.47
| Customer Count | 649 | [5 empty] | 700 | Member/Public Caused |  | 1 | 6.67 | 1 | 80.4 | 0.04
| Circuit 5 Year Average (SAIDI |  |  |  | 129.1813 |  |  | 999 | Cause unknown |  | 2 | 13.33 | 72 | 4064.4 | 1.83
| Reporting Year (SAIDI |  | 322.3408
| Circuit 5 Year Average (SAIFI |  |  |  | 1.0583
| Reporting Year (SAIFI |  | 1.0241
| Total Circuit Length: |  |  |  |  | 28.1
| Date of Last Circuit Trim: |  |  |  |  | 2017
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | CALVERT CITY | [5 empty] | 110 | JPEC - Planned |  | 1 | 11.11 | 2 | 19.8 | 0.24
| Feeder Name: | Gilbertsville | [5 empty] | 420 | ROW |  | 3 | 33.33 | 11 | 1998 | 24.22
[8 empty] | 500 | Lightning |  | 1 | 11.11 | 9 | 4202.4 | 50.95
| Feeder Number: | 234
[8 empty] | 690 | Animal |  | 3 | 33.33 | 32 | 1873.2 | 22.71
| Feeder Location | 43234-Gilbertsville | [5 empty] | 999 | Cause unknown |  | 1 | 11.11 | 2 | 155.4 | 1.88
| Customer Count | 340
| Circuit 5 Year Average (SAIDI |  |  |  | 52.3556
| Reporting Year (SAIDI |  | 12.3466
| Circuit 5 Year Average (SAIFI |  |  |  | 0.51
| Reporting Year (SAIFI |  | 0.094
| Total Circuit Length: |  |  |  |  | 23.7
| Date of Last Circuit Trim: |  |  |  |  | 2017
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | CALVERT CITY | [5 empty] | 500 | Lightning |  | 1 | 100 | 25 | 15187.8 | 100
| Feeder Name: | Industrial Park
| Feeder Number: | 244
| Feeder Location | 43244-Industrial Park
| Customer Count | 25
| Circuit 5 Year Average (SAIDI |  |  |  | 152.8249
| Reporting Year (SAIDI |  | 614.6297
| Circuit 5 Year Average (SAIFI |  |  |  | 0.4452
| Reporting Year (SAIFI |  | 1.0117
| Total Circuit Length: |  |  |  |  | 5
| Date of Last Circuit Trim: |  |  |  |  | 2017
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | COLEMAN ROAD | [5 empty] | 420 | ROW |  | 4 | 80 | 226 | 47334 | 99.93
| Feeder Name: | Conrad Heights | [5 empty] | 690 | Animal |  | 1 | 20 | 1 | 34.2 | 0.07
| Feeder Number: | 224
| Feeder Location | 30224-Conrad Height
| Customer Count | 370
| Circuit 5 Year Average (SAIDI |  |  |  | 188.681
| Reporting Year (SAIDI |  | 127.8164
| Circuit 5 Year Average (SAIFI |  |  |  | 1.6979
| Reporting Year (SAIFI |  | 0.6103
| Total Circuit Length: |  |  |  |  | 18.1
| Date of Last Circuit Trim: |  |  |  |  | 2018
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | COLEMAN ROAD | [5 empty] | 100 | Contractor - Planned |  | 1 | 50 | 3 | 858 | 91.96
| Feeder Name: | Hwy 60 Business | [5 empty] | 420 | ROW |  | 1 | 50 | 1 | 75 | 8.04
| Feeder Number: | 244
| Feeder Location | 30244-Hwy 60 Busin
| Customer Count | 104
| Circuit 5 Year Average (SAIDI |  |  |  | 54.1264
| Reporting Year (SAIDI |  | 8.2294
| Circuit 5 Year Average (SAIFI |  |  |  | 0.7385
| Reporting Year (SAIFI |  | 0.0288
| Total Circuit Length: |  |  |  |  | 7.7
| Date of Last Circuit Trim: |  |  |  |  | 2018
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | COLEMAN ROAD | [5 empty] | None | None |  | 0 | 0 | 0 | 0 | 0
| Feeder Name: | KY Oaks Mall
| Feeder Number: | 254
| Feeder Location | 30254-KY Oaks Mall
| Customer Count | 79
| Circuit 5 Year Average (SAIDI |  |  |  | 49.7671
| Reporting Year (SAIDI |  | 0
| Circuit 5 Year Average (SAIFI |  |  |  | 0.405
| Reporting Year (SAIFI |  | 0
| Total Circuit Length: |  |  |  |  | 3.9
| Date of Last Circuit Trim: |  |  |  |  | 2018
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | CULP | [5 empty] | 100 | Contractor - Planned |  | 2 | 28.57 | 6 | 466.2 | 6.01
| Feeder Name: | Proform | [5 empty] | 420 | ROW |  | 2 | 28.57 | 9 | 6352.2 | 81.94
[8 empty] | 690 | Animal |  | 3 | 42.86 | 17 | 933.6 | 12.04
| Feeder Number: | 214
| Feeder Location | 42214-Proform
| Customer Count | 428
| Circuit 5 Year Average (SAIDI |  |  |  | 107.0646
| Reporting Year (SAIDI |  | 14.8472
| Circuit 5 Year Average (SAIFI |  |  |  | 1.1009
| Reporting Year (SAIFI |  | 0.0397
| Total Circuit Length: |  |  |  |  | 25.8
| Date of Last Circuit Trim: |  |  |  |  | 2018
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | CULP | [5 empty] | 420 | ROW |  | 4 | 100 | 6 | 2964 | 100
| Feeder Name: | Little Cypress
| Feeder Number: | 224
| Feeder Location | 42224-Little Cypress
| Customer Count | 49
| Circuit 5 Year Average (SAIDI |  |  |  | 94.5248
| Reporting Year (SAIDI |  | 60.757
| Circuit 5 Year Average (SAIFI |  |  |  | 1.1191
| Reporting Year (SAIFI |  | 0.123
| Total Circuit Length: |  |  |  |  | 8.1
| Date of Last Circuit Trim: |  |  |  |  | 2018
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | CULP | [5 empty] | 100 | Contractor - Planned |  | 6 | 42.86 | 11 | 1273.2 | 6.52
| Feeder Name: | Possum Trot | [5 empty] | 300 | Equipment Failure |  | 1 | 7.14 | 1 | 32.4 | 0.17
[8 empty] | 420 | ROW |  | 4 | 28.57 | 122 | 14736.6 | 75.51
| Feeder Number: | 234
[8 empty] | 690 | Animal |  | 2 | 14.29 | 17 | 664.2 | 3.4
| Feeder Location | 42234-Possum Trot | [5 empty] | 700 | Member/Public Caused |  | 1 | 7.14 | 33 | 2809.8 | 14.4
| Customer Count | 203
| Circuit 5 Year Average (SAIDI |  |  |  | 200.6856
| Reporting Year (SAIDI |  | 72.5407
| Circuit 5 Year Average (SAIFI |  |  |  | 1.9414
| Reporting Year (SAIFI |  | 0.6005
| Total Circuit Length: |  |  |  |  | 18.7
| Date of Last Circuit Trim: |  |  |  |  | 2018
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | CULP | [5 empty] | 100 | Contractor - Planned |  | 29 | 56.86 | 60 | 6933 | 10.07
| Feeder Name: | Sharpe | [5 empty] | 300 | Equipment Failure |  | 3 | 5.88 | 104 | 8417.4 | 12.23
[8 empty] | 420 | ROW |  | 11 | 21.57 | 147 | 51807.6 | 75.25
| Feeder Number: | 244
[8 empty] | 690 | Animal |  | 7 | 13.73 | 29 | 1520.4 | 2.21
| Feeder Location | 42244-Sharpe | [5 empty] | 999 | Cause unknown |  | 1 | 1.96 | 2 | 165.6 | 0.24
| Customer Count | 1111
| Circuit 5 Year Average (SAIDI |  |  |  | 166.2662
| Reporting Year (SAIDI |  | 46.6373
| Circuit 5 Year Average (SAIFI |  |  |  | 1.7314
| Reporting Year (SAIFI |  | 0.1323
| Total Circuit Length: |  |  |  |  | 79.9
| Date of Last Circuit Trim: |  |  |  |  | 2018
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | CUMBERLAND JPEC | [5 empty] | 100 | Contractor - Planned |  | 1 | 20 | 1 | 45 | 0.2
| Feeder Name: | Pinckneyville | [5 empty] | 300 | Equipment Failure |  | 1 | 20 | 1 | 98.4 | 0.44
[8 empty] | 420 | ROW |  | 2 | 40 | 119 | 20788.2 | 92.81
| Feeder Number: | 224
[8 empty] | 700 | Member/Public Caused |  | 1 | 20 | 7 | 1468.2 | 6.55
| Feeder Location | 15224-Pinckneyville
| Customer Count | 115
| Circuit 5 Year Average (SAIDI |  |  |  | 255.7543
| Reporting Year (SAIDI |  | 181.1321
| Circuit 5 Year Average (SAIFI |  |  |  | 2.1591
| Reporting Year (SAIFI |  | 1.0369
| Total Circuit Length: |  |  |  |  | 27.6
| Date of Last Circuit Trim: |  |  |  |  | 2019
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | CUMBERLANDQUA | [5 empty] | None | None |  | 0 | 0 | 0 | 0 | 0
| Feeder Name: | Quarry
| Feeder Number: | 234
| Feeder Location | 15234-Quarry
| Customer Count | 31
| Circuit 5 Year Average (SAIDI |  |  |  | 214.2021
| Reporting Year (SAIDI |  | 0
| Circuit 5 Year Average (SAIFI |  |  |  | 1.6607
| Reporting Year (SAIFI |  | 0
| Total Circuit Length: |  |  |  |  | 5.5
| Date of Last Circuit Trim: |  |  |  |  | 2019
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | DRAFFENVILLE | [5 empty] | 100 | Contractor - Planned |  | 9 | 69.23 | 23 | 3485.4 | 22.21
| Feeder Name: | Draffenville | [5 empty] | 300 | Equipment Failure |  | 1 | 7.69 | 1 | 562.2 | 3.58
[8 empty] | 420 | ROW |  | 2 | 15.38 | 19 | 11596.2 | 73.9
| Feeder Number: | 214
[8 empty] | 999 | Cause unknown |  | 1 | 7.69 | 1 | 48 | 0.31
| Feeder Location | 66214-Draffenville
| Customer Count | 491
| Circuit 5 Year Average (SAIDI |  |  |  | 111.3275
| Reporting Year (SAIDI |  | 23.6249
| Circuit 5 Year Average (SAIFI |  |  |  | 0.8789
| Reporting Year (SAIFI |  | 0.0469
| Total Circuit Length: |  |  |  |  | 28.8
| Date of Last Circuit Trim: |  |  |  |  | 2019
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | FREEMONT | [5 empty] | 100 | Contractor - Planned |  | 16 | 25.81 | 26 | 3021.6 | 0.12
| Feeder Name: | Symsonia | [5 empty] | 110 | JPEC - Planned |  | 1 | 1.61 | 517 | 78006.6 | 3.07
[8 empty] | 300 | Equipment Failure |  | 6 | 9.68 | 191 | 28540.8 | 1.12
| Feeder Number: | 214
[8 empty] | 420 | ROW |  | 25 | 40.32 | 1539 | 455057.4 | 17.92
| Feeder Location | 51214-Symsonia | [5 empty] | 500 | Lightning |  | 6 | 9.68 | 47 | 32397 | 1.28
| Customer Count | 1012 | [5 empty] | 510 | Wind - Not Trees |  | 1 | 1.61 | 254 | 1940505.6 | 76.4
| Circuit 5 Year Average (SAIDI |  |  |  | 683.7901 |  |  | 690 | Animal |  | 4 | 6.45 | 5 | 319.8 | 0.01
| Reporting Year (SAIDI |  | 1917.6093 |  |  |  |  | 999 | Cause unknown |  | 3 | 4.84 | 30 | 2225.4 | 0.09
| Circuit 5 Year Average (SAIFI |  |  |  | 2.6314
| Reporting Year (SAIFI |  | 1.9794
| Total Circuit Length: |  |  |  |  | 93.8
| Date of Last Circuit Trim: |  |  |  |  | 2019
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | FREEMONT | [5 empty] | 100 | Contractor - Planned |  | 11 | 55 | 21 | 2752.2 | 1.52
| Feeder Name: | McNeil Lane | [5 empty] | 300 | Equipment Failure |  | 1 | 5 | 1 | 112.8 | 0.06
[8 empty] | 420 | ROW |  | 6 | 30 | 260 | 176757 | 97.79
| Feeder Number: | 224
[8 empty] | 510 | Wind - Not Trees |  | 1 | 5 | 5 | 470.4 | 0.26
| Feeder Location | 51224-McNeil Lane | [5 empty] | 690 | Animal |  | 1 | 5 | 9 | 658.2 | 0.36
| Customer Count | 334
| Circuit 5 Year Average (SAIDI |  |  |  | 503.8935
| Reporting Year (SAIDI |  | 529.2273
| Circuit 5 Year Average (SAIFI |  |  |  | 0.8437
| Reporting Year (SAIFI |  | 0.7785
| Total Circuit Length: |  |  |  |  | 41
| Date of Last Circuit Trim: |  |  |  |  | 2019
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | FREEMONT | [5 empty] | 100 | Contractor - Planned |  | 1 | 10 | 1 | 147.6 | 0.38
| Feeder Name: | Freemont | [5 empty] | 300 | Equipment Failure |  | 1 | 10 | 34 | 5463.6 | 14.01
[8 empty] | 420 | ROW |  | 1 | 10 | 24 | 5118.6 | 13.12
| Feeder Number: | 244
[8 empty] | 500 | Lightning |  | 3 | 30 | 9 | 852 | 2.18
| Feeder Location | 51244-Freemont | [5 empty] | 690 | Animal |  | 1 | 10 | 1 | 304.8 | 0.78
| Customer Count | 334 | [5 empty] | 999 | Cause unknown |  | 3 | 30 | 113 | 27118.2 | 69.53
| Circuit 5 Year Average (SAIDI |  |  |  | 117.0084
| Reporting Year (SAIDI |  | 81.1496
| Circuit 5 Year Average (SAIFI |  |  |  | 0.9791
| Reporting Year (SAIFI |  | 0.3382
| Total Circuit Length: |  |  |  |  | 25.2
| Date of Last Circuit Trim: |  |  |  |  | 2019
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | FREEMONT | [5 empty] | 100 | Contractor - Planned |  | 4 | 57.14 | 128 | 1133.4 | 3.18
| Feeder Name: | Bonds Rd | [5 empty] | 420 | ROW |  | 2 | 28.57 | 128 | 30841.2 | 86.62
[8 empty] | 510 | Wind - Not Trees |  | 1 | 14.29 | 25 | 3631.8 | 10.2
| Feeder Number: | 254
| Feeder Location | 51254-Bonds Rd
| Customer Count | 127
| Circuit 5 Year Average (SAIDI |  |  |  | 688.5878
| Reporting Year (SAIDI |  | 242.6521
| Circuit 5 Year Average (SAIFI |  |  |  | 2.0566
| Reporting Year (SAIFI |  | 1.0071
| Total Circuit Length: |  |  |  |  | 17.3
| Date of Last Circuit Trim: |  |  |  |  | 2019
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | GRAND RIVERS | [5 empty] | 300 | Equipment Failure |  | 4 | 18.18 | 5 | 509.4 | 0.4
| Feeder Name: | Iuka | [5 empty] | 420 | ROW |  | 14 | 63.64 | 391 | 124063.8 | 98.27
[8 empty] | 500 | Lightning |  | 2 | 9.09 | 12 | 1561.8 | 1.24
| Feeder Number: | 214
[8 empty] | 690 | Animal |  | 2 | 9.09 | 2 | 112.2 | 0.09
| Feeder Location | 76214-Iuka
| Customer Count | 301
| Circuit 5 Year Average (SAIDI |  |  |  | 407.2162
| Reporting Year (SAIDI |  | 412.5021
| Circuit 5 Year Average (SAIFI |  |  |  | 1.8932
| Reporting Year (SAIFI |  | 1.3
| Total Circuit Length: |  |  |  |  | 48.5
| Date of Last Circuit Trim: |  |  |  |  | 2016
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | GRAND RIVERS | [5 empty] | 100 | Contractor - Planned |  | 1 | 12.5 | 8 | 643.8 | 1.88
| Feeder Name: | Smithland | [5 empty] | 420 | ROW |  | 3 | 37.5 | 363 | 31446 | 92.07
[8 empty] | 690 | Animal |  | 3 | 37.5 | 5 | 307.8 | 0.9
| Feeder Number: | 224
[8 empty] | 999 | Cause unknown |  | 1 | 12.5 | 32 | 1757.4 | 5.15
| Feeder Location | 76224-Smithland
| Customer Count | 312
| Circuit 5 Year Average (SAIDI |  |  |  | 4568.9014
| Reporting Year (SAIDI |  | 100.7264
| Circuit 5 Year Average (SAIFI |  |  |  | 1.4427
| Reporting Year (SAIFI |  | 1.1628
| Total Circuit Length: |  |  |  |  | 31.4
| Date of Last Circuit Trim: |  |  |  |  | 2016
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | GRAND RIVERS | [5 empty] | 110 | JPEC - Planned |  | 4 | 40 | 6 | 473.4 | 0.64
| Feeder Name: | Pelican GR #1 | [5 empty] | 300 | Equipment Failure |  | 1 | 10 | 2 | 132.6 | 0.18
[8 empty] | 420 | ROW |  | 2 | 20 | 72 | 72229.2 | 97.16
| Feeder Number: | 244
[8 empty] | 500 | Lightning |  | 1 | 10 | 7 | 977.4 | 1.31
| Feeder Location | 76244-Pelican GR #1 | [5 empty] | 690 | Animal |  | 1 | 10 | 3 | 466.2 | 0.63
| Customer Count | 379 | [5 empty] | 810 | Load |  | 1 | 10 | 1 | 61.2 | 0.08
| Circuit 5 Year Average (SAIDI |  |  |  | 162.9579
| Reporting Year (SAIDI |  | 190.5884
| Circuit 5 Year Average (SAIFI |  |  |  | 0.8745
| Reporting Year (SAIFI |  | 0.19
| Total Circuit Length: |  |  |  |  | 23.9
| Date of Last Circuit Trim: |  |  |  |  | 2016
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | GRAND RIVERS | [5 empty] | 110 | JPEC - Planned |  | 3 | 25 | 10 | 709.2 | 0.19
| Feeder Name: | Averitt GR #2 | [5 empty] | 300 | Equipment Failure |  | 3 | 25 | 1377 | 266983.2 | 71.81
[8 empty] | 690 | Animal |  | 6 | 50 | 712 | 104110.8 | 28
| Feeder Number: | 254
| Feeder Location | 76254-Averitt GR #2
| Customer Count | 673
| Circuit 5 Year Average (SAIDI |  |  |  | 451.2613
| Reporting Year (SAIDI |  | 396.8123
| Circuit 5 Year Average (SAIFI |  |  |  | 3.3043
| Reporting Year (SAIFI |  | 2.0466
| Total Circuit Length: |  |  |  |  | 46.4
| Date of Last Circuit Trim: |  |  |  |  | 2022
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | HIGHPOINT | [5 empty] | 300 | Equipment Failure |  | 1 | 11.11 | 2 | 154.2 | 0.62
| Feeder Name: | High Point | [5 empty] | 420 | ROW |  | 5 | 55.56 | 51 | 6140.4 | 24.58
[8 empty] | 500 | Lightning |  | 1 | 11.11 | 189 | 18512.4 | 74.1
| Feeder Number: | 214
[8 empty] | 690 | Animal |  | 1 | 11.11 | 2 | 85.2 | 0.34
| Feeder Location | 29214-High Point | [5 empty] | 999 | Cause unknown |  | 1 | 11.11 | 2 | 89.4 | 0.36
| Customer Count | 192
| Circuit 5 Year Average (SAIDI |  |  |  | 101.9162
| Reporting Year (SAIDI |  | 96.4999
| Circuit 5 Year Average (SAIFI |  |  |  | 0.9675
| Reporting Year (SAIFI |  | 0.9852
| Total Circuit Length: |  |  |  |  | 20.9
| Date of Last Circuit Trim: |  |  |  |  | 2015
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | HIGHPOINT | [5 empty] | 300 | Equipment Failure |  | 1 | 100 | 1 | 57.6 | 100
| Feeder Name: | Carneal Rd
| Feeder Number: | 224
| Feeder Location | 29224-Carneal Rd
| Customer Count | 243
| Circuit 5 Year Average (SAIDI |  |  |  | 312.5247
| Reporting Year (SAIDI |  | 0.2364
| Circuit 5 Year Average (SAIFI |  |  |  | 2.8931
| Reporting Year (SAIFI |  | 0.0041
| Total Circuit Length: |  |  |  |  | 33.1
| Date of Last Circuit Trim: |  |  |  |  | 2023
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | HUSBANDS ROAD | [5 empty] | 100 | Contractor - Planned |  | 2 | 11.11 | 7 | 1324.8 | 1.99
| Feeder Name: | Husbands Rd | [5 empty] | 110 | JPEC - Planned |  | 2 | 11.11 | 9 | 1104.6 | 1.66
[8 empty] | 300 | Equipment Failure |  | 1 | 5.56 | 1 | 19.2 | 0.03
| Feeder Number: | 224
[8 empty] | 420 | ROW |  | 8 | 44.44 | 192 | 61905 | 93.12
| Feeder Location | 40224-Husbands Rd | [5 empty] | 690 | Animal |  | 3 | 16.67 | 42 | 1744.8 | 2.62
| Customer Count | 778 | [5 empty] | 700 | Member/Public Caused |  | 1 | 5.56 | 1 | 99.6 | 0.15
| Circuit 5 Year Average (SAIDI |  |  |  | 82.4059 |  |  | 810 | Load |  | 1 | 5.56 | 3 | 279.6 | 0.42
| Reporting Year (SAIDI |  | 79.5721
| Circuit 5 Year Average (SAIFI |  |  |  | 0.619
| Reporting Year (SAIFI |  | 0.2468
| Total Circuit Length: |  |  |  |  | 44.7
| Date of Last Circuit Trim: |  |  |  |  | 2018
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | HUSBANDS ROAD | [5 empty] | 110 | JPEC - Planned |  | 1 | 25 | 4 | 446.4 | 0.28
| Feeder Name: | Lydon Rd | [5 empty] | 420 | ROW |  | 2 | 50 | 481 | 157976.4 | 99.43
[8 empty] | 500 | Lightning |  | 1 | 25 | 1 | 460.2 | 0.29
| Feeder Number: | 234
| Feeder Location | 40234-Lydon Rd
| Customer Count | 457
| Circuit 5 Year Average (SAIDI |  |  |  | 208.7587
| Reporting Year (SAIDI |  | 345.5144
| Circuit 5 Year Average (SAIFI |  |  |  | 1.5642
| Reporting Year (SAIFI |  | 1.052
| Total Circuit Length: |  |  |  |  | 32.2
| Date of Last Circuit Trim: |  |  |  |  | 2018
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | HUSBANDS ROAD | [5 empty] | 300 | Equipment Failure |  | 4 | 40 | 58 | 4745.4 | 1.95
| Feeder Name: | Clarkline Rd | [5 empty] | 420 | ROW |  | 4 | 40 | 356 | 234312.6 | 96.44
[8 empty] | 510 | Wind - Not Trees |  | 1 | 10 | 51 | 3864 | 1.59
| Feeder Number: | 244
[8 empty] | 690 | Animal |  | 1 | 10 | 2 | 51.6 | 0.02
| Feeder Location | 40244-Clarkline Rd
| Customer Count | 359
| Circuit 5 Year Average (SAIDI |  |  |  | 278.2464
| Reporting Year (SAIDI |  | 652.3001
| Circuit 5 Year Average (SAIFI |  |  |  | 2.7772
| Reporting Year (SAIFI |  | 0.9911
| Total Circuit Length: |  |  |  |  | 26.4
| Date of Last Circuit Trim: |  |  |  |  | 2018
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | JOY | [5 empty] | 300 | Equipment Failure |  | 2 | 25 | 2 | 307.8 | 0.28
| Feeder Name: | Hampton South | [5 empty] | 420 | ROW |  | 5 | 62.5 | 342 | 111320.4 | 99.61
[8 empty] | 690 | Animal |  | 1 | 12.5 | 1 | 128.4 | 0.11
| Feeder Number: | 214
| Feeder Location | 05214-Hampton Sout
| Customer Count | 183
| Circuit 5 Year Average (SAIDI |  |  |  | 626.3303
| Reporting Year (SAIDI |  | 607.5437
| Circuit 5 Year Average (SAIFI |  |  |  | 2.8489
| Reporting Year (SAIFI |  | 1.8665
| Total Circuit Length: |  |  |  |  | 57.6
| Date of Last Circuit Trim: |  |  |  |  | 2023
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | JOY | [5 empty] | 110 | JPEC - Planned |  | 1 | 50 | 2 | 56.4 | 0.82
| Feeder Name: | Carrsville | [5 empty] | 420 | ROW |  | 1 | 50 | 70 | 6852 | 99.18
| Feeder Number: | 244
| Feeder Location | 05244-Carrsville
| Customer Count | 71
| Circuit 5 Year Average (SAIDI |  |  |  | 114.3068
| Reporting Year (SAIDI |  | 96.9005
| Circuit 5 Year Average (SAIFI |  |  |  | 0.8853
| Reporting Year (SAIFI |  | 0.99
| Total Circuit Length: |  |  |  |  | 10.8
| Date of Last Circuit Trim: |  |  |  |  | 2016
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | JOY | [5 empty] | 110 | JPEC - Planned |  | 1 | 11.11 | 6 | 609 | 6.1
| Feeder Name: | Lola | [5 empty] | 300 | Equipment Failure |  | 1 | 11.11 | 1 | 150.6 | 1.51
[8 empty] | 420 | ROW |  | 5 | 55.56 | 62 | 8189.4 | 82.07
| Feeder Number: | 254
[8 empty] | 500 | Lightning |  | 1 | 11.11 | 1 | 632.4 | 6.34
| Feeder Location | 05254-Lola | [5 empty] | 700 | Member/Public Caused |  | 1 | 11.11 | 1 | 397.2 | 3.98
| Customer Count | 286
| Circuit 5 Year Average (SAIDI |  |  |  | 233.9161
| Reporting Year (SAIDI |  | 28.6018
| Circuit 5 Year Average (SAIFI |  |  |  | 1.6191
| Reporting Year (SAIFI |  | 0.2165
| Total Circuit Length: |  |  |  |  | 56.4
| Date of Last Circuit Trim: |  |  |  |  | 2016
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | KANSAS | [5 empty] | 100 | Contractor - Planned |  | 2 | 40 | 2 | 371.4 | 42.4
| Feeder Name: | Lowes | [5 empty] | 110 | JPEC - Planned |  | 1 | 20 | 2 | 235.2 | 26.85
[8 empty] | 300 | Equipment Failure |  | 1 | 20 | 1 | 103.2 | 11.78
| Feeder Number: | 214
[8 empty] | 500 | Lightning |  | 1 | 20 | 2 | 166.2 | 18.97
| Feeder Location | 61214-Lowes
| Customer Count | 455
| Circuit 5 Year Average (SAIDI |  |  |  | 76.6036
| Reporting Year (SAIDI |  | 0.8164
| Circuit 5 Year Average (SAIFI |  |  |  | 1.282
| Reporting Year (SAIFI |  | 0.9035
| Total Circuit Length: |  |  |  |  | 58.9
| Date of Last Circuit Trim: |  |  |  |  | 2022
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | KANSAS | [5 empty] | 420 | ROW |  | 5 | 62.5 | 122 | 37038.6 | 97.44
| Feeder Name: | Folsomdale | [5 empty] | 500 | Lightning |  | 3 | 37.5 | 3 | 973.2 | 2.56
| Feeder Number: | 224
| Feeder Location | 61224-Folsomdale
| Customer Count | 210
| Circuit 5 Year Average (SAIDI |  |  |  | 245.7233
| Reporting Year (SAIDI |  | 176.5324
| Circuit 5 Year Average (SAIFI |  |  |  | 1.2421
| Reporting Year (SAIFI |  | 0.5815
| Total Circuit Length: |  |  |  |  | 29.4
| Date of Last Circuit Trim: |  |  |  |  | 2016
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | KANSAS | [5 empty] | 300 | Equipment Failure |  | 1 | 11.11 | 2 | 515.4 | 1.86
| Feeder Name: | Melber | [5 empty] | 420 | ROW |  | 3 | 33.33 | 125 | 20274.6 | 73.2
[8 empty] | 500 | Lightning |  | 2 | 22.22 | 8 | 6459.6 | 23.32
| Feeder Number: | 234
[8 empty] | 510 | Wind - Not Trees |  | 1 | 11.11 | 2 | 187.2 | 0.68
| Feeder Location | 61234-Melber | [5 empty] | 690 | Animal |  | 1 | 11.11 | 1 | 32.4 | 0.12
| Customer Count | 598 | [5 empty] | 700 | Member/Public Caused |  | 1 | 11.11 | 2 | 226.8 | 0.82
| Circuit 5 Year Average (SAIDI |  |  |  | 328.452
| Reporting Year (SAIDI |  | 33.8903
| Circuit 5 Year Average (SAIFI |  |  |  | 2.054
| Reporting Year (SAIFI |  | 0.2089
| Total Circuit Length: |  |  |  |  | 54.1
| Date of Last Circuit Trim: |  |  |  |  | 2016
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | KANSAS | [5 empty] | 300 | Equipment Failure |  | 1 | 9.09 | 31 | 3525.6 | 12.13
| Feeder Name: | Pottsville | [5 empty] | 420 | ROW |  | 5 | 45.45 | 73 | 22854.6 | 78.61
[8 empty] | 500 | Lightning |  | 2 | 18.18 | 45 | 2063.4 | 7.1
| Feeder Number: | 244
[8 empty] | 690 | Animal |  | 1 | 9.09 | 8 | 331.8 | 1.14
| Feeder Location | 61244-Pottsville | [5 empty] | 730 | Fire |  | 1 | 9.09 | 3 | 231.6 | 0.8
| Customer Count | 363 | [5 empty] | 999 | Cause unknown |  | 1 | 9.09 | 1 | 67.8 | 0.23
| Circuit 5 Year Average (SAIDI |  |  |  | 517.0242
| Reporting Year (SAIDI |  | 62.8794
| Circuit 5 Year Average (SAIFI |  |  |  | 3.7401
| Reporting Year (SAIFI |  | 0.2008
| Total Circuit Length: |  |  |  |  | 47
| Date of Last Circuit Trim: |  |  |  |  | 2023
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | KEVIL | [5 empty] | 110 | JPEC - Planned |  | 3 | 21.43 | 65 | 2642.4 | 19
| Feeder Name: | Hobbs Rd | [5 empty] | 420 | ROW |  | 5 | 35.71 | 76 | 9555.6 | 68.71
[8 empty] | 500 | Lightning |  | 2 | 14.29 | 2 | 134.4 | 0.97
| Feeder Number: | 214
[8 empty] | 690 | Animal |  | 3 | 21.43 | 13 | 438 | 3.15
| Feeder Location | 28214-Hobbs Rd | [5 empty] | 700 | Member/Public Caused |  | 1 | 7.14 | 12 | 1137.6 | 8.18
| Customer Count | 545
| Circuit 5 Year Average (SAIDI |  |  |  | 216.8682
| Reporting Year (SAIDI |  | 17.5244
| Circuit 5 Year Average (SAIFI |  |  |  | 1.5812
| Reporting Year (SAIFI |  | 0.1394
| Total Circuit Length: |  |  |  |  | 52.7
| Date of Last Circuit Trim: |  |  |  |  | 2016
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | KEVIL | [5 empty] | 110 | JPEC - Planned |  | 2 | 14.29 | 3 | 222 | 1.41
| Feeder Name: | Woodville Rd | [5 empty] | 300 | Equipment Failure |  | 2 | 14.29 | 42 | 6619.8 | 42.06
[8 empty] | 420 | ROW |  | 6 | 42.86 | 30 | 7517.4 | 47.76
| Feeder Number: | 224
[8 empty] | 690 | Animal |  | 2 | 14.29 | 7 | 472.2 | 3
| Feeder Location | 28224-Woodville Rd | [5 empty] | 700 | Member/Public Caused |  | 1 | 7.14 | 4 | 460.8 | 2.93
| Customer Count | 501 | [5 empty] | 999 | Cause unknown |  | 1 | 7.14 | 6 | 448.2 | 2.85
| Circuit 5 Year Average (SAIDI |  |  |  | 93.1395
| Reporting Year (SAIDI |  | 15.0164
| Circuit 5 Year Average (SAIFI |  |  |  | 0.9908
| Reporting Year (SAIFI |  | 0.0839
| Total Circuit Length: |  |  |  |  | 56.2
| Date of Last Circuit Trim: |  |  |  |  | 2016
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | KEVIL | [5 empty] | 420 | ROW |  | 1 | 50 | 2 | 1128.6 | 9.19
| Feeder Name: | Kelley Rd | [5 empty] | 500 | Lightning |  | 1 | 50 | 21 | 11147.4 | 90.81
| Feeder Number: | 234
| Feeder Location | 28234-Kelley Rd
| Customer Count | 427
| Circuit 5 Year Average (SAIDI |  |  |  | 51.0987
| Reporting Year (SAIDI |  | 26.1298
| Circuit 5 Year Average (SAIFI |  |  |  | 0.6062
| Reporting Year (SAIFI |  | 0.0492
| Total Circuit Length: |  |  |  |  | 47.9
| Date of Last Circuit Trim: |  |  |  |  | 2016
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | KREBS STATION RD | [5 empty] | 100 | Contractor - Planned |  | 3 | 17.65 | 5 | 738.6 | 0.29
| Feeder Name: | Browns Plating | [5 empty] | 110 | JPEC - Planned |  | 1 | 5.88 | 4 | 117.6 | 0.05
[8 empty] | 300 | Equipment Failure |  | 1 | 5.88 | 13 | 382.8 | 0.15
| Feeder Number: | 214
[8 empty] | 420 | ROW |  | 10 | 58.82 | 958 | 209650.2 | 81.54
| Feeder Location | 50214-Browns Platin | [5 empty] | 510 | Wind - Not Trees |  | 1 | 5.88 | 89 | 46140.6 | 17.94
| Customer Count | 527 | [5 empty] | 690 | Animal |  | 1 | 5.88 | 4 | 95.4 | 0.04
| Circuit 5 Year Average (SAIDI |  |  |  | 242.7261
| Reporting Year (SAIDI |  | 397.9896
| Circuit 5 Year Average (SAIFI |  |  |  | 1.7902
| Reporting Year (SAIFI |  | 1.8186
| Total Circuit Length: |  |  |  |  | 37.3
| Date of Last Circuit Trim: |  |  |  |  | 2016
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | KREBS STATION RD | [5 empty] | 100 | Contractor - Planned |  | 5 | 17.86 | 11 | 2280.6 | 0.56
| Feeder Name: | Old US 45 | [5 empty] | 110 | JPEC - Planned |  | 1 | 3.57 | 3 | 562.2 | 0.14
[8 empty] | 300 | Equipment Failure |  | 4 | 14.29 | 75 | 9048.6 | 2.23
| Feeder Number: | 224
[8 empty] | 420 | ROW |  | 8 | 28.57 | 678 | 257511 | 63.54
| Feeder Location | 50224-Old US 45 | [5 empty] | 500 | Lightning |  | 2 | 7.14 | 24 | 6238.2 | 1.54
| Customer Count | 908 | [5 empty] | 510 | Wind - Not Trees |  | 1 | 3.57 | 742 | 117953.4 | 29.11
| Circuit 5 Year Average (SAIDI |  |  |  | 243.2834 |  |  | 690 | Animal |  | 4 | 14.29 | 12 | 649.2 | 0.16
| Reporting Year (SAIDI |  | 283.5335 |  |  |  |  | 700 | Member/Public Caused |  | 1 | 3.57 | 1 | 90 | 0.02
[8 empty] | 999 | Cause unknown |  | 2 | 7.14 | 17 | 10927.8 | 2.7
| Circuit 5 Year Average (SAIFI |  |  |  | 1.7062
| Reporting Year (SAIFI |  | 0.817
| Total Circuit Length: |  |  |  |  | 82.7
| Date of Last Circuit Trim: |  |  |  |  | 2016
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | KREBS STATION RD | [5 empty] | 000 | No Cause Selected |  | 1 | 11.11 | 357 | 108738 | 80.82
| Feeder Name: | Clinton Rd | [5 empty] | 100 | Contractor - Planned |  | 2 | 22.22 | 4 | 777 | 0.58
[8 empty] | 300 | Equipment Failure |  | 1 | 11.11 | 28 | 2581.8 | 1.92
| Feeder Number: | 234
[8 empty] | 420 | ROW |  | 4 | 44.44 | 128 | 21968.4 | 16.33
| Feeder Location | 50234-Clinton Rd | [5 empty] | 500 | Lightning |  | 1 | 11.11 | 2 | 483 | 0.36
| Customer Count | 521
| Circuit 5 Year Average (SAIDI |  |  |  | 134.8753
| Reporting Year (SAIDI |  | 208.6463
| Circuit 5 Year Average (SAIFI |  |  |  | 1.5788
| Reporting Year (SAIFI |  | 0.685
| Total Circuit Length: |  |  |  |  | 19.3
| Date of Last Circuit Trim: |  |  |  |  | 2021
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | KREBS STATION RD | [5 empty] | 100 | Contractor - Planned |  | 2 | 33.33 | 9 | 1225.2 | 21.32
| Feeder Name: | New Hope | [5 empty] | 300 | Equipment Failure |  | 1 | 16.67 | 45 | 3590.4 | 62.48
[8 empty] | 420 | ROW |  | 1 | 16.67 | 13 | 561.6 | 9.77
| Feeder Number: | 244
[8 empty] | 690 | Animal |  | 1 | 16.67 | 13 | 319.2 | 5.55
| Feeder Location | 50244-New Hope | [5 empty] | 999 | Cause unknown |  | 1 | 16.67 | 1 | 49.8 | 0.87
| Customer Count | 269
| Circuit 5 Year Average (SAIDI |  |  |  | 38.5591
| Reporting Year (SAIDI |  | 13.3412
| Circuit 5 Year Average (SAIFI |  |  |  | 0.4883
| Reporting Year (SAIFI |  | 0.1672
| Total Circuit Length: |  |  |  |  | 36
| Date of Last Circuit Trim: |  |  |  |  | 2021
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | LaCENTER | [5 empty] | 300 | Equipment Failure |  | 1 | 14.29 | 2 | 142.2 | 0.3
| Feeder Name: | Damrons | [5 empty] | 420 | ROW |  | 3 | 42.86 | 122 | 46044.6 | 98.46
[8 empty] | 500 | Lightning |  | 1 | 14.29 | 5 | 441.6 | 0.94
| Feeder Number: | 214
[8 empty] | 690 | Animal |  | 2 | 28.57 | 2 | 135.6 | 0.29
| Feeder Location | 26214-Damrons
| Customer Count | 227
| Circuit 5 Year Average (SAIDI |  |  |  | 175.3949
| Reporting Year (SAIDI |  | 203.1178
| Circuit 5 Year Average (SAIFI |  |  |  | 1.9983
| Reporting Year (SAIFI |  | 0.5382
| Total Circuit Length: |  |  |  |  | 39.8
| Date of Last Circuit Trim: |  |  |  |  | 2015
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | LaCENTER | [5 empty] | 300 | Equipment Failure |  | 4 | 33.33 | 40 | 19229.4 | 29.9
| Feeder Name: | Oscar | [5 empty] | 420 | ROW |  | 2 | 16.67 | 375 | 27501 | 42.77
[8 empty] | 500 | Lightning |  | 2 | 16.67 | 45 | 17067 | 26.54
| Feeder Number: | 224
[8 empty] | 690 | Animal |  | 3 | 25 | 5 | 360 | 0.56
| Feeder Location | 26224-Oscar | [5 empty] | 810 | Load |  | 1 | 8.33 | 2 | 148.2 | 0.23
| Customer Count | 363
| Circuit 5 Year Average (SAIDI |  |  |  | 332.9561
| Reporting Year (SAIDI |  | 75.8099
| Circuit 5 Year Average (SAIFI |  |  |  | 2.658
| Reporting Year (SAIFI |  | 1.0337
| Total Circuit Length: |  |  |  |  | 69.4
| Date of Last Circuit Trim: |  |  |  |  | 2023
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | LEDBETTER | [5 empty] | 110 | JPEC - Planned |  | 2 | 25 | 2 | 141 | 0.3
| Feeder Name: | US 60 East | [5 empty] | 300 | Equipment Failure |  | 1 | 12.5 | 2 | 213 | 0.45
[8 empty] | 420 | ROW |  | 3 | 37.5 | 55 | 32818.2 | 69.66
| Feeder Number: | 224
[8 empty] | 999 | Cause unknown |  | 2 | 25 | 98 | 13940.4 | 29.59
| Feeder Location | 31224-US 60 East
| Customer Count | 317
| Circuit 5 Year Average (SAIDI |  |  |  | 85.7963
| Reporting Year (SAIDI |  | 103.5829
| Circuit 5 Year Average (SAIFI |  |  |  | 0.7329
| Reporting Year (SAIFI |  | 0.3093
| Total Circuit Length: |  |  |  |  | 35.6
| Date of Last Circuit Trim: |  |  |  |  | 2016
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | LEDBETTER | [5 empty] | 420 | ROW |  | 1 | 100 | 3 | 105 | 100
| Feeder Name: | River Crossing
| Feeder Number: | 234
| Feeder Location | 31234-River Crossin
| Customer Count | 36
| Circuit 5 Year Average (SAIDI |  |  |  | 50.4291
| Reporting Year (SAIDI |  | 2.8952
| Circuit 5 Year Average (SAIFI |  |  |  | 1.0979
| Reporting Year (SAIFI |  | 0.0828
| Total Circuit Length: |  |  |  |  | 5.2
| Date of Last Circuit Trim: |  |  |  |  | 2016
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | LEDBETTER | [5 empty] | 100 | Contractor - Planned |  | 3 | 11.11 | 8 | 751.8 | 0.53
| Feeder Name: | Ledbetter | [5 empty] | 110 | JPEC - Planned |  | 2 | 7.41 | 3 | 1125 | 0.79
[8 empty] | 300 | Equipment Failure |  | 3 | 11.11 | 32 | 4225.2 | 2.98
| Feeder Number: | 244
[8 empty] | 420 | ROW |  | 3 | 11.11 | 68 | 19589.4 | 13.83
| Feeder Location | 31244-Ledbetter | [5 empty] | 500 | Lightning |  | 4 | 14.81 | 41 | 3084.6 | 2.18
| Customer Count | 1026 | [5 empty] | 690 | Animal |  | 6 | 22.22 | 13 | 813.6 | 0.57
| Circuit 5 Year Average (SAIDI |  |  |  | 95.3071 |  |  | 700 | Member/Public Caused |  | 4 | 14.81 | 1589 | 111792.6 | 78.93
| Reporting Year (SAIDI |  | 108.9581 |  |  |  |  | 810 | Load |  | 2 | 7.41 | 4 | 247.2 | 0.17
| Circuit 5 Year Average (SAIFI |  |  |  | 0.9082
| Reporting Year (SAIFI |  | 1.5487
| Total Circuit Length: |  |  |  |  | 61.5
| Date of Last Circuit Trim: |  |  |  |  | 2022
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | LITTLE UNION | [5 empty] | 300 | Equipment Failure |  | 2 | 40 | 4 | 659.4 | 27.21
| Feeder Name: | Airport | [5 empty] | 690 | Animal |  | 2 | 40 | 34 | 1581.6 | 65.26
[8 empty] | 810 | Load |  | 1 | 20 | 3 | 182.4 | 7.53
| Feeder Number: | 214
| Feeder Location | 39214-Airport
| Customer Count | 565
| Circuit 5 Year Average (SAIDI |  |  |  | 144.1144
| Reporting Year (SAIDI |  | 2.797
| Circuit 5 Year Average (SAIFI |  |  |  | 1.4318
| Reporting Year (SAIFI |  | 0.0601
| Total Circuit Length: |  |  |  |  | 36.2
| Date of Last Circuit Trim: |  |  |  |  | 2017
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | LITTLE UNION | [5 empty] | 110 | JPEC - Planned |  | 3 | 75 | 4 | 43.8 | 73
| Feeder Name: | US 60 West | [5 empty] | 700 | Member/Public Caused |  | 1 | 25 | 1 | 16.2 | 27
| Feeder Number: | 224
| Feeder Location | 39224-US 60 West
| Customer Count | 471
| Circuit 5 Year Average (SAIDI |  |  |  | 212.112
| Reporting Year (SAIDI |  | 0.0931
| Circuit 5 Year Average (SAIFI |  |  |  | 1.9043
| Reporting Year (SAIFI |  | 0.0085
| Total Circuit Length: |  |  |  |  | 37.2
| Date of Last Circuit Trim: |  |  |  |  | 2022
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | LITTLE UNION | [5 empty] | 300 | Equipment Failure |  | 1 | 100 | 3 | 223.8 | 100
| Feeder Name: | US 60 East Mall
| Feeder Number: | 234
| Feeder Location | 39234-US 60 East M
| Customer Count | 163
| Circuit 5 Year Average (SAIDI |  |  |  | 18.6046
| Reporting Year (SAIDI |  | 1.3755
| Circuit 5 Year Average (SAIFI |  |  |  | 0.2544
| Reporting Year (SAIFI |  | 0.0184
| Total Circuit Length: |  |  |  |  | 10.4
| Date of Last Circuit Trim: |  |  |  |  | 2017
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | LITTLE UNION | [5 empty] | 300 | Equipment Failure |  | 1 | 14.29 | 1 | 47.4 | 0.06
| Feeder Name: | Roy Lee Rd | [5 empty] | 420 | ROW |  | 3 | 42.86 | 141 | 71692.2 | 83.63
[8 empty] | 690 | Animal |  | 2 | 28.57 | 34 | 2521.2 | 2.94
| Feeder Number: | 244
[8 empty] | 999 | Cause unknown |  | 1 | 14.29 | 96 | 11469 | 13.38
| Feeder Location | 39244-Roy Lee Rd
| Customer Count | 539
| Circuit 5 Year Average (SAIDI |  |  |  | 137.3456
| Reporting Year (SAIDI |  | 133.0638
| Circuit 5 Year Average (SAIFI |  |  |  | 1.6519
| Reporting Year (SAIFI |  | 0.2617
| Total Circuit Length: |  |  |  |  | 56.6
| Date of Last Circuit Trim: |  |  |  |  | 2022
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | LOVELACEVILLE | [5 empty] | 420 | ROW |  | 1 | 33.33 | 7 | 1222.2 | 35.57
| Feeder Name: | Blandville | [5 empty] | 500 | Lightning |  | 2 | 66.67 | 8 | 2214 | 64.43
| Feeder Number: | 214
| Feeder Location | 49214-Blandville
| Customer Count | 132
| Circuit 5 Year Average (SAIDI |  |  |  | 155.5335
| Reporting Year (SAIDI |  | 16.7471
| Circuit 5 Year Average (SAIFI |  |  |  | 0.9896
| Reporting Year (SAIFI |  | 0.0605
| Total Circuit Length: |  |  |  |  | 20.5
| Date of Last Circuit Trim: |  |  |  |  | 2015
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | LOVELACEVILLE | [5 empty] | 300 | Equipment Failure |  | 2 | 20 | 8 | 2845.2 | 4.14
| Feeder Name: | Lovelaceville | [5 empty] | 420 | ROW |  | 7 | 70 | 159 | 65024.4 | 94.6
[8 empty] | 700 | Member/Public Caused |  | 1 | 10 | 9 | 869.4 | 1.26
| Feeder Number: | 224
| Feeder Location | 49224-Lovelaceville
| Customer Count | 527
| Circuit 5 Year Average (SAIDI |  |  |  | 78.8799
| Reporting Year (SAIDI |  | 123.322
| Circuit 5 Year Average (SAIFI |  |  |  | 0.8762
| Reporting Year (SAIFI |  | 0.3016
| Total Circuit Length: |  |  |  |  | 58.5
| Date of Last Circuit Trim: |  |  |  |  | 2015
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | LOVELACEVILLE | [5 empty] | 100 | Contractor - Planned |  | 11 | 47.83 | 15 | 1312.2 | 2.56
| Feeder Name: | Cunningham | [5 empty] | 300 | Equipment Failure |  | 3 | 13.04 | 4 | 287.4 | 0.56
[8 empty] | 420 | ROW |  | 2 | 8.7 | 63 | 27198 | 52.98
| Feeder Number: | 234
[8 empty] | 510 | Wind - Not Trees |  | 2 | 8.7 | 16 | 1391.4 | 2.71
| Feeder Location | 49234-Cunningham | [5 empty] | 690 | Animal |  | 4 | 17.39 | 300 | 18684.6 | 36.4
| Customer Count | 526 | [5 empty] | 710 | Motor Vehicle |  | 1 | 4.35 | 33 | 2458.2 | 4.79
| Circuit 5 Year Average (SAIDI |  |  |  | 142.72
| Reporting Year (SAIDI |  | 51.6909
| Circuit 5 Year Average (SAIFI |  |  |  | 1.4585
| Reporting Year (SAIFI |  | 0.5702
| Total Circuit Length: |  |  |  |  | 65.7
| Date of Last Circuit Trim: |  |  |  |  | 2015
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | MAXON | [5 empty] | 110 | JPEC - Planned |  | 2 | 66.67 | 31 | 2024.4 | 95.77
| Feeder Name: | Maxon Rd | [5 empty] | 690 | Animal |  | 1 | 33.33 | 1 | 89.4 | 4.23
| Feeder Number: | 214
| Feeder Location | 79214-Maxon Rd
| Customer Count | 261
| Circuit 5 Year Average (SAIDI |  |  |  | 81.7293
| Reporting Year (SAIDI |  | 7.7675
| Circuit 5 Year Average (SAIFI |  |  |  | 1.1743
| Reporting Year (SAIFI |  | 0.119
| Total Circuit Length: |  |  |  |  | 16.4
| Date of Last Circuit Trim: |  |  |  |  | 2023
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | MAXON | [5 empty] | 420 | ROW |  | 1 | 50 | 6 | 341.4 | 2.97
| Feeder Name: | Express | [5 empty] | 500 | Lightning |  | 1 | 50 | 331 | 11154.6 | 97.03
| Feeder Number: | 224
| Feeder Location | 79224-Express
| Customer Count | 395
| Circuit 5 Year Average (SAIDI |  |  |  | 131.8784
| Reporting Year (SAIDI |  | 28.2505
| Circuit 5 Year Average (SAIFI |  |  |  | 1.3879
| Reporting Year (SAIFI |  | 0.8383
| Total Circuit Length: |  |  |  |  | 19
| Date of Last Circuit Trim: |  |  |  |  | 2023
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | MAXON | [5 empty] | None | None |  | 0 | 0 | 0 | 0 | 0
| Feeder Name: | Industrial Park
| Feeder Number: | 234
| Feeder Location | 79234-Industrial Park
| Customer Count | 4
| Circuit 5 Year Average (SAIDI |  |  |  | 39.133
| Reporting Year (SAIDI |  | 0
| Circuit 5 Year Average (SAIFI |  |  |  | 0.5769
| Reporting Year (SAIFI |  | 0
| Total Circuit Length: |  |  |  |  | 2
| Date of Last Circuit Trim: |  |  |  |  | 2017
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | NEW YORK | [5 empty] | 300 | Equipment Failure |  | 1 | 16.67 | 2 | 90.6 | 0.5
| Feeder Name: | Hinkleville | [5 empty] | 420 | ROW |  | 5 | 83.33 | 73 | 18105 | 99.5
| Feeder Number: | 214
| Feeder Location | 47214-Hinkleville
| Customer Count | 265
| Circuit 5 Year Average (SAIDI |  |  |  | 204.3962
| Reporting Year (SAIDI |  | 68.3758
| Circuit 5 Year Average (SAIFI |  |  |  | 1.8294
| Reporting Year (SAIFI |  | 0.2757
| Total Circuit Length: |  |  |  |  | 44.8
| Date of Last Circuit Trim: |  |  |  |  | 2022
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | NEW YORK | [5 empty] | 100 | Contractor - Planned |  | 2 | 50 | 3 | 210.6 | 5.35
| Feeder Name: | US 286 East Gage | [5 empty] | 420 | ROW |  | 1 | 25 | 33 | 3192 | 81.06
[8 empty] | 500 | Lightning |  | 1 | 25 | 1 | 535.2 | 13.59
| Feeder Number: | 224
| Feeder Location | 47224-US 286 East
| Customer Count | 264
| Circuit 5 Year Average (SAIDI |  |  |  | 212.0757
| Reporting Year (SAIDI |  | 12.0848
| Circuit 5 Year Average (SAIFI |  |  |  | 1.3242
| Reporting Year (SAIFI |  | 0.1249
| Total Circuit Length: |  |  |  |  | 45.5
| Date of Last Circuit Trim: |  |  |  |  | 2015
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | NEW YORK | [5 empty] | 420 | ROW |  | 6 | 66.67 | 203 | 165216.6 | 98.48
| Feeder Name: | Blandville | [5 empty] | 690 | Animal |  | 1 | 11.11 | 4 | 280.8 | 0.17
[8 empty] | 700 | Member/Public Caused |  | 1 | 11.11 | 16 | 1633.2 | 0.97
| Feeder Number: | 234
[8 empty] | 999 | Cause unknown |  | 1 | 11.11 | 7 | 642.6 | 0.38
| Feeder Location | 47234-Blandville
| Customer Count | 219
| Circuit 5 Year Average (SAIDI |  |  |  | 590.0191
| Reporting Year (SAIDI |  | 753.1432
| Circuit 5 Year Average (SAIFI |  |  |  | 3.6486
| Reporting Year (SAIFI |  | 0.9254
| Total Circuit Length: |  |  |  |  | 30.1
| Date of Last Circuit Trim: |  |  |  |  | 2022
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | NEW YORK | [5 empty] | 300 | Equipment Failure |  | 1 | 6.25 | 7 | 787.2 | 1.17
| Feeder Name: | Wickliffe | [5 empty] | 420 | ROW |  | 9 | 56.25 | 141 | 55738.8 | 82.61
[8 empty] | 500 | Lightning |  | 3 | 18.75 | 26 | 8496.6 | 12.59
| Feeder Number: | 244
[8 empty] | 999 | Cause unknown |  | 3 | 18.75 | 20 | 2451 | 3.63
| Feeder Location | 47244-Wickliffe
| Customer Count | 355
| Circuit 5 Year Average (SAIDI |  |  |  | 317.6329
| Reporting Year (SAIDI |  | 157.0811
| Circuit 5 Year Average (SAIFI |  |  |  | 2.4005
| Reporting Year (SAIFI |  | 1.0202
| Total Circuit Length: |  |  |  |  | 49.3
| Date of Last Circuit Trim: |  |  |  |  | 2021
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | NEW YORK | [5 empty] | 100 | Contractor - Planned |  | 1 | 5.88 | 2 | 94.2 | 0.21
| Feeder Name: | Slater | [5 empty] | 110 | JPEC - Planned |  | 3 | 17.65 | 27 | 8340.6 | 18.33
[8 empty] | 300 | Equipment Failure |  | 2 | 11.76 | 4 | 310.2 | 0.68
| Feeder Number: | 254
[8 empty] | 420 | ROW |  | 5 | 29.41 | 59 | 32661 | 71.77
| Feeder Location | 47254-Slater | [5 empty] | 500 | Lightning |  | 1 | 5.88 | 1 | 634.2 | 1.39
| Customer Count | 358 | [5 empty] | 690 | Animal |  | 1 | 5.88 | 2 | 175.8 | 0.39
| Circuit 5 Year Average (SAIDI |  |  |  | 258.6838 |  |  | 700 | Member/Public Caused |  | 1 | 5.88 | 2 | 113.4 | 0.25
| Reporting Year (SAIDI |  | 91.1785 |  |  |  |  | 810 | Load |  | 1 | 5.88 | 26 | 3055.2 | 6.71
[8 empty] | 999 | Cause unknown |  | 2 | 11.76 | 2 | 123.6 | 0.27
| Circuit 5 Year Average (SAIFI |  |  |  | 2.3349
| Reporting Year (SAIFI |  | 0.1647
| Total Circuit Length: |  |  |  |  | 67.8
| Date of Last Circuit Trim: |  |  |  |  | 2023
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | OLIVET CHURCH RD | [5 empty] | 500 | Lightning |  | 1 | 100 | 2 | 48.6 | 100
| Feeder Name: | Olivet Ch Rd
| Feeder Number: | 214
| Feeder Location | 74214-Olivet Ch Rd
| Customer Count | 589
| Circuit 5 Year Average (SAIDI |  |  |  | 66.8251
| Reporting Year (SAIDI |  | 0.0822
| Circuit 5 Year Average (SAIFI |  |  |  | 1.4107
| Reporting Year (SAIFI |  | 0.0034
| Total Circuit Length: |  |  |  |  | 24
| Date of Last Circuit Trim: |  |  |  |  | 2022
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | OLIVET CHURCH RD | [5 empty] | 110 | JPEC - Planned |  | 1 | 33.33 | 2 | 66 | 0.28
| Feeder Name: | Highland Ch Rd | [5 empty] | 420 | ROW |  | 1 | 33.33 | 146 | 23571.6 | 99.51
[8 empty] | 690 | Animal |  | 1 | 33.33 | 1 | 49.2 | 0.21
| Feeder Number: | 224
| Feeder Location | 74224-Highland Ch
| Customer Count | 481
| Circuit 5 Year Average (SAIDI |  |  |  | 150.6153
| Reporting Year (SAIDI |  | 48.9959
| Circuit 5 Year Average (SAIFI |  |  |  | 1.7257
| Reporting Year (SAIFI |  | 0.3035
| Total Circuit Length: |  |  |  |  | 33.1
| Date of Last Circuit Trim: |  |  |  |  | 2015
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | OLIVET CHURCH RD | [5 empty] | 300 | Equipment Failure |  | 1 | 50 | 1 | 576.6 | 26.95
| Feeder Name: | Info Age Park | [5 empty] | 690 | Animal |  | 1 | 50 | 8 | 1563 | 73.05
| Feeder Number: | 234
| Feeder Location | 74234-Info Age Park
| Customer Count | 8
| Circuit 5 Year Average (SAIDI |  |  |  | 152.7175
| Reporting Year (SAIDI |  | 195.35
| Circuit 5 Year Average (SAIFI |  |  |  | 1.1
| Reporting Year (SAIFI |  | 1
| Total Circuit Length: |  |  |  |  | 2.8
| Date of Last Circuit Trim: |  |  |  |  | 2015
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | PALMA | [5 empty] | 100 | Contractor - Planned |  | 1 | 9.09 | 1 | 126.6 | 0.13
| Feeder Name: | Hwy 95 | [5 empty] | 300 | Equipment Failure |  | 1 | 9.09 | 369 | 76075.8 | 78.71
[8 empty] | 420 | ROW |  | 8 | 72.73 | 121 | 20242.2 | 20.94
| Feeder Number: | 214
[8 empty] | 690 | Animal |  | 1 | 9.09 | 8 | 214.8 | 0.22
| Feeder Location | 54214-Hwy 95
| Customer Count | 369
| Circuit 5 Year Average (SAIDI |  |  |  | 229.7376
| Reporting Year (SAIDI |  | 206.3624
| Circuit 5 Year Average (SAIFI |  |  |  | 1.7713
| Reporting Year (SAIFI |  | 1.0009
| Total Circuit Length: |  |  |  |  | 29.9
| Date of Last Circuit Trim: |  |  |  |  | 2015
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | PALMA | [5 empty] | 100 | Contractor - Planned |  | 1 | 25 | 1 | 163.2 | 1.48
| Feeder Name: | Draffenville | [5 empty] | 110 | JPEC - Planned |  | 1 | 25 | 2 | 101.4 | 0.92
[8 empty] | 500 | Lightning |  | 1 | 25 | 25 | 10706.4 | 97.16
| Feeder Number: | 224
[8 empty] | 690 | Animal |  | 1 | 25 | 1 | 48.6 | 0.44
| Feeder Location | 54224-Draffenville
| Customer Count | 302
| Circuit 5 Year Average (SAIDI |  |  |  | 151.1272
| Reporting Year (SAIDI |  | 35.5064
| Circuit 5 Year Average (SAIFI |  |  |  | 1.6171
| Reporting Year (SAIFI |  | 0.0829
| Total Circuit Length: |  |  |  |  | 21.7
| Date of Last Circuit Trim: |  |  |  |  | 2015
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | PALMA | [5 empty] | 110 | JPEC - Planned |  | 2 | 9.52 | 4 | 172.2 | 0.47
| Feeder Name: | Palma | [5 empty] | 420 | ROW |  | 7 | 33.33 | 112 | 25150.2 | 69.08
[8 empty] | 500 | Lightning |  | 2 | 9.52 | 55 | 6178.2 | 16.97
| Feeder Number: | 234
[8 empty] | 690 | Animal |  | 8 | 38.1 | 72 | 4554 | 12.51
| Feeder Location | 54234-Palma | [5 empty] | 700 | Member/Public Caused |  | 1 | 4.76 | 3 | 301.2 | 0.83
| Customer Count | 744 | [5 empty] | 999 | Cause unknown |  | 1 | 4.76 | 1 | 52.2 | 0.14
| Circuit 5 Year Average (SAIDI |  |  |  | 126.0116
| Reporting Year (SAIDI |  | 33.7892
| Circuit 5 Year Average (SAIFI |  |  |  | 1.6727
| Reporting Year (SAIFI |  | 0.1505
| Total Circuit Length: |  |  |  |  | 57.4
| Date of Last Circuit Trim: |  |  |  |  | 2015
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | POSSUM TROT | [5 empty] | 100 | Contractor - Planned |  | 1 | 5.88 | 4 | 351.6 | 0.2
| Feeder Name: | Possum Trot | [5 empty] | 300 | Equipment Failure |  | 6 | 35.29 | 20 | 1354.2 | 0.76
[8 empty] | 420 | ROW |  | 4 | 23.53 | 15 | 4447.8 | 2.5
| Feeder Number: | 224
[8 empty] | 500 | Lightning |  | 2 | 11.76 | 607 | 170176.8 | 95.71
| Feeder Location | 78224-Possum Trot | [5 empty] | 690 | Animal |  | 3 | 17.65 | 32 | 1379.4 | 0.78
| Customer Count | 545 | [5 empty] | 810 | Load |  | 1 | 5.88 | 2 | 85.8 | 0.05
| Circuit 5 Year Average (SAIDI |  |  |  | 238.509
| Reporting Year (SAIDI |  | 312.4858
| Circuit 5 Year Average (SAIFI |  |  |  | 2.1444
| Reporting Year (SAIFI |  | 1.1146
| Total Circuit Length: |  |  |  |  | 42.2
| Date of Last Circuit Trim: |  |  |  |  | 2015
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | POSSUM TROT | [5 empty] | 110 | JPEC - Planned |  | 1 | 14.29 | 5 | 129.6 | 0.39
| Feeder Name: | Hwy 95 | [5 empty] | 300 | Equipment Failure |  | 1 | 14.29 | 40 | 5349.6 | 16.3
[8 empty] | 420 | ROW |  | 4 | 57.14 | 16 | 2077.8 | 6.33
| Feeder Number: | 234
[8 empty] | 500 | Lightning |  | 1 | 14.29 | 203 | 25253.4 | 76.97
| Feeder Location | 78234-Hwy 95
| Customer Count | 201
| Circuit 5 Year Average (SAIDI |  |  |  | 149.3802
| Reporting Year (SAIDI |  | 125.8632
| Circuit 5 Year Average (SAIFI |  |  |  | 1.2261
| Reporting Year (SAIFI |  | 1.0118
| Total Circuit Length: |  |  |  |  | 15
| Date of Last Circuit Trim: |  |  |  |  | 2015
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | POSSUM TROT | [5 empty] | 100 | Contractor - Planned |  | 1 | 10 | 8 | 1670.4 | 1.54
| Feeder Name: | Industrial Loop | [5 empty] | 420 | ROW |  | 2 | 20 | 3 | 319.8 | 0.3
[8 empty] | 500 | Lightning |  | 2 | 20 | 208 | 92856.6 | 85.73
| Feeder Number: | 254
[8 empty] | 510 | Wind - Not Trees |  | 1 | 10 | 1 | 67.8 | 0.06
| Feeder Location | 78254-Industrial Loo | [5 empty] | 690 | Animal |  | 4 | 40 | 230 | 13401 | 12.37
| Customer Count | 207
| Circuit 5 Year Average (SAIDI |  |  |  | 285.9497
| Reporting Year (SAIDI |  | 449.2977
| Circuit 5 Year Average (SAIFI |  |  |  | 1.4168
| Reporting Year (SAIFI |  | 1.1129
| Total Circuit Length: |  |  |  |  | 29.5
| Date of Last Circuit Trim: |  |  |  |  | 2015
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | POSSUM TROT | [5 empty] | None | None |  | 0 | 0 | 0 | 0 | 0
| Feeder Name: | CoalTek
| Feeder Number: | 264
| Feeder Location | 78264-CoalTek
| Customer Count | 2
| Circuit 5 Year Average (SAIDI |  |  |  | 6.6133
| Reporting Year (SAIDI |  | 0
| Circuit 5 Year Average (SAIFI |  |  |  | 0.2
| Reporting Year (SAIFI |  | 0
| Total Circuit Length: |  |  |  |  | 3.9
| Date of Last Circuit Trim: |  |  |  |  | 2015
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | RAGLAND | [5 empty] | 420 | ROW |  | 4 | 44.44 | 20 | 2745.6 | 11.89
| Feeder Name: | Monkeys Eyebrow | [5 empty] | 500 | Lightning |  | 1 | 11.11 | 241 | 19203.6 | 83.19
[8 empty] | 510 | Wind - Not Trees |  | 1 | 11.11 | 1 | 322.8 | 1.4
| Feeder Number: | 214
[8 empty] | 700 | Member/Public Caused |  | 1 | 11.11 | 5 | 680.4 | 2.95
| Feeder Location | 19214-Monkeys Eye | [5 empty] | 810 | Load |  | 1 | 11.11 | 1 | 79.8 | 0.35
| Customer Count | 238 | [5 empty] | 999 | Cause unknown |  | 1 | 11.11 | 1 | 52.8 | 0.23
| Circuit 5 Year Average (SAIDI |  |  |  | 208.8192
| Reporting Year (SAIDI |  | 80.7692
| Circuit 5 Year Average (SAIFI |  |  |  | 1.6294
| Reporting Year (SAIFI |  | 1.0136
| Total Circuit Length: |  |  |  |  | 50
| Date of Last Circuit Trim: |  |  |  |  | 2022
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | RAGLAND | [5 empty] | 300 | Equipment Failure |  | 2 | 33.33 | 45 | 4290.6 | 44.98
| Feeder Name: | Ragland | [5 empty] | 500 | Lightning |  | 1 | 16.67 | 1 | 82.8 | 0.87
[8 empty] | 690 | Animal |  | 2 | 33.33 | 2 | 98.4 | 1.03
| Feeder Number: | 224
[8 empty] | 999 | Cause unknown |  | 1 | 16.67 | 44 | 5066.4 | 53.12
| Feeder Location | 19224-Ragland
| Customer Count | 222
| Circuit 5 Year Average (SAIDI |  |  |  | 156.9842
| Reporting Year (SAIDI |  | 22.8143
| Circuit 5 Year Average (SAIFI |  |  |  | 1.5724
| Reporting Year (SAIFI |  | 0.2026
| Total Circuit Length: |  |  |  |  | 33.4
| Date of Last Circuit Trim: |  |  |  |  | 2023
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | REIDLAND | [5 empty] | 100 | Contractor - Planned |  | 2 | 33.33 | 5 | 439.2 | 0.21
| Feeder Name: | Ken Mar Rd | [5 empty] | 300 | Equipment Failure |  | 1 | 16.67 | 44 | 9926.4 | 4.68
[8 empty] | 420 | ROW |  | 2 | 33.33 | 358 | 201610.8 | 95.09
| Feeder Number: | 214
[8 empty] | 690 | Animal |  | 1 | 16.67 | 2 | 48.6 | 0.02
| Feeder Location | 41214-Ken Mar Rd
| Customer Count | 341
| Circuit 5 Year Average (SAIDI |  |  |  | 408.1702
| Reporting Year (SAIDI |  | 591.9463
| Circuit 5 Year Average (SAIFI |  |  |  | 1.6254
| Reporting Year (SAIFI |  | 1.0511
| Total Circuit Length: |  |  |  |  | 20.1
| Date of Last Circuit Trim: |  |  |  |  | 2022
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | REIDLAND | [5 empty] | 100 | Contractor - Planned |  | 2 | 66.67 | 11 | 1457.4 | 25.51
| Feeder Name: | Reidland Water | [5 empty] | 420 | ROW |  | 1 | 33.33 | 7 | 4255.8 | 74.49
| Feeder Number: | 224
| Feeder Location | 41224-Reidland Wat
| Customer Count | 50
| Circuit 5 Year Average (SAIDI |  |  |  | 176.3034
| Reporting Year (SAIDI |  | 84.646
| Circuit 5 Year Average (SAIFI |  |  |  | 0.887
| Reporting Year (SAIFI |  | 0.2188
| Total Circuit Length: |  |  |  |  | 2.9
| Date of Last Circuit Trim: |  |  |  |  | 2017
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | REIDLAND | [5 empty] | 110 | JPEC - Planned |  | 1 | 33.33 | 193 | 6095.4 | 19.8
| Feeder Name: | Epperson Rd | [5 empty] | 300 | Equipment Failure |  | 1 | 33.33 | 193 | 3287.4 | 10.68
[8 empty] | 420 | ROW |  | 1 | 33.33 | 193 | 21397.2 | 69.52
| Feeder Number: | 234
| Feeder Location | 41234-Epperson Rd
| Customer Count | 197
| Circuit 5 Year Average (SAIDI |  |  |  | 216.6188
| Reporting Year (SAIDI |  | 108.5935
| Circuit 5 Year Average (SAIFI |  |  |  | 1.7255
| Reporting Year (SAIFI |  | 0.9795
| Total Circuit Length: |  |  |  |  | 11.7
| Date of Last Circuit Trim: |  |  |  |  | 2017
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | REIDLAND | [5 empty] | 110 | JPEC - Planned |  | 1 | 20 | 94 | 987 | 7.36
| Feeder Name: | Walker Boat Yard | [5 empty] | 300 | Equipment Failure |  | 1 | 20 | 2 | 175.8 | 1.31
[8 empty] | 420 | ROW |  | 3 | 60 | 190 | 12245.4 | 91.33
| Feeder Number: | 244
| Feeder Location | 41244-Walker Boat
| Customer Count | 98
| Circuit 5 Year Average (SAIDI |  |  |  | 330.737
| Reporting Year (SAIDI |  | 124.4173
| Circuit 5 Year Average (SAIFI |  |  |  | 1.455
| Reporting Year (SAIFI |  | 1.9305
| Total Circuit Length: |  |  |  |  | 11
| Date of Last Circuit Trim: |  |  |  |  | 2017
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | SMITHLAND | [5 empty] | 100 | Contractor - Planned |  | 3 | 33.33 | 6 | 548.4 | 3.81
| Feeder Name: | Smithland | [5 empty] | 420 | ROW |  | 4 | 44.44 | 24 | 13752.6 | 95.45
[8 empty] | 500 | Lightning |  | 1 | 11.11 | 1 | 32.4 | 0.22
| Feeder Number: | 214
[8 empty] | 999 | Cause unknown |  | 1 | 11.11 | 1 | 75 | 0.52
| Feeder Location | 32214-Smithland
| Customer Count | 381
| Circuit 5 Year Average (SAIDI |  |  |  | 51.798
| Reporting Year (SAIDI |  | 36.0482
| Circuit 5 Year Average (SAIFI |  |  |  | 0.2999
| Reporting Year (SAIFI |  | 0.0629
| Total Circuit Length: |  |  |  |  | 30.2
| Date of Last Circuit Trim: |  |  |  |  | 2019
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | SMITHLAND | [5 empty] | 110 | JPEC - Planned |  | 4 | 12.12 | 6 | 453.6 | 0.24
| Feeder Name: | Tiline | [5 empty] | 300 | Equipment Failure |  | 4 | 12.12 | 77 | 38505.6 | 20.13
[8 empty] | 420 | ROW |  | 11 | 33.33 | 726 | 148953.6 | 77.87
| Feeder Number: | 224
[8 empty] | 500 | Lightning |  | 3 | 9.09 | 4 | 517.2 | 0.27
| Feeder Location | 32224-Tiline | [5 empty] | 510 | Wind - Not Trees |  | 1 | 3.03 | 1 | 87 | 0.05
| Customer Count | 558 | [5 empty] | 690 | Animal |  | 4 | 12.12 | 4 | 327 | 0.17
| Circuit 5 Year Average (SAIDI |  |  |  | 254.0883 |  |  | 810 | Load |  | 1 | 3.03 | 13 | 628.2 | 0.33
| Reporting Year (SAIDI |  | 267.0274 |  |  |  |  | 999 | Cause unknown |  | 5 | 15.15 | 21 | 1802.4 | 0.94
| Circuit 5 Year Average (SAIFI |  |  |  | 1.389
| Reporting Year (SAIFI |  | 1.3015
| Total Circuit Length: |  |  |  |  | 107.1
| Date of Last Circuit Trim: |  |  |  |  | 2019
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | SMITHLAND | [5 empty] | 110 | JPEC - Planned |  | 1 | 12.5 | 1 | 24 | 0.22
| Feeder Name: | Mitchell Store | [5 empty] | 420 | ROW |  | 3 | 37.5 | 41 | 8516.4 | 78.84
[8 empty] | 500 | Lightning |  | 2 | 25 | 7 | 781.2 | 7.23
| Feeder Number: | 244 | [11 empty] | 0
[8 empty] | 690 | Animal |  | 1 | 12.5 | 10 | 1378.2 | 12.76
| Feeder Location | 32244-Mitchell Store | [5 empty] | 999 | Cause unknown |  | 1 | 12.5 | 1 | 102 | 0.94
| Customer Count | 385
| Circuit 5 Year Average (SAIDI |  |  |  | 78.1515
| Reporting Year (SAIDI |  | 22.0979
| Circuit 5 Year Average (SAIFI |  |  |  | 0.9212
| Reporting Year (SAIFI |  | 0.1064
| Total Circuit Length: |  |  |  |  | 57.8
| Date of Last Circuit Trim: |  |  |  |  | 2019
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | SMITHLAND | [5 empty] | None | None |  | 0 | 0 | 0 | 0 | 0
| Feeder Name: | REC_00004485
| Feeder Number: | 3
| Feeder Location | 04485-REC_000044
| Customer Count | 0
| Circuit 5 Year Average (SAIDI |  |  |  | 0
| Reporting Year (SAIDI |  | 0
| Circuit 5 Year Average (SAIFI |  |  |  | 0
| Reporting Year (SAIFI |  | 0
Total Circuit Length:
Date of Last Circuit Trim:
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | STRAWBERRY HILL | [5 empty] | 110 | JPEC - Planned |  | 1 | 9.09 | 52 | 3634.8 | 1.73
| Feeder Name: | Hansen Rd | [5 empty] | 420 | ROW |  | 8 | 72.73 | 471 | 205984.8 | 98.17
[8 empty] | 810 | Load |  | 1 | 9.09 | 3 | 128.4 | 0.06
| Feeder Number: | 224
[8 empty] | 999 | Cause unknown |  | 1 | 9.09 | 1 | 66 | 0.03
| Feeder Location | 77224-Hansen Rd
| Customer Count | 731
| Circuit 5 Year Average (SAIDI |  |  |  | 138.3438
| Reporting Year (SAIDI |  | 281.9351
| Circuit 5 Year Average (SAIFI |  |  |  | 0.9644
| Reporting Year (SAIFI |  | 0.6447
| Total Circuit Length: |  |  |  |  | 31.5
| Date of Last Circuit Trim: |  |  |  |  | 2015
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | STRAWBERRY HILL | [5 empty] | None | None |  | 0 | 0 | 0 | 0 | 0
| Feeder Name: | Walmart
| Feeder Number: | 234
| Feeder Location | 77234-Walmart
| Customer Count | 542
| Circuit 5 Year Average (SAIDI |  |  |  | 10.0184
| Reporting Year (SAIDI |  | 0
| Circuit 5 Year Average (SAIFI |  |  |  | 0.2559
| Reporting Year (SAIFI |  | 0
| Total Circuit Length: |  |  |  |  | 9.8
| Date of Last Circuit Trim: |  |  |  |  | 2015
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | STRAWBERRY HILL | [5 empty] | None | None |  | 0 | 0 | 0 | 0 | 0
| Feeder Name: | CSI
| Feeder Number: | 254
| Feeder Location | 77254-CSI
| Customer Count | 87
| Circuit 5 Year Average (SAIDI |  |  |  | 1.2438
| Reporting Year (SAIDI |  | 0
| Circuit 5 Year Average (SAIFI |  |  |  | 0.2039
| Reporting Year (SAIFI |  | 0
| Total Circuit Length: |  |  |  |  | 5
| Date of Last Circuit Trim: |  |  |  |  | 2015
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | STRAWBERRY HILL | [5 empty] | None | None |  | 0 | 0 | 0 | 0 | 0
| Feeder Name: | Hwy 60
| Feeder Number: | 264
| Feeder Location | 77264-Hwy 60
| Customer Count | 13
| Circuit 5 Year Average (SAIDI |  |  |  | 0.5128
| Reporting Year (SAIDI |  | 0
| Circuit 5 Year Average (SAIFI |  |  |  | 0.1709
| Reporting Year (SAIFI |  | 0
| Total Circuit Length: |  |  |  |  | 1.8
| Date of Last Circuit Trim: |  |  |  |  | 2015
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | STRAWBERRY HILL | [5 empty] | None | None |  | 0 | 0 | 0 | 0 | 0
| Feeder Name: | REC_00000309
| Feeder Number: | 4
| Feeder Location | 77244-REC_000003
| Customer Count | 0
| Circuit 5 Year Average (SAIDI |  |  |  | 0
| Reporting Year (SAIDI |  | 0
| Circuit 5 Year Average (SAIFI |  |  |  | 0
| Reporting Year (SAIFI |  | 0
Total Circuit Length:
Date of Last Circuit Trim:
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | VULCAN | [5 empty] | None | None |  | 0 | 0 | 0 | 0 | 0
| Feeder Name: | Vulcan Pit
| Feeder Number: | 224
| Feeder Location | 45224-Vulcan Pit
| Customer Count | 0
| Circuit 5 Year Average (SAIDI |  |  |  | 0
| Reporting Year (SAIDI |  | 0
| Circuit 5 Year Average (SAIFI |  |  |  | 0
| Reporting Year (SAIFI |  | 0
| Total Circuit Length: |  |  |  |  | 2.4
Date of Last Circuit Trim:
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | VULCAN | [5 empty] | None | None |  | 0 | 0 | 0 | 0 | 0
| Feeder Name: | Vulcan 1 Rock Crush
| Feeder Number: | 234
| Feeder Location | 45234-Vulcan 1 Roc
| Customer Count | 1
| Circuit 5 Year Average (SAIDI |  |  |  | 164.3733
| Reporting Year (SAIDI |  | 0
| Circuit 5 Year Average (SAIFI |  |  |  | 1.4
| Reporting Year (SAIFI |  | 0
| Total Circuit Length: |  |  |  |  | 1.3
Date of Last Circuit Trim:
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | VULCAN | [5 empty] | 420 | ROW |  | 1 | 33.33 | 1 | 140.4 | 1.89
| Feeder Name: | Kinder Morgan | [5 empty] | 690 | Animal |  | 2 | 66.67 | 72 | 7304.4 | 98.11
| Feeder Number: | 244
| Feeder Location | 45244-Kinder Morga
| Customer Count | 35
| Circuit 5 Year Average (SAIDI |  |  |  | 1203.1007
| Reporting Year (SAIDI |  | 211.0488
| Circuit 5 Year Average (SAIFI |  |  |  | 11.5458
| Reporting Year (SAIFI |  | 2.0803
| Total Circuit Length: |  |  |  |  | 8.1
Date of Last Circuit Trim:
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | VULCAN | [5 empty] | 300 | Equipment Failure |  | 1 | 25 | 0 | 0 | 0
| Feeder Name: | Vulcan 2 Hwy 62 | [5 empty] | 690 | Animal |  | 2 | 50 | 1 | 105 | 100
[8 empty] | 810 | Load |  | 1 | 25 | 0 | 0 | 0
| Feeder Number: | 254
| Feeder Location | 45254-Vulcan 2 Hwy
| Customer Count | 2
| Circuit 5 Year Average (SAIDI |  |  |  | 253.3777
| Reporting Year (SAIDI |  | 55.8954
| Circuit 5 Year Average (SAIFI |  |  |  | 1.5957
| Reporting Year (SAIFI |  | 0.5319
| Total Circuit Length: |  |  |  |  | 5
Date of Last Circuit Trim:
Corrective Action Plan:
| Total Customer Hrs Off: |  |  | 125835.34 |  |  | Total Customer Mins Off: |  |  | 7550120.4
| Total Customers Affected: |  |  | 24936
| Total Outage Count: |  |  | 840
53040 | [7 empty] | /report/19020/rptcustom/oms/OMS_ANNUAL_RLBLTY_RPT_19020.xml.rpt

## 2023 Circuit Details
JACKSON PURCHASE ENERGY CORP.
Rev: 202306200609
| 2024-05-29 | 8:30 | [5 empty] | ANNUAL RELIABILITY REPORT
2023
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | BURNA | [5 empty] | 300 | Equipment Failure |  | 2 | 25 | 2 | 4.26 | 0.8
| Feeder Name: | Hampton | [5 empty] | 500 | Lightning |  | 2 | 25 | 18 | 48.72 | 9.14
[8 empty] | 510 | Wind - Not Trees |  | 3 | 37.5 | 28 | 476.79 | 89.47
| Feeder Number: | 214
[8 empty] | 999 | Cause unknown |  | 1 | 12.5 | 3 | 3.16 | 0.59
| Feeder Location | 14214-Hampton
| Customer Count | 85
| Circuit 5 Year Average (SAIDI |  |  |  | 94.0372
| Reporting Year (SAIDI |  | 335.8851
| Circuit 5 Year Average (SAIFI |  |  |  | 0.3452
| Reporting Year (SAIFI |  | 0.3288
| Total Circuit Length: |  |  |  |  | 11.8
| Date of Last Circuit Trim: |  |  |  |  | 2019
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | BURNA | [5 empty] | 100 | Contractor - Planned |  | 1 | 4.55 | 3 | 243.6 | 0.21
| Feeder Name: | Salem | [5 empty] | 110 | JPEC - Planned |  | 1 | 4.55 | 4 | 337.2 | 0.29
[8 empty] | 300 | Equipment Failure |  | 4 | 18.18 | 22 | 2189.4 | 1.86
| Feeder Number: | 244
[8 empty] | 420 | ROW |  | 8 | 36.36 | 148 | 81553.8 | 69.17
| Feeder Location | 14244-Salem | [5 empty] | 500 | Lightning |  | 2 | 9.09 | 2 | 164.4 | 0.14
| Customer Count | 325 | [5 empty] | 510 | Wind - Not Trees |  | 2 | 9.09 | 49 | 32538 | 27.6
| Circuit 5 Year Average (SAIDI |  |  |  | 240.3719 |  |  | 690 | Animal |  | 2 | 9.09 | 7 | 690 | 0.59
| Reporting Year (SAIDI |  | 251.2357 |  |  |  |  | 810 | Load |  | 1 | 4.55 | 1 | 85.2 | 0.07
[8 empty] | 999 | Cause unknown |  | 1 | 4.55 | 1 | 99.6 | 0.08
| Circuit 5 Year Average (SAIFI |  |  |  | 0.9162
| Reporting Year (SAIFI |  | 0.4559
| Total Circuit Length: |  |  |  |  | 52.9
| Date of Last Circuit Trim: |  |  |  |  | 2019
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | BURNA | [5 empty] | 100 | Contractor - Planned |  | 28 | 47.46 | 38 | 3604.8 | 4.01
| Feeder Name: | Smithland | [5 empty] | 110 | JPEC - Planned |  | 1 | 1.69 | 1 | 27.6 | 0.03
[8 empty] | 300 | Equipment Failure |  | 6 | 10.17 | 355 | 12870 | 14.32
| Feeder Number: | 254
[8 empty] | 420 | ROW |  | 9 | 15.25 | 222 | 46154.4 | 51.36
| Feeder Location | 14254-Smithland | [5 empty] | 500 | Lightning |  | 10 | 16.95 | 377 | 26622.6 | 29.63
| Customer Count | 350 | [5 empty] | 510 | Wind - Not Trees |  | 1 | 1.69 | 1 | 258 | 0.29
| Circuit 5 Year Average (SAIDI |  |  |  | 354.8228 |  |  | 690 | Animal |  | 1 | 1.69 | 1 | 61.8 | 0.07
| Reporting Year (SAIDI |  | 131.8794 |  |  |  |  | 710 | Motor Vehicle |  | 1 | 1.69 | 1 | 67.8 | 0.08
[8 empty] | 999 | Cause unknown |  | 2 | 3.39 | 3 | 196.2 | 0.22
| Circuit 5 Year Average (SAIFI |  |  |  | 2.7511
| Reporting Year (SAIFI |  | 1.0772
| Total Circuit Length: |  |  |  |  | 69.7
| Date of Last Circuit Trim: |  |  |  |  | 2019
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | CALVERT CITY | [5 empty] | 100 | Contractor - Planned |  | 2 | 10 | 2 | 275.4 | 1.68
| Feeder Name: | Hwy 95 | [5 empty] | 110 | JPEC - Planned |  | 1 | 5 | 1 | 22.8 | 0.14
[8 empty] | 300 | Equipment Failure |  | 3 | 15 | 5 | 758.4 | 4.63
| Feeder Number: | 214 | [11 empty] | 0
[8 empty] | 420 | ROW |  | 2 | 10 | 9 | 805.2 | 4.92
| Feeder Location | 43214-Hwy 95 | [5 empty] | 510 | Wind - Not Trees |  | 1 | 5 | 34 | 8961.6 | 54.7
| Customer Count | 250 | [5 empty] | 690 | Animal |  | 10 | 50 | 100 | 5387.4 | 32.89
| Circuit 5 Year Average (SAIDI |  |  |  | 123.713 |  |  | 700 | Member/Public Caused |  | 1 | 5 | 2 | 171 | 1.04
| Reporting Year (SAIDI |  | 35.8416
| Circuit 5 Year Average (SAIFI |  |  |  | 0.8807
| Reporting Year (SAIFI |  | 0.4
| Total Circuit Length: |  |  |  |  | 18.9
| Date of Last Circuit Trim: |  |  |  |  | 2017
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | CALVERT CITY | [5 empty] | 100 | Contractor - Planned |  | 5 | 10.2 | 48 | 4404.6 | 3.33
| Feeder Name: | Calvert Heights | [5 empty] | 110 | JPEC - Planned |  | 1 | 2.04 | 3 | 340.8 | 0.26
[8 empty] | 300 | Equipment Failure |  | 3 | 6.12 | 6 | 547.2 | 0.41
| Feeder Number: | 224
[8 empty] | 420 | ROW |  | 18 | 36.73 | 859 | 59752.8 | 45.12
| Feeder Location | 43224-Calvert Height | [5 empty] | 500 | Lightning |  | 2 | 4.08 | 32 | 1860 | 1.4
| Customer Count | 649 | [5 empty] | 510 | Wind - Not Trees |  | 6 | 12.24 | 100 | 56111.4 | 42.37
| Circuit 5 Year Average (SAIDI |  |  |  | 136.1173 |  |  | 690 | Animal |  | 10 | 20.41 | 119 | 6340.8 | 4.79
| Reporting Year (SAIDI |  | 92.0206 |  |  |  |  | 710 | Motor Vehicle |  | 1 | 2.04 | 34 | 2814 | 2.12
[8 empty] | 999 | Cause unknown |  | 3 | 6.12 | 5 | 266.4 | 0.2
| Circuit 5 Year Average (SAIFI |  |  |  | 1.1944
| Reporting Year (SAIFI |  | 1.3229
| Total Circuit Length: |  |  |  |  | 28.1
| Date of Last Circuit Trim: |  |  |  |  | 2017
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | CALVERT CITY | [5 empty] | 100 | Contractor - Planned |  | 1 | 9.09 | 1 | 255 | 2.41
| Feeder Name: | Gilbertsville | [5 empty] | 300 | Equipment Failure |  | 1 | 9.09 | 3 | 150.6 | 1.42
[8 empty] | 420 | ROW |  | 4 | 36.36 | 40 | 4341 | 40.98
| Feeder Number: | 234
[8 empty] | 500 | Lightning |  | 1 | 9.09 | 1 | 160.8 | 1.52
| Feeder Location | 43234-Gilbertsville | [5 empty] | 510 | Wind - Not Trees |  | 1 | 9.09 | 4 | 417.6 | 3.94
| Customer Count | 340 | [5 empty] | 690 | Animal |  | 1 | 9.09 | 3 | 134.4 | 1.27
| Circuit 5 Year Average (SAIDI |  |  |  | 81.3735 |  |  | 700 | Member/Public Caused |  | 1 | 9.09 | 19 | 2645.4 | 24.98
| Reporting Year (SAIDI |  | 12.7525 |  |  |  |  | 999 | Cause unknown |  | 1 | 9.09 | 27 | 2487 | 23.48
| Circuit 5 Year Average (SAIFI |  |  |  | 0.7251
| Reporting Year (SAIFI |  | 0.1175
| Total Circuit Length: |  |  |  |  | 23.7
| Date of Last Circuit Trim: |  |  |  |  | 2017
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | CALVERT CITY | [5 empty] | 300 | Equipment Failure |  | 1 | 100 | 1 | 40.8 | 100
| Feeder Name: | Industrial Park
| Feeder Number: | 244
| Feeder Location | 43244-Industrial Park
| Customer Count | 25
| Circuit 5 Year Average (SAIDI |  |  |  | 57.5373
| Reporting Year (SAIDI |  | 1.6451
| Circuit 5 Year Average (SAIFI |  |  |  | 0.4694
| Reporting Year (SAIFI |  | 0.0405
| Total Circuit Length: |  |  |  |  | 5
| Date of Last Circuit Trim: |  |  |  |  | 2017
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | COLEMAN ROAD | [5 empty] | 0 | BREC |  | 1 | 3.85 | 377 | 28947.6 | 19.85
| Feeder Name: | Conrad Heights | [5 empty] | 100 | Contractor - Planned |  | 3 | 11.54 | 42 | 4099.2 | 2.81
[8 empty] | 110 | JPEC - Planned |  | 1 | 3.85 | 0 | 0 | 0
| Feeder Number: | 224
[8 empty] | 300 | Equipment Failure |  | 5 | 19.23 | 60 | 12083.4 | 8.28
| Feeder Location | 30224-Conrad Height | [5 empty] | 420 | ROW |  | 6 | 23.08 | 455 | 89743.8 | 61.53
| Customer Count | 370 | [5 empty] | 510 | Wind - Not Trees |  | 2 | 7.69 | 6 | 3798 | 2.6
| Circuit 5 Year Average (SAIDI |  |  |  | 182.6258 |  |  | 690 | Animal |  | 5 | 19.23 | 40 | 6335.4 | 4.34
| Reporting Year (SAIDI |  | 242.3351 |  |  |  |  | 999 | Cause unknown |  | 3 | 11.54 | 8 | 841.2 | 0.58
| Circuit 5 Year Average (SAIFI |  |  |  | 1.7114
| Reporting Year (SAIFI |  | 1.2286
| Total Circuit Length: |  |  |  |  | 18.1
| Date of Last Circuit Trim: |  |  |  |  | 2018
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | COLEMAN ROAD | [5 empty] | 0 | BREC |  | 1 | 14.29 | 105 | 7885.8 | 43.81
| Feeder Name: | Hwy 60 Business | [5 empty] | 110 | JPEC - Planned |  | 3 | 42.86 | 3 | 208.8 | 1.16
[8 empty] | 300 | Equipment Failure |  | 2 | 28.57 | 117 | 9790.8 | 54.4
| Feeder Number: | 244
[8 empty] | 710 | Motor Vehicle |  | 1 | 14.29 | 1 | 113.4 | 0.63
| Feeder Location | 30244-Hwy 60 Busin
| Customer Count | 104
| Circuit 5 Year Average (SAIDI |  |  |  | 198.4465
| Reporting Year (SAIDI |  | 93.9063
| Circuit 5 Year Average (SAIFI |  |  |  | 0.9879
| Reporting Year (SAIFI |  | 1.1222
| Total Circuit Length: |  |  |  |  | 7.7
| Date of Last Circuit Trim: |  |  |  |  | 2018
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | COLEMAN ROAD | [5 empty] | 0 | BREC |  | 1 | 33.33 | 84 | 6374.4 | 75.18
| Feeder Name: | KY Oaks Mall | [5 empty] | 100 | Contractor - Planned |  | 1 | 33.33 | 1 | 163.2 | 1.92
[8 empty] | 510 | Wind - Not Trees |  | 1 | 33.33 | 3 | 1941.6 | 22.9
| Feeder Number: | 254
| Feeder Location | 30254-KY Oaks Mall
| Customer Count | 79
| Circuit 5 Year Average (SAIDI |  |  |  | 170.4795
| Reporting Year (SAIDI |  | 80.6759
| Circuit 5 Year Average (SAIFI |  |  |  | 0.6404
| Reporting Year (SAIFI |  | 1.0632
| Total Circuit Length: |  |  |  |  | 3.9
| Date of Last Circuit Trim: |  |  |  |  | 2018
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | CULP | [5 empty] | 100 | Contractor - Planned |  | 2 | 7.69 | 4 | 288 | 0.21
| Feeder Name: | Proform | [5 empty] | 110 | JPEC - Planned |  | 1 | 3.85 | 20 | 1408.2 | 1
[8 empty] | 300 | Equipment Failure |  | 1 | 3.85 | 1 | 53.4 | 0.04
| Feeder Number: | 214
[8 empty] | 420 | ROW |  | 8 | 30.77 | 145 | 13374.6 | 9.53
| Feeder Location | 42214-Proform | [5 empty] | 510 | Wind - Not Trees |  | 3 | 11.54 | 436 | 114921.6 | 81.86
| Customer Count | 428 | [5 empty] | 690 | Animal |  | 6 | 23.08 | 80 | 4765.8 | 3.39
| Circuit 5 Year Average (SAIDI |  |  |  | 159.4736 |  |  | 700 | Member/Public Caused |  | 1 | 3.85 | 20 | 1423.2 | 1.01
| Reporting Year (SAIDI |  | 268.6094 |  |  |  |  | 999 | Cause unknown |  | 4 | 15.38 | 76 | 4153.8 | 2.96
| Circuit 5 Year Average (SAIFI |  |  |  | 1.4328
| Reporting Year (SAIFI |  | 1.0191
| Total Circuit Length: |  |  |  |  | 25.8
| Date of Last Circuit Trim: |  |  |  |  | 2018
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | CULP | [5 empty] | 300 | Equipment Failure |  | 1 | 14.29 | 2 | 103.8 | 3.4
| Feeder Name: | Little Cypress | [5 empty] | 420 | ROW |  | 1 | 14.29 | 2 | 271.8 | 8.89
[8 empty] | 500 | Lightning |  | 1 | 14.29 | 1 | 126.6 | 4.14
| Feeder Number: | 224
[8 empty] | 510 | Wind - Not Trees |  | 2 | 28.57 | 4 | 2301.6 | 75.3
| Feeder Location | 42224-Little Cypress | [5 empty] | 690 | Animal |  | 1 | 14.29 | 1 | 46.8 | 1.53
| Customer Count | 49 | [5 empty] | 999 | Cause unknown |  | 1 | 14.29 | 3 | 205.8 | 6.73
| Circuit 5 Year Average (SAIDI |  |  |  | 114.0038
| Reporting Year (SAIDI |  | 47.175
| Circuit 5 Year Average (SAIFI |  |  |  | 1.3322
| Reporting Year (SAIFI |  | 0.082
| Total Circuit Length: |  |  |  |  | 8.1
| Date of Last Circuit Trim: |  |  |  |  | 2018
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | CULP | [5 empty] | 100 | Contractor - Planned |  | 1 | 4.55 | 1 | 247.8 | 0.22
| Feeder Name: | Possum Trot | [5 empty] | 300 | Equipment Failure |  | 1 | 4.55 | 205 | 27439.2 | 23.82
[8 empty] | 420 | ROW |  | 5 | 22.73 | 251 | 16015.8 | 13.9
| Feeder Number: | 234
[8 empty] | 500 | Lightning |  | 2 | 9.09 | 34 | 4250.4 | 3.69
| Feeder Location | 42234-Possum Trot | [5 empty] | 510 | Wind - Not Trees |  | 8 | 36.36 | 259 | 64891.2 | 56.32
| Customer Count | 203 | [5 empty] | 690 | Animal |  | 4 | 18.18 | 29 | 1910.4 | 1.66
| Circuit 5 Year Average (SAIDI |  |  |  | 368.496 |  |  | 999 | Cause unknown |  | 1 | 4.55 | 26 | 456.6 | 0.4
| Reporting Year (SAIDI |  | 319.4267
| Circuit 5 Year Average (SAIFI |  |  |  | 2.2811
| Reporting Year (SAIFI |  | 1.2749
| Total Circuit Length: |  |  |  |  | 18.7
| Date of Last Circuit Trim: |  |  |  |  | 2018
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | CULP | [5 empty] | 100 | Contractor - Planned |  | 2 | 3.17 | 8 | 297 | 0.07
| Feeder Name: | Sharpe | [5 empty] | 110 | JPEC - Planned |  | 2 | 3.17 | 5 | 703.8 | 0.17
[8 empty] | 300 | Equipment Failure |  | 4 | 6.35 | 22 | 2235 | 0.53
| Feeder Number: | 244
[8 empty] | 420 | ROW |  | 13 | 20.63 | 129 | 32731.8 | 7.76
| Feeder Location | 42244-Sharpe | [5 empty] | 500 | Lightning |  | 11 | 17.46 | 57 | 7995.6 | 1.89
| Customer Count | 1111 | [5 empty] | 510 | Wind - Not Trees |  | 11 | 17.46 | 1155 | 320771.4 | 76.02
| Circuit 5 Year Average (SAIDI |  |  |  | 181.547 |  |  | 690 | Animal |  | 13 | 20.63 | 27 | 1431.6 | 0.34
| Reporting Year (SAIDI |  | 288.7574 |  |  |  |  | 710 | Motor Vehicle |  | 3 | 4.76 | 1603 | 54568.2 | 12.93
[8 empty] | 999 | Cause unknown |  | 4 | 6.35 | 23 | 1214.4 | 0.29
| Circuit 5 Year Average (SAIFI |  |  |  | 1.9327
| Reporting Year (SAIFI |  | 1.443
| Total Circuit Length: |  |  |  |  | 79.9
| Date of Last Circuit Trim: |  |  |  |  | 2018
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | CUMBERLAND JPEC | [5 empty] | 110 | JPEC - Planned |  | 2 | 16.67 | 118 | 11947.2 | 67.87
| Feeder Name: | Pinckneyville | [5 empty] | 300 | Equipment Failure |  | 1 | 8.33 | 1 | 144 | 0.82
[8 empty] | 420 | ROW |  | 1 | 8.33 | 22 | 4119 | 23.4
| Feeder Number: | 224
[8 empty] | 500 | Lightning |  | 3 | 25 | 5 | 873.6 | 4.96
| Feeder Location | 15224-Pinckneyville | [5 empty] | 690 | Animal |  | 3 | 25 | 4 | 288 | 1.64
| Customer Count | 115 | [5 empty] | 700 | Member/Public Caused |  | 1 | 8.33 | 1 | 132 | 0.75
| Circuit 5 Year Average (SAIDI |  |  |  | 497.5181 |  |  | 999 | Cause unknown |  | 1 | 8.33 | 1 | 99 | 0.56
| Reporting Year (SAIDI |  | 104.0969
| Circuit 5 Year Average (SAIFI |  |  |  | 2.2567
| Reporting Year (SAIFI |  | 1.0281
| Total Circuit Length: |  |  |  |  | 27.6
| Date of Last Circuit Trim: |  |  |  |  | 2019
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | CUMBERLANDQUA | [5 empty] | 300 | Equipment Failure |  | 1 | 50 | 32 | 2217 | 38.98
| Feeder Name: | Quarry | [5 empty] | 510 | Wind - Not Trees |  | 1 | 50 | 31 | 3470.4 | 61.02
| Feeder Number: | 234
| Feeder Location | 15234-Quarry
| Customer Count | 31
| Circuit 5 Year Average (SAIDI |  |  |  | 306.6043
| Reporting Year (SAIDI |  | 113.0072
| Circuit 5 Year Average (SAIFI |  |  |  | 2.2273
| Reporting Year (SAIFI |  | 1.042
| Total Circuit Length: |  |  |  |  | 5.5
| Date of Last Circuit Trim: |  |  |  |  | 2019
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | DRAFFENVILLE | [5 empty] | 100 | Contractor - Planned |  | 3 | 15.79 | 7 | 756.6 | 0.32
| Feeder Name: | Draffenville | [5 empty] | 110 | JPEC - Planned |  | 3 | 15.79 | 7 | 1219.2 | 0.51
[8 empty] | 300 | Equipment Failure |  | 1 | 5.26 | 3 | 444.6 | 0.19
| Feeder Number: | 214
[8 empty] | 420 | ROW |  | 8 | 42.11 | 999 | 103123.2 | 43.17
| Feeder Location | 66214-Draffenville | [5 empty] | 510 | Wind - Not Trees |  | 1 | 5.26 | 492 | 132036.6 | 55.27
| Customer Count | 491 | [5 empty] | 690 | Animal |  | 3 | 15.79 | 13 | 1296 | 0.54
| Circuit 5 Year Average (SAIDI |  |  |  | 107.8453
| Reporting Year (SAIDI |  | 268.9954
| Circuit 5 Year Average (SAIFI |  |  |  | 0.8805
| Reporting Year (SAIFI |  | 2.9439
| Total Circuit Length: |  |  |  |  | 28.8
| Date of Last Circuit Trim: |  |  |  |  | 2019
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | FREEMONT | [5 empty] | 100 | Contractor - Planned |  | 32 | 29.09 | 59 | 7221.6 | 1.49
| Feeder Name: | Symsonia | [5 empty] | 110 | JPEC - Planned |  | 3 | 2.73 | 5 | 614.4 | 0.13
[8 empty] | 300 | Equipment Failure |  | 10 | 9.09 | 1123 | 127986 | 26.37
| Feeder Number: | 214
[8 empty] | 420 | ROW |  | 30 | 27.27 | 1103 | 193926.6 | 39.96
| Feeder Location | 51214-Symsonia | [5 empty] | 500 | Lightning |  | 9 | 8.18 | 134 | 27556.8 | 5.68
| Customer Count | 1012 | [5 empty] | 510 | Wind - Not Trees |  | 7 | 6.36 | 1026 | 118933.8 | 24.51
| Circuit 5 Year Average (SAIDI |  |  |  | 239.3374 |  |  | 690 | Animal |  | 11 | 10 | 11 | 828 | 0.17
| Reporting Year (SAIDI |  | 191.6378 |  |  |  |  | 700 | Member/Public Caused |  | 2 | 1.82 | 26 | 677.4 | 0.14
[8 empty] | 999 | Cause unknown |  | 6 | 5.45 | 134 | 7565.4 | 1.56
| Circuit 5 Year Average (SAIFI |  |  |  | 2.599
| Reporting Year (SAIFI |  | 1.1097
| Total Circuit Length: |  |  |  |  | 93.8
| Date of Last Circuit Trim: |  |  |  |  | 2019
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | FREEMONT | [5 empty] | 100 | Contractor - Planned |  | 4 | 11.43 | 10 | 1259.4 | 0.2
| Feeder Name: | McNeil Lane | [5 empty] | 300 | Equipment Failure |  | 4 | 11.43 | 13 | 3971.4 | 0.62
[8 empty] | 420 | ROW |  | 10 | 28.57 | 532 | 91054.2 | 14.16
| Feeder Number: | 224
[8 empty] | 500 | Lightning |  | 3 | 8.57 | 3 | 360 | 0.06
| Feeder Location | 51224-McNeil Lane | [5 empty] | 510 | Wind - Not Trees |  | 1 | 2.86 | 338 | 542912.4 | 84.44
| Customer Count | 334 | [5 empty] | 690 | Animal |  | 6 | 17.14 | 17 | 1075.8 | 0.17
| Circuit 5 Year Average (SAIDI |  |  |  | 484.4116 |  |  | 700 | Member/Public Caused |  | 1 | 2.86 | 1 | 182.4 | 0.03
| Reporting Year (SAIDI |  | 1625.5352 |  |  |  |  | 999 | Cause unknown |  | 6 | 17.14 | 17 | 2178.6 | 0.34
| Circuit 5 Year Average (SAIFI |  |  |  | 1.1791
| Reporting Year (SAIFI |  | 1.5929
| Total Circuit Length: |  |  |  |  | 41
| Date of Last Circuit Trim: |  |  |  |  | 2019
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | FREEMONT | [5 empty] | 100 | Contractor - Planned |  | 14 | 31.82 | 30 | 3660 | 3.3
| Feeder Name: | Freemont | [5 empty] | 110 | JPEC - Planned |  | 3 | 6.82 | 2 | 76.2 | 0.07
[8 empty] | 300 | Equipment Failure |  | 3 | 6.82 | 350 | 44962.8 | 40.51
| Feeder Number: | 244
[8 empty] | 420 | ROW |  | 7 | 15.91 | 96 | 30891 | 27.83
| Feeder Location | 51244-Freemont | [5 empty] | 500 | Lightning |  | 6 | 13.64 | 74 | 14433.6 | 13
| Customer Count | 334 | [5 empty] | 510 | Wind - Not Trees |  | 6 | 13.64 | 27 | 13158.6 | 11.86
| Circuit 5 Year Average (SAIDI |  |  |  | 141.0045 |  |  | 690 | Animal |  | 2 | 4.55 | 4 | 162 | 0.15
| Reporting Year (SAIDI |  | 134.5505 |  |  |  |  | 700 | Member/Public Caused |  | 1 | 2.27 | 18 | 3497.4 | 3.15
[8 empty] | 999 | Cause unknown |  | 2 | 4.55 | 2 | 151.8 | 0.14
| Circuit 5 Year Average (SAIFI |  |  |  | 0.9977
| Reporting Year (SAIFI |  | 1.0713
| Total Circuit Length: |  |  |  |  | 25.2
| Date of Last Circuit Trim: |  |  |  |  | 2019
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | FREEMONT | [5 empty] | 100 | Contractor - Planned |  | 10 | 52.63 | 19 | 3306.6 | 2.16
| Feeder Name: | Bonds Rd | [5 empty] | 300 | Equipment Failure |  | 1 | 5.26 | 1 | 84 | 0.05
[8 empty] | 420 | ROW |  | 5 | 26.32 | 414 | 48950.4 | 31.93
| Feeder Number: | 254
[8 empty] | 510 | Wind - Not Trees |  | 1 | 5.26 | 131 | 100782.6 | 65.75
| Feeder Location | 51254-Bonds Rd | [5 empty] | 690 | Animal |  | 2 | 10.53 | 2 | 158.4 | 0.1
| Customer Count | 127
| Circuit 5 Year Average (SAIDI |  |  |  | 762.5977
| Reporting Year (SAIDI |  | 792.9399
| Circuit 5 Year Average (SAIFI |  |  |  | 2.2329
| Reporting Year (SAIFI |  | 3.2573
| Total Circuit Length: |  |  |  |  | 17.3
| Date of Last Circuit Trim: |  |  |  |  | 2019
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | GRAND RIVERS | [5 empty] | 100 | Contractor - Planned |  | 3 | 9.38 | 6 | 981 | 0.33
| Feeder Name: | Iuka | [5 empty] | 110 | JPEC - Planned |  | 1 | 3.12 | 301 | 3597 | 1.21
[8 empty] | 300 | Equipment Failure |  | 4 | 12.5 | 105 | 12583.2 | 4.22
| Feeder Number: | 214
[8 empty] | 420 | ROW |  | 10 | 31.25 | 616 | 225461.4 | 75.62
| Feeder Location | 76214-Iuka | [5 empty] | 500 | Lightning |  | 2 | 6.25 | 16 | 2739.6 | 0.92
| Customer Count | 301 | [5 empty] | 510 | Wind - Not Trees |  | 6 | 18.75 | 36 | 39624.6 | 13.29
| Circuit 5 Year Average (SAIDI |  |  |  | 385.8091 |  |  | 690 | Animal |  | 3 | 9.38 | 33 | 2314.8 | 0.78
| Reporting Year (SAIDI |  | 749.641 |  |  |  |  | 700 | Member/Public Caused |  | 1 | 3.12 | 135 | 10386 | 3.48
[8 empty] | 999 | Cause unknown |  | 2 | 6.25 | 4 | 460.8 | 0.15
| Circuit 5 Year Average (SAIFI |  |  |  | 2.092
| Reporting Year (SAIFI |  | 2.0481
| Total Circuit Length: |  |  |  |  | 48.5
| Date of Last Circuit Trim: |  |  |  |  | 2016
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | GRAND RIVERS | [5 empty] | 100 | Contractor - Planned |  | 2 | 11.11 | 6 | 819 | 1.29
| Feeder Name: | Smithland | [5 empty] | 110 | JPEC - Planned |  | 1 | 5.56 | 2 | 240.6 | 0.38
[8 empty] | 300 | Equipment Failure |  | 2 | 11.11 | 6 | 606.6 | 0.96
| Feeder Number: | 224
[8 empty] | 420 | ROW |  | 9 | 50 | 379 | 50116.8 | 79.03
| Feeder Location | 76224-Smithland | [5 empty] | 500 | Lightning |  | 3 | 16.67 | 17 | 1276.2 | 2.01
| Customer Count | 312 | [5 empty] | 510 | Wind - Not Trees |  | 1 | 5.56 | 8 | 10353.6 | 16.33
| Circuit 5 Year Average (SAIDI |  |  |  | 4569.2141
| Reporting Year (SAIDI |  | 160.5299
| Circuit 5 Year Average (SAIFI |  |  |  | 1.4132
| Reporting Year (SAIFI |  | 1.214
| Total Circuit Length: |  |  |  |  | 31.4
| Date of Last Circuit Trim: |  |  |  |  | 2016
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | GRAND RIVERS | [5 empty] | 100 | Contractor - Planned |  | 7 | 23.33 | 26 | 3798.6 | 3.98
| Feeder Name: | Pelican GR #1 | [5 empty] | 110 | JPEC - Planned |  | 3 | 10 | 20 | 13081.8 | 13.72
[8 empty] | 300 | Equipment Failure |  | 2 | 6.67 | 5 | 767.4 | 0.8
| Feeder Number: | 244
[8 empty] | 420 | ROW |  | 8 | 26.67 | 202 | 53876.4 | 56.5
| Feeder Location | 76244-Pelican GR #1 | [5 empty] | 500 | Lightning |  | 1 | 3.33 | 1 | 170.4 | 0.18
| Customer Count | 379 | [5 empty] | 510 | Wind - Not Trees |  | 3 | 10 | 24 | 22891.8 | 24.01
| Circuit 5 Year Average (SAIDI |  |  |  | 173.2108 |  |  | 690 | Animal |  | 5 | 16.67 | 9 | 722.4 | 0.76
| Reporting Year (SAIDI |  | 142.1603 |  |  |  |  | 999 | Cause unknown |  | 1 | 3.33 | 1 | 49.2 | 0.05
| Circuit 5 Year Average (SAIFI |  |  |  | 1.3811
| Reporting Year (SAIFI |  | 0.533
| Total Circuit Length: |  |  |  |  | 23.9
| Date of Last Circuit Trim: |  |  |  |  | 2016
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | GRAND RIVERS | [5 empty] | 100 | Contractor - Planned |  | 2 | 6.06 | 10 | 1141.2 | 0.23
| Feeder Name: | Averitt GR #2 | [5 empty] | 110 | JPEC - Planned |  | 3 | 9.09 | 12 | 397.8 | 0.08
[8 empty] | 300 | Equipment Failure |  | 1 | 3.03 | 1 | 112.2 | 0.02
| Feeder Number: | 254
[8 empty] | 420 | ROW |  | 13 | 39.39 | 1610 | 325032 | 65.27
| Feeder Location | 76254-Averitt GR #2 | [5 empty] | 500 | Lightning |  | 3 | 9.09 | 700 | 115449 | 23.18
| Customer Count | 673 | [5 empty] | 510 | Wind - Not Trees |  | 2 | 6.06 | 6 | 8533.8 | 1.71
| Circuit 5 Year Average (SAIDI |  |  |  | 513.486 |  |  | 690 | Animal |  | 5 | 15.15 | 93 | 8937 | 1.79
| Reporting Year (SAIDI |  | 483.0888 |  |  |  |  | 730 | Fire |  | 1 | 3.03 | 4 | 219.6 | 0.04
[8 empty] | 810 | Load |  | 1 | 3.03 | 1 | 36.6 | 0.01
| Circuit 5 Year Average (SAIFI |  |  |  | 4.0923
[8 empty] | 999 | Cause unknown |  | 2 | 6.06 | 689 | 38151 | 7.66
| Reporting Year (SAIFI |  | 2.3929
| Total Circuit Length: |  |  |  |  | 46.4
| Date of Last Circuit Trim: |  |  |  |  | 2022
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | HIGHPOINT | [5 empty] | 100 | Contractor - Planned |  | 9 | 47.37 | 13 | 1258.8 | 36.41
| Feeder Name: | High Point | [5 empty] | 110 | JPEC - Planned |  | 1 | 5.26 | 1 | 167.4 | 4.84
[8 empty] | 420 | ROW |  | 1 | 5.26 | 8 | 366.6 | 10.6
| Feeder Number: | 214
[8 empty] | 500 | Lightning |  | 4 | 21.05 | 4 | 312 | 9.02
| Feeder Location | 29214-High Point | [5 empty] | 510 | Wind - Not Trees |  | 1 | 5.26 | 1 | 924 | 26.73
| Customer Count | 192 | [5 empty] | 690 | Animal |  | 3 | 15.79 | 10 | 428.4 | 12.39
| Circuit 5 Year Average (SAIDI |  |  |  | 131.5737
| Reporting Year (SAIDI |  | 6.565
| Circuit 5 Year Average (SAIFI |  |  |  | 1.0634
| Reporting Year (SAIFI |  | 0.0678
| Total Circuit Length: |  |  |  |  | 20.9
| Date of Last Circuit Trim: |  |  |  |  | 2015
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | HIGHPOINT | [5 empty] | 100 | Contractor - Planned |  | 7 | 23.33 | 20 | 2351.4 | 1.96
| Feeder Name: | Carneal Rd | [5 empty] | 300 | Equipment Failure |  | 3 | 10 | 3 | 259.8 | 0.22
[8 empty] | 420 | ROW |  | 2 | 6.67 | 52 | 17654.4 | 14.71
| Feeder Number: | 224
[8 empty] | 500 | Lightning |  | 6 | 20 | 289 | 58024.2 | 48.35
| Feeder Location | 29224-Carneal Rd | [5 empty] | 690 | Animal |  | 4 | 13.33 | 4 | 294.6 | 0.25
| Customer Count | 243 | [5 empty] | 700 | Member/Public Caused |  | 2 | 6.67 | 285 | 14267.4 | 11.89
| Circuit 5 Year Average (SAIDI |  |  |  | 365.1478 |  |  | 999 | Cause unknown |  | 6 | 20 | 319 | 27163.2 | 22.63
| Reporting Year (SAIDI |  | 238.7242
| Circuit 5 Year Average (SAIFI |  |  |  | 3.4469
| Reporting Year (SAIFI |  | 1.3124
| Total Circuit Length: |  |  |  |  | 33.1
| Date of Last Circuit Trim: |  |  |  |  | 2023
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | HIGHPOINT | [5 empty] | None | None |  | 0 | 0 | 0 | 0 | 0
| Feeder Name: | REC_00000340
| Feeder Number: | 3
| Feeder Location | 00340-REC_000003
| Customer Count | 0
| Circuit 5 Year Average (SAIDI |  |  |  | 0
| Reporting Year (SAIDI |  | 0
| Circuit 5 Year Average (SAIFI |  |  |  | 0
| Reporting Year (SAIFI |  | 0
Total Circuit Length:
Date of Last Circuit Trim:
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | HUSBANDS ROAD | [5 empty] | 110 | JPEC - Planned |  | 2 | 7.69 | 8 | 1274.4 | 0.78
| Feeder Name: | Husbands Rd | [5 empty] | 300 | Equipment Failure |  | 9 | 34.62 | 45 | 2371.8 | 1.46
[8 empty] | 420 | ROW |  | 3 | 11.54 | 918 | 139690.2 | 85.8
| Feeder Number: | 224
[8 empty] | 500 | Lightning |  | 1 | 3.85 | 1 | 58.2 | 0.04
| Feeder Location | 40224-Husbands Rd | [5 empty] | 510 | Wind - Not Trees |  | 3 | 11.54 | 37 | 13305.6 | 8.17
| Customer Count | 778 | [5 empty] | 690 | Animal |  | 7 | 26.92 | 13 | 1762.8 | 1.08
| Circuit 5 Year Average (SAIDI |  |  |  | 92.3702 |  |  | 999 | Cause unknown |  | 1 | 3.85 | 37 | 4351.2 | 2.67
| Reporting Year (SAIDI |  | 179.5578
| Circuit 5 Year Average (SAIFI |  |  |  | 0.789
| Reporting Year (SAIFI |  | 1.18
| Total Circuit Length: |  |  |  |  | 44.7
| Date of Last Circuit Trim: |  |  |  |  | 2018
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | HUSBANDS ROAD | [5 empty] | 100 | Contractor - Planned |  | 1 | 3.45 | 1 | 418.2 | 0.25
| Feeder Name: | Lydon Rd | [5 empty] | 300 | Equipment Failure |  | 5 | 17.24 | 56 | 5092.2 | 3.04
[8 empty] | 420 | ROW |  | 8 | 27.59 | 504 | 83441.4 | 49.88
| Feeder Number: | 234
[8 empty] | 500 | Lightning |  | 4 | 13.79 | 461 | 19985.4 | 11.95
| Feeder Location | 40234-Lydon Rd | [5 empty] | 510 | Wind - Not Trees |  | 2 | 6.9 | 51 | 7876.2 | 4.71
| Customer Count | 457 | [5 empty] | 690 | Animal |  | 4 | 13.79 | 169 | 24090.6 | 14.4
| Circuit 5 Year Average (SAIDI |  |  |  | 160.1654 |  |  | 700 | Member/Public Caused |  | 4 | 13.79 | 507 | 25515.6 | 15.25
| Reporting Year (SAIDI |  | 182.4989 |  |  |  |  | 999 | Cause unknown |  | 1 | 3.45 | 12 | 869.4 | 0.52
| Circuit 5 Year Average (SAIFI |  |  |  | 1.6561
| Reporting Year (SAIFI |  | 1.1089
| Total Circuit Length: |  |  |  |  | 32.2
| Date of Last Circuit Trim: |  |  |  |  | 2018
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | HUSBANDS ROAD | [5 empty] | 100 | Contractor - Planned |  | 1 | 3.45 | 3 | 466.2 | 0.23
| Feeder Name: | Clarkline Rd | [5 empty] | 110 | JPEC - Planned |  | 3 | 10.34 | 681 | 5128.8 | 2.54
[8 empty] | 300 | Equipment Failure |  | 7 | 24.14 | 1082 | 71417.4 | 35.35
| Feeder Number: | 244
[8 empty] | 420 | ROW |  | 5 | 17.24 | 49 | 10203.6 | 5.05
| Feeder Location | 40244-Clarkline Rd | [5 empty] | 510 | Wind - Not Trees |  | 11 | 37.93 | 845 | 114482.4 | 56.66
| Customer Count | 359 | [5 empty] | 690 | Animal |  | 2 | 6.9 | 6 | 353.4 | 0.17
| Circuit 5 Year Average (SAIDI |  |  |  | 170.5268
| Reporting Year (SAIDI |  | 318.7061
| Circuit 5 Year Average (SAIFI |  |  |  | 2.6219
| Reporting Year (SAIFI |  | 3.7805
| Total Circuit Length: |  |  |  |  | 26.4
| Date of Last Circuit Trim: |  |  |  |  | 2018
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | JOY | [5 empty] | 300 | Equipment Failure |  | 1 | 5 | 1 | 585.6 | 0.24
| Feeder Name: | Hampton South | [5 empty] | 420 | ROW |  | 9 | 45 | 412 | 110610 | 45.42
[8 empty] | 500 | Lightning |  | 2 | 10 | 31 | 2897.4 | 1.19
| Feeder Number: | 214
[8 empty] | 510 | Wind - Not Trees |  | 5 | 25 | 173 | 114985.2 | 47.21
| Feeder Location | 05214-Hampton Sout | [5 empty] | 700 | Member/Public Caused |  | 1 | 5 | 107 | 14232.6 | 5.84
| Customer Count | 183 | [5 empty] | 999 | Cause unknown |  | 2 | 10 | 2 | 237.6 | 0.1
| Circuit 5 Year Average (SAIDI |  |  |  | 649.9094
| Reporting Year (SAIDI |  | 627.5468
| Circuit 5 Year Average (SAIFI |  |  |  | 2.8172
| Reporting Year (SAIFI |  | 2.2485
| Total Circuit Length: |  |  |  |  | 57.6
| Date of Last Circuit Trim: |  |  |  |  | 2023
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | JOY | [5 empty] | 100 | Contractor - Planned |  | 1 | 25 | 1 | 181.2 | 1.04
| Feeder Name: | Carrsville | [5 empty] | 420 | ROW |  | 3 | 75 | 118 | 17228.4 | 98.96
| Feeder Number: | 244
| Feeder Location | 05244-Carrsville
| Customer Count | 71
| Circuit 5 Year Average (SAIDI |  |  |  | 208.4627
| Reporting Year (SAIDI |  | 243.6471
| Circuit 5 Year Average (SAIFI |  |  |  | 1.089
| Reporting Year (SAIFI |  | 1.6688
| Total Circuit Length: |  |  |  |  | 10.8
| Date of Last Circuit Trim: |  |  |  |  | 2016
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | JOY | [5 empty] | 100 | Contractor - Planned |  | 23 | 47.92 | 59 | 5607 | 8.66
| Feeder Name: | Lola | [5 empty] | 300 | Equipment Failure |  | 3 | 6.25 | 8 | 772.8 | 1.19
[8 empty] | 420 | ROW |  | 8 | 16.67 | 359 | 54404.4 | 84
| Feeder Number: | 254
[8 empty] | 500 | Lightning |  | 9 | 18.75 | 10 | 1533 | 2.37
| Feeder Location | 05254-Lola | [5 empty] | 510 | Wind - Not Trees |  | 1 | 2.08 | 2 | 1158.6 | 1.79
| Customer Count | 286 | [5 empty] | 690 | Animal |  | 1 | 2.08 | 2 | 185.4 | 0.29
| Circuit 5 Year Average (SAIDI |  |  |  | 254.2562 |  |  | 999 | Cause unknown |  | 3 | 6.25 | 8 | 1107 | 1.71
| Reporting Year (SAIDI |  | 190.0049
| Circuit 5 Year Average (SAIFI |  |  |  | 2.0312
| Reporting Year (SAIFI |  | 1.2538
| Total Circuit Length: |  |  |  |  | 56.4
| Date of Last Circuit Trim: |  |  |  |  | 2016
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | KANSAS | [5 empty] | 100 | Contractor - Planned |  | 8 | 22.22 | 10 | 1432.8 | 3.35
| Feeder Name: | Lowes | [5 empty] | 300 | Equipment Failure |  | 2 | 5.56 | 16 | 980.4 | 2.29
[8 empty] | 420 | ROW |  | 8 | 22.22 | 187 | 31145.4 | 72.9
| Feeder Number: | 214
[8 empty] | 500 | Lightning |  | 5 | 13.89 | 15 | 1900.2 | 4.45
| Feeder Location | 61214-Lowes | [5 empty] | 510 | Wind - Not Trees |  | 1 | 2.78 | 1 | 210.6 | 0.49
| Customer Count | 455 | [5 empty] | 690 | Animal |  | 10 | 27.78 | 91 | 6930.6 | 16.22
| Circuit 5 Year Average (SAIDI |  |  |  | 246.4077 |  |  | 700 | Member/Public Caused |  | 1 | 2.78 | 1 | 60 | 0.14
| Reporting Year (SAIDI |  | 68.4665 |  |  |  |  | 999 | Cause unknown |  | 1 | 2.78 | 2 | 66 | 0.15
| Circuit 5 Year Average (SAIFI |  |  |  | 1.5151
| Reporting Year (SAIFI |  | 0.4111
| Total Circuit Length: |  |  |  |  | 58.9
| Date of Last Circuit Trim: |  |  |  |  | 2022
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | KANSAS | [5 empty] | 100 | Contractor - Planned |  | 4 | 13.79 | 6 | 994.8 | 0.67
| Feeder Name: | Folsomdale | [5 empty] | 110 | JPEC - Planned |  | 1 | 3.45 | 8 | 745.8 | 0.51
[8 empty] | 300 | Equipment Failure |  | 2 | 6.9 | 3 | 376.2 | 0.25
| Feeder Number: | 224
[8 empty] | 420 | ROW |  | 13 | 44.83 | 39 | 16734 | 11.34
| Feeder Location | 61224-Folsomdale | [5 empty] | 500 | Lightning |  | 2 | 6.9 | 3 | 258.6 | 0.18
| Customer Count | 210 | [5 empty] | 510 | Wind - Not Trees |  | 3 | 10.34 | 211 | 127598.4 | 86.45
| Circuit 5 Year Average (SAIDI |  |  |  | 273.4505 |  |  | 690 | Animal |  | 2 | 6.9 | 9 | 530.4 | 0.36
| Reporting Year (SAIDI |  | 608.1637 |  |  |  |  | 700 | Member/Public Caused |  | 1 | 3.45 | 1 | 107.4 | 0.07
[8 empty] | 810 | Load |  | 1 | 3.45 | 3 | 257.4 | 0.17
| Circuit 5 Year Average (SAIFI |  |  |  | 1.4089
| Reporting Year (SAIFI |  | 1.0057
| Total Circuit Length: |  |  |  |  | 29.4
| Date of Last Circuit Trim: |  |  |  |  | 2016
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | KANSAS | [5 empty] | 100 | Contractor - Planned |  | 13 | 18.57 | 17 | 2793.6 | 0.39
| Feeder Name: | Melber | [5 empty] | 110 | JPEC - Planned |  | 2 | 2.86 | 8 | 1002 | 0.14
[8 empty] | 300 | Equipment Failure |  | 7 | 10 | 686 | 66351 | 9.25
| Feeder Number: | 234
[8 empty] | 320 | Clearance |  | 1 | 1.43 | 7 | 580.8 | 0.08
| Feeder Location | 61234-Melber | [5 empty] | 420 | ROW |  | 16 | 22.86 | 1024 | 253844.4 | 35.37
| Customer Count | 598 | [5 empty] | 500 | Lightning |  | 6 | 8.57 | 15 | 3728.4 | 0.52
| Circuit 5 Year Average (SAIDI |  |  |  | 352.7338 |  |  | 510 | Wind - Not Trees |  | 16 | 22.86 | 676 | 385713 | 53.75
| Reporting Year (SAIDI |  | 644.7974 |  |  |  |  | 690 | Animal |  | 2 | 2.86 | 3 | 468.6 | 0.07
[8 empty] | 810 | Load |  | 1 | 1.43 | 1 | 82.2 | 0.01
| Circuit 5 Year Average (SAIFI |  |  |  | 2.2573
[8 empty] | 999 | Cause unknown |  | 6 | 8.57 | 31 | 3042 | 0.42
| Reporting Year (SAIFI |  | 1.7117
| Total Circuit Length: |  |  |  |  | 54.1
| Date of Last Circuit Trim: |  |  |  |  | 2016
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | KANSAS | [5 empty] | 100 | Contractor - Planned |  | 15 | 21.43 | 25 | 3175.2 | 0.92
| Feeder Name: | Pottsville | [5 empty] | 110 | JPEC - Planned |  | 2 | 2.86 | 93 | 2650.8 | 0.77
[8 empty] | 300 | Equipment Failure |  | 8 | 11.43 | 1119 | 105369 | 30.5
| Feeder Number: | 244
[8 empty] | 420 | ROW |  | 19 | 27.14 | 704 | 128799 | 37.28
| Feeder Location | 61244-Pottsville | [5 empty] | 500 | Lightning |  | 11 | 15.71 | 268 | 57762.6 | 16.72
| Customer Count | 363 | [5 empty] | 510 | Wind - Not Trees |  | 6 | 8.57 | 8 | 4894.8 | 1.42
| Circuit 5 Year Average (SAIDI |  |  |  | 580.5492 |  |  | 690 | Animal |  | 3 | 4.29 | 13 | 917.4 | 0.27
| Reporting Year (SAIDI |  | 354.359 |  |  |  |  | 700 | Member/Public Caused |  | 2 | 2.86 | 377 | 15813 | 4.58
[8 empty] | 730 | Fire |  | 1 | 1.43 | 367 | 22050.6 | 6.38
| Circuit 5 Year Average (SAIFI |  |  |  | 4.1005
[8 empty] | 999 | Cause unknown |  | 3 | 4.29 | 36 | 4020 | 1.16
| Reporting Year (SAIFI |  | 3.0787
| Total Circuit Length: |  |  |  |  | 47
| Date of Last Circuit Trim: |  |  |  |  | 2023
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | KEVIL | [5 empty] | 100 | Contractor - Planned |  | 3 | 10.34 | 14 | 1897.2 | 0.94
| Feeder Name: | Hobbs Rd | [5 empty] | 300 | Equipment Failure |  | 2 | 6.9 | 2 | 766.8 | 0.38
[8 empty] | 420 | ROW |  | 10 | 34.48 | 656 | 159103.8 | 79.02
| Feeder Number: | 214
[8 empty] | 500 | Lightning |  | 5 | 17.24 | 7 | 1204.2 | 0.6
| Feeder Location | 28214-Hobbs Rd | [5 empty] | 510 | Wind - Not Trees |  | 2 | 6.9 | 51 | 37677.6 | 18.71
| Customer Count | 545 | [5 empty] | 690 | Animal |  | 7 | 24.14 | 16 | 696 | 0.35
| Circuit 5 Year Average (SAIDI |  |  |  | 245.6775
| Reporting Year (SAIDI |  | 291.7843
| Circuit 5 Year Average (SAIFI |  |  |  | 1.8009
| Reporting Year (SAIFI |  | 1.2031
| Total Circuit Length: |  |  |  |  | 52.7
| Date of Last Circuit Trim: |  |  |  |  | 2016
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | KEVIL | [5 empty] | 100 | Contractor - Planned |  | 6 | 13.64 | 17 | 2676 | 3.25
| Feeder Name: | Woodville Rd | [5 empty] | 110 | JPEC - Planned |  | 3 | 6.82 | 502 | 12252 | 14.9
[8 empty] | 300 | Equipment Failure |  | 5 | 11.36 | 26 | 1996.8 | 2.43
| Feeder Number: | 224
[8 empty] | 420 | ROW |  | 15 | 34.09 | 198 | 52315.2 | 63.63
| Feeder Location | 28224-Woodville Rd | [5 empty] | 500 | Lightning |  | 4 | 9.09 | 16 | 3357.6 | 4.08
| Customer Count | 501 | [5 empty] | 510 | Wind - Not Trees |  | 2 | 4.55 | 8 | 1105.2 | 1.34
| Circuit 5 Year Average (SAIDI |  |  |  | 145.8121 |  |  | 690 | Animal |  | 7 | 15.91 | 95 | 5058 | 6.15
| Reporting Year (SAIDI |  | 104.5035 |  |  |  |  | 999 | Cause unknown |  | 2 | 4.55 | 20 | 3454.2 | 4.2
| Circuit 5 Year Average (SAIFI |  |  |  | 1.2829
| Reporting Year (SAIFI |  | 1.0028
| Total Circuit Length: |  |  |  |  | 56.2
| Date of Last Circuit Trim: |  |  |  |  | 2016
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | KEVIL | [5 empty] | 100 | Contractor - Planned |  | 2 | 8.7 | 6 | 246.6 | 0.84
| Feeder Name: | Kelley Rd | [5 empty] | 110 | JPEC - Planned |  | 2 | 8.7 | 6 | 319.8 | 1.09
[8 empty] | 300 | Equipment Failure |  | 4 | 17.39 | 5 | 333 | 1.13
| Feeder Number: | 234
[8 empty] | 420 | ROW |  | 11 | 47.83 | 103 | 26988 | 91.78
| Feeder Location | 28234-Kelley Rd | [5 empty] | 500 | Lightning |  | 2 | 8.7 | 10 | 1290 | 4.39
| Customer Count | 427 | [5 empty] | 690 | Animal |  | 2 | 8.7 | 3 | 228.6 | 0.78
| Circuit 5 Year Average (SAIDI |  |  |  | 114.8697
| Reporting Year (SAIDI |  | 63.2613
| Circuit 5 Year Average (SAIFI |  |  |  | 1.082
| Reporting Year (SAIFI |  | 0.2414
| Total Circuit Length: |  |  |  |  | 47.9
| Date of Last Circuit Trim: |  |  |  |  | 2016
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | KREBS STATION RD | [5 empty] | 100 | Contractor - Planned |  | 2 | 8.7 | 7 | 1282.2 | 0.52
| Feeder Name: | Browns Plating | [5 empty] | 300 | Equipment Failure |  | 2 | 8.7 | 528 | 42076.8 | 17.14
[8 empty] | 420 | ROW |  | 8 | 34.78 | 805 | 120122.4 | 48.92
| Feeder Number: | 214
[8 empty] | 500 | Lightning |  | 2 | 8.7 | 1054 | 78382.2 | 31.92
| Feeder Location | 50214-Browns Platin | [5 empty] | 690 | Animal |  | 7 | 30.43 | 12 | 543.6 | 0.22
| Customer Count | 527 | [5 empty] | 700 | Member/Public Caused |  | 1 | 4.35 | 44 | 2592.6 | 1.06
| Circuit 5 Year Average (SAIDI |  |  |  | 176.9222 |  |  | 999 | Cause unknown |  | 1 | 4.35 | 10 | 538.2 | 0.22
| Reporting Year (SAIDI |  | 228.0368
| Circuit 5 Year Average (SAIFI |  |  |  | 1.7066
| Reporting Year (SAIFI |  | 2.0009
| Total Circuit Length: |  |  |  |  | 37.3
| Date of Last Circuit Trim: |  |  |  |  | 2016
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | KREBS STATION RD | [5 empty] | 100 | Contractor - Planned |  | 3 | 6.82 | 6 | 1199.4 | 0.3
| Feeder Name: | Old US 45 | [5 empty] | 110 | JPEC - Planned |  | 2 | 4.55 | 4 | 279.6 | 0.07
[8 empty] | 300 | Equipment Failure |  | 3 | 6.82 | 43 | 2949.6 | 0.73
| Feeder Number: | 224
[8 empty] | 420 | ROW |  | 15 | 34.09 | 947 | 250122.6 | 62.21
| Feeder Location | 50224-Old US 45 | [5 empty] | 500 | Lightning |  | 9 | 20.45 | 1845 | 136385.4 | 33.92
| Customer Count | 908 | [5 empty] | 510 | Wind - Not Trees |  | 1 | 2.27 | 1 | 189.6 | 0.05
| Circuit 5 Year Average (SAIDI |  |  |  | 193.3697 |  |  | 690 | Animal |  | 10 | 22.73 | 54 | 4453.8 | 1.11
| Reporting Year (SAIDI |  | 275.3982 |  |  |  |  | 999 | Cause unknown |  | 1 | 2.27 | 81 | 6488.4 | 1.61
| Circuit 5 Year Average (SAIFI |  |  |  | 1.591
| Reporting Year (SAIFI |  | 2.0314
| Total Circuit Length: |  |  |  |  | 82.7
| Date of Last Circuit Trim: |  |  |  |  | 2016
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | KREBS STATION RD | [5 empty] | 100 | Contractor - Planned |  | 5 | 33.33 | 7 | 925.8 | 1.23
| Feeder Name: | Clinton Rd | [5 empty] | 300 | Equipment Failure |  | 2 | 13.33 | 48 | 2712 | 3.6
[8 empty] | 420 | ROW |  | 3 | 20 | 59 | 13256.4 | 17.61
| Feeder Number: | 234
[8 empty] | 500 | Lightning |  | 4 | 26.67 | 764 | 58206.6 | 77.32
| Feeder Location | 50234-Clinton Rd | [5 empty] | 690 | Animal |  | 1 | 6.67 | 3 | 180 | 0.24
| Customer Count | 521
| Circuit 5 Year Average (SAIDI |  |  |  | 250.1856
| Reporting Year (SAIDI |  | 111.6864
| Circuit 5 Year Average (SAIFI |  |  |  | 1.9514
| Reporting Year (SAIFI |  | 1.466
| Total Circuit Length: |  |  |  |  | 19.3
| Date of Last Circuit Trim: |  |  |  |  | 2021
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | KREBS STATION RD | [5 empty] | 300 | Equipment Failure |  | 1 | 8.33 | 1 | 241.2 | 0.52
| Feeder Name: | New Hope | [5 empty] | 420 | ROW |  | 2 | 16.67 | 21 | 4038.6 | 8.75
[8 empty] | 500 | Lightning |  | 5 | 41.67 | 542 | 41142 | 89.17
| Feeder Number: | 244
[8 empty] | 690 | Animal |  | 4 | 33.33 | 12 | 716.4 | 1.55
| Feeder Location | 50244-New Hope
| Customer Count | 269
| Circuit 5 Year Average (SAIDI |  |  |  | 34.2884
| Reporting Year (SAIDI |  | 152.8804
| Circuit 5 Year Average (SAIFI |  |  |  | 0.4281
| Reporting Year (SAIFI |  | 2.014
| Total Circuit Length: |  |  |  |  | 36
| Date of Last Circuit Trim: |  |  |  |  | 2021
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | LaCENTER | [5 empty] | 100 | Contractor - Planned |  | 6 | 16.67 | 16 | 1698.6 | 3.89
| Feeder Name: | Damrons | [5 empty] | 300 | Equipment Failure |  | 3 | 8.33 | 4 | 708 | 1.62
[8 empty] | 420 | ROW |  | 8 | 22.22 | 93 | 14845.2 | 34.03
| Feeder Number: | 214
[8 empty] | 500 | Lightning |  | 10 | 27.78 | 54 | 11808.6 | 27.07
| Feeder Location | 26214-Damrons | [5 empty] | 510 | Wind - Not Trees |  | 1 | 2.78 | 43 | 6663 | 15.27
| Customer Count | 227 | [5 empty] | 690 | Animal |  | 6 | 16.67 | 239 | 7672.2 | 17.59
| Circuit 5 Year Average (SAIDI |  |  |  | 202.6289 |  |  | 700 | Member/Public Caused |  | 1 | 2.78 | 2 | 110.4 | 0.25
| Reporting Year (SAIDI |  | 65.4844 |  |  |  |  | 810 | Load |  | 1 | 2.78 | 3 | 123 | 0.28
| Circuit 5 Year Average (SAIFI |  |  |  | 2.4853
| Reporting Year (SAIFI |  | 1.0543
| Total Circuit Length: |  |  |  |  | 39.8
| Date of Last Circuit Trim: |  |  |  |  | 2015
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | LaCENTER | [5 empty] | 100 | Contractor - Planned |  | 4 | 8 | 45 | 4168.8 | 3
| Feeder Name: | Oscar | [5 empty] | 300 | Equipment Failure |  | 4 | 8 | 23 | 2592 | 1.87
[8 empty] | 420 | ROW |  | 20 | 40 | 221 | 108295.2 | 78.04
| Feeder Number: | 224
[8 empty] | 500 | Lightning |  | 10 | 20 | 19 | 1487.4 | 1.07
| Feeder Location | 26224-Oscar | [5 empty] | 510 | Wind - Not Trees |  | 2 | 4 | 47 | 6523.2 | 4.7
| Customer Count | 363 | [5 empty] | 690 | Animal |  | 4 | 8 | 368 | 12841.2 | 9.25
| Circuit 5 Year Average (SAIDI |  |  |  | 367.5048 |  |  | 700 | Member/Public Caused |  | 2 | 4 | 2 | 161.4 | 0.12
| Reporting Year (SAIDI |  | 298.5289 |  |  |  |  | 999 | Cause unknown |  | 4 | 8 | 23 | 2695.8 | 1.94
| Circuit 5 Year Average (SAIFI |  |  |  | 2.9579
| Reporting Year (SAIFI |  | 1.0144
| Total Circuit Length: |  |  |  |  | 69.4
| Date of Last Circuit Trim: |  |  |  |  | 2023
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | LEDBETTER | [5 empty] | 100 | Contractor - Planned |  | 2 | 7.41 | 4 | 401.4 | 0.64
| Feeder Name: | US 60 East | [5 empty] | 300 | Equipment Failure |  | 1 | 3.7 | 317 | 16632 | 26.51
[8 empty] | 420 | ROW |  | 7 | 25.93 | 349 | 18018 | 28.72
| Feeder Number: | 224
[8 empty] | 500 | Lightning |  | 2 | 7.41 | 5 | 367.2 | 0.59
| Feeder Location | 31224-US 60 East | [5 empty] | 510 | Wind - Not Trees |  | 7 | 25.93 | 27 | 22027.8 | 35.11
| Customer Count | 317 | [5 empty] | 690 | Animal |  | 1 | 3.7 | 1 | 135 | 0.22
| Circuit 5 Year Average (SAIDI |  |  |  | 120.6374 |  |  | 999 | Cause unknown |  | 7 | 25.93 | 30 | 5156.4 | 8.22
| Reporting Year (SAIDI |  | 69.5225
| Circuit 5 Year Average (SAIFI |  |  |  | 0.7436
| Reporting Year (SAIFI |  | 1.1015
| Total Circuit Length: |  |  |  |  | 35.6
| Date of Last Circuit Trim: |  |  |  |  | 2016
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | LEDBETTER | [5 empty] | 110 | JPEC - Planned |  | 2 | 33.33 | 78 | 1072.2 | 17.97
| Feeder Name: | River Crossing | [5 empty] | 300 | Equipment Failure |  | 1 | 16.67 | 38 | 3391.8 | 56.84
[8 empty] | 420 | ROW |  | 1 | 16.67 | 37 | 398.4 | 6.68
| Feeder Number: | 234
[8 empty] | 500 | Lightning |  | 1 | 16.67 | 3 | 447.6 | 7.5
| Feeder Location | 31234-River Crossin | [5 empty] | 510 | Wind - Not Trees |  | 1 | 16.67 | 1 | 657 | 11.01
| Customer Count | 36
| Circuit 5 Year Average (SAIDI |  |  |  | 64.0824
| Reporting Year (SAIDI |  | 93.5586
| Circuit 5 Year Average (SAIFI |  |  |  | 1.2966
| Reporting Year (SAIFI |  | 2.1517
| Total Circuit Length: |  |  |  |  | 5.2
| Date of Last Circuit Trim: |  |  |  |  | 2016
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | LEDBETTER | [5 empty] | 100 | Contractor - Planned |  | 7 | 13.46 | 16 | 1148.4 | 0.8
| Feeder Name: | Ledbetter | [5 empty] | 110 | JPEC - Planned |  | 2 | 3.85 | 6 | 352.8 | 0.25
[8 empty] | 300 | Equipment Failure |  | 2 | 3.85 | 13 | 1599 | 1.12
| Feeder Number: | 244
[8 empty] | 420 | ROW |  | 9 | 17.31 | 93 | 21715.8 | 15.19
| Feeder Location | 31244-Ledbetter | [5 empty] | 500 | Lightning |  | 6 | 11.54 | 71 | 13080 | 9.15
| Customer Count | 1026 | [5 empty] | 510 | Wind - Not Trees |  | 7 | 13.46 | 83 | 92330.4 | 64.56
| Circuit 5 Year Average (SAIDI |  |  |  | 172.1902 |  |  | 690 | Animal |  | 10 | 19.23 | 45 | 2842.8 | 1.99
| Reporting Year (SAIDI |  | 89.9897 |  |  |  |  | 700 | Member/Public Caused |  | 3 | 5.77 | 3 | 162.6 | 0.11
[8 empty] | 810 | Load |  | 1 | 1.92 | 1 | 39 | 0.03
| Circuit 5 Year Average (SAIFI |  |  |  | 1.1413
[8 empty] | 999 | Cause unknown |  | 5 | 9.62 | 37 | 9736.2 | 6.81
| Reporting Year (SAIFI |  | 0.0906
| Total Circuit Length: |  |  |  |  | 61.5
| Date of Last Circuit Trim: |  |  |  |  | 2022
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | LITTLE UNION | [5 empty] | 100 | Contractor - Planned |  | 3 | 13.04 | 7 | 946.8 | 0.3
| Feeder Name: | Airport | [5 empty] | 110 | JPEC - Planned |  | 5 | 21.74 | 13 | 1673.4 | 0.52
[8 empty] | 300 | Equipment Failure |  | 2 | 8.7 | 204 | 18525 | 5.77
| Feeder Number: | 214
[8 empty] | 420 | ROW |  | 1 | 4.35 | 3 | 1818 | 0.57
| Feeder Location | 39214-Airport | [5 empty] | 500 | Lightning |  | 2 | 8.7 | 104 | 8880.6 | 2.77
| Customer Count | 565 | [5 empty] | 510 | Wind - Not Trees |  | 2 | 8.7 | 1130 | 231792 | 72.24
| Circuit 5 Year Average (SAIDI |  |  |  | 143.2572 |  |  | 690 | Animal |  | 6 | 26.09 | 631 | 21990 | 6.85
| Reporting Year (SAIDI |  | 409.924 |  |  |  |  | 700 | Member/Public Caused |  | 2 | 8.7 | 320 | 35259.6 | 10.99
| Circuit 5 Year Average (SAIFI |  |  |  | 1.4173
| Reporting Year (SAIFI |  | 1.9984
| Total Circuit Length: |  |  |  |  | 36.2
| Date of Last Circuit Trim: |  |  |  |  | 2017
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | LITTLE UNION | [5 empty] | 110 | JPEC - Planned |  | 1 | 12.5 | 122 | 1512.6 | 1.67
| Feeder Name: | US 60 West | [5 empty] | 300 | Equipment Failure |  | 1 | 12.5 | 2 | 270.6 | 0.3
[8 empty] | 420 | ROW |  | 3 | 37.5 | 759 | 82956.6 | 91.62
| Feeder Number: | 224
[8 empty] | 500 | Lightning |  | 1 | 12.5 | 8 | 1030.2 | 1.14
| Feeder Location | 39224-US 60 West | [5 empty] | 690 | Animal |  | 2 | 25 | 123 | 4778.4 | 5.28
| Customer Count | 471
| Circuit 5 Year Average (SAIDI |  |  |  | 250.4255
| Reporting Year (SAIDI |  | 175.9539
| Circuit 5 Year Average (SAIFI |  |  |  | 2.1808
| Reporting Year (SAIFI |  | 1.6099
| Total Circuit Length: |  |  |  |  | 37.2
| Date of Last Circuit Trim: |  |  |  |  | 2022
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | LITTLE UNION | [5 empty] | 110 | JPEC - Planned |  | 2 | 25 | 3 | 783 | 5.86
| Feeder Name: | US 60 East Mall | [5 empty] | 300 | Equipment Failure |  | 1 | 12.5 | 17 | 2697.6 | 20.2
[8 empty] | 420 | ROW |  | 1 | 12.5 | 1 | 84.6 | 0.63
| Feeder Number: | 234
[8 empty] | 500 | Lightning |  | 1 | 12.5 | 4 | 723.6 | 5.42
| Feeder Location | 39234-US 60 East M | [5 empty] | 690 | Animal |  | 1 | 12.5 | 2 | 82.2 | 0.62
| Customer Count | 163 | [5 empty] | 999 | Cause unknown |  | 2 | 25 | 110 | 8982.6 | 67.27
| Circuit 5 Year Average (SAIDI |  |  |  | 115.5417
| Reporting Year (SAIDI |  | 55.1966
| Circuit 5 Year Average (SAIFI |  |  |  | 0.4818
| Reporting Year (SAIFI |  | 0.6759
| Total Circuit Length: |  |  |  |  | 10.4
| Date of Last Circuit Trim: |  |  |  |  | 2017
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | LITTLE UNION | [5 empty] | 100 | Contractor - Planned |  | 7 | 20 | 17 | 2776.8 | 8.36
| Feeder Name: | Roy Lee Rd | [5 empty] | 110 | JPEC - Planned |  | 3 | 8.57 | 6 | 754.8 | 2.27
[8 empty] | 300 | Equipment Failure |  | 2 | 5.71 | 23 | 2530.2 | 7.62
| Feeder Number: | 244
[8 empty] | 420 | ROW |  | 5 | 14.29 | 116 | 14251.8 | 42.91
| Feeder Location | 39244-Roy Lee Rd | [5 empty] | 500 | Lightning |  | 4 | 11.43 | 26 | 5560.8 | 16.74
| Customer Count | 539 | [5 empty] | 510 | Wind - Not Trees |  | 4 | 11.43 | 9 | 4353.6 | 13.11
| Circuit 5 Year Average (SAIDI |  |  |  | 507.9569 |  |  | 690 | Animal |  | 4 | 11.43 | 4 | 188.4 | 0.57
| Reporting Year (SAIDI |  | 26.4514 |  |  |  |  | 700 | Member/Public Caused |  | 4 | 11.43 | 35 | 2547 | 7.67
[8 empty] | 999 | Cause unknown |  | 2 | 5.71 | 4 | 253.2 | 0.76
| Circuit 5 Year Average (SAIFI |  |  |  | 1.9529
| Reporting Year (SAIFI |  | 0.2153
| Total Circuit Length: |  |  |  |  | 56.6
| Date of Last Circuit Trim: |  |  |  |  | 2022
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | LOVELACEVILLE | [5 empty] | 420 | ROW |  | 5 | 71.43 | 216 | 49932.6 | 98.54
| Feeder Name: | Blandville | [5 empty] | 500 | Lightning |  | 1 | 14.29 | 3 | 150.6 | 0.3
[8 empty] | 510 | Wind - Not Trees |  | 1 | 14.29 | 1 | 586.8 | 1.16
| Feeder Number: | 214
| Feeder Location | 49214-Blandville
| Customer Count | 132
| Circuit 5 Year Average (SAIDI |  |  |  | 410.0836
| Reporting Year (SAIDI |  | 377.7666
| Circuit 5 Year Average (SAIFI |  |  |  | 1.619
| Reporting Year (SAIFI |  | 1.6341
| Total Circuit Length: |  |  |  |  | 20.5
| Date of Last Circuit Trim: |  |  |  |  | 2015
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | LOVELACEVILLE | [5 empty] | 100 | Contractor - Planned |  | 51 | 71.83 | 72 | 6298.2 | 12.32
| Feeder Name: | Lovelaceville | [5 empty] | 300 | Equipment Failure |  | 2 | 2.82 | 272 | 17311.8 | 33.86
[8 empty] | 420 | ROW |  | 6 | 8.45 | 50 | 18558.6 | 36.3
| Feeder Number: | 224
[8 empty] | 500 | Lightning |  | 3 | 4.23 | 14 | 1600.2 | 3.13
| Feeder Location | 49224-Lovelaceville | [5 empty] | 510 | Wind - Not Trees |  | 2 | 2.82 | 2 | 1069.8 | 2.09
| Customer Count | 527 | [5 empty] | 690 | Animal |  | 3 | 4.23 | 8 | 325.8 | 0.64
| Circuit 5 Year Average (SAIDI |  |  |  | 246.9105 |  |  | 700 | Member/Public Caused |  | 2 | 2.82 | 28 | 1391.4 | 2.72
| Reporting Year (SAIDI |  | 35.1968 |  |  |  |  | 999 | Cause unknown |  | 2 | 2.82 | 94 | 4567.8 | 8.93
| Circuit 5 Year Average (SAIFI |  |  |  | 1.2115
| Reporting Year (SAIFI |  | 0.5159
| Total Circuit Length: |  |  |  |  | 58.5
| Date of Last Circuit Trim: |  |  |  |  | 2015
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | LOVELACEVILLE | [5 empty] | 100 | Contractor - Planned |  | 5 | 13.16 | 8 | 1404 | 0.55
| Feeder Name: | Cunningham | [5 empty] | 110 | JPEC - Planned |  | 3 | 7.89 | 7 | 454.2 | 0.18
[8 empty] | 300 | Equipment Failure |  | 3 | 7.89 | 3 | 240 | 0.09
| Feeder Number: | 234
[8 empty] | 420 | ROW |  | 14 | 36.84 | 1854 | 242684.4 | 94.75
| Feeder Location | 49234-Cunningham | [5 empty] | 500 | Lightning |  | 3 | 7.89 | 4 | 229.2 | 0.09
| Customer Count | 526 | [5 empty] | 510 | Wind - Not Trees |  | 2 | 5.26 | 35 | 9102 | 3.55
| Circuit 5 Year Average (SAIDI |  |  |  | 517.9396 |  |  | 690 | Animal |  | 3 | 7.89 | 7 | 600 | 0.23
| Reporting Year (SAIDI |  | 461.2279 |  |  |  |  | 700 | Member/Public Caused |  | 2 | 5.26 | 5 | 90 | 0.04
[8 empty] | 710 | Motor Vehicle |  | 1 | 2.63 | 2 | 181.8 | 0.07
| Circuit 5 Year Average (SAIFI |  |  |  | 1.5744
[8 empty] | 999 | Cause unknown |  | 2 | 5.26 | 4 | 1144.2 | 0.45
| Reporting Year (SAIFI |  | 3.5236
| Total Circuit Length: |  |  |  |  | 65.7
| Date of Last Circuit Trim: |  |  |  |  | 2015
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | MAXON | [5 empty] | 0 | BREC |  | 1 | 7.69 | 260 | 20514 | 33.04
| Feeder Name: | Maxon Rd | [5 empty] | 110 | JPEC - Planned |  | 1 | 7.69 | 6 | 510 | 0.82
[8 empty] | 300 | Equipment Failure |  | 3 | 23.08 | 553 | 37045.8 | 59.67
| Feeder Number: | 214
[8 empty] | 420 | ROW |  | 2 | 15.38 | 11 | 2016 | 3.25
| Feeder Location | 79214-Maxon Rd | [5 empty] | 510 | Wind - Not Trees |  | 1 | 7.69 | 1 | 411 | 0.66
| Customer Count | 261 | [5 empty] | 690 | Animal |  | 4 | 30.77 | 24 | 1452.6 | 2.34
| Circuit 5 Year Average (SAIDI |  |  |  | 165.1451 |  |  | 999 | Cause unknown |  | 1 | 7.69 | 2 | 132 | 0.21
| Reporting Year (SAIDI |  | 142.1621
| Circuit 5 Year Average (SAIFI |  |  |  | 1.611
| Reporting Year (SAIFI |  | 2.1221
| Total Circuit Length: |  |  |  |  | 16.4
| Date of Last Circuit Trim: |  |  |  |  | 2023
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | MAXON | [5 empty] | 0 | BREC |  | 1 | 5 | 333 | 26684.4 | 16.92
| Feeder Name: | Express | [5 empty] | 100 | Contractor - Planned |  | 1 | 5 | 49 | 40219.2 | 25.51
[8 empty] | 110 | JPEC - Planned |  | 1 | 5 | 317 | 7465.2 | 4.73
| Feeder Number: | 224
[8 empty] | 300 | Equipment Failure |  | 3 | 15 | 60 | 3269.4 | 2.07
| Feeder Location | 79224-Express | [5 empty] | 420 | ROW |  | 8 | 40 | 393 | 76357.8 | 48.43
| Customer Count | 395 | [5 empty] | 500 | Lightning |  | 4 | 20 | 14 | 108.6 | 0.07
| Circuit 5 Year Average (SAIDI |  |  |  | 132.3303 |  |  | 510 | Wind - Not Trees |  | 1 | 5 | 16 | 3485.4 | 2.21
| Reporting Year (SAIDI |  | 193.3828 |  |  |  |  | 690 | Animal |  | 1 | 5 | 2 | 76.2 | 0.05
| Circuit 5 Year Average (SAIFI |  |  |  | 1.2263
| Reporting Year (SAIFI |  | 0.9953
| Total Circuit Length: |  |  |  |  | 19
| Date of Last Circuit Trim: |  |  |  |  | 2023
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | MAXON | [5 empty] | 0 | BREC |  | 1 | 100 | 5 | 387.6 | 100
| Feeder Name: | Industrial Park
| Feeder Number: | 234
| Feeder Location | 79234-Industrial Park
| Customer Count | 4
| Circuit 5 Year Average (SAIDI |  |  |  | 39.133
| Reporting Year (SAIDI |  | 93.129
| Circuit 5 Year Average (SAIFI |  |  |  | 0.5769
| Reporting Year (SAIFI |  | 1.2019
| Total Circuit Length: |  |  |  |  | 2
| Date of Last Circuit Trim: |  |  |  |  | 2017
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | NEW YORK | [5 empty] | 100 | Contractor - Planned |  | 2 | 6.25 | 3 | 582 | 0.54
| Feeder Name: | Hinkleville | [5 empty] | 110 | JPEC - Planned |  | 2 | 6.25 | 354 | 27796.8 | 25.83
[8 empty] | 300 | Equipment Failure |  | 2 | 6.25 | 6 | 1173.6 | 1.09
| Feeder Number: | 214
[8 empty] | 420 | ROW |  | 10 | 31.25 | 436 | 69895.2 | 64.96
| Feeder Location | 47214-Hinkleville | [5 empty] | 500 | Lightning |  | 6 | 18.75 | 37 | 5056.2 | 4.7
| Customer Count | 265 | [5 empty] | 510 | Wind - Not Trees |  | 2 | 6.25 | 3 | 2298 | 2.14
| Circuit 5 Year Average (SAIDI |  |  |  | 896.0635 |  |  | 690 | Animal |  | 3 | 9.38 | 10 | 443.4 | 0.41
| Reporting Year (SAIDI |  | 263.9748 |  |  |  |  | 700 | Member/Public Caused |  | 1 | 3.12 | 1 | 7.2 | 0.01
[8 empty] | 810 | Load |  | 1 | 3.12 | 1 | 180 | 0.17
| Circuit 5 Year Average (SAIFI |  |  |  | 3.3371
[8 empty] | 999 | Cause unknown |  | 3 | 9.38 | 3 | 168.6 | 0.16
| Reporting Year (SAIFI |  | 1.6467
| Total Circuit Length: |  |  |  |  | 44.8
| Date of Last Circuit Trim: |  |  |  |  | 2022
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | NEW YORK | [5 empty] | 100 | Contractor - Planned |  | 4 | 10 | 8 | 612 | 0.32
| Feeder Name: | US 286 East Gage | [5 empty] | 110 | JPEC - Planned |  | 1 | 2.5 | 6 | 388.8 | 0.2
[8 empty] | 300 | Equipment Failure |  | 1 | 2.5 | 1 | 87 | 0.05
| Feeder Number: | 224
[8 empty] | 320 | Clearance |  | 1 | 2.5 | 9 | 842.4 | 0.44
| Feeder Location | 47224-US 286 East | [5 empty] | 420 | ROW |  | 15 | 37.5 | 167 | 22375.8 | 11.65
| Customer Count | 264 | [5 empty] | 500 | Lightning |  | 11 | 27.5 | 62 | 12206.4 | 6.35
| Circuit 5 Year Average (SAIDI |  |  |  | 422.3394 |  |  | 510 | Wind - Not Trees |  | 2 | 5 | 269 | 154874.4 | 80.62
| Reporting Year (SAIDI |  | 586.3116 |  |  |  |  | 700 | Member/Public Caused |  | 3 | 7.5 | 3 | 255.6 | 0.13
[8 empty] | 999 | Cause unknown |  | 2 | 5 | 10 | 463.8 | 0.24
| Circuit 5 Year Average (SAIFI |  |  |  | 1.6014
| Reporting Year (SAIFI |  | 1.0184
| Total Circuit Length: |  |  |  |  | 45.5
| Date of Last Circuit Trim: |  |  |  |  | 2015
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | NEW YORK | [5 empty] | 100 | Contractor - Planned |  | 4 | 12.9 | 6 | 817.8 | 0.39
| Feeder Name: | Blandville | [5 empty] | 300 | Equipment Failure |  | 2 | 6.45 | 224 | 17403 | 8.22
[8 empty] | 320 | Clearance |  | 1 | 3.23 | 3 | 53.4 | 0.03
| Feeder Number: | 234
[8 empty] | 420 | ROW |  | 16 | 51.61 | 759 | 95447.4 | 45.07
| Feeder Location | 47234-Blandville | [5 empty] | 500 | Lightning |  | 3 | 9.68 | 11 | 3445.2 | 1.63
| Customer Count | 219 | [5 empty] | 510 | Wind - Not Trees |  | 2 | 6.45 | 251 | 50916 | 24.04
| Circuit 5 Year Average (SAIDI |  |  |  | 847.2441 |  |  | 690 | Animal |  | 2 | 6.45 | 19 | 2498.4 | 1.18
| Reporting Year (SAIDI |  | 435.0966 |  |  |  |  | 700 | Member/Public Caused |  | 1 | 3.23 | 220 | 41191.8 | 19.45
| Circuit 5 Year Average (SAIFI |  |  |  | 4.2349
| Reporting Year (SAIFI |  | 3.4599
| Total Circuit Length: |  |  |  |  | 30.1
| Date of Last Circuit Trim: |  |  |  |  | 2022
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | NEW YORK | [5 empty] | 100 | Contractor - Planned |  | 7 | 21.88 | 37 | 5026.8 | 2.18
| Feeder Name: | Wickliffe | [5 empty] | 300 | Equipment Failure |  | 1 | 3.12 | 1 | 167.4 | 0.07
[8 empty] | 420 | ROW |  | 13 | 40.62 | 832 | 216156.6 | 93.82
| Feeder Number: | 244
[8 empty] | 500 | Lightning |  | 4 | 12.5 | 11 | 1173.6 | 0.51
| Feeder Location | 47244-Wickliffe | [5 empty] | 510 | Wind - Not Trees |  | 1 | 3.12 | 2 | 2512.2 | 1.09
| Customer Count | 355 | [5 empty] | 690 | Animal |  | 1 | 3.12 | 2 | 148.2 | 0.06
| Circuit 5 Year Average (SAIDI |  |  |  | 586.7261 |  |  | 999 | Cause unknown |  | 5 | 15.62 | 58 | 5208 | 2.26
| Reporting Year (SAIDI |  | 609.1664
| Circuit 5 Year Average (SAIFI |  |  |  | 2.6085
| Reporting Year (SAIFI |  | 2.3447
| Total Circuit Length: |  |  |  |  | 49.3
| Date of Last Circuit Trim: |  |  |  |  | 2021
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | NEW YORK | [5 empty] | 100 | Contractor - Planned |  | 8 | 20.51 | 15 | 2278.2 | 1.33
| Feeder Name: | Slater | [5 empty] | 300 | Equipment Failure |  | 5 | 12.82 | 366 | 41944.2 | 24.58
[8 empty] | 420 | ROW |  | 13 | 33.33 | 301 | 112220.4 | 65.76
| Feeder Number: | 254
[8 empty] | 500 | Lightning |  | 5 | 12.82 | 32 | 8231.4 | 4.82
| Feeder Location | 47254-Slater | [5 empty] | 510 | Wind - Not Trees |  | 1 | 2.56 | 2 | 578.4 | 0.34
| Customer Count | 358 | [5 empty] | 690 | Animal |  | 3 | 7.69 | 5 | 365.4 | 0.21
| Circuit 5 Year Average (SAIDI |  |  |  | 353.3157 |  |  | 700 | Member/Public Caused |  | 2 | 5.13 | 40 | 4231.2 | 2.48
| Reporting Year (SAIDI |  | 313.2807 |  |  |  |  | 999 | Cause unknown |  | 2 | 5.13 | 8 | 807 | 0.47
| Circuit 5 Year Average (SAIFI |  |  |  | 2.5918
| Reporting Year (SAIFI |  | 1.0217
| Total Circuit Length: |  |  |  |  | 67.8
| Date of Last Circuit Trim: |  |  |  |  | 2023
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | OLIVET CHURCH RD | [5 empty] | 110 | JPEC - Planned |  | 1 | 33.33 | 598 | 3069.6 | 63.67
| Feeder Name: | Olivet Ch Rd | [5 empty] | 420 | ROW |  | 1 | 33.33 | 11 | 1714.8 | 35.57
[8 empty] | 999 | Cause unknown |  | 1 | 33.33 | 2 | 36.6 | 0.76
| Feeder Number: | 214
| Feeder Location | 74214-Olivet Ch Rd
| Customer Count | 589
| Circuit 5 Year Average (SAIDI |  |  |  | 91.652
| Reporting Year (SAIDI |  | 5.2149
| Circuit 5 Year Average (SAIFI |  |  |  | 1.796
| Reporting Year (SAIFI |  | 1.0159
| Total Circuit Length: |  |  |  |  | 24
| Date of Last Circuit Trim: |  |  |  |  | 2022
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | OLIVET CHURCH RD | [5 empty] | 300 | Equipment Failure |  | 2 | 9.52 | 2 | 309.6 | 0.32
| Feeder Name: | Highland Ch Rd | [5 empty] | 420 | ROW |  | 6 | 28.57 | 196 | 35520.6 | 37.11
[8 empty] | 500 | Lightning |  | 1 | 4.76 | 3 | 1587 | 1.66
| Feeder Number: | 224
[8 empty] | 690 | Animal |  | 8 | 38.1 | 31 | 2157 | 2.25
| Feeder Location | 74224-Highland Ch | [5 empty] | 700 | Member/Public Caused |  | 3 | 14.29 | 518 | 55930.2 | 58.43
| Customer Count | 481 | [5 empty] | 999 | Cause unknown |  | 1 | 4.76 | 5 | 222.6 | 0.23
| Circuit 5 Year Average (SAIDI |  |  |  | 150.5201
| Reporting Year (SAIDI |  | 116.2559
| Circuit 5 Year Average (SAIFI |  |  |  | 1.7772
| Reporting Year (SAIFI |  | 1.0767
| Total Circuit Length: |  |  |  |  | 33.1
| Date of Last Circuit Trim: |  |  |  |  | 2015
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | OLIVET CHURCH RD | [5 empty] | None | None |  | 0 | 0 | 0 | 0 | 0
| Feeder Name: | Info Age Park
| Feeder Number: | 234
| Feeder Location | 74234-Info Age Park
| Customer Count | 8
| Circuit 5 Year Average (SAIDI |  |  |  | 119.5817
| Reporting Year (SAIDI |  | 0
| Circuit 5 Year Average (SAIFI |  |  |  | 0.925
| Reporting Year (SAIFI |  | 0
| Total Circuit Length: |  |  |  |  | 2.8
| Date of Last Circuit Trim: |  |  |  |  | 2015
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | PALMA | [5 empty] | 100 | Contractor - Planned |  | 6 | 20.69 | 11 | 1841.4 | 1.43
| Feeder Name: | Hwy 95 | [5 empty] | 110 | JPEC - Planned |  | 1 | 3.45 | 2 | 212.4 | 0.17
[8 empty] | 300 | Equipment Failure |  | 2 | 6.9 | 19 | 1056 | 0.82
| Feeder Number: | 214
[8 empty] | 420 | ROW |  | 2 | 6.9 | 109 | 20336.4 | 15.8
| Feeder Location | 54214-Hwy 95 | [5 empty] | 500 | Lightning |  | 3 | 10.34 | 6 | 1327.8 | 1.03
| Customer Count | 369 | [5 empty] | 510 | Wind - Not Trees |  | 9 | 31.03 | 382 | 88265.4 | 68.59
| Circuit 5 Year Average (SAIDI |  |  |  | 264.9072 |  |  | 690 | Animal |  | 3 | 10.34 | 5 | 340.8 | 0.26
| Reporting Year (SAIDI |  | 239.4275 |  |  |  |  | 700 | Member/Public Caused |  | 1 | 3.45 | 1 | 35.4 | 0.03
[8 empty] | 710 | Motor Vehicle |  | 1 | 3.45 | 55 | 14872.8 | 11.56
| Circuit 5 Year Average (SAIFI |  |  |  | 1.5804
[8 empty] | 999 | Cause unknown |  | 1 | 3.45 | 17 | 404.4 | 0.31
| Reporting Year (SAIFI |  | 1.0362
| Total Circuit Length: |  |  |  |  | 29.9
| Date of Last Circuit Trim: |  |  |  |  | 2015
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | PALMA | [5 empty] | 100 | Contractor - Planned |  | 1 | 16.67 | 2 | 252.6 | 0.34
| Feeder Name: | Draffenville | [5 empty] | 110 | JPEC - Planned |  | 1 | 16.67 | 3 | 121.2 | 0.16
[8 empty] | 300 | Equipment Failure |  | 2 | 33.33 | 10 | 2413.2 | 3.22
| Feeder Number: | 224
[8 empty] | 500 | Lightning |  | 1 | 16.67 | 25 | 1375.2 | 1.84
| Feeder Location | 54224-Draffenville | [5 empty] | 510 | Wind - Not Trees |  | 1 | 16.67 | 303 | 70684.8 | 94.44
| Customer Count | 302
| Circuit 5 Year Average (SAIDI |  |  |  | 156.9994
| Reporting Year (SAIDI |  | 234.4206
| Circuit 5 Year Average (SAIFI |  |  |  | 1.6443
| Reporting Year (SAIFI |  | 1.0049
| Total Circuit Length: |  |  |  |  | 21.7
| Date of Last Circuit Trim: |  |  |  |  | 2015
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | PALMA | [5 empty] | 100 | Contractor - Planned |  | 7 | 15.22 | 14 | 2024.4 | 0.96
| Feeder Name: | Palma | [5 empty] | 110 | JPEC - Planned |  | 4 | 8.7 | 13 | 777.6 | 0.37
[8 empty] | 300 | Equipment Failure |  | 4 | 8.7 | 66 | 5941.8 | 2.83
| Feeder Number: | 234
[8 empty] | 420 | ROW |  | 8 | 17.39 | 118 | 12843 | 6.12
| Feeder Location | 54234-Palma | [5 empty] | 500 | Lightning |  | 4 | 8.7 | 83 | 5608.2 | 2.67
| Customer Count | 744 | [5 empty] | 510 | Wind - Not Trees |  | 3 | 6.52 | 753 | 170363.4 | 81.14
| Circuit 5 Year Average (SAIDI |  |  |  | 153.9594 |  |  | 690 | Animal |  | 11 | 23.91 | 24 | 1272.6 | 0.61
| Reporting Year (SAIDI |  | 228.8938 |  |  |  |  | 700 | Member/Public Caused |  | 1 | 2.17 | 747 | 6013.2 | 2.86
[8 empty] | 710 | Motor Vehicle |  | 1 | 2.17 | 479 | 4869 | 2.32
| Circuit 5 Year Average (SAIFI |  |  |  | 1.8772
[8 empty] | 999 | Cause unknown |  | 3 | 6.52 | 5 | 244.2 | 0.12
| Reporting Year (SAIFI |  | 1.0117
| Total Circuit Length: |  |  |  |  | 57.4
| Date of Last Circuit Trim: |  |  |  |  | 2015
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | POSSUM TROT | [5 empty] | 300 | Equipment Failure |  | 2 | 6.67 | 5 | 1384.8 | 0.46
| Feeder Name: | Possum Trot | [5 empty] | 420 | ROW |  | 12 | 40 | 1175 | 130242 | 43.71
[8 empty] | 500 | Lightning |  | 5 | 16.67 | 55 | 9577.2 | 3.21
| Feeder Number: | 224
[8 empty] | 510 | Wind - Not Trees |  | 3 | 10 | 613 | 153921 | 51.65
| Feeder Location | 78224-Possum Trot | [5 empty] | 690 | Animal |  | 6 | 20 | 28 | 2616 | 0.88
| Customer Count | 545 | [5 empty] | 810 | Load |  | 1 | 3.33 | 3 | 216 | 0.07
| Circuit 5 Year Average (SAIDI |  |  |  | 237.3968 |  |  | 999 | Cause unknown |  | 1 | 3.33 | 1 | 42 | 0.01
| Reporting Year (SAIDI |  | 282.6368
| Circuit 5 Year Average (SAIFI |  |  |  | 2.3317
| Reporting Year (SAIFI |  | 2.1576
| Total Circuit Length: |  |  |  |  | 42.2
| Date of Last Circuit Trim: |  |  |  |  | 2015
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | POSSUM TROT | [5 empty] | 100 | Contractor - Planned |  | 13 | 43.33 | 29 | 2970.6 | 3.44
| Feeder Name: | Hwy 95 | [5 empty] | 110 | JPEC - Planned |  | 3 | 10 | 6 | 523.8 | 0.61
[8 empty] | 300 | Equipment Failure |  | 1 | 3.33 | 202 | 22287.6 | 25.77
| Feeder Number: | 234
[8 empty] | 420 | ROW |  | 6 | 20 | 268 | 56866.2 | 65.76
| Feeder Location | 78234-Hwy 95 | [5 empty] | 500 | Lightning |  | 3 | 10 | 22 | 1896.6 | 2.19
| Customer Count | 201 | [5 empty] | 510 | Wind - Not Trees |  | 1 | 3.33 | 2 | 261 | 0.3
| Circuit 5 Year Average (SAIDI |  |  |  | 159.7444 |  |  | 690 | Animal |  | 2 | 6.67 | 9 | 669.6 | 0.77
| Reporting Year (SAIDI |  | 283.4242 |  |  |  |  | 700 | Member/Public Caused |  | 1 | 3.33 | 12 | 1002.6 | 1.16
| Circuit 5 Year Average (SAIFI |  |  |  | 1.3786
| Reporting Year (SAIFI |  | 1.3357
| Total Circuit Length: |  |  |  |  | 15
| Date of Last Circuit Trim: |  |  |  |  | 2015
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | POSSUM TROT | [5 empty] | 100 | Contractor - Planned |  | 7 | 24.14 | 16 | 1607.4 | 1.1
| Feeder Name: | Industrial Loop | [5 empty] | 110 | JPEC - Planned |  | 1 | 3.45 | 1 | 126 | 0.09
[8 empty] | 300 | Equipment Failure |  | 1 | 3.45 | 3 | 4810.2 | 3.31
| Feeder Number: | 254
[8 empty] | 420 | ROW |  | 3 | 10.34 | 127 | 38610.6 | 26.53
| Feeder Location | 78254-Industrial Loo | [5 empty] | 500 | Lightning |  | 1 | 3.45 | 2 | 186 | 0.13
| Customer Count | 207 | [5 empty] | 510 | Wind - Not Trees |  | 5 | 17.24 | 310 | 94923.6 | 65.23
| Circuit 5 Year Average (SAIDI |  |  |  | 278.9439 |  |  | 690 | Animal |  | 3 | 10.34 | 5 | 346.2 | 0.24
| Reporting Year (SAIDI |  | 459.2999 |  |  |  |  | 700 | Member/Public Caused |  | 3 | 10.34 | 24 | 4195.2 | 2.88
[8 empty] | 999 | Cause unknown |  | 5 | 17.24 | 10 | 723 | 0.5
| Circuit 5 Year Average (SAIFI |  |  |  | 1.5522
| Reporting Year (SAIFI |  | 1.5
| Total Circuit Length: |  |  |  |  | 29.5
| Date of Last Circuit Trim: |  |  |  |  | 2015
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | POSSUM TROT | [5 empty] | None | None |  | 0 | 0 | 0 | 0 | 0
| Feeder Name: | CoalTek
| Feeder Number: | 264
| Feeder Location | 78264-CoalTek
| Customer Count | 2
| Circuit 5 Year Average (SAIDI |  |  |  | 34.86
| Reporting Year (SAIDI |  | 0
| Circuit 5 Year Average (SAIFI |  |  |  | 0.4
| Reporting Year (SAIFI |  | 0
| Total Circuit Length: |  |  |  |  | 3.9
| Date of Last Circuit Trim: |  |  |  |  | 2015
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | RAGLAND | [5 empty] | 100 | Contractor - Planned |  | 2 | 5.71 | 3 | 244.2 | 0.26
| Feeder Name: | Monkeys Eyebrow | [5 empty] | 420 | ROW |  | 16 | 45.71 | 208 | 29244.6 | 30.96
[8 empty] | 500 | Lightning |  | 8 | 22.86 | 168 | 8233.8 | 8.72
| Feeder Number: | 214
[8 empty] | 510 | Wind - Not Trees |  | 3 | 8.57 | 371 | 52696.8 | 55.79
| Feeder Location | 19214-Monkeys Eye | [5 empty] | 690 | Animal |  | 3 | 8.57 | 16 | 2632.2 | 2.79
| Customer Count | 238 | [5 empty] | 999 | Cause unknown |  | 3 | 8.57 | 12 | 1401 | 1.48
| Circuit 5 Year Average (SAIDI |  |  |  | 301.2728
| Reporting Year (SAIDI |  | 221.6407
| Circuit 5 Year Average (SAIFI |  |  |  | 2.1223
| Reporting Year (SAIFI |  | 1.5604
| Total Circuit Length: |  |  |  |  | 50
| Date of Last Circuit Trim: |  |  |  |  | 2022
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | RAGLAND | [5 empty] | 100 | Contractor - Planned |  | 10 | 35.71 | 13 | 2395.2 | 1.98
| Feeder Name: | Ragland | [5 empty] | 110 | JPEC - Planned |  | 1 | 3.57 | 2 | 10.8 | 0.01
[8 empty] | 300 | Equipment Failure |  | 4 | 14.29 | 519 | 35116.2 | 29.08
| Feeder Number: | 224
[8 empty] | 420 | ROW |  | 6 | 21.43 | 533 | 82072.2 | 67.95
| Feeder Location | 19224-Ragland | [5 empty] | 500 | Lightning |  | 1 | 3.57 | 2 | 112.8 | 0.09
| Customer Count | 222 | [5 empty] | 510 | Wind - Not Trees |  | 1 | 3.57 | 0 | 0 | 0
| Circuit 5 Year Average (SAIDI |  |  |  | 188.4802 |  |  | 690 | Animal |  | 3 | 10.71 | 10 | 691.8 | 0.57
| Reporting Year (SAIDI |  | 369.5625 |  |  |  |  | 810 | Load |  | 1 | 3.57 | 1 | 135.6 | 0.11
[8 empty] | 999 | Cause unknown |  | 1 | 3.57 | 1 | 241.2 | 0.2
| Circuit 5 Year Average (SAIFI |  |  |  | 1.7678
| Reporting Year (SAIFI |  | 2.4
| Total Circuit Length: |  |  |  |  | 33.4
| Date of Last Circuit Trim: |  |  |  |  | 2023
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | REIDLAND | [5 empty] | 100 | Contractor - Planned |  | 4 | 25 | 11 | 1617 | 0.43
| Feeder Name: | Ken Mar Rd | [5 empty] | 110 | JPEC - Planned |  | 1 | 6.25 | 2 | 151.8 | 0.04
[8 empty] | 420 | ROW |  | 4 | 25 | 55 | 69471 | 18.32
| Feeder Number: | 214
[8 empty] | 500 | Lightning |  | 1 | 6.25 | 354 | 30868.8 | 8.14
| Feeder Location | 41214-Ken Mar Rd | [5 empty] | 510 | Wind - Not Trees |  | 4 | 25 | 501 | 276687.6 | 72.97
| Customer Count | 341 | [5 empty] | 690 | Animal |  | 2 | 12.5 | 11 | 396.6 | 0.1
| Circuit 5 Year Average (SAIDI |  |  |  | 307.71
| Reporting Year (SAIDI |  | 812.3772
| Circuit 5 Year Average (SAIFI |  |  |  | 1.4616
| Reporting Year (SAIFI |  | 1.471
| Total Circuit Length: |  |  |  |  | 20.1
| Date of Last Circuit Trim: |  |  |  |  | 2022
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | REIDLAND | [5 empty] | 100 | Contractor - Planned |  | 3 | 27.27 | 11 | 1159.8 | 3.29
| Feeder Name: | Reidland Water | [5 empty] | 420 | ROW |  | 3 | 27.27 | 78 | 10572 | 29.98
[8 empty] | 510 | Wind - Not Trees |  | 3 | 27.27 | 54 | 23297.4 | 66.08
| Feeder Number: | 224
[8 empty] | 690 | Animal |  | 2 | 18.18 | 4 | 229.2 | 0.65
| Feeder Location | 41224-Reidland Wat
| Customer Count | 50
| Circuit 5 Year Average (SAIDI |  |  |  | 156.2896
| Reporting Year (SAIDI |  | 463.3496
| Circuit 5 Year Average (SAIFI |  |  |  | 0.8393
| Reporting Year (SAIFI |  | 1.5513
| Total Circuit Length: |  |  |  |  | 2.9
| Date of Last Circuit Trim: |  |  |  |  | 2017
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | REIDLAND | [5 empty] | 100 | Contractor - Planned |  | 9 | 32.14 | 20 | 1950.6 | 1.16
| Feeder Name: | Epperson Rd | [5 empty] | 110 | JPEC - Planned |  | 3 | 10.71 | 32 | 2622.6 | 1.56
[8 empty] | 420 | ROW |  | 8 | 28.57 | 343 | 114045.6 | 67.68
| Feeder Number: | 234
[8 empty] | 500 | Lightning |  | 1 | 3.57 | 1 | 57 | 0.03
| Feeder Location | 41234-Epperson Rd | [5 empty] | 510 | Wind - Not Trees |  | 5 | 17.86 | 206 | 49677.6 | 29.48
| Customer Count | 197 | [5 empty] | 690 | Animal |  | 2 | 7.14 | 5 | 157.8 | 0.09
| Circuit 5 Year Average (SAIDI |  |  |  | 328.2813
| Reporting Year (SAIDI |  | 578.7947
| Circuit 5 Year Average (SAIFI |  |  |  | 1.4576
| Reporting Year (SAIFI |  | 1.7408
| Total Circuit Length: |  |  |  |  | 11.7
| Date of Last Circuit Trim: |  |  |  |  | 2017
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | REIDLAND | [5 empty] | 100 | Contractor - Planned |  | 4 | 23.53 | 4 | 370.2 | 0.28
| Feeder Name: | Walker Boat Yard | [5 empty] | 420 | ROW |  | 6 | 35.29 | 134 | 84583.8 | 63.25
[8 empty] | 500 | Lightning |  | 1 | 5.88 | 12 | 3166.8 | 2.37
| Feeder Number: | 244
[8 empty] | 510 | Wind - Not Trees |  | 1 | 5.88 | 97 | 42308.4 | 31.64
| Feeder Location | 41244-Walker Boat | [5 empty] | 690 | Animal |  | 1 | 5.88 | 13 | 1180.2 | 0.88
| Customer Count | 98 | [5 empty] | 999 | Cause unknown |  | 4 | 23.53 | 30 | 2110.8 | 1.58
| Circuit 5 Year Average (SAIDI |  |  |  | 352.4213
| Reporting Year (SAIDI |  | 859.417
| Circuit 5 Year Average (SAIFI |  |  |  | 1.1238
| Reporting Year (SAIFI |  | 1.3615
| Total Circuit Length: |  |  |  |  | 11
| Date of Last Circuit Trim: |  |  |  |  | 2017
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | SMITHLAND | [5 empty] | 100 | Contractor - Planned |  | 4 | 22.22 | 18 | 3358.8 | 12.56
| Feeder Name: | Smithland | [5 empty] | 300 | Equipment Failure |  | 3 | 16.67 | 9 | 1285.8 | 4.81
[8 empty] | 420 | ROW |  | 4 | 22.22 | 157 | 20058 | 75.01
| Feeder Number: | 214
[8 empty] | 500 | Lightning |  | 2 | 11.11 | 2 | 718.2 | 2.69
| Feeder Location | 32214-Smithland | [5 empty] | 510 | Wind - Not Trees |  | 1 | 5.56 | 2 | 934.8 | 3.5
| Customer Count | 381 | [5 empty] | 690 | Animal |  | 2 | 11.11 | 3 | 171 | 0.64
| Circuit 5 Year Average (SAIDI |  |  |  | 130.4128 |  |  | 810 | Load |  | 1 | 5.56 | 2 | 87 | 0.33
| Reporting Year (SAIDI |  | 52.5798 |  |  |  |  | 999 | Cause unknown |  | 1 | 5.56 | 2 | 125.4 | 0.47
| Circuit 5 Year Average (SAIFI |  |  |  | 0.9316
| Reporting Year (SAIFI |  | 0.4115
| Total Circuit Length: |  |  |  |  | 30.2
| Date of Last Circuit Trim: |  |  |  |  | 2019
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | SMITHLAND | [5 empty] | 110 | JPEC - Planned |  | 4 | 8.51 | 41 | 1895.4 | 0.59
| Feeder Name: | Tiline | [5 empty] | 300 | Equipment Failure |  | 4 | 8.51 | 259 | 22842 | 7.14
[8 empty] | 420 | ROW |  | 14 | 29.79 | 203 | 185892.6 | 58.11
| Feeder Number: | 224
[8 empty] | 500 | Lightning |  | 10 | 21.28 | 100 | 16071 | 5.02
| Feeder Location | 32224-Tiline | [5 empty] | 510 | Wind - Not Trees |  | 3 | 6.38 | 47 | 37038 | 11.58
| Customer Count | 558 | [5 empty] | 690 | Animal |  | 5 | 10.64 | 18 | 1723.8 | 0.54
| Circuit 5 Year Average (SAIDI |  |  |  | 320.495 |  |  | 700 | Member/Public Caused |  | 1 | 2.13 | 115 | 36376.8 | 11.37
| Reporting Year (SAIDI |  | 333.2499 |  |  |  |  | 999 | Cause unknown |  | 6 | 12.77 | 156 | 18078 | 5.65
| Circuit 5 Year Average (SAIFI |  |  |  | 1.5163
| Reporting Year (SAIFI |  | 0.4643
| Total Circuit Length: |  |  |  |  | 107.1
| Date of Last Circuit Trim: |  |  |  |  | 2019
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | SMITHLAND | [5 empty] | 300 | Equipment Failure |  | 2 | 6.06 | 3 | 446.4 | 0.67
| Feeder Name: | Mitchell Store | [5 empty] | 420 | ROW |  | 10 | 30.3 | 456 | 50586.6 | 75.37
[8 empty] | 500 | Lightning |  | 5 | 15.15 | 10 | 1251 | 1.86
| Feeder Number: | 244
[8 empty] | 510 | Wind - Not Trees |  | 1 | 3.03 | 2 | 1742.4 | 2.6
| Feeder Location | 32244-Mitchell Store | [5 empty] | 690 | Animal |  | 5 | 15.15 | 63 | 4650 | 6.93
| Customer Count | 385 | [5 empty] | 700 | Member/Public Caused |  | 3 | 9.09 | 59 | 6273.6 | 9.35
| Circuit 5 Year Average (SAIDI |  |  |  | 207.1416 |  |  | 999 | Cause unknown |  | 7 | 21.21 | 32 | 2172 | 3.24
| Reporting Year (SAIDI |  | 131.2635
| Circuit 5 Year Average (SAIFI |  |  |  | 1.4837
| Reporting Year (SAIFI |  | 1.1832
| Total Circuit Length: |  |  |  |  | 57.8
| Date of Last Circuit Trim: |  |  |  |  | 2019
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | SMITHLAND | [5 empty] | None | None |  | 0 | 0 | 0 | 0 | 0
| Feeder Name: | REC_00004485
| Feeder Number: | 3
| Feeder Location | 04485-REC_000044
| Customer Count | 0
| Circuit 5 Year Average (SAIDI |  |  |  | 0
| Reporting Year (SAIDI |  | 0
| Circuit 5 Year Average (SAIFI |  |  |  | 0
| Reporting Year (SAIFI |  | 0
Total Circuit Length:
Date of Last Circuit Trim:
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | STRAWBERRY HILL | [5 empty] | 110 | JPEC - Planned |  | 4 | 11.43 | 10 | 829.2 | 0.32
| Feeder Name: | Hansen Rd | [5 empty] | 300 | Equipment Failure |  | 6 | 17.14 | 270 | 64353.6 | 24.56
[8 empty] | 420 | ROW |  | 12 | 34.29 | 672 | 61253.4 | 23.38
| Feeder Number: | 224
[8 empty] | 500 | Lightning |  | 1 | 2.86 | 2 | 297 | 0.11
| Feeder Location | 77224-Hansen Rd | [5 empty] | 530 | Flood |  | 2 | 5.71 | 964 | 132919.2 | 50.73
| Customer Count | 731 | [5 empty] | 690 | Animal |  | 6 | 17.14 | 11 | 465 | 0.18
| Circuit 5 Year Average (SAIDI |  |  |  | 126.2383 |  |  | 999 | Cause unknown |  | 4 | 11.43 | 41 | 1906.8 | 0.73
| Reporting Year (SAIDI |  | 181.9285
| Circuit 5 Year Average (SAIFI |  |  |  | 1.3323
| Reporting Year (SAIFI |  | 1.3194
| Total Circuit Length: |  |  |  |  | 31.5
| Date of Last Circuit Trim: |  |  |  |  | 2015
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | STRAWBERRY HILL | [5 empty] | None | None |  | 0 | 0 | 0 | 0 | 0
| Feeder Name: | Walmart
| Feeder Number: | 234
| Feeder Location | 77234-Walmart
| Customer Count | 542
| Circuit 5 Year Average (SAIDI |  |  |  | 66.2029
| Reporting Year (SAIDI |  | 0
| Circuit 5 Year Average (SAIFI |  |  |  | 0.4528
| Reporting Year (SAIFI |  | 0
| Total Circuit Length: |  |  |  |  | 9.8
| Date of Last Circuit Trim: |  |  |  |  | 2015
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | STRAWBERRY HILL | [5 empty] | 999 | Cause unknown |  | 1 | 100 | 1 | 67.2 | 100
| Feeder Name: | CSI
| Feeder Number: | 254
| Feeder Location | 77254-CSI
| Customer Count | 87
| Circuit 5 Year Average (SAIDI |  |  |  | 2.3182
| Reporting Year (SAIDI |  | 0.7685
| Circuit 5 Year Average (SAIFI |  |  |  | 0.3987
| Reporting Year (SAIFI |  | 0.0115
| Total Circuit Length: |  |  |  |  | 5
| Date of Last Circuit Trim: |  |  |  |  | 2015
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | STRAWBERRY HILL | [5 empty] | None | None |  | 0 | 0 | 0 | 0 | 0
| Feeder Name: | Hwy 60
| Feeder Number: | 264
| Feeder Location | 77264-Hwy 60
| Customer Count | 13
| Circuit 5 Year Average (SAIDI |  |  |  | 49.8632
| Reporting Year (SAIDI |  | 0
| Circuit 5 Year Average (SAIFI |  |  |  | 0.3419
| Reporting Year (SAIFI |  | 0
| Total Circuit Length: |  |  |  |  | 1.8
| Date of Last Circuit Trim: |  |  |  |  | 2015
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | STRAWBERRY HILL | [5 empty] | None | None |  | 0 | 0 | 0 | 0 | 0
| Feeder Name: | REC_00000309
| Feeder Number: | 4
| Feeder Location | 77244-REC_000003
| Customer Count | 0
| Circuit 5 Year Average (SAIDI |  |  |  | 0
| Reporting Year (SAIDI |  | 0
| Circuit 5 Year Average (SAIFI |  |  |  | 0
| Reporting Year (SAIFI |  | 0
Total Circuit Length:
Date of Last Circuit Trim:
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | VULCAN | [5 empty] | None | None |  | 0 | 0 | 0 | 0 | 0
| Feeder Name: | Vulcan Pit
| Feeder Number: | 224
| Feeder Location | 45224-Vulcan Pit
| Customer Count | 0
| Circuit 5 Year Average (SAIDI |  |  |  | 0
| Reporting Year (SAIDI |  | 0
| Circuit 5 Year Average (SAIFI |  |  |  | 0
| Reporting Year (SAIFI |  | 0
| Total Circuit Length: |  |  |  |  | 2.4
Date of Last Circuit Trim:
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | VULCAN | [5 empty] | None | None |  | 0 | 0 | 0 | 0 | 0
| Feeder Name: | Vulcan 1 Rock Crush
| Feeder Number: | 234
| Feeder Location | 45234-Vulcan 1 Roc
| Customer Count | 1
| Circuit 5 Year Average (SAIDI |  |  |  | 322.02
| Reporting Year (SAIDI |  | 0
| Circuit 5 Year Average (SAIFI |  |  |  | 2.2
| Reporting Year (SAIFI |  | 0
| Total Circuit Length: |  |  |  |  | 1.3
Date of Last Circuit Trim:
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | VULCAN | [5 empty] | 110 | JPEC - Planned |  | 2 | 25 | 39 | 1357.2 | 19.65
| Feeder Name: | Kinder Morgan | [5 empty] | 420 | ROW |  | 3 | 37.5 | 3 | 588 | 8.51
[8 empty] | 500 | Lightning |  | 1 | 12.5 | 1 | 135 | 1.95
| Feeder Number: | 244
[8 empty] | 690 | Animal |  | 2 | 25 | 72 | 4828.2 | 69.89
| Feeder Location | 45244-Kinder Morga
| Customer Count | 35
| Circuit 5 Year Average (SAIDI |  |  |  | 1315.9121
| Reporting Year (SAIDI |  | 139.503
| Circuit 5 Year Average (SAIFI |  |  |  | 11.6903
| Reporting Year (SAIFI |  | 2.0803
| Total Circuit Length: |  |  |  |  | 8.1
Date of Last Circuit Trim:
Corrective Action Plan:
[8 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | VULCAN | [5 empty] | 420 | ROW |  | 1 | 25 | 2 | 529.8 | 60.44
| Feeder Name: | Vulcan 2 Hwy 62 | [5 empty] | 500 | Lightning |  | 1 | 25 | 0 | 0 | 0
[8 empty] | 690 | Animal |  | 1 | 25 | 2 | 346.8 | 39.56
| Feeder Number: | 254
[8 empty] | 999 | Cause unknown |  | 1 | 25 | 0 | 0 | 0
| Feeder Location | 45254-Vulcan 2 Hwy
| Customer Count | 2
| Circuit 5 Year Average (SAIDI |  |  |  | 286.1348
| Reporting Year (SAIDI |  | 281.8262
| Circuit 5 Year Average (SAIFI |  |  |  | 1.9149
| Reporting Year (SAIFI |  | 1.0638
| Total Circuit Length: |  |  |  |  | 5
Date of Last Circuit Trim:
Corrective Action Plan:
| Total Customer Hrs Off: |  |  | 203014.11 |  |  | Total Customer Mins Off: |  |  | 12180846.6
| Total Customers Affected: |  |  | 74573
| Total Outage Count: |  |  | 2322
53040 | [7 empty] | /report/19020/rptcustom/oms/OMS_ANNUAL_RLBLTY_RPT_19020.xml.rpt

## 2022 Circuit Details
JACKSON PURCHASE ENERGY CORP.
Rev: 202306200609
| 2024-05-29 | 9:35 |  |  |  |  | ANNUAL RELIABILITY REPORT | [6 empty] | Page: 1
2022
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | BURNA |  |  |  |  | 100 | Contractor - Planned |  | 2 | 100 | 2 | 529.2 |  | 100
| Feeder Name: | Hampton
| Feeder Number: | 214
| Feeder Location | 14214-Hampton
| Customer Count | 85
| Circuit 5 Year Average (SAIDI |  |  |  | 173.1175
| Reporting Year (SAIDI |  | 6.2072
| Circuit 5 Year Average (SAIFI |  |  |  | 0.7162
| Reporting Year (SAIFI |  | 0.0235
| Total Circuit Length: |  |  |  | 12
| Date of Last Circuit Trim: |  |  |  | 2019
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | BURNA |  |  |  |  | 110 | JPEC - Planned |  | 2 | 10.53 | 13 | 655.2 |  | 4.35
| Feeder Name: | Salem |  |  |  |  | 300 | Equipment Failure |  | 7 | 36.84 | 73 | 10396.8 |  | 69.04
[7 empty] | 420 | ROW |  | 4 | 21.05 | 22 | 2866.2 |  | 19.03
| Feeder Number: | 244
[7 empty] | 500 | Lightning |  | 2 | 10.53 | 5 | 839.4 |  | 5.57
| Feeder Location | 14244-Salem |  |  |  |  | 510 | Wind - Not Trees |  | 1 | 5.26 | 1 | 105.6 |  | 0.7
| Customer Count | 325 |  |  |  |  | 690 | Animal |  | 2 | 10.53 | 4 | 114 |  | 0.76
| Circuit 5 Year Average (SAIDI |  |  |  | 682.3504 |  | 999 | Cause unknown |  | 1 | 5.26 | 2 | 82.2 |  | 0.55
| Reporting Year (SAIDI |  | 32.0279
| Circuit 5 Year Average (SAIFI |  |  |  | 1.5052
| Reporting Year (SAIFI |  | 0.2249
| Total Circuit Length: |  |  |  | 52.8
| Date of Last Circuit Trim: |  |  |  | 2019
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | BURNA |  |  |  |  | 100 | Contractor - Planned |  | 7 | 25 | 24 | 3963.6 |  | 4.19
| Feeder Name: | Smithland |  |  |  |  | 300 | Equipment Failure |  | 1 | 3.57 | 2 | 120 |  | 0.13
[7 empty] | 420 | ROW |  | 5 | 17.86 | 489 | 87105.6 |  | 92.17
| Feeder Number: | 254
[7 empty] | 500 | Lightning |  | 2 | 7.14 | 8 | 747 |  | 0.79
| Feeder Location | 14254-Smithland |  |  |  |  | 510 | Wind - Not Trees |  | 1 | 3.57 | 0 | 0 |  | 0
| Customer Count | 350 |  |  |  |  | 690 | Animal |  | 9 | 32.14 | 16 | 1386 |  | 1.47
| Circuit 5 Year Average (SAIDI |  |  |  | 505.2356 |  | 999 | Cause unknown |  | 3 | 10.71 | 13 | 1187.4 |  | 1.26
| Reporting Year (SAIDI |  | 248.8938
| Circuit 5 Year Average (SAIFI |  |  |  | 2.9848
| Reporting Year (SAIFI |  | 1.3973
| Total Circuit Length: |  |  |  | 69.9
| Date of Last Circuit Trim: |  |  |  | 2019
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | CALVERT CITY |  |  |  |  | 300 | Equipment Failure |  | 2 | 22.22 | 3 | 236.4 |  | 0.62
| Feeder Name: | Hwy 95 |  |  |  |  | 420 | ROW |  | 1 | 11.11 | 8 | 2623.8 |  | 6.85
[7 empty] | 500 | Lightning |  | 2 | 22.22 | 6 | 814.2 |  | 2.13
| Feeder Number: | 214
[7 empty] | 690 | Animal |  | 3 | 33.33 | 282 | 30939 |  | 80.77
| Feeder Location | 43214-Hwy 95 |  |  |  |  | 999 | Cause unknown |  | 1 | 11.11 | 34 | 3690.6 |  | 9.64
| Customer Count | 250
| Circuit 5 Year Average (SAIDI |  |  |  | 182.0113
| Reporting Year (SAIDI |  | 123.7393
| Circuit 5 Year Average (SAIFI |  |  |  | 0.8239
| Reporting Year (SAIFI |  | 1.1279
| Total Circuit Length: |  |  |  | 18.6
| Date of Last Circuit Trim: |  |  |  | 2017
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | CALVERT CITY |  |  |  |  | 100 | Contractor - Planned |  | 3 | 9.38 | 11 | 1827.6 |  | 5.25
| Feeder Name: | Calvert Heights |  |  |  |  | 110 | JPEC - Planned |  | 4 | 12.5 | 16 | 1055.4 |  | 3.03
[7 empty] | 300 | Equipment Failure |  | 3 | 9.38 | 29 | 1507.2 |  | 4.33
| Feeder Number: | 224
[7 empty] | 420 | ROW |  | 10 | 31.25 | 103 | 15037.2 |  | 43.2
| Feeder Location | 43224-Calvert Height |  |  |  |  | 500 | Lightning |  | 2 | 6.25 | 63 | 12727.2 |  | 36.56
| Customer Count | 649 |  |  |  |  | 690 | Animal |  | 7 | 21.88 | 24 | 1599.6 |  | 4.6
| Circuit 5 Year Average (SAIDI |  |  |  | 147.8394 |  | 999 | Cause unknown |  | 3 | 9.38 | 39 | 1053.6 |  | 3.03
| Reporting Year (SAIDI |  | 25.8727
| Circuit 5 Year Average (SAIFI |  |  |  | 0.9625
| Reporting Year (SAIFI |  | 1.1643
| Total Circuit Length: |  |  |  | 28.3
| Date of Last Circuit Trim: |  |  |  | 2017
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | CALVERT CITY |  |  |  |  | 300 | Equipment Failure |  | 1 | 5.26 | 1 | 80.4 |  | 0.34
| Feeder Name: | Gilbertsville |  |  |  |  | 420 | ROW |  | 6 | 31.58 | 47 | 7462.2 |  | 31.55
[7 empty] | 500 | Lightning |  | 2 | 10.53 | 19 | 915.6 |  | 3.87
| Feeder Number: | 234
[7 empty] | 510 | Wind - Not Trees |  | 1 | 5.26 | 29 | 5320.8 |  | 22.5
| Feeder Location | 43234-Gilbertsville |  |  |  |  | 690 | Animal |  | 5 | 26.32 | 57 | 5029.2 |  | 21.27
| Customer Count | 340 |  |  |  |  | 700 | Member/Public Caused |  | 3 | 15.79 | 35 | 4818.6 |  | 20.37
| Circuit 5 Year Average (SAIDI |  |  |  | 10366.7364 |  | 999 | Cause unknown |  | 1 | 5.26 | 1 | 22.8 |  | 0.1
| Reporting Year (SAIDI |  | 21.9223
| Circuit 5 Year Average (SAIFI |  |  |  | 0.7762
| Reporting Year (SAIFI |  | 0.1675
| Total Circuit Length: |  |  |  | 23.6
| Date of Last Circuit Trim: |  |  |  | 2017
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | CALVERT CITY |  |  |  |  | None | None |  | 0 | 0 | 0 | 0 |  | 0
| Feeder Name: | Industrial Park
| Feeder Number: | 244
| Feeder Location | 43244-Industrial Park
| Customer Count | 25
| Circuit 5 Year Average (SAIDI |  |  |  | 135.0165
| Reporting Year (SAIDI |  | 0
| Circuit 5 Year Average (SAIFI |  |  |  | 0.6961
| Reporting Year (SAIFI |  | 0
| Total Circuit Length: |  |  |  | 5
| Date of Last Circuit Trim: |  |  |  | 2017
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | COLEMAN ROAD |  |  |  |  | 300 | Equipment Failure |  | 1 | 6.25 | 39 | 1608 |  | 15.93
| Feeder Name: | Conrad Heights |  |  |  |  | 420 | ROW |  | 4 | 25 | 15 | 3461.4 |  | 34.3
[7 empty] | 500 | Lightning |  | 2 | 12.5 | 13 | 919.8 |  | 9.11
| Feeder Number: | 224
[7 empty] | 690 | Animal |  | 7 | 43.75 | 50 | 2944.2 |  | 29.17
| Feeder Location | 30224-Conrad Height |  |  |  |  | 999 | Cause unknown |  | 2 | 12.5 | 31 | 1159.2 |  | 11.49
| Customer Count | 370
| Circuit 5 Year Average (SAIDI |  |  |  | 249.1545
| Reporting Year (SAIDI |  | 9.3463
| Circuit 5 Year Average (SAIFI |  |  |  | 1.4938
| Reporting Year (SAIFI |  | 0.135
| Total Circuit Length: |  |  |  | 18
| Date of Last Circuit Trim: |  |  |  | 2018
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | COLEMAN ROAD |  |  |  |  | 690 | Animal |  | 1 | 33.33 | 10 | 411 |  | 76.45
| Feeder Name: | Hwy 60 Business |  |  |  |  | 700 | Member/Public Caused |  | 1 | 33.33 | 1 | 48 |  | 8.93
[7 empty] | 999 | Cause unknown |  | 1 | 33.33 | 1 | 78.6 |  | 14.62
| Feeder Number: | 244
| Feeder Location | 30244-Hwy 60 Busin
| Customer Count | 104
| Circuit 5 Year Average (SAIDI |  |  |  | 163.9201
| Reporting Year (SAIDI |  | 3.9421
| Circuit 5 Year Average (SAIFI |  |  |  | 0.5544
| Reporting Year (SAIFI |  | 0.0959
| Total Circuit Length: |  |  |  | 7.7
| Date of Last Circuit Trim: |  |  |  | 2018
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | COLEMAN ROAD |  |  |  |  | None | None |  | 0 | 0 | 0 | 0 |  | 0
| Feeder Name: | KY Oaks Mall
| Feeder Number: | 254
| Feeder Location | 30254-KY Oaks Mall
| Customer Count | 79
| Circuit 5 Year Average (SAIDI |  |  |  | 149.539
| Reporting Year (SAIDI |  | 0
| Circuit 5 Year Average (SAIFI |  |  |  | 0.4227
| Reporting Year (SAIFI |  | 0
| Total Circuit Length: |  |  |  | 3.9
| Date of Last Circuit Trim: |  |  |  | 2018
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | CULP |  |  |  |  | 100 | Contractor - Planned |  | 3 | 15 | 3 | 259.8 |  | 9.07
| Feeder Name: | Proform |  |  |  |  | 300 | Equipment Failure |  | 3 | 15 | 12 | 691.2 |  | 24.13
[7 empty] | 420 | ROW |  | 3 | 15 | 4 | 235.8 |  | 8.23
| Feeder Number: | 214
[7 empty] | 500 | Lightning |  | 1 | 5 | 1 | 46.8 |  | 1.63
| Feeder Location | 42214-Proform |  |  |  |  | 690 | Animal |  | 9 | 45 | 11 | 688.8 |  | 24.05
| Customer Count | 428 |  |  |  |  | 999 | Cause unknown |  | 1 | 5 | 19 | 942 |  | 32.89
| Circuit 5 Year Average (SAIDI |  |  |  | 624.665
| Reporting Year (SAIDI |  | 2.202
| Circuit 5 Year Average (SAIFI |  |  |  | 1.2804
| Reporting Year (SAIFI |  | 0.0444
| Total Circuit Length: |  |  |  | 25.7
| Date of Last Circuit Trim: |  |  |  | 2018
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | CULP |  |  |  |  | 110 | JPEC - Planned |  | 1 | 25 | 5 | 607.2 |  | 64.54
| Feeder Name: | Little Cypress |  |  |  |  | 420 | ROW |  | 1 | 25 | 1 | 170.4 |  | 18.11
[7 empty] | 999 | Cause unknown |  | 2 | 50 | 2 | 163.2 |  | 17.35
| Feeder Number: | 224
| Feeder Location | 42224-Little Cypress
| Customer Count | 49
| Circuit 5 Year Average (SAIDI |  |  |  | 101.4758
| Reporting Year (SAIDI |  | 12.4479
| Circuit 5 Year Average (SAIFI |  |  |  | 1.279
| Reporting Year (SAIFI |  | 0.1025
| Total Circuit Length: |  |  |  | 8
| Date of Last Circuit Trim: |  |  |  | 2018
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | CULP |  |  |  |  | 100 | Contractor - Planned |  | 3 | 30 | 6 | 294 |  | 7.32
| Feeder Name: | Possum Trot |  |  |  |  | 300 | Equipment Failure |  | 2 | 20 | 4 | 287.4 |  | 7.15
[7 empty] | 420 | ROW |  | 2 | 20 | 32 | 2081.4 |  | 51.81
| Feeder Number: | 234
[7 empty] | 500 | Lightning |  | 1 | 10 | 12 | 1138.2 |  | 28.33
| Feeder Location | 42234-Possum Trot |  |  |  |  | 700 | Member/Public Caused |  | 2 | 20 | 4 | 216 |  | 5.38
| Customer Count | 203
| Circuit 5 Year Average (SAIDI |  |  |  | 444.2819
| Reporting Year (SAIDI |  | 10.2466
| Circuit 5 Year Average (SAIFI |  |  |  | 1.8095
| Reporting Year (SAIFI |  | 0.1575
| Total Circuit Length: |  |  |  | 17.4
| Date of Last Circuit Trim: |  |  |  | 2018
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | CULP |  |  |  |  | 100 | Contractor - Planned |  | 5 | 9.8 | 11 | 2097 |  | 1.44
| Feeder Name: | Sharpe |  |  |  |  | 110 | JPEC - Planned |  | 6 | 11.76 | 53 | 1471.8 |  | 1.01
[7 empty] | 300 | Equipment Failure |  | 8 | 15.69 | 470 | 69793.8 |  | 47.85
| Feeder Number: | 244
[7 empty] | 420 | ROW |  | 7 | 13.73 | 1206 | 56913 |  | 39.02
| Feeder Location | 42244-Sharpe |  |  |  |  | 500 | Lightning |  | 2 | 3.92 | 11 | 657.6 |  | 0.45
| Customer Count | 1111 |  |  |  |  | 690 | Animal |  | 18 | 35.29 | 55 | 2947.2 |  | 2.02
| Circuit 5 Year Average (SAIDI |  |  |  | 137.7173 |  | 710 | Motor Vehicle |  | 1 | 1.96 | 45 | 7317.6 |  | 5.02
| Reporting Year (SAIDI |  | 62.8274 |  |  |  | 999 | Cause unknown |  | 4 | 7.84 | 68 | 4672.8 |  | 3.2
| Circuit 5 Year Average (SAIFI |  |  |  | 1.4661
| Reporting Year (SAIFI |  | 1.0856
| Total Circuit Length: |  |  |  | 56.2
| Date of Last Circuit Trim: |  |  |  | 2018
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | CUMBERLAND JPEC |  |  |  |  | 100 | Contractor - Planned |  | 3 | 21.43 | 5 | 1324.2 |  | 4.92
| Feeder Name: | Pinckneyville |  |  |  |  | 300 | Equipment Failure |  | 3 | 21.43 | 48 | 5824.8 |  | 21.62
[7 empty] | 420 | ROW |  | 4 | 28.57 | 115 | 15492.6 |  | 57.51
| Feeder Number: | 224
[7 empty] | 500 | Lightning |  | 1 | 7.14 | 5 | 241.8 |  | 0.9
| Feeder Location | 15224-Pinckneyville |  |  |  |  | 690 | Animal |  | 2 | 14.29 | 47 | 3943.8 |  | 14.64
| Customer Count | 115 |  |  |  |  | 999 | Cause unknown |  | 1 | 7.14 | 1 | 110.4 |  | 0.41
| Circuit 5 Year Average (SAIDI |  |  |  | 472.4943
| Reporting Year (SAIDI |  | 134.9898
| Circuit 5 Year Average (SAIFI |  |  |  | 2.0406
| Reporting Year (SAIFI |  | 1.002
| Total Circuit Length: |  |  |  | 28
| Date of Last Circuit Trim: |  |  |  | 2019
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | CUMBERLANDQUA |  |  |  |  | 100 | Contractor - Planned |  | 1 | 20 | 7 | 2076.6 |  | 11.89
| Feeder Name: | Quarry |  |  |  |  | 110 | JPEC - Planned |  | 1 | 20 | 30 | 3166.8 |  | 18.13
[7 empty] | 420 | ROW |  | 3 | 60 | 84 | 12221.4 |  | 69.98
| Feeder Number: | 234
| Feeder Location | 15234-Quarry
| Customer Count | 31
| Circuit 5 Year Average (SAIDI |  |  |  | 369.3677
| Reporting Year (SAIDI |  | 397.9583
| Circuit 5 Year Average (SAIFI |  |  |  | 1.8691
| Reporting Year (SAIFI |  | 2.7353
| Total Circuit Length: |  |  |  | 5.3
| Date of Last Circuit Trim: |  |  |  | 2019
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | DRAFFENVILLE |  |  |  |  | 100 | Contractor - Planned |  | 2 | 16.67 | 10 | 1044.6 |  | 11.12
| Feeder Name: | Draffenville |  |  |  |  | 110 | JPEC - Planned |  | 1 | 8.33 | 3 | 118.2 |  | 1.26
[7 empty] | 300 | Equipment Failure |  | 2 | 16.67 | 3 | 204 |  | 2.17
| Feeder Number: | 214
[7 empty] | 420 | ROW |  | 2 | 16.67 | 6 | 464.4 |  | 4.94
| Feeder Location | 66214-Draffenville |  |  |  |  | 690 | Animal |  | 3 | 25 | 7 | 373.8 |  | 3.98
| Customer Count | 491 |  |  |  |  | 700 | Member/Public Caused |  | 1 | 8.33 | 8 | 2742.6 |  | 29.2
| Circuit 5 Year Average (SAIDI |  |  |  | 11.0679 |  | 710 | Motor Vehicle |  | 1 | 8.33 | 28 | 4444.8 |  | 47.32
| Reporting Year (SAIDI |  | 9.0557
| Circuit 5 Year Average (SAIFI |  |  |  | 0.0876
| Reporting Year (SAIFI |  | 0.057
| Total Circuit Length: |  |  |  | 29.6
| Date of Last Circuit Trim: |  |  |  | 2019
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | FREEMONT |  |  |  |  | 100 | Contractor - Planned |  | 2 | 5.26 | 3 | 529.8 |  | 0.39
| Feeder Name: | Symsonia |  |  |  |  | 110 | JPEC - Planned |  | 2 | 5.26 | 9 | 443.4 |  | 0.33
[7 empty] | 300 | Equipment Failure |  | 10 | 26.32 | 1035 | 82398.6 |  | 60.73
| Feeder Number: | 214
[7 empty] | 420 | ROW |  | 9 | 23.68 | 239 | 25644.6 |  | 18.9
| Feeder Location | 51214-Symsonia |  |  |  |  | 500 | Lightning |  | 5 | 13.16 | 156 | 17966.4 |  | 13.24
| Customer Count | 1012 |  |  |  |  | 690 | Animal |  | 5 | 13.16 | 6 | 496.8 |  | 0.37
| Circuit 5 Year Average (SAIDI |  |  |  | 219.0497 |  | 700 | Member/Public Caused |  | 1 | 2.63 | 5 | 207 |  | 0.15
| Reporting Year (SAIDI |  | 81.4262 |  |  |  | 810 | Load |  | 1 | 2.63 | 1 | 57.6 |  | 0.04
[7 empty] | 999 | Cause unknown |  | 3 | 7.89 | 53 | 7937.4 |  | 5.85
| Circuit 5 Year Average (SAIFI |  |  |  | 2.2547
| Reporting Year (SAIFI |  | 1.0228
| Total Circuit Length: |  |  |  | 93.6
| Date of Last Circuit Trim: |  |  |  | 2019
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | FREEMONT |  |  |  |  | 100 | Contractor - Planned |  | 8 | 32 | 9 | 1302 |  | 15.91
| Feeder Name: | McNeil Lane |  |  |  |  | 110 | JPEC - Planned |  | 3 | 12 | 9 | 2146.2 |  | 26.23
[7 empty] | 300 | Equipment Failure |  | 1 | 4 | 2 | 411 |  | 5.02
| Feeder Number: | 224
[7 empty] | 420 | ROW |  | 5 | 20 | 16 | 1093.2 |  | 13.36
| Feeder Location | 51224-McNeil Lane |  |  |  |  | 500 | Lightning |  | 2 | 8 | 5 | 662.4 |  | 8.1
| Customer Count | 334 |  |  |  |  | 690 | Animal |  | 3 | 12 | 11 | 714.6 |  | 8.73
| Circuit 5 Year Average (SAIDI |  |  |  | 387.8317 |  | 999 | Cause unknown |  | 3 | 12 | 21 | 1851.6 |  | 22.63
| Reporting Year (SAIDI |  | 6.4241
| Circuit 5 Year Average (SAIFI |  |  |  | 1.1545
| Reporting Year (SAIFI |  | 0.0629
| Total Circuit Length: |  |  |  | 41.1
| Date of Last Circuit Trim: |  |  |  | 2019
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | FREEMONT |  |  |  |  | 100 | Contractor - Planned |  | 6 | 27.27 | 8 | 747 |  | 1.96
| Feeder Name: | Freemont |  |  |  |  | 300 | Equipment Failure |  | 5 | 22.73 | 169 | 6542.4 |  | 17.2
[7 empty] | 420 | ROW |  | 3 | 13.64 | 88 | 6691.8 |  | 17.59
| Feeder Number: | 244
[7 empty] | 500 | Lightning |  | 1 | 4.55 | 1 | 42 |  | 0.11
| Feeder Location | 51244-Freemont |  |  |  |  | 510 | Wind - Not Trees |  | 1 | 4.55 | 142 | 22968.6 |  | 60.37
| Customer Count | 334 |  |  |  |  | 690 | Animal |  | 3 | 13.64 | 6 | 353.4 |  | 0.93
| Circuit 5 Year Average (SAIDI |  |  |  | 116.3753 |  | 999 | Cause unknown |  | 3 | 13.64 | 13 | 699.6 |  | 1.84
| Reporting Year (SAIDI |  | 68.733
| Circuit 5 Year Average (SAIFI |  |  |  | 0.7032
| Reporting Year (SAIFI |  | 0.5057
| Total Circuit Length: |  |  |  | 25.2
| Date of Last Circuit Trim: |  |  |  | 2019
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | FREEMONT |  |  |  |  | 100 | Contractor - Planned |  | 3 | 21.43 | 4 | 121.2 |  | 1.82
| Feeder Name: | Bonds Rd |  |  |  |  | 110 | JPEC - Planned |  | 1 | 7.14 | 1 | 87.6 |  | 1.31
[7 empty] | 300 | Equipment Failure |  | 1 | 7.14 | 1 | 70.8 |  | 1.06
| Feeder Number: | 254
[7 empty] | 420 | ROW |  | 1 | 7.14 | 26 | 4618.8 |  | 69.26
| Feeder Location | 51254-Bonds Rd |  |  |  |  | 500 | Lightning |  | 1 | 7.14 | 1 | 16.8 |  | 0.25
| Customer Count | 127 |  |  |  |  | 510 | Wind - Not Trees |  | 1 | 7.14 | 2 | 313.8 |  | 4.71
| Circuit 5 Year Average (SAIDI |  |  |  | 1039.014 |  | 690 | Animal |  | 3 | 21.43 | 3 | 126 |  | 1.89
| Reporting Year (SAIDI |  | 36.3407 |  |  |  | 999 | Cause unknown |  | 3 | 21.43 | 7 | 1313.4 |  | 19.7
| Circuit 5 Year Average (SAIFI |  |  |  | 1.5877
| Reporting Year (SAIFI |  | 0.2046
| Total Circuit Length: |  |  |  | 17.3
| Date of Last Circuit Trim: |  |  |  | 2019
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | GRAND RIVERS |  |  |  |  | 100 | Contractor - Planned |  | 1 | 4.17 | 2 | 401.4 |  | 1.41
| Feeder Name: | Iuka |  |  |  |  | 110 | JPEC - Planned |  | 2 | 8.33 | 32 | 1611.6 |  | 5.68
[7 empty] | 300 | Equipment Failure |  | 4 | 16.67 | 5 | 1073.4 |  | 3.78
| Feeder Number: | 214
[7 empty] | 420 | ROW |  | 7 | 29.17 | 98 | 16830 |  | 59.3
| Feeder Location | 76214-Iuka |  |  |  |  | 500 | Lightning |  | 7 | 29.17 | 9 | 1003.2 |  | 3.54
| Customer Count | 301 |  |  |  |  | 690 | Animal |  | 1 | 4.17 | 1 | 99.6 |  | 0.35
| Circuit 5 Year Average (SAIDI |  |  |  | 497.2919 |  | 999 | Cause unknown |  | 2 | 8.33 | 31 | 7359.6 |  | 25.93
| Reporting Year (SAIDI |  | 55.9621
| Circuit 5 Year Average (SAIFI |  |  |  | 1.9065
| Reporting Year (SAIFI |  | 0.3258
| Total Circuit Length: |  |  |  | 48.4
| Date of Last Circuit Trim: |  |  |  | 2016
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | GRAND RIVERS |  |  |  |  | 100 | Contractor - Planned |  | 6 | 28.57 | 9 | 1852.2 |  | 13.2
| Feeder Name: | Smithland |  |  |  |  | 420 | ROW |  | 5 | 23.81 | 47 | 3359.4 |  | 23.94
[7 empty] | 500 | Lightning |  | 2 | 9.52 | 4 | 919.2 |  | 6.55
| Feeder Number: | 224
[7 empty] | 690 | Animal |  | 7 | 33.33 | 76 | 5197.8 |  | 37.04
| Feeder Location | 76224-Smithland |  |  |  |  | 999 | Cause unknown |  | 1 | 4.76 | 33 | 2704.2 |  | 19.27
| Customer Count | 312
| Circuit 5 Year Average (SAIDI |  |  |  | 4624.1027
| Reporting Year (SAIDI |  | 16.6507
| Circuit 5 Year Average (SAIFI |  |  |  | 1.362
| Reporting Year (SAIFI |  | 1.0154
| Total Circuit Length: |  |  |  | 31.1
| Date of Last Circuit Trim: |  |  |  | 2016
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | GRAND RIVERS |  |  |  |  | 100 | Contractor - Planned |  | 3 | 13.04 | 7 | 738 |  | 3.38
| Feeder Name: | Pelican GR #1 |  |  |  |  | 110 | JPEC - Planned |  | 1 | 4.35 | 16 | 1454.4 |  | 6.66
[7 empty] | 300 | Equipment Failure |  | 3 | 13.04 | 5 | 502.2 |  | 2.3
| Feeder Number: | 244
[7 empty] | 420 | ROW |  | 4 | 17.39 | 12 | 1039.2 |  | 4.76
| Feeder Location | 76244-Pelican GR #1 |  |  |  |  | 500 | Lightning |  | 2 | 8.7 | 7 | 1459.2 |  | 6.68
| Customer Count | 379 |  |  |  |  | 690 | Animal |  | 6 | 26.09 | 124 | 10431.6 |  | 47.76
| Circuit 5 Year Average (SAIDI |  |  |  | 252.0804 |  | 999 | Cause unknown |  | 4 | 17.39 | 66 | 6216 |  | 28.46
| Reporting Year (SAIDI |  | 27.5264
| Circuit 5 Year Average (SAIFI |  |  |  | 1.5605
| Reporting Year (SAIFI |  | 0.3272
| Total Circuit Length: |  |  |  | 23.8
| Date of Last Circuit Trim: |  |  |  | 2016
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | GRAND RIVERS |  |  |  |  | 100 | Contractor - Planned |  | 3 | 11.11 | 8 | 1162.2 |  | 0.55
| Feeder Name: | Averitt GR #2 |  |  |  |  | 110 | JPEC - Planned |  | 3 | 11.11 | 86 | 2637.6 |  | 1.26
[7 empty] | 300 | Equipment Failure |  | 2 | 7.41 | 4 | 348 |  | 0.17
| Feeder Number: | 254
[7 empty] | 420 | ROW |  | 6 | 22.22 | 1830 | 148651.2 |  | 70.74
| Feeder Location | 76254-Averitt GR #2 |  |  |  |  | 510 | Wind - Not Trees |  | 1 | 3.7 | 74 | 9153.6 |  | 4.36
| Customer Count | 673 |  |  |  |  | 690 | Animal |  | 6 | 22.22 | 266 | 36924 |  | 17.57
| Circuit 5 Year Average (SAIDI |  |  |  | 519.9121 |  | 999 | Cause unknown |  | 6 | 22.22 | 160 | 11265 |  | 5.36
| Reporting Year (SAIDI |  | 220.9373
| Circuit 5 Year Average (SAIFI |  |  |  | 3.5953
| Reporting Year (SAIFI |  | 2.7199
| Total Circuit Length: |  |  |  | 45.6
| Date of Last Circuit Trim: |  |  |  | 2016
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | HIGHPOINT |  |  |  |  | 420 | ROW |  | 8 | 42.11 | 285 | 46180.2 |  | 76.59
| Feeder Name: | High Point |  |  |  |  | 500 | Lightning |  | 1 | 5.26 | 2 | 254.4 |  | 0.42
[7 empty] | 690 | Animal |  | 7 | 36.84 | 207 | 13566 |  | 22.5
| Feeder Number: | 214
[7 empty] | 999 | Cause unknown |  | 3 | 15.79 | 6 | 295.8 |  | 0.49
| Feeder Location | 29214-High Point
| Customer Count | 192
| Circuit 5 Year Average (SAIDI |  |  |  | 211.7741
| Reporting Year (SAIDI |  | 240.7249
| Circuit 5 Year Average (SAIFI |  |  |  | 1.2688
| Reporting Year (SAIFI |  | 1.4856
| Total Circuit Length: |  |  |  | 21.2
| Date of Last Circuit Trim: |  |  |  | 2015
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | HIGHPOINT |  |  |  |  | 000 | No Cause Selected |  | 1 | 4 | 64 | 5057.4 |  | 3.73
| Feeder Name: | Carneal Rd |  |  |  |  | 110 | JPEC - Planned |  | 1 | 4 | 1 | 18 |  | 0.01
[7 empty] | 300 | Equipment Failure |  | 3 | 12 | 6 | 588.6 |  | 0.43
| Feeder Number: | 224
[7 empty] | 420 | ROW |  | 5 | 20 | 353 | 50029.2 |  | 36.9
| Feeder Location | 29224-Carneal Rd |  |  |  |  | 500 | Lightning |  | 3 | 12 | 47 | 4012.8 |  | 2.96
| Customer Count | 243 |  |  |  |  | 690 | Animal |  | 8 | 32 | 274 | 18801 |  | 13.87
| Circuit 5 Year Average (SAIDI |  |  |  | 919.6748 |  | 710 | Motor Vehicle |  | 2 | 8 | 257 | 27548.4 |  | 20.32
| Reporting Year (SAIDI |  | 205.8298 |  |  |  | 999 | Cause unknown |  | 2 | 8 | 292 | 29508.6 |  | 21.77
| Circuit 5 Year Average (SAIFI |  |  |  | 3.2354
| Reporting Year (SAIFI |  | 1.4523
| Total Circuit Length: |  |  |  | 33
| Date of Last Circuit Trim: |  |  |  | 2015
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | HIGHPOINT |  |  |  |  | None | None |  | 0 | 0 | 0 | 0 |  | 0
| Feeder Name: | REC_00000340
| Feeder Number: | 3
| Feeder Location | 00340-REC_000003
| Customer Count | 0
| Circuit 5 Year Average (SAIDI |  |  |  | 0
| Reporting Year (SAIDI |  | 0
| Circuit 5 Year Average (SAIFI |  |  |  | 0
| Reporting Year (SAIFI |  | 0
Total Circuit Length:
Date of Last Circuit Trim:
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | HUSBANDS ROAD |  |  |  |  | 100 | Contractor - Planned |  | 4 | 15.38 | 6 | 219 |  | 0.3
| Feeder Name: | Husbands Rd |  |  |  |  | 110 | JPEC - Planned |  | 9 | 34.62 | 26 | 1962 |  | 2.64
[7 empty] | 300 | Equipment Failure |  | 4 | 15.38 | 4 | 321 |  | 0.43
| Feeder Number: | 224
[7 empty] | 420 | ROW |  | 1 | 3.85 | 3 | 440.4 |  | 0.59
| Feeder Location | 40224-Husbands Rd |  |  |  |  | 690 | Animal |  | 5 | 19.23 | 6 | 240.6 |  | 0.32
| Customer Count | 778 |  |  |  |  | 710 | Motor Vehicle |  | 1 | 3.85 | 790 | 70810.2 |  | 95.46
| Circuit 5 Year Average (SAIDI |  |  |  | 305.4783 |  | 999 | Cause unknown |  | 2 | 7.69 | 3 | 184.8 |  | 0.25
| Reporting Year (SAIDI |  | 91.0194
| Circuit 5 Year Average (SAIFI |  |  |  | 0.9887
| Reporting Year (SAIFI |  | 1.0155
| Total Circuit Length: |  |  |  | 44
| Date of Last Circuit Trim: |  |  |  | 2018
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | HUSBANDS ROAD |  |  |  |  | 110 | JPEC - Planned |  | 1 | 9.09 | 3 | 124.8 |  | 0.32
| Feeder Name: | Lydon Rd |  |  |  |  | 300 | Equipment Failure |  | 2 | 18.18 | 5 | 1069.8 |  | 2.73
[7 empty] | 420 | ROW |  | 2 | 18.18 | 457 | 35499 |  | 90.7
| Feeder Number: | 234
[7 empty] | 500 | Lightning |  | 1 | 9.09 | 3 | 169.8 |  | 0.43
| Feeder Location | 40234-Lydon Rd |  |  |  |  | 690 | Animal |  | 5 | 45.45 | 32 | 2274 |  | 5.81
| Customer Count | 457
| Circuit 5 Year Average (SAIDI |  |  |  | 166.2154
| Reporting Year (SAIDI |  | 77.6414
| Circuit 5 Year Average (SAIFI |  |  |  | 1.3188
| Reporting Year (SAIFI |  | 0.9995
| Total Circuit Length: |  |  |  | 32.1
| Date of Last Circuit Trim: |  |  |  | 2018
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | HUSBANDS ROAD |  |  |  |  | 100 | Contractor - Planned |  | 2 | 8 | 4 | 446.4 |  | 0.92
| Feeder Name: | Clarkline Rd |  |  |  |  | 110 | JPEC - Planned |  | 2 | 8 | 870 | 18918 |  | 39.18
[7 empty] | 300 | Equipment Failure |  | 5 | 20 | 94 | 6642.6 |  | 13.76
| Feeder Number: | 244
[7 empty] | 420 | ROW |  | 3 | 12 | 50 | 11650.2 |  | 24.13
| Feeder Location | 40244-Clarkline Rd |  |  |  |  | 510 | Wind - Not Trees |  | 1 | 4 | 18 | 6276 |  | 13
| Customer Count | 359 |  |  |  |  | 690 | Animal |  | 10 | 40 | 17 | 966.6 |  | 2
| Circuit 5 Year Average (SAIDI |  |  |  | 90.1301 |  | 810 | Load |  | 2 | 8 | 47 | 3379.2 |  | 7
| Reporting Year (SAIDI |  | 52.6647
| Circuit 5 Year Average (SAIFI |  |  |  | 0.9571
| Reporting Year (SAIFI |  | 2.422
| Total Circuit Length: |  |  |  | 26.4
| Date of Last Circuit Trim: |  |  |  | 2018
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | JOY |  |  |  |  | 000 | No Cause Selected |  | 1 | 4.76 | 1 | 90.6 |  | 0.06
| Feeder Name: | Hampton South |  |  |  |  | 110 | JPEC - Planned |  | 1 | 4.76 | 1 | 217.8 |  | 0.16
[7 empty] | 300 | Equipment Failure |  | 1 | 4.76 | 1 | 247.2 |  | 0.18
| Feeder Number: | 214
[7 empty] | 420 | ROW |  | 7 | 33.33 | 417 | 71835.6 |  | 51.14
| Feeder Location | 05214-Hampton Sout |  |  |  |  | 500 | Lightning |  | 3 | 14.29 | 186 | 35296.2 |  | 25.13
| Customer Count | 183 |  |  |  |  | 520 | Ice - Not Trees |  | 1 | 4.76 | 15 | 3278.4 |  | 2.33
| Circuit 5 Year Average (SAIDI |  |  |  | 556.2395 |  | 690 | Animal |  | 2 | 9.52 | 2 | 219.6 |  | 0.16
| Reporting Year (SAIDI |  | 392.0549 |  |  |  | 700 | Member/Public Caused |  | 1 | 4.76 | 183 | 11007.6 |  | 7.84
[7 empty] | 999 | Cause unknown |  | 4 | 19.05 | 188 | 18279 |  | 13.01
| Circuit 5 Year Average (SAIFI |  |  |  | 2.5574
| Reporting Year (SAIFI |  | 2.2758
| Total Circuit Length: |  |  |  | 53.2
| Date of Last Circuit Trim: |  |  |  | 2016
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | JOY |  |  |  |  | 100 | Contractor - Planned |  | 1 | 33.33 | 1 | 253.8 |  | 1.62
| Feeder Name: | Carrsville |  |  |  |  | 420 | ROW |  | 2 | 66.67 | 117 | 15388.2 |  | 98.38
| Feeder Number: | 244
| Feeder Location | 05244-Carrsville
| Customer Count | 71
| Circuit 5 Year Average (SAIDI |  |  |  | 161.4202
| Reporting Year (SAIDI |  | 217.6199
| Circuit 5 Year Average (SAIFI |  |  |  | 0.7665
| Reporting Year (SAIFI |  | 1.6546
| Total Circuit Length: |  |  |  | 10.8
| Date of Last Circuit Trim: |  |  |  | 2016
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | JOY |  |  |  |  | 100 | Contractor - Planned |  | 5 | 18.52 | 11 | 1667.4 |  | 1.35
| Feeder Name: | Lola |  |  |  |  | 110 | JPEC - Planned |  | 2 | 7.41 | 250 | 1426.2 |  | 1.15
[7 empty] | 300 | Equipment Failure |  | 6 | 22.22 | 323 | 34011 |  | 27.48
| Feeder Number: | 254
[7 empty] | 420 | ROW |  | 8 | 29.63 | 310 | 83357.4 |  | 67.35
| Feeder Location | 05254-Lola |  |  |  |  | 500 | Lightning |  | 2 | 7.41 | 4 | 1123.8 |  | 0.91
| Customer Count | 286 |  |  |  |  | 690 | Animal |  | 1 | 3.7 | 2 | 215.4 |  | 0.17
| Circuit 5 Year Average (SAIDI |  |  |  | 328.7303 |  | 999 | Cause unknown |  | 3 | 11.11 | 14 | 1972.8 |  | 1.59
| Reporting Year (SAIDI |  | 291.122
| Circuit 5 Year Average (SAIFI |  |  |  | 1.9816
| Reporting Year (SAIFI |  | 1.1281
| Total Circuit Length: |  |  |  | 56.5
| Date of Last Circuit Trim: |  |  |  | 2016
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | KANSAS |  |  |  |  | 100 | Contractor - Planned |  | 49 | 68.06 | 64 | 6309 |  | 10.15
| Feeder Name: | Lowes |  |  |  |  | 300 | Equipment Failure |  | 3 | 4.17 | 3 | 332.4 |  | 0.53
[7 empty] | 420 | ROW |  | 3 | 4.17 | 5 | 1101 |  | 1.77
| Feeder Number: | 214
[7 empty] | 500 | Lightning |  | 4 | 5.56 | 455 | 34162.2 |  | 54.94
| Feeder Location | 61214-Lowes |  |  |  |  | 690 | Animal |  | 9 | 12.5 | 487 | 19557 |  | 31.45
| Customer Count | 455 |  |  |  |  | 700 | Member/Public Caused |  | 2 | 2.78 | 2 | 181.8 |  | 0.29
| Circuit 5 Year Average (SAIDI |  |  |  | 385.1638 |  | 999 | Cause unknown |  | 2 | 2.78 | 2 | 537 |  | 0.86
| Reporting Year (SAIDI |  | 75.0978
| Circuit 5 Year Average (SAIFI |  |  |  | 1.6958
| Reporting Year (SAIFI |  | 1.0706
| Total Circuit Length: |  |  |  | 59
| Date of Last Circuit Trim: |  |  |  | 2016
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | KANSAS |  |  |  |  | 100 | Contractor - Planned |  | 5 | 21.74 | 22 | 2306.4 |  | 7.24
| Feeder Name: | Folsomdale |  |  |  |  | 300 | Equipment Failure |  | 2 | 8.7 | 87 | 8291.4 |  | 26.02
[7 empty] | 420 | ROW |  | 1 | 4.35 | 6 | 3186 |  | 10
| Feeder Number: | 224
[7 empty] | 500 | Lightning |  | 10 | 43.48 | 28 | 3164.4 |  | 9.93
| Feeder Location | 61224-Folsomdale |  |  |  |  | 690 | Animal |  | 3 | 13.04 | 214 | 14810.4 |  | 46.49
| Customer Count | 210 |  |  |  |  | 999 | Cause unknown |  | 2 | 8.7 | 3 | 101.4 |  | 0.32
| Circuit 5 Year Average (SAIDI |  |  |  | 143.6384
| Reporting Year (SAIDI |  | 70.5896
| Circuit 5 Year Average (SAIFI |  |  |  | 1.4013
| Reporting Year (SAIFI |  | 1.02
| Total Circuit Length: |  |  |  | 29.4
| Date of Last Circuit Trim: |  |  |  | 2016
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | KANSAS |  |  |  |  | 100 | Contractor - Planned |  | 38 | 65.52 | 61 | 6912.6 |  | 7.26
| Feeder Name: | Melber |  |  |  |  | 110 | JPEC - Planned |  | 2 | 3.45 | 69 | 12623.4 |  | 13.25
[7 empty] | 300 | Equipment Failure |  | 4 | 6.9 | 97 | 13323.6 |  | 13.99
| Feeder Number: | 234
[7 empty] | 420 | ROW |  | 5 | 8.62 | 58 | 3748.2 |  | 3.93
| Feeder Location | 61234-Melber |  |  |  |  | 500 | Lightning |  | 2 | 3.45 | 2 | 123.6 |  | 0.13
| Customer Count | 598 |  |  |  |  | 510 | Wind - Not Trees |  | 1 | 1.72 | 2 | 98.4 |  | 0.1
| Circuit 5 Year Average (SAIDI |  |  |  | 240.021 |  | 690 | Animal |  | 3 | 5.17 | 837 | 57801.6 |  | 60.67
| Reporting Year (SAIDI |  | 96.6198 |  |  |  | 700 | Member/Public Caused |  | 1 | 1.72 | 1 | 89.4 |  | 0.09
[7 empty] | 999 | Cause unknown |  | 2 | 3.45 | 8 | 548.4 |  | 0.58
| Circuit 5 Year Average (SAIFI |  |  |  | 1.4947
| Reporting Year (SAIFI |  | 1.3991
| Total Circuit Length: |  |  |  | 53.8
| Date of Last Circuit Trim: |  |  |  | 2016
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | KANSAS |  |  |  |  | 100 | Contractor - Planned |  | 11 | 26.19 | 18 | 2754 |  | 3.15
| Feeder Name: | Pottsville |  |  |  |  | 110 | JPEC - Planned |  | 1 | 2.38 | 2 | 144 |  | 0.16
[7 empty] | 300 | Equipment Failure |  | 4 | 9.52 | 10 | 990.6 |  | 1.13
| Feeder Number: | 244
[7 empty] | 420 | ROW |  | 14 | 33.33 | 218 | 51641.4 |  | 59
| Feeder Location | 61244-Pottsville |  |  |  |  | 500 | Lightning |  | 6 | 14.29 | 89 | 7509 |  | 8.58
| Customer Count | 363 |  |  |  |  | 690 | Animal |  | 4 | 9.52 | 369 | 24350.4 |  | 27.82
| Circuit 5 Year Average (SAIDI |  |  |  | 432.2114 |  | 700 | Member/Public Caused |  | 2 | 4.76 | 2 | 142.8 |  | 0.16
| Reporting Year (SAIDI |  | 142.0766
| Circuit 5 Year Average (SAIFI |  |  |  | 2.9372
| Reporting Year (SAIFI |  | 1.0152
| Total Circuit Length: |  |  |  | 47
| Date of Last Circuit Trim: |  |  |  | 2016
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | KEVIL |  |  |  |  | 000 | No Cause Selected |  | 1 | 4.17 | 5 | 604.8 |  | 3.36
| Feeder Name: | Hobbs Rd |  |  |  |  | 100 | Contractor - Planned |  | 4 | 16.67 | 14 | 1729.2 |  | 9.61
[7 empty] | 110 | JPEC - Planned |  | 2 | 8.33 | 3 | 196.2 |  | 1.09
| Feeder Number: | 214
[7 empty] | 300 | Equipment Failure |  | 6 | 25 | 12 | 958.2 |  | 5.33
| Feeder Location | 28214-Hobbs Rd |  |  |  |  | 420 | ROW |  | 8 | 33.33 | 141 | 14011.8 |  | 77.89
| Customer Count | 545 |  |  |  |  | 690 | Animal |  | 3 | 12.5 | 6 | 489 |  | 2.72
| Circuit 5 Year Average (SAIDI |  |  |  | 285.7333
| Reporting Year (SAIDI |  | 25.6946
| Circuit 5 Year Average (SAIFI |  |  |  | 2.0074
| Reporting Year (SAIFI |  | 0.2586
| Total Circuit Length: |  |  |  | 52.8
| Date of Last Circuit Trim: |  |  |  | 2016
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | KEVIL |  |  |  |  | 100 | Contractor - Planned |  | 4 | 10.81 | 8 | 538.8 |  | 1.01
| Feeder Name: | Woodville Rd |  |  |  |  | 110 | JPEC - Planned |  | 2 | 5.41 | 122 | 3304.8 |  | 6.21
[7 empty] | 300 | Equipment Failure |  | 7 | 18.92 | 110 | 15374.4 |  | 28.9
| Feeder Number: | 224
[7 empty] | 420 | ROW |  | 14 | 37.84 | 231 | 27804.6 |  | 52.27
| Feeder Location | 28224-Woodville Rd |  |  |  |  | 500 | Lightning |  | 2 | 5.41 | 2 | 196.8 |  | 0.37
| Customer Count | 501 |  |  |  |  | 510 | Wind - Not Trees |  | 1 | 2.7 | 16 | 5126.4 |  | 9.64
| Circuit 5 Year Average (SAIDI |  |  |  | 173.8598 |  | 690 | Animal |  | 6 | 16.22 | 8 | 460.2 |  | 0.87
| Reporting Year (SAIDI |  | 55.54 |  |  |  | 999 | Cause unknown |  | 1 | 2.7 | 3 | 390 |  | 0.73
| Circuit 5 Year Average (SAIFI |  |  |  | 1.1534
| Reporting Year (SAIFI |  | 0.4614
| Total Circuit Length: |  |  |  | 55.4
| Date of Last Circuit Trim: |  |  |  | 2016
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | KEVIL |  |  |  |  | 100 | Contractor - Planned |  | 7 | 30.43 | 15 | 2643 |  | 15.04
| Feeder Name: | Kelley Rd |  |  |  |  | 110 | JPEC - Planned |  | 4 | 17.39 | 12 | 184.8 |  | 1.05
[7 empty] | 420 | ROW |  | 6 | 26.09 | 52 | 11209.2 |  | 63.8
| Feeder Number: | 234
[7 empty] | 690 | Animal |  | 5 | 21.74 | 12 | 765 |  | 4.35
| Feeder Location | 28234-Kelley Rd |  |  |  |  | 999 | Cause unknown |  | 1 | 4.35 | 24 | 2766.6 |  | 15.75
| Customer Count | 427
| Circuit 5 Year Average (SAIDI |  |  |  | 118.853
| Reporting Year (SAIDI |  | 26.2726
| Circuit 5 Year Average (SAIFI |  |  |  | 1.0609
| Reporting Year (SAIFI |  | 0.1219
| Total Circuit Length: |  |  |  | 47.3
| Date of Last Circuit Trim: |  |  |  | 2016
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | KREBS STATION RD |  |  |  |  | 100 | Contractor - Planned |  | 2 | 9.52 | 8 | 1230.6 |  | 3.93
| Feeder Name: | Browns Plating |  |  |  |  | 300 | Equipment Failure |  | 2 | 9.52 | 3 | 141 |  | 0.45
[7 empty] | 420 | ROW |  | 10 | 47.62 | 187 | 23392.8 |  | 74.67
| Feeder Number: | 214
[7 empty] | 500 | Lightning |  | 2 | 9.52 | 26 | 1810.8 |  | 5.78
| Feeder Location | 50214-Browns Platin |  |  |  |  | 690 | Animal |  | 2 | 9.52 | 3 | 180.6 |  | 0.58
| Customer Count | 527 |  |  |  |  | 710 | Motor Vehicle |  | 2 | 9.52 | 11 | 4423.8 |  | 14.12
| Circuit 5 Year Average (SAIDI |  |  |  | 148.453 |  | 999 | Cause unknown |  | 1 | 4.76 | 4 | 149.4 |  | 0.48
| Reporting Year (SAIDI |  | 44.4074
| Circuit 5 Year Average (SAIFI |  |  |  | 1.2176
| Reporting Year (SAIFI |  | 0.355
| Total Circuit Length: |  |  |  | 37.4
| Date of Last Circuit Trim: |  |  |  | 2016
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | KREBS STATION RD |  |  |  |  | 100 | Contractor - Planned |  | 1 | 3.7 | 4 | 1363.8 |  | 4.49
| Feeder Name: | Old US 45 |  |  |  |  | 110 | JPEC - Planned |  | 1 | 3.7 | 1 | 97.8 |  | 0.32
[7 empty] | 300 | Equipment Failure |  | 7 | 25.93 | 7 | 658.2 |  | 2.17
| Feeder Number: | 224
[7 empty] | 420 | ROW |  | 9 | 33.33 | 280 | 25182.6 |  | 82.98
| Feeder Location | 50224-Old US 45 |  |  |  |  | 500 | Lightning |  | 1 | 3.7 | 32 | 1874.4 |  | 6.18
| Customer Count | 908 |  |  |  |  | 690 | Animal |  | 4 | 14.81 | 8 | 552 |  | 1.82
| Circuit 5 Year Average (SAIDI |  |  |  | 185.4541 |  | 999 | Cause unknown |  | 4 | 14.81 | 6 | 617.4 |  | 2.03
| Reporting Year (SAIDI |  | 27.7275
| Circuit 5 Year Average (SAIFI |  |  |  | 1.3838
| Reporting Year (SAIFI |  | 0.3083
| Total Circuit Length: |  |  |  | 83
| Date of Last Circuit Trim: |  |  |  | 2016
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | KREBS STATION RD |  |  |  |  | 000 | No Cause Selected |  | 1 | 3.23 | 603 | 3638.4 |  | 8.2
| Feeder Name: | Clinton Rd |  |  |  |  | 100 | Contractor - Planned |  | 12 | 38.71 | 106 | 7085.4 |  | 15.96
[7 empty] | 110 | JPEC - Planned |  | 3 | 9.68 | 9 | 747.6 |  | 1.68
| Feeder Number: | 234
[7 empty] | 300 | Equipment Failure |  | 5 | 16.13 | 361 | 28943.4 |  | 65.21
| Feeder Location | 50234-Clinton Rd |  |  |  |  | 420 | ROW |  | 2 | 6.45 | 21 | 1716.6 |  | 3.87
| Customer Count | 521 |  |  |  |  | 500 | Lightning |  | 2 | 6.45 | 14 | 780 |  | 1.76
| Circuit 5 Year Average (SAIDI |  |  |  | 308.9986 |  | 690 | Animal |  | 4 | 12.9 | 13 | 767.4 |  | 1.73
| Reporting Year (SAIDI |  | 55.5376 |  |  |  | 999 | Cause unknown |  | 2 | 6.45 | 12 | 704.4 |  | 1.59
| Circuit 5 Year Average (SAIFI |  |  |  | 2.1375
| Reporting Year (SAIFI |  | 1.2299
| Total Circuit Length: |  |  |  | 19.1
| Date of Last Circuit Trim: |  |  |  | 2021
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | KREBS STATION RD |  |  |  |  | None | None |  | 0 | 0 | 0 | 0 |  | 0
| Feeder Name: | New Hope
| Feeder Number: | 244
| Feeder Location | 50244-New Hope
| Customer Count | 269
| Circuit 5 Year Average (SAIDI |  |  |  | 0
| Reporting Year (SAIDI |  | 0
| Circuit 5 Year Average (SAIFI |  |  |  | 0
| Reporting Year (SAIFI |  | 0
Total Circuit Length:
Date of Last Circuit Trim:
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | LaCENTER |  |  |  |  | 100 | Contractor - Planned |  | 3 | 11.54 | 6 | 779.4 |  | 2.4
| Feeder Name: | Damrons |  |  |  |  | 300 | Equipment Failure |  | 2 | 7.69 | 19 | 1636.8 |  | 5.04
[7 empty] | 320 | Clearance |  | 1 | 3.85 | 33 | 1836 |  | 5.65
| Feeder Number: | 214
[7 empty] | 420 | ROW |  | 11 | 42.31 | 309 | 25614.6 |  | 78.85
| Feeder Location | 26214-Damrons |  |  |  |  | 500 | Lightning |  | 2 | 7.69 | 7 | 366 |  | 1.13
| Customer Count | 227 |  |  |  |  | 690 | Animal |  | 6 | 23.08 | 31 | 2187 |  | 6.73
| Circuit 5 Year Average (SAIDI |  |  |  | 261.3714 |  | 999 | Cause unknown |  | 1 | 3.85 | 1 | 67.2 |  | 0.21
| Reporting Year (SAIDI |  | 112.9981
| Circuit 5 Year Average (SAIFI |  |  |  | 2.2462
| Reporting Year (SAIFI |  | 1.3631
| Total Circuit Length: |  |  |  | 39.6
| Date of Last Circuit Trim: |  |  |  | 2015
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | LaCENTER |  |  |  |  | 100 | Contractor - Planned |  | 5 | 11.36 | 10 | 1420.8 |  | 1.03
| Feeder Name: | Oscar |  |  |  |  | 110 | JPEC - Planned |  | 1 | 2.27 | 5 | 398.4 |  | 0.29
[7 empty] | 300 | Equipment Failure |  | 4 | 9.09 | 5 | 429 |  | 0.31
| Feeder Number: | 224
[7 empty] | 420 | ROW |  | 17 | 38.64 | 1355 | 130624.8 |  | 94.68
| Feeder Location | 26224-Oscar |  |  |  |  | 500 | Lightning |  | 3 | 6.82 | 4 | 321.6 |  | 0.23
| Customer Count | 363 |  |  |  |  | 690 | Animal |  | 6 | 13.64 | 16 | 1527.6 |  | 1.11
| Circuit 5 Year Average (SAIDI |  |  |  | 377.8784 |  | 810 | Load |  | 1 | 2.27 | 12 | 1465.8 |  | 1.06
| Reporting Year (SAIDI |  | 360.0856 |  |  |  | 999 | Cause unknown |  | 7 | 15.91 | 14 | 1772.4 |  | 1.28
| Circuit 5 Year Average (SAIFI |  |  |  | 2.9254
| Reporting Year (SAIFI |  | 3.7353
| Total Circuit Length: |  |  |  | 69.5
| Date of Last Circuit Trim: |  |  |  | 2015
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | LEDBETTER |  |  |  |  | 100 | Contractor - Planned |  | 6 | 23.08 | 8 | 813 |  | 7.76
| Feeder Name: | US 60 East |  |  |  |  | 300 | Equipment Failure |  | 3 | 11.54 | 5 | 411.6 |  | 3.93
[7 empty] | 420 | ROW |  | 7 | 26.92 | 61 | 7044.6 |  | 67.28
| Feeder Number: | 224
[7 empty] | 500 | Lightning |  | 3 | 11.54 | 2 | 141.6 |  | 1.35
| Feeder Location | 31224-US 60 East |  |  |  |  | 690 | Animal |  | 6 | 23.08 | 15 | 903 |  | 8.62
| Customer Count | 317 |  |  |  |  | 700 | Member/Public Caused |  | 1 | 3.85 | 4 | 1157.4 |  | 11.05
| Circuit 5 Year Average (SAIDI |  |  |  | 84.4248
| Reporting Year (SAIDI |  | 22.2346
| Circuit 5 Year Average (SAIFI |  |  |  | 0.3238
| Reporting Year (SAIFI |  | 0.1925
| Total Circuit Length: |  |  |  | 35.5
| Date of Last Circuit Trim: |  |  |  | 2016
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | LEDBETTER |  |  |  |  | 100 | Contractor - Planned |  | 1 | 33.33 | 4 | 711 |  | 82.23
| Feeder Name: | River Crossing |  |  |  |  | 300 | Equipment Failure |  | 1 | 33.33 | 1 | 85.8 |  | 9.92
[7 empty] | 500 | Lightning |  | 1 | 33.33 | 1 | 67.8 |  | 7.84
| Feeder Number: | 234
| Feeder Location | 31234-River Crossin
| Customer Count | 36
| Circuit 5 Year Average (SAIDI |  |  |  | 31.1651
| Reporting Year (SAIDI |  | 19.6083
| Circuit 5 Year Average (SAIFI |  |  |  | 0.4303
| Reporting Year (SAIFI |  | 0.1103
| Total Circuit Length: |  |  |  | 5.2
| Date of Last Circuit Trim: |  |  |  | 2016
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | LEDBETTER |  |  |  |  | 100 | Contractor - Planned |  | 6 | 11.76 | 22 | 4192.8 |  | 4.36
| Feeder Name: | Ledbetter |  |  |  |  | 110 | JPEC - Planned |  | 2 | 3.92 | 3 | 205.2 |  | 0.21
[7 empty] | 300 | Equipment Failure |  | 6 | 11.76 | 13 | 1494 |  | 1.55
| Feeder Number: | 244
[7 empty] | 420 | ROW |  | 15 | 29.41 | 595 | 76894.8 |  | 79.98
| Feeder Location | 31244-Ledbetter |  |  |  |  | 500 | Lightning |  | 3 | 5.88 | 4 | 608.4 |  | 0.63
| Customer Count | 1026 |  |  |  |  | 690 | Animal |  | 8 | 15.69 | 19 | 1021.8 |  | 1.06
| Circuit 5 Year Average (SAIDI |  |  |  | 250.0366 |  | 700 | Member/Public Caused |  | 1 | 1.96 | 7 | 518.4 |  | 0.54
| Reporting Year (SAIDI |  | 74.9452 |  |  |  | 810 | Load |  | 3 | 5.88 | 7 | 466.2 |  | 0.48
[7 empty] | 999 | Cause unknown |  | 7 | 13.73 | 95 | 10742.4 |  | 11.17
| Circuit 5 Year Average (SAIFI |  |  |  | 1.3398
| Reporting Year (SAIFI |  | 0.5799
| Total Circuit Length: |  |  |  | 61.5
| Date of Last Circuit Trim: |  |  |  | 2016
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | LITTLE UNION |  |  |  |  | 100 | Contractor - Planned |  | 3 | 15.79 | 7 | 1188 |  | 1.87
| Feeder Name: | Airport |  |  |  |  | 110 | JPEC - Planned |  | 1 | 5.26 | 2 | 75.6 |  | 0.12
[7 empty] | 300 | Equipment Failure |  | 2 | 10.53 | 4 | 341.4 |  | 0.54
| Feeder Number: | 214
[7 empty] | 420 | ROW |  | 2 | 10.53 | 44 | 5146.8 |  | 8.11
| Feeder Location | 39214-Airport |  |  |  |  | 500 | Lightning |  | 2 | 10.53 | 35 | 3703.8 |  | 5.83
| Customer Count | 565 |  |  |  |  | 510 | Wind - Not Trees |  | 1 | 5.26 | 43 | 8326.8 |  | 13.12
| Circuit 5 Year Average (SAIDI |  |  |  | 29.1179 |  | 690 | Animal |  | 3 | 15.79 | 591 | 42848.4 |  | 67.49
| Reporting Year (SAIDI |  | 75.7782 |  |  |  | 700 | Member/Public Caused |  | 2 | 10.53 | 8 | 1157.4 |  | 1.82
[7 empty] | 710 | Motor Vehicle |  | 1 | 5.26 | 2 | 177.6 |  | 0.28
| Circuit 5 Year Average (SAIFI |  |  |  | 0.3654
[7 empty] | 810 | Load |  | 1 | 5.26 | 3 | 163.2 |  | 0.26
| Reporting Year (SAIFI |  | 1.0452
[7 empty] | 999 | Cause unknown |  | 1 | 5.26 | 2 | 357.6 |  | 0.56
Total Circuit Length:
36.3
| Date of Last Circuit Trim: |  |  |  | 2021
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | LITTLE UNION |  |  |  |  | 0 | BREC |  | 1 | 2.78 | 4 | 36 |  | 0.11
| Feeder Name: | US 60 West |  |  |  |  | 100 | Contractor - Planned |  | 25 | 69.44 | 89 | 8760 |  | 26.48
[7 empty] | 110 | JPEC - Planned |  | 2 | 5.56 | 3 | 99.6 |  | 0.3
| Feeder Number: | 224
[7 empty] | 300 | Equipment Failure |  | 1 | 2.78 | 1 | 64.2 |  | 0.19
| Feeder Location | 39224-US 60 West |  |  |  |  | 420 | ROW |  | 1 | 2.78 | 467 | 16306.2 |  | 49.29
| Customer Count | 471 |  |  |  |  | 690 | Animal |  | 4 | 11.11 | 22 | 913.8 |  | 2.76
| Circuit 5 Year Average (SAIDI |  |  |  | 220.4646 |  | 700 | Member/Public Caused |  | 1 | 2.78 | 476 | 2689.2 |  | 8.13
| Reporting Year (SAIDI |  | 34.5856 |  |  |  | 999 | Cause unknown |  | 1 | 2.78 | 100 | 4210.2 |  | 12.73
| Circuit 5 Year Average (SAIFI |  |  |  | 1.8203
| Reporting Year (SAIFI |  | 1.0096
| Total Circuit Length: |  |  |  | 37
| Date of Last Circuit Trim: |  |  |  | 2017
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | LITTLE UNION |  |  |  |  | 300 | Equipment Failure |  | 1 | 25 | 1 | 443.4 |  | 38.75
| Feeder Name: | US 60 East Mall |  |  |  |  | 690 | Animal |  | 1 | 25 | 1 | 36.6 |  | 3.2
[7 empty] | 710 | Motor Vehicle |  | 1 | 25 | 3 | 560.4 |  | 48.98
| Feeder Number: | 234
[7 empty] | 999 | Cause unknown |  | 1 | 25 | 3 | 103.8 |  | 9.07
| Feeder Location | 39234-US 60 East M
| Customer Count | 163
| Circuit 5 Year Average (SAIDI |  |  |  | 104.679
| Reporting Year (SAIDI |  | 3.4429
| Circuit 5 Year Average (SAIFI |  |  |  | 0.3429
| Reporting Year (SAIFI |  | 0.3441
| Total Circuit Length: |  |  |  | 35.5
| Date of Last Circuit Trim: |  |  |  | 2017
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | LITTLE UNION |  |  |  |  | 0 | BREC |  | 4 | 8.7 | 5 | 28.8 |  | 0.02
| Feeder Name: | Roy Lee Rd |  |  |  |  | 100 | Contractor - Planned |  | 23 | 50 | 78 | 5144.4 |  | 3.35
[7 empty] | 110 | JPEC - Planned |  | 2 | 4.35 | 38 | 3316.8 |  | 2.16
| Feeder Number: | 244
[7 empty] | 300 | Equipment Failure |  | 2 | 4.35 | 2 | 430.2 |  | 0.28
| Feeder Location | 39244-Roy Lee Rd |  |  |  |  | 420 | ROW |  | 8 | 17.39 | 1347 | 136221.6 |  | 88.63
| Customer Count | 539 |  |  |  |  | 500 | Lightning |  | 1 | 2.17 | 4 | 332.4 |  | 0.22
| Circuit 5 Year Average (SAIDI |  |  |  | 754.7591 |  | 690 | Animal |  | 3 | 6.52 | 32 | 1875 |  | 1.22
| Reporting Year (SAIDI |  | 252.8324 |  |  |  | 700 | Member/Public Caused |  | 1 | 2.17 | 1 | 109.8 |  | 0.07
[7 empty] | 710 | Motor Vehicle |  | 1 | 2.17 | 67 | 6106.8 |  | 3.97
| Circuit 5 Year Average (SAIFI |  |  |  | 2.293
[7 empty] | 999 | Cause unknown |  | 1 | 2.17 | 2 | 132.6 |  | 0.09
| Reporting Year (SAIFI |  | 2.5001
| Total Circuit Length: |  |  |  | 56.6
| Date of Last Circuit Trim: |  |  |  | 2017
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | LOVELACEVILLE |  |  |  |  | 100 | Contractor - Planned |  | 2 | 15.38 | 3 | 294.6 |  | 0.85
| Feeder Name: | Blandville |  |  |  |  | 110 | JPEC - Planned |  | 1 | 7.69 | 8 | 655.8 |  | 1.9
[7 empty] | 300 | Equipment Failure |  | 6 | 46.15 | 136 | 19753.8 |  | 57.23
| Feeder Number: | 214
[7 empty] | 420 | ROW |  | 3 | 23.08 | 8 | 2022 |  | 5.86
| Feeder Location | 49214-Blandville |  |  |  |  | 700 | Member/Public Caused |  | 1 | 7.69 | 135 | 11787.6 |  | 34.15
| Customer Count | 132
| Circuit 5 Year Average (SAIDI |  |  |  | 552.63
| Reporting Year (SAIDI |  | 149.4495
| Circuit 5 Year Average (SAIFI |  |  |  | 1.9564
| Reporting Year (SAIFI |  | 1.0289
| Total Circuit Length: |  |  |  | 20.5
| Date of Last Circuit Trim: |  |  |  | 2015
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | LOVELACEVILLE |  |  |  |  | 100 | Contractor - Planned |  | 3 | 18.75 | 5 | 592.8 |  | 1.97
| Feeder Name: | Lovelaceville |  |  |  |  | 110 | JPEC - Planned |  | 1 | 6.25 | 524 | 12951.6 |  | 43.13
[7 empty] | 300 | Equipment Failure |  | 1 | 6.25 | 6 | 525.6 |  | 1.75
| Feeder Number: | 224
[7 empty] | 420 | ROW |  | 3 | 18.75 | 31 | 2075.4 |  | 6.91
| Feeder Location | 49224-Lovelaceville |  |  |  |  | 500 | Lightning |  | 1 | 6.25 | 1 | 41.4 |  | 0.14
| Customer Count | 527 |  |  |  |  | 510 | Wind - Not Trees |  | 3 | 18.75 | 68 | 12055.2 |  | 40.14
| Circuit 5 Year Average (SAIDI |  |  |  | 358.1221 |  | 690 | Animal |  | 1 | 6.25 | 13 | 431.4 |  | 1.44
| Reporting Year (SAIDI |  | 24.5634 |  |  |  | 999 | Cause unknown |  | 3 | 18.75 | 31 | 1357.8 |  | 4.52
| Circuit 5 Year Average (SAIFI |  |  |  | 1.6879
| Reporting Year (SAIFI |  | 0.9938
| Total Circuit Length: |  |  |  | 57.8
| Date of Last Circuit Trim: |  |  |  | 2015
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | LOVELACEVILLE |  |  |  |  | 100 | Contractor - Planned |  | 15 | 53.57 | 33 | 3573 |  | 27.71
| Feeder Name: | Cunningham |  |  |  |  | 300 | Equipment Failure |  | 5 | 17.86 | 14 | 1602 |  | 12.43
[7 empty] | 420 | ROW |  | 5 | 17.86 | 53 | 7083.6 |  | 54.94
| Feeder Number: | 234
[7 empty] | 690 | Animal |  | 2 | 7.14 | 8 | 405 |  | 3.14
| Feeder Location | 49234-Cunningham |  |  |  |  | 999 | Cause unknown |  | 1 | 3.57 | 3 | 228.6 |  | 1.77
| Customer Count | 526
| Circuit 5 Year Average (SAIDI |  |  |  | 653.4017
| Reporting Year (SAIDI |  | 13.463
| Circuit 5 Year Average (SAIFI |  |  |  | 1.6219
| Reporting Year (SAIFI |  | 0.1007
| Total Circuit Length: |  |  |  | 65.3
| Date of Last Circuit Trim: |  |  |  | 2015
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | MAXON |  |  |  |  | 0 | BREC |  | 1 | 14.29 | 260 | 17285.4 |  | 72.91
| Feeder Name: | Maxon Rd |  |  |  |  | 100 | Contractor - Planned |  | 2 | 28.57 | 3 | 377.4 |  | 1.59
[7 empty] | 110 | JPEC - Planned |  | 1 | 14.29 | 2 | 66.6 |  | 0.28
| Feeder Number: | 214
[7 empty] | 300 | Equipment Failure |  | 1 | 14.29 | 35 | 4872.6 |  | 20.55
| Feeder Location | 79214-Maxon Rd |  |  |  |  | 420 | ROW |  | 2 | 28.57 | 15 | 1105.8 |  | 4.66
| Customer Count | 261
| Circuit 5 Year Average (SAIDI |  |  |  | 122.0932
| Reporting Year (SAIDI |  | 66.3328
| Circuit 5 Year Average (SAIFI |  |  |  | 0.9993
| Reporting Year (SAIFI |  | 0.9977
| Total Circuit Length: |  |  |  | 16.4
| Date of Last Circuit Trim: |  |  |  | 2017
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | MAXON |  |  |  |  | 0 | BREC |  | 1 | 6.67 | 333 | 22138.8 |  | 63.75
| Feeder Name: | Express |  |  |  |  | 100 | Contractor - Planned |  | 8 | 53.33 | 27 | 4361.4 |  | 12.56
[7 empty] | 300 | Equipment Failure |  | 1 | 6.67 | 4 | 3548.4 |  | 10.22
| Feeder Number: | 224
[7 empty] | 500 | Lightning |  | 1 | 6.67 | 27 | 1903.8 |  | 5.48
| Feeder Location | 79224-Express |  |  |  |  | 690 | Animal |  | 3 | 20 | 9 | 427.2 |  | 1.23
| Customer Count | 395 |  |  |  |  | 999 | Cause unknown |  | 1 | 6.67 | 34 | 2349.6 |  | 6.77
| Circuit 5 Year Average (SAIDI |  |  |  | 85.0104
| Reporting Year (SAIDI |  | 56.0693
| Circuit 5 Year Average (SAIFI |  |  |  | 0.819
| Reporting Year (SAIFI |  | 0.8434
| Total Circuit Length: |  |  |  | 19
| Date of Last Circuit Trim: |  |  |  | 2017
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | MAXON |  |  |  |  | 0 | BREC |  | 1 | 100 | 5 | 340.2 |  | 100
| Feeder Name: | Industrial Park
| Feeder Number: | 234
| Feeder Location | 79234-Industrial Park
| Customer Count | 4
| Circuit 5 Year Average (SAIDI |  |  |  | 20.5072
| Reporting Year (SAIDI |  | 81.7107
| Circuit 5 Year Average (SAIFI |  |  |  | 0.3365
| Reporting Year (SAIFI |  | 1.2019
| Total Circuit Length: |  |  |  | 2
| Date of Last Circuit Trim: |  |  |  | 2017
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | NEW YORK |  |  |  |  | 100 | Contractor - Planned |  | 5 | 23.81 | 10 | 1486.8 |  | 9.79
| Feeder Name: | Hinkleville |  |  |  |  | 110 | JPEC - Planned |  | 1 | 4.76 | 11 | 749.4 |  | 4.94
[7 empty] | 300 | Equipment Failure |  | 3 | 14.29 | 4 | 331.2 |  | 2.18
| Feeder Number: | 214
[7 empty] | 420 | ROW |  | 4 | 19.05 | 34 | 5883.6 |  | 38.76
| Feeder Location | 47214-Hinkleville |  |  |  |  | 500 | Lightning |  | 5 | 23.81 | 38 | 4798.8 |  | 31.61
| Customer Count | 265 |  |  |  |  | 690 | Animal |  | 2 | 9.52 | 4 | 387 |  | 2.55
| Circuit 5 Year Average (SAIDI |  |  |  | 960.8381 |  | 999 | Cause unknown |  | 1 | 4.76 | 15 | 1543.8 |  | 10.17
| Reporting Year (SAIDI |  | 22.2188
| Circuit 5 Year Average (SAIFI |  |  |  | 2.8552
| Reporting Year (SAIFI |  | 0.1435
| Total Circuit Length: |  |  |  | 44.5
| Date of Last Circuit Trim: |  |  |  | 2017
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | NEW YORK |  |  |  |  | 100 | Contractor - Planned |  | 6 | 23.08 | 13 | 866.4 |  | 3.71
| Feeder Name: | US 286 East Gage |  |  |  |  | 300 | Equipment Failure |  | 2 | 7.69 | 3 | 165.6 |  | 0.71
[7 empty] | 420 | ROW |  | 9 | 34.62 | 134 | 16311 |  | 69.81
| Feeder Number: | 224
[7 empty] | 500 | Lightning |  | 2 | 7.69 | 27 | 3004.2 |  | 12.86
| Feeder Location | 47224-US 286 East |  |  |  |  | 690 | Animal |  | 5 | 19.23 | 37 | 2941.8 |  | 12.59
| Customer Count | 264 |  |  |  |  | 700 | Member/Public Caused |  | 2 | 7.69 | 2 | 76.8 |  | 0.33
| Circuit 5 Year Average (SAIDI |  |  |  | 377.731
| Reporting Year (SAIDI |  | 61.7501
| Circuit 5 Year Average (SAIFI |  |  |  | 1.3053
| Reporting Year (SAIFI |  | 0.5073
| Total Circuit Length: |  |  |  | 45.5
| Date of Last Circuit Trim: |  |  |  | 2015
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | NEW YORK |  |  |  |  | 100 | Contractor - Planned |  | 6 | 18.18 | 11 | 1626 |  | 4.26
| Feeder Name: | Blandville |  |  |  |  | 110 | JPEC - Planned |  | 4 | 12.12 | 9 | 2070 |  | 5.42
[7 empty] | 300 | Equipment Failure |  | 1 | 3.03 | 1 | 64.8 |  | 0.17
| Feeder Number: | 234
[7 empty] | 420 | ROW |  | 12 | 36.36 | 334 | 22273.8 |  | 58.31
| Feeder Location | 47234-Blandville |  |  |  |  | 500 | Lightning |  | 4 | 12.12 | 4 | 412.8 |  | 1.08
| Customer Count | 219 |  |  |  |  | 690 | Animal |  | 3 | 9.09 | 9 | 541.8 |  | 1.42
| Circuit 5 Year Average (SAIDI |  |  |  | 837.8804 |  | 700 | Member/Public Caused |  | 2 | 6.06 | 11 | 1000.8 |  | 2.62
| Reporting Year (SAIDI |  | 101.538 |  |  |  | 999 | Cause unknown |  | 1 | 3.03 | 217 | 10206 |  | 26.72
| Circuit 5 Year Average (SAIFI |  |  |  | 3.449
| Reporting Year (SAIFI |  | 1.5225
| Total Circuit Length: |  |  |  | 30
| Date of Last Circuit Trim: |  |  |  | 2015
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | NEW YORK |  |  |  |  | 100 | Contractor - Planned |  | 12 | 36.36 | 21 | 2701.2 |  | 2.14
| Feeder Name: | Wickliffe |  |  |  |  | 110 | JPEC - Planned |  | 1 | 3.03 | 7 | 1737.6 |  | 1.37
[7 empty] | 300 | Equipment Failure |  | 4 | 12.12 | 95 | 8013 |  | 6.34
| Feeder Number: | 244
[7 empty] | 420 | ROW |  | 7 | 21.21 | 1036 | 108773.4 |  | 86.02
| Feeder Location | 47244-Wickliffe |  |  |  |  | 500 | Lightning |  | 2 | 6.06 | 3 | 378 |  | 0.3
| Customer Count | 355 |  |  |  |  | 690 | Animal |  | 4 | 12.12 | 11 | 1174.8 |  | 0.93
| Circuit 5 Year Average (SAIDI |  |  |  | 551.5283 |  | 999 | Cause unknown |  | 3 | 9.09 | 43 | 3667.2 |  | 2.9
| Reporting Year (SAIDI |  | 306.5425
| Circuit 5 Year Average (SAIFI |  |  |  | 2.3825
| Reporting Year (SAIFI |  | 2.9196
| Total Circuit Length: |  |  |  | 48.3
| Date of Last Circuit Trim: |  |  |  | 2021
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | NEW YORK |  |  |  |  | 100 | Contractor - Planned |  | 45 | 50.56 | 145 | 12418.2 |  | 7.92
| Feeder Name: | Slater |  |  |  |  | 110 | JPEC - Planned |  | 5 | 5.62 | 132 | 17106 |  | 10.91
[7 empty] | 300 | Equipment Failure |  | 8 | 8.99 | 167 | 28528.2 |  | 18.2
| Feeder Number: | 254
[7 empty] | 420 | ROW |  | 13 | 14.61 | 929 | 85578 |  | 54.6
| Feeder Location | 47254-Slater |  |  |  |  | 500 | Lightning |  | 3 | 3.37 | 16 | 1327.8 |  | 0.85
| Customer Count | 358 |  |  |  |  | 510 | Wind - Not Trees |  | 2 | 2.25 | 18 | 3610.2 |  | 2.3
| Circuit 5 Year Average (SAIDI |  |  |  | 414.5587 |  | 690 | Animal |  | 4 | 4.49 | 44 | 3388.2 |  | 2.16
| Reporting Year (SAIDI |  | 241.8247 |  |  |  | 700 | Member/Public Caused |  | 1 | 1.12 | 1 | 72 |  | 0.05
[7 empty] | 710 | Motor Vehicle |  | 1 | 1.12 | 1 | 90 |  | 0.06
| Circuit 5 Year Average (SAIFI |  |  |  | 2.5728
[7 empty] | 810 | Load |  | 5 | 5.62 | 36 | 4206 |  | 2.68
| Reporting Year (SAIFI |  | 3.6068
[7 empty] | 999 | Cause unknown |  | 2 | 2.25 | 4 | 403.8 |  | 0.26
Total Circuit Length:
67.5
| Date of Last Circuit Trim: |  |  |  | 2015
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | OLIVET CHURCH RD |  |  |  |  | 0 | BREC |  | 1 | 11.11 | 9 | 148.2 |  | 0.17
| Feeder Name: | Olivet Ch Rd |  |  |  |  | 100 | Contractor - Planned |  | 1 | 11.11 | 2 | 55.2 |  | 0.06
[7 empty] | 110 | JPEC - Planned |  | 1 | 11.11 | 4 | 637.8 |  | 0.74
| Feeder Number: | 214
[7 empty] | 300 | Equipment Failure |  | 1 | 11.11 | 5 | 60 |  | 0.07
| Feeder Location | 74214-Olivet Ch Rd |  |  |  |  | 420 | ROW |  | 3 | 33.33 | 604 | 36532.2 |  | 42.13
| Customer Count | 589 |  |  |  |  | 700 | Member/Public Caused |  | 1 | 11.11 | 2 | 82.2 |  | 0.09
| Circuit 5 Year Average (SAIDI |  |  |  | 112.237 |  | 710 | Motor Vehicle |  | 1 | 11.11 | 597 | 49203 |  | 56.74
| Reporting Year (SAIDI |  | 83.5857
| Circuit 5 Year Average (SAIFI |  |  |  | 1.7841
| Reporting Year (SAIFI |  | 1.0261
| Total Circuit Length: |  |  |  | 23.2
| Date of Last Circuit Trim: |  |  |  | 2015
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | OLIVET CHURCH RD |  |  |  |  | 100 | Contractor - Planned |  | 3 | 15.79 | 6 | 1332.6 |  | 2.05
| Feeder Name: | Highland Ch Rd |  |  |  |  | 300 | Equipment Failure |  | 3 | 15.79 | 579 | 30978 |  | 47.65
[7 empty] | 690 | Animal |  | 9 | 47.37 | 59 | 3047.4 |  | 4.69
| Feeder Number: | 224
[7 empty] | 700 | Member/Public Caused |  | 1 | 5.26 | 137 | 27580.8 |  | 42.43
| Feeder Location | 74224-Highland Ch |  |  |  |  | 999 | Cause unknown |  | 3 | 15.79 | 28 | 2068.8 |  | 3.18
| Customer Count | 481
| Circuit 5 Year Average (SAIDI |  |  |  | 180.058
| Reporting Year (SAIDI |  | 64.3911
| Circuit 5 Year Average (SAIFI |  |  |  | 1.5494
| Reporting Year (SAIFI |  | 1.2035
| Total Circuit Length: |  |  |  | 36
| Date of Last Circuit Trim: |  |  |  | 2015
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | OLIVET CHURCH RD |  |  |  |  | 300 | Equipment Failure |  | 1 | 50 | 8 | 10.2 |  | 0.45
| Feeder Name: | Info Age Park |  |  |  |  | 999 | Cause unknown |  | 1 | 50 | 8 | 2256 |  | 99.55
| Feeder Number: | 234
| Feeder Location | 74234-Info Age Park
| Customer Count | 8
| Circuit 5 Year Average (SAIDI |  |  |  | 169.0308
| Reporting Year (SAIDI |  | 282.0229
| Circuit 5 Year Average (SAIFI |  |  |  | 1.1
| Reporting Year (SAIFI |  | 1
| Total Circuit Length: |  |  |  | 2.7
| Date of Last Circuit Trim: |  |  |  | 2015
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | PALMA |  |  |  |  | 100 | Contractor - Planned |  | 5 | 29.41 | 6 | 303 |  | 0.21
| Feeder Name: | Hwy 95 |  |  |  |  | 300 | Equipment Failure |  | 2 | 11.76 | 365 | 42282 |  | 29.9
[7 empty] | 420 | ROW |  | 6 | 35.29 | 33 | 4705.2 |  | 3.33
| Feeder Number: | 214
[7 empty] | 999 | Cause unknown |  | 4 | 23.53 | 1125 | 94116.6 |  | 66.56
| Feeder Location | 54214-Hwy 95
| Customer Count | 369
| Circuit 5 Year Average (SAIDI |  |  |  | 217.1072
| Reporting Year (SAIDI |  | 255.2999
| Circuit 5 Year Average (SAIFI |  |  |  | 1.4643
| Reporting Year (SAIFI |  | 3.0517
| Total Circuit Length: |  |  |  | 29.8
| Date of Last Circuit Trim: |  |  |  | 2015
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | PALMA |  |  |  |  | 300 | Equipment Failure |  | 1 | 8.33 | 1 | 100.2 |  | 0.09
| Feeder Name: | Draffenville |  |  |  |  | 420 | ROW |  | 3 | 25 | 28 | 2366.4 |  | 2.17
[7 empty] | 500 | Lightning |  | 1 | 8.33 | 302 | 16096.8 |  | 14.79
| Feeder Number: | 224
[7 empty] | 510 | Wind - Not Trees |  | 1 | 8.33 | 10 | 570.6 |  | 0.52
| Feeder Location | 54224-Draffenville |  |  |  |  | 700 | Member/Public Caused |  | 1 | 8.33 | 1 | 105 |  | 0.1
| Customer Count | 302 |  |  |  |  | 710 | Motor Vehicle |  | 3 | 25 | 687 | 46892.4 |  | 43.09
| Circuit 5 Year Average (SAIDI |  |  |  | 132.1958 |  | 999 | Cause unknown |  | 2 | 16.67 | 604 | 42682.2 |  | 39.23
| Reporting Year (SAIDI |  | 155.5144
| Circuit 5 Year Average (SAIFI |  |  |  | 1.6542
| Reporting Year (SAIFI |  | 2.2784
| Total Circuit Length: |  |  |  | 21.7
| Date of Last Circuit Trim: |  |  |  | 2015
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | PALMA |  |  |  |  | 100 | Contractor - Planned |  | 2 | 5 | 4 | 311.4 |  | 0.16
| Feeder Name: | Palma |  |  |  |  | 110 | JPEC - Planned |  | 3 | 7.5 | 6 | 988.2 |  | 0.52
[7 empty] | 300 | Equipment Failure |  | 4 | 10 | 759 | 14847.6 |  | 7.78
| Feeder Number: | 234
[7 empty] | 420 | ROW |  | 8 | 20 | 133 | 3789.6 |  | 1.99
| Feeder Location | 54234-Palma |  |  |  |  | 500 | Lightning |  | 3 | 7.5 | 63 | 3610.8 |  | 1.89
| Customer Count | 744 |  |  |  |  | 510 | Wind - Not Trees |  | 1 | 2.5 | 30 | 8118.6 |  | 4.26
| Circuit 5 Year Average (SAIDI |  |  |  | 173.9651 |  | 690 | Animal |  | 12 | 30 | 48 | 2144.4 |  | 1.12
| Reporting Year (SAIDI |  | 143.4627 |  |  |  | 700 | Member/Public Caused |  | 1 | 2.5 | 14 | 952.8 |  | 0.5
[7 empty] | 710 | Motor Vehicle |  | 1 | 2.5 | 739 | 49155.6 |  | 25.76
| Circuit 5 Year Average (SAIFI |  |  |  | 1.799
[7 empty] | 810 | Load |  | 1 | 2.5 | 3 | 93 |  | 0.05
| Reporting Year (SAIFI |  | 1.9952
[7 empty] | 999 | Cause unknown |  | 4 | 10 | 1485 | 106777.8 |  | 55.97
Total Circuit Length:
57.3
| Date of Last Circuit Trim: |  |  |  | 2015
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | POSSUM TROT |  |  |  |  | 000 | No Cause Selected |  | 2 | 6.25 | 1068 | 27727.8 |  | 28.61
| Feeder Name: | Possum Trot |  |  |  |  | 100 | Contractor - Planned |  | 4 | 12.5 | 9 | 979.8 |  | 1.01
[7 empty] | 110 | JPEC - Planned |  | 1 | 3.12 | 545 | 53782.2 |  | 55.5
| Feeder Number: | 224
[7 empty] | 300 | Equipment Failure |  | 3 | 9.38 | 7 | 779.4 |  | 0.8
| Feeder Location | 78224-Possum Trot |  |  |  |  | 420 | ROW |  | 3 | 9.38 | 19 | 7635 |  | 7.88
| Customer Count | 545 |  |  |  |  | 500 | Lightning |  | 3 | 9.38 | 5 | 673.8 |  | 0.7
| Circuit 5 Year Average (SAIDI |  |  |  | 140.8413 |  | 690 | Animal |  | 14 | 43.75 | 106 | 5205.6 |  | 5.37
| Reporting Year (SAIDI |  | 98.7576 |  |  |  | 999 | Cause unknown |  | 2 | 6.25 | 2 | 126 |  | 0.13
| Circuit 5 Year Average (SAIFI |  |  |  | 1.7235
| Reporting Year (SAIFI |  | 1.9611
| Total Circuit Length: |  |  |  | 42.3
| Date of Last Circuit Trim: |  |  |  | 2015
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | POSSUM TROT |  |  |  |  | 100 | Contractor - Planned |  | 6 | 46.15 | 5 | 775.8 |  | 19.04
| Feeder Name: | Hwy 95 |  |  |  |  | 300 | Equipment Failure |  | 1 | 7.69 | 1 | 53.4 |  | 1.31
[7 empty] | 420 | ROW |  | 3 | 23.08 | 14 | 2630.4 |  | 64.57
| Feeder Number: | 234
[7 empty] | 500 | Lightning |  | 2 | 15.38 | 4 | 503.4 |  | 12.36
| Feeder Location | 78234-Hwy 95 |  |  |  |  | 999 | Cause unknown |  | 1 | 7.69 | 2 | 111 |  | 2.72
| Customer Count | 201
| Circuit 5 Year Average (SAIDI |  |  |  | 256.1155
| Reporting Year (SAIDI |  | 13.1115
| Circuit 5 Year Average (SAIFI |  |  |  | 1.3567
| Reporting Year (SAIFI |  | 0.0698
| Total Circuit Length: |  |  |  | 14.9
| Date of Last Circuit Trim: |  |  |  | 2015
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | POSSUM TROT |  |  |  |  | 420 | ROW |  | 3 | 37.5 | 72 | 7456.2 |  | 91.47
| Feeder Name: | Industrial Loop |  |  |  |  | 500 | Lightning |  | 1 | 12.5 | 2 | 135.6 |  | 1.66
[7 empty] | 700 | Member/Public Caused |  | 1 | 12.5 | 1 | 39 |  | 0.48
| Feeder Number: | 254
[7 empty] | 999 | Cause unknown |  | 3 | 37.5 | 7 | 520.8 |  | 6.39
| Feeder Location | 78254-Industrial Loo
| Customer Count | 207
| Circuit 5 Year Average (SAIDI |  |  |  | 207.1434
| Reporting Year (SAIDI |  | 36.0766
| Circuit 5 Year Average (SAIFI |  |  |  | 1.3393
| Reporting Year (SAIFI |  | 0.3484
| Total Circuit Length: |  |  |  | 24.4
| Date of Last Circuit Trim: |  |  |  | 2015
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | POSSUM TROT |  |  |  |  | None | None |  | 0 | 0 | 0 | 0 |  | 0
| Feeder Name: | CoalTek
| Feeder Number: | 264
| Feeder Location | 78264-CoalTek
| Customer Count | 2
| Circuit 5 Year Average (SAIDI |  |  |  | 97.06
| Reporting Year (SAIDI |  | 0
| Circuit 5 Year Average (SAIFI |  |  |  | 0.6
| Reporting Year (SAIFI |  | 0
| Total Circuit Length: |  |  |  | 3.9
| Date of Last Circuit Trim: |  |  |  | 2015
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | RAGLAND |  |  |  |  | 100 | Contractor - Planned |  | 20 | 35.71 | 24 | 4028.4 |  | 6.07
| Feeder Name: | Monkeys Eyebrow |  |  |  |  | 110 | JPEC - Planned |  | 1 | 1.79 | 1 | 111 |  | 0.17
[7 empty] | 300 | Equipment Failure |  | 6 | 10.71 | 15 | 1366.8 |  | 2.06
| Feeder Number: | 214
[7 empty] | 420 | ROW |  | 13 | 23.21 | 151 | 17419.8 |  | 26.23
| Feeder Location | 19214-Monkeys Eye |  |  |  |  | 500 | Lightning |  | 1 | 1.79 | 4 | 583.2 |  | 0.88
| Customer Count | 238 |  |  |  |  | 510 | Wind - Not Trees |  | 2 | 3.57 | 259 | 35031 |  | 52.76
| Circuit 5 Year Average (SAIDI |  |  |  | 246.857 |  | 690 | Animal |  | 7 | 12.5 | 43 | 4042.8 |  | 6.09
| Reporting Year (SAIDI |  | 147.3386 |  |  |  | 999 | Cause unknown |  | 6 | 10.71 | 24 | 3819.6 |  | 5.75
| Circuit 5 Year Average (SAIFI |  |  |  | 1.5882
| Reporting Year (SAIFI |  | 1.0893
| Total Circuit Length: |  |  |  | 50
| Date of Last Circuit Trim: |  |  |  | 2017
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | RAGLAND |  |  |  |  | 100 | Contractor - Planned |  | 3 | 17.65 | 4 | 1118.4 |  | 11.18
| Feeder Name: | Ragland |  |  |  |  | 110 | JPEC - Planned |  | 1 | 5.88 | 2 | 78.6 |  | 0.79
[7 empty] | 300 | Equipment Failure |  | 4 | 23.53 | 5 | 686.4 |  | 6.86
| Feeder Number: | 224
[7 empty] | 420 | ROW |  | 2 | 11.76 | 1 | 131.4 |  | 1.31
| Feeder Location | 19224-Ragland |  |  |  |  | 500 | Lightning |  | 1 | 5.88 | 34 | 4405.2 |  | 44.02
| Customer Count | 222 |  |  |  |  | 690 | Animal |  | 4 | 23.53 | 4 | 292.8 |  | 2.93
| Circuit 5 Year Average (SAIDI |  |  |  | 254.5866 |  | 810 | Load |  | 1 | 5.88 | 35 | 2996.4 |  | 29.94
| Reporting Year (SAIDI |  | 19.8364 |  |  |  | 999 | Cause unknown |  | 1 | 5.88 | 2 | 298.8 |  | 2.99
| Circuit 5 Year Average (SAIFI |  |  |  | 1.0798
| Reporting Year (SAIFI |  | 0.1576
| Total Circuit Length: |  |  |  | 33.4
| Date of Last Circuit Trim: |  |  |  | 2017
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | REIDLAND |  |  |  |  | 100 | Contractor - Planned |  | 6 | 37.5 | 12 | 639.6 |  | 1.25
| Feeder Name: | Ken Mar Rd |  |  |  |  | 110 | JPEC - Planned |  | 2 | 12.5 | 11 | 970.8 |  | 1.9
[7 empty] | 300 | Equipment Failure |  | 3 | 18.75 | 8 | 811.2 |  | 1.59
| Feeder Number: | 214
[7 empty] | 420 | ROW |  | 4 | 25 | 665 | 48318 |  | 94.54
| Feeder Location | 41214-Ken Mar Rd |  |  |  |  | 999 | Cause unknown |  | 1 | 6.25 | 7 | 368.4 |  | 0.72
| Customer Count | 341
| Circuit 5 Year Average (SAIDI |  |  |  | 192.0235
| Reporting Year (SAIDI |  | 141.865
| Circuit 5 Year Average (SAIFI |  |  |  | 1.8744
| Reporting Year (SAIFI |  | 1.9525
| Total Circuit Length: |  |  |  | 20.1
| Date of Last Circuit Trim: |  |  |  | 2017
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | REIDLAND |  |  |  |  | 420 | ROW |  | 1 | 20 | 2 | 131.4 |  | 24.39
| Feeder Name: | Reidland Water |  |  |  |  | 690 | Animal |  | 3 | 60 | 6 | 346.2 |  | 64.25
[7 empty] | 999 | Cause unknown |  | 1 | 20 | 2 | 61.2 |  | 11.36
| Feeder Number: | 224
| Feeder Location | 41224-Reidland Wat
| Customer Count | 50
| Circuit 5 Year Average (SAIDI |  |  |  | 27.5514
| Reporting Year (SAIDI |  | 6.8874
| Circuit 5 Year Average (SAIFI |  |  |  | 0.4177
| Reporting Year (SAIFI |  | 0.1193
| Total Circuit Length: |  |  |  | 2.9
| Date of Last Circuit Trim: |  |  |  | 2017
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | REIDLAND |  |  |  |  | 100 | Contractor - Planned |  | 1 | 14.29 | 3 | 496.8 |  | 8.19
| Feeder Name: | Epperson Rd |  |  |  |  | 110 | JPEC - Planned |  | 1 | 14.29 | 2 | 61.2 |  | 1.01
[7 empty] | 300 | Equipment Failure |  | 2 | 28.57 | 7 | 361.8 |  | 5.96
| Feeder Number: | 234
[7 empty] | 420 | ROW |  | 2 | 28.57 | 33 | 4931.4 |  | 81.25
| Feeder Location | 41234-Epperson Rd |  |  |  |  | 999 | Cause unknown |  | 1 | 14.29 | 4 | 218.4 |  | 3.6
| Customer Count | 197
| Circuit 5 Year Average (SAIDI |  |  |  | 170.0368
| Reporting Year (SAIDI |  | 25.0256
| Circuit 5 Year Average (SAIFI |  |  |  | 0.9237
| Reporting Year (SAIFI |  | 0.1675
| Total Circuit Length: |  |  |  | 9.9
| Date of Last Circuit Trim: |  |  |  | 2017
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | REIDLAND |  |  |  |  | 300 | Equipment Failure |  | 1 | 16.67 | 2 | 418.8 |  | 3.14
| Feeder Name: | Walker Boat Yard |  |  |  |  | 420 | ROW |  | 3 | 50 | 105 | 12300.6 |  | 92.14
[7 empty] | 500 | Lightning |  | 1 | 16.67 | 4 | 340.2 |  | 2.55
| Feeder Number: | 244
[7 empty] | 690 | Animal |  | 1 | 16.67 | 4 | 290.4 |  | 2.18
| Feeder Location | 41244-Walker Boat
| Customer Count | 98
| Circuit 5 Year Average (SAIDI |  |  |  | 112.9257
| Reporting Year (SAIDI |  | 124.9788
| Circuit 5 Year Average (SAIFI |  |  |  | 0.8515
| Reporting Year (SAIFI |  | 1.0669
| Total Circuit Length: |  |  |  | 12.9
| Date of Last Circuit Trim: |  |  |  | 2017
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | SMITHLAND |  |  |  |  | 100 | Contractor - Planned |  | 3 | 15.79 | 5 | 1916.4 |  | 19.63
| Feeder Name: | Smithland |  |  |  |  | 110 | JPEC - Planned |  | 4 | 21.05 | 7 | 609 |  | 6.24
[7 empty] | 300 | Equipment Failure |  | 2 | 10.53 | 9 | 1084.8 |  | 11.11
| Feeder Number: | 214
[7 empty] | 420 | ROW |  | 1 | 5.26 | 1 | 92.4 |  | 0.95
| Feeder Location | 32214-Smithland |  |  |  |  | 500 | Lightning |  | 1 | 5.26 | 1 | 58.8 |  | 0.6
| Customer Count | 381 |  |  |  |  | 690 | Animal |  | 3 | 15.79 | 13 | 786 |  | 8.05
| Circuit 5 Year Average (SAIDI |  |  |  | 210.549 |  | 700 | Member/Public Caused |  | 2 | 10.53 | 12 | 1236.6 |  | 12.66
| Reporting Year (SAIDI |  | 8.9637 |  |  |  | 710 | Motor Vehicle |  | 1 | 5.26 | 4 | 561.6 |  | 5.75
[7 empty] | 999 | Cause unknown |  | 2 | 10.53 | 19 | 3419.4 |  | 35.02
| Circuit 5 Year Average (SAIFI |  |  |  | 1.0139
| Reporting Year (SAIFI |  | 0.0498
| Total Circuit Length: |  |  |  | 30
| Date of Last Circuit Trim: |  |  |  | 2019
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | SMITHLAND |  |  |  |  | 100 | Contractor - Planned |  | 7 | 20 | 8 | 1047 |  | 1.09
| Feeder Name: | Tiline |  |  |  |  | 110 | JPEC - Planned |  | 1 | 2.86 | 3 | 895.8 |  | 0.94
[7 empty] | 300 | Equipment Failure |  | 2 | 5.71 | 15 | 886.8 |  | 0.93
| Feeder Number: | 224
[7 empty] | 420 | ROW |  | 5 | 14.29 | 688 | 35659.8 |  | 37.22
| Feeder Location | 32224-Tiline |  |  |  |  | 500 | Lightning |  | 8 | 22.86 | 79 | 10291.2 |  | 10.74
| Customer Count | 558 |  |  |  |  | 510 | Wind - Not Trees |  | 1 | 2.86 | 78 | 23669.4 |  | 24.71
| Circuit 5 Year Average (SAIDI |  |  |  | 490.2855 |  | 690 | Animal |  | 7 | 20 | 55 | 4678.2 |  | 4.88
| Reporting Year (SAIDI |  | 63.9267 |  |  |  | 810 | Load |  | 1 | 2.86 | 1 | 112.8 |  | 0.12
[7 empty] | 999 | Cause unknown |  | 3 | 8.57 | 158 | 18557.4 |  | 19.37
| Circuit 5 Year Average (SAIFI |  |  |  | 2.3753
| Reporting Year (SAIFI |  | 1.2334
| Total Circuit Length: |  |  |  | 105.9
| Date of Last Circuit Trim: |  |  |  | 2019
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | SMITHLAND |  |  |  |  | 100 | Contractor - Planned |  | 6 | 21.43 | 9 | 1454.4 |  | 3.36
| Feeder Name: | Mitchell Store |  |  |  |  | 110 | JPEC - Planned |  | 2 | 7.14 | 3 | 118.2 |  | 0.27
[7 empty] | 300 | Equipment Failure |  | 3 | 10.71 | 5 | 267.6 |  | 0.62
| Feeder Number: | 244
[7 empty] | 420 | ROW |  | 6 | 21.43 | 30 | 7668.6 |  | 17.7
| Feeder Location | 32244-Mitchell Store |  |  |  |  | 500 | Lightning |  | 5 | 17.86 | 15 | 1217.4 |  | 2.81
| Customer Count | 385 |  |  |  |  | 690 | Animal |  | 1 | 3.57 | 1 | 50.4 |  | 0.12
| Circuit 5 Year Average (SAIDI |  |  |  | 464.8189 |  | 700 | Member/Public Caused |  | 1 | 3.57 | 1 | 68.4 |  | 0.16
| Reporting Year (SAIDI |  | 84.2723 |  |  |  | 999 | Cause unknown |  | 4 | 14.29 | 403 | 32476.8 |  | 74.97
| Circuit 5 Year Average (SAIFI |  |  |  | 2.0266
| Reporting Year (SAIFI |  | 1.0457
| Total Circuit Length: |  |  |  | 56.7
| Date of Last Circuit Trim: |  |  |  | 2019
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | SMITHLAND |  |  |  |  | None | None |  | 0 | 0 | 0 | 0 |  | 0
| Feeder Name: | REC_00004485
| Feeder Number: | 3
| Feeder Location | 04485-REC_000044
| Customer Count | 0
| Circuit 5 Year Average (SAIDI |  |  |  | 0
| Reporting Year (SAIDI |  | 0
| Circuit 5 Year Average (SAIFI |  |  |  | 0
| Reporting Year (SAIFI |  | 0
Total Circuit Length:
Date of Last Circuit Trim:
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | STRAWBERRY HILL |  |  |  |  | 100 | Contractor - Planned |  | 4 | 12.9 | 15 | 2402.4 |  | 8.6
| Feeder Name: | Hansen Rd |  |  |  |  | 110 | JPEC - Planned |  | 4 | 12.9 | 8 | 585.6 |  | 2.1
[7 empty] | 300 | Equipment Failure |  | 5 | 16.13 | 69 | 8269.2 |  | 29.62
| Feeder Number: | 224
[7 empty] | 420 | ROW |  | 7 | 22.58 | 62 | 6146.4 |  | 22.01
| Feeder Location | 77224-Hansen Rd |  |  |  |  | 530 | Flood |  | 4 | 12.9 | 91 | 7171.8 |  | 25.69
| Customer Count | 731 |  |  |  |  | 690 | Animal |  | 6 | 19.35 | 20 | 1006.2 |  | 3.6
| Circuit 5 Year Average (SAIDI |  |  |  | 126.7881 |  | 999 | Cause unknown |  | 1 | 3.23 | 30 | 2337.6 |  | 8.37
| Reporting Year (SAIDI |  | 11.3185
| Circuit 5 Year Average (SAIFI |  |  |  | 1.3014
| Reporting Year (SAIFI |  | 0.1246
| Total Circuit Length: |  |  |  | 31.1
| Date of Last Circuit Trim: |  |  |  | 2015
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | STRAWBERRY HILL |  |  |  |  | 0 | BREC |  | 1 | 50 | 13 | 78.6 |  | 0.58
| Feeder Name: | Walmart |  |  |  |  | 999 | Cause unknown |  | 1 | 50 | 93 | 13477.2 |  | 99.42
| Feeder Number: | 234
| Feeder Location | 77234-Walmart
| Customer Count | 542
| Circuit 5 Year Average (SAIDI |  |  |  | 66.233
| Reporting Year (SAIDI |  | 24.8484
| Circuit 5 Year Average (SAIFI |  |  |  | 0.4539
| Reporting Year (SAIFI |  | 0.1715
| Total Circuit Length: |  |  |  | 9.7
| Date of Last Circuit Trim: |  |  |  | 2015
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | STRAWBERRY HILL |  |  |  |  | None | None |  | 0 | 0 | 0 | 0 |  | 0
| Feeder Name: | CSI
| Feeder Number: | 254
| Feeder Location | 77254-CSI
| Customer Count | 87
| Circuit 5 Year Average (SAIDI |  |  |  | 2.1645
| Reporting Year (SAIDI |  | 0
| Circuit 5 Year Average (SAIFI |  |  |  | 0.3964
| Reporting Year (SAIFI |  | 0
| Total Circuit Length: |  |  |  | 5
| Date of Last Circuit Trim: |  |  |  | 2015
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | STRAWBERRY HILL |  |  |  |  | None | None |  | 0 | 0 | 0 | 0 |  | 0
| Feeder Name: | Hwy 60
| Feeder Number: | 264
| Feeder Location | 77264-Hwy 60
| Customer Count | 13
| Circuit 5 Year Average (SAIDI |  |  |  | 60.0958
| Reporting Year (SAIDI |  | 0
| Circuit 5 Year Average (SAIFI |  |  |  | 0.5439
| Reporting Year (SAIFI |  | 0
| Total Circuit Length: |  |  |  | 1.8
| Date of Last Circuit Trim: |  |  |  | 2015
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | STRAWBERRY HILL |  |  |  |  | None | None |  | 0 | 0 | 0 | 0 |  | 0
| Feeder Name: | REC_00000309
| Feeder Number: | 4
| Feeder Location | 77244-REC_000003
| Customer Count | 0
| Circuit 5 Year Average (SAIDI |  |  |  | 0
| Reporting Year (SAIDI |  | 0
| Circuit 5 Year Average (SAIFI |  |  |  | 0
| Reporting Year (SAIFI |  | 0
Total Circuit Length:
Date of Last Circuit Trim:
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | VULCAN |  |  |  |  | None | None |  | 0 | 0 | 0 | 0 |  | 0
| Feeder Name: | Vulcan Pit
| Feeder Number: | 224
| Feeder Location | 45224-Vulcan Pit
| Customer Count | 0
| Circuit 5 Year Average (SAIDI |  |  |  | 0
| Reporting Year (SAIDI |  | 0
| Circuit 5 Year Average (SAIFI |  |  |  | 0
| Reporting Year (SAIFI |  | 0
| Total Circuit Length: |  |  |  | 2.4
Date of Last Circuit Trim:
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | VULCAN |  |  |  |  | None | None |  | 0 | 0 | 0 | 0 |  | 0
| Feeder Name: | Vulcan 1 Rock Crush
| Feeder Number: | 234
| Feeder Location | 45234-Vulcan 1 Roc
| Customer Count | 1
| Circuit 5 Year Average (SAIDI |  |  |  | 322.02
| Reporting Year (SAIDI |  | 0
| Circuit 5 Year Average (SAIFI |  |  |  | 2.2
| Reporting Year (SAIFI |  | 0
| Total Circuit Length: |  |  |  | 1
Date of Last Circuit Trim:
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | VULCAN |  |  |  |  | 110 | JPEC - Planned |  | 1 | 25 | 35 | 274.2 |  | 2.34
| Feeder Name: | Kinder Morgan |  |  |  |  | 690 | Animal |  | 3 | 75 | 104 | 11442.6 |  | 97.66
| Feeder Number: | 244
| Feeder Location | 45244-Kinder Morga
| Customer Count | 35
| Circuit 5 Year Average (SAIDI |  |  |  | 1275.9898
| Reporting Year (SAIDI |  | 330.6227
| Circuit 5 Year Average (SAIFI |  |  |  | 11.0257
| Reporting Year (SAIFI |  | 3.0049
| Total Circuit Length: |  |  |  | 8.1
Date of Last Circuit Trim:
Corrective Action Plan:
[7 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins |  | % of Total
| Substation Name | VULCAN |  |  |  |  | 690 | Animal |  | 1 | 33.33 | 2 | 393 |  | 48.23
| Feeder Name: | Vulcan 2 Hwy 62 |  |  |  |  | 810 | Load |  | 1 | 33.33 | 0 | 0 |  | 0
[7 empty] | 999 | Cause unknown |  | 1 | 33.33 | 2 | 421.8 |  | 51.77
| Feeder Number: | 254
| Feeder Location | 45254-Vulcan 2 Hwy
| Customer Count | 2
| Circuit 5 Year Average (SAIDI |  |  |  | 192.8582
| Reporting Year (SAIDI |  | 224.4858
| Circuit 5 Year Average (SAIFI |  |  |  | 1.4894
| Reporting Year (SAIFI |  | 1.0638
| Total Circuit Length: |  |  |  | 5
Date of Last Circuit Trim:
Corrective Action Plan:
| Total Customer Hrs Off: |  |  | 67948.61 |  | Total Customer Mins Off |  |  | 4076916.6
| Total Customers Affected: |  |  | 46807
| Total Outage Count: |  |  | 1871
53040 | [6 empty] | /report/19020/rptcustom/oms/OMS_ANNUAL_RLBLTY_RPT_19020.xml.rpt

## 2021 Circuit Details
JACKSON PURCHASE ENERGY CORP.
Rev: 202306200609
| 2024-05-29 | 10:08 |  |  |  | ANNUAL RELIABILITY REPORT
2021
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | BURNA |  |  |  | 500 | Lightning |  | 1 | 100 | 1 | 159 | 100
| Feeder Name: | Hampton
| Feeder Number: | 214
| Feeder Location | 14214-Hampton
| Customer Count | 85
| Circuit 5 Year Average (SAIDI |  |  | 284.1884
| Reporting Year (SAIDI |  | 1.8674
| Circuit 5 Year Average (SAIFI |  |  | 1.1319
| Reporting Year (SAIFI |  | 0.0117
| Total Circuit Length: | 10
| Date of Last Circuit Trim: | 2019
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | BURNA |  |  |  | 100 | Contractor - Planned |  | 1 | 6.67 | 1 | 139.2 | 1.3
| Feeder Name: | Salem |  |  |  | 110 | JPEC - Planned |  | 3 | 20 | 8 | 1576.2 | 14.72
[6 empty] | 300 | Equipment Failure |  | 2 | 13.33 | 30 | 3853.2 | 36
| Feeder Number: | 244
[6 empty] | 430 | Tree failure from overhang or dead tree without ice/snow |  | 1 | 6.67 | 1 | 306 | 2.86
| Feeder Location | 14244-Salem |  |  |  | 435 | Tree Failure from outside of ROW |  | 1 | 6.67 | 16 | 1876.2 | 17.53
| Customer Count | 325 |  |  |  | 500 | Lightning |  | 3 | 20 | 24 | 2600.4 | 24.29
| Circuit 5 Year Average (SAIDI |  |  | 706.5254 |  | 600 | Small animal/bird |  | 1 | 6.67 | 1 | 106.2 | 0.99
| Reporting Year (SAIDI |  | 11.8706 |  |  | 630 | Squirrel |  | 1 | 6.67 | 1 | 132 | 1.23
[6 empty] | 690 | Animal |  | 2 | 13.33 | 2 | 115.2 | 1.08
| Circuit 5 Year Average (SAIFI |  |  | 1.5422
| Reporting Year (SAIFI |  | 0.0924
| Total Circuit Length: | 39.4
| Date of Last Circuit Trim: | 2019
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | BURNA |  |  |  | 100 | Contractor - Planned |  | 1 | 7.69 | 4 | 413.4 | 0.26
| Feeder Name: | Smithland |  |  |  | 300 | Equipment Failure |  | 3 | 23.08 | 5 | 799.8 | 0.5
[6 empty] | 420 | ROW |  | 1 | 7.69 | 117 | 60350.4 | 37.38
| Feeder Number: | 254
[6 empty] | 430 | Tree failure from overhang or dead tree without ice/snow |  | 1 | 7.69 | 1 | 294.6 | 0.18
| Feeder Location | 14254-Smithland |  |  |  | 435 | Tree Failure from outside of ROW |  | 2 | 15.38 | 351 | 74353.2 | 46.05
| Customer Count | 350 |  |  |  | 540 | Storm |  | 1 | 7.69 | 1 | 135.6 | 0.08
| Circuit 5 Year Average (SAIDI |  |  | 464.6589 |  | 690 | Animal |  | 1 | 7.69 | 1 | 162.6 | 0.1
| Reporting Year (SAIDI |  | 212.4571 |  |  | 700 | Member/Public Caused |  | 2 | 15.38 | 19 | 1817.4 | 1.13
[6 empty] | 999 | Cause unknown |  | 1 | 7.69 | 350 | 23123.4 | 14.32
| Circuit 5 Year Average (SAIFI |  |  | 2.6997
| Reporting Year (SAIFI |  | 1.0029
| Total Circuit Length: | 69.7
| Date of Last Circuit Trim: | 2019
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | CALVERT CITY |  |  |  | 110 | JPEC - Planned |  | 2 | 28.57 | 4 | 367.8 | 8.36
| Feeder Name: | Hwy 95 |  |  |  | 300 | Equipment Failure |  | 1 | 14.29 | 33 | 2951.4 | 67.07
[6 empty] | 500 | Lightning |  | 1 | 14.29 | 8 | 793.2 | 18.03
| Feeder Number: | 214
[6 empty] | 630 | Squirrel |  | 2 | 28.57 | 3 | 226.2 | 5.14
| Feeder Location | 43214-Hwy 95 |  |  |  | 690 | Animal |  | 1 | 14.29 | 1 | 61.8 | 1.4
| Customer Count | 250
| Circuit 5 Year Average (SAIDI |  |  | 154.3016
| Reporting Year (SAIDI |  | 11.8038
| Circuit 5 Year Average (SAIFI |  |  | 0.5919
| Reporting Year (SAIFI |  | 0.132
| Total Circuit Length: | 18.6
| Date of Last Circuit Trim: | 2017
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
| Substation Name | CALVERT CITY |  |  |  | 100 | Contractor - Planned |  | 1 | 5.56 | 4 | 122.4 | 1.15
| Feeder Name: | Calvert Heights |  |  |  | 110 | JPEC - Planned |  | 6 | 33.33 | 9 | 1008.6 | 9.46
[6 empty] | 400 | Decay/age of material/equipment |  | 1 | 5.56 | 1 | 73.8 | 0.69
| Feeder Number: | 224 |  |  |  | 420 | ROW |  | 6 | 33.33 | 108 | 7251.6 | 68.02
[6 empty] | 600 | Small animal/bird |  | 1 | 5.56 | 4 | 244.2 | 2.29
| Feeder Location | 43224-Calvert Height |  |  |  | 630 | Squirrel |  | 1 | 5.56 | 24 | 1689 | 15.84
| Customer Count | 649 |  |  |  | 999 | Cause unknown |  | 2 | 11.11 | 3 | 270.6 | 2.54
| Circuit 5 Year Average (SAIDI |  |  | 146.5112
| Reporting Year (SAIDI |  | 11.1686
| Circuit 5 Year Average (SAIFI |  |  | 0.7672
| Reporting Year (SAIFI |  | 0.1663
| Total Circuit Length: | 28.2
| Date of Last Circuit Trim: | 2017
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | 100 | Contractor - Planned |  | 1 | 8.33 | 1 | 125.4 | 0.59
| Substation Name | CALVERT CITY |  |  |  | 110 | JPEC - Planned |  | 7 | 58.33 | 101 | 19355.4 | 90.92
| Feeder Name: | Gilbertsville |  |  |  | 300 | Equipment Failure |  | 2 | 16.67 | 5 | 1582.8 | 7.43
| Feeder Number: | 234 |  |  |  | 500 | Lightning |  | 1 | 8.33 | 1 | 54.6 | 0.26
[6 empty] | 740 | Public cuts tree |  | 1 | 8.33 | 3 | 171 | 0.8
| Feeder Location | 43234-Gilbertsville
| Customer Count | 340
| Circuit 5 Year Average (SAIDI |  |  | 10390.2025
| Reporting Year (SAIDI |  | 56.8657
| Circuit 5 Year Average (SAIFI |  |  | 0.765
| Reporting Year (SAIFI |  | 0.2967
| Total Circuit Length: | 12.6
| Date of Last Circuit Trim: | 2017
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | 999 | Cause unknown |  | 1 | 100 | 1 | 46.2 | 100
| Substation Name | CALVERT CITY
| Feeder Name: | Industrial Park
| Feeder Number: | 244
| Feeder Location | 43244-Industrial Park
| Customer Count | 25
| Circuit 5 Year Average (SAIDI |  |  | 135.0165
| Reporting Year (SAIDI |  | 1.8656
| Circuit 5 Year Average (SAIFI |  |  | 0.6961
| Reporting Year (SAIFI |  | 0.0405
| Total Circuit Length: | 3.4
| Date of Last Circuit Trim: | 2017
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | 110 | JPEC - Planned |  | 3 | 17.65 | 388 | 1059 | 7.28
| Substation Name | COLEMAN ROAD |  |  |  | 300 | Equipment Failure |  | 2 | 11.76 | 63 | 705.6 | 14.16
| Feeder Name: | Conrad Heights |  |  |  | 420 | ROW |  | 5 | 29.41 | 425 | 1764.6 | 24.24
| Feeder Number: | 224 |  |  |  | 430 | Tree failure from overhang or dead tree without ice/snow |  | 1 | 5.88 | 7 | 1552.8 | 1.31
[6 empty] | 510 | Wind - Not Trees |  | 1 | 5.88 | 2 | 167.4 | 0.14
| Feeder Location | 30224-Conrad Height |  |  |  | 630 | Squirrel |  | 1 | 5.88 | 5 | 188.4 | 0.16
| Customer Count | 370 |  |  |  | 690 | Animal |  | 1 | 5.88 | 4 | 290.4 | 0.24
| Circuit 5 Year Average (SAIDI |  |  | 307.9173 |  | 800 | Other |  | 1 | 5.88 | 377 | 61809 | 52.06
| Reporting Year (SAIDI |  | 166.9029 |  |  | 999 | Cause unknown |  | 2 | 11.76 | 8 | 478.8 | 0.4
| Circuit 5 Year Average (SAIFI |  |  | 1.982
| Reporting Year (SAIFI |  | 1.1476
| Total Circuit Length: | 4.5
| Date of Last Circuit Trim: | 2018
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | 300 | Equipment Failure |  | 1 | 20 | 1 | 88.2 | 10.7
| Substation Name | COLEMAN ROAD |  |  |  | 690 | Animal |  | 1 | 20 | 3 | 93.6 | 11.35
| Feeder Name: | Hwy 60 Business |  |  |  | 999 | Cause unknown |  | 3 | 60 | 25 | 642.6 | 77.95
| Feeder Number: | 244
| Feeder Location | 30244-Hwy 60 Busin
| Customer Count | 104
| Circuit 5 Year Average (SAIDI |  |  | 193.5016
| Reporting Year (SAIDI |  | 6.1617
| Circuit 5 Year Average (SAIFI |  |  | 0.9284
| Reporting Year (SAIFI |  | 0.2398
| Total Circuit Length: | 3.2
| Date of Last Circuit Trim: | 2018
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | 435 | Tree Failure from outside of ROW |  | 1 | 100 | 72 | 11181.6 | 100
| Substation Name | COLEMAN ROAD
| Feeder Name: | KY Oaks Mall
| Feeder Number: | 254
| Feeder Location | 30254-KY Oaks Mall
| Customer Count | 79
| Circuit 5 Year Average (SAIDI |  |  | 183.4989
| Reporting Year (SAIDI |  | 141.5213
| Circuit 5 Year Average (SAIFI |  |  | 0.8176
| Reporting Year (SAIFI |  | 0.9113
| Total Circuit Length: | 1.3
| Date of Last Circuit Trim: | 2018
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | 300 | Equipment Failure |  | 3 | 27.27 | 431 | 22948.2 | 33.48
| Substation Name | CULP |  |  |  | 430 | Tree failure from overhang or dead tree without ice/snow |  | 1 | 9.09 | 1 | 6 | 0.01
| Feeder Name: | Proform |  |  |  | 630 | Squirrel |  | 1 | 9.09 | 427 | 9607.8 | 14.02
| Feeder Number: | 214 |  |  |  | 690 | Animal |  | 4 | 36.36 | 448 | 32049.6 | 46.76
[6 empty] | 999 | Cause unknown |  | 2 | 18.18 | 49 | 3922.8 | 5.72
| Feeder Location | 42214-Proform
| Customer Count | 428
| Circuit 5 Year Average (SAIDI |  |  | 649.3008
| Reporting Year (SAIDI |  | 74.9113
| Circuit 5 Year Average (SAIFI |  |  | 1.5763
| Reporting Year (SAIFI |  | 1.0471
| Total Circuit Length: | 25.7
| Date of Last Circuit Trim: | 2018
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | 190 | Other planned |  | 1 | 12.5 | 49 | 6488.4 | 40.46
| Substation Name | CULP |  |  |  | 300 | Equipment Failure |  | 3 | 37.5 | 98 | 2815.2 | 17.55
| Feeder Name: | Little Cypress |  |  |  | 510 | Wind - Not Trees |  | 1 | 12.5 | 1 | 111.6 | 0.7
| Feeder Number: | 224 |  |  |  | 630 | Squirrel |  | 1 | 12.5 | 49 | 1123.2 | 7
[6 empty] | 690 | Animal |  | 2 | 25 | 48 | 5499.6 | 34.29
| Feeder Location | 42224-Little Cypress
| Customer Count | 49
| Circuit 5 Year Average (SAIDI |  |  | 553.3068
| Reporting Year (SAIDI |  | 132.9866
| Circuit 5 Year Average (SAIFI |  |  | 1.6848
| Reporting Year (SAIFI |  | 2.0086
| Total Circuit Length: | 8.1
| Date of Last Circuit Trim: | 2018
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | 100 | Contractor - Planned |  | 8 | 16.33 | 12 | 2368.8 | 3.72
| Substation Name | CULP |  |  |  | 110 | JPEC - Planned |  | 27 | 55.1 | 70 | 6190.2 | 9.71
| Feeder Name: | Possum Trot |  |  |  | 300 | Equipment Failure |  | 2 | 4.08 | 202 | 10443.6 | 16.39
| Feeder Number: | 234 |  |  |  | 420 | ROW |  | 1 | 2.04 | 2 | 295.2 | 0.46
[6 empty] | 500 | Lightning |  | 1 | 2.04 | 201 | 19630.8 | 30.81
| Feeder Location | 42234-Possum Trot |  |  |  | 630 | Squirrel |  | 1 | 2.04 | 199 | 5598.6 | 8.79
| Customer Count | 203 |  |  |  | 690 | Animal |  | 3 | 6.12 | 203 | 17451.6 | 27.39
| Circuit 5 Year Average (SAIDI |  |  | 446.8884 |  | 800 | Other |  | 1 | 2.04 | 1 | 55.8 | 0.09
| Reporting Year (SAIDI |  | 96.633 |  |  | 999 | Cause unknown |  | 5 | 10.2 | 15 | 1688.4 | 2.65
| Circuit 5 Year Average (SAIFI |  |  | 1.7819
| Reporting Year (SAIFI |  | 0.9993
| Total Circuit Length: | 18.7
| Date of Last Circuit Trim: | 2018
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | 100 | Contractor - Planned |  | 1 | 3.7 | 3 | 679.8 | 0.69
| Substation Name | CULP |  |  |  | 110 | JPEC - Planned |  | 2 | 7.41 | 5 | 615.6 | 0.62
| Feeder Name: | Sharpe |  |  |  | 300 | Equipment Failure |  | 4 | 14.81 | 1106 | 59441.4 | 60.11
| Feeder Number: | 244 |  |  |  | 420 | ROW |  | 4 | 14.81 | 13 | 1455 | 1.47
[6 empty] | 435 | Tree Failure from outside of ROW |  | 3 | 11.11 | 41 | 3710.4 | 3.75
| Feeder Location | 42244-Sharpe |  |  |  | 630 | Squirrel |  | 4 | 14.81 | 1107 | 32009.4 | 32.37
| Customer Count | 1111 |  |  |  | 690 | Animal |  | 6 | 22.22 | 20 | 432.6 | 0.44
| Circuit 5 Year Average (SAIDI |  |  | 125.3903 |  | 999 | Cause unknown |  | 3 | 11.11 | 12 | 541.2 | 0.55
| Reporting Year (SAIDI |  | 53.5089
| Circuit 5 Year Average (SAIFI |  |  | 1.232
| Reporting Year (SAIFI |  | 0.9965
| Total Circuit Length: | 78.5
| Date of Last Circuit Trim: | 2018
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | 0 | BREC |  | 1 | 12.5 | 114 | 8838.6 | 17.15
| Substation Name | CUMBERLAND JPEC |  |  |  | 110 | JPEC - Planned |  | 2 | 25 | 115 | 1172.4 | 2.28
| Feeder Name: | Pinckneyville |  |  |  | 320 | Clearance |  | 1 | 12.5 | 47 | 10182 | 19.76
| Feeder Number: | 224 |  |  |  | 690 | Animal |  | 2 | 25 | 228 | 31046.4 | 60.25
[6 empty] | 999 | Cause unknown |  | 2 | 25 | 2 | 286.2 | 0.56
| Feeder Location | 15224-Pinckneyville
| Customer Count | 115
| Circuit 5 Year Average (SAIDI |  |  | 459.1585
| Reporting Year (SAIDI |  | 270.5062
| Circuit 5 Year Average (SAIFI |  |  | 1.8803
| Reporting Year (SAIFI |  | 1.9866
| Total Circuit Length: | 23.2
| Date of Last Circuit Trim: | 2019
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | 500 | Lightning |  | 1 | 33.33 | 3 | 634.8 | 8.26
| Substation Name | CUMBERLANDQUA |  |  |  | 690 | Animal |  | 1 | 33.33 | 3 | 445.8 | 5.8
| Feeder Name: | Quarry |  |  |  | 998 | Unknown-will determine later |  | 1 | 33.33 | 30 | 6607.8 | 85.95
| Feeder Number: | 234
| Feeder Location | 15234-Quarry
| Customer Count | 31
| Circuit 5 Year Average (SAIDI |  |  | 256.2907
| Reporting Year (SAIDI |  | 215.1742
| Circuit 5 Year Average (SAIFI |  |  | 1.2699
| Reporting Year (SAIFI |  | 0.9769
| Total Circuit Length: | 3.8
| Date of Last Circuit Trim: | 2019
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | 100 | Contractor - Planned |  | 1 | 11.11 | 1 | 26.4 | 0.33
| Substation Name | DRAFFENVILLE |  |  |  | 110 | JPEC - Planned |  | 2 | 22.22 | 5 | 312 | 3.94
| Feeder Name: | Draffenville |  |  |  | 360 | Other equipment installation/design |  | 1 | 11.11 | 8 | 757.2 | 9.55
| Feeder Number: | 214 |  |  |  | 420 | ROW |  | 1 | 11.11 | 4 | 1858.2 | 23.45
[6 empty] | 690 | Animal |  | 1 | 11.11 | 1 | 111.6 | 1.41
| Feeder Location | 66214-Draffenville |  |  |  | 999 | Cause unknown |  | 3 | 33.33 | 51 | 4859.4 | 61.32
| Customer Count | 491
| Circuit 5 Year Average (SAIDI |  |  | 11.451
| Reporting Year (SAIDI |  | 9.8998
| Circuit 5 Year Average (SAIFI |  |  | 0.0689
| Reporting Year (SAIFI |  | 0.1039
| Total Circuit Length: | 29.3
| Date of Last Circuit Trim: | 2019
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | 110 | JPEC - Planned |  | 2 | 5.13 | 8 | 651 | 0.3
| Substation Name | FREEMONT |  |  |  | 300 | Equipment Failure |  | 3 | 7.69 | 4 | 1205.4 | 0.56
| Feeder Name: | Symsonia |  |  |  | 420 | ROW |  | 6 | 15.38 | 2076 | 56549.4 | 26.46
| Feeder Number: | 214 |  |  |  | 430 | Tree failure from overhang or dead tree without ice/snow |  | 3 | 7.69 | 5 | 674.4 | 0.32
[6 empty] | 435 | Tree Failure from outside of ROW |  | 2 | 5.13 | 301 | 27282 | 12.76
| Feeder Location | 51214-Symsonia |  |  |  | 500 | Lightning |  | 1 | 2.56 | 5 | 166.2 | 0.08
| Customer Count | 1012 |  |  |  | 510 | Wind - Not Trees |  | 1 | 2.56 | 49 | 4262.4 | 1.99
| Circuit 5 Year Average (SAIDI |  |  | 203.2439 |  | 600 | Small animal/bird |  | 3 | 7.69 | 52 | 3216.6 | 1.5
| Reporting Year (SAIDI |  | 117.4452 |  |  | 630 | Squirrel |  | 5 | 12.82 | 11 | 559.2 | 0.26
| Circuit 5 Year Average (SAIFI |  |  | 2.0268 |  | 690 | Animal |  | 3 | 7.69 | 3 | 252.6 | 0.12
| Reporting Year (SAIFI |  | 2.0515 |  |  | 700 | Member/Public Caused |  | 1 | 2.56 | 2 | 79.8 | 0.04
| Total Circuit Length: | 93.3 |  |  |  | 999 | Cause unknown |  | 9 | 23.08 | 1132 | 118848 | 55.6
| Date of Last Circuit Trim: | 2019
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | 110 | JPEC - Planned |  | 3 | 16.67 | 6 | 388.8 | 6.9
| Substation Name | FREEMONT |  |  |  | 300 | Equipment Failure |  | 1 | 5.56 | 6 | 387 | 6.86
| Feeder Name: | McNeil Lane |  |  |  | 435 | Tree Failure from outside of ROW |  | 1 | 5.56 | 4 | 649.8 | 11.52
| Feeder Number: | 224 |  |  |  | 440 | Trees with ice/snow |  | 1 | 5.56 | 9 | 414.6 | 7.35
[6 empty] | 500 | Lightning |  | 1 | 5.56 | 9 | 773.4 | 13.72
| Feeder Location | 51224-McNeil Lane |  |  |  | 600 | Small animal/bird |  | 1 | 5.56 | 1 | 124.2 | 2.2
| Customer Count | 334 |  |  |  | 630 | Squirrel |  | 1 | 5.56 | 2 | 208.8 | 3.7
| Circuit 5 Year Average (SAIDI |  |  | 521.8251 |  | 690 | Animal |  | 2 | 11.11 | 3 | 131.4 | 2.33
| Reporting Year (SAIDI |  | 7.4564 |  |  | 998 | Unknown-will determine later |  | 1 | 5.56 | 2 | 70.2 | 1.25
| Circuit 5 Year Average (SAIFI |  |  | 1.7545 |  | 999 | Cause unknown |  | 6 | 33.33 | 22 | 2490 | 44.16
| Reporting Year (SAIFI |  | 0.0659
| Total Circuit Length: | 26.1
| Date of Last Circuit Trim: | 2019
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | 110 | JPEC - Planned |  | 2 | 16.67 | 23 | 1284.6 | 23.54
| Substation Name | FREEMONT |  |  |  | 420 | ROW |  | 1 | 8.33 | 19 | 1748.4 | 32.04
| Feeder Name: | Freemont |  |  |  | 510 | Wind - Not Trees |  | 1 | 8.33 | 2 | 1395.6 | 25.58
| Feeder Number: | 244 |  |  |  | 690 | Animal |  | 5 | 41.67 | 6 | 303.6 | 5.56
[6 empty] | 710 | Motor Vehicle |  | 2 | 16.67 | 25 | 665.4 | 12.19
| Feeder Location | 51244-Freemont |  |  |  | 999 | Cause unknown |  | 1 | 8.33 | 1 | 58.8 | 1.08
| Customer Count | 334
| Circuit 5 Year Average (SAIDI |  |  | 105.1092
| Reporting Year (SAIDI |  | 5.2328
| Circuit 5 Year Average (SAIFI |  |  | 0.5039
| Reporting Year (SAIFI |  | 0.0748
| Total Circuit Length: | 12.9
| Date of Last Circuit Trim: | 2019
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | 300 | Equipment Failure |  | 1 | 20 | 1 | 90.6 | 1.04
| Substation Name | FREEMONT |  |  |  | 420 | ROW |  | 1 | 20 | 26 | 7305 | 83.69
| Feeder Name: | Bonds Rd |  |  |  | 500 | Lightning |  | 1 | 20 | 2 | 156 | 1.79
| Feeder Number: | 254 |  |  |  | 710 | Motor Vehicle |  | 1 | 20 | 4 | 908.4 | 10.41
[6 empty] | 999 | Cause unknown |  | 1 | 20 | 3 | 268.2 | 3.07
| Feeder Location | 51254-Bonds Rd
| Customer Count | 127
| Circuit 5 Year Average (SAIDI |  |  | 1060.6064
| Reporting Year (SAIDI |  | 57.4755
| Circuit 5 Year Average (SAIFI |  |  | 1.9024
| Reporting Year (SAIFI |  | 0.2046
| Total Circuit Length: | 11.5
| Date of Last Circuit Trim: | 2019
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | 100 | Contractor - Planned |  | 1 | 4.55 | 1 | 94.2 | 0.43
| Substation Name | GRAND RIVERS |  |  |  | 110 | JPEC - Planned |  | 6 | 27.27 | 6 | 735 | 3.33
| Feeder Name: | Iuka |  |  |  | 300 | Equipment Failure |  | 1 | 4.55 | 49 | 5361.6 | 24.28
| Feeder Number: | 214 |  |  |  | 420 | ROW |  | 2 | 9.09 | 52 | 2654.4 | 12.02
[6 empty] | 430 | Tree failure from overhang or dead tree without ice/snow |  | 1 | 4.55 | 1 | 130.8 | 0.59
| Feeder Location | 76214-Iuka |  |  |  | 440 | Trees with ice/snow |  | 1 | 4.55 | 22 | 1930.8 | 8.74
| Customer Count | 301 |  |  |  | 500 | Lightning |  | 1 | 4.55 | 1 | 72 | 0.33
| Circuit 5 Year Average (SAIDI |  |  | 580.9834 |  | 510 | Wind - Not Trees |  | 2 | 9.09 | 31 | 10214.4 | 46.26
| Reporting Year (SAIDI |  | 33.9617 |  |  | 600 | Small animal/bird |  | 2 | 9.09 | 2 | 136.8 | 0.62
| Circuit 5 Year Average (SAIFI |  |  | 2.7949 |  | 690 | Animal |  | 1 | 4.55 | 1 | 70.8 | 0.32
| Reporting Year (SAIFI |  | 0.1729 |  |  | 700 | Member/Public Caused |  | 1 | 4.55 | 2 | 148.2 | 0.67
| Total Circuit Length: | 36.1 |  |  |  | 800 | Other |  | 1 | 4.55 | 1 | 114.6 | 0.52
[6 empty] | 999 | Cause unknown |  | 2 | 9.09 | 6 | 417.6 | 1.89
| Date of Last Circuit Trim: | 2016
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | 110 | JPEC - Planned |  | 11 | 44 | 17 | 2572.2 | 18.6
| Substation Name | GRAND RIVERS |  |  |  | 300 | Equipment Failure |  | 2 | 8 | 3 | 299.4 | 2.16
| Feeder Name: | Smithland |  |  |  | 420 | ROW |  | 1 | 4 | 4 | 291.6 | 2.11
| Feeder Number: | 224 |  |  |  | 430 | Tree failure from overhang or dead tree without ice/snow |  | 2 | 8 | 35 | 4780.8 | 34.57
[6 empty] | 500 | Lightning |  | 4 | 16 | 11 | 1795.8 | 12.99
| Feeder Location | 76224-Smithland |  |  |  | 540 | Storm |  | 1 | 4 | 6 | 796.2 | 5.76
| Customer Count | 312 |  |  |  | 690 | Animal |  | 1 | 4 | 1 | 72 | 0.52
| Circuit 5 Year Average (SAIDI |  |  | 4781.2055 |  | 700 | Member/Public Caused |  | 1 | 4 | 1 | 13.8 | 0.1
| Reporting Year (SAIDI |  | 15.3128 |  |  | 710 | Motor Vehicle |  | 1 | 4 | 79 | 3025.8 | 21.88
| Circuit 5 Year Average (SAIFI |  |  | 2.5882 |  | 999 | Cause unknown |  | 1 | 4 | 3 | 181.8 | 1.31
| Reporting Year (SAIFI |  | 0.2531
| Total Circuit Length: | 19.3
| Date of Last Circuit Trim: | 2016
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | 100 | Contractor - Planned |  | 2 | 8 | 2 | 273 | 2.27
| Substation Name | GRAND RIVERS |  |  |  | 110 | JPEC - Planned |  | 7 | 28 | 12 | 2860.2 | 23.76
| Feeder Name: | Pelican GR #1 |  |  |  | 300 | Equipment Failure |  | 1 | 4 | 1 | 127.2 | 1.06
| Feeder Number: | 244 |  |  |  | 400 | Decay/age of material/equipment |  | 1 | 4 | 3 | 206.4 | 1.71
[6 empty] | 420 | ROW |  | 1 | 4 | 2 | 144.6 | 1.2
| Feeder Location | 76244-Pelican GR #1 |  |  |  | 435 | Tree Failure from outside of ROW |  | 1 | 4 | 53 | 5829 | 48.42
| Customer Count | 379 |  |  |  | 500 | Lightning |  | 3 | 12 | 12 | 759 | 6.3
| Circuit 5 Year Average (SAIDI |  |  | 349.3789 |  | 630 | Squirrel |  | 1 | 4 | 3 | 139.8 | 1.16
| Reporting Year (SAIDI |  | 15.3811 |  |  | 700 | Member/Public Caused |  | 1 | 4 | 1 | 51.6 | 0.43
| Circuit 5 Year Average (SAIFI |  |  | 2.2856 |  | 810 | Load |  | 1 | 4 | 2 | 104.4 | 0.87
| Reporting Year (SAIFI |  | 0.1398 |  |  | 998 | Unknown-will determine later |  | 1 | 4 | 1 | 54 | 0.45
| Total Circuit Length: | 24.3 |  |  |  | 999 | Cause unknown |  | 5 | 20 | 36 | 1489.8 | 12.37
| Date of Last Circuit Trim: | 2016
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | 100 | Contractor - Planned |  | 2 | 6.25 | 6 | 781.8 | 0.59
| Substation Name | GRAND RIVERS |  |  |  | 110 | JPEC - Planned |  | 14 | 43.75 | 689 | 50724.6 | 38.43
| Feeder Name: | Averitt GR #2 |  |  |  | 300 | Equipment Failure |  | 2 | 6.25 | 6 | 455.4 | 0.35
| Feeder Number: | 254 |  |  |  | 420 | ROW |  | 3 | 9.38 | 664 | 71268 | 54
[6 empty] | 600 | Small animal/bird |  | 1 | 3.12 | 2 | 104.4 | 0.08
| Feeder Location | 76254-Averitt GR #2 |  |  |  | 690 | Animal |  | 1 | 3.12 | 3 | 346.8 | 0.26
| Customer Count | 673 |  |  |  | 700 | Member/Public Caused |  | 1 | 3.12 | 11 | 2834.4 | 2.15
| Circuit 5 Year Average (SAIDI |  |  | 554.1829 |  | 710 | Motor Vehicle |  | 3 | 9.38 | 14 | 1350 | 1.02
| Reporting Year (SAIDI |  | 105.9244 |  |  | 999 | Cause unknown |  | 5 | 15.62 | 62 | 4116 | 3.12
| Circuit 5 Year Average (SAIFI |  |  | 3.7847
| Reporting Year (SAIFI |  | 1.024
| Total Circuit Length: | 44
| Date of Last Circuit Trim: | 2016
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | 100 | Contractor - Planned |  | 1 | 8.33 | 4 | 1006.8 | 17.2
| Substation Name | HIGHPOINT |  |  |  | 300 | Equipment Failure |  | 3 | 25 | 3 | 332.4 | 5.68
| Feeder Name: | High Point |  |  |  | 435 | Tree Failure from outside of ROW |  | 1 | 8.33 | 26 | 3550.8 | 60.66
| Feeder Number: | 214 |  |  |  | 500 | Lightning |  | 2 | 16.67 | 28 | 700.8 | 11.97
[6 empty] | 630 | Squirrel |  | 1 | 8.33 | 1 | 76.2 | 1.3
| Feeder Location | 29214-High Point |  |  |  | 690 | Animal |  | 3 | 25 | 5 | 126.6 | 2.16
| Customer Count | 192 |  |  |  | 999 | Cause unknown |  | 1 | 8.33 | 1 | 60 | 1.03
| Circuit 5 Year Average (SAIDI |  |  | 199.759
| Reporting Year (SAIDI |  | 18.5088
| Circuit 5 Year Average (SAIFI |  |  | 1.0446
| Reporting Year (SAIFI |  | 0.146
| Total Circuit Length: | 21.4
| Date of Last Circuit Trim: | 2015
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | 110 | JPEC - Planned |  | 3 | 16.67 | 9 | 1308 | 2.4
| Substation Name | HIGHPOINT |  |  |  | 300 | Equipment Failure |  | 1 | 5.56 | 1 | 65.4 | 0.12
| Feeder Name: | Carneal Rd |  |  |  | 420 | ROW |  | 3 | 16.67 | 21 | 1730.4 | 3.18
| Feeder Number: | 224 |  |  |  | 430 | Tree failure from overhang or dead tree without ice/snow |  | 1 | 5.56 | 11 | 1200 | 2.2
[6 empty] | 435 | Tree Failure from outside of ROW |  | 1 | 5.56 | 4 | 168.6 | 0.31
| Feeder Location | 29224-Carneal Rd |  |  |  | 500 | Lightning |  | 2 | 11.11 | 4 | 459.6 | 0.84
| Customer Count | 243 |  |  |  | 610 | Large animal |  | 1 | 5.56 | 1 | 92.4 | 0.17
| Circuit 5 Year Average (SAIDI |  |  | 968.9317 |  | 630 | Squirrel |  | 1 | 5.56 | 1 | 45.6 | 0.08
| Reporting Year (SAIDI |  | 155.4463 |  |  | 690 | Animal |  | 1 | 5.56 | 8 | 385.8 | 0.71
| Circuit 5 Year Average (SAIFI |  |  | 2.5813 |  | 700 | Member/Public Caused |  | 2 | 11.11 | 194 | 11142 | 20.45
| Reporting Year (SAIFI |  | 1.0162 |  |  | 790 | Public other |  | 1 | 5.56 | 247 | 37782.6 | 69.36
| Total Circuit Length: | 32.5 |  |  |  | 999 | Cause unknown |  | 1 | 5.56 | 1 | 93.6 | 0.17
| Date of Last Circuit Trim: | 2015
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | None | None |  | 0 | 0 | 0 | 0 | 0
| Substation Name | HIGHPOINT
| Feeder Name: | REC_00000340
| Feeder Number: | 3
| Feeder Location | 00340-REC_000003
| Customer Count | 0
| Circuit 5 Year Average (SAIDI |  |  | 0
| Reporting Year (SAIDI |  | 0
| Circuit 5 Year Average (SAIFI |  |  | 0
| Reporting Year (SAIFI |  | 0
Total Circuit Length:
Date of Last Circuit Trim:
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | 100 | Contractor - Planned |  | 2 | 9.09 | 3 | 252.6 | 1.86
| Substation Name | HUSBANDS ROAD |  |  |  | 110 | JPEC - Planned |  | 3 | 13.64 | 8 | 222 | 1.63
| Feeder Name: | Husbands Rd |  |  |  | 300 | Equipment Failure |  | 5 | 22.73 | 35 | 918 | 6.75
| Feeder Number: | 224 |  |  |  | 310 | Installation fault |  | 1 | 4.55 | 2 | 135 | 0.99
[6 empty] | 320 | Clearance |  | 1 | 4.55 | 60 | 6358.8 | 46.79
| Feeder Location | 40224-Husbands Rd |  |  |  | 420 | ROW |  | 1 | 4.55 | 9 | 1483.8 | 10.92
| Customer Count | 778 |  |  |  | 600 | Small animal/bird |  | 3 | 13.64 | 45 | 2603.4 | 19.16
| Circuit 5 Year Average (SAIDI |  |  | 319.4335 |  | 690 | Animal |  | 2 | 9.09 | 2 | 271.8 | 2
| Reporting Year (SAIDI |  | 8.1738 |  |  | 700 | Member/Public Caused |  | 1 | 4.55 | 6 | 1106.4 | 8.14
| Circuit 5 Year Average (SAIFI |  |  | 1.0579 |  | 999 | Cause unknown |  | 3 | 13.64 | 4 | 238.2 | 1.75
| Reporting Year (SAIFI |  | 0.0771
| Total Circuit Length: | 20
| Date of Last Circuit Trim: | 2018
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | 100 | Contractor - Planned |  | 1 | 5 | 2 | 307.8 | 1.11
| Substation Name | HUSBANDS ROAD |  |  |  | 110 | JPEC - Planned |  | 3 | 15 | 9 | 300.6 | 1.08
| Feeder Name: | Lydon Rd |  |  |  | 420 | ROW |  | 4 | 20 | 459 | 21008.4 | 75.76
| Feeder Number: | 234 |  |  |  | 510 | Wind - Not Trees |  | 1 | 5 | 2 | 612 | 2.21
[6 empty] | 600 | Small animal/bird |  | 3 | 15 | 15 | 536.4 | 1.93
| Feeder Location | 40234-Lydon Rd |  |  |  | 630 | Squirrel |  | 1 | 5 | 1 | 43.8 | 0.16
| Customer Count | 457 |  |  |  | 690 | Animal |  | 4 | 20 | 34 | 2885.4 | 10.4
| Circuit 5 Year Average (SAIDI |  |  | 149.6416 |  | 710 | Motor Vehicle |  | 1 | 5 | 2 | 1729.8 | 6.24
| Reporting Year (SAIDI |  | 45.9471 |  |  | 999 | Cause unknown |  | 2 | 10 | 7 | 307.8 | 1.11
| Circuit 5 Year Average (SAIFI |  |  | 1.108
| Reporting Year (SAIFI |  | 1.0039
| Total Circuit Length: | 32.1
| Date of Last Circuit Trim: | 2018
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | 110 | JPEC - Planned |  | 4 | 40 | 4 | 351 | 32.13
| Substation Name | HUSBANDS ROAD |  |  |  | 300 | Equipment Failure |  | 1 | 10 | 1 | 63 | 5.77
| Feeder Name: | Clarkline Rd |  |  |  | 420 | ROW |  | 1 | 10 | 4 | 226.2 | 20.7
| Feeder Number: | 244 |  |  |  | 435 | Tree Failure from outside of ROW |  | 1 | 10 | 4 | 234 | 21.42
[6 empty] | 500 | Lightning |  | 1 | 10 | 1 | 37.2 | 3.4
| Feeder Location | 40244-Clarkline Rd |  |  |  | 690 | Animal |  | 1 | 10 | 2 | 96 | 8.79
| Customer Count | 359 |  |  |  | 999 | Cause unknown |  | 1 | 10 | 2 | 85.2 | 7.8
| Circuit 5 Year Average (SAIDI |  |  | 84.2799
| Reporting Year (SAIDI |  | 0.9788
| Circuit 5 Year Average (SAIFI |  |  | 0.3864
| Reporting Year (SAIFI |  | 0.0111
| Total Circuit Length: | 14.4
| Date of Last Circuit Trim: | 2018
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | 300 | Equipment Failure |  | 1 | 7.69 | 1 | 78.6 | 0.17
| Substation Name | JOY |  |  |  | 420 | ROW |  | 6 | 46.15 | 168 | 23793 | 51.21
| Feeder Name: | Hampton South |  |  |  | 500 | Lightning |  | 3 | 23.08 | 151 | 22251.6 | 47.89
| Feeder Number: | 214 |  |  |  | 800 | Other |  | 1 | 7.69 | 2 | 275.4 | 0.59
[6 empty] | 810 | Load |  | 2 | 15.38 | 2 | 67.2 | 0.14
| Feeder Location | 05214-Hampton Sout
| Customer Count | 183
| Circuit 5 Year Average (SAIDI |  |  | 586.7234
| Reporting Year (SAIDI |  | 129.851
| Circuit 5 Year Average (SAIFI |  |  | 2.111
| Reporting Year (SAIFI |  | 0.9169
| Total Circuit Length: | 49.1
| Date of Last Circuit Trim: | 2016
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | 730 | Fire |  | 1 | 100 | 2 | 258.6 | 100
| Substation Name | JOY
| Feeder Name: | Carrsville
| Feeder Number: | 244
| Feeder Location | 05244-Carrsville
| Customer Count | 71
| Circuit 5 Year Average (SAIDI |  |  | 254.4025
| Reporting Year (SAIDI |  | 3.6553
| Circuit 5 Year Average (SAIFI |  |  | 1.0409
| Reporting Year (SAIFI |  | 0.0283
| Total Circuit Length: | 10.9
| Date of Last Circuit Trim: | 2016
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | 300 | Equipment Failure |  | 3 | 13.64 | 5 | 614.4 | 0.99
| Substation Name | JOY |  |  |  | 420 | ROW |  | 6 | 27.27 | 328 | 28069.2 | 45.05
| Feeder Name: | Lola |  |  |  | 430 | Tree failure from overhang or dead tree without ice/snow |  | 2 | 9.09 | 38 | 4876.8 | 7.83
| Feeder Number: | 254 |  |  |  | 500 | Lightning |  | 3 | 13.64 | 85 | 23320.2 | 37.43
[6 empty] | 510 | Wind - Not Trees |  | 1 | 4.55 | 1 | 423 | 0.68
| Feeder Location | 05254-Lola |  |  |  | 520 | Ice - Not Trees |  | 1 | 4.55 | 6 | 1394.4 | 2.24
| Customer Count | 286 |  |  |  | 999 | Cause unknown |  | 6 | 27.27 | 17 | 3610.2 | 5.79
| Circuit 5 Year Average (SAIDI |  |  | 412.8792
| Reporting Year (SAIDI |  | 98.0305
| Circuit 5 Year Average (SAIFI |  |  | 1.9111
| Reporting Year (SAIFI |  | 1.1455
| Total Circuit Length: | 45.3
| Date of Last Circuit Trim: | 2016
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | 110 | JPEC - Planned |  | 9 | 36 | 12 | 1835.4 | 3.09
| Substation Name | KANSAS |  |  |  | 300 | Equipment Failure |  | 2 | 8 | 3 | 495 | 0.83
| Feeder Name: | Lowes |  |  |  | 420 | ROW |  | 2 | 8 | 462 | 15520.2 | 26.17
| Feeder Number: | 214 |  |  |  | 500 | Lightning |  | 2 | 8 | 48 | 3369.6 | 5.68
[6 empty] | 600 | Small animal/bird |  | 2 | 8 | 4 | 219 | 0.37
| Feeder Location | 61214-Lowes |  |  |  | 630 | Squirrel |  | 1 | 4 | 3 | 212.4 | 0.36
| Customer Count | 455 |  |  |  | 690 | Animal |  | 2 | 8 | 2 | 147.6 | 0.25
| Circuit 5 Year Average (SAIDI |  |  | 424.8749 |  | 700 | Member/Public Caused |  | 1 | 4 | 43 | 1290 | 2.17
| Reporting Year (SAIDI |  | 78.9854 |  |  | 710 | Motor Vehicle |  | 1 | 4 | 1 | 183 | 0.31
| Circuit 5 Year Average (SAIFI |  |  | 1.5792 |  | 998 | Unknown-will determine later |  | 1 | 4 | 453 | 35930.4 | 60.58
| Reporting Year (SAIFI |  | 1.0156 |  |  | 999 | Cause unknown |  | 2 | 8 | 2 | 108 | 0.18
| Total Circuit Length: | 40.1
| Date of Last Circuit Trim: | 2016
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | 100 | Contractor - Planned |  | 1 | 6.25 | 1 | 46.2 | 0.13
| Substation Name | KANSAS |  |  |  | 110 | JPEC - Planned |  | 3 | 18.75 | 4 | 571.2 | 1.58
| Feeder Name: | Folsomdale |  |  |  | 300 | Equipment Failure |  | 4 | 25 | 7 | 486 | 1.34
| Feeder Number: | 224 |  |  |  | 420 | ROW |  | 2 | 12.5 | 47 | 3674.4 | 10.16
[6 empty] | 430 | Tree failure from overhang or dead tree without ice/snow |  | 1 | 6.25 | 204 | 14497.8 | 40.08
| Feeder Location | 61224-Folsomdale |  |  |  | 500 | Lightning |  | 1 | 6.25 | 6 | 627 | 1.73
| Customer Count | 210 |  |  |  | 690 | Animal |  | 2 | 12.5 | 3 | 218.4 | 0.6
| Circuit 5 Year Average (SAIDI |  |  | 139.8778 |  | 998 | Unknown-will determine later |  | 1 | 6.25 | 205 | 15839.4 | 43.79
| Reporting Year (SAIDI |  | 75.4953 |  |  | 999 | Cause unknown |  | 1 | 6.25 | 5 | 210.6 | 0.58
| Circuit 5 Year Average (SAIFI |  |  | 1.1448
| Reporting Year (SAIFI |  | 0.9771
| Total Circuit Length: | 29.1
| Date of Last Circuit Trim: | 2016
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | 100 | Contractor - Planned |  | 2 | 8 | 3 | 524.4 | 0.44
| Substation Name | KANSAS |  |  |  | 110 | JPEC - Planned |  | 8 | 32 | 11 | 1372.8 | 1.16
| Feeder Name: | Melber |  |  |  | 300 | Equipment Failure |  | 2 | 8 | 3 | 411.6 | 0.35
| Feeder Number: | 234 |  |  |  | 420 | ROW |  | 4 | 16 | 82 | 8797.8 | 7.46
[6 empty] | 435 | Tree Failure from outside of ROW |  | 2 | 8 | 528 | 63283.2 | 53.66
| Feeder Location | 61234-Melber |  |  |  | 500 | Lightning |  | 1 | 4 | 1 | 237.6 | 0.2
| Customer Count | 598 |  |  |  | 630 | Squirrel |  | 2 | 8 | 2 | 165.6 | 0.14
| Circuit 5 Year Average (SAIDI |  |  | 269.9408 |  | 998 | Unknown-will determine later |  | 1 | 4 | 544 | 41199 | 34.93
| Reporting Year (SAIDI |  | 105.7825 |  |  | 999 | Cause unknown |  | 3 | 12 | 39 | 1945.8 | 1.65
| Circuit 5 Year Average (SAIFI |  |  | 1.1203
| Reporting Year (SAIFI |  | 0.9093
| Total Circuit Length: | 53.1
| Date of Last Circuit Trim: | 2016
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | 100 | Contractor - Planned |  | 2 | 7.41 | 3 | 164.4 | 0.09
| Substation Name | KANSAS |  |  |  | 110 | JPEC - Planned |  | 7 | 25.93 | 10 | 826.2 | 0.47
| Feeder Name: | Pottsville |  |  |  | 420 | ROW |  | 7 | 25.93 | 112 | 15727.2 | 8.97
| Feeder Number: | 244 |  |  |  | 435 | Tree Failure from outside of ROW |  | 1 | 3.7 | 359 | 125368.8 | 71.47
[6 empty] | 500 | Lightning |  | 1 | 3.7 | 1 | 25.8 | 0.01
| Feeder Location | 61244-Pottsville |  |  |  | 630 | Squirrel |  | 1 | 3.7 | 1 | 102.6 | 0.06
| Customer Count | 363 |  |  |  | 690 | Animal |  | 1 | 3.7 | 1 | 52.2 | 0.03
| Circuit 5 Year Average (SAIDI |  |  | 558.3182 |  | 700 | Member/Public Caused |  | 1 | 3.7 | 2 | 88.8 | 0.05
| Reporting Year (SAIDI |  | 344.922 |  |  | 800 | Other |  | 2 | 7.41 | 2 | 177.6 | 0.1
| Circuit 5 Year Average (SAIFI |  |  | 2.9532 |  | 998 | Unknown-will determine later |  | 1 | 3.7 | 359 | 31490.4 | 17.95
| Reporting Year (SAIFI |  | 0.9877 |  |  | 999 | Cause unknown |  | 3 | 11.11 | 21 | 1402.2 | 0.8
| Total Circuit Length: | 32.1
| Date of Last Circuit Trim: | 2016
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | 110 | JPEC - Planned |  | 2 | 9.09 | 3 | 215.4 | 0.31
| Substation Name | KEVIL |  |  |  | 300 | Equipment Failure |  | 4 | 18.18 | 29 | 3306 | 4.72
| Feeder Name: | Hobbs Rd |  |  |  | 420 | ROW |  | 3 | 13.64 | 61 | 8145 | 11.63
| Feeder Number: | 214 |  |  |  | 430 | Tree failure from overhang or dead tree without ice/snow |  | 2 | 9.09 | 21 | 2459.4 | 3.51
[6 empty] | 500 | Lightning |  | 1 | 4.55 | 2 | 746.4 | 1.07
| Feeder Location | 28214-Hobbs Rd |  |  |  | 510 | Wind - Not Trees |  | 1 | 4.55 | 4 | 803.4 | 1.15
| Customer Count | 545 |  |  |  | 600 | Small animal/bird |  | 1 | 4.55 | 18 | 1756.2 | 2.51
| Circuit 5 Year Average (SAIDI |  |  | 518.8222 |  | 630 | Squirrel |  | 2 | 9.09 | 2 | 54 | 0.08
| Reporting Year (SAIDI |  | 49.9136 |  |  | 690 | Animal |  | 3 | 13.64 | 557 | 27217.2 | 38.86
| Circuit 5 Year Average (SAIFI |  |  | 2.8198 |  | 700 | Member/Public Caused |  | 1 | 4.55 | 125 | 25083.6 | 35.82
| Reporting Year (SAIFI |  | 1.0215 |  |  | 999 | Cause unknown |  | 2 | 9.09 | 4 | 246 | 0.35
| Total Circuit Length: | ?
| Date of Last Circuit Trim: | 2016
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | 100 | Contractor - Planned |  | 5 | 10.42 | 18 | 1601.4 | 2.9
| Substation Name | KEVIL |  |  |  | 110 | JPEC - Planned |  | 26 | 54.17 | 207 | 31128 | 56.33
| Feeder Name: | Woodville Rd |  |  |  | 190 | Other planned |  | 1 | 2.08 | 9 | 1599 | 2.89
| Feeder Number: | 224 |  |  |  | 300 | Equipment Failure |  | 3 | 6.25 | 47 | 5717.4 | 10.35
[6 empty] | 420 | ROW |  | 7 | 14.58 | 108 | 13780.2 | 24.94
| Feeder Location | 28224-Woodville Rd |  |  |  | 500 | Lightning |  | 2 | 4.17 | 9 | 799.8 | 1.45
| Customer Count | 501 |  |  |  | 690 | Animal |  | 3 | 6.25 | 9 | 599.4 | 1.08
| Circuit 5 Year Average (SAIDI |  |  | 272.2521 |  | 999 | Cause unknown |  | 1 | 2.08 | 1 | 34.2 | 0.06
| Reporting Year (SAIDI |  | 62.1799
| Circuit 5 Year Average (SAIFI |  |  | 1.7147
| Reporting Year (SAIFI |  | 0.4135
| Total Circuit Length: | 38.1
| Date of Last Circuit Trim: | 2016
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | 100 | Contractor - Planned |  | 1 | 10 | 4 | 366 | 1.09
| Substation Name | KEVIL |  |  |  | 110 | JPEC - Planned |  | 2 | 20 | 5 | 480.6 | 1.43
| Feeder Name: | Kelley Rd |  |  |  | 300 | Equipment Failure |  | 2 | 20 | 3 | 144.6 | 0.43
| Feeder Number: | 234 |  |  |  | 420 | ROW |  | 3 | 30 | 55 | 20115.6 | 59.67
[6 empty] | 800 | Other |  | 1 | 10 | 417 | 12294.6 | 36.47
| Feeder Location | 28234-Kelley Rd |  |  |  | 999 | Cause unknown |  | 1 | 10 | 2 | 307.8 | 0.91
| Customer Count | 427
| Circuit 5 Year Average (SAIDI |  |  | 246.5611
| Reporting Year (SAIDI |  | 47.1518
| Circuit 5 Year Average (SAIFI |  |  | 1.562
| Reporting Year (SAIFI |  | 0.9775
| Total Circuit Length: | 22.2
| Date of Last Circuit Trim: | 2016
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | 100 | Contractor - Planned |  | 1 | 4.55 | 1 | 115.8 | 0.13
| Substation Name | KREBS STATION RD |  |  |  | 110 | JPEC - Planned |  | 1 | 4.55 | 4 | 127.2 | 0.14
| Feeder Name: | Browns Plating |  |  |  | 300 | Equipment Failure |  | 3 | 13.64 | 533 | 38587.2 | 42.18
| Feeder Number: | 214 |  |  |  | 420 | ROW |  | 3 | 13.64 | 106 | 40377 | 44.13
[6 empty] | 430 | Tree failure from overhang or dead tree without ice/snow |  | 2 | 9.09 | 11 | 675.6 | 0.74
| Feeder Location | 50214-Browns Platin |  |  |  | 435 | Tree Failure from outside of ROW |  | 1 | 4.55 | 58 | 6398.4 | 6.99
| Customer Count | 527 |  |  |  | 510 | Wind - Not Trees |  | 1 | 4.55 | 3 | 799.2 | 0.87
| Circuit 5 Year Average (SAIDI |  |  | 343.9452 |  | 600 | Small animal/bird |  | 2 | 9.09 | 3 | 139.8 | 0.15
| Reporting Year (SAIDI |  | 76.6503 |  |  | 630 | Squirrel |  | 3 | 13.64 | 54 | 3643.8 | 3.98
| Circuit 5 Year Average (SAIFI |  |  | 1.5392 |  | 690 | Animal |  | 3 | 13.64 | 6 | 274.8 | 0.3
| Reporting Year (SAIFI |  | 1.0118 |  |  | 999 | Cause unknown |  | 2 | 9.09 | 5 | 353.4 | 0.39
| Total Circuit Length: | 18.9
| Date of Last Circuit Trim: | 2016
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | 100 | Contractor - Planned |  | 3 | 8.11 | 11 | 1171.8 | 0.57
| Substation Name | KREBS STATION RD |  |  |  | 110 | JPEC - Planned |  | 2 | 5.41 | 2 | 163.8 | 0.08
| Feeder Name: | Old US 45 |  |  |  | 300 | Equipment Failure |  | 4 | 10.81 | 18 | 1749.6 | 0.84
| Feeder Number: | 224 |  |  |  | 420 | ROW |  | 9 | 24.32 | 983 | 144858.6 | 69.95
[6 empty] | 435 | Tree Failure from outside of ROW |  | 3 | 8.11 | 25 | 4603.2 | 2.22
| Feeder Location | 50224-Old US 45 |  |  |  | 500 | Lightning |  | 1 | 2.7 | 1 | 72 | 0.03
| Customer Count | 908 |  |  |  | 630 | Squirrel |  | 6 | 16.22 | 31 | 2101.8 | 1.01
| Circuit 5 Year Average (SAIDI |  |  | 373.6892 |  | 690 | Animal |  | 3 | 8.11 | 3 | 120.6 | 0.06
| Reporting Year (SAIDI |  | 159.4975 |  |  | 700 | Member/Public Caused |  | 2 | 5.41 | 904 | 46902.6 | 22.65
| Circuit 5 Year Average (SAIFI |  |  | 1.7516 |  | 999 | Cause unknown |  | 4 | 10.81 | 54 | 5356.2 | 2.59
| Reporting Year (SAIFI |  | 1.0823
| Total Circuit Length: | 42.4
| Date of Last Circuit Trim: | 2016
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | 100 | Contractor - Planned |  | 4 | 11.76 | 7 | 1516.8 | 4.26
| Substation Name | KREBS STATION RD |  |  |  | 110 | JPEC - Planned |  | 9 | 26.47 | 11 | 1701.6 | 4.77
| Feeder Name: | Clinton Rd |  |  |  | 300 | Equipment Failure |  | 7 | 20.59 | 9 | 790.2 | 2.22
| Feeder Number: | 234 |  |  |  | 400 | Decay/age of material/equipment |  | 1 | 2.94 | 2 | 172.8 | 0.48
[6 empty] | 420 | ROW |  | 5 | 14.71 | 115 | 18882 | 52.98
| Feeder Location | 50234-Clinton Rd |  |  |  | 430 | Tree failure from overhang or dead tree without ice/snow |  | 1 | 2.94 | 1 | 41.4 | 0.12
| Customer Count | 521 |  |  |  | 435 | Tree Failure from outside of ROW |  | 1 | 2.94 | 20 | 1093.2 | 3.07
| Circuit 5 Year Average (SAIDI |  |  | 333.4765 |  | 500 | Lightning |  | 1 | 2.94 | 2 | 178.8 | 0.5
| Reporting Year (SAIDI |  | 36.2304 |  |  | 630 | Squirrel |  | 1 | 2.94 | 2 | 47.4 | 0.13
| Circuit 5 Year Average (SAIFI |  |  | 1.6129 |  | 690 | Animal |  | 2 | 5.88 | 8 | 493.2 | 1.38
| Reporting Year (SAIFI |  | 0.259 |  |  | 999 | Cause unknown |  | 2 | 5.88 | 135 | 10725.6 | 30.09
| Total Circuit Length: | 28.6
| Date of Last Circuit Trim: | 2016
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | None | None |  | 0 | 0 | 0 | 0 | 0
| Substation Name | KREBS STATION RD
| Feeder Name: | New Hope
| Feeder Number: | 244
| Feeder Location | 50244-New Hope
| Customer Count | 269
| Circuit 5 Year Average (SAIDI |  |  | 0
| Reporting Year (SAIDI |  | 0
| Circuit 5 Year Average (SAIFI |  |  | 0
| Reporting Year (SAIFI |  | 0
Total Circuit Length:
Date of Last Circuit Trim:
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | 110 | JPEC - Planned |  | 5 | 26.32 | 8 | 1130.4 | 2.88
| Substation Name | LaCENTER |  |  |  | 300 | Equipment Failure |  | 2 | 10.53 | 227 | 10455.6 | 26.67
| Feeder Name: | Damrons |  |  |  | 420 | ROW |  | 1 | 5.26 | 32 | 2574 | 6.56
| Feeder Number: | 214 |  |  |  | 500 | Lightning |  | 4 | 21.05 | 64 | 6672.6 | 17.02
[6 empty] | 600 | Small animal/bird |  | 1 | 5.26 | 21 | 1501.8 | 3.83
| Feeder Location | 26214-Damrons |  |  |  | 690 | Animal |  | 1 | 5.26 | 5 | 451.8 | 1.15
| Customer Count | 227 |  |  |  | 710 | Motor Vehicle |  | 1 | 5.26 | 33 | 2599.8 | 6.63
| Circuit 5 Year Average (SAIDI |  |  | 351.9184 |  | 800 | Other |  | 1 | 5.26 | 15 | 1149.6 | 2.93
| Reporting Year (SAIDI |  | 55.912 |  |  | 999 | Cause unknown |  | 3 | 15.79 | 226 | 12674.4 | 32.32
| Circuit 5 Year Average (SAIFI |  |  | 2.1236
| Reporting Year (SAIFI |  | 1.0014
| Total Circuit Length: | 39.7
| Date of Last Circuit Trim: | 2015
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | 100 | Contractor - Planned |  | 4 | 9.3 | 34 | 3947.4 | 2.79
| Substation Name | LaCENTER |  |  |  | 110 | JPEC - Planned |  | 6 | 13.95 | 11 | 1702.2 | 1.2
| Feeder Name: | Oscar |  |  |  | 300 | Equipment Failure |  | 4 | 9.3 | 478 | 23988.6 | 16.93
| Feeder Number: | 224 |  |  |  | 340 | Overload |  | 1 | 2.33 | 1 | 58.8 | 0.04
[6 empty] | 420 | ROW |  | 9 | 20.93 | 599 | 103563 | 73.09
| Feeder Location | 26224-Oscar |  |  |  | 430 | Tree failure from overhang or dead tree without ice/snow |  | 3 | 6.98 | 39 | 5328 | 3.76
| Customer Count | 363 |  |  |  | 500 | Lightning |  | 3 | 6.98 | 3 | 220.2 | 0.16
| Circuit 5 Year Average (SAIDI |  |  | 630.5569 |  | 540 | Storm |  | 1 | 2.33 | 5 | 1273.8 | 0.9
| Reporting Year (SAIDI |  | 285.4835 |  |  | 600 | Small animal/bird |  | 1 | 2.33 | 1 | 87 | 0.06
| Circuit 5 Year Average (SAIFI |  |  | 2.4782 |  | 630 | Squirrel |  | 2 | 4.65 | 2 | 226.2 | 0.16
| Reporting Year (SAIFI |  | 1.6512 |  |  | 690 | Animal |  | 2 | 4.65 | 3 | 187.8 | 0.13
| Total Circuit Length: | 51.4 |  |  |  | 810 | Load |  | 2 | 4.65 | 6 | 393 | 0.28
[6 empty] | 999 | Cause unknown |  | 5 | 11.63 | 10 | 719.4 | 0.51
| Date of Last Circuit Trim: | 2015
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | 110 | JPEC - Planned |  | 7 | 33.33 | 12 | 922.8 | 14.5
| Substation Name | LEDBETTER |  |  |  | 300 | Equipment Failure |  | 1 | 4.76 | 1 | 30.6 | 0.48
| Feeder Name: | US 60 East |  |  |  | 420 | ROW |  | 2 | 9.52 | 8 | 505.8 | 7.95
| Feeder Number: | 224 |  |  |  | 500 | Lightning |  | 4 | 19.05 | 27 | 3249.6 | 51.05
[6 empty] | 610 | Large animal |  | 1 | 4.76 | 10 | 436.2 | 6.85
| Feeder Location | 31224-US 60 East |  |  |  | 690 | Animal |  | 4 | 19.05 | 13 | 1121.4 | 17.62
| Customer Count | 317 |  |  |  | 999 | Cause unknown |  | 2 | 9.52 | 3 | 99.6 | 1.56
| Circuit 5 Year Average (SAIDI |  |  | 101.3457
| Reporting Year (SAIDI |  | 10.2561
| Circuit 5 Year Average (SAIFI |  |  | 0.3295
| Reporting Year (SAIFI |  | 0.0852
| Total Circuit Length: | 23.6
| Date of Last Circuit Trim: | 2016
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | None | None |  | 0 | 0 | 0 | 0 | 0
| Substation Name | LEDBETTER
| Feeder Name: | River Crossing
| Feeder Number: | 234
| Feeder Location | 31234-River Crossin
| Customer Count | 36
| Circuit 5 Year Average (SAIDI |  |  | 26.3975
| Reporting Year (SAIDI |  | 0
| Circuit 5 Year Average (SAIFI |  |  | 0.3972
| Reporting Year (SAIFI |  | 0
Total Circuit Length:
Date of Last Circuit Trim:
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | 100 | Contractor - Planned |  | 1 | 1.89 | 2 | 132 | 0.3
| Substation Name | LEDBETTER |  |  |  | 110 | JPEC - Planned |  | 14 | 26.42 | 49 | 5367 | 12.34
| Feeder Name: | Ledbetter |  |  |  | 300 | Equipment Failure |  | 2 | 3.77 | 30 | 8195.4 | 18.84
| Feeder Number: | 244 |  |  |  | 310 | Installation fault |  | 1 | 1.89 | 7 | 451.8 | 1.04
[6 empty] | 420 | ROW |  | 16 | 30.19 | 282 | 22124.4 | 50.86
| Feeder Location | 31244-Ledbetter |  |  |  | 430 | Tree failure from overhang or dead tree without ice/snow |  | 1 | 1.89 | 17 | 1410.6 | 3.24
| Customer Count | 1026 |  |  |  | 435 | Tree Failure from outside of ROW |  | 1 | 1.89 | 7 | 745.2 | 1.71
| Circuit 5 Year Average (SAIDI |  |  | 248.4194 |  | 500 | Lightning |  | 3 | 5.66 | 37 | 2888.4 | 6.64
| Reporting Year (SAIDI |  | 21.5632 |  |  | 600 | Small animal/bird |  | 3 | 5.66 | 9 | 739.8 | 1.7
| Circuit 5 Year Average (SAIFI |  |  | 1.2466 |  | 630 | Squirrel |  | 4 | 7.55 | 38 | 975.6 | 2.24
| Reporting Year (SAIFI |  | 0.2749 |  |  | 800 | Other |  | 1 | 1.89 | 2 | 90.6 | 0.21
| Total Circuit Length: | 61.6 |  |  |  | 999 | Cause unknown |  | 6 | 11.32 | 8 | 383.4 | 0.88
| Date of Last Circuit Trim: | 2016
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | 100 | Contractor - Planned |  | 2 | 6.9 | 3 | 138 | 0.74
| Substation Name | LITTLE UNION |  |  |  | 110 | JPEC - Planned |  | 12 | 41.38 | 22 | 2281.2 | 12.25
| Feeder Name: | Airport |  |  |  | 300 | Equipment Failure |  | 1 | 3.45 | 2 | 84.6 | 0.45
| Feeder Number: | 214 |  |  |  | 360 | Other equipment installation/design |  | 1 | 3.45 | 3 | 261.6 | 1.41
[6 empty] | 420 | ROW |  | 1 | 3.45 | 2 | 37.2 | 0.2
| Feeder Location | 39214-Airport |  |  |  | 435 | Tree Failure from outside of ROW |  | 2 | 6.9 | 32 | 4107.6 | 22.06
| Customer Count | 565 |  |  |  | 470 | Borrower crew cuts tree |  | 1 | 3.45 | 1 | 48 | 0.26
| Circuit 5 Year Average (SAIDI |  |  | 6.5889 |  | 500 | Lightning |  | 1 | 3.45 | 2 | 80.4 | 0.43
| Reporting Year (SAIDI |  | 14.2132 |  |  | 630 | Squirrel |  | 2 | 6.9 | 15 | 966.6 | 5.19
| Circuit 5 Year Average (SAIFI |  |  | 0.0785 |  | 700 | Member/Public Caused |  | 1 | 3.45 | 1 | 203.4 | 1.09
| Reporting Year (SAIFI |  | 0.1857 |  |  | 710 | Motor Vehicle |  | 2 | 6.9 | 105 | 8037 | 43.17
| Total Circuit Length: | 35.9 |  |  |  | 800 | Other |  | 1 | 3.45 | 1 | 73.2 | 0.39
[6 empty] | 999 | Cause unknown |  | 2 | 6.9 | 31 | 2299.2 | 12.35
| Date of Last Circuit Trim: | 2017
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | 000 | No Cause Selected |  | 2 | 4.55 | 506 | 107359.2 | 36.9
| Substation Name | LITTLE UNION |  |  |  | 100 | Contractor - Planned |  | 4 | 9.09 | 14 | 1492.2 | 0.51
| Feeder Name: | US 60 West |  |  |  | 110 | JPEC - Planned |  | 19 | 43.18 | 64 | 6558 | 2.25
| Feeder Number: | 224 |  |  |  | 190 | Other planned |  | 1 | 2.27 | 1 | 271.8 | 0.09
[6 empty] | 300 | Equipment Failure |  | 6 | 13.64 | 42 | 6855.6 | 2.36
| Feeder Location | 39224-US 60 West |  |  |  | 400 | Decay/age of material/equipment |  | 1 | 2.27 | 472 | 162125.4 | 55.72
| Customer Count | 471 |  |  |  | 420 | ROW |  | 1 | 2.27 | 2 | 73.8 | 0.03
| Circuit 5 Year Average (SAIDI |  |  | 390.7854 |  | 500 | Lightning |  | 3 | 6.82 | 3 | 265.2 | 0.09
| Reporting Year (SAIDI |  | 343.8725 |  |  | 630 | Squirrel |  | 2 | 4.55 | 56 | 2043 | 0.7
| Circuit 5 Year Average (SAIFI |  |  | 2.099 |  | 690 | Animal |  | 1 | 2.27 | 10 | 514.2 | 0.18
| Reporting Year (SAIFI |  | 1.0732 |  |  | 700 | Member/Public Caused |  | 1 | 2.27 | 1 | 33.6 | 0.01
| Total Circuit Length: | 15.9 |  |  |  | 710 | Motor Vehicle |  | 1 | 2.27 | 11 | 2697.6 | 0.93
[6 empty] | 800 | Other |  | 1 | 2.27 | 3 | 445.8 | 0.15
| Date of Last Circuit Trim: | 2017 |  |  |  | 999 | Cause unknown |  | 1 | 2.27 | 9 | 214.8 | 0.07
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | None | None |  | 0 | 0 | 0 | 0 | 0
| Substation Name | LITTLE UNION
| Feeder Name: | US 60 East Mall
| Feeder Number: | 234
| Feeder Location | 39234-US 60 East M
| Customer Count | 163
| Circuit 5 Year Average (SAIDI |  |  | 117.4213
| Reporting Year (SAIDI |  | 0
| Circuit 5 Year Average (SAIFI |  |  | 0.4842
| Reporting Year (SAIFI |  | 0
Total Circuit Length:
Date of Last Circuit Trim:
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | 100 | Contractor - Planned |  | 1 | 3.57 | 1 | 112.2 | 0.15
| Substation Name | LITTLE UNION |  |  |  | 110 | JPEC - Planned |  | 9 | 32.14 | 13 | 1851.6 | 2.47
| Feeder Name: | Roy Lee Rd |  |  |  | 300 | Equipment Failure |  | 2 | 7.14 | 254 | 26520 | 35.42
| Feeder Number: | 244 |  |  |  | 340 | Overload |  | 1 | 3.57 | 2 | 32.4 | 0.04
[6 empty] | 400 | Decay/age of material/equipment |  | 1 | 3.57 | 2 | 163.8 | 0.22
| Feeder Location | 39244-Roy Lee Rd |  |  |  | 420 | ROW |  | 5 | 17.86 | 476 | 22911.6 | 30.6
| Customer Count | 539 |  |  |  | 430 | Tree failure from overhang or dead tree without ice/snow |  | 1 | 3.57 | 10 | 634.2 | 0.85
| Circuit 5 Year Average (SAIDI |  |  | 804.5378 |  | 630 | Squirrel |  | 1 | 3.57 | 1 | 96.6 | 0.13
| Reporting Year (SAIDI |  | 49.2224 |  |  | 690 | Animal |  | 2 | 7.14 | 3 | 108.6 | 0.15
| Circuit 5 Year Average (SAIFI |  |  | 2.0825 |  | 700 | Member/Public Caused |  | 1 | 3.57 | 2 | 397.2 | 0.53
| Reporting Year (SAIFI |  | 1.7428 |  |  | 999 | Cause unknown |  | 4 | 14.29 | 939 | 22041.6 | 29.44
| Total Circuit Length: | 25.6
| Date of Last Circuit Trim: | 2017
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | 100 | Contractor - Planned |  | 3 | 37.5 | 4 | 880.8 | 6.88
| Substation Name | LOVELACEVILLE |  |  |  | 420 | ROW |  | 1 | 12.5 | 1 | 82.2 | 0.64
| Feeder Name: | Blandville |  |  |  | 510 | Wind - Not Trees |  | 1 | 12.5 | 47 | 7544.4 | 58.89
| Feeder Number: | 214 |  |  |  | 700 | Member/Public Caused |  | 1 | 12.5 | 1 | 81 | 0.63
[6 empty] | 810 | Load |  | 1 | 12.5 | 27 | 2813.4 | 21.96
| Feeder Location | 49214-Blandville |  |  |  | 999 | Cause unknown |  | 1 | 12.5 | 29 | 1409.4 | 11
| Customer Count | 132
| Circuit 5 Year Average (SAIDI |  |  | 594.4094
| Reporting Year (SAIDI |  | 57.0758
| Circuit 5 Year Average (SAIFI |  |  | 2.1531
| Reporting Year (SAIFI |  | 0.3556
| Total Circuit Length: | 20.3
| Date of Last Circuit Trim: | 2015
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | 100 | Contractor - Planned |  | 3 | 13.04 | 4 | 658.8 | 3.63
| Substation Name | LOVELACEVILLE |  |  |  | 110 | JPEC - Planned |  | 3 | 13.04 | 4 | 493.2 | 2.72
| Feeder Name: | Lovelaceville |  |  |  | 300 | Equipment Failure |  | 4 | 17.39 | 185 | 13795.8 | 76.01
| Feeder Number: | 224 |  |  |  | 420 | ROW |  | 1 | 4.35 | 1 | 214.2 | 1.18
[6 empty] | 430 | Tree failure from overhang or dead tree without ice/snow |  | 2 | 8.7 | 5 | 456 | 2.51
| Feeder Location | 49224-Lovelaceville |  |  |  | 630 | Squirrel |  | 1 | 4.35 | 1 | 50.4 | 0.28
| Customer Count | 527 |  |  |  | 700 | Member/Public Caused |  | 1 | 4.35 | 5 | 834 | 4.6
| Circuit 5 Year Average (SAIDI |  |  | 424.8364 |  | 710 | Motor Vehicle |  | 2 | 8.7 | 2 | 156 | 0.86
| Reporting Year (SAIDI |  | 26.1643 |  |  | 790 | Public other |  | 1 | 4.35 | 5 | 195 | 1.07
| Circuit 5 Year Average (SAIFI |  |  | 1.6329 |  | 800 | Other |  | 1 | 4.35 | 1 | 109.2 | 0.6
| Reporting Year (SAIFI |  | 0.3509 |  |  | 999 | Cause unknown |  | 4 | 17.39 | 16 | 1187.4 | 6.54
| Total Circuit Length: | 36.8
| Date of Last Circuit Trim: | 2015
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | 100 | Contractor - Planned |  | 1 | 6.67 | 1 | 72 | 0.89
| Substation Name | LOVELACEVILLE |  |  |  | 110 | JPEC - Planned |  | 2 | 13.33 | 2 | 302.4 | 3.72
| Feeder Name: | Cunningham |  |  |  | 300 | Equipment Failure |  | 3 | 20 | 7 | 724.2 | 8.91
| Feeder Number: | 234 |  |  |  | 410 | Corrosion/abrasion of material/equipment |  | 1 | 6.67 | 3 | 224.4 | 2.76
[6 empty] | 420 | ROW |  | 1 | 6.67 | 4 | 309 | 3.8
| Feeder Location | 49234-Cunningham |  |  |  | 490 | Maintenance other |  | 1 | 6.67 | 2 | 37.2 | 0.46
| Customer Count | 526 |  |  |  | 500 | Lightning |  | 1 | 6.67 | 2 | 76.2 | 0.94
| Circuit 5 Year Average (SAIDI |  |  | 745.9095 |  | 690 | Animal |  | 1 | 6.67 | 2 | 412.2 | 5.07
| Reporting Year (SAIDI |  | 11.002 |  |  | 700 | Member/Public Caused |  | 2 | 13.33 | 53 | 5788.8 | 71.2
| Circuit 5 Year Average (SAIFI |  |  | 2.0047 |  | 999 | Cause unknown |  | 2 | 13.33 | 2 | 183.6 | 2.26
| Reporting Year (SAIFI |  | 0.9921
| Total Circuit Length: | 45.5
| Date of Last Circuit Trim: | 2015
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | 420 | ROW |  | 1 | 100 | 261 | 11845.2 | 100
| Substation Name | MAXON
| Feeder Name: | Maxon Rd
| Feeder Number: | 214
| Feeder Location | 79214-Maxon Rd
| Customer Count | 261
| Circuit 5 Year Average (SAIDI |  |  | 194.353
| Reporting Year (SAIDI |  | 45.4547
| Circuit 5 Year Average (SAIFI |  |  | 1.1735
| Reporting Year (SAIFI |  | 1.0016
| Total Circuit Length: | 15.4
| Date of Last Circuit Trim: | 2017
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | 110 | JPEC - Planned |  | 2 | 50 | 37 | 750 | 15.94
| Substation Name | MAXON |  |  |  | 420 | ROW |  | 2 | 50 | 35 | 3955.2 | 84.06
| Feeder Name: | Express
| Feeder Number: | 224
| Feeder Location | 79224-Express
| Customer Count | 395
| Circuit 5 Year Average (SAIDI |  |  | 164.9948
| Reporting Year (SAIDI |  | 10.0161
| Circuit 5 Year Average (SAIFI |  |  | 1.2227
| Reporting Year (SAIFI |  | 0.0937
| Total Circuit Length: | 3.6
| Date of Last Circuit Trim: | 2017
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | 420 | ROW |  | 1 | 100 | 0 | 0 | 0
| Substation Name | MAXON
| Feeder Name: | Industrial Park
| Feeder Number: | 234
| Feeder Location | 79234-Industrial Park
| Customer Count | 4
| Circuit 5 Year Average (SAIDI |  |  | 16.3141
| Reporting Year (SAIDI |  | 0
| Circuit 5 Year Average (SAIFI |  |  | 0.2885
| Reporting Year (SAIFI |  | 0
Total Circuit Length:
Date of Last Circuit Trim:
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | 0 | BREC |  | 1 | 8.33 | 266 | 33369.6 | 31.26
| Substation Name | NEW YORK |  |  |  | 100 | Contractor - Planned |  | 2 | 16.67 | 3 | 222.6 | 0.21
| Feeder Name: | Hinkleville |  |  |  | 110 | JPEC - Planned |  | 1 | 8.33 | 1 | 60.6 | 0.06
| Feeder Number: | 214 |  |  |  | 300 | Equipment Failure |  | 2 | 16.67 | 2 | 213 | 0.2
[6 empty] | 430 | Tree failure from overhang or dead tree without ice/snow |  | 1 | 8.33 | 8 | 931.2 | 0.87
| Feeder Location | 47214-Hinkleville |  |  |  | 435 | Tree Failure from outside of ROW |  | 1 | 8.33 | 8 | 847.2 | 0.79
| Customer Count | 265 |  |  |  | 500 | Lightning |  | 2 | 16.67 | 267 | 70978.2 | 66.5
| Circuit 5 Year Average (SAIDI |  |  | 1235.0564 |  | 690 | Animal |  | 2 | 16.67 | 2 | 111.6 | 0.1
| Reporting Year (SAIDI |  | 268.0645
| Circuit 5 Year Average (SAIFI |  |  | 3.6899
| Reporting Year (SAIFI |  | 1.0084
| Total Circuit Length: | 44.6
| Date of Last Circuit Trim: | 2017
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | 0 | BREC |  | 1 | 4.35 | 266 | 33103.8 | 63.13
| Substation Name | NEW YORK |  |  |  | 110 | JPEC - Planned |  | 1 | 4.35 | 3 | 596.4 | 1.14
| Feeder Name: | US 286 East Gage |  |  |  | 300 | Equipment Failure |  | 4 | 17.39 | 6 | 487.8 | 0.93
| Feeder Number: | 224 |  |  |  | 400 | Decay/age of material/equipment |  | 1 | 4.35 | 1 | 76.8 | 0.15
[6 empty] | 420 | ROW |  | 2 | 8.7 | 27 | 3345.6 | 6.38
| Feeder Location | 47224-US 286 East |  |  |  | 500 | Lightning |  | 2 | 8.7 | 2 | 114.6 | 0.22
| Customer Count | 264 |  |  |  | 600 | Small animal/bird |  | 1 | 4.35 | 2 | 85.2 | 0.16
| Circuit 5 Year Average (SAIDI |  |  | 496.5245 |  | 630 | Squirrel |  | 1 | 4.35 | 2 | 10.2 | 0.02
| Reporting Year (SAIDI |  | 125.3216 |  |  | 690 | Animal |  | 3 | 13.04 | 32 | 4311 | 8.22
| Circuit 5 Year Average (SAIFI |  |  | 1.9148 |  | 700 | Member/Public Caused |  | 5 | 21.74 | 277 | 10173.6 | 19.4
| Reporting Year (SAIFI |  | 1.0486 |  |  | 999 | Cause unknown |  | 2 | 8.7 | 3 | 134.4 | 0.26
| Total Circuit Length: | 34.6
| Date of Last Circuit Trim: | 2015
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | 0 | BREC |  | 1 | 5 | 221 | 27728.4 | 23.89
| Substation Name | NEW YORK |  |  |  | 100 | Contractor - Planned |  | 1 | 5 | 1 | 102 | 0.09
| Feeder Name: | Blandville |  |  |  | 110 | JPEC - Planned |  | 3 | 15 | 5 | 675 | 0.58
| Feeder Number: | 234 |  |  |  | 300 | Equipment Failure |  | 1 | 5 | 5 | 659.4 | 0.57
[6 empty] | 420 | ROW |  | 3 | 15 | 183 | 23493 | 20.24
| Feeder Location | 47234-Blandville |  |  |  | 430 | Tree failure from overhang or dead tree without ice/snow |  | 2 | 10 | 223 | 37696.2 | 32.47
| Customer Count | 219 |  |  |  | 500 | Lightning |  | 3 | 15 | 11 | 1496.4 | 1.29
| Circuit 5 Year Average (SAIDI |  |  | 1312.6 |  | 690 | Animal |  | 1 | 5 | 3 | 406.8 | 0.35
| Reporting Year (SAIDI |  | 171.84 |  |  | 800 | Other |  | 1 | 5 | 1 | 70.2 | 0.06
| Circuit 5 Year Average (SAIFI |  |  | 3.7371 |  | 810 | Load |  | 2 | 10 | 222 | 23495.4 | 20.24
| Reporting Year (SAIFI |  | 1.0165 |  |  | 999 | Cause unknown |  | 2 | 10 | 5 | 266.4 | 0.23
| Total Circuit Length: | 21.9
| Date of Last Circuit Trim: | 2015
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | 0 | BREC |  | 1 | 3.03 | 355 | 43759.8 | 76.88
| Substation Name | NEW YORK |  |  |  | 100 | Contractor - Planned |  | 4 | 12.12 | 10 | 956.4 | 1.68
| Feeder Name: | Wickliffe |  |  |  | 110 | JPEC - Planned |  | 6 | 18.18 | 15 | 2125.8 | 3.73
| Feeder Number: | 244 |  |  |  | 300 | Equipment Failure |  | 2 | 6.06 | 2 | 127.8 | 0.22
[6 empty] | 420 | ROW |  | 6 | 18.18 | 83 | 6759 | 11.88
| Feeder Location | 47244-Wickliffe |  |  |  | 500 | Lightning |  | 2 | 6.06 | 19 | 916.8 | 1.61
| Customer Count | 355 |  |  |  | 540 | Storm |  | 1 | 3.03 | 1 | 77.4 | 0.14
| Circuit 5 Year Average (SAIDI |  |  | 764.3749 |  | 600 | Small animal/bird |  | 1 | 3.03 | 1 | 108 | 0.19
| Reporting Year (SAIDI |  | 123.3222 |  |  | 630 | Squirrel |  | 1 | 3.03 | 3 | 260.4 | 0.46
| Circuit 5 Year Average (SAIFI |  |  | 2.6046 |  | 690 | Animal |  | 1 | 3.03 | 1 | 53.4 | 0.09
| Reporting Year (SAIFI |  | 1.0005 |  |  | 700 | Member/Public Caused |  | 2 | 6.06 | 9 | 489 | 0.86
| Total Circuit Length: | 36.7 |  |  |  | 810 | Load |  | 5 | 15.15 | 12 | 1224.6 | 2.15
[6 empty] | 999 | Cause unknown |  | 1 | 3.03 | 1 | 59.4 | 0.1
| Date of Last Circuit Trim: | 2015
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | 0 | BREC |  | 1 | 5.88 | 353 | 43725 | 80.58
| Substation Name | NEW YORK |  |  |  | 100 | Contractor - Planned |  | 1 | 5.88 | 5 | 336.6 | 0.62
| Feeder Name: | Slater |  |  |  | 420 | ROW |  | 4 | 23.53 | 13 | 1078.2 | 1.99
| Feeder Number: | 254 |  |  |  | 430 | Tree failure from overhang or dead tree without ice/snow |  | 1 | 5.88 | 36 | 4503 | 8.3
[6 empty] | 435 | Tree Failure from outside of ROW |  | 1 | 5.88 | 2 | 388.2 | 0.72
| Feeder Location | 47254-Slater |  |  |  | 500 | Lightning |  | 3 | 17.65 | 3 | 334.8 | 0.62
| Customer Count | 358 |  |  |  | 710 | Motor Vehicle |  | 1 | 5.88 | 30 | 3346.8 | 6.17
| Circuit 5 Year Average (SAIDI |  |  | 591.4164 |  | 999 | Cause unknown |  | 5 | 29.41 | 6 | 549.6 | 1.01
| Reporting Year (SAIDI |  | 122.0651
| Circuit 5 Year Average (SAIFI |  |  | 3.0016
| Reporting Year (SAIFI |  | 0.9855
| Total Circuit Length: | 46.6
| Date of Last Circuit Trim: | 2015
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | 300 | Equipment Failure |  | 2 | 66.67 | 576 | 27512.4 | 99.48
| Substation Name | OLIVET CHURCH RD |  |  |  | 999 | Cause unknown |  | 1 | 33.33 | 3 | 142.8 | 0.52
| Feeder Name: | Olivet Ch Rd
| Feeder Number: | 214
| Feeder Location | 74214-Olivet Ch Rd
| Customer Count | 589
| Circuit 5 Year Average (SAIDI |  |  | 89.771
| Reporting Year (SAIDI |  | 46.7378
| Circuit 5 Year Average (SAIFI |  |  | 1.3835
| Reporting Year (SAIFI |  | 0.9785
| Total Circuit Length: | 23.2
| Date of Last Circuit Trim: | 2015
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | 0 | BREC |  | 1 | 2.27 | 472 | 60250.8 | 53.53
| Substation Name | OLIVET CHURCH RD |  |  |  | 100 | Contractor - Planned |  | 7 | 15.91 | 164 | 34928.4 | 31.04
| Feeder Name: | Highland Ch Rd |  |  |  | 110 | JPEC - Planned |  | 17 | 38.64 | 66 | 4188.6 | 3.72
| Feeder Number: | 224 |  |  |  | 300 | Equipment Failure |  | 1 | 2.27 | 1 | 76.2 | 0.07
[6 empty] | 420 | ROW |  | 5 | 11.36 | 68 | 3883.2 | 3.45
| Feeder Location | 74224-Highland Ch |  |  |  | 500 | Lightning |  | 1 | 2.27 | 1 | 136.2 | 0.12
| Customer Count | 481 |  |  |  | 600 | Small animal/bird |  | 3 | 6.82 | 20 | 1878.6 | 1.67
| Circuit 5 Year Average (SAIDI |  |  | 190.4088 |  | 630 | Squirrel |  | 5 | 11.36 | 43 | 3291.6 | 2.92
| Reporting Year (SAIDI |  | 125.2381 |  |  | 690 | Animal |  | 2 | 4.55 | 4 | 158.4 | 0.14
| Circuit 5 Year Average (SAIFI |  |  | 1.3178 |  | 999 | Cause unknown |  | 2 | 4.55 | 40 | 3753 | 3.33
| Reporting Year (SAIFI |  | 0.9811
| Total Circuit Length: | 10.2
| Date of Last Circuit Trim: | 2015
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | None | None |  | 0 | 0 | 0 | 0 | 0
| Substation Name | OLIVET CHURCH RD
| Feeder Name: | Info Age Park
| Feeder Number: | 234
| Feeder Location | 74234-Info Age Park
| Customer Count | 8
| Circuit 5 Year Average (SAIDI |  |  | 112.3696
| Reporting Year (SAIDI |  | 0
| Circuit 5 Year Average (SAIFI |  |  | 0.7
| Reporting Year (SAIFI |  | 0
Total Circuit Length:
Date of Last Circuit Trim:
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | 110 | JPEC - Planned |  | 5 | 27.78 | 137 | 15240.6 | 28.25
| Substation Name | PALMA |  |  |  | 300 | Equipment Failure |  | 1 | 5.56 | 4 | 1603.8 | 2.97
| Feeder Name: | Hwy 95 |  |  |  | 320 | Clearance |  | 1 | 5.56 | 1 | 95.4 | 0.18
| Feeder Number: | 214 |  |  |  | 400 | Decay/age of material/equipment |  | 1 | 5.56 | 8 | 1609.8 | 2.98
[6 empty] | 420 | ROW |  | 2 | 11.11 | 370 | 28762.2 | 53.31
| Feeder Location | 54214-Hwy 95 |  |  |  | 435 | Tree Failure from outside of ROW |  | 1 | 5.56 | 6 | 1809.6 | 3.35
| Customer Count | 369 |  |  |  | 500 | Lightning |  | 1 | 5.56 | 1 | 74.4 | 0.14
| Circuit 5 Year Average (SAIDI |  |  | 158.4371 |  | 630 | Squirrel |  | 5 | 27.78 | 63 | 4703.4 | 8.72
| Reporting Year (SAIDI |  | 78.0196 |  |  | 690 | Animal |  | 1 | 5.56 | 1 | 48.6 | 0.09
| Circuit 5 Year Average (SAIFI |  |  | 0.8556
| Reporting Year (SAIFI |  | 1.0037
| Total Circuit Length: | 17
| Date of Last Circuit Trim: | 2015
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | 100 | Contractor - Planned |  | 1 | 10 | 2 | 159.6 | 1.59
| Substation Name | PALMA |  |  |  | 110 | JPEC - Planned |  | 6 | 60 | 44 | 5479.2 | 54.47
| Feeder Name: | Draffenville |  |  |  | 300 | Equipment Failure |  | 2 | 20 | 69 | 4299 | 42.74
| Feeder Number: | 224 |  |  |  | 420 | ROW |  | 1 | 10 | 1 | 121.8 | 1.21
| Feeder Location | 54224-Draffenville
| Customer Count | 302
| Circuit 5 Year Average (SAIDI |  |  | 64.0017
| Reporting Year (SAIDI |  | 18.1701
| Circuit 5 Year Average (SAIFI |  |  | 0.5857
| Reporting Year (SAIFI |  | 0.2288
| Total Circuit Length: | 8.8
| Date of Last Circuit Trim: | 2015
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | 110 | JPEC - Planned |  | 1 | 4.17 | 5 | 838.2 | 6.84
| Substation Name | PALMA |  |  |  | 300 | Equipment Failure |  | 6 | 25 | 10 | 1896.6 | 15.48
| Feeder Name: | Palma |  |  |  | 420 | ROW |  | 2 | 8.33 | 4 | 848.4 | 6.92
| Feeder Number: | 234 |  |  |  | 470 | Borrower crew cuts tree |  | 1 | 4.17 | 38 | 1714.8 | 14
[6 empty] | 500 | Lightning |  | 2 | 8.33 | 3 | 495 | 4.04
| Feeder Location | 54234-Palma |  |  |  | 590 | Weather other |  | 1 | 4.17 | 28 | 1448.4 | 11.82
| Customer Count | 744 |  |  |  | 600 | Small animal/bird |  | 2 | 8.33 | 16 | 924 | 7.54
| Circuit 5 Year Average (SAIDI |  |  | 155.8878 |  | 630 | Squirrel |  | 2 | 8.33 | 16 | 987.6 | 8.06
| Reporting Year (SAIDI |  | 2.9915 |  |  | 690 | Animal |  | 4 | 16.67 | 18 | 871.8 | 7.12
| Circuit 5 Year Average (SAIFI |  |  | 1.1702 |  | 999 | Cause unknown |  | 3 | 12.5 | 28 | 2226.6 | 18.17
| Reporting Year (SAIFI |  | 0.0511
| Total Circuit Length: | 26.2
| Date of Last Circuit Trim: | 2015
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | 100 | Contractor - Planned |  | 4 | 12.12 | 9 | 1214.4 | 2.02
| Substation Name | POSSUM TROT |  |  |  | 110 | JPEC - Planned |  | 8 | 24.24 | 13 | 1836.6 | 3.06
| Feeder Name: | Possum Trot |  |  |  | 300 | Equipment Failure |  | 3 | 9.09 | 68 | 4890.6 | 8.15
| Feeder Number: | 224 |  |  |  | 420 | ROW |  | 2 | 6.06 | 547 | 17823 | 29.7
[6 empty] | 435 | Tree Failure from outside of ROW |  | 2 | 6.06 | 36 | 4902.6 | 8.17
| Feeder Location | 78224-Possum Trot |  |  |  | 540 | Storm |  | 1 | 3.03 | 1 | 115.2 | 0.19
| Customer Count | 545 |  |  |  | 600 | Small animal/bird |  | 1 | 3.03 | 538 | 16830.6 | 28.04
| Circuit 5 Year Average (SAIDI |  |  | 121.5368 |  | 630 | Squirrel |  | 1 | 3.03 | 3 | 336.6 | 0.56
| Reporting Year (SAIDI |  | 32.7273 |  |  | 690 | Animal |  | 6 | 18.18 | 90 | 7368.6 | 12.28
| Circuit 5 Year Average (SAIFI |  |  | 1.1469 |  | 700 | Member/Public Caused |  | 1 | 3.03 | 19 | 1279.2 | 2.13
| Reporting Year (SAIFI |  | 1.0044 |  |  | 999 | Cause unknown |  | 4 | 12.12 | 44 | 3422.4 | 5.7
| Total Circuit Length: | 15
| Date of Last Circuit Trim: | 2015
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | 100 | Contractor - Planned |  | 1 | 7.14 | 2 | 285.6 | 1.32
| Substation Name | POSSUM TROT |  |  |  | 110 | JPEC - Planned |  | 3 | 21.43 | 7 | 730.8 | 3.37
| Feeder Name: | Hwy 95 |  |  |  | 600 | Small animal/bird |  | 1 | 7.14 | 198 | 6412.2 | 29.59
| Feeder Number: | 234 |  |  |  | 690 | Animal |  | 8 | 57.14 | 108 | 13126.8 | 60.57
[6 empty] | 999 | Cause unknown |  | 1 | 7.14 | 12 | 1116.6 | 5.15
| Feeder Location | 78234-Hwy 95
| Customer Count | 201
| Circuit 5 Year Average (SAIDI |  |  | 256.6475
| Reporting Year (SAIDI |  | 65.4273
| Circuit 5 Year Average (SAIFI |  |  | 1.3646
| Reporting Year (SAIFI |  | 0.9868
| Total Circuit Length: | 42.2
| Date of Last Circuit Trim: | 2015
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | 300 | Equipment Failure |  | 2 | 20 | 2 | 141.6 | 0.65
| Substation Name | POSSUM TROT |  |  |  | 435 | Tree Failure from outside of ROW |  | 1 | 10 | 32 | 3604.2 | 16.58
| Feeder Name: | Industrial Loop |  |  |  | 500 | Lightning |  | 1 | 10 | 3 | 220.2 | 1.01
| Feeder Number: | 254 |  |  |  | 600 | Small animal/bird |  | 1 | 10 | 210 | 6888 | 31.68
[6 empty] | 700 | Member/Public Caused |  | 1 | 10 | 62 | 9218.4 | 42.39
| Feeder Location | 78254-Industrial Loo |  |  |  | 790 | Public other |  | 1 | 10 | 3 | 336 | 1.55
| Customer Count | 207 |  |  |  | 999 | Cause unknown |  | 3 | 30 | 20 | 1336.2 | 6.14
| Circuit 5 Year Average (SAIDI |  |  | 209.706
| Reporting Year (SAIDI |  | 44.6043
| Circuit 5 Year Average (SAIFI |  |  | 1.3519
| Reporting Year (SAIFI |  | 1.0161
| Total Circuit Length: | 28.6
| Date of Last Circuit Trim: | 2015
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | 600 | Small animal/bird |  | 1 | 100 | 2 | 66 | 100
| Substation Name | POSSUM TROT
| Feeder Name: | CoalTek
| Feeder Number: | 264
| Feeder Location | 78264-CoalTek
| Customer Count | 2
| Circuit 5 Year Average (SAIDI |  |  | 97.06
| Reporting Year (SAIDI |  | 33.0667
| Circuit 5 Year Average (SAIFI |  |  | 0.6
| Reporting Year (SAIFI |  | 1
| Total Circuit Length: | 4
| Date of Last Circuit Trim: | 2015
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | 100 | Contractor - Planned |  | 2 | 12.5 | 2 | 150 | 1.12
| Substation Name | RAGLAND |  |  |  | 110 | JPEC - Planned |  | 3 | 18.75 | 5 | 571.8 | 4.26
| Feeder Name: | Monkeys Eyebrow |  |  |  | 300 | Equipment Failure |  | 1 | 6.25 | 1 | 142.2 | 1.06
| Feeder Number: | 214 |  |  |  | 320 | Clearance |  | 1 | 6.25 | 1 | 123 | 0.92
[6 empty] | 420 | ROW |  | 2 | 12.5 | 24 | 3004.8 | 22.36
| Feeder Location | 19214-Monkeys Eye |  |  |  | 430 | Tree failure from overhang or dead tree without ice/snow |  | 3 | 18.75 | 21 | 3589.2 | 26.71
| Customer Count | 238 |  |  |  | 600 | Small animal/bird |  | 1 | 6.25 | 1 | 54 | 0.4
| Circuit 5 Year Average (SAIDI |  |  | 273.2344 |  | 700 | Member/Public Caused |  | 2 | 12.5 | 38 | 5725.8 | 42.61
| Reporting Year (SAIDI |  | 24.0815 |  |  | 999 | Cause unknown |  | 1 | 6.25 | 1 | 76.2 | 0.57
| Circuit 5 Year Average (SAIFI |  |  | 1.4384
| Reporting Year (SAIFI |  | 0.1598
| Total Circuit Length: | 51
| Date of Last Circuit Trim: | 2017
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | 110 | JPEC - Planned |  | 2 | 15.38 | 3 | 267 | 1.01
| Substation Name | RAGLAND |  |  |  | 300 | Equipment Failure |  | 1 | 7.69 | 45 | 1038.6 | 3.94
| Feeder Name: | Ragland |  |  |  | 420 | ROW |  | 4 | 30.77 | 324 | 23143.8 | 87.87
| Feeder Number: | 224 |  |  |  | 690 | Animal |  | 1 | 7.69 | 1 | 72 | 0.27
[6 empty] | 700 | Member/Public Caused |  | 3 | 23.08 | 34 | 1509.6 | 5.73
| Feeder Location | 19224-Ragland |  |  |  | 999 | Cause unknown |  | 2 | 15.38 | 3 | 306.6 | 1.16
| Customer Count | 222
| Circuit 5 Year Average (SAIDI |  |  | 268.7554
| Reporting Year (SAIDI |  | 104.2139
| Circuit 5 Year Average (SAIFI |  |  | 1.2851
| Reporting Year (SAIFI |  | 1.4589
| Total Circuit Length: | 20.9
| Date of Last Circuit Trim: | 2017
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | 110 | JPEC - Planned |  | 1 | 16.67 | 10 | 2963.4 | 9.02
| Substation Name | REIDLAND |  |  |  | 435 | Tree Failure from outside of ROW |  | 1 | 16.67 | 329 | 28628.4 | 87.12
| Feeder Name: | Ken Mar Rd |  |  |  | 600 | Small animal/bird |  | 1 | 16.67 | 1 | 52.2 | 0.16
| Feeder Number: | 214 |  |  |  | 630 | Squirrel |  | 1 | 16.67 | 5 | 191.4 | 0.58
[6 empty] | 999 | Cause unknown |  | 2 | 33.33 | 18 | 1024.8 | 3.12
| Feeder Location | 41214-Ken Mar Rd
| Customer Count | 341
| Circuit 5 Year Average (SAIDI |  |  | 165.5859
| Reporting Year (SAIDI |  | 84.0556
| Circuit 5 Year Average (SAIFI |  |  | 1.5097
| Reporting Year (SAIFI |  | 0.966
| Total Circuit Length: | 7.8
| Date of Last Circuit Trim: | 2017
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | 100 | Contractor - Planned |  | 1 | 33.33 | 2 | 177 | 13.73
| Substation Name | REIDLAND |  |  |  | 420 | ROW |  | 1 | 33.33 | 7 | 811.2 | 62.91
| Feeder Name: | Reidland Water |  |  |  | 500 | Lightning |  | 1 | 33.33 | 4 | 301.2 | 23.36
| Feeder Number: | 224
| Feeder Location | 41224-Reidland Wat
| Customer Count | 50
| Circuit 5 Year Average (SAIDI |  |  | 68.7115
| Reporting Year (SAIDI |  | 16.1356
| Circuit 5 Year Average (SAIFI |  |  | 0.6603
| Reporting Year (SAIFI |  | 0.1392
| Total Circuit Length: | 1.6
| Date of Last Circuit Trim: | 2017
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | 110 | JPEC - Planned |  | 1 | 14.29 | 3 | 282 | 7.68
| Substation Name | REIDLAND |  |  |  | 420 | ROW |  | 5 | 71.43 | 16 | 3322.8 | 90.55
| Feeder Name: | Epperson Rd |  |  |  | 690 | Animal |  | 1 | 14.29 | 1 | 64.8 | 1.77
| Feeder Number: | 234
| Feeder Location | 41234-Epperson Rd
| Customer Count | 197
| Circuit 5 Year Average (SAIDI |  |  | 168.854
| Reporting Year (SAIDI |  | 16.8654
| Circuit 5 Year Average (SAIFI |  |  | 0.9572
| Reporting Year (SAIFI |  | 2.0402
| Total Circuit Length: | 4.6
| Date of Last Circuit Trim: | 2017
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | 300 | Equipment Failure |  | 1 | 25 | 1 | 38.4 | 5.65
| Substation Name | REIDLAND |  |  |  | 435 | Tree Failure from outside of ROW |  | 1 | 25 | 1 | 44.4 | 6.54
| Feeder Name: | Walker Boat Yard |  |  |  | 999 | Cause unknown |  | 2 | 50 | 6 | 596.4 | 87.81
| Feeder Number: | 244
| Feeder Location | 41244-Walker Boat
| Customer Count | 98
| Circuit 5 Year Average (SAIDI |  |  | 90.8448
| Reporting Year (SAIDI |  | 6.056
| Circuit 5 Year Average (SAIFI |  |  | 0.6747
| Reporting Year (SAIFI |  | 0.061
| Total Circuit Length: | 7.9
| Date of Last Circuit Trim: | 2017
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | 110 | JPEC - Planned |  | 2 | 22.22 | 7 | 388.2 | 4.29
| Substation Name | SMITHLAND |  |  |  | 420 | ROW |  | 3 | 33.33 | 46 | 7048.2 | 77.8
| Feeder Name: | Smithland |  |  |  | 500 | Lightning |  | 2 | 22.22 | 15 | 1116 | 12.32
| Feeder Number: | 214 |  |  |  | 630 | Squirrel |  | 1 | 11.11 | 2 | 115.8 | 1.28
[6 empty] | 690 | Animal |  | 1 | 11.11 | 7 | 391.2 | 4.32
| Feeder Location | 32214-Smithland
| Customer Count | 381
| Circuit 5 Year Average (SAIDI |  |  | 263.9505
| Reporting Year (SAIDI |  | 18.4764
| Circuit 5 Year Average (SAIFI |  |  | 1.48
| Reporting Year (SAIFI |  | 0.1206
| Total Circuit Length: | 67.9
| Date of Last Circuit Trim: | 2019
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | 110 | JPEC - Planned |  | 3 | 8.57 | 3 | 261.6 | 0.39
| Substation Name | SMITHLAND |  |  |  | 300 | Equipment Failure |  | 6 | 17.14 | 69 | 6798.6 | 10.17
| Feeder Name: | Tiline |  |  |  | 420 | ROW |  | 7 | 20 | 165 | 50029.8 | 74.81
| Feeder Number: | 224 |  |  |  | 435 | Tree Failure from outside of ROW |  | 2 | 5.71 | 31 | 3312.6 | 4.95
[6 empty] | 500 | Lightning |  | 5 | 14.29 | 9 | 1161 | 1.74
| Feeder Location | 32224-Tiline |  |  |  | 690 | Animal |  | 1 | 2.86 | 1 | 78 | 0.12
| Customer Count | 558 |  |  |  | 700 | Member/Public Caused |  | 1 | 2.86 | 13 | 2356.2 | 3.52
| Circuit 5 Year Average (SAIDI |  |  | 491.1862 |  | 810 | Load |  | 1 | 2.86 | 1 | 90 | 0.13
| Reporting Year (SAIDI |  | 89.6877 |  |  | 999 | Cause unknown |  | 9 | 25.71 | 37 | 2784.6 | 4.16
| Circuit 5 Year Average (SAIFI |  |  | 2.2635
| Reporting Year (SAIFI |  | 0.2958
| Total Circuit Length: | 85
| Date of Last Circuit Trim: | 2019
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | 100 | Contractor - Planned |  | 1 | 5.56 | 1 | 114.6 | 0.42
| Substation Name | SMITHLAND |  |  |  | 110 | JPEC - Planned |  | 1 | 5.56 | 5 | 1608.6 | 5.89
| Feeder Name: | Mitchell Store |  |  |  | 300 | Equipment Failure |  | 3 | 16.67 | 46 | 5430 | 19.9
| Feeder Number: | 244 |  |  |  | 420 | ROW |  | 3 | 16.67 | 36 | 4252.8 | 15.58
[6 empty] | 430 | Tree failure from overhang or dead tree without ice/snow |  | 2 | 11.11 | 111 | 14049.6 | 51.48
| Feeder Location | 32244-Mitchell Store |  |  |  | 435 | Tree Failure from outside of ROW |  | 1 | 5.56 | 1 | 174 | 0.64
| Customer Count | 385 |  |  |  | 500 | Lightning |  | 2 | 11.11 | 12 | 1010.4 | 3.7
| Circuit 5 Year Average (SAIDI |  |  | 636.6726 |  | 999 | Cause unknown |  | 5 | 27.78 | 9 | 649.2 | 2.38
| Reporting Year (SAIDI |  | 36.4564
| Circuit 5 Year Average (SAIFI |  |  | 2.9695
| Reporting Year (SAIFI |  | 0.288
| Total Circuit Length: | 38.6
| Date of Last Circuit Trim: | 2019
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | None | None |  | 0 | 0 | 0 | 0 | 0
| Substation Name | SMITHLAND
| Feeder Name: | REC_00004485
| Feeder Number: | 3
| Feeder Location | 04485-REC_000044
| Customer Count | 0
| Circuit 5 Year Average (SAIDI |  |  | 0
| Reporting Year (SAIDI |  | 0
| Circuit 5 Year Average (SAIFI |  |  | 0
| Reporting Year (SAIFI |  | 0
Total Circuit Length:
Date of Last Circuit Trim:
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | 100 | Contractor - Planned |  | 1 | 16.67 | 1 | 69.6 | 6.78
| Substation Name | STRAWBERRY HILL |  |  |  | 110 | JPEC - Planned |  | 1 | 16.67 | 3 | 96.6 | 9.41
| Feeder Name: | Hansen Rd |  |  |  | 630 | Squirrel |  | 1 | 16.67 | 1 | 56.4 | 5.49
| Feeder Number: | 224 |  |  |  | 690 | Animal |  | 2 | 33.33 | 6 | 688.8 | 67.1
[6 empty] | 999 | Cause unknown |  | 1 | 16.67 | 3 | 115.2 | 11.22
| Feeder Location | 77224-Hansen Rd
| Customer Count | 731
| Circuit 5 Year Average (SAIDI |  |  | 132.7151
| Reporting Year (SAIDI |  | 0.9428
| Circuit 5 Year Average (SAIFI |  |  | 1.4514
| Reporting Year (SAIFI |  | 0.0082
| Total Circuit Length: | 30.2
| Date of Last Circuit Trim: | 2015
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | None | None |  | 0 | 0 | 0 | 0 | 0
| Substation Name | STRAWBERRY HILL
| Feeder Name: | Walmart
| Feeder Number: | 234
| Feeder Location | 77234-Walmart
| Customer Count | 542
| Circuit 5 Year Average (SAIDI |  |  | 77.2032
| Reporting Year (SAIDI |  | 0
| Circuit 5 Year Average (SAIFI |  |  | 0.7545
| Reporting Year (SAIFI |  | 0
Total Circuit Length:
Date of Last Circuit Trim:
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | None | None |  | 0 | 0 | 0 | 0 | 0
| Substation Name | STRAWBERRY HILL
| Feeder Name: | CSI
| Feeder Number: | 254
| Feeder Location | 77254-CSI
| Customer Count | 87
| Circuit 5 Year Average (SAIDI |  |  | 12.0917
| Reporting Year (SAIDI |  | 0
| Circuit 5 Year Average (SAIFI |  |  | 0.6026
| Reporting Year (SAIFI |  | 0
Total Circuit Length:
Date of Last Circuit Trim:
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | None | None |  | 0 | 0 | 0 | 0 | 0
| Substation Name | STRAWBERRY HILL
| Feeder Name: | Hwy 60
| Feeder Number: | 264
| Feeder Location | 77264-Hwy 60
| Customer Count | 13
| Circuit 5 Year Average (SAIDI |  |  | 69.5504
| Reporting Year (SAIDI |  | 0
| Circuit 5 Year Average (SAIFI |  |  | 0.7304
| Reporting Year (SAIFI |  | 0
Total Circuit Length:
Date of Last Circuit Trim:
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | None | None |  | 0 | 0 | 0 | 0 | 0
| Substation Name | STRAWBERRY HILL
| Feeder Name: | REC_00000309
| Feeder Number: | 4
| Feeder Location | 77244-REC_000003
| Customer Count | 0
| Circuit 5 Year Average (SAIDI |  |  | 0
| Reporting Year (SAIDI |  | 0
| Circuit 5 Year Average (SAIFI |  |  | 0
| Reporting Year (SAIFI |  | 0
Total Circuit Length:
Date of Last Circuit Trim:
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | None | None |  | 0 | 0 | 0 | 0 | 0
| Substation Name | VULCAN
| Feeder Name: | Vulcan Pit
| Feeder Number: | 224
| Feeder Location | 45224-Vulcan Pit
| Customer Count | 0
| Circuit 5 Year Average (SAIDI |  |  | 0
| Reporting Year (SAIDI |  | 0
| Circuit 5 Year Average (SAIFI |  |  | 0
| Reporting Year (SAIFI |  | 0
Total Circuit Length:
Date of Last Circuit Trim:
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | 999 | Cause unknown |  | 1 | 100 | 0 | 0 | 0
| Substation Name | VULCAN
| Feeder Name: | Vulcan 1 Rock Crush
| Feeder Number: | 234
| Feeder Location | 45234-Vulcan 1 Roc
| Customer Count | 1
| Circuit 5 Year Average (SAIDI |  |  | 398.3333
| Reporting Year (SAIDI |  | 0
| Circuit 5 Year Average (SAIFI |  |  | 2.8
| Reporting Year (SAIFI |  | 0
Total Circuit Length:
Date of Last Circuit Trim:
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | 600 | Small animal/bird |  | 3 | 75 | 101 | 21046.2 | 75.9
| Substation Name | VULCAN |  |  |  | 690 | Animal |  | 1 | 25 | 33 | 6682.8 | 24.1
| Feeder Name: | Kinder Morgan
| Feeder Number: | 244
| Feeder Location | 45244-Kinder Morga
| Customer Count | 35
| Circuit 5 Year Average (SAIDI |  |  | 1208.2809
| Reporting Year (SAIDI |  | 608.0979
| Circuit 5 Year Average (SAIFI |  |  | 10.2225
| Reporting Year (SAIFI |  | 2.9182
| Total Circuit Length: | 7.7
Date of Last Circuit Trim:
Corrective Action Plan:
[6 empty] | Cause Code/ Description |  |  | Nbr Outages | % of Total | Nbr Cons Out | Cons Mins | % of Total
[6 empty] | 110 | JPEC - Planned |  | 1 | 50 | 2 | 33 | 100
| Substation Name | VULCAN |  |  |  | 999 | Cause unknown |  | 1 | 50 | 0 | 0 | 0
| Feeder Name: | Vulcan 2 Hwy 62
| Feeder Number: | 254
| Feeder Location | 45254-Vulcan 2 Hwy
| Customer Count | 2
| Circuit 5 Year Average (SAIDI |  |  | 106.1348
| Reporting Year (SAIDI |  | 17.5887
| Circuit 5 Year Average (SAIFI |  |  | 1.0638
| Reporting Year (SAIFI |  | 1.0638
| Total Circuit Length: | 5.5
Date of Last Circuit Trim:
Corrective Action Plan:
| Total Customer Hrs Off: |  | 62477.65 |  | Total Customer Mins Off |  |  | 3748659
| Total Customers Affected: |  | 39657
| Total Outage Count: |  | 1442
/report/19020/rptcustom/oms/OMS_ANNUAL_RLBLTY_RPT_19020.xml.rpt
53040

## 2020 Circuit Details
Electric Distribution Utility Annual Reliability ReportA1:I44
SECTION 1: CONTACT INFORMATION
|  |  | UTILITY NAME | 1.1 | Jackson Purchase Energy Corporation
|  |  | REPORT PREPARED BY | 1.2 | Kristy Reed
|  |  | E-MAIL ADDRESS OF PREPARER | 1.3 | kristy.reed@jpenergy.com
|  |  | PHONE NUMBER OF PREPARER | 1.4 | 270-442-7321
SECTION 2: REPORT YEAR
|  |  | CALENDAR YEAR OF REPORT | 2.1 | 2020
SECTION 3: MAJOR EVENT DAYS
|  |  | TMED | 3.1 | 9.77
|  |  | FIRST DATE USED TO DETERMINE TMED | 3.2 | 2015-01-01
|  |  | LAST DATE USED TO DETERMINE TMED | 3.3 | 2019-12-31
|  |  | NUMBER OF MED IN REPORT YEAR | 3.4 | 1
NOTE: Per IEEE 1366 TMED should be calculated using the daily SAIDI values for the five prior years. If five years of data are not available, then utilities should use what is available until five years are accumulated.
SECTION 4: SYSTEM RELIABILITY RESULTS
System - Wide Information
| Total Customers | 30337 |  |  | Total Circuits | 91
Excluding MED
| 5 Year Average |  |  |  | Reporting Year
| SAIDI | 108.07 |  |  | SAIDI | 93.472
| SAIFI | 1.17 |  |  | SAIFI | 1.3127
Including MED
| 5 Year Average |  |  |  | Reporting Year
| SAIDI | 343.12 |  |  | SAIDI | 103.296
| SAIFI | 1.73 |  |  | SAIFI | 1.3776
SECTION 5: CIRCUIT REPORTING
Circuit Name | Circuit Number | Circuit Location | Substation Name | Substation Number | Avg # of Customers |  | Previous 5 Year Average SAIFI | Current Year SAIFI Excluding MED | Comparison | Circuit Length | Date of Last Trim For Circuit | Previous 5 Year Average SAIDI | Current Year SAIDI Excluding MED |  |  | # of Outages | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | %
Hampton-South | 5214 | 05214-Hampton South | Joy | 5 | 192.0487 |  | 2.5792 | 1.1507 | OK | 57.9 | 2016 | 540.3751 | 164.3021 | OK | Good | 16
Carrsville | 5244 | 05244-Carrsville | Joy | 5 | 72.7221 |  | 1.5915 | 0.027502 | OK | 10.8 | 2016 | 340.7013 | 2.6677 | OK | Good | 1
Lola | 5254 | 05254-Lola | Joy | 5 | 298.467 |  | 1.3663 | 1.4306 | PSC | 56.5 | 2016 | 321.0894 | 237.7783 | OK | More Info Required | 14 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 435 Tree failure from outside of ROW | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Hampton | 14214 | 14214-Hampton | Burna | 14 | 87.6819 |  | 0.92984 | 1.0492 | PSC | 12.6 | 2020 | 262.7378 | 83.0616 | OK | More Info Required | 4 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 435 Tree failure from outside of ROW | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Salem | 14244 | 14244-Salem | Burna | 14 | 317.5473 |  | 0.97126 | 1.4297 | PSC | 52.9 | 2020 | 207.9277 | 146.0475 | OK | More Info Required | 16 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 435 Tree failure from outside of ROW | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Smithland | 14254 | 14254-Smithland | Burna | 14 | 343.0688 |  | 1.9999 | 2.2357 | PSC | 69.7 | 2020 | 386.6662 | 131.5625 | OK | More Info Required | 19 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 435 Tree failure from outside of ROW | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Pinckneyville | 15224 | 15224-Pinckneyville | Cumberland | 15 | 114.5645 |  | 1.6049 | 2.0251 | PSC | 28 | 2015 | 256.8558 | 247.747 | OK | More Info Required | 5 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 435 Tree failure from outside of ROW | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Quarry | 15234 | 15234-Quarry | Cumberland | 15 | 31 |  | 0.63426 | 1.129 | PSC | 5.5 | 2015 | 195.3342 | 65.3226 | OK | More Info Required | 4 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 435 Tree failure from outside of ROW | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Monkey's Eyebrow | 19214 | 19214-Monkeys Eyebrow | Ragland | 19 | 247.9857 |  | 1.4384 | 0.91134 | OK | 50.5 | 2017 | 214.1913 | 159.7996 | OK | Good | 28
Ragland | 19224 | 19224-Ragland | Ragland | 19 | 227.0229 |  | 0.69883 | 0.33477 | OK | 33.3 | 2017 | 203.9737 | 35.2079 | OK | Good | 32
Damron's | 26214 | 26214-Damrons | LaCenter | 26 | 228.8797 |  | 1.156 | 1.8263 | PSC | 39.7 | 2015 | 272.5504 | 163.1076 | OK | More Info Required | 32 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 435 Tree failure from outside of ROW | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Oscar | 26224 | 26224-Oscar | LaCenter | 26 | 356.8625 |  | 2.0903 | 1.7654 | OK | 69.7 | 2015 | 555.8255 | 338.3404 | OK | Good | 55
Hobbs Rd | 28214 | 28214-Hobbs Rd | Kevil | 28 | 554.6905 |  | 2.022 | 4.7197 | PSC | 53.7 | 2017 | 327.5704 | 229.0196 | OK | More Info Required | 43 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 435 Tree failure from outside of ROW | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Woodville Rd | 28224 | 28224-Woodville Rd | Kevil | 28 | 480.8453 |  | 1.3265 | 1.254 | OK | 55.8 | 2017 | 198.8845 | 56.5421 | OK | Good | 19
Kelley Rd | 28234 | 28234-Kelley Rd | Kevil | 28 | 409.7192 |  | 0.91108 | 1.3107 | PSC | 46.8 | 2017 | 162.9733 | 42.4657 | OK | More Info Required | 22 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 435 Tree failure from outside of ROW | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
High Point | 29214 | 29214-High Point | High Point | 29 | 197.4928 |  | 1.0316 | 0.38989 | OK | 21.3 | 2015 | 173.9493 | 16.9525 | OK | Good | 6
Carneal Rd | 29224 | 29224-Carneal Rd | High Point | 29 | 248.4269 |  | 2.3073 | 6.7666 | PSC | 33.2 | 2015 | 436.6489 | 171.6279 | OK | More Info Required | 10 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 435 Tree failure from outside of ROW | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Essex | 29234 | 29234-Essex | High Point | 29 | 0 |  | 0 | 0 | OK | 0.04 | 2015 | 0 | 0 | OK | Good | 0
Conrad Heights | 30224 | 30224-Conrad Heights | Coleman Road | 30 | 390.8166 |  | 1.577 | 1.2435 | OK | 18.2 | 2015 | 264.0602 | 69.713 | OK | Good | 8
Holt Rd | 30244 | 30244-Hwy 60 Business | Coleman Road | 30 | 102.1805 |  | 0.61453 | 1.1157 | PSC | 7.7 | 2015 | 42.4978 | 77.6665 | PSC | More Info Required | 3 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 435 Tree failure from outside of ROW | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Ky Oaks Mall | 30254 | 30254-KY Oaks Mall | Coleman Road | 30 | 0 |  | 0.3922 | 0 | OK | 3.9 | 2015 | 32.9625 | 0 | OK | Good | 0
US 60 East | 31224 | 31224-US 60 East | Ledbetter | 31 | 320.8539 |  | 0.29219 | 0.3179 | PSC | 35.6 | 2016 | 44.4335 | 28.7327 | OK | More Info Required | 14 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 435 Tree failure from outside of ROW | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
River Crossing | 31234 | 31234-River Crossing | Ledbetter | 31 | 33.7278 |  | 0.22937 | 0.97842 | PSC | 4.3 | 2016 | 15.3152 | 64.5758 | PSC | More Info Required | 1 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 435 Tree failure from outside of ROW | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Ledbetter | 31244 | 31244-Ledbetter | Ledbetter | 31 | 1018.3582 |  | 1.009 | 1.254 | PSC | 61.6 | 2016 | 169.8136 | 63.1919 | OK | More Info Required | 33 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 435 Tree failure from outside of ROW | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Smithland | 32214 | 32214-Smithland | Smithland | 32 | 380.8252 |  | 1.5793 | 0.5173 | OK | 30.3 | 2019 | 249.3751 | 72.0015 | OK | Good | 13
Tiline | 32224 | 32224-Tiline | Smithland | 32 | 565.9656 |  | 2.8621 | 1.1714 | OK | 108.8 | 2019 | 450.0435 | 60.5956 | OK | Good | 35
Mitchell Store | 32244 | 32244-Mitchell Store | Smithland | 32 | 389.8052 |  | 3.3294 | 1.0313 | OK | 56.3 | 2019 | 597.6663 | 6.0825 | OK | Good | 9
Airport | 39214 | 39214-Airport | Little Union | 39 | 554.6848 |  | 1.882 | 0.75538 | OK | 35.9 | 2017 | 192.875 | 50.5206 | OK | Good | 8
US 60 West | 39224 | 39224-US 60 West | Little Union | 39 | 474.3639 |  | 1.4543 | 2.2894 | PSC | 37.2 | 2017 | 260.1536 | 178.0321 | OK | More Info Required | 19 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 435 Tree failure from outside of ROW | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
US 60 East-K O M | 39234 | 39234-US 60 East Mall | Little Union | 39 | 159.9054 |  | 0.5774 | 0.018761 | OK | 10.1 | 2017 | 49.3542 | 1.4008 | OK | Good | 3
Roy Lee Rd | 39244 | 39244-Roy Lee Rd | Little Union | 39 | 467.9971 |  | 1.3951 | 0.88462 | OK | 52.4 | 2017 | 449.4036 | 47.9341 | OK | Good | 30
Husbands Rd | 40224 | 40224-Husbands Rd | Husbands Road | 40 | 768.7765 |  | 1.3094 | 0.10146 | OK | 44.1 | 2018 | 272.379 | 4.2652 | OK | Good | 15
Lydon Rd | 40234 | 40234-Lydon Rd | Husbands Road | 40 | 456.1805 |  | 0.82694 | 0.6949 | OK | 32.1 | 2018 | 98.8846 | 99.0397 | PSC | More Info Required | 15 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 435 Tree failure from outside of ROW | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Clarkline Rd | 40244 | 40244-Clarkline Rd | Husbands Road | 40 | 298.7249 |  | 0.44371 | 0.17742 | OK | 26.5 | 2018 | 71.5606 | 12.4529 | OK | Good | 16
Ken Mar Rd | 41214 | 41214-Ken Mar Rd | Reidland | 41 | 328.4871 |  | 1.357 | 1.0929 | OK | 20 | 2018 | 122.2445 | 61.1592 | OK | Good | 15
Reidland Water | 41224 | 41224-Reidland Water | Reidland | 41 | 52.7307 |  | 0.44539 | 0.66375 | PSC | 2.9 | 2018 | 53.5191 | 28.8068 | OK | More Info Required | 2 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 435 Tree failure from outside of ROW | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Epperson Rd | 41234 | 41234-Epperson Rd | Reidland | 41 | 203.0086 |  | 0.50429 | 0.21181 | OK | 9.4 | 2018 | 43.0301 | 18.7874 | OK | Good | 7
Walker Boat Yard | 41244 | 41244-Walker Boat Yard | Reidland | 41 | 102.2178 |  | 0.81631 | 0.15653 | OK | 13.1 | 2018 | 75.7163 | 13.4419 | OK | Good | 6
Proform | 42214 | 42214-Proform | Culp | 42 | 427.4728 |  | 1.1439 | 0.31581 | OK | 25.7 | 2018 | 206.331 | 22.2166 | OK | Good | 11
Little Cypress | 42224 | 42224-Little Cypress | Culp | 42 | 50.4241 |  | 0.65497 | 0.019832 | OK | 8.1 | 2018 | 147.9581 | 1.1899 | OK | Good | 1
Possum Trot | 42234 | 42234-Possum Trot | Culp | 42 | 201.1748 |  | 0.98044 | 0.089474 | OK | 18.6 | 2018 | 267.8 | 6.5068 | OK | Good | 6
Sharpe | 42244 | 42244-Sharpe | Culp | 42 | 1089.3897 |  | 1.0196 | 1.8506 | PSC | 78.8 | 2018 | 78.323 | 170.0007 | PSC | More Info Required | 47 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 435 Tree failure from outside of ROW | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
CC/Hwy 95 | 43214 | 43214-Hwy 95 | Calvert City | 43 | 241.1261 |  | 0.6451 | 0.099533 | OK | 18.7 | 2017 | 160.1055 | 15.7179 | OK | Good | 6
CC Hgts | 43224 | 43224-Calvert Heights | Calvert City | 43 | 650.2951 |  | 0.87743 | 0.39367 | OK | 28.4 | 2017 | 111.6972 | 25.4961 | OK | Good | 29
Gilbertsville | 43234 | 43234-Gilbertsville | Calvert City | 43 | 348.3668 |  | 0.36118 | 1.1884 | PSC | 23.6 | 2017 | 99.6642 | 71.3817 | OK | More Info Required | 12 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 435 Tree failure from outside of ROW | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
CC Ind Park | 43244 | 43244-Industrial Park | Calvert City | 43 | 25.9799 |  | 0.42134 | 2.0785 | PSC | 4.9 | 2017 | 87.9788 | 138.145 | PSC | More Info Required | 3 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 435 Tree failure from outside of ROW | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Vulcan Pit | 45224 | 45224-Vulcan Pit | Vulcan | 45 | 0 |  | 0 | 0 | OK | 2.4 |  | 0 | 0 | OK | Good | 0
Vulcan 1-Rock Crusher | 45234 | 45234-Vulcan1 Rock Crusher | Vulcan | 45 | 2 |  | 0.7 | 0 | OK | 1.3 |  | 116.9 | 0 | OK | Good | 0
Kinder Morgan 1 | 45244 | 45244-Kinder Morgan 1 | Vulcan | 45 | 34.9284 |  | 1.1957 | 44.9778 | PSC | 7.8 |  | 244.2125 | 4419.846 | PSC | More Info Required | 7 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 435 Tree failure from outside of ROW | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Vulcan 2 Hwy 62 | 45254 | 45254-Vulcan 2 Hwy 62 | Vulcan | 45 | 3 |  | 0.63333 | 1.3333 | PSC | 5 |  | 84.0333 | 184 | PSC | More Info Required | 2 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 435 Tree failure from outside of ROW | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Hinkleville | 47214 | 47214-Hinkleville | New York | 47 | 263.8653 |  | 2.9313 | 3.0546 | PSC | 44.7 | 2017 | 545.8148 | 82.2882 | OK | More Info Required | 13 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 435 Tree failure from outside of ROW | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
US 286 East-Gage | 47224 | 47224-US 286 East Gage | New York | 47 | 263.2779 |  | 1.3939 | 1.2914 | OK | 45.5 | 2017 | 285.7536 | 33.4361 | OK | Good | 23
Blandville | 47234 | 47234-Blandville | New York | 47 | 222.553 |  | 3.0109 | 3.5991 | PSC | 30.2 | 2017 | 864.0128 | 502.6488 | OK | More Info Required | 18 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 435 Tree failure from outside of ROW | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Wickliffe | 47244 | 47244-Wickliffe | New York | 47 | 347.5845 |  | 1.8959 | 2.9892 | PSC | 49.2 | 2017 | 440.0806 | 237.0877 | OK | More Info Required | 26 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 435 Tree failure from outside of ROW | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Slater | 47254 | 47254-Slater | New York | 47 | 348.3467 |  | 2.9286 | 1.7138 | OK | 67.8 | 2017 | 546.6251 | 89.9908 | OK | Good | 27
Blandville | 49214 | 49214-Blandville | Lovelaceville | 49 | 129.149 |  | 2.4037 | 0.15486 | OK | 20.3 | 2020 | 436.7401 | 10.5072 | OK | Good | 6
Lovelaceville | 49224 | 49224-Lovelaceville | Lovelaceville | 49 | 527.2579 |  | 1.0249 | 1.303 | PSC | 57.9 | 2020 | 240.0159 | 76.162 | OK | More Info Required | 19 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 435 Tree failure from outside of ROW | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Cunningham | 49234 | 49234-Cunningham | Lovelaceville | 49 | 689.0315 |  | 1.7645 | 1.0522 | OK | 65 | 2020 | 361.4676 | 65.1596 | OK | Good | 35
Browns Plating | 50214 | 50214-Browns Plating | Krebs Station Road | 50 | 525.7765 |  | 1.3866 | 0.24535 | OK | 37.5 | 2016 | 288.226 | 19.98 | OK | Good | 25
Old US 45 | 50224 | 50224-Old US 45 | Krebs Station Road | 50 | 904.6562 |  | 2.3416 | 0.10722 | OK | 82.5 | 2016 | 400.8991 | 8.328 | OK | Good | 28
Clinton Road | 50234 | 50234-Clinton Rd | Krebs Station Road | 50 | 615.0458 |  | 1.3477 | 1.0113 | OK | 52.7 | 2016 | 220.6994 | 98.3423 | OK | Good | 35
Symsonia | 51214 | 51214-Symsonia | Freemont | 51 | 1014.6619 |  | 1.1565 | 1.4359 | PSC | 93.3 | 2019 | 149.4782 | 52.3337 | OK | More Info Required | 42 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 435 Tree failure from outside of ROW | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Mc Neil Lane | 51224 | 51224-McNeil Lane | Freemont | 51 | 338.1261 |  | 2.0316 | 0.13309 | OK | 40.4 | 2019 | 515.7262 | 11.5608 | OK | Good | 14
Freemont | 51244 | 51244-Freemont | Freemont | 51 | 339.4413 |  | 0.83373 | 0.050082 | OK | 25.7 | 2019 | 97.7906 | 4.696 | OK | Good | 7
Bonds Rd | 51254 | 51254-Bonds Rd | Freemont | 51 | 123.9685 |  | 1.6723 | 2.7023 | PSC | 17.5 | 2019 | 273.1015 | 168.3412 | OK | More Info Required | 6 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 435 Tree failure from outside of ROW | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Hwy 95 N to Hwy 62 | 54214 | 54214-Hwy 95 | Palma | 54 | 368.3639 |  | 0.76497 | 0.10316 | OK | 29.8 | 2019 | 73.3039 | 7.479 | OK | Good | 6
Draffenville | 54224 | 54224-Draffenville | Palma | 54 | 295.4642 |  | 0.30619 | 1.0729 | PSC | 21.3 | 2019 | 34.6814 | 78.1279 | PSC | More Info Required | 2 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 435 Tree failure from outside of ROW | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Palma | 54234 | 54234-Palma | Palma | 54 | 736.3897 |  | 1.0971 | 0.30554 | OK | 56.6 | 2019 | 102.4052 | 26.2144 | OK | Good | 31
Lowes | 61214 | 61214-Lowes | Kansas | 61 | 453.6769 |  | 1.1147 | 0.27332 | OK | 58.4 | 2016 | 285.1464 | 17.8916 | OK | Good | 13
US 45-Folsomdale | 61224 | 61224-US 45 Folsomdale | Kansas | 61 | 210.2577 |  | 0.71656 | 0.25207 | OK | 29.1 | 2016 | 77.4385 | 19.6093 | OK | Good | 8
Melber | 61234 | 61234-Melber | Kansas | 61 | 543.2423 |  | 1.0651 | 0.34975 | OK | 53.1 | 2016 | 271.965 | 37.9794 | OK | Good | 20
Pottsville | 61244 | 61244-Pottsville | Kansas | 61 | 503.4556 |  | 1.4087 | 4.0659 | PSC | 47.2 | 2016 | 286.5716 | 460.0982 | PSC | More Info Required | 43 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 435 Tree failure from outside of ROW | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Draffenville | 66214 | 66214-Draffenville | Draffenville | 66 | 489.6218 |  | 0.060723 | 0.022466 | OK | 29.4 | 2019 | 10.0517 | 1.736 | OK | Good | 7
Olivet Ch Rd | 74214 | 74214-Olivet Ch Rd | Olivet Church Road | 74 | 573.702 |  | 0.44895 | 3.0277 | PSC | 23.2 | 2015 | 45.7292 | 136.5047 | PSC | More Info Required | 9 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 435 Tree failure from outside of ROW | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Highland Ch Rd | 74224 | 74224-Highland Ch Rd | Olivet Church Road | 74 | 453.9226 |  | 0.98786 | 2.3969 | PSC | 36 | 2015 | 157.9317 | 131.6788 | OK | More Info Required | 16 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 435 Tree failure from outside of ROW | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Info Age Park | 74234 | 74234-Info Age Park | Olivet Church Road | 74 | 9 |  | 0.22473 | 2.1111 | PSC | 2.7 | 2015 | 69.7641 | 189.1111 | PSC | More Info Required | 5 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 435 Tree failure from outside of ROW | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Iuka | 76214 | 76214-Iuka | Grand Rivers | 76 | 300.4957 |  | 2.1994 | 1.7704 | OK | 48.2 | 2016 | 476.6386 | 125.5825 | OK | Good | 15
Smithland | 76224 | 76224-Smithland | Grand Rivers | 76 | 296.6648 |  | 2.4975 | 1.6281 | OK | 30.7 | 2016 | 330.5273 | 122.7075 | OK | Good | 17
Pelican-GR #1 | 76244 | 76244-Pelican GR #1 | Grand Rivers | 76 | 368.9628 |  | 1.8969 | 1.4744 | OK | 24.3 | 2016 | 294.4747 | 101.7962 | OK | Good | 14
Averitt-GR #2 | 76254 | 76254-Averitt GR #2 | Grand Rivers | 76 | 653.8768 |  | 3.1695 | 3.3003 | PSC | 44.1 | 2016 | 487.9585 | 282.3101 | OK | More Info Required | 20 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 435 Tree failure from outside of ROW | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Hansen Rd-Top Circuit | 7702 | 7702-Hansen Rd | Strawberry Hill | 77 | 663.4527 |  | 1.4777 | 1.0777 | OK | 30.2 | 2015 | 164.0378 | 8.923 | OK | Good | 11
Walmart-Hansen Rd Bottom | 7703 | 7703-Walmart | Strawberry Hill | 77 | 532.4585 |  | 0.45834 | 1.0048 | PSC | 9.6 | 2015 | 20.7872 | 25.9494 | PSC | More Info Required | 4 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 435 Tree failure from outside of ROW | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
CSI--Jas Sanders-Botom Cir | 7705 | 7705-CSI | Strawberry Hill | 77 | 87.0544 |  | 0.45249 | 1.0109 | PSC | 4.9 | 2015 | 21.0978 | 5.4449 | OK | More Info Required | 1 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 435 Tree failure from outside of ROW | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Hwy 60-Jas Sanders-Top Cir | 7706 | 7706-Hwy 60 | Strawberry Hill | 77 | 12.404 |  | 0.42961 | 0 | OK | 1.7 | 2015 | 23.3596 | 0 | OK | Good | 0
Hwy 95 North | 78221 | 78224-Possum Trot | Possum Trot | 78 | 541.1089 |  | 0.46932 | 0.23286 | OK | 42.2 | 2015 | 68.2177 | 29.9903 | OK | Good | 16
Possum Trot | 78234 | 78234-Hwy 95 | Possum Trot | 78 | 193.2665 |  | 1.1355 | 0.32597 | OK | 15 | 2015 | 251.5592 | 24.9034 | OK | Good | 9
Industrial Loop North | 78254 | 78254-Industrial Loop | Possum Trot | 78 | 211.4527 |  | 0.86452 | 0.38779 | OK | 28.6 | 2015 | 139.7121 | 51.2739 | OK | Good | 9
Coal Tek | 78264 | 78264-CoalTek | Possum Trot | 78 | 0 |  | 0.26667 | 0 | OK | 4 | 2015 | 60.2667 | 0 | OK | Good | 0
Maxon Rd | 79214 | 79214-Maxon Rd | Maxon | 79 | 256.0458 |  | 1.0011 | 0.25386 | OK | 15.4 | 2017 | 137.9295 | 26.4796 | OK | Good | 7
Express | 79224 | 79224-Express | Maxon | 79 | 320.9456 |  | 1.1558 | 2.1966 | PSC | 20.9 | 2017 | 179.5924 | 162.6974 | OK | More Info Required | 10 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 435 Tree failure from outside of ROW | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Industrial Park | 79234 | 79234-Industrial Park | Maxon | 79 | 3.037 |  | 0.33662 | 0.65854 | PSC | 0.8 | 2017 | 23.4462 | 28.3171 | PSC | More Info Required | 1 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 435 Tree failure from outside of ROW | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Electric Distribution Utility Annual Reliability Report
Additional pages may be attached as necessary
SECTION 7: VEGETATION MANAGEMENT PLAN REVIEW
JPEC had established a four (4) year cycle on right-of-way maintenance and employs a contractor to perform that cycle clearing. JPEC is looking at increasing that cycle due to the cost per mile of trimming and clearing trees triple. JPEC has begun reclaiming the full width of the ROW to help extend the process. JPEC will use outage data to track tree related outages and will prioritize ROW spending to those circuits that require it. JPEC also employs contract crews that handles "hot-spot" or service order trimming. We have experienced over the last couple of years an increased tree problem from "danger trees" (trees outside of right-of-way) falling into our ROW and tearing down lines and poles. We are working with our members and contractors to identify those danger trees for removal.
SECTION 8: UTILITY COMMENTS
Overall, JPEC's system averaged 99.98% reliable when factoring out major event days and power supply outages. JPEC reliability numbers ended at CAIDI - 93.4 mins, SAIFI - 1.17, and SAIDI - 108.1. All reliability indices were within the past 5 year average. Engineering and Operations is focusing on a number of different areas in 2021 including the continuing our ROW program, bird deterrents around the lakes area, substation maintenance program and improving sectionalizing system-wide.

## 2019 Circuit Details
Electric Distribution Utility Annual Reliability ReportA1:I44
SECTION 1: CONTACT INFORMATION
|  |  | UTILITY NAME | 1.1 | Jackson Purchase Energy Corporation
|  |  | REPORT PREPARED BY | 1.2 | Scott Ribble
|  |  | E-MAIL ADDRESS OF PREPARER | 1.3 | scott.ribble@jpenergy.com
|  |  | PHONE NUMBER OF PREPARER | 1.4 | 270-442-7321
SECTION 2: REPORT YEAR
|  |  | CALENDAR YEAR OF REPORT | 2.1 | 2019
SECTION 3: MAJOR EVENT DAYS
|  |  | TMED | 3.1 | 8.86
|  |  | FIRST DATE USED TO DETERMINE TMED | 3.2 | 2014-01-01
|  |  | LAST DATE USED TO DETERMINE TMED | 3.3 | 2018-12-31
|  |  | NUMBER OF MED IN REPORT YEAR | 3.4 | 4
NOTE: Per IEEE 1366 TMED should be calculated using the daily SAIDI values for the five prior years. If five years of data are not available, then utilities should use what is available until five years are accumulated.
SECTION 4: SYSTEM RELIABILITY RESULTS
System - Wide Information
| Total Customers | 30044 |  |  | Total Circuits | 91
Excluding MED
| 5 Year Average |  |  |  | Reporting Year
| SAIDI | 113.56 |  |  | SAIDI | 137.356
| SAIFI | 1.18 |  |  | SAIFI | 1.5619
Including MED
| 5 Year Average |  |  |  | Reporting Year
| SAIDI | 351.16 |  |  | SAIDI | 404.293
| SAIFI | 1.75 |  |  | SAIFI | 2.3401
SECTION 5: CIRCUIT REPORTING
Circuit Name | Circuit Number | Circuit Location | Substation Name | Substation Number | Avg # of Customers |  | Previous 5 Year Average SAIFI | Current Year SAIFI Excluding MED | Comparison | Circuit Length | Date of Last Trim For Circuit | Previous 5 Year Average SAIDI | Current Year SAIDI Excluding MED |  |  | # of Outages | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | %
Hampton-South | 5214 | 05214-Hampton South | Joy | 5 | 194.6193 |  | 3.0408 | 1.0225 | OK | 57.5 | 2016 | 572.3712 | 85.4746 | OK | Good | 7
Carrsville | 5244 | 05244-Carrsville | Joy | 5 | 73.017 |  | 1.2041 | 1.9721 | PSC | 10.9 | 2016 | 244.8857 | 550.1181 | PSC | More Info Required | 3 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 435 Tree failure from outside of ROW | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Lola | 5254 | 05254-Lola | Joy | 5 | 298.6335 |  | 1.2416 | 2.1933 | PSC | 56.5 | 2016 | 354.6918 | 120.8036 | OK | More Info Required | 20 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 435 Tree failure from outside of ROW | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Hampton | 14214 | 14214-Hampton | Burna | 14 | 87.5781 |  | 0.9322 | 0.011418 | OK | 12.7 | 2015 | 262.9278 | 1.2103 | OK | Good | 1
Salem | 14244 | 14244-Salem | Burna | 14 | 316.3589 |  | 0.95713 | 0.19282 | OK | 53 | 2015 | 192.4056 | 94.4212 | OK | Good | 18
Smithland | 14254 | 14254-Smithland | Burna | 14 | 332.7288 |  | 1.899 | 3.8019 | PSC | 69.7 | 2015 | 361.5929 | 452.7562 | PSC | More Info Required | 24 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 435 Tree failure from outside of ROW | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Pinckneyville | 15224 | 15224-Pinckneyville | Cumberland | 15 | 113.6712 |  | 1.4917 | 0.63341 | OK | 28.9 | 2015 | 220.5859 | 194.9394 | OK | Good | 8
Quarry | 15234 | 15234-Quarry | Cumberland | 15 | 30.6438 |  | 0.33389 | 2.8391 | PSC | 5.5 | 2015 | 132.6656 | 459.5704 | PSC | More Info Required | 3 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 435 Tree failure from outside of ROW | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Monkey's Eyebrow | 19214 | 19214-Monkeys Eyebrow | Ragland | 19 | 253.3671 |  | 1.001 | 2.3444 | PSC | 51 | 2017 | 155.7616 | 317.1524 | PSC | More Info Required | 31 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 435 Tree failure from outside of ROW | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Ragland | 19224 | 19224-Ragland | Ragland | 19 | 228.7205 |  | 0.67222 | 0.23172 | OK | 33.7 | 2017 | 198.5764 | 35.0296 | OK | Good | 10
Damron's | 26214 | 26214-Damrons | LaCenter | 26 | 229.411 |  | 0.94714 | 1.5344 | PSC | 39.7 | 2015 | 263.8559 | 89.8867 | OK | More Info Required | 14 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 435 Tree failure from outside of ROW | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Oscar | 26224 | 26224-Oscar | LaCenter | 26 | 362.5726 |  | 2.1607 | 1.8176 | OK | 70 | 2015 | 546.9875 | 250.1485 | OK | Good | 27
Hobbs Rd | 28214 | 28214-Hobbs Rd | Kevil | 28 | 554.3123 |  | 2.0613 | 0.23813 | OK | 53.6 | 2017 | 329.188 | 26.0846 | OK | Good | 35
Woodville Rd | 28224 | 28224-Woodville Rd | Kevil | 28 | 475.3014 |  | 1.2848 | 0.40606 | OK | 55.7 | 2017 | 191.4792 | 59.741 | OK | Good | 21
Kelley Rd | 28234 | 28234-Kelley Rd | Kevil | 28 | 408.5589 |  | 1.3067 | 1.3046 | OK | 46.4 | 2017 | 185.6403 | 114.4388 | OK | Good | 21
High Point | 2901 | 2901-High Point | High Point | 29 | 197.0822 |  | 1.3371 | 1.5932 | PSC | 21.4 | 2015 | 177.2797 | 154.8998 | OK | More Info Required | 29 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 435 Tree failure from outside of ROW | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Carneal Rd | 2902 | 2902-Carneal Rd | High Point | 29 | 247.5644 |  | 2.0804 | 2.7104 | PSC | 32.5 | 2015 | 496.0513 | 181.6982 | OK | More Info Required | 31 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 435 Tree failure from outside of ROW | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Essex | 2903 | 2903-Essex | High Point | 29 | 0 |  | 0 | 0 | OK | 0.04 | 2015 | 0 | 0 | OK | Good | 0
Conrad Heights | 30224 | 30224-Conrad Heights | Coleman Road | 30 | 392.2247 |  | 1.472 | 0.52521 | OK | 18.2 | 2015 | 255.7946 | 41.3284 | OK | Good | 13
Holt Rd | 30244 | 30244-Hwy 60 Business | Coleman Road | 30 | 103.4658 |  | 0.56066 | 0.28995 | OK | 7.6 | 2015 | 40.2568 | 13.908 | OK | Good | 6
Ky Oaks Mall | 30254 | 30254-KY Oaks Mall | Coleman Road | 30 | 0 |  | 0.3922 | 0 | OK | 3.9 | 2015 | 32.9625 | 0 | OK | Good | 0
US 60 East | 3102 | 3102-US 60 East | Ledbetter | 31 | 316.589 |  | 0.66653 | 0.34114 | OK | 35.5 | 2016 | 73.1858 | 20.6419 | OK | Good | 15
River Crossing | 3103 | 3103-River Crossing | Ledbetter | 31 | 34.0055 |  | 0.2064 | 1.1469 | PSC | 5.2 | 2016 | 22.5976 | 76.5759 | PSC | More Info Required | 2 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 435 Tree failure from outside of ROW | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Ledbetter | 3104 | 3104-Ledbetter | Ledbetter | 31 | 1005.7863 |  | 1.1899 | 1.4605 | PSC | 61.6 | 2016 | 196.52 | 101.1229 | OK | More Info Required | 47 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 435 Tree failure from outside of ROW | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Smithland | 3201 | 3201-Smithland | Smithland | 32 | 381.3945 |  | 1.9927 | 2.2129 | PSC | 67.9 | 2019 | 285.733 | 234.9509 | OK | More Info Required | 22 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 435 Tree failure from outside of ROW | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Tiline | 3202 | 3202-Tiline | Smithland | 32 | 563.5041 |  | 3.6097 | 1.7533 | OK | 109.5 | 2019 | 485.2637 | 304.8248 | OK | Good | 53
Mitchell Store | 3204 | 3204-Mitchell Store | Smithland | 32 | 388.3671 |  | 2.8361 | 2.7603 | OK | 56.2 | 2019 | 515.8212 | 440.6861 | OK | Good | 24
Airport | 3901 | 3901-Airport | Little Union | 39 | 543.9205 |  | 1.7969 | 2.664 | PSC | 35.9 | 2017 | 167.8193 | 258.6187 | PSC | More Info Required | 29 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 435 Tree failure from outside of ROW | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
US 60 West | 3902 | 3902-US 60 West | Little Union | 39 | 471.5041 |  | 1.4704 | 1.2725 | OK | 36.9 | 2017 | 259.9412 | 69.9506 | OK | Good | 12
US 60 East-K O M | 3903 | 3903-US 60 East Mall | Little Union | 39 | 155.9151 |  | 0.5325 | 0.22448 | OK | 10.1 | 2017 | 42.9045 | 32.2483 | OK | Good | 9
Roy Lee Rd | 3904 | 3904-Roy Lee Rd | Little Union | 39 | 470.526 |  | 1.3888 | 0.14239 | OK | 52.3 | 2017 | 447.6768 | 17.6271 | OK | Good | 16
Husbands Rd | 40224 | 40224-Husbands Rd | Husbands Road | 40 | 765.1973 |  | 1.5014 | 1.1448 | OK | 44.3 | 2018 | 280.9032 | 126.9228 | OK | Good | 23
Lydon Rd | 40234 | 40234-Lydon Rd | Husbands Road | 40 | 454.2849 |  | 0.81064 | 1.1116 | PSC | 32.1 | 2018 | 107.2236 | 20.6941 | OK | More Info Required | 12 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 435 Tree failure from outside of ROW | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Clarkline Rd | 40244 | 40244-Clarkline Rd | Husbands Road | 40 | 295.4356 |  | 0.7649 | 0.44341 | OK | 26.6 | 2018 | 83.3794 | 37.7273 | OK | Good | 18
Ken Mar Rd | 41214 | 41214-Ken Mar Rd | Reidland | 41 | 325.2493 |  | 1.3288 | 0.29823 | OK | 20 | 2018 | 119.5148 | 28.2952 | OK | Good | 9
Reidland Water | 41224 | 41224-Reidland Water | Reidland | 41 | 52.874 |  | 0.79011 | 0.056739 | OK | 2.9 | 2018 | 92.6097 | 9.3619 | OK | Good | 1
Epperson Rd | 41234 | 41234-Epperson Rd | Reidland | 41 | 203.1205 |  | 0.44225 | 0.32985 | OK | 10.1 | 2018 | 38.8355 | 21.8294 | OK | Good | 6
Walker Boat Yard | 41244 | 41244-Walker Boat Yard | Reidland | 41 | 103.6329 |  | 0.80416 | 0.19299 | OK | 11.6 | 2018 | 75.319 | 16.3944 | OK | Good | 5
Proform | 42214 | 42214-Proform | Culp | 42 | 428.4767 |  | 1.0511 | 1.6034 | PSC | 25.7 | 2018 | 203.1346 | 95.9562 | OK | More Info Required | 23 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 435 Tree failure from outside of ROW | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Little Cypress | 42224 | 42224-Little Cypress | Culp | 42 | 50.9616 |  | 0.48927 | 1.0596 | PSC | 8.1 | 2018 | 143.4503 | 52.4708 | OK | More Info Required | 4 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 435 Tree failure from outside of ROW | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Possum Trot | 42234 | 42234-Possum Trot | Culp | 42 | 203.3041 |  | 0.73127 | 1.8593 | PSC | 18.7 | 2018 | 239.4465 | 214.6735 | OK | More Info Required | 13 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 435 Tree failure from outside of ROW | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Sharpe | 42244 | 42244-Sharpe | Culp | 42 | 1072.7753 |  | 0.84373 | 1.2006 | PSC | 78.5 | 2018 | 70.5578 | 74.0556 | PSC | More Info Required | 56 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 435 Tree failure from outside of ROW | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
CC/Hwy 95 | 43214 | 43214-Hwy 95 | Calvert City | 43 | 240.3973 |  | 0.51157 | 1.2563 | PSC | 18.6 | 2017 | 119.1778 | 248.9463 | PSC | More Info Required | 15 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 435 Tree failure from outside of ROW | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
CC Hgts | 43224 | 43224-Calvert Heights | Calvert City | 43 | 648.8164 |  | 0.65266 | 1.6492 | PSC | 28.2 | 2017 | 95.8541 | 121.1252 | PSC | More Info Required | 29 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 435 Tree failure from outside of ROW | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Gilbertsville | 43234 | 43234-Gilbertsville | Calvert City | 43 | 347.8493 |  | 0.39681 | 0.16386 | OK | 23 | 2017 | 102.4445 | 15.2796 | OK | Good | 13
CC Ind Park | 43244 | 43244-Industrial Park | Calvert City | 43 | 27 |  | 0.41393 | 0.037037 | OK | 4.9 | 2017 | 86.8232 | 5.7778 | OK | Good | 1
Vulcan Pit | 45224 | 45224-Vulcan Pit | Vulcan | 45 | 0 |  | 0 | 0 | OK | 2.4 |  | 0 | 0 | OK | Good | 0
Vulcan 1-Rock Crusher | 45234 | 45234-Vulcan1 Rock Crusher | Vulcan | 45 | 2 |  | 0.3 | 2 | PSC | 1.3 |  | 38 | 394.5 | PSC | More Info Required | 4 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 435 Tree failure from outside of ROW | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Kinder Morgan 1 | 45244 | 45244-Kinder Morgan 1 | Vulcan | 45 | 33.9234 |  | 1.0101 | 2.8889 | PSC | 7.7 |  | 156.8098 | 721.0656 | PSC | More Info Required | 3 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 435 Tree failure from outside of ROW | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Vulcan 2 Hwy 62 | 45254 | 45254-Vulcan 2 Hwy 62 | Vulcan | 45 | 3 |  | 0.36667 | 1.3333 | PSC | 5.5 |  | 56.5667 | 137.3333 | PSC | More Info Required | 2 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 435 Tree failure from outside of ROW | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Hinkleville | 47210 | 47214-Hinkleville | New York | 47 | 265.5562 |  | 2.4457 | 4.7787 | PSC | 44.6 | 2017 | 458.865 | 606.0827 | PSC | More Info Required | 21 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 435 Tree failure from outside of ROW | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
US 286 East-Gage | 47224 | 47224-US 286 East Gage | New York | 47 | 260.914 |  | 1.4541 | 0.18014 | OK | 45.4 | 2017 | 282.6211 | 58.6975 | OK | Good | 30
Blandville | 47234 | 47234-Blandville | New York | 47 | 223.0036 |  | 2.8452 | 2.0583 | OK | 30.2 | 2017 | 849.4741 | 255.0094 | OK | Good | 10
Wickliffe | 47244 | 47244-Wickliffe | New York | 47 | 347.8889 |  | 1.9696 | 0.53178 | OK | 49.2 | 2017 | 444.9677 | 66.0096 | OK | Good | 20
Slater | 47254 | 47254-Slater | New York | 47 | 345.3799 |  | 2.8933 | 0.65435 | OK | 67.9 | 2017 | 539.8917 | 101.6301 | OK | Good | 30
Blandville | 4901 | 4901-Blandville | Lovelaceville | 49 | 129.4274 |  | 1.9585 | 2.2638 | PSC | 20.3 | 2015 | 382.2523 | 275.3436 | OK | More Info Required | 17 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 435 Tree failure from outside of ROW | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Lovelaceville | 4902 | 4902-Lovelaceville | Lovelaceville | 49 | 521.4274 |  | 1.0938 | 0.11507 | OK | 57.8 | 2015 | 244.0659 | 16.7885 | OK | Good | 20
Cunningham | 4903 | 4903-Cunningham | Lovelaceville | 49 | 525.7068 |  | 2.1426 | 0.26441 | OK | 65 | 2015 | 390.8209 | 39.9367 | OK | Good | 15
Browns Plating | 5001 | 5001-Browns Plating | Krebs Station Road | 50 | 521.5808 |  | 1.5153 | 1.5185 | PSC | 37.5 | 2016 | 306.1377 | 79.5255 | OK | More Info Required | 16 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 435 Tree failure from outside of ROW | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Old US 45 | 5002 | 5002-Old US 45 | Krebs Station Road | 50 | 866.9836 |  | 2.8411 | 0.19724 | OK | 82.5 | 2016 | 415.5318 | 16.4778 | OK | Good | 35
Clinton Road | 5003 | 5003-Clinton Rd | Krebs Station Road | 50 | 602.8521 |  | 1.3389 | 1.6405 | PSC | 52.7 | 2016 | 178.7281 | 339.5012 | PSC | More Info Required | 44 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 435 Tree failure from outside of ROW | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Symsonia | 51214 | 51214-Symsonia | Freemont | 51 | 1013.7068 |  | 0.86724 | 1.7619 | PSC | 93.3 | 2019 | 124.8173 | 168.018 | PSC | More Info Required | 42 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 435 Tree failure from outside of ROW | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Mc Neil Lane | 51224 | 51224-McNeil Lane | Freemont | 51 | 379.8986 |  | 2.2054 | 2.0269 | OK | 40.4 | 2019 | 516.5542 | 217.7344 | OK | Good | 25
Freemont | 51244 | 51244-Freemont | Freemont | 51 | 339.7699 |  | 0.79555 | 0.34435 | OK | 25.7 | 2019 | 92.1992 | 44.8039 | OK | Good | 16
Bonds Rd | 51254 | 51254-Bonds Rd | Freemont | 51 | 119.9808 |  | 1.136 | 3.0338 | PSC | 17.5 | 2019 | 185.7696 | 485.5026 | PSC | More Info Required | 10 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 435 Tree failure from outside of ROW | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Hwy 95 N to Hwy 62 | 54214 | 54214-Hwy 95 | Palma | 54 | 359.5233 |  | 1.6534 | 0.086225 | OK | 29.8 | 2019 | 163.9314 | 12.9088 | OK | Good | 16
Draffenville | 54224 | 54224-Draffenville | Palma | 54 | 293.0384 |  | 0.28389 | 0.1911 | OK | 21.3 | 2019 | 32.1478 | 19.2671 | OK | Good | 16
Palma | 54234 | 54234-Palma | Palma | 54 | 730 |  | 1.3101 | 1.263 | OK | 56.6 | 2019 | 113.2669 | 71.7233 | OK | Good | 41
Lowes | 6101 | 6101-Lowes | Kansas | 61 | 449.5479 |  | 1.0148 | 0.67623 | OK | 58.4 | 2016 | 268.387 | 104.1179 | OK | Good | 22
US 45-Folsomdale | 6102 | 6102-US 45 Folsomdale | Kansas | 61 | 212.5836 |  | 0.7121 | 1.1054 | PSC | 29.1 | 2016 | 85.3536 | 74.3519 | OK | More Info Required | 12 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 435 Tree failure from outside of ROW | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Melber | 6103 | 6103-Melber | Kansas | 61 | 536.7836 |  | 0.89882 | 0.97432 | PSC | 53.1 | 2016 | 255.3426 | 96.0052 | OK | More Info Required | 35 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 435 Tree failure from outside of ROW | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Pottsville | 6104 | 6104-Pottsville | Kansas | 61 | 361.9425 |  | 1.9306 | 1.0913 | OK | 47.2 | 2016 | 345.2666 | 109.3102 | OK | Good | 38
Draffenville | 66214 | 66214-Draffenville | Draffenville | 66 | 483.874 |  | 0.060958 | 0.095066 | PSC | 29.3 | 2019 | 8.5582 | 12.8174 | PSC | More Info Required | 11 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 435 Tree failure from outside of ROW | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Olivet Ch Rd | 74214 | 74214-Olivet Ch Rd | Olivet Church Road | 74 | 563.4 |  | 0.4449 | 1.0259 | PSC | 23.2 | 2015 | 43.8759 | 58.9457 | PSC | More Info Required | 11 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 435 Tree failure from outside of ROW | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Highland Ch Rd | 74224 | 74224-Highland Ch Rd | Olivet Church Road | 74 | 454.8959 |  | 0.95876 | 0.59794 | OK | 36 | 2015 | 155.7015 | 45.9182 | OK | Good | 35
Info Age Park | 74234 | 74234-Info Age Park | Olivet Church Road | 74 | 8.0438 |  | 0.175 | 0.24864 | PSC | 2.7 | 2015 | 49.525 | 101.1955 | PSC | More Info Required | 2 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 435 Tree failure from outside of ROW | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Iuka | 7601 | 7601-Iuka | Grand Rivers | 76 | 299.7479 |  | 1.9355 | 1.3645 | OK | 47.8 | 2016 | 449.0678 | 142.026 | OK | Good | 16
Smithland | 7602 | 7602-Smithland | Grand Rivers | 76 | 290.674 |  | 2.3244 | 1.2385 | OK | 30.7 | 2016 | 315.134 | 114.3274 | OK | Good | 15
Pelican-GR #1 | 7604 | 7604-Pelican GR #1 | Grand Rivers | 76 | 368.7479 |  | 1.3509 | 2.8502 | PSC | 24.3 | 2016 | 245.7733 | 255.036 | PSC | More Info Required | 16 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 435 Tree failure from outside of ROW | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Averitt-GR #2 | 7605 | 7605-Averitt GR #2 | Grand Rivers | 76 | 650.8384 |  | 1.9657 | 6.3011 | PSC | 44 | 2016 | 340.327 | 758.7214 | PSC | More Info Required | 37 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 435 Tree failure from outside of ROW | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Hansen Rd-Top Circuit | 7702 | 7702-Hansen Rd | Strawberry Hill | 77 | 651.3205 |  | 1.2758 | 1.5476 | PSC | 30.2 | 2015 | 149.9501 | 126.308 | OK | More Info Required | 33 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 435 Tree failure from outside of ROW | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Walmart-Hansen Rd Bottom | 7703 | 7703-Walmart | Strawberry Hill | 77 | 527.8219 |  | 0.47992 | 0.02084 | OK | 9.6 | 2015 | 21.3874 | 3.9521 | OK | Good | 2
CSI--Jas Sanders-Botom Cir | 7705 | 7705-CSI | Strawberry Hill | 77 | 0 |  | 0.70517 | 0 | OK | 4.9 | 2015 | 35.7002 | 0 | OK | Good | 0
Hwy 60-Jas Sanders-Top Cir | 7706 | 7706-Hwy 60 | Strawberry Hill | 77 | 0 |  | 0.42961 | 0 | OK | 1.7 | 2015 | 23.3596 | 0 | OK | Good | 0
Hwy 95 North | 7802 | 7802-Possum Trot | Possum Trot | 78 | 536.6329 |  | 0.28164 | 1.2057 | PSC | 42.2 | 2015 | 41.4407 | 160.6797 | PSC | More Info Required | 23 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 435 Tree failure from outside of ROW | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Possum Trot | 7803 | 7803-Hwy 95 | Possum Trot | 78 | 194.7753 |  | 0.71459 | 2.1409 | PSC | 15 | 2015 | 207.7644 | 221.0701 | PSC | More Info Required | 13 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 435 Tree failure from outside of ROW | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Industrial Loop North | 7805 | 7805-Industrial Loop | Possum Trot | 78 | 208.2986 |  | 1.0975 | 1.6899 | PSC | 28.6 | 2015 | 151.0664 | 201.0623 | PSC | More Info Required | 20 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 435 Tree failure from outside of ROW | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Coal Tek | 7806 | 7806-CoalTek | Possum Trot | 78 | 3 |  | 0.3091 | 0.66667 | PSC | 4 | 2015 | 65.1946 | 94 | PSC | More Info Required | 1 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 435 Tree failure from outside of ROW | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Maxon Rd | 79214 | 79214-Maxon Rd | Maxon | 79 | 252.3589 |  | 0.63412 | 2.2349 | PSC | 15.4 | 2017 | 110.4078 | 160.2083 | PSC | More Info Required | 8 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 435 Tree failure from outside of ROW | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Express | 79224 | 79224-Express | Maxon | 79 | 307.7562 |  | 1.1696 | 0.025995 | OK | 20.9 | 2017 | 182.0581 | 3.4898 | OK | Good | 4
Industrial Park | 79234 | 79234-Industrial Park | Maxon | 79 | 0 |  | 0.33662 | 0 | OK | 0.8 | 2017 | 23.4462 | 0 | OK | Good | 0
Electric Distribution Utility Annual Reliability Report
Additional pages may be attached as necessary
SECTION 7: VEGETATION MANAGEMENT PLAN REVIEW
JPEC had established a four (4) year cycle on right-of-way maintenance and employs a contractor to perform that cycle clearing. JPEC is looking at increasing that cycle due to the cost per mile of trimming and clearing trees triple. JPEC has begun reclaiming the full width of the ROW to help extend the process. JPEC will use outage data to track tree related outages and will prioritize ROW spending to those circuits that require it. JPEC also employs contract crews that handles "hot-spot" or service order trimming. We have experienced over the last couple of years an increased tree problem from "danger trees" (trees outside of right-of-way) falling into our ROW and tearing down lines and poles. We are working with our members and contractors to identify those danger trees for removal.
SECTION 8: UTILITY COMMENTS
Overall, JPEC's system averaged 99.98% reliable when factoring out major event days and power supply outages. JPEC reliability numbers ended at CAIDI - 95.3 mins, SAIFI - 1.158, and SAIDI - 110.3. All reliability indices were within the past 5 year average. Engineering and Operations is focusing on a number of different areas in 2020 and beyond including the widening of ROW, bird deterrents around the lakes area, substation maintenance program and a new sectionalizing study.

## 2018 Circuit Details
Electric Distribution Utility Annual Reliability Report
SECTION 1: CONTACT INFORMATION
|  |  | UTILITY NAME | 1.1 | Jackson Purchase Energy Corporation
|  |  | REPORT PREPARED BY | 1.2 | Scott Ribble
|  |  | E-MAIL ADDRESS OF PREPARER | 1.3 | scott.ribble@jpenergy.com
|  |  | PHONE NUMBER OF PREPARER | 1.4 | 270-442-7321
SECTION 2: REPORT YEAR
|  |  | CALENDAR YEAR OF REPORT | 2.1 | 2018
SECTION 3: MAJOR EVENT DAYS
|  |  | TMED | 3.1 | 8.38
|  |  | FIRST DATE USED TO DETERMINE TMED | 3.2 | 2013-01-01
|  |  | LAST DATE USED TO DETERMINE TMED | 3.3 | 2017-12-31
|  |  | NUMBER OF MED IN REPORT YEAR | 3.4 | 3
NOTE: Per IEEE 1366 TMED should be calculated using the daily SAIDI values for the five prior years. If five years of data are not available, then utilities should use what is available until five years are accumulated.
SECTION 4: SYSTEM RELIABILITY RESULTS
System - Wide Information
| Total Customers | 29752 |  |  | Total Circuits | 91
Excluding MED
| 5 Year Average |  |  |  | Reporting Year
| SAIDI | 111.2 |  |  | SAIDI | 122.816
| SAIFI | 1.2 |  |  | SAIFI | 1.2121
Including MED
| 5 Year Average |  |  |  | Reporting Year
| SAIDI | 295.41 |  |  | SAIDI | 488.576
| SAIFI | 1.61 |  |  | SAIFI | 1.7691
SECTION 5: CIRCUIT REPORTING
Circuit Name | Circuit Number | Circuit Location | Substation Name | Substation Number | Avg # of Customers |  | Previous 5 Year Average SAIFI | Current Year SAIFI Excluding MED | Comparison | Circuit Length | Date of Last Trim For Circuit | Previous 5 Year Average SAIDI | Current Year SAIDI Excluding MED |  |  | # of Outages | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | %
Hampton-South | 501 | 0501-Hampton South | Joy | 5 | 196.1315 |  | 2.577 | 1.2696 | OK | 57.5 | 2016 | 417.0033 | 129.9944 | OK | Good | 7
Carrsville | 504 | 0504-Carrsville | Joy | 5 | 72.6247 |  | 1.3978 | 0.068847 | OK | 10.9 | 2016 | 262.1849 | 10.7264 | OK | Good | 3
Lola | 505 | 0505-Lola | Joy | 5 | 298.8986 |  | 1.0691 | 0.25092 | OK | 56.7 | 2016 | 250.7705 | 40.4619 | OK | Good | 15
Hampton | 14214 | 14214-Hampton | Burna | 14 | 88.1562 |  | 0.54874 | 1.1797 | PSC | 12.8 | 2015 | 125.8938 | 91.4287 | OK | More Info Required | 5 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Salem | 14244 | 14244-Salem | Burna | 14 | 319.189 |  | 0.25203 | 2.6567 | PSC | 52.5 | 2015 | 52.5484 | 200.9186 | PSC | More Info Required | 19 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Smithland | 14254 | 14254-Smithland | Burna | 14 | 334.5123 |  | 1.3126 | 2.8848 | PSC | 69.97 | 2015 | 173.002 | 454.2224 | PSC | More Info Required | 23 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Pinckneyville | 15224 | 15224-Pinckneyville | Cumberland | 15 | 113.0959 |  | 1.71 | 0.24758 | OK | 28.8 | 2015 | 289.3824 | 28.5598 | OK | Good | 6
Quarry | 15234 | 15234-Quarry | Cumberland | 15 | 29.9836 |  | 0.55639 | 0.033352 | OK | 5.29 | 2015 | 67.63 | 3.9355 | OK | Good | 1
Monkey's Eyebrow | 19214 | 19214-Monkeys Eyebrow | Ragland | 19 | 259.2247 |  | 1.2311 | 0.70209 | OK | 50.9 | 2017 | 159.4001 | 95.8126 | OK | Good | 24
Ragland | 19224 | 19224-Ragland | Ragland | 19 | 235.5068 |  | 0.41873 | 1.1847 | PSC | 31.2 | 2017 | 31.7947 | 426.9897 | PSC | More Info Required | 11 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Damron's | 26214 | 26214-Damrons | LaCenter | 26 | 229.9352 |  | 2.5038 | 0.4436 | OK | 39.49 | 2015 | 309.2262 | 22.6933 | OK | Good | 19
Oscar | 26224 | 26224-Oscar | LaCenter | 26 | 363.1208 |  | 1.8109 | 1.7845 | OK | 69.9 | 2015 | 462.5496 | 158.7764 | OK | Good | 23
Hobbs Rd | 28214 | 28214-Hobbs Rd | Kevil | 28 | 554.5994 |  | 1.6506 | 2.1565 | PSC | 53.6 | 2017 | 221.7036 | 130.532 | OK | More Info Required | 27 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Woodville Rd | 28224 | 28224-Woodville Rd | Kevil | 28 | 492.5608 |  | 1.3461 | 1.1592 | OK | 55.3 | 2017 | 176.4051 | 100.2658 | OK | Good | 22
Kelley Rd | 28234 | 28234-Kelley Rd | Kevil | 28 | 408.5718 |  | 1.9698 | 0.15909 | OK | 46.2 | 2017 | 296.9221 | 10.1353 | OK | Good | 9
High Point | 2901 | 2901-High Point | High Point | 29 | 191.926 |  | 1.6437 | 0.18757 | OK | 21.47 | 2015 | 149.0062 | 12.6247 | OK | Good | 7
Carneal Rd | 2902 | 2902-Carneal Rd | High Point | 29 | 232.5562 |  | 2.0198 | 2.0081 | OK | 32.48 | 2015 | 356.6788 | 312.2171 | OK | Good | 19
Essex | 2903 | 2903-Essex | High Point | 29 | 0 |  | 0 | 0 | OK | 0.04 | 2015 | 0 | 0 | OK | Good | 0
Conrad Heights | 3002 | 3002-Conrad Heights | Coleman Road | 30 | 392.2329 |  | 1.3959 | 1.1396 | OK | 18.1 | 2015 | 128.1799 | 107.7855 | OK | Good | 18
Holt Rd | 3004 | 3004-Hwy 60 Business | Coleman Road | 30 | 0 |  | 0.59248 | 0 | OK | 7.6 | 2015 | 41.4659 | 0 | OK | Good | 0
Ky Oaks Mall | 3005 | 3005-KY Oaks Mall | Coleman Road | 30 | 84.7205 |  | 0.39001 | 0.023607 | OK | 3.85 | 2015 | 32.7192 | 2.4315 | OK | Good | 1
US 60 East | 3102 | 3102-US 60 East | Ledbetter | 31 | 313.9068 |  | 1.1697 | 0.21662 | OK | 35.46 | 2016 | 87.6421 | 17.0815 | OK | Good | 10
River Crossing | 3103 | 3103-River Crossing | Ledbetter | 31 | 0 |  | 0.22458 | 0 | OK | 5.17 | 2016 | 23.7431 | 0 | OK | Good | 0
Ledbetter | 3104 | 3104-Ledbetter | Ledbetter | 31 | 1006.7507 |  | 1.2279 | 0.20462 | OK | 62 | 2016 | 100.049 | 27.6911 | OK | Good | 44
Smithland | 3201 | 3201-Smithland | Smithland | 32 | 384.5397 |  | 2.5319 | 0.69954 | OK | 29.8 | 2018 | 276.4959 | 71.6883 | OK | Good | 24
Tiline | 3202 | 3202-Tiline | Smithland | 32 | 561.6548 |  | 3.5621 | 3.7746 | PSC | 109.1 | 2018 | 429.1171 | 427.9586 | OK | More Info Required | 43 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Mitchell Store | 3204 | 3204-Mitchell Store | Smithland | 32 | 378.2055 |  | 2.0182 | 3.9899 | PSC | 56.3 | 2018 | 318.1127 | 444.7001 | PSC | More Info Required | 19 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Airport | 3901 | 3901-Airport | Little Union | 39 | 542.6429 |  | 1.3243 | 2.6095 | PSC | 35.9 | 2017 | 107.0983 | 179.2026 | PSC | More Info Required | 30 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
US 60 West | 3902 | 3902-US 60 West | Little Union | 39 | 466.3808 |  | 1.464 | 0.461 | OK | 36.8 | 2017 | 256.7378 | 65.8989 | OK | Good | 29
US 60 East-K O M | 3903 | 3903-US 60 East Mall | Little Union | 39 | 152.463 |  | 1.5873 | 0.15742 | OK | 10.68 | 2017 | 77.0028 | 29.4629 | OK | Good | 2
Roy Lee Rd | 3904 | 3904-Roy Lee Rd | Little Union | 39 | 468.9233 |  | 1.4162 | 1.3755 | OK | 52.05 | 2017 | 235.4467 | 154.8675 | OK | Good | 22
Husbands Rd | 40224 | 40224-Husbands Rd | Husbands Road | 40 | 771.5096 |  | 1.0286 | 1.3726 | PSC | 44.28 | 2018 | 88.1332 | 186.8493 | PSC | More Info Required | 24 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Lydon Rd | 40234 | 40234-Lydon Rd | Husbands Road | 40 | 454.1616 |  | 0.51219 | 1.1714 | PSC | 31.88 | 2018 | 35.3302 | 158.492 | PSC | More Info Required | 25 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Clarkline Rd | 40244 | 40244-Clarkline Rd | Husbands Road | 40 | 299.9068 |  | 0.56149 | 1.1103 | PSC | 26.46 | 2018 | 50.389 | 140.7704 | PSC | More Info Required | 11 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Ken Mar Rd | 4101 | 4101-Ken Mar Rd | Reidland | 41 | 323.6795 |  | 0.57961 | 1.2636 | PSC | 19.85 | 2018 | 33.7999 | 114.0264 | PSC | More Info Required | 15 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Reidland Water | 4102 | 4102-Reidland Water | Reidland | 41 | 53.8986 |  | 0.63957 | 0.76069 | PSC | 2.9 | 2018 | 81.7726 | 54.417 | OK | More Info Required | 5 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Epperson Rd | 4103 | 4103-Epperson Rd | Reidland | 41 | 204.0329 |  | 0.54785 | 0.37739 | OK | 10.1 | 2018 | 44.4562 | 32.828 | OK | Good | 10
Walker Boat Yard | 4104 | 4104-Walker Boat Yard | Reidland | 41 | 102.4548 |  | 0.61202 | 0.5173 | OK | 11.7 | 2018 | 51.9291 | 38.0558 | OK | Good | 8
Proform | 42214 | 42214-Proform | Culp | 42 | 416.7479 |  | 1.0034 | 0.071986 | OK | 25.75 | 2018 | 72.6312 | 10.354 | OK | Good | 9
Little Cypress | 42224 | 42224-Little Cypress | Culp | 42 | 0 |  | 0.50888 | 0 | OK | 8.2 | 2018 | 144.3679 | 0 | OK | Good | 0
Possum Trot | 42234 | 42234-Possum Trot | Culp | 42 | 205.274 |  | 0.49422 | 0.51151 | PSC | 18.5 | 2018 | 58.9515 | 30.4179 | OK | More Info Required | 9 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Sharpe | 42244 | 42244-Sharpe | Culp | 42 | 1069.8959 |  | 0.95709 | 0.32246 | OK | 77.87 | 2018 | 51.2386 | 38.8496 | OK | Good | 42
CC/Hwy 95 | 4301 | 4301-Hwy 95 | Calvert City | 43 | 238.8575 |  | 0.4942 | 0.14653 | OK | 18.6 | 2017 | 50.6014 | 13.4767 | OK | Good | 5
CC Hgts | 4302 | 4302-Calvert Heights | Calvert City | 43 | 651.3753 |  | 0.6204 | 0.59106 | OK | 28.1 | 2017 | 51.8582 | 65.1529 | PSC | More Info Required | 23 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Gilbertsville | 4303 | 4303-Gilbertsville | Calvert City | 43 | 356.7726 |  | 0.37975 | 0.15977 | OK | 23.1 | 2017 | 55.8536 | 16.4222 | OK | Good | 10
CC Ind Park | 4304 | 4304-Industrial Park | Calvert City | 43 | 26.9315 |  | 0.22466 | 0.074262 | OK | 4.9 | 2017 | 16.7715 | 3.2304 | OK | Good | 2
Vulcan Pit | 4502 | 4502-Vulcan Pit | Vulcan | 45 | 0 |  | 0 | 0 | OK | 2.39 |  | 0 | 0 | OK | Good | 0
Vulcan 1-Rock Crusher | 4503 | 4503-Vulcan1 Rock Crusher | Vulcan | 45 | 0 |  | 0.3 | 0 | OK | 1.29 |  | 38 | 0 | OK | Good | 0
Kinder Morgan 1 | 4504 | 4504-Kinder Morgan 1 | Vulcan | 45 | 0 |  | 1.0101 | 0 | OK | 7.8 |  | 156.8098 | 0 | OK | Good | 0
Vulcan 2 Hwy 62 | 4505 | 4505-Vulcan 2 Hwy 62 | Vulcan | 45 | 3 |  | 0.23333 | 0.66667 | PSC | 4.99 |  | 41.1 | 77.3333 | PSC | More Info Required | 1 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Hinkleville | 4701 | 4701-Hinkleville | New York | 47 | 265.6685 |  | 2.3401 | 0.54956 | OK | 44.46 | 2017 | 317.5226 | 89.8149 | OK | Good | 16
US 286 East-Gage | 4702 | 4702-US 286 East Gage | New York | 47 | 265.8055 |  | 1.6125 | 0.34236 | OK | 45.36 | 2017 | 213.9896 | 26.0266 | OK | Good | 10
Blandville | 4703 | 4703-Blandville | New York | 47 | 228.3205 |  | 2.8409 | 1.8176 | OK | 30.3 | 2017 | 720.044 | 241.7128 | OK | Good | 13
Wickliffe | 4704 | 4704-Wickliffe | New York | 47 | 352.074 |  | 1.7157 | 0.88902 | OK | 49.26 | 2017 | 354.2913 | 112.9393 | OK | Good | 17
Slater | 4705 | 4705-Slater | New York | 47 | 348.7068 |  | 2.5931 | 0.9865 | OK | 67.7 | 2017 | 394.9141 | 157.3585 | OK | Good | 24
Blandville | 4901 | 4901-Blandville | Lovelaceville | 49 | 132.8411 |  | 1.7358 | 1.9346 | PSC | 20.3 | 2015 | 213.5526 | 138.4285 | OK | More Info Required | 9 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Lovelaceville | 4902 | 4902-Lovelaceville | Lovelaceville | 49 | 522.7342 |  | 0.78605 | 1.1555 | PSC | 57.87 | 2015 | 135.308 | 18.4453 | OK | More Info Required | 18 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Cunningham | 4903 | 4903-Cunningham | Lovelaceville | 49 | 526.9863 |  | 1.5363 | 2.391 | PSC | 64.47 | 2015 | 206.5207 | 73.1195 | OK | More Info Required | 17 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Browns Plating | 5001 | 5001-Browns Plating | Krebs Station Road | 50 | 514.3452 |  | 1.5871 | 2.0784 | PSC | 37.55 | 2016 | 287.3221 | 147.5138 | OK | More Info Required | 21 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Old US 45 | 5002 | 5002-Old US 45 | Krebs Station Road | 50 | 866.9918 |  | 2.9886 | 2.5479 | OK | 77.1 | 2016 | 426.2778 | 253.0935 | OK | Good | 43
Clinton Road | 5003 | 5003-Clinton Rd | Krebs Station Road | 50 | 603.5534 |  | 1.1464 | 2.0744 | PSC | 52.5 | 2016 | 127.0859 | 162.2508 | PSC | More Info Required | 31 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Symsonia | 51214 | 51214-Symsonia | Freemont | 51 | 1013.7726 |  | 0.82755 | 1.7164 | PSC | 93.38 | 2018 | 71.7012 | 179.0697 | PSC | More Info Required | 68 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Mc Neil Lane | 51224 | 51224-McNeil Lane | Freemont | 51 | 373.3863 |  | 2.1016 | 1.3659 | OK | 45.69 | 2018 | 294.5322 | 115.6202 | OK | Good | 19
Freemont | 51244 | 51244-Freemont | Freemont | 51 | 345.7507 |  | 0.55111 | 1.2581 | PSC | 25.78 | 2018 | 53.0943 | 159.6613 | PSC | More Info Required | 14 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Bonds Rd | 51254 | 51254-Bonds Rd | Freemont | 51 | 121.2712 |  | 1.1716 | 0.28861 | OK | 17.6 | 2018 | 98.9721 | 54.9842 | OK | Good | 5
Hwy 95 N to Hwy 62 | 54214 | 54214-Hwy 95 | Palma | 54 | 357.6849 |  | 1.4685 | 1.0959 | OK | 29.57 | 2018 | 146.3121 | 111.327 | OK | Good | 8
Draffenville | 54224 | 54224-Draffenville | Palma | 54 | 287.6904 |  | 0.039841 | 1.2444 | PSC | 21.36 | 2018 | 6.3802 | 131.1444 | PSC | More Info Required | 10 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Palma | 54234 | 54234-Palma | Palma | 54 | 732.5479 |  | 0.80438 | 2.7452 | PSC | 56.46 | 2018 | 66.8121 | 259.6676 | PSC | More Info Required | 23 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Lowes | 6101 | 6101-Lowes | Kansas | 61 | 454.3041 |  | 0.76422 | 1.2745 | PSC | 58.3 | 2016 | 119.8663 | 47.7852 | OK | More Info Required | 14 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
US 45-Folsomdale | 6102 | 6102-US 45 Folsomdale | Kansas | 61 | 213.2849 |  | 0.74412 | 1.28 | PSC | 29.15 | 2016 | 115.809 | 31.193 | OK | More Info Required | 10 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Melber | 6103 | 6103-Melber | Kansas | 61 | 527.674 |  | 0.84871 | 1.3342 | PSC | 52.6 | 2016 | 158.3419 | 54.9449 | OK | More Info Required | 17 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Pottsville | 6104 | 6104-Pottsville | Kansas | 61 | 360.1014 |  | 1.5203 | 2.4299 | PSC | 46.87 | 2016 | 317.4259 | 121.7879 | OK | More Info Required | 25 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Draffenville | 6601 | 6601-Draffenville | Draffenville | 66 | 480.7178 |  | 0.39626 | 0.043685 | OK | 29.15 | 2018 | 32.683 | 3.838 | OK | Good | 6
Olivet Ch Rd | 74214 | 74214-Olivet Ch Rd | Olivet Church Road | 74 | 557.663 |  | 0.2436 | 1.0311 | PSC | 21.4 | 2015 | 20.719 | 117.7109 | PSC | More Info Required | 8 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Highland Ch Rd | 74224 | 74224-Highland Ch Rd | Olivet Church Road | 74 | 454.611 |  | 1.0137 | 0.18477 | OK | 36 | 2015 | 102.7115 | 15.0942 | OK | Good | 23
Info Age Park | 74234 | 74234-Info Age Park | Olivet Church Road | 74 | 8 |  | 0 | 0.875 | PSC | 2.45 | 2015 | 0 | 247.625 | PSC | More Info Required | 1 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Iuka | 7601 | 7601-Iuka | Grand Rivers | 76 | 299.0164 |  | 1.2421 | 1.1906 | OK | 47.8 | 2016 | 127.3814 | 223.3857 | PSC | More Info Required | 15 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Smithland | 7602 | 7602-Smithland | Grand Rivers | 76 | 285.811 |  | 2.1336 | 0.073475 | OK | 30.6 | 2016 | 211.8862 | 11.4341 | OK | Good | 10
Pelican-GR #1 | 7604 | 7604-Pelican GR #1 | Grand Rivers | 76 | 371.8324 |  | 1.0353 | 0.39265 | OK | 24.1 | 2016 | 115.9441 | 32.7997 | OK | Good | 7
Averitt-GR #2 | 7605 | 7605-Averitt GR #2 | Grand Rivers | 76 | 659.4959 |  | 1.5656 | 1.072 | OK | 43.19 | 2016 | 181.6467 | 318.8996 | PSC | More Info Required | 10 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Hansen Rd-Top Circuit | 7702 | 7702-Hansen Rd | Strawberry Hill | 77 | 639.7562 |  | 1.1088 | 1.9726 | PSC | 29.4 | 2015 | 93.8566 | 182.2601 | PSC | More Info Required | 18 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Walmart-Hansen Rd Bottom | 7703 | 7703-Walmart | Strawberry Hill | 77 | 508.611 |  | 0.50097 | 0.0058984 | OK | 9.5 | 2015 | 23.0229 | 0.19268 | OK | Good | 2
CSI--Jas Sanders-Botom Cir | 7705 | 7705-CSI | Strawberry Hill | 77 | 0 |  | 1.3341 | 0 | OK | 5 | 2015 | 88.1566 | 0 | OK | Good | 0
Hwy 60-Jas Sanders-Top Cir | 7706 | 7706-Hwy 60 | Strawberry Hill | 77 | 12.3616 |  | 0.21929 | 1.0516 | PSC | 1.6 | 2015 | 12.7785 | 52.9056 | PSC | More Info Required | 2 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Hwy 95 North | 7802 | 7802-Possum Trot | Possum Trot | 78 | 533.389 |  | 0.27509 | 0.41433 | PSC | 42.4 | 2015 | 31.7911 | 51.139 | PSC | More Info Required | 22 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Possum Trot | 7803 | 7803-Hwy 95 | Possum Trot | 78 | 195.3918 |  | 0.22414 | 1.6992 | PSC | 15 | 2015 | 23.9701 | 202.68 | PSC | More Info Required | 17 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Industrial Loop North | 7805 | 7805-Industrial Loop | Possum Trot | 78 | 206.9973 |  | 1.0409 | 0.33817 | OK | 4.5 | 2015 | 107.9671 | 33.3917 | OK | Good | 12
Coal Tek | 7806 | 7806-CoalTek | Possum Trot | 78 | 0 |  | 0.17576 | 0 | OK | 3.96 | 2015 | 23.7279 | 0 | OK | Good | 0
Meredith Rd | 79214 | 79214-Meredith Rd | Maxon | 79 | 250.8192 |  | 0.78628 | 0.23922 | OK | 15.2 | 2017 | 131.1656 | 23.8778 | OK | Good | 9
Maxon Rd | 79224 | 79224-Express | Maxon | 79 | 302.9562 |  | 0.96362 | 0.28057 | OK | 20.6 | 2017 | 144.6638 | 17.6791 | OK | Good | 3
Industrial Park | 79234 | 79234-Industrial Park | Maxon | 79 | 0 |  | 0.33662 | 0 | OK | 0.8 | 2017 | 23.4462 | 0 | OK | Good | 0
Electric Distribution Utility Annual Reliability Report
Additional pages may be attached as necessary
SECTION 7: VEGETATION MANAGEMENT PLAN REVIEW
JPEC has established a four (4) year cycle on right-of-way maintenance and employs a contractor to perform that cycle clearing. JPEC also employs contract crews that handles mid-cycle trimming. We have experienced over the last couple of years an increased tree problem from "danger trees" (trees outside of right-of-way) falling into our ROW and tearing down lines and poles. We are working with our members and contractors to identify those danger trees for removal. In addition to JPEC's contractors, JPEC construction and maintenance crews have the tools and ability to recognize hazards and trim trees away from the line as they perform their duties.
SECTION 8: UTILITY COMMENTS
Overall, 2018 was a good year in comparison to previous years. JPEC is only reporting 36 circuits compared to 43 last year. JPEC continues to focus on identification and replacement of structures in an effort to harden JPEC system which is proven in the reporting number of circuits. JPEC continues to work with BREC to increase reliability on the transmission system by installing radio controlled switches. New technologies are being tested that will put more information into the hands of crews. This new technology will make reporting restoration times closer to real time. New switching points are being installed to isolate outages and return as many members back on as possible.

## 2017 Circuit Details
Electric Distribution Utility Annual Reliability Report
SECTION 1: CONTACT INFORMATION
|  |  | UTILITY NAME | 1.1 | Jackson Purchase Energy Corporation
|  |  | REPORT PREPARED BY | 1.2 | Scott Ribble
|  |  | E-MAIL ADDRESS OF PREPARER | 1.3 | scott.ribble@jpenergy.com
|  |  | PHONE NUMBER OF PREPARER | 1.4 | 270-442-7321
SECTION 2: REPORT YEAR
|  |  | CALENDAR YEAR OF REPORT | 2.1 | 2017
SECTION 3: MAJOR EVENT DAYS
|  |  | TMED | 3.1 | 8.01
|  |  | FIRST DATE USED TO DETERMINE TMED | 3.2 | 2012-01-01
|  |  | LAST DATE USED TO DETERMINE TMED | 3.3 | 2016-12-31
|  |  | NUMBER OF MED IN REPORT YEAR | 3.4 | 4
NOTE: Per IEEE 1366 TMED should be calculated using the daily SAIDI values for the five prior years. If five years of data are not available, then utilities should use what is available until five years are accumulated.
SECTION 4: SYSTEM RELIABILITY RESULTS
System - Wide Information
| Total Customers | 29752 |  |  | Total Circuits | 91
Excluding MED
| 5 Year Average |  |  |  | Reporting Year
| SAIDI | 116.24 |  |  | SAIDI | 121.105
| SAIFI | 1.27 |  |  | SAIFI | 1.1002
Including MED
| 5 Year Average |  |  |  | Reporting Year
| SAIDI | 381.56 |  |  | SAIDI | 380.53
| SAIFI | 1.59 |  |  | SAIFI | 1.8555
SECTION 5: CIRCUIT REPORTING
Circuit Name | Circuit Number | Circuit Location | Substation Name | Substation Number | Avg # of Customers |  | Previous 5 Year Average SAIFI | Current Year SAIFI Excluding MED | Comparison | Circuit Length | Date of Last Trim For Circuit | Previous 5 Year Average SAIDI | Current Year SAIDI Excluding MED |  |  | # of Outages | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | %
Hampton-South | 501 | 0501-Hampton South | Joy | 5 | 194.2411 |  | 2.2255 | 2.327 | PSC | 57.417 | 2016 | 270.1383 | 574.1524 | PSC | More Info Required | 13 | 000 Power Supply | 0.15385 | 100 Construction | 0.076923 | 110 Maintenance | 0 | 190 Other Planned | 0.076923 | 300 Material or equipment fault/failure | 0 | 310 Installation Fault | 0 | 320 Conductor Sag or inadequate clearance | 0 | 340 Overload | 0 | 350 Miscoordination of protection devices | 0 | 360 Other Equipment installation/design | 0 | 400 Decay/Age of Material/Equipment | 0 | 420 Tree Growth | 0 | 430 Tree failure from overhang or dead tree without Ice/snow | 0.076923 | 440 Trees with Ice/snow | 0 | 470 Borrower Crew Cuts Tree | 0 | 490 Maintenance, Other | 0.076923 | 500 Lightning | 0.076923 | 510 Wind, Not Trees | 0 | 520 Ice, Sleet, Frost, not Trees | 0 | 530 Flood | 0 | 540 Storm | 0 | 590 Weather, Other | 0 | 600 Animal/bird | 0 | 630 Squirrel | 0 | 690 Animal, Other | 0 | 700 Customer-Caused | 0 | 710 Motor Vehicle | 0.15385 | 715 Farming Equipment | 0 | 720 Aircraft | 0 | 730 Fire | 0 | 740 Public Cuts Tree | 0 | 750 Vandalism | 0 | 760 Switching Error or Caused by Construction or Maintenance | 0 | 790 Public, Other | 0 | 800 Other | 0 | 999 Cause Unknown | 0.30769
Carrsville | 504 | 0504-Carrsville | Joy | 5 | 72.0931 |  | 1.4913 | 2.9545 | PSC | 10.735 | 2016 | 183.8995 | 680.5224 | PSC | More Info Required | 3 | 000 Power Supply | 0.66667 | 100 Construction | 0 | 110 Maintenance | 0 | 190 Other Planned | 0 | 300 Material or equipment fault/failure | 0 | 310 Installation Fault | 0 | 320 Conductor Sag or inadequate clearance | 0 | 340 Overload | 0 | 350 Miscoordination of protection devices | 0 | 360 Other Equipment installation/design | 0 | 400 Decay/Age of Material/Equipment | 0 | 420 Tree Growth | 0 | 430 Tree failure from overhang or dead tree without Ice/snow | 0 | 440 Trees with Ice/snow | 0 | 470 Borrower Crew Cuts Tree | 0 | 490 Maintenance, Other | 0 | 500 Lightning | 0.33333 | 510 Wind, Not Trees | 0 | 520 Ice, Sleet, Frost, not Trees | 0 | 530 Flood | 0 | 540 Storm | 0 | 590 Weather, Other | 0 | 600 Animal/bird | 0 | 630 Squirrel | 0 | 690 Animal, Other | 0 | 700 Customer-Caused | 0 | 710 Motor Vehicle | 0 | 715 Farming Equipment | 0 | 720 Aircraft | 0 | 730 Fire | 0 | 740 Public Cuts Tree | 0 | 750 Vandalism | 0 | 760 Switching Error or Caused by Construction or Maintenance | 0 | 790 Public, Other | 0 | 800 Other | 0 | 999 Cause Unknown | 0
Lola | 505 | 0505-Lola | Joy | 5 | 298.7425 |  | 0.77799 | 2.1524 | PSC | 56.512 | 2016 | 122.5605 | 563.1606 | PSC | More Info Required | 16 | 000 Power Supply | 0.125 | 100 Construction | 0.125 | 110 Maintenance | 0.125 | 190 Other Planned | 0 | 300 Material or equipment fault/failure | 0.0625 | 310 Installation Fault | 0 | 320 Conductor Sag or inadequate clearance | 0 | 340 Overload | 0 | 350 Miscoordination of protection devices | 0 | 360 Other Equipment installation/design | 0 | 400 Decay/Age of Material/Equipment | 0 | 420 Tree Growth | 0 | 430 Tree failure from overhang or dead tree without Ice/snow | 0.0625 | 440 Trees with Ice/snow | 0 | 470 Borrower Crew Cuts Tree | 0 | 490 Maintenance, Other | 0 | 500 Lightning | 0.0625 | 510 Wind, Not Trees | 0 | 520 Ice, Sleet, Frost, not Trees | 0 | 530 Flood | 0 | 540 Storm | 0 | 590 Weather, Other | 0 | 600 Animal/bird | 0 | 630 Squirrel | 0.0625 | 690 Animal, Other | 0 | 700 Customer-Caused | 0 | 710 Motor Vehicle | 0 | 715 Farming Equipment | 0 | 720 Aircraft | 0 | 730 Fire | 0 | 740 Public Cuts Tree | 0 | 750 Vandalism | 0 | 760 Switching Error or Caused by Construction or Maintenance | 0 | 790 Public, Other | 0 | 800 Other | 0 | 999 Cause Unknown | 0.375
Hampton | 1401 | 1401-Hampton | Burna | 14 | 87.1753 |  | 0.16179 | 2.0419 | PSC | 12.903 | 2015 | 19.2459 | 544.4774 | PSC | More Info Required | 6 | 000 Power Supply | 0.33333 | 100 Construction | 0.33333 | 110 Maintenance | 0.16667 | 190 Other Planned | 0 | 300 Material or equipment fault/failure | 0 | 310 Installation Fault | 0 | 320 Conductor Sag or inadequate clearance | 0 | 340 Overload | 0 | 350 Miscoordination of protection devices | 0 | 360 Other Equipment installation/design | 0 | 400 Decay/Age of Material/Equipment | 0 | 420 Tree Growth | 0 | 430 Tree failure from overhang or dead tree without Ice/snow | 0 | 440 Trees with Ice/snow | 0 | 470 Borrower Crew Cuts Tree | 0 | 490 Maintenance, Other | 0 | 500 Lightning | 0 | 510 Wind, Not Trees | 0.16667 | 520 Ice, Sleet, Frost, not Trees | 0 | 530 Flood | 0 | 540 Storm | 0 | 590 Weather, Other | 0 | 600 Animal/bird | 0 | 630 Squirrel | 0 | 690 Animal, Other | 0 | 700 Customer-Caused | 0 | 710 Motor Vehicle | 0 | 715 Farming Equipment | 0 | 720 Aircraft | 0 | 730 Fire | 0 | 740 Public Cuts Tree | 0 | 750 Vandalism | 0 | 760 Switching Error or Caused by Construction or Maintenance | 0 | 790 Public, Other | 0 | 800 Other | 0 | 999 Cause Unknown | 0
Salem | 1404 | 1404-Salem | Burna | 14 | 328.5205 |  | 0.17119 | 0.36832 | PSC | 53.744 | 2015 | 26.9428 | 69.0611 | PSC | More Info Required | 24 | 000 Power Supply | 0 | 100 Construction | 0.125 | 110 Maintenance | 0.125 | 190 Other Planned | 0 | 300 Material or equipment fault/failure | 0.083333 | 310 Installation Fault | 0 | 320 Conductor Sag or inadequate clearance | 0 | 340 Overload | 0 | 350 Miscoordination of protection devices | 0 | 360 Other Equipment installation/design | 0 | 400 Decay/Age of Material/Equipment | 0 | 420 Tree Growth | 0 | 430 Tree failure from overhang or dead tree without Ice/snow | 0.083333 | 440 Trees with Ice/snow | 0 | 470 Borrower Crew Cuts Tree | 0 | 490 Maintenance, Other | 0 | 500 Lightning | 0.083333 | 510 Wind, Not Trees | 0.041667 | 520 Ice, Sleet, Frost, not Trees | 0 | 530 Flood | 0 | 540 Storm | 0 | 590 Weather, Other | 0 | 600 Animal/bird | 0 | 630 Squirrel | 0.125 | 690 Animal, Other | 0.041667 | 700 Customer-Caused | 0 | 710 Motor Vehicle | 0 | 715 Farming Equipment | 0 | 720 Aircraft | 0 | 730 Fire | 0 | 740 Public Cuts Tree | 0.041667 | 750 Vandalism | 0 | 760 Switching Error or Caused by Construction or Maintenance | 0 | 790 Public, Other | 0 | 800 Other | 0.041667 | 999 Cause Unknown | 0.20833
Smithland | 1405 | 1405-Smithland | Burna | 14 | 336.5616 |  | 1.3491 | 0.42786 | OK | 70.627 | 2015 | 154.2258 | 105.523 | OK | Good | 21
Pinckneyville | 15224 | 15224-Pinckneyville | Cumberland | 15 | 114.5014 |  | 2.2016 | 1.1266 | OK | 28.789 | 2015 | 305.3265 | 168.0591 | OK | Good | 5
Quarry | 15234 | 15234-Quarry | Cumberland | 15 | 0 |  | 1.115 | 0 | OK | 5.285 | 2015 | 102.9956 | 0 | OK | Good | 0
Monkey's Eyebrow | 1901 | 1901-Monkeys Eyebrow | Ragland | 19 | 261.6959 |  | 1.0552 | 0.11464 | OK | 51.116 | 2017 | 98.2496 | 22.9236 | OK | Good | 7
Ragland | 1902 | 1902-Ragland | Ragland | 19 | 231.1589 |  | 0.66687 | 0.35041 | OK | 33.568 | 2017 | 36.6338 | 45.9294 | PSC | More Info Required | 8 | 000 Power Supply | 0 | 100 Construction | 0 | 110 Maintenance | 0.125 | 190 Other Planned | 0 | 300 Material or equipment fault/failure | 0 | 310 Installation Fault | 0 | 320 Conductor Sag or inadequate clearance | 0 | 340 Overload | 0 | 350 Miscoordination of protection devices | 0 | 360 Other Equipment installation/design | 0 | 400 Decay/Age of Material/Equipment | 0 | 420 Tree Growth | 0 | 430 Tree failure from overhang or dead tree without Ice/snow | 0.375 | 440 Trees with Ice/snow | 0 | 470 Borrower Crew Cuts Tree | 0 | 490 Maintenance, Other | 0 | 500 Lightning | 0 | 510 Wind, Not Trees | 0 | 520 Ice, Sleet, Frost, not Trees | 0 | 530 Flood | 0 | 540 Storm | 0 | 590 Weather, Other | 0 | 600 Animal/bird | 0.125 | 630 Squirrel | 0.125 | 690 Animal, Other | 0 | 700 Customer-Caused | 0 | 710 Motor Vehicle | 0 | 715 Farming Equipment | 0 | 720 Aircraft | 0 | 730 Fire | 0 | 740 Public Cuts Tree | 0 | 750 Vandalism | 0 | 760 Switching Error or Caused by Construction or Maintenance | 0 | 790 Public, Other | 0 | 800 Other | 0.125 | 999 Cause Unknown | 0.125
Damron's | 2601 | 2601-Damrons | LaCenter | 26 | 230.263 |  | 2.167 | 0.97714 | OK | 39.285 | 2015 | 201.4871 | 207.0762 | PSC | More Info Required | 17 | 000 Power Supply | 0 | 100 Construction | 0.058824 | 110 Maintenance | 0 | 190 Other Planned | 0 | 300 Material or equipment fault/failure | 0.17647 | 310 Installation Fault | 0 | 320 Conductor Sag or inadequate clearance | 0 | 340 Overload | 0 | 350 Miscoordination of protection devices | 0 | 360 Other Equipment installation/design | 0 | 400 Decay/Age of Material/Equipment | 0 | 420 Tree Growth | 0 | 430 Tree failure from overhang or dead tree without Ice/snow | 0 | 440 Trees with Ice/snow | 0 | 470 Borrower Crew Cuts Tree | 0 | 490 Maintenance, Other | 0 | 500 Lightning | 0.058824 | 510 Wind, Not Trees | 0.058824 | 520 Ice, Sleet, Frost, not Trees | 0 | 530 Flood | 0 | 540 Storm | 0.29412 | 590 Weather, Other | 0 | 600 Animal/bird | 0 | 630 Squirrel | 0 | 690 Animal, Other | 0 | 700 Customer-Caused | 0 | 710 Motor Vehicle | 0 | 715 Farming Equipment | 0.058824 | 720 Aircraft | 0 | 730 Fire | 0 | 740 Public Cuts Tree | 0 | 750 Vandalism | 0 | 760 Switching Error or Caused by Construction or Maintenance | 0 | 790 Public, Other | 0 | 800 Other | 0.058824 | 999 Cause Unknown | 0.23529
Oscar | 2602 | 2602-Oscar | LaCenter | 26 | 367.4822 |  | 1.3788 | 0.44628 | OK | 69.896 | 2015 | 149.2487 | 131.1519 | OK | Good | 21
Hobbs Rd | 2801 | 2801-Hobbs Rd | Kevil | 28 | 557.2603 |  | 0.88223 | 2.2898 | PSC | 53.455 | 2017 | 79.0381 | 245.0112 | PSC | More Info Required | 17 | 000 Power Supply | 0.058824 | 100 Construction | 0.058824 | 110 Maintenance | 0 | 190 Other Planned | 0 | 300 Material or equipment fault/failure | 0.058824 | 310 Installation Fault | 0 | 320 Conductor Sag or inadequate clearance | 0 | 340 Overload | 0 | 350 Miscoordination of protection devices | 0 | 360 Other Equipment installation/design | 0 | 400 Decay/Age of Material/Equipment | 0 | 420 Tree Growth | 0 | 430 Tree failure from overhang or dead tree without Ice/snow | 0.17647 | 440 Trees with Ice/snow | 0 | 470 Borrower Crew Cuts Tree | 0 | 490 Maintenance, Other | 0 | 500 Lightning | 0.11765 | 510 Wind, Not Trees | 0 | 520 Ice, Sleet, Frost, not Trees | 0 | 530 Flood | 0 | 540 Storm | 0.11765 | 590 Weather, Other | 0 | 600 Animal/bird | 0.058824 | 630 Squirrel | 0.058824 | 690 Animal, Other | 0 | 700 Customer-Caused | 0 | 710 Motor Vehicle | 0 | 715 Farming Equipment | 0.058824 | 720 Aircraft | 0 | 730 Fire | 0 | 740 Public Cuts Tree | 0 | 750 Vandalism | 0 | 760 Switching Error or Caused by Construction or Maintenance | 0 | 790 Public, Other | 0 | 800 Other | 0 | 999 Cause Unknown | 0.23529
Woodville Rd | 2802 | 2802-Woodville Rd | Kevil | 28 | 544.7562 |  | 0.83119 | 2.4818 | PSC | 70.665 | 2017 | 89.1847 | 264.4155 | PSC | More Info Required | 24 | 000 Power Supply | 0.041667 | 100 Construction | 0 | 110 Maintenance | 0.041667 | 190 Other Planned | 0 | 300 Material or equipment fault/failure | 0.041667 | 310 Installation Fault | 0 | 320 Conductor Sag or inadequate clearance | 0 | 340 Overload | 0 | 350 Miscoordination of protection devices | 0 | 360 Other Equipment installation/design | 0 | 400 Decay/Age of Material/Equipment | 0 | 420 Tree Growth | 0.041667 | 430 Tree failure from overhang or dead tree without Ice/snow | 0.083333 | 440 Trees with Ice/snow | 0 | 470 Borrower Crew Cuts Tree | 0 | 490 Maintenance, Other | 0 | 500 Lightning | 0.083333 | 510 Wind, Not Trees | 0.083333 | 520 Ice, Sleet, Frost, not Trees | 0 | 530 Flood | 0 | 540 Storm | 0.041667 | 590 Weather, Other | 0 | 600 Animal/bird | 0 | 630 Squirrel | 0.25 | 690 Animal, Other | 0 | 700 Customer-Caused | 0 | 710 Motor Vehicle | 0 | 715 Farming Equipment | 0 | 720 Aircraft | 0 | 730 Fire | 0 | 740 Public Cuts Tree | 0 | 750 Vandalism | 0 | 760 Switching Error or Caused by Construction or Maintenance | 0 | 790 Public, Other | 0 | 800 Other | 0.083333 | 999 Cause Unknown | 0.20833
Kelley Rd | 2803 | 2803-Kelley Rd | Kevil | 28 | 411.3973 |  | 1.6589 | 1.1619 | OK | 45.651 | 2017 | 208.763 | 42.2779 | OK | Good | 12
High Point | 2901 | 2901-High Point | High Point | 29 | 199.7288 |  | 1.4329 | 0.38052 | OK | 21.562 | 2015 | 111.4654 | 40.56 | OK | Good | 6
Carneal Rd | 2902 | 2902-Carneal Rd | High Point | 29 | 186.0192 |  | 1.7611 | 1.7041 | OK | 17.372 | 2015 | 160.2091 | 236.9756 | PSC | More Info Required | 14 | 000 Power Supply | 0 | 100 Construction | 0.35714 | 110 Maintenance | 0.071429 | 190 Other Planned | 0 | 300 Material or equipment fault/failure | 0 | 310 Installation Fault | 0 | 320 Conductor Sag or inadequate clearance | 0 | 340 Overload | 0 | 350 Miscoordination of protection devices | 0 | 360 Other Equipment installation/design | 0 | 400 Decay/Age of Material/Equipment | 0 | 420 Tree Growth | 0 | 430 Tree failure from overhang or dead tree without Ice/snow | 0.071429 | 440 Trees with Ice/snow | 0 | 470 Borrower Crew Cuts Tree | 0 | 490 Maintenance, Other | 0 | 500 Lightning | 0.14286 | 510 Wind, Not Trees | 0 | 520 Ice, Sleet, Frost, not Trees | 0 | 530 Flood | 0 | 540 Storm | 0 | 590 Weather, Other | 0 | 600 Animal/bird | 0 | 630 Squirrel | 0 | 690 Animal, Other | 0 | 700 Customer-Caused | 0 | 710 Motor Vehicle | 0 | 715 Farming Equipment | 0 | 720 Aircraft | 0 | 730 Fire | 0 | 740 Public Cuts Tree | 0 | 750 Vandalism | 0 | 760 Switching Error or Caused by Construction or Maintenance | 0 | 790 Public, Other | 0.071429 | 800 Other | 0.14286 | 999 Cause Unknown | 0.14286
Essex | 2903 | 2903-Essex | High Point | 29 | 0 |  | 0 | 0 | OK | 0.042 | 2015 | 0 | 0 | OK | Good | 0
Conrad Heights | 3002 | 3002-Conrad Heights | Coleman Road | 30 | 393.4027 |  | 0.85675 | 1.6116 | PSC | 18.174 | 2015 | 68.0696 | 105.8788 | PSC | More Info Required | 12 | 000 Power Supply | 0 | 100 Construction | 0 | 110 Maintenance | 0.083333 | 190 Other Planned | 0.083333 | 300 Material or equipment fault/failure | 0.083333 | 310 Installation Fault | 0 | 320 Conductor Sag or inadequate clearance | 0 | 340 Overload | 0 | 350 Miscoordination of protection devices | 0 | 360 Other Equipment installation/design | 0 | 400 Decay/Age of Material/Equipment | 0 | 420 Tree Growth | 0 | 430 Tree failure from overhang or dead tree without Ice/snow | 0.16667 | 440 Trees with Ice/snow | 0 | 470 Borrower Crew Cuts Tree | 0 | 490 Maintenance, Other | 0 | 500 Lightning | 0.083333 | 510 Wind, Not Trees | 0 | 520 Ice, Sleet, Frost, not Trees | 0 | 530 Flood | 0 | 540 Storm | 0.083333 | 590 Weather, Other | 0 | 600 Animal/bird | 0 | 630 Squirrel | 0.083333 | 690 Animal, Other | 0.083333 | 700 Customer-Caused | 0 | 710 Motor Vehicle | 0 | 715 Farming Equipment | 0 | 720 Aircraft | 0 | 730 Fire | 0 | 740 Public Cuts Tree | 0 | 750 Vandalism | 0 | 760 Switching Error or Caused by Construction or Maintenance | 0 | 790 Public, Other | 0 | 800 Other | 0.083333 | 999 Cause Unknown | 0.16667
Holt Rd | 3004 | 3004-Hwy 60 Business | Coleman Road | 30 | 103.3616 |  | 0.21803 | 0.98683 | PSC | 7.678 | 2015 | 11.6702 | 99.921 | PSC | More Info Required | 2 | 000 Power Supply | 0 | 100 Construction | 0 | 110 Maintenance | 0 | 190 Other Planned | 0 | 300 Material or equipment fault/failure | 0 | 310 Installation Fault | 0 | 320 Conductor Sag or inadequate clearance | 0 | 340 Overload | 0 | 350 Miscoordination of protection devices | 0 | 360 Other Equipment installation/design | 0 | 400 Decay/Age of Material/Equipment | 0 | 420 Tree Growth | 0 | 430 Tree failure from overhang or dead tree without Ice/snow | 0 | 440 Trees with Ice/snow | 0 | 470 Borrower Crew Cuts Tree | 0 | 490 Maintenance, Other | 0 | 500 Lightning | 0.5 | 510 Wind, Not Trees | 0 | 520 Ice, Sleet, Frost, not Trees | 0 | 530 Flood | 0 | 540 Storm | 0 | 590 Weather, Other | 0 | 600 Animal/bird | 0 | 630 Squirrel | 0 | 690 Animal, Other | 0.5 | 700 Customer-Caused | 0 | 710 Motor Vehicle | 0 | 715 Farming Equipment | 0 | 720 Aircraft | 0 | 730 Fire | 0 | 740 Public Cuts Tree | 0 | 750 Vandalism | 0 | 760 Switching Error or Caused by Construction or Maintenance | 0 | 790 Public, Other | 0 | 800 Other | 0 | 999 Cause Unknown | 0
Ky Oaks Mall | 3005 | 3005-KY Oaks Mall | Coleman Road | 30 | 80.5205 |  | 0.24984 | 0.95628 | PSC | 3.877 | 2015 | 6.4258 | 110.3818 | PSC | More Info Required | 1 | 000 Power Supply | 0 | 100 Construction | 0 | 110 Maintenance | 0 | 190 Other Planned | 0 | 300 Material or equipment fault/failure | 0 | 310 Installation Fault | 0 | 320 Conductor Sag or inadequate clearance | 0 | 340 Overload | 0 | 350 Miscoordination of protection devices | 0 | 360 Other Equipment installation/design | 0 | 400 Decay/Age of Material/Equipment | 0 | 420 Tree Growth | 0 | 430 Tree failure from overhang or dead tree without Ice/snow | 0 | 440 Trees with Ice/snow | 0 | 470 Borrower Crew Cuts Tree | 0 | 490 Maintenance, Other | 0 | 500 Lightning | 0 | 510 Wind, Not Trees | 0 | 520 Ice, Sleet, Frost, not Trees | 0 | 530 Flood | 0 | 540 Storm | 0 | 590 Weather, Other | 0 | 600 Animal/bird | 0 | 630 Squirrel | 0 | 690 Animal, Other | 1 | 700 Customer-Caused | 0 | 710 Motor Vehicle | 0 | 715 Farming Equipment | 0 | 720 Aircraft | 0 | 730 Fire | 0 | 740 Public Cuts Tree | 0 | 750 Vandalism | 0 | 760 Switching Error or Caused by Construction or Maintenance | 0 | 790 Public, Other | 0 | 800 Other | 0 | 999 Cause Unknown | 0
US 60 East | 3102 | 3102-US 60 East | Ledbetter | 31 | 319.0493 |  | 1.4988 | 0.14418 | OK | 35.417 | 2016 | 113.8141 | 24.6827 | OK | Good | 12
River Crossing | 3103 | 3103-River Crossing | Ledbetter | 31 | 0 |  | 0.22458 | 0 | OK | 5.154 | 2016 | 23.7431 | 0 | OK | Good | 0
Ledbetter | 3104 | 3104-Ledbetter | Ledbetter | 31 | 1010.6 |  | 1.2484 | 0.2078 | OK | 62.267 | 2016 | 93.3404 | 14.1263 | OK | Good | 34
Smithland | 3201 | 3201-Smithland | Smithland | 32 | 388.4 |  | 2.0637 | 2.4691 | PSC | 29.715 | 2014 | 222.4705 | 287.155 | PSC | More Info Required | 13 | 000 Power Supply | 0.076923 | 100 Construction | 0.076923 | 110 Maintenance | 0.15385 | 190 Other Planned | 0 | 300 Material or equipment fault/failure | 0 | 310 Installation Fault | 0 | 320 Conductor Sag or inadequate clearance | 0 | 340 Overload | 0 | 350 Miscoordination of protection devices | 0 | 360 Other Equipment installation/design | 0.076923 | 400 Decay/Age of Material/Equipment | 0 | 420 Tree Growth | 0 | 430 Tree failure from overhang or dead tree without Ice/snow | 0.15385 | 440 Trees with Ice/snow | 0 | 470 Borrower Crew Cuts Tree | 0 | 490 Maintenance, Other | 0.15385 | 500 Lightning | 0 | 510 Wind, Not Trees | 0 | 520 Ice, Sleet, Frost, not Trees | 0 | 530 Flood | 0 | 540 Storm | 0 | 590 Weather, Other | 0 | 600 Animal/bird | 0 | 630 Squirrel | 0.23077 | 690 Animal, Other | 0 | 700 Customer-Caused | 0 | 710 Motor Vehicle | 0 | 715 Farming Equipment | 0 | 720 Aircraft | 0 | 730 Fire | 0 | 740 Public Cuts Tree | 0 | 750 Vandalism | 0 | 760 Switching Error or Caused by Construction or Maintenance | 0 | 790 Public, Other | 0 | 800 Other | 0 | 999 Cause Unknown | 0.076923
Tiline | 3202 | 3202-Tiline | Smithland | 32 | 561.4959 |  | 4.1326 | 1.5833 | OK | 108.763 | 2014 | 508.0333 | 173.5578 | OK | Good | 19
Mitchell Store | 3204 | 3204-Mitchell Store | Smithland | 32 | 379.9315 |  | 1.1205 | 3.0295 | PSC | 55.336 | 2014 | 160.3691 | 251.2348 | PSC | More Info Required | 23 | 000 Power Supply | 0.043478 | 100 Construction | 0 | 110 Maintenance | 0 | 190 Other Planned | 0.043478 | 300 Material or equipment fault/failure | 0 | 310 Installation Fault | 0 | 320 Conductor Sag or inadequate clearance | 0 | 340 Overload | 0 | 350 Miscoordination of protection devices | 0 | 360 Other Equipment installation/design | 0 | 400 Decay/Age of Material/Equipment | 0 | 420 Tree Growth | 0.086957 | 430 Tree failure from overhang or dead tree without Ice/snow | 0.30435 | 440 Trees with Ice/snow | 0 | 470 Borrower Crew Cuts Tree | 0 | 490 Maintenance, Other | 0 | 500 Lightning | 0 | 510 Wind, Not Trees | 0.086957 | 520 Ice, Sleet, Frost, not Trees | 0 | 530 Flood | 0 | 540 Storm | 0.043478 | 590 Weather, Other | 0 | 600 Animal/bird | 0 | 630 Squirrel | 0.13043 | 690 Animal, Other | 0 | 700 Customer-Caused | 0 | 710 Motor Vehicle | 0 | 715 Farming Equipment | 0 | 720 Aircraft | 0 | 730 Fire | 0 | 740 Public Cuts Tree | 0 | 750 Vandalism | 0 | 760 Switching Error or Caused by Construction or Maintenance | 0 | 790 Public, Other | 0.043478 | 800 Other | 0.086957 | 999 Cause Unknown | 0.13043
Airport | 3901 | 3901-Airport | Little Union | 39 | 547.1205 |  | 1.2538 | 0.37469 | OK | 35.872 | 2017 | 105.8238 | 23.1905 | OK | Good | 5
US 60 West | 3902 | 3902-US 60 West | Little Union | 39 | 462.537 |  | 0.81773 | 0.41943 | OK | 36.427 | 2017 | 58.4072 | 64.0814 | PSC | More Info Required | 15 | 000 Power Supply | 0 | 100 Construction | 0.2 | 110 Maintenance | 0 | 190 Other Planned | 0 | 300 Material or equipment fault/failure | 0 | 310 Installation Fault | 0 | 320 Conductor Sag or inadequate clearance | 0 | 340 Overload | 0 | 350 Miscoordination of protection devices | 0 | 360 Other Equipment installation/design | 0 | 400 Decay/Age of Material/Equipment | 0 | 420 Tree Growth | 0 | 430 Tree failure from overhang or dead tree without Ice/snow | 0.13333 | 440 Trees with Ice/snow | 0 | 470 Borrower Crew Cuts Tree | 0 | 490 Maintenance, Other | 0 | 500 Lightning | 0.13333 | 510 Wind, Not Trees | 0 | 520 Ice, Sleet, Frost, not Trees | 0 | 530 Flood | 0 | 540 Storm | 0 | 590 Weather, Other | 0 | 600 Animal/bird | 0.066667 | 630 Squirrel | 0 | 690 Animal, Other | 0 | 700 Customer-Caused | 0.13333 | 710 Motor Vehicle | 0 | 715 Farming Equipment | 0 | 720 Aircraft | 0 | 730 Fire | 0 | 740 Public Cuts Tree | 0 | 750 Vandalism | 0 | 760 Switching Error or Caused by Construction or Maintenance | 0 | 790 Public, Other | 0.13333 | 800 Other | 0.066667 | 999 Cause Unknown | 0.13333
US 60 East-K O M | 3903 | 3903-US 60 East Mall | Little Union | 39 | 147.9205 |  | 1.3905 | 0.18929 | OK | 10.354 | 2017 | 64.6298 | 12.4864 | OK | Good | 3
Roy Lee Rd | 3904 | 3904-Roy Lee Rd | Little Union | 39 | 465.9096 |  | 1.1644 | 0.47219 | OK | 51.676 | 2017 | 125.1936 | 28.9648 | OK | Good | 16
Husbands Rd | 4002 | 4002-Husbands Rd | Husbands Road | 40 | 777.1425 |  | 0.80428 | 0.35257 | OK | 44.183 | 2014 | 59.4554 | 20.4467 | OK | Good | 27
Lydon Rd | 4034 | 4034-Lydon Rd | Husbands Road | 40 | 453.0931 |  | 0.75833 | 0.039727 | OK | 31.75 | 2014 | 48.3838 | 2.7676 | OK | Good | 10
Clarkline Rd | 4044 | 4044-Clarkline Rd | Husbands Road | 40 | 300.4516 |  | 0.52975 | 0.18306 | OK | 26.55 | 2014 | 26.1907 | 26.7065 | PSC | More Info Required | 5 | 000 Power Supply | 0 | 100 Construction | 0 | 110 Maintenance | 0.2 | 190 Other Planned | 0 | 300 Material or equipment fault/failure | 0.2 | 310 Installation Fault | 0 | 320 Conductor Sag or inadequate clearance | 0 | 340 Overload | 0 | 350 Miscoordination of protection devices | 0 | 360 Other Equipment installation/design | 0 | 400 Decay/Age of Material/Equipment | 0 | 420 Tree Growth | 0 | 430 Tree failure from overhang or dead tree without Ice/snow | 0.2 | 440 Trees with Ice/snow | 0 | 470 Borrower Crew Cuts Tree | 0 | 490 Maintenance, Other | 0 | 500 Lightning | 0 | 510 Wind, Not Trees | 0 | 520 Ice, Sleet, Frost, not Trees | 0 | 530 Flood | 0 | 540 Storm | 0 | 590 Weather, Other | 0 | 600 Animal/bird | 0 | 630 Squirrel | 0 | 690 Animal, Other | 0 | 700 Customer-Caused | 0 | 710 Motor Vehicle | 0 | 715 Farming Equipment | 0 | 720 Aircraft | 0 | 730 Fire | 0 | 740 Public Cuts Tree | 0 | 750 Vandalism | 0 | 760 Switching Error or Caused by Construction or Maintenance | 0 | 790 Public, Other | 0.2 | 800 Other | 0 | 999 Cause Unknown | 0.2
Ken Mar Rd | 4101 | 4101-Ken Mar Rd | Reidland | 41 | 323.3397 |  | 1.704 | 0.24123 | OK | 19.621 | 2014 | 138.6278 | 14.8884 | OK | Good | 10
Reidland Water | 4102 | 4102-Reidland Water | Reidland | 41 | 53.9342 |  | 0.56 | 1.1681 | PSC | 2.956 | 2014 | 57.9023 | 105.1095 | PSC | More Info Required | 5 | 000 Power Supply | 0 | 100 Construction | 0.2 | 110 Maintenance | 0 | 190 Other Planned | 0 | 300 Material or equipment fault/failure | 0 | 310 Installation Fault | 0 | 320 Conductor Sag or inadequate clearance | 0 | 340 Overload | 0 | 350 Miscoordination of protection devices | 0 | 360 Other Equipment installation/design | 0 | 400 Decay/Age of Material/Equipment | 0 | 420 Tree Growth | 0 | 430 Tree failure from overhang or dead tree without Ice/snow | 0.2 | 440 Trees with Ice/snow | 0 | 470 Borrower Crew Cuts Tree | 0 | 490 Maintenance, Other | 0 | 500 Lightning | 0 | 510 Wind, Not Trees | 0 | 520 Ice, Sleet, Frost, not Trees | 0 | 530 Flood | 0 | 540 Storm | 0 | 590 Weather, Other | 0 | 600 Animal/bird | 0 | 630 Squirrel | 0 | 690 Animal, Other | 0 | 700 Customer-Caused | 0 | 710 Motor Vehicle | 0.2 | 715 Farming Equipment | 0 | 720 Aircraft | 0 | 730 Fire | 0 | 740 Public Cuts Tree | 0 | 750 Vandalism | 0 | 760 Switching Error or Caused by Construction or Maintenance | 0 | 790 Public, Other | 0 | 800 Other | 0 | 999 Cause Unknown | 0.4
Epperson Rd | 4103 | 4103-Epperson Rd | Reidland | 41 | 204.8548 |  | 1.3377 | 0.40028 | OK | 10.082 | 2014 | 161.1884 | 23.7827 | OK | Good | 8
Walker Boat Yard | 4104 | 4104-Walker Boat Yard | Reidland | 41 | 103.9233 |  | 4.5848 | 0.23094 | OK | 11.962 | 2014 | 79.9144 | 16.2812 | OK | Good | 2
Proform | 4201 | 4201-Proform | Culp | 42 | 423.4219 |  | 0.76208 | 1.5682 | PSC | 25.596 | 2014 | 51.791 | 101.0411 | PSC | More Info Required | 18 | 000 Power Supply | 0 | 100 Construction | 0 | 110 Maintenance | 0.055556 | 190 Other Planned | 0 | 300 Material or equipment fault/failure | 0.055556 | 310 Installation Fault | 0 | 320 Conductor Sag or inadequate clearance | 0 | 340 Overload | 0 | 350 Miscoordination of protection devices | 0 | 360 Other Equipment installation/design | 0 | 400 Decay/Age of Material/Equipment | 0 | 420 Tree Growth | 0.11111 | 430 Tree failure from overhang or dead tree without Ice/snow | 0.16667 | 440 Trees with Ice/snow | 0 | 470 Borrower Crew Cuts Tree | 0 | 490 Maintenance, Other | 0 | 500 Lightning | 0 | 510 Wind, Not Trees | 0 | 520 Ice, Sleet, Frost, not Trees | 0 | 530 Flood | 0 | 540 Storm | 0.055556 | 590 Weather, Other | 0 | 600 Animal/bird | 0.055556 | 630 Squirrel | 0.22222 | 690 Animal, Other | 0 | 700 Customer-Caused | 0 | 710 Motor Vehicle | 0 | 715 Farming Equipment | 0 | 720 Aircraft | 0 | 730 Fire | 0 | 740 Public Cuts Tree | 0 | 750 Vandalism | 0 | 760 Switching Error or Caused by Construction or Maintenance | 0 | 790 Public, Other | 0 | 800 Other | 0.055556 | 999 Cause Unknown | 0.22222
Little Cypress | 4202 | 4202-Little Cypress | Culp | 42 | 50.5589 |  | 0.12407 | 1.1274 | PSC | 8.224 | 2014 | 10.7814 | 68.9097 | PSC | More Info Required | 6 | 000 Power Supply | 0 | 100 Construction | 0 | 110 Maintenance | 0 | 190 Other Planned | 0 | 300 Material or equipment fault/failure | 0 | 310 Installation Fault | 0.16667 | 320 Conductor Sag or inadequate clearance | 0 | 340 Overload | 0 | 350 Miscoordination of protection devices | 0 | 360 Other Equipment installation/design | 0.33333 | 400 Decay/Age of Material/Equipment | 0 | 420 Tree Growth | 0.16667 | 430 Tree failure from overhang or dead tree without Ice/snow | 0.16667 | 440 Trees with Ice/snow | 0 | 470 Borrower Crew Cuts Tree | 0 | 490 Maintenance, Other | 0 | 500 Lightning | 0 | 510 Wind, Not Trees | 0 | 520 Ice, Sleet, Frost, not Trees | 0 | 530 Flood | 0 | 540 Storm | 0 | 590 Weather, Other | 0 | 600 Animal/bird | 0 | 630 Squirrel | 0 | 690 Animal, Other | 0 | 700 Customer-Caused | 0 | 710 Motor Vehicle | 0 | 715 Farming Equipment | 0 | 720 Aircraft | 0 | 730 Fire | 0 | 740 Public Cuts Tree | 0 | 750 Vandalism | 0 | 760 Switching Error or Caused by Construction or Maintenance | 0 | 790 Public, Other | 0 | 800 Other | 0 | 999 Cause Unknown | 0.16667
Possum Trot | 4203 | 4203-Possum Trot | Culp | 42 | 205.7068 |  | 0.6293 | 0.11667 | OK | 18.58 | 2014 | 72.5246 | 9.8684 | OK | Good | 13
Sharpe | 4204 | 4204-Sharpe | Culp | 42 | 1068.2438 |  | 0.91444 | 0.55512 | OK | 77.482 | 2014 | 43.6551 | 69.9728 | PSC | More Info Required | 29 | 000 Power Supply | 0 | 100 Construction | 0.034483 | 110 Maintenance | 0.068966 | 190 Other Planned | 0 | 300 Material or equipment fault/failure | 0.10345 | 310 Installation Fault | 0 | 320 Conductor Sag or inadequate clearance | 0 | 340 Overload | 0 | 350 Miscoordination of protection devices | 0 | 360 Other Equipment installation/design | 0.034483 | 400 Decay/Age of Material/Equipment | 0 | 420 Tree Growth | 0 | 430 Tree failure from overhang or dead tree without Ice/snow | 0.068966 | 440 Trees with Ice/snow | 0 | 470 Borrower Crew Cuts Tree | 0 | 490 Maintenance, Other | 0.034483 | 500 Lightning | 0.068966 | 510 Wind, Not Trees | 0.034483 | 520 Ice, Sleet, Frost, not Trees | 0 | 530 Flood | 0 | 540 Storm | 0.034483 | 590 Weather, Other | 0 | 600 Animal/bird | 0.034483 | 630 Squirrel | 0.31034 | 690 Animal, Other | 0 | 700 Customer-Caused | 0 | 710 Motor Vehicle | 0.034483 | 715 Farming Equipment | 0 | 720 Aircraft | 0 | 730 Fire | 0 | 740 Public Cuts Tree | 0 | 750 Vandalism | 0 | 760 Switching Error or Caused by Construction or Maintenance | 0 | 790 Public, Other | 0 | 800 Other | 0 | 999 Cause Unknown | 0.13793
CC/Hwy 95 | 4301 | 4301-Hwy 95 | Calvert City | 43 | 240.8658 |  | 0.99917 | 0.17852 | OK | 18.672 | 2017 | 112.8056 | 15.2159 | OK | Good | 3
CC Hgts | 4302 | 4302-Calvert Heights | Calvert City | 43 | 658.1808 |  | 0.85903 | 0.32514 | OK | 27.83 | 2017 | 74.3044 | 20.9122 | OK | Good | 15
Gilbertsville | 4303 | 4303-Gilbertsville | Calvert City | 43 | 366.4027 |  | 0.48056 | 0.35753 | OK | 23.086 | 2017 | 43.9373 | 117.2508 | PSC | More Info Required | 17 | 000 Power Supply | 0 | 100 Construction | 0 | 110 Maintenance | 0.11765 | 190 Other Planned | 0 | 300 Material or equipment fault/failure | 0.11765 | 310 Installation Fault | 0 | 320 Conductor Sag or inadequate clearance | 0 | 340 Overload | 0 | 350 Miscoordination of protection devices | 0 | 360 Other Equipment installation/design | 0 | 400 Decay/Age of Material/Equipment | 0 | 420 Tree Growth | 0 | 430 Tree failure from overhang or dead tree without Ice/snow | 0.17647 | 440 Trees with Ice/snow | 0 | 470 Borrower Crew Cuts Tree | 0 | 490 Maintenance, Other | 0 | 500 Lightning | 0 | 510 Wind, Not Trees | 0 | 520 Ice, Sleet, Frost, not Trees | 0 | 530 Flood | 0 | 540 Storm | 0.058824 | 590 Weather, Other | 0 | 600 Animal/bird | 0 | 630 Squirrel | 0.058824 | 690 Animal, Other | 0.058824 | 700 Customer-Caused | 0 | 710 Motor Vehicle | 0 | 715 Farming Equipment | 0 | 720 Aircraft | 0 | 730 Fire | 0 | 740 Public Cuts Tree | 0 | 750 Vandalism | 0 | 760 Switching Error or Caused by Construction or Maintenance | 0 | 790 Public, Other | 0 | 800 Other | 0.058824 | 999 Cause Unknown | 0.35294
CC Ind Park | 4304 | 4304-Industrial Park | Calvert City | 43 | 0 |  | 0.42466 | 0 | OK | 4.87 | 2017 | 38.7715 | 0 | OK | Good | 0
Vulcan Pit | 4502 | 4502-Vulcan Pit | Vulcan | 45 | 0 |  | 0.2 | 0 | OK | 2.39 | 2016 | 25.4 | 0 | OK | Good | 0
Vulcan 1-Rock Crusher | 4503 | 4503-Vulcan1 Rock Crusher | Vulcan | 45 | 2 |  | 0.2 | 1.5 | PSC | 1.273 | 2016 | 30.9 | 190 | PSC | More Info Required | 3 | 000 Power Supply | 0 | 100 Construction | 0 | 110 Maintenance | 0 | 190 Other Planned | 0 | 300 Material or equipment fault/failure | 0 | 310 Installation Fault | 0 | 320 Conductor Sag or inadequate clearance | 0 | 340 Overload | 0 | 350 Miscoordination of protection devices | 0 | 360 Other Equipment installation/design | 0.33333 | 400 Decay/Age of Material/Equipment | 0 | 420 Tree Growth | 0 | 430 Tree failure from overhang or dead tree without Ice/snow | 0 | 440 Trees with Ice/snow | 0 | 470 Borrower Crew Cuts Tree | 0 | 490 Maintenance, Other | 0 | 500 Lightning | 0 | 510 Wind, Not Trees | 0 | 520 Ice, Sleet, Frost, not Trees | 0 | 530 Flood | 0 | 540 Storm | 0 | 590 Weather, Other | 0 | 600 Animal/bird | 0 | 630 Squirrel | 0 | 690 Animal, Other | 0 | 700 Customer-Caused | 0 | 710 Motor Vehicle | 0 | 715 Farming Equipment | 0 | 720 Aircraft | 0 | 730 Fire | 0 | 740 Public Cuts Tree | 0 | 750 Vandalism | 0 | 760 Switching Error or Caused by Construction or Maintenance | 0 | 790 Public, Other | 0 | 800 Other | 0.33333 | 999 Cause Unknown | 0.33333
Kinder Morgan 1 | 4504 | 4504-Kinder Morgan 1 | Vulcan | 45 | 31.6438 |  | 0.8746 | 1.9277 | PSC | 7.774 | 2016 | 111.965 | 378.5571 | PSC | More Info Required | 3 | 000 Power Supply | 0 | 100 Construction | 0 | 110 Maintenance | 0 | 190 Other Planned | 0 | 300 Material or equipment fault/failure | 0 | 310 Installation Fault | 0 | 320 Conductor Sag or inadequate clearance | 0 | 340 Overload | 0 | 350 Miscoordination of protection devices | 0 | 360 Other Equipment installation/design | 0.33333 | 400 Decay/Age of Material/Equipment | 0 | 420 Tree Growth | 0 | 430 Tree failure from overhang or dead tree without Ice/snow | 0.33333 | 440 Trees with Ice/snow | 0 | 470 Borrower Crew Cuts Tree | 0 | 490 Maintenance, Other | 0 | 500 Lightning | 0 | 510 Wind, Not Trees | 0 | 520 Ice, Sleet, Frost, not Trees | 0 | 530 Flood | 0 | 540 Storm | 0 | 590 Weather, Other | 0 | 600 Animal/bird | 0 | 630 Squirrel | 0 | 690 Animal, Other | 0 | 700 Customer-Caused | 0 | 710 Motor Vehicle | 0 | 715 Farming Equipment | 0 | 720 Aircraft | 0 | 730 Fire | 0 | 740 Public Cuts Tree | 0 | 750 Vandalism | 0 | 760 Switching Error or Caused by Construction or Maintenance | 0 | 790 Public, Other | 0 | 800 Other | 0.33333 | 999 Cause Unknown | 0
Vulcan 2 Hwy 62 | 4505 | 4505-Vulcan 2 Hwy 62 | Vulcan | 45 | 3 |  | 0.38182 | 0.66667 | PSC | 5.015 | 2016 | 49.7091 | 134 | PSC | More Info Required | 1 | 000 Power Supply | 0 | 100 Construction | 0 | 110 Maintenance | 0 | 190 Other Planned | 0 | 300 Material or equipment fault/failure | 0 | 310 Installation Fault | 0 | 320 Conductor Sag or inadequate clearance | 0 | 340 Overload | 0 | 350 Miscoordination of protection devices | 0 | 360 Other Equipment installation/design | 1 | 400 Decay/Age of Material/Equipment | 0 | 420 Tree Growth | 0 | 430 Tree failure from overhang or dead tree without Ice/snow | 0 | 440 Trees with Ice/snow | 0 | 470 Borrower Crew Cuts Tree | 0 | 490 Maintenance, Other | 0 | 500 Lightning | 0 | 510 Wind, Not Trees | 0 | 520 Ice, Sleet, Frost, not Trees | 0 | 530 Flood | 0 | 540 Storm | 0 | 590 Weather, Other | 0 | 600 Animal/bird | 0 | 630 Squirrel | 0 | 690 Animal, Other | 0 | 700 Customer-Caused | 0 | 710 Motor Vehicle | 0 | 715 Farming Equipment | 0 | 720 Aircraft | 0 | 730 Fire | 0 | 740 Public Cuts Tree | 0 | 750 Vandalism | 0 | 760 Switching Error or Caused by Construction or Maintenance | 0 | 790 Public, Other | 0 | 800 Other | 0 | 999 Cause Unknown | 0
Hinkleville | 4701 | 4701-Hinkleville | New York | 47 | 264.4082 |  | 1.6967 | 2.602 | PSC | 44.517 | 2017 | 182.2732 | 311.2763 | PSC | More Info Required | 25 | 000 Power Supply | 0 | 100 Construction | 0.16 | 110 Maintenance | 0.16 | 190 Other Planned | 0 | 300 Material or equipment fault/failure | 0.08 | 310 Installation Fault | 0 | 320 Conductor Sag or inadequate clearance | 0.04 | 340 Overload | 0 | 350 Miscoordination of protection devices | 0 | 360 Other Equipment installation/design | 0 | 400 Decay/Age of Material/Equipment | 0 | 420 Tree Growth | 0 | 430 Tree failure from overhang or dead tree without Ice/snow | 0 | 440 Trees with Ice/snow | 0 | 470 Borrower Crew Cuts Tree | 0 | 490 Maintenance, Other | 0 | 500 Lightning | 0.08 | 510 Wind, Not Trees | 0 | 520 Ice, Sleet, Frost, not Trees | 0 | 530 Flood | 0 | 540 Storm | 0 | 590 Weather, Other | 0 | 600 Animal/bird | 0 | 630 Squirrel | 0.2 | 690 Animal, Other | 0.04 | 700 Customer-Caused | 0 | 710 Motor Vehicle | 0 | 715 Farming Equipment | 0 | 720 Aircraft | 0 | 730 Fire | 0 | 740 Public Cuts Tree | 0 | 750 Vandalism | 0 | 760 Switching Error or Caused by Construction or Maintenance | 0 | 790 Public, Other | 0 | 800 Other | 0.04 | 999 Cause Unknown | 0.2
US 286 East-Gage | 4702 | 4702-US 286 East Gage | New York | 47 | 267.2795 |  | 1.0878 | 2.5105 | PSC | 45.25 | 2017 | 97.3717 | 304.9916 | PSC | More Info Required | 20 | 000 Power Supply | 0 | 100 Construction | 0.1 | 110 Maintenance | 0.3 | 190 Other Planned | 0 | 300 Material or equipment fault/failure | 0.05 | 310 Installation Fault | 0 | 320 Conductor Sag or inadequate clearance | 0 | 340 Overload | 0 | 350 Miscoordination of protection devices | 0 | 360 Other Equipment installation/design | 0 | 400 Decay/Age of Material/Equipment | 0 | 420 Tree Growth | 0 | 430 Tree failure from overhang or dead tree without Ice/snow | 0.2 | 440 Trees with Ice/snow | 0 | 470 Borrower Crew Cuts Tree | 0 | 490 Maintenance, Other | 0 | 500 Lightning | 0.05 | 510 Wind, Not Trees | 0 | 520 Ice, Sleet, Frost, not Trees | 0 | 530 Flood | 0 | 540 Storm | 0 | 590 Weather, Other | 0 | 600 Animal/bird | 0.05 | 630 Squirrel | 0.1 | 690 Animal, Other | 0 | 700 Customer-Caused | 0 | 710 Motor Vehicle | 0.1 | 715 Farming Equipment | 0 | 720 Aircraft | 0 | 730 Fire | 0 | 740 Public Cuts Tree | 0 | 750 Vandalism | 0 | 760 Switching Error or Caused by Construction or Maintenance | 0 | 790 Public, Other | 0 | 800 Other | 0 | 999 Cause Unknown | 0.05
Blandville | 4703 | 4703-Blandville | New York | 47 | 228.1178 |  | 2.5146 | 1.9376 | OK | 30.357 | 2017 | 292.5424 | 279.4959 | OK | Good | 12
Wickliffe | 4704 | 4704-Wickliffe | New York | 47 | 354.4932 |  | 1.0045 | 2.993 | PSC | 49.217 | 2017 | 102.9242 | 337.4565 | PSC | More Info Required | 26 | 000 Power Supply | 0 | 100 Construction | 0.076923 | 110 Maintenance | 0 | 190 Other Planned | 0 | 300 Material or equipment fault/failure | 0.038462 | 310 Installation Fault | 0 | 320 Conductor Sag or inadequate clearance | 0 | 340 Overload | 0 | 350 Miscoordination of protection devices | 0 | 360 Other Equipment installation/design | 0 | 400 Decay/Age of Material/Equipment | 0 | 420 Tree Growth | 0.11538 | 430 Tree failure from overhang or dead tree without Ice/snow | 0.38462 | 440 Trees with Ice/snow | 0 | 470 Borrower Crew Cuts Tree | 0 | 490 Maintenance, Other | 0 | 500 Lightning | 0.038462 | 510 Wind, Not Trees | 0 | 520 Ice, Sleet, Frost, not Trees | 0 | 530 Flood | 0 | 540 Storm | 0.038462 | 590 Weather, Other | 0 | 600 Animal/bird | 0 | 630 Squirrel | 0.11538 | 690 Animal, Other | 0.038462 | 700 Customer-Caused | 0 | 710 Motor Vehicle | 0 | 715 Farming Equipment | 0 | 720 Aircraft | 0 | 730 Fire | 0 | 740 Public Cuts Tree | 0 | 750 Vandalism | 0 | 760 Switching Error or Caused by Construction or Maintenance | 0 | 790 Public, Other | 0 | 800 Other | 0.038462 | 999 Cause Unknown | 0.11538
Slater | 4705 | 4705-Slater | New York | 47 | 346.211 |  | 1.1919 | 3.8849 | PSC | 68.382 | 2017 | 149.4221 | 325.1544 | PSC | More Info Required | 34 | 000 Power Supply | 0 | 100 Construction | 0 | 110 Maintenance | 0.029412 | 190 Other Planned | 0 | 300 Material or equipment fault/failure | 0.11765 | 310 Installation Fault | 0 | 320 Conductor Sag or inadequate clearance | 0 | 340 Overload | 0 | 350 Miscoordination of protection devices | 0 | 360 Other Equipment installation/design | 0.058824 | 400 Decay/Age of Material/Equipment | 0 | 420 Tree Growth | 0.029412 | 430 Tree failure from overhang or dead tree without Ice/snow | 0.11765 | 440 Trees with Ice/snow | 0 | 470 Borrower Crew Cuts Tree | 0 | 490 Maintenance, Other | 0 | 500 Lightning | 0.058824 | 510 Wind, Not Trees | 0.029412 | 520 Ice, Sleet, Frost, not Trees | 0 | 530 Flood | 0 | 540 Storm | 0.058824 | 590 Weather, Other | 0.029412 | 600 Animal/bird | 0 | 630 Squirrel | 0.029412 | 690 Animal, Other | 0 | 700 Customer-Caused | 0.029412 | 710 Motor Vehicle | 0 | 715 Farming Equipment | 0.029412 | 720 Aircraft | 0 | 730 Fire | 0 | 740 Public Cuts Tree | 0 | 750 Vandalism | 0 | 760 Switching Error or Caused by Construction or Maintenance | 0 | 790 Public, Other | 0.029412 | 800 Other | 0.11765 | 999 Cause Unknown | 0.23529
Blandville | 4901 | 4901-Blandville | Lovelaceville | 49 | 134.5644 |  | 0.9882 | 2.1328 | PSC | 20.368 | 2015 | 122.5094 | 116.9998 | OK | More Info Required | 3 | 000 Power Supply | 0 | 100 Construction | 0 | 110 Maintenance | 0 | 190 Other Planned | 0 | 300 Material or equipment fault/failure | 0 | 310 Installation Fault | 0 | 320 Conductor Sag or inadequate clearance | 0 | 340 Overload | 0 | 350 Miscoordination of protection devices | 0 | 360 Other Equipment installation/design | 0 | 400 Decay/Age of Material/Equipment | 0 | 420 Tree Growth | 0 | 430 Tree failure from overhang or dead tree without Ice/snow | 0.66667 | 440 Trees with Ice/snow | 0 | 470 Borrower Crew Cuts Tree | 0 | 490 Maintenance, Other | 0 | 500 Lightning | 0 | 510 Wind, Not Trees | 0 | 520 Ice, Sleet, Frost, not Trees | 0 | 530 Flood | 0 | 540 Storm | 0 | 590 Weather, Other | 0 | 600 Animal/bird | 0 | 630 Squirrel | 0 | 690 Animal, Other | 0 | 700 Customer-Caused | 0 | 710 Motor Vehicle | 0 | 715 Farming Equipment | 0.33333 | 720 Aircraft | 0 | 730 Fire | 0 | 740 Public Cuts Tree | 0 | 750 Vandalism | 0 | 760 Switching Error or Caused by Construction or Maintenance | 0 | 790 Public, Other | 0 | 800 Other | 0 | 999 Cause Unknown | 0
Lovelaceville | 4902 | 4902-Lovelaceville | Lovelaceville | 49 | 521.0575 |  | 0.70394 | 0.82908 | PSC | 57.681 | 2015 | 68.8287 | 257.2173 | PSC | More Info Required | 19 | 000 Power Supply | 0 | 100 Construction | 0 | 110 Maintenance | 0.21053 | 190 Other Planned | 0 | 300 Material or equipment fault/failure | 0.052632 | 310 Installation Fault | 0 | 320 Conductor Sag or inadequate clearance | 0 | 340 Overload | 0 | 350 Miscoordination of protection devices | 0 | 360 Other Equipment installation/design | 0 | 400 Decay/Age of Material/Equipment | 0 | 420 Tree Growth | 0 | 430 Tree failure from overhang or dead tree without Ice/snow | 0 | 440 Trees with Ice/snow | 0 | 470 Borrower Crew Cuts Tree | 0 | 490 Maintenance, Other | 0 | 500 Lightning | 0 | 510 Wind, Not Trees | 0 | 520 Ice, Sleet, Frost, not Trees | 0 | 530 Flood | 0 | 540 Storm | 0 | 590 Weather, Other | 0 | 600 Animal/bird | 0.052632 | 630 Squirrel | 0 | 690 Animal, Other | 0 | 700 Customer-Caused | 0 | 710 Motor Vehicle | 0.42105 | 715 Farming Equipment | 0 | 720 Aircraft | 0 | 730 Fire | 0 | 740 Public Cuts Tree | 0 | 750 Vandalism | 0 | 760 Switching Error or Caused by Construction or Maintenance | 0 | 790 Public, Other | 0 | 800 Other | 0.10526 | 999 Cause Unknown | 0.15789
Cunningham | 4903 | 4903-Cunningham | Lovelaceville | 49 | 527.8521 |  | 1.388 | 0.9946 | OK | 64.468 | 2015 | 132.8838 | 217.345 | PSC | More Info Required | 20 | 000 Power Supply | 0 | 100 Construction | 0.05 | 110 Maintenance | 0.1 | 190 Other Planned | 0 | 300 Material or equipment fault/failure | 0.05 | 310 Installation Fault | 0 | 320 Conductor Sag or inadequate clearance | 0 | 340 Overload | 0 | 350 Miscoordination of protection devices | 0 | 360 Other Equipment installation/design | 0 | 400 Decay/Age of Material/Equipment | 0 | 420 Tree Growth | 0.05 | 430 Tree failure from overhang or dead tree without Ice/snow | 0.3 | 440 Trees with Ice/snow | 0 | 470 Borrower Crew Cuts Tree | 0 | 490 Maintenance, Other | 0 | 500 Lightning | 0.05 | 510 Wind, Not Trees | 0 | 520 Ice, Sleet, Frost, not Trees | 0 | 530 Flood | 0 | 540 Storm | 0 | 590 Weather, Other | 0 | 600 Animal/bird | 0.05 | 630 Squirrel | 0 | 690 Animal, Other | 0.05 | 700 Customer-Caused | 0 | 710 Motor Vehicle | 0 | 715 Farming Equipment | 0.05 | 720 Aircraft | 0 | 730 Fire | 0 | 740 Public Cuts Tree | 0 | 750 Vandalism | 0 | 760 Switching Error or Caused by Construction or Maintenance | 0 | 790 Public, Other | 0 | 800 Other | 0.2 | 999 Cause Unknown | 0.05
Browns Plating | 5001 | 5001-Browns Plating | Krebs Station Road | 50 | 511.1973 |  | 1.4142 | 1.2598 | OK | 36.923 | 2016 | 105.7357 | 142.9663 | PSC | More Info Required | 23 | 000 Power Supply | 0 | 100 Construction | 0.086957 | 110 Maintenance | 0.13043 | 190 Other Planned | 0 | 300 Material or equipment fault/failure | 0.043478 | 310 Installation Fault | 0 | 320 Conductor Sag or inadequate clearance | 0 | 340 Overload | 0 | 350 Miscoordination of protection devices | 0 | 360 Other Equipment installation/design | 0 | 400 Decay/Age of Material/Equipment | 0 | 420 Tree Growth | 0 | 430 Tree failure from overhang or dead tree without Ice/snow | 0.21739 | 440 Trees with Ice/snow | 0 | 470 Borrower Crew Cuts Tree | 0 | 490 Maintenance, Other | 0.043478 | 500 Lightning | 0.043478 | 510 Wind, Not Trees | 0 | 520 Ice, Sleet, Frost, not Trees | 0 | 530 Flood | 0 | 540 Storm | 0.13043 | 590 Weather, Other | 0 | 600 Animal/bird | 0.043478 | 630 Squirrel | 0.086957 | 690 Animal, Other | 0 | 700 Customer-Caused | 0 | 710 Motor Vehicle | 0 | 715 Farming Equipment | 0.086957 | 720 Aircraft | 0 | 730 Fire | 0 | 740 Public Cuts Tree | 0 | 750 Vandalism | 0 | 760 Switching Error or Caused by Construction or Maintenance | 0 | 790 Public, Other | 0.043478 | 800 Other | 0 | 999 Cause Unknown | 0.043478
Old US 45 | 5002 | 5002-Old US 45 | Krebs Station Road | 50 | 862.8411 |  | 2.6155 | 1.0697 | OK | 77.238 | 2016 | 248.2148 | 89.298 | OK | Good | 33
Clinton Road | 5003 | 5003-Clinton Rd | Krebs Station Road | 50 | 599.9288 |  | 1.1876 | 0.40671 | OK | 52.268 | 2016 | 110.207 | 43.8669 | OK | Good | 31
Symsonia | 5101 | 5101-Symsonia | Freemont | 51 | 1016.5973 |  | 1.5802 | 0.34527 | OK | 93.592 | 2014 | 149.0779 | 49.9716 | OK | Good | 41
Mc Neil Lane | 5102 | 5102-McNeil Lane | Freemont | 51 | 386.4055 |  | 1.7928 | 1.677 | OK | 45.863 | 2014 | 206.3683 | 211.5084 | PSC | More Info Required | 16 | 000 Power Supply | 0 | 100 Construction | 0.125 | 110 Maintenance | 0 | 190 Other Planned | 0 | 300 Material or equipment fault/failure | 0 | 310 Installation Fault | 0 | 320 Conductor Sag or inadequate clearance | 0 | 340 Overload | 0 | 350 Miscoordination of protection devices | 0 | 360 Other Equipment installation/design | 0 | 400 Decay/Age of Material/Equipment | 0 | 420 Tree Growth | 0 | 430 Tree failure from overhang or dead tree without Ice/snow | 0.25 | 440 Trees with Ice/snow | 0 | 470 Borrower Crew Cuts Tree | 0 | 490 Maintenance, Other | 0 | 500 Lightning | 0.1875 | 510 Wind, Not Trees | 0 | 520 Ice, Sleet, Frost, not Trees | 0 | 530 Flood | 0 | 540 Storm | 0 | 590 Weather, Other | 0 | 600 Animal/bird | 0.0625 | 630 Squirrel | 0.1875 | 690 Animal, Other | 0 | 700 Customer-Caused | 0 | 710 Motor Vehicle | 0 | 715 Farming Equipment | 0 | 720 Aircraft | 0 | 730 Fire | 0 | 740 Public Cuts Tree | 0.0625 | 750 Vandalism | 0 | 760 Switching Error or Caused by Construction or Maintenance | 0 | 790 Public, Other | 0 | 800 Other | 0.0625 | 999 Cause Unknown | 0.0625
Freemont | 5104 | 5104-Freemont | Freemont | 51 | 356.7151 |  | 0.51813 | 0.16259 | OK | 25.765 | 2014 | 43.6511 | 19.1581 | OK | Good | 18
Bonds Rd | 5105 | 5105-Bonds Rd | Freemont | 51 | 122.0438 |  | 1.4504 | 1.9993 | PSC | 17.668 | 2014 | 112.6013 | 166.1944 | PSC | More Info Required | 4 | 000 Power Supply | 0 | 100 Construction | 0.25 | 110 Maintenance | 0 | 190 Other Planned | 0 | 300 Material or equipment fault/failure | 0 | 310 Installation Fault | 0 | 320 Conductor Sag or inadequate clearance | 0 | 340 Overload | 0 | 350 Miscoordination of protection devices | 0 | 360 Other Equipment installation/design | 0 | 400 Decay/Age of Material/Equipment | 0 | 420 Tree Growth | 0 | 430 Tree failure from overhang or dead tree without Ice/snow | 0.25 | 440 Trees with Ice/snow | 0 | 470 Borrower Crew Cuts Tree | 0 | 490 Maintenance, Other | 0 | 500 Lightning | 0 | 510 Wind, Not Trees | 0.25 | 520 Ice, Sleet, Frost, not Trees | 0 | 530 Flood | 0 | 540 Storm | 0 | 590 Weather, Other | 0.25 | 600 Animal/bird | 0 | 630 Squirrel | 0 | 690 Animal, Other | 0 | 700 Customer-Caused | 0 | 710 Motor Vehicle | 0 | 715 Farming Equipment | 0 | 720 Aircraft | 0 | 730 Fire | 0 | 740 Public Cuts Tree | 0 | 750 Vandalism | 0 | 760 Switching Error or Caused by Construction or Maintenance | 0 | 790 Public, Other | 0 | 800 Other | 0 | 999 Cause Unknown | 0
Hwy 95 N to Hwy 62 | 54214 | 54214-Hwy 95 | Palma | 54 | 355.3534 |  | 1.6939 | 1.1341 | OK | 29.367 | 2014 | 149.1177 | 92.8287 | OK | Good | 27
Draffenville | 54224 | 54224-Draffenville | Palma | 54 | 281.9479 |  | 0.26975 | 0.049655 | OK | 20.953 | 2014 | 17.9538 | 5.9373 | OK | Good | 6
Palma | 54234 | 54234-Palma | Palma | 54 | 728.9918 |  | 0.83528 | 0.17833 | OK | 55.927 | 2014 | 54.0455 | 22.6038 | OK | Good | 10
Lowes | 6101 | 6101-Lowes | Kansas | 61 | 456.5315 |  | 0.4698 | 1.3274 | PSC | 58.526 | 2016 | 57.0814 | 97.3142 | PSC | More Info Required | 22 | 000 Power Supply | 0 | 100 Construction | 0.090909 | 110 Maintenance | 0.27273 | 190 Other Planned | 0 | 300 Material or equipment fault/failure | 0.045455 | 310 Installation Fault | 0 | 320 Conductor Sag or inadequate clearance | 0 | 340 Overload | 0 | 350 Miscoordination of protection devices | 0 | 360 Other Equipment installation/design | 0 | 400 Decay/Age of Material/Equipment | 0 | 420 Tree Growth | 0 | 430 Tree failure from overhang or dead tree without Ice/snow | 0.090909 | 440 Trees with Ice/snow | 0 | 470 Borrower Crew Cuts Tree | 0 | 490 Maintenance, Other | 0.13636 | 500 Lightning | 0.045455 | 510 Wind, Not Trees | 0 | 520 Ice, Sleet, Frost, not Trees | 0 | 530 Flood | 0 | 540 Storm | 0 | 590 Weather, Other | 0 | 600 Animal/bird | 0 | 630 Squirrel | 0.045455 | 690 Animal, Other | 0 | 700 Customer-Caused | 0 | 710 Motor Vehicle | 0 | 715 Farming Equipment | 0 | 720 Aircraft | 0 | 730 Fire | 0 | 740 Public Cuts Tree | 0.045455 | 750 Vandalism | 0 | 760 Switching Error or Caused by Construction or Maintenance | 0 | 790 Public, Other | 0.045455 | 800 Other | 0.045455 | 999 Cause Unknown | 0.13636
US 45-Folsomdale | 6102 | 6102-US 45 Folsomdale | Kansas | 61 | 214.9205 |  | 0.71238 | 0.30244 | OK | 29.264 | 2016 | 96.2849 | 25.5304 | OK | Good | 17
Melber | 6103 | 6103-Melber | Kansas | 61 | 529.989 |  | 0.85325 | 0.2434 | OK | 52.228 | 2016 | 98.7613 | 39.9065 | OK | Good | 25
Pottsville | 6104 | 6104-Pottsville | Kansas | 61 | 356.2849 |  | 1.6857 | 0.99078 | OK | 46.749 | 2016 | 212.8012 | 175.8705 | OK | Good | 25
Draffenville | 6601 | 6601-Draffenville | Draffenville | 66 | 471.8603 |  | 0.94361 | 0.036028 | OK | 28.798 | 2014 | 88.8938 | 5.1689 | OK | Good | 11
Olivet Ch Rd | 7401 | 7401-Info Age Park | Olivet Church Road | 74 | 552.1233 |  | 0.65697 | 0.052525 | OK | 21.238 | 2015 | 29.9031 | 3.8669 | OK | Good | 5
Highland Ch Rd | 7402 | 7402-Highland Ch Rd | Olivet Church Road | 74 | 450.9425 |  | 0.92673 | 0.45682 | OK | 35.822 | 2015 | 67.7998 | 40.7968 | OK | Good | 19
Info Age Park | 7403 | 7403-Info Age Park | Olivet Church Road | 74 | 0 |  | 0 | 0 | OK | 2.438 | 2015 | 0 | 0 | OK | Good | 0
Iuka | 7601 | 7601-Iuka | Grand Rivers | 76 | 296.5808 |  | 2.5053 | 4.8655 | PSC | 47.35 | 2016 | 314.751 | 390.477 | PSC | More Info Required | 16 | 000 Power Supply | 0 | 100 Construction | 0.0625 | 110 Maintenance | 0 | 190 Other Planned | 0 | 300 Material or equipment fault/failure | 0.0625 | 310 Installation Fault | 0 | 320 Conductor Sag or inadequate clearance | 0 | 340 Overload | 0 | 350 Miscoordination of protection devices | 0 | 360 Other Equipment installation/design | 0.125 | 400 Decay/Age of Material/Equipment | 0 | 420 Tree Growth | 0 | 430 Tree failure from overhang or dead tree without Ice/snow | 0.25 | 440 Trees with Ice/snow | 0 | 470 Borrower Crew Cuts Tree | 0 | 490 Maintenance, Other | 0.0625 | 500 Lightning | 0 | 510 Wind, Not Trees | 0 | 520 Ice, Sleet, Frost, not Trees | 0 | 530 Flood | 0 | 540 Storm | 0 | 590 Weather, Other | 0 | 600 Animal/bird | 0 | 630 Squirrel | 0.0625 | 690 Animal, Other | 0 | 700 Customer-Caused | 0 | 710 Motor Vehicle | 0 | 715 Farming Equipment | 0 | 720 Aircraft | 0 | 730 Fire | 0 | 740 Public Cuts Tree | 0 | 750 Vandalism | 0 | 760 Switching Error or Caused by Construction or Maintenance | 0 | 790 Public, Other | 0.0625 | 800 Other | 0.0625 | 999 Cause Unknown | 0.25
Smithland | 7602 | 7602-Smithland | Grand Rivers | 76 | 282.8466 |  | 1.0594 | 6.8093 | PSC | 30.075 | 2016 | 97.1984 | 496.7074 | PSC | More Info Required | 17 | 000 Power Supply | 0 | 100 Construction | 0 | 110 Maintenance | 0.11765 | 190 Other Planned | 0 | 300 Material or equipment fault/failure | 0.058824 | 310 Installation Fault | 0 | 320 Conductor Sag or inadequate clearance | 0.058824 | 340 Overload | 0 | 350 Miscoordination of protection devices | 0 | 360 Other Equipment installation/design | 0.058824 | 400 Decay/Age of Material/Equipment | 0 | 420 Tree Growth | 0 | 430 Tree failure from overhang or dead tree without Ice/snow | 0.058824 | 440 Trees with Ice/snow | 0 | 470 Borrower Crew Cuts Tree | 0 | 490 Maintenance, Other | 0 | 500 Lightning | 0.058824 | 510 Wind, Not Trees | 0.058824 | 520 Ice, Sleet, Frost, not Trees | 0 | 530 Flood | 0 | 540 Storm | 0.058824 | 590 Weather, Other | 0 | 600 Animal/bird | 0 | 630 Squirrel | 0 | 690 Animal, Other | 0 | 700 Customer-Caused | 0 | 710 Motor Vehicle | 0 | 715 Farming Equipment | 0 | 720 Aircraft | 0 | 730 Fire | 0 | 740 Public Cuts Tree | 0 | 750 Vandalism | 0 | 760 Switching Error or Caused by Construction or Maintenance | 0 | 790 Public, Other | 0.058824 | 800 Other | 0.23529 | 999 Cause Unknown | 0.17647
Pelican-GR #1 | 7604 | 7604-Pelican GR #1 | Grand Rivers | 76 | 371.6493 |  | 0.63108 | 4.3294 | PSC | 24.039 | 2016 | 71.3132 | 485.9447 | PSC | More Info Required | 14 | 000 Power Supply | 0 | 100 Construction | 0.071429 | 110 Maintenance | 0 | 190 Other Planned | 0 | 300 Material or equipment fault/failure | 0 | 310 Installation Fault | 0 | 320 Conductor Sag or inadequate clearance | 0 | 340 Overload | 0 | 350 Miscoordination of protection devices | 0 | 360 Other Equipment installation/design | 0.071429 | 400 Decay/Age of Material/Equipment | 0 | 420 Tree Growth | 0 | 430 Tree failure from overhang or dead tree without Ice/snow | 0 | 440 Trees with Ice/snow | 0 | 470 Borrower Crew Cuts Tree | 0 | 490 Maintenance, Other | 0 | 500 Lightning | 0 | 510 Wind, Not Trees | 0 | 520 Ice, Sleet, Frost, not Trees | 0 | 530 Flood | 0 | 540 Storm | 0 | 590 Weather, Other | 0 | 600 Animal/bird | 0 | 630 Squirrel | 0.21429 | 690 Animal, Other | 0 | 700 Customer-Caused | 0 | 710 Motor Vehicle | 0.071429 | 715 Farming Equipment | 0 | 720 Aircraft | 0 | 730 Fire | 0 | 740 Public Cuts Tree | 0 | 750 Vandalism | 0 | 760 Switching Error or Caused by Construction or Maintenance | 0 | 790 Public, Other | 0.14286 | 800 Other | 0.071429 | 999 Cause Unknown | 0.35714
Averitt-GR #2 | 7605 | 7605-Averitt GR #2 | Grand Rivers | 76 | 666.4822 |  | 1.8423 | 4.0301 | PSC | 43.336 | 2016 | 204.5405 | 314.367 | PSC | More Info Required | 13 | 000 Power Supply | 0 | 100 Construction | 0.076923 | 110 Maintenance | 0 | 190 Other Planned | 0 | 300 Material or equipment fault/failure | 0 | 310 Installation Fault | 0 | 320 Conductor Sag or inadequate clearance | 0 | 340 Overload | 0 | 350 Miscoordination of protection devices | 0 | 360 Other Equipment installation/design | 0.076923 | 400 Decay/Age of Material/Equipment | 0 | 420 Tree Growth | 0 | 430 Tree failure from overhang or dead tree without Ice/snow | 0.15385 | 440 Trees with Ice/snow | 0 | 470 Borrower Crew Cuts Tree | 0 | 490 Maintenance, Other | 0.076923 | 500 Lightning | 0 | 510 Wind, Not Trees | 0 | 520 Ice, Sleet, Frost, not Trees | 0 | 530 Flood | 0 | 540 Storm | 0 | 590 Weather, Other | 0 | 600 Animal/bird | 0.076923 | 630 Squirrel | 0 | 690 Animal, Other | 0 | 700 Customer-Caused | 0 | 710 Motor Vehicle | 0.076923 | 715 Farming Equipment | 0 | 720 Aircraft | 0 | 730 Fire | 0 | 740 Public Cuts Tree | 0 | 750 Vandalism | 0 | 760 Switching Error or Caused by Construction or Maintenance | 0 | 790 Public, Other | 0.076923 | 800 Other | 0.15385 | 999 Cause Unknown | 0.23077
Hansen Rd-Top Circuit | 7702 | 7702-Hansen Rd | Strawberry Hill | 77 | 637.9479 |  | 0.93051 | 0.33232 | OK | 29.532 | 2015 | 84.5349 | 28.4914 | OK | Good | 10
Walmart-Hansen Rd Bottom | 7703 | 7703-Walmart | Strawberry Hill | 77 | 481.3425 |  | 0.1048 | 1.0076 | PSC | 8.867 | 2015 | 5.5926 | 39.7098 | PSC | More Info Required | 3 | 000 Power Supply | 0 | 100 Construction | 0 | 110 Maintenance | 0 | 190 Other Planned | 0 | 300 Material or equipment fault/failure | 0 | 310 Installation Fault | 0 | 320 Conductor Sag or inadequate clearance | 0 | 340 Overload | 0 | 350 Miscoordination of protection devices | 0 | 360 Other Equipment installation/design | 0 | 400 Decay/Age of Material/Equipment | 0 | 420 Tree Growth | 0 | 430 Tree failure from overhang or dead tree without Ice/snow | 0 | 440 Trees with Ice/snow | 0 | 470 Borrower Crew Cuts Tree | 0 | 490 Maintenance, Other | 0 | 500 Lightning | 0 | 510 Wind, Not Trees | 0 | 520 Ice, Sleet, Frost, not Trees | 0 | 530 Flood | 0 | 540 Storm | 0 | 590 Weather, Other | 0 | 600 Animal/bird | 0 | 630 Squirrel | 0.33333 | 690 Animal, Other | 0 | 700 Customer-Caused | 0 | 710 Motor Vehicle | 0 | 715 Farming Equipment | 0 | 720 Aircraft | 0 | 730 Fire | 0 | 740 Public Cuts Tree | 0 | 750 Vandalism | 0 | 760 Switching Error or Caused by Construction or Maintenance | 0 | 790 Public, Other | 0 | 800 Other | 0 | 999 Cause Unknown | 0.66667
CSI--Jas Sanders-Botom Cir | 7705 | 7705-CSI | Strawberry Hill | 77 | 85.2055 |  | 2.0718 | 0.058682 | OK | 4.887 | 2015 | 120.8475 | 1.5492 | OK | Good | 2
Hwy 60-Jas Sanders-Top Cir | 7706 | 7706-Hwy 60 | Strawberry Hill | 77 | 0 |  | 0.034671 | 0 | OK | 1.623 | 2015 | 3.3631 | 0 | OK | Good | 0
Hwy 95 North | 7802 | 7802-Possum Trot | Possum Trot | 78 | 536.4219 |  | 0.77106 | 0.2759 | OK | 42.372 | 2015 | 54.7758 | 23.4069 | OK | Good | 21
Possum Trot | 7803 | 7803-Hwy 95 | Possum Trot | 78 | 193.4356 |  | 0.66116 | 0.1706 | OK | 15.003 | 2015 | 45.0853 | 23.4342 | OK | Good | 7
Industrial Loop North | 7805 | 7805-Industrial Loop | Possum Trot | 78 | 208.6137 |  | 1.8246 | 0.45539 | OK | 28.697 | 2015 | 155.6561 | 51.8183 | OK | Good | 8
Coal Tek | 7806 | 7806-CoalTek | Possum Trot | 78 | 0 |  | 0.64243 | 0 | OK | 3.96 | 2015 | 49.1613 | 0 | OK | Good | 0
Meredith Rd | 7914 | 7914-Meredith Rd | Maxon | 79 | 251.4247 |  | 0.35513 | 0.11137 | OK | 15.318 | 2017 | 37.4699 | 6.2325 | OK | Good | 6
Maxon Rd | 7924 | 7924-Maxon Rd | Maxon | 79 | 290.0027 |  | 0.11466 | 2.0827 | PSC | 20.317 | 2013 | 12.0595 | 88.7819 | PSC | More Info Required | 4 | 000 Power Supply | 0 | 100 Construction | 0 | 110 Maintenance | 0 | 190 Other Planned | 0 | 300 Material or equipment fault/failure | 0.25 | 310 Installation Fault | 0 | 320 Conductor Sag or inadequate clearance | 0 | 340 Overload | 0 | 350 Miscoordination of protection devices | 0 | 360 Other Equipment installation/design | 0 | 400 Decay/Age of Material/Equipment | 0 | 420 Tree Growth | 0 | 430 Tree failure from overhang or dead tree without Ice/snow | 0.25 | 440 Trees with Ice/snow | 0 | 470 Borrower Crew Cuts Tree | 0 | 490 Maintenance, Other | 0 | 500 Lightning | 0 | 510 Wind, Not Trees | 0 | 520 Ice, Sleet, Frost, not Trees | 0 | 530 Flood | 0 | 540 Storm | 0 | 590 Weather, Other | 0 | 600 Animal/bird | 0 | 630 Squirrel | 0 | 690 Animal, Other | 0 | 700 Customer-Caused | 0 | 710 Motor Vehicle | 0 | 715 Farming Equipment | 0 | 720 Aircraft | 0 | 730 Fire | 0 | 740 Public Cuts Tree | 0.5 | 750 Vandalism | 0 | 760 Switching Error or Caused by Construction or Maintenance | 0 | 790 Public, Other | 0 | 800 Other | 0 | 999 Cause Unknown | 0
Industrial Park | 7934 | 7934-Industrial Park | Maxon | 79 | 3 |  | 0.069951 | 0.66667 | PSC | 0.844 | 2017 | 6.5128 | 41.3333 | PSC | More Info Required | 1 | 000 Power Supply | 0 | 100 Construction | 0 | 110 Maintenance | 0 | 190 Other Planned | 0 | 300 Material or equipment fault/failure | 0 | 310 Installation Fault | 0 | 320 Conductor Sag or inadequate clearance | 0 | 340 Overload | 0 | 350 Miscoordination of protection devices | 0 | 360 Other Equipment installation/design | 0 | 400 Decay/Age of Material/Equipment | 0 | 420 Tree Growth | 0 | 430 Tree failure from overhang or dead tree without Ice/snow | 0 | 440 Trees with Ice/snow | 0 | 470 Borrower Crew Cuts Tree | 0 | 490 Maintenance, Other | 0 | 500 Lightning | 0 | 510 Wind, Not Trees | 0 | 520 Ice, Sleet, Frost, not Trees | 0 | 530 Flood | 0 | 540 Storm | 0 | 590 Weather, Other | 0 | 600 Animal/bird | 0 | 630 Squirrel | 0 | 690 Animal, Other | 0 | 700 Customer-Caused | 0 | 710 Motor Vehicle | 0 | 715 Farming Equipment | 0 | 720 Aircraft | 0 | 730 Fire | 0 | 740 Public Cuts Tree | 1 | 750 Vandalism | 0 | 760 Switching Error or Caused by Construction or Maintenance | 0 | 790 Public, Other | 0 | 800 Other | 0 | 999 Cause Unknown | 0
Electric Distribution Utility Annual Reliability Report
Additional pages may be attached as necessary
SECTION 7: VEGETATION MANAGEMENT PLAN REVIEW
JPEC has established a four (4) year cycle on right-of-way maintenance and employs a contractor to perform that cycle clearing. JPEC also employs contract crews that handles mid-cycle trimming. We have experienced over the last couple of years an increased tree problem from "danger trees" (trees outside of right-of-way) falling into our ROW and tearing down lines and poles. We are working with our members and contractors to identify those danger trees for removal. In addition to JPEC's contractors, JPEC construction and maintenance crews have the tools and ability to recognize hazards and trim trees away from the line as they perform their duties.
SECTION 8: UTILITY COMMENTS
Overall, 2017 was a good year in comparison to previous years. JPEC worked with BREC to increase reliability on the transmission system by installing a number of radio controlled switches. These new switch points will keep future power supply caused outages to a minimum as BREC will be able to isolate problems faster and restore unaffected station sooner. Unfortunatly, some of this work has cause interruptions to our members. JPEC has worked to keep those interruptions to a minimum. JPEC and BREC have three more switches to add in 2018. JPEC has brought in additional contract crews to continue the work started last year replacing structures and hardening the system. New technolgies will be tested in 2018 that will put more information into the hands of crews. This new technology will make reporting restoration closer to real time. New switching poiints are being installed to isolate outages and return as many members back on as possible.

## 2016 Circuit Details
Electric Distribution Utility Annual Reliability Report
SECTION 1: CONTACT INFORMATION
|  |  | UTILITY NAME | 1.1 | Jackson Purchase Energy Corporation
|  |  | REPORT PREPARED BY | 1.2 | Scott Ribble
|  |  | E-MAIL ADDRESS OF PREPARER | 1.3 | scott.ribble@jpenergy.com
|  |  | PHONE NUMBER OF PREPARER | 1.4 | 270-442-7321
SECTION 2: REPORT YEAR
|  |  | CALENDAR YEAR OF REPORT | 2.1 | 2016
SECTION 3: MAJOR EVENT DAYS
|  |  | TMED | 3.1 | 8.05
|  |  | FIRST DATE USED TO DETERMINE TMED | 3.2 | 2011-01-01
|  |  | LAST DATE USED TO DETERMINE TMED | 3.3 | 2015-12-31
|  |  | NUMBER OF MED IN REPORT YEAR | 3.4 | 4
NOTE: Per IEEE 1366 TMED should be calculated using the daily SAIDI values for the five prior years. If five years of data are not available, then utilities should use what is available until five years are accumulated.
SECTION 4: SYSTEM RELIABILITY RESULTS
System - Wide Information
| Total Customers | 29689 |  |  | Total Circuits | 91
Excluding MED
| 5 Year Average |  |  |  | Reporting Year
| SAIDI | 132.78 |  |  | SAIDI | 65.6017
| SAIFI | 1.59 |  |  | SAIFI | 0.6811
Including MED
| 5 Year Average |  |  |  | Reporting Year
| SAIDI | 196.87 |  |  | SAIDI | 338.926
| SAIFI | 1.75 |  |  | SAIFI | 1.2972
SECTION 5: CIRCUIT REPORTING
Circuit Name | Circuit Number | Circuit Location | Substation Name | Substation Number | Avg # of Customers |  | Previous 5 Year Average SAIFI | Current Year SAIFI Excluding MED | Comparison | Circuit Length | Date of Last Trim For Circuit | Previous 5 Year Average SAIDI | Current Year SAIDI Excluding MED |  |  | # of Outages | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | % | Outage Cause | %
Hampton-South | 501 | 0501-Hampton South | Joy | 5 | 192.7158 |  | 2.6856 | 0.81986 | OK | 57.417 | 2016 | 319.9634 | 101.372 | OK | Good | 9
Carrsville | 504 | 0504-Carrsville | Joy | 5 | 73.4235 |  | 1.8256 | 1.0079 | OK | 10.735 | 2016 | 238.8925 | 107.4452 | OK | Good | 2
Lola | 505 | 0505-Lola | Joy | 5 | 300.0492 |  | 1.7842 | 0.43326 | OK | 56.512 | 2016 | 241.7256 | 34.7443 | OK | Good | 8
Hampton | 1401 | 1401-Hampton | Burna | 14 | 84.3306 |  | 0.12148 | 0.20159 | PSC | 12.903 | 2015 | 16.0609 | 15.9254 | OK | More Info Required | 1 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Salem | 1404 | 1404-Salem | Burna | 14 | 330.4071 |  | 0.16779 | 0.24213 | PSC | 53.744 | 2015 | 27.0611 | 51.1278 | PSC | More Info Required | 9 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Smithland | 1405 | 1405-Smithland | Burna | 14 | 340.4208 |  | 1.3155 | 1.1104 | OK | 70.627 | 2015 | 150.0395 | 214.9487 | PSC | More Info Required | 11 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Pinckneyville | 1502 | 1502-Pinckneyville | Cumberland | 15 | 118.0683 |  | 2.0565 | 1.0672 | OK | 28.789 | 2015 | 281.0568 | 175.2884 | OK | Good | 4
Quarry | 1503 | 1503-Quarry | Cumberland | 15 | 0 |  | 1.1775 | 0 | OK | 5.285 | 2015 | 110.2268 | 0 | OK | Good | 0
Monkey's Eyebrow | 1901 | 1901-Monkeys Eyebrow | Ragland | 19 | 262.9344 |  | 1.429 | 0.27383 | OK | 51.116 | 2013 | 129.0813 | 48.8373 | OK | Good | 6
Ragland | 1902 | 1902-Ragland | Ragland | 19 | 229.0464 |  | 1.0124 | 0.10915 | OK | 33.568 | 2013 | 88.6278 | 11.1724 | OK | Good | 7
Damron's | 2601 | 2601-Damrons | LaCenter | 26 | 229.1557 |  | 2.5392 | 0.52803 | OK | 39.285 | 2015 | 225.1663 | 87.8049 | OK | Good | 15
Oscar | 2602 | 2602-Oscar | LaCenter | 26 | 361.4208 |  | 1.3341 | 1.7348 | PSC | 69.896 | 2015 | 127.1554 | 242.8969 | PSC | More Info Required | 23 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Hobbs Rd | 2801 | 2801-Hobbs Rd | Kevil | 28 | 554.4781 |  | 0.87252 | 0.42563 | OK | 53.455 | 2013 | 80.605 | 32.3728 | OK | Good | 19
Woodville Rd | 2802 | 2802-Woodville Rd | Kevil | 28 | 550.3361 |  | 1.0195 | 0.47244 | OK | 70.665 | 2013 | 119.2131 | 107.0891 | OK | Good | 18
Kelley Rd | 2803 | 2803-Kelley Rd | Kevil | 28 | 411.8716 |  | 1.716 | 0.029135 | OK | 45.651 | 2013 | 213.3527 | 1.3766 | OK | Good | 5
High Point | 2901 | 2901-High Point | High Point | 29 | 197.4727 |  | 1.5868 | 0.33422 | OK | 21.562 | 2015 | 118.6639 | 22.6259 | OK | Good | 10
Carneal Rd | 2902 | 2902-Carneal Rd | High Point | 29 | 182.8579 |  | 1.6767 | 1.4164 | OK | 17.372 | 2015 | 159.832 | 85.591 | OK | Good | 6
Essex | 2903 | 2903-Essex | High Point | 29 | 0 |  | 0 | 0 | OK | 0.042 | 2015 | 0 | 0 | OK | Good | 0
Conrad Heights | 3002 | 3002-Conrad Heights | Coleman Road | 30 | 369.4672 |  | 0.88838 | 0.81198 | OK | 18.174 | 2015 | 78.3642 | 56.5896 | OK | Good | 11
Holt Rd | 3004 | 3004-Hwy 60 Business | Coleman Road | 30 | 50 |  | 0.082032 | 0.68 | PSC | 7.678 | 2015 | 5.3262 | 31.72 | PSC | More Info Required | 1 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Ky Oaks Mall | 3005 | 3005-KY Oaks Mall | Coleman Road | 30 | 0 |  | 0.26275 | 0 | OK | 3.877 | 2015 | 11.1226 | 0 | OK | Good | 0
US 60 East | 3102 | 3102-US 60 East | Ledbetter | 31 | 318.8197 |  | 2.1666 | 0.17251 | OK | 35.417 | 2016 | 181.8212 | 31.4786 | OK | Good | 14
River Crossing | 3103 | 3103-River Crossing | Ledbetter | 31 | 0 |  | 0.49125 | 0 | OK | 5.154 | 2016 | 35.7734 | 0 | OK | Good | 0
Ledbetter | 3104 | 3104-Ledbetter | Ledbetter | 31 | 1014.806 |  | 1.6657 | 1.5648 | OK | 62.267 | 2016 | 120.0026 | 88.0208 | OK | Good | 46
Smithland | 3201 | 3201-Smithland | Smithland | 32 | 391.4754 |  | 2.8961 | 1.0575 | OK | 29.715 | 2014 | 359.5823 | 58.4277 | OK | Good | 9
Tiline | 3202 | 3202-Tiline | Smithland | 32 | 543.4044 |  | 3.9995 | 1.244 | OK | 108.763 | 2014 | 505.6722 | 108.3337 | OK | Good | 29
Mitchell Store | 3204 | 3204-Mitchell Store | Smithland | 32 | 392.0437 |  | 1.0954 | 0.34435 | OK | 55.336 | 2014 | 158.9917 | 60.9116 | OK | Good | 18
Airport | 3901 | 3901-Airport | Little Union | 39 | 551.8279 |  | 2.2073 | 1.1181 | OK | 35.872 | 2013 | 191.8437 | 155.9236 | OK | Good | 12
US 60 West | 3902 | 3902-US 60 West | Little Union | 39 | 461.0929 |  | 1.3353 | 0.31447 | OK | 36.427 | 2013 | 112.7643 | 13.3097 | OK | Good | 9
US 60 East-K O M | 3903 | 3903-US 60 East Mall | Little Union | 39 | 144.6503 |  | 1.8695 | 0.062219 | OK | 10.354 | 2013 | 119.3955 | 16.5226 | OK | Good | 4
Roy Lee Rd | 3904 | 3904-Roy Lee Rd | Little Union | 39 | 465.1175 |  | 1.6108 | 0.3139 | OK | 51.676 | 2013 | 163.4325 | 49.523 | OK | Good | 14
Husbands Rd | 4024 | 4024-Husbands Rd | Husbands Road | 40 | 775.2104 |  | 0.82364 | 1.1171 | PSC | 44.183 | 2014 | 63.9104 | 70.7176 | PSC | More Info Required | 14 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Lydon Rd | 4034 | 4034-Lydon Rd | Husbands Road | 40 | 453.4481 |  | 0.64333 | 0.73437 | PSC | 31.75 | 2014 | 36.1643 | 72.8374 | PSC | More Info Required | 34 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Clarkline Rd | 4044 | 4044-Clarkline Rd | Husbands Road | 40 | 298.571 |  | 0.74957 | 0.27464 | OK | 26.55 | 2014 | 33.7332 | 13.012 | OK | Good | 9
Ken Mar Rd | 4101 | 4101-Ken Mar Rd | Reidland | 41 | 321.6667 |  | 1.7306 | 0.16477 | OK | 19.621 | 2014 | 141.3777 | 15.6 | OK | Good | 6
Reidland Water | 4102 | 4102-Reidland Water | Reidland | 41 | 0 |  | 0.69877 | 0 | OK | 2.956 | 2014 | 64.0452 | 0 | OK | Good | 0
Epperson Rd | 4103 | 4103-Epperson Rd | Reidland | 41 | 200.4536 |  | 1.1917 | 1.2571 | PSC | 10.082 | 2014 | 149.6837 | 104.1588 | OK | More Info Required | 5 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Walker Boat Yard | 4104 | 4104-Walker Boat Yard | Reidland | 41 | 104.0219 |  | 4.2238 | 1.9996 | OK | 11.962 | 2014 | 48.8089 | 174.4441 | PSC | More Info Required | 4 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Proform | 4201 | 4201-Proform | Culp | 42 | 420.541 |  | 0.63063 | 1.0391 | PSC | 25.596 | 2014 | 51.0432 | 82.5603 | PSC | More Info Required | 15 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Little Cypress | 4202 | 4202-Little Cypress | Culp | 42 | 50.3197 |  | 0.1671 | 0.039746 | OK | 8.224 | 2014 | 14.4366 | 2.8617 | OK | Good | 1
Possum Trot | 4203 | 4203-Possum Trot | Culp | 42 | 206.0656 |  | 0.54488 | 0.6066 | PSC | 18.58 | 2014 | 59.433 | 86.1037 | PSC | More Info Required | 6 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Sharpe | 4204 | 4204-Sharpe | Culp | 42 | 1060.306 |  | 1.6889 | 0.1509 | OK | 77.482 | 2014 | 104.7752 | 11.4363 | OK | Good | 22
CC/Hwy 95 | 4301 | 4301-Hwy 95 | Calvert City | 43 | 243.7022 |  | 1.4877 | 0.065654 | OK | 18.672 | 2013 | 151.7986 | 6.3684 | OK | Good | 2
CC Hgts | 4302 | 4302-Calvert Heights | Calvert City | 43 | 657.2923 |  | 0.92352 | 0.21147 | OK | 27.83 | 2013 | 80.2123 | 11.9688 | OK | Good | 9
Gilbertsville | 4303 | 4303-Gilbertsville | Calvert City | 43 | 363.7514 |  | 0.46465 | 0.25017 | OK | 23.086 | 2013 | 45.1155 | 8.033 | OK | Good | 3
CC Ind Park | 4304 | 4304-Industrial Park | Calvert City | 43 | 0 |  | 0.43266 | 0 | OK | 4.87 | 2013 | 40.3315 | 0 | OK | Good | 0
Vulcan Pit | 4502 | 4502-Vulcan Pit | Vulcan | 45 | 0 |  | 0.2 | 0 | OK | 2.39 |  | 25.4 | 0 | OK | Good | 0
Vulcan 1-Rock Crusher | 4503 | 4503-Vulcan1 Rock Crusher | Vulcan | 45 | 0 |  | 0.2 | 0 | OK | 1.273 |  | 30.9 | 0 | OK | Good | 0
Kinder Morgan 1 | 4504 | 4504-Kinder Morgan 1 | Vulcan | 45 | 34.3989 |  | 0.69281 | 1.0756 | PSC | 7.774 |  | 95.519 | 106.9801 | PSC | More Info Required | 4 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Vulcan 2 Hwy 62 | 4505 | 4505-Vulcan 2 Hwy 62 | Vulcan | 45 | 0 |  | 0.70182 | 0 | OK | 5.015 |  | 106.0091 | 0 | OK | Good | 0
Hinkleville | 4701 | 4701-Hinkleville | New York | 47 | 261.2787 |  | 2.0245 | 0.67744 | OK | 44.517 | 2013 | 302.43 | 79.907 | OK | Good | 18
US 286 East-Gage | 4702 | 4702-US 286 East Gage | New York | 47 | 266.0191 |  | 1.1678 | 0.1842 | OK | 45.25 | 2013 | 105.008 | 26.5282 | OK | Good | 10
Blandville | 4703 | 4703-Blandville | New York | 47 | 228.4973 |  | 2.9923 | 1.5449 | OK | 30.357 | 2013 | 368.3708 | 142.6932 | OK | Good | 11
Wickliffe | 4704 | 4704-Wickliffe | New York | 47 | 355.3907 |  | 1.3077 | 0.46146 | OK | 49.217 | 2013 | 142.4509 | 46.3068 | OK | Good | 16
Slater | 4705 | 4705-Slater | New York | 47 | 348.4454 |  | 1.5881 | 1.1566 | OK | 68.382 | 2013 | 281.1837 | 157.072 | OK | Good | 15
Blandville | 4901 | 4901-Blandville | Lovelaceville | 49 | 134.9262 |  | 0.86968 | 0.6448 | OK | 20.368 | 2015 | 104.4253 | 100.4549 | OK | Good | 6
Lovelaceville | 4902 | 4902-Lovelaceville | Lovelaceville | 49 | 514.112 |  | 1.0224 | 0.14783 | OK | 57.681 | 2015 | 78.4016 | 67.0185 | OK | Good | 17
Cunningham | 4903 | 4903-Cunningham | Lovelaceville | 49 | 527.3388 |  | 1.9457 | 0.68078 | OK | 64.468 | 2015 | 215.1435 | 75.022 | OK | Good | 11
Browns Plating | 5001 | 5001-Browns Plating | Krebs Station Road | 50 | 511.5574 |  | 1.9563 | 0.33818 | OK | 36.923 | 2016 | 174.6121 | 23.9211 | OK | Good | 15
Old US 45 | 5002 | 5002-Old US 45 | Krebs Station Road | 50 | 858.0164 |  | 2.0609 | 2.9382 | PSC | 77.238 | 2016 | 224.8447 | 133.4543 | OK | More Info Required | 33 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Clinton Road | 5003 | 5003-Clinton Rd | Krebs Station Road | 50 | 595.1393 |  | 1.2373 | 0.59146 | OK | 52.268 | 2016 | 117.3222 | 75.9839 | OK | Good | 36
Symsonia | 5101 | 5101-Symsonia | Freemont | 51 | 1011.306 |  | 1.8595 | 0.25215 | OK | 93.592 | 2014 | 176.9686 | 24.237 | OK | Good | 38
Mc Neil Lane | 5102 | 5102-McNeil Lane | Freemont | 51 | 386.0027 |  | 2.2536 | 0.46891 | OK | 45.863 | 2014 | 274.3357 | 49.4763 | OK | Good | 17
Freemont | 5104 | 5104-Freemont | Freemont | 51 | 359.8798 |  | 0.98524 | 1.1476 | PSC | 25.765 | 2014 | 92.1653 | 69.1481 | OK | More Info Required | 10 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Bonds Rd | 5105 | 5105-Bonds Rd | Freemont | 51 | 125.5656 |  | 1.4117 | 1.7282 | PSC | 17.668 | 2014 | 116.1914 | 117.1181 | PSC | More Info Required | 5 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Hwy 95 N to Hwy 62 | 5401 | 5401-Hwy 95 | Palma | 54 | 356.4044 |  | 1.69 | 0.40404 | OK | 29.367 | 2014 | 147.822 | 51.1722 | OK | Good | 9
Draffenville | 5402 | 5402-Draffenville | Palma | 54 | 285.3115 |  | 0.28079 | 0.01402 | OK | 20.953 | 2014 | 19.8825 | 1.083 | OK | Good | 2
Palma | 5403 | 5403-Palma | Palma | 54 | 727.2869 |  | 0.90044 | 0.0165 | OK | 55.927 | 2014 | 63.1662 | 1.067 | OK | Good | 7
Lowes | 6101 | 6101-Lowes | Kansas | 61 | 455.6503 |  | 0.49012 | 0.15143 | OK | 58.526 | 2016 | 60.1761 | 12.6413 | OK | Good | 15
US 45-Folsomdale | 6102 | 6102-US 45 Folsomdale | Kansas | 61 | 214.0273 |  | 0.72948 | 0.20558 | OK | 29.264 | 2016 | 108.6696 | 20.1797 | OK | Good | 9
Melber | 6103 | 6103-Melber | Kansas | 61 | 523.9262 |  | 0.59504 | 1.6224 | PSC | 52.228 | 2016 | 76.7039 | 147.3013 | PSC | More Info Required | 16 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Pottsville | 6104 | 6104-Pottsville | Kansas | 61 | 355.5902 |  | 1.7992 | 1.0518 | OK | 46.749 | 2016 | 199.0305 | 187.6205 | OK | Good | 5
Draffenville | 6601 | 6601-Draffenville | Draffenville | 66 | 466.4508 |  | 1.1468 | 0.064315 | OK | 28.798 | 2014 | 114.6917 | 6.8282 | OK | Good | 9
Olivet Ch Rd | 7401 | 7401-Info Age Park | Olivet Church Road | 74 | 541.5519 |  | 0.86582 | 0.033238 | OK | 21.238 | 2015 | 43.1022 | 2.8344 | OK | Good | 5
Highland Ch Rd | 7402 | 7402-Highland Ch Rd | Olivet Church Road | 74 | 450.2541 |  | 0.73249 | 2.0922 | PSC | 35.822 | 2015 | 81.025 | 170.788 | PSC | More Info Required | 27 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Info Age Park | 7403 | 7403-Info Age Park | Olivet Church Road | 74 | 0 |  | 0.04 | 0 | OK | 2.438 | 2015 | 12.8 | 0 | OK | Good | 0
Iuka | 7601 | 7601-Iuka | Grand Rivers | 76 | 292.2705 |  | 2.5463 | 0.41742 | OK | 47.35 | 2016 | 317.9903 | 54.5556 | OK | Good | 17
Smithland | 7602 | 7602-Smithland | Grand Rivers | 76 | 278.5738 |  | 0.84424 | 1.5005 | PSC | 30.075 | 2016 | 84.9842 | 90.7515 | PSC | More Info Required | 17 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Pelican-GR #1 | 7604 | 7604-Pelican GR #1 | Grand Rivers | 76 | 373.2322 |  | 0.62353 | 0.18219 | OK | 24.039 | 2016 | 69.1455 | 21.0673 | OK | Good | 11
Averitt-GR #2 | 7605 | 7605-Averitt GR #2 | Grand Rivers | 76 | 670.2322 |  | 1.6735 | 1.1832 | OK | 43.336 | 2016 | 172.3205 | 237.2387 | PSC | More Info Required | 19 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Hansen Rd-Top Circuit | 7702 | 7702-Hansen Rd | Strawberry Hill | 77 | 630.2705 |  | 1.0801 | 0.53152 | OK | 29.532 | 2015 | 98.267 | 36.5303 | OK | Good | 12
Walmart-Hansen Rd Bottom | 7703 | 7703-Walmart | Strawberry Hill | 77 | 293.459 |  | 0.32321 | 0.21468 | OK | 8.867 | 2015 | 19.3372 | 5.6942 | OK | Good | 4
CSI--Jas Sanders-Botom Cir | 7705 | 7705-CSI | Strawberry Hill | 77 | 107.5929 |  | 3.0607 | 0.56695 | OK | 4.887 | 2015 | 193.1074 | 17.5755 | OK | Good | 1
Hwy 60-Jas Sanders-Top Cir | 7706 | 7706-Hwy 60 | Strawberry Hill | 77 | 0 |  | 0.30134 | 0 | OK | 1.623 | 2015 | 19.6798 | 0 | OK | Good | 0
Hwy 95 North | 7802 | 7802-Possum Trot | Possum Trot | 78 | 537.7268 |  | 1.0536 | 0.091124 | OK | 42.372 | 2015 | 67.7017 | 4.0597 | OK | Good | 9
Possum Trot | 7803 | 7803-Hwy 95 | Possum Trot | 78 | 190.9153 |  | 1.123 | 0.13619 | OK | 15.003 | 2015 | 67.8238 | 14.0848 | OK | Good | 5
Industrial Loop North | 7805 | 7805-Industrial Loop | Possum Trot | 78 | 205.9945 |  | 2.4052 | 0.41263 | OK | 28.697 | 2015 | 176.2386 | 50.3557 | OK | Good | 17
Coal Tek | 7806 | 7806-CoalTek | Possum Trot | 78 | 0 |  | 0.87576 | 0 | OK | 3.96 | 2015 | 55.2279 | 0 | OK | Good | 0
Meredith Rd | 7914 | 7914-Meredith Rd | Maxon | 79 | 119.5492 |  | 0.32 | 0.17566 | OK | 15.318 | 2013 | 33.0533 | 22.083 | OK | Good | 5
Maxon Rd | 7924 | 7924-Maxon Rd | Maxon | 79 | 257.1818 |  | 0.11155 | 0.015553 | OK | 20.317 | 2013 | 11.7959 | 1.3181 | OK | Good | 2
Industrial Park | 7934 | 7934-Industrial Park | Maxon | 79 | 486.0547 |  | 0 | 0.34975 | PSC | 0.844 | 2013 | 0 | 32.5642 | PSC | More Info Required | 27 | 000 Power Supply | #VALUE! | 100 Construction | #VALUE! | 110 Maintenance | #VALUE! | 190 Other Planned | #VALUE! | 300 Material or equipment fault/failure | #VALUE! | 310 Installation Fault | #VALUE! | 320 Conductor Sag or inadequate clearance | #VALUE! | 340 Overload | #VALUE! | 350 Miscoordination of protection devices | #VALUE! | 360 Other Equipment installation/design | #VALUE! | 400 Decay/Age of Material/Equipment | #VALUE! | 420 Tree Growth | #VALUE! | 430 Tree failure from overhang or dead tree without Ice/snow | #VALUE! | 440 Trees with Ice/snow | #VALUE! | 470 Borrower Crew Cuts Tree | #VALUE! | 490 Maintenance, Other | #VALUE! | 500 Lightning | #VALUE! | 510 Wind, Not Trees | #VALUE! | 520 Ice, Sleet, Frost, not Trees | #VALUE! | 530 Flood | #VALUE! | 540 Storm | #VALUE! | 590 Weather, Other | #VALUE! | 600 Animal/bird | #VALUE! | 630 Squirrel | #VALUE! | 690 Animal, Other | #VALUE! | 700 Customer-Caused | #VALUE! | 710 Motor Vehicle | #VALUE! | 715 Farming Equipment | #VALUE! | 720 Aircraft | #VALUE! | 730 Fire | #VALUE! | 740 Public Cuts Tree | #VALUE! | 750 Vandalism | #VALUE! | 760 Switching Error or Caused by Construction or Maintenance | #VALUE! | 790 Public, Other | #VALUE! | 800 Other | #VALUE! | 999 Cause Unknown | #VALUE!
Electric Distribution Utility Annual Reliability Report
Additional pages may be attached as necessary
SECTION 7: VEGETATION MANAGEMENT PLAN REVIEW
JPEC has established a four (4) year cycle on R.O.W. Maintenance and has employed a contractor to handle those responsibilities. JPEC also employees a contract crew that handles mid-cycle trimming as well as all of our in-house construction and maintenance crews have the ability to recognize hazards and trim trees away from the line.
SECTION 8: UTILITY COMMENTS
For the year 2015, JPEC customers reported fewer outages than 2014. Reviewing the outage cause codes for 2015 reveal Storms, Trees outside of ROW, Squirrels, and Unknown causes as the top causes for outages. JPEC has discussed these cause codes and is actively pursuing ways to reduce outage times for our members. For example, JPEC's current 2016-2019 CWP addresses the installation of new switch points on circuits that will reduce outage sizes in the case of a circuit outage. Another example is that JPEC is working with their ROW contractor to identifying and remove danger trees outside the ROW while maintaining the current corridor.