## R1b, R1c, R2 - Table
Comparison Table | RICE | F-Class CT | JK Smith ABB 1-3 | JK Smith 7EA 4-7 | JK Smith LMS100 9-10 | BG Sie W501FD2 1-3
Dispatch Type | Mid-load | Peaker | Peaker | Peaker | Peaker | Peaker
Primary Fuel | Natural Gas | Natural Gas | Natural Gas | Natural Gas | Natural Gas | Natural Gas
Secondary/Backup Fuel | Fuel Oil | Fuel Oil | Fuel Oil | Fuel Oil | n/a | Fuel Oil
Power Output per Unit (MW) | 18-20 | 200-260 | 100-135 | 55-88 | 35-100 | 110-192
Average Heat Rate (Btu/kWh) | 8500 | 9,300-9,500
Average Dispatch Cost at $3/MMBtu ($/MWh)* | 25.5 | 27.9-28.5
Startup Cost ($)** | n/a | unknown
No-Load Cost ($/Hr)** | n/a | unknown
Variable O&M Cost ($/Start)** | n/a | unknown
Variable O&M Cost ($/MWh)*** | 10 | 6.44
Fixed O&M ($/kW/Yr)*** | 17.90-22.5 | 23.7
Startup to Full Load time (minutes) | 5 | 30 | 30 | 34 | 12 | 32
Estimated Capacify Factor (%) | 50 | 10 | 5 | 7 | 14 | 3
*Assumes fuel costs only, excludes startup, no-load, and O&M.
**EKPC fleet startup, no-load, and variable O&M data sourced from current EKPC PJM offer calcualtions as of 6/17/2024.
***RICE variable and fixed O&M costs sourced from OEM. F-Class CT variable and fixed O&M costs sourced from NREL ATB. EKPC fleet fixed O&M costs are 2024 values sourced from EKPC 2022 IRP, averaged by unit type.

## R1a - CT Start-Time
PLANT | UNIT | Date | Time | Net Output (MW) | DA Bid | Economic
SMITH | 1 | 2023-02-03 | 17:30 | CLEARED TO COME ONLINE FOR 18:00 | Economic | Max MW
SMITH | 1 | 2023-02-03 | 17:55 | -0.648 |  | 131
SMITH | 1 | 2023-02-03 | 18:00 | 35.376
SMITH | 1 | 2023-02-03 | 18:05 | 62.46
SMITH | 1 | 2023-02-03 | 18:10 | 88.944
SMITH | 1 | 2023-02-03 | 18:15 | 109.26
SMITH | 2 | 2023-02-03 | 17:30 | CLEARED TO COME ONLINE FOR 18:00 | DA Bid | Economic
SMITH | 2 | 2023-02-03 | 18:00 | -4.296 | Economic | Max MW
SMITH | 2 | 2023-02-03 | 18:05 | 18.336 |  | 131
SMITH | 2 | 2023-02-03 | 18:10 | 51
SMITH | 2 | 2023-02-03 | 18:15 | 79.056
SMITH | 2 | 2023-02-03 | 18:20 | 103.848
SMITH | 3 | 2023-02-03 | 17:30 | CLEARED TO COME ONLINE FOR 18:00 | DA Bid | Economic
SMITH | 3 | 2023-02-03 | 17:50 | -2.856 | Economic | Max MW
SMITH | 3 | 2023-02-03 | 17:55 | 0.192 |  | 131
SMITH | 3 | 2023-02-03 | 18:00 | 36.576
SMITH | 3 | 2023-02-03 | 18:05 | 63.528
SMITH | 3 | 2023-02-03 | 18:10 | 89.964
SMITH | 3 | 2023-02-03 | 18:15 | 109.656
SMITH | 4 | 2023-02-03 | 15:59 | PJM CLEARED | DA Bid | Economic
SMITH | 4 | 2023-02-03 | 16:10 | -0.636 | Economic | Max MW
SMITH | 4 | 2023-02-03 | 16:15 | 2.64 |  | 87
SMITH | 4 | 2023-02-03 | 16:20 | 32.76
SMITH | 4 | 2023-02-03 | 16:25 | 68.268
SMITH | 5 | 2023-02-03 | 15:59 | PJM CLEARED | DA Bid | Economic
SMITH | 5 | 2023-02-03 | 16:10 | -0.636 | Economic | Max MW
SMITH | 5 | 2023-02-03 | 16:15 | 1.812 |  | 87
SMITH | 5 | 2023-02-03 | 16:20 | 30.792
SMITH | 5 | 2023-02-03 | 16:25 | 66.336
SMITH | 6 | 2023-02-03 | 15:59 | PJM CLEARED | DA Bid | Economic
SMITH | 6 | 2023-02-03 | 16:10 | -1.152 | Economic | Max MW
SMITH | 6 | 2023-02-03 | 16:15 | 1.728 |  | 87
SMITH | 6 | 2023-02-03 | 16:20 | 31.91
SMITH | 6 | 2023-02-03 | 16:25 | 66.47
SMITH | 7 | 2023-02-03 | 15:59 | PJM CLEARED | DA Bid | Economic
SMITH | 7 | 2023-02-03 | 16:10 | -1.036 | Economic | Max MW
SMITH | 7 | 2023-02-03 | 16:15 | 13.478 |  | 87
SMITH | 7 | 2023-02-03 | 16:20 | 48.038
SMITH | 7 | 2023-02-03 | 16:25 | 82.483
SMITH | 9 | 2023-02-03 | 15:59 | PJM CLEARED | DA Bid | Economic
SMITH | 9 | 2023-02-03 | 16:10 | 0 | Economic | Max MW
SMITH | 9 | 2023-02-03 | 16:15 | 3.372 |  | 97
SMITH | 9 | 2023-02-03 | 16:20 | 68.64
BLUEGRASS | 1 | 2023-02-03 | 15:35 | PJM CLEARED | DA Bid | Economic
BLUEGRASS | 1 | 2023-02-03 | 16:00 | ONLINE | Economic | Max MW
BLUEGRASS | 1 | 2023-02-03 | N/A | NO 5-MIN DATA |  | 188
BLUEGRASS | 2 | 2023-02-03 | 15:35 | PJM CLEARED | DA Bid | Economic
BLUEGRASS | 2 | 2023-02-03 | 16:11 | ONLINE | Economic | Max MW
BLUEGRASS | 2 | 2023-02-03 | N/A | NO 5-MIN DATA |  | 188