## Sheet1
Unit | Date | Time of Outage | Reason | Hours | Minutes | Monthly Net Cap Ftr % | DA or RT Clearing | LMP ($/MWh)
Spurlock Unit 4 | 2022-12-23 | 722 | PRIMARY AIR FAN LUBE OIL SYSTEM. | 14 | 46 | 78.86 | DA | 37.75
J.K. Smith Unit 4 | 2022-12-23 | 623 | FORCED OUTAGE -- LINE VOLTAGE PROBLEMS. | 1 | 47 | 10.85 | RT | 116.26
J.K. Smith Unit 4 | 2022-12-23 | 836 | FORCED OUTAGE -- UNIT CONTROL ISSUES. | 2 | 4 | 10.85 | RT | 196.51
J.K. Smith Unit 4 | 2022-12-23 | 1345 | FORCED OUTAGE -- FROZEN INSTRUMENTATION. | 1 | 25 | 10.85 | DA | 111.36
J.K. Smith Unit 4 | 2022-12-23 | 1532 | FORCED OUTAGE -- FROZEN INSTRUMENTATION. | 2 | 40 | 10.85 | DA | 105.61
J.K. Smith Unit 4 | 2022-12-23 | 2152 | FORCED OUTAGE -- UNIT CONTROL ISSUES. | 8 | 56 | 10.85 | DA | 137.84
Bluegrass Unit 1 | 2022-12-23 | 1820 | NATURAL GAS NOT AVAILABLE. UNIT SWITCHED TO FUEL OIL. UNIT FAILED TO START. | 1 | 48 | 6.12 | DA | 169.69
Bluegrass Unit 1 | 2022-12-23 | 2053 | TRIPPED ON REDUCTION OF FO WHEN CT-2 WAS LINED UP WHEN ITS ESD OPENED. | 17 | 2 | 6.12 | DA | 160.94
Bluegrass Unit 1 | 2022-12-24 | 1505 | TRIPPED ON REDUCTION OF FO WHEN CT-2 WAS LINED UP WHEN ITS ESD OPENED. | 1 | 11 | 6.12 | DA | 114.76
Bluegrass Unit 2 | 2022-12-23 | 1551 | NATURAL GAS NOT AVAILABLE. UNIT SWITCHED TO FUEL OIL. UNIT FAILED TO START. | 25 | 25 | 6.79 | RT | 520.57
Bluegrass Unit 3 | 2022-12-23 | 1810 | NATURAL GAS NOT AVAILABLE. UNIT SWITCHED TO FUEL OIL. UNIT FAILED TO START. | 23 | 6 | 0.3 | RT | 2260.78