## PSC 1.15
DEK FAC 2024-00140
PSC DR 1.15
Review Period: 11/1/2022 - 4/30/2023
Unit | Event Type | Schedule Hours | Forced Hours | Actual Hours | Event Duration Hours | Event Start | Event End | Event Description
Woodsdale CT-1 | U1 | 0 | 0.517 | 0.517 | 0.517 | 2022-12-05 09:31 | 2022-12-05 10:02 | Remote start; Flame out, restarted from control room.
East Bend Steam-2 | MO | 21.667 | 0 | 21.667 | 21.667 | 2022-12-08 08:20 | 2022-12-09 06:00 | DCS Patch Outage
East Bend Steam-2 | U1 | 0 | 2.4 | 2.4 | 2.4 | 2022-12-09 06:10 | 2022-12-09 08:34 | Drum Level control trip
East Bend Steam-2 | U1 | 0 | 15.633 | 15.633 | 15.633 | 2022-12-09 10:30 | 2022-12-10 02:08 | Feedwater control trip
East Bend Steam-2 | U1 | 0 | 1.233 | 1.233 | 1.233 | 2022-12-10 03:08 | 2022-12-10 04:22 | Feedwater control trip
Woodsdale CT-4 | U1 | 0 | 15.517 | 15.517 | 15.517 | 2022-12-11 22:05 | 2022-12-12 13:36 | Bad Exhaust TC, replaced, made unit available.
Woodsdale CT-1 | MO | 3 | 0 | 3 | 3 | 2022-12-20 21:05 | 2022-12-21 00:05 | CT unavailable so substation maint can add SF6 gas
Woodsdale CT-2 | MO | 3 | 0 | 3 | 3 | 2022-12-20 21:05 | 2022-12-21 00:05 | CT unavailable so substation maint can add SF6 gas
Woodsdale CT-4 | MO | 3 | 0 | 3 | 3 | 2022-12-20 21:05 | 2022-12-21 00:05 | CT unavailable so substation maint can add SF6 gas
Woodsdale CT-6 | U1 | 0 | 1.433 | 1.433 | 1.433 | 2022-12-23 21:32 | 2022-12-23 22:58 | Flame scanner not indicating.
Woodsdale CT-4 | U1 | 0 | 0.5 | 0.5 | 0.5 | 2022-12-24 00:21 | 2022-12-24 00:51 | Flame scanner not indicating.
Woodsdale CT-5 | MO | 4.167 | 0 | 4.167 | 4.167 | 2023-01-04 12:23 | 2023-01-04 16:33 | Switchyard maintenance, OMC
Woodsdale CT-6 | MO | 4.167 | 0 | 4.167 | 4.167 | 2023-01-04 12:23 | 2023-01-04 16:33 | Switchyard maintenance, OMC
Woodsdale CT-1 | U1 | 0 | 0.3 | 0.3 | 0.3 | 2023-01-09 11:42 | 2023-01-09 12:00 | Trip-Gas valve chattered, appeared to be open too early.
Woodsdale CT-6 | SF | 0 | 0.433 | 0.433 | 0.433 | 2023-01-10 12:04 | 2023-01-10 12:30 | Start up trip during ignition
Woodsdale CT-5 | U1 | 0 | 3.167 | 3.167 | 3.167 | 2023-01-11 10:52 | 2023-01-11 14:02 | Start up trip during ignition
Woodsdale CT-1 | MO | 9.8 | 0 | 9.8 | 9.8 | 2023-01-24 11:00 | 2023-01-24 20:48 | Boroscope inspection
East Bend Steam-2 | MO | 198 | 0 | 198 | 198 | 2023-02-12 05:00 | 2023-02-20 11:00 | Burner lines?
East Bend Steam-2 | MO | 530.567 | 0 | 530.567 | 530.567 | 2023-02-21 05:00 | 2023-03-15 07:34 | A Module Duct Work
Woodsdale CT-6 | MO | 0.583 | 0 | 0.583 | 0.583 | 2023-02-28 21:36 | 2023-02-28 22:11 | 24 VDC battery needed bypassed.
Woodsdale CT-1 | PO | 342.567 | 0 | 342.567 | 342.567 | 2023-03-04 11:00 | 2023-03-18 17:34 | Borescope inspection / Spring Prep
Woodsdale CT-2 | PO | 342.817 | 0 | 342.817 | 342.817 | 2023-03-04 11:00 | 2023-03-18 17:49 | Borescope inspection / Spring Prep
Woodsdale CT-4 | PO | 313.883 | 0 | 313.883 | 313.883 | 2023-03-11 11:00 | 2023-03-24 12:53 | Borescope inspection / Spring Prep
East Bend Steam-2 | U1 | 0 | 2.767 | 2.767 | 2.767 | 2023-03-15 08:32 | 2023-03-15 11:18 | Feedwater drum level control trip
Woodsdale CT-5 | PO | 344.383 | 0 | 344.383 | 344.383 | 2023-03-18 10:00 | 2023-04-01 18:23 | Borescope inspection / Spring Prep.
Woodsdale CT-6 | PO | 344.333 | 0 | 344.333 | 344.333 | 2023-03-18 10:00 | 2023-04-01 18:20 | Borescope inspection / Spring Prep
Woodsdale CT-2 | PO | 1.667 | 0 | 1.667 | 1.667 | 2023-03-18 17:55 | 2023-03-18 19:35 | Borescope inspection / Spring Prep
Woodsdale CT-1 | U1 | 0 | 0.767 | 0.767 | 0.767 | 2023-03-29 10:22 | 2023-03-29 11:08 | Water injection pump tripped on startup. Tested ran and sounded good.
East Bend Steam-2 | U1 | 0 | 143.5 | 143.5 | 143.5 | 2023-04-05 07:30 | 2023-04-11 07:00 | 24SR1 & 24SR2 Bus Failure
East Bend Steam-2 | PO | 411.767 | 0 | 411.767 | 411.767 | 2023-04-20 03:40 | 2023-05-07 07:26 | Summer Prep Spring Outage
Event Type Legend:
PO | Planned Outage
PE | Planned Outage Extension
MO | Maintenance Outage
ME | Maintenance Outage Extension
U1 | Unplanned (Forced) Outage – Immediate
U2 | Unplanned (Forced) Outage – Delayed
U3 | Unplanned (Forced) Outage – Postponed
SF | Startup Failure