## PSC 1.15
DEK FAC 2024-00148
PSC DR 1.15
Review Period: 5/1/2023 - 10/31/2023
Unit | Event Type | Schedule Hours | Forced Hours | Actual Hours | Event Duration Hours | Event Start | Event End | Event Description
Woodsdale CT-1 | PO | 82 | 0 | 82 | 82 | 2023-05-01 10:00 | 2023-05-04 20:00 | Outage for Fuel Oil Tubing Repairs
Woodsdale CT-5 | MO | 3.25 | 0 | 3.25 | 3.25 | 2023-05-03 17:00 | 2023-05-03 20:15 | Outage for Generator Borescope.
Woodsdale CT-2 | PO | 35 | 0 | 35 | 35 | 2023-05-04 10:00 | 2023-05-05 21:00 | Outage for Fuel Oil Tubing Repairs
Woodsdale CT-6 | SF | 0 | 0.733 | 0.733 | 0.733 | 2023-05-07 10:16 | 2023-05-07 11:00 | Start Fail; tripped on flame, RS at 0700, Load Desk didn't want to restart.
Woodsdale CT-4 | PO | 33.45 | 0 | 33.45 | 33.45 | 2023-05-11 10:00 | 2023-05-12 19:27 | Outage for Fuel Oil Tubing Repairs
Woodsdale CT-6 | U1 | 0 | 88.533 | 88.533 | 88.533 | 2023-05-14 03:15 | 2023-05-17 19:47 | Trip, Fire Prot, CO2 Discharged.
East Bend Steam-2 | MO | 171.467 | 0 | 171.467 | 171.467 | 2023-05-15 04:22 | 2023-05-22 07:50 | 2-2 ID Booster Fan VIVs repairs
East Bend Steam-2 | MO | 14.3 | 0 | 14.3 | 14.3 | 2023-06-07 06:04 | 2023-06-07 20:22 | Repair #8 governor valve
Woodsdale CT-6 | U1 | 0 | 14.783 | 14.783 | 14.783 | 2023-06-26 22:16 | 2023-06-27 13:03 | Trip due to Exhaust Thermocouple faults
Woodsdale CT-4 | PO | 56.517 | 0 | 56.517 | 56.517 | 2023-06-30 10:00 | 2023-07-02 18:31 | Opened Bank 1602 to move crane for GT3 Gen lift.
Woodsdale CT-2 | U1 | 0 | 2.383 | 2.383 | 2.383 | 2023-07-18 13:12 | 2023-07-18 15:35 | AVR went to manual, made unavailable, reset
Woodsdale CT-1 | U1 | 0 | 26.783 | 26.783 | 26.783 | 2023-07-20 16:37 | 2023-07-21 19:24 | Took offline due to oil leak on burner
Woodsdale CT-4 | MO | 10.5 | 0 | 10.5 | 10.5 | 2023-07-21 10:00 | 2023-07-21 20:30 | Unavailable to restore GT3 Links
Woodsdale CT-3 | SF | 0 | 2.583 | 2.583 | 2.583 | 2023-07-26 19:02 | 2023-07-26 21:37 | Would not light off; propane ignition pressure too high
Woodsdale CT-3 | U1 | 0 | 9.5 | 9.5 | 9.5 | 2023-08-04 02:16 | 2023-08-04 11:46 | Trip; Inner Ring Exhaust TC Bad
Woodsdale CT-1 | PO | 49.583 | 0 | 49.583 | 49.583 | 2023-08-08 10:00 | 2023-08-10 11:35 | Plant outage to inspect receiver air tanks
Woodsdale CT-2 | PO | 49.583 | 0 | 49.583 | 49.583 | 2023-08-08 10:00 | 2023-08-10 11:35 | Plant outage to inspect receiver air tanks
Woodsdale CT-3 | PO | 49.583 | 0 | 49.583 | 49.583 | 2023-08-08 10:00 | 2023-08-10 11:35 | Plant outage to inspect receiver air tanks
Woodsdale CT-4 | PO | 49.583 | 0 | 49.583 | 49.583 | 2023-08-08 10:00 | 2023-08-10 11:35 | Plant outage to inspect receiver air tanks
Woodsdale CT-5 | PO | 49.583 | 0 | 49.583 | 49.583 | 2023-08-08 10:00 | 2023-08-10 11:35 | Plant outage to inspect receiver air tanks
Woodsdale CT-6 | PO | 49.583 | 0 | 49.583 | 49.583 | 2023-08-08 10:00 | 2023-08-10 11:35 | Plant outage to inspect receiver air tanks
Woodsdale CT-6 | U1 | 0 | 1.933 | 1.933 | 1.933 | 2023-08-15 12:20 | 2023-08-15 14:16 | Unavailable due to Fire Protection Fault
East Bend Steam-2 | MO | 114.233 | 0 | 114.233 | 114.233 | 2023-08-26 07:28 | 2023-08-31 01:42 | Secondary Superheater Intermediate tube leak
East Bend Steam-2 | MO | 46.083 | 0 | 46.083 | 46.083 | 2023-09-16 05:54 | 2023-09-18 03:59 | Fall Maintenace Outage
Woodsdale CT-1 | PO | 327.2 | 0 | 327.2 | 327.2 | 2023-09-23 04:00 | 2023-10-06 19:12 | Fall outage / Borescope
Woodsdale CT-2 | PO | 328.217 | 0 | 328.217 | 328.217 | 2023-09-23 04:00 | 2023-10-06 20:13 | Fall outage / Borescope
Woodsdale CT-4 | U1 | 0 | 24.217 | 24.217 | 24.217 | 2023-09-25 14:40 | 2023-09-26 14:53 | Replaced starting breaker; adjustment in cubicle
Woodsdale CT-3 | PO | 323.4 | 0 | 323.4 | 323.4 | 2023-09-30 04:00 | 2023-10-13 15:24 | Fall outage / Borescope
Woodsdale CT-4 | PO | 323.3 | 0 | 323.3 | 323.3 | 2023-09-30 04:00 | 2023-10-13 15:18 | Fall outage / Borescope
Woodsdale CT-5 | PO | 281.267 | 0 | 281.267 | 281.267 | 2023-10-09 04:00 | 2023-10-20 21:16 | Fall outage / Borescope
Woodsdale CT-6 | PO | 281.533 | 0 | 281.533 | 281.533 | 2023-10-09 04:00 | 2023-10-20 21:32 | Fall outage / Borescope
Woodsdale CT-1 | U1 | 0 | 5.55 | 5.55 | 5.55 | 2023-10-10 09:41 | 2023-10-10 15:14 | Trip on Water Injection
Woodsdale CT-2 | SF | 0 | 3.3 | 3.3 | 3.3 | 2023-10-10 17:10 | 2023-10-10 20:28 | Start up fail; AVR Fault
Woodsdale CT-2 | MO | 1.917 | 0 | 1.917 | 1.917 | 2023-10-18 10:00 | 2023-10-18 11:55 | Work on AVR Fault
Event Type Legend:
PO | Planned Outage
PE | Planned Outage Extension
MO | Maintenance Outage
ME | Maintenance Outage Extension
U1 | Unplanned (Forced) Outage – Immediate
U2 | Unplanned (Forced) Outage – Delayed
U3 | Unplanned (Forced) Outage – Postponed
SF | Startup Failure