## STAFF 2.06
Duke Energy Kentucky
2024 Case 2024-00152
STAFF DR 2.06
Unit | Event Type | Event Start | Event End | Event Duration Hours | Equiv MWh Lost | Outside Mgmnt Control | Cause Code | Cause Description | Event Description
East Bend Steam-2 | D1 | 2019-01-02 12:30 | 2019-01-02 17:00 | 4.5 | 180 |  | 340 | Other pulverizer problems | Wet coal
East Bend Steam-2 | D1 | 2019-01-21 07:25 | 2019-01-22 20:43 | 37.3 | 962.34 |  | 340 | Other pulverizer problems | MILL ISSUE
East Bend Steam-2 | D4 | 2019-01-23 03:01 | 2019-01-23 09:00 | 5.983 | 338.66 |  | 1488 | Air heater (regenerative) | 2-1 Air Heater Air Drive Coupling
East Bend Steam-2 | D4 | 2019-01-24 05:01 | 2019-01-24 09:00 | 3.983 | 1347.56 |  | 920 | Other slag and ash removal problems | DESLAG
East Bend Steam-2 | D4 | 2019-01-25 05:00 | 2019-01-25 09:27 | 4.45 | 1561.99 |  | 920 | Other slag and ash removal problems | DESLAG
East Bend Steam-2 | D4 | 2019-01-27 05:00 | 2019-01-27 10:15 | 5.25 | 1748.25 |  | 920 | Other slag and ash removal problems | DESLAG
East Bend Steam-2 | D1 | 2019-03-06 15:24 | 2019-03-06 16:55 | 1.517 | 148 |  | 3811 | Service water piping | FGD Service Water Line Leak
East Bend Steam-2 | D1 | 2019-03-08 22:04 | 2019-03-08 22:44 | 0.667 | 23.99 |  | 250 | Pulverizer feeders | 2-5 Coal Feeder Issue
East Bend Steam-2 | U1 | 2019-03-30 15:00 | 2019-04-03 04:00 | 85 | 51000 |  | 3110 | Condenser tube leaks | Condenser Tube Leak
East Bend Steam-2 | D1 | 2019-05-06 | 2019-05-08 | 48 | 10463.04 |  | 8250 | Dampers other than bypass | A Module Dampers
East Bend Steam-2 | D4 | 2019-05-08 14:05 | 2019-05-08 21:00 | 6.917 | 345.83 |  | 9656 | Other stack or exhaust emissions testing - fossil | Stack Linearity Testing
East Bend Steam-2 | D1 | 2019-05-09 20:37 | 2019-05-09 22:57 | 2.333 | 108.99 |  | 250 | Pulverizer feeders | feeder issues
East Bend Steam-2 | D1 | 2019-05-15 14:42 | 2019-05-15 15:37 | 0.917 | 50.99 |  | 310 | Pulverizer mills | Loss of Mill
East Bend Steam-2 | D4 | 2019-05-15 16:01 | 2019-05-15 22:56 | 6.917 | 775.01 |  | 3414 | Feedwater pump local controls | 2-2 BFP I/H Repairs
East Bend Steam-2 | D4 | 2019-05-28 04:00 | 2019-05-30 23:48 | 67.8 | 13560 |  | 8230 | Ducting | C Module Ductwork Repairs
East Bend Steam-2 | U1 | 2019-05-31 20:29 | 2019-06-01 13:22 | 16.883 | 10130 |  | 4299 | Other hydraulic system problems | #4 Throttle Valve Actuator Failure
East Bend Steam-2 | D4 | 2019-07-11 17:00 | 2019-07-11 22:00 | 5 | 250 |  | 344 | Pulverizer inspection | 2-3 Pulverizer Inspection/Repairs
East Bend Steam-2 | D1 | 2019-07-20 03:33 | 2019-07-20 04:19 | 0.767 | 79.99 |  | 250 | Pulverizer feeders | 2-1 Feeder Trips
East Bend Steam-2 | D4 | 2019-08-03 14:00 | 2019-08-03 20:15 | 6.25 | 1250 |  | 8140 | Reaction tanks including agitators | C Module Return to Service Issues
East Bend Steam-2 | D1 | 2019-09-03 13:30 | 2019-09-04 03:00 | 13.5 | 3213 |  | 30 | Coal conveyors and feeders | F Conv Fluid Drive
East Bend Steam-2 | D1 | 2019-09-09 15:20 | 2019-09-09 20:32 | 5.2 | 254.8 |  | 250 | Pulverizer feeders | 2-1 Feeder Belt
East Bend Steam-2 | U1 | 2019-10-01 19:10 | 2019-10-04 02:00 | 54.833 | 32900 |  | 3110 | Condenser tube leaks | Condenser leak - chemistry issues
East Bend Steam-2 | U1 | 2019-11-24 22:12 | 2019-11-25 07:46 | 9.567 | 5740 |  | 4300 | Turbine supervisory system (use codes 4290 to 4299 for hydraulic oil) | Unit trip due to vibration indication
East Bend Steam-2 | U1 | 2019-11-26 14:50 | 2019-11-26 18:40 | 3.833 | 2300 |  | 4300 | Turbine supervisory system (use codes 4290 to 4299 for hydraulic oil) | #1 Bearing vibration indication
East Bend Steam-2 | D1 | 2019-12-03 12:14 | 2019-12-03 13:57 | 1.717 | 249.36 |  | 250 | Pulverizer feeders | 2-2 No coal on belt
East Bend Steam-2 | D1 | 2019-12-06 19:48 | 2019-12-06 20:50 | 1.033 | 140.12 |  | 250 | Pulverizer feeders | 2-3 No coal on belt
East Bend Steam-2 | D4 | 2019-12-14 05:00 | 2019-12-14 08:10 | 3.167 | 475 |  | 1980 | Boiler safety valve test | Setting safety valves
East Bend Steam-2 | D4 | 2019-12-16 17:00 | 2019-12-19 01:20 | 56.333 | 1126.67 |  | 344 | Pulverizer inspection | 2-3 Pulverizer inspection and repairs
East Bend Steam-2 | D1 | 2019-12-18 20:39 | 2019-12-18 22:28 | 1.817 | 282.87 |  | 250 | Pulverizer feeders | 2-1 and 2-4 No coal on belt
East Bend Steam-2 | D1 | 2019-12-21 19:41 | 2019-12-21 19:54 | 0.217 | 5 |  | 3819 | Other service water problems | Service water pressure issues
East Bend Steam-2 | D4 | 2019-12-26 12:00 | 2019-12-26 19:50 | 7.833 | 783.33 |  | 920 | Other slag and ash removal problems | Boiler DeSlag
East Bend Steam-2 | D1 | 2020-01-07 10:23 | 2020-01-07 10:51 | 0.467 | 122 |  | 250 | Pulverizer feeders | 2-1 mill lost coal
East Bend Steam-2 | D1 | 2020-01-20 07:05 | 2020-01-20 07:08 | 0.05 | 3 |  | 250 | Pulverizer feeders | 2-6 mill lost coal
East Bend Steam-2 | D1 | 2020-01-20 23:29 | 2020-01-21 00:07 | 0.633 | 28.99 |  | 250 | Pulverizer feeders | 2-6 mill lost coal
East Bend Steam-2 | D1 | 2020-01-21 08:23 | 2020-01-21 09:04 | 0.683 | 30 |  | 250 | Pulverizer feeders | 2-6 mill lost coal
East Bend Steam-2 | D1 | 2020-01-24 18:18 | 2020-01-24 18:33 | 0.25 | 48 |  | 250 | Pulverizer feeders | 2-6 mill lost coal
East Bend Steam-2 | D1 | 2020-02-15 21:42 | 2020-02-15 22:03 | 0.35 | 108 |  | 250 | Pulverizer feeders | 2-6 Feeder Plugged
East Bend Steam-2 | D4 | 2020-02-18 18:39 | 2020-02-19 01:30 | 6.85 | 1164.5 |  | 310 | Pulverizer mills | 2-3 Pulverizer Plugged Feed Tube
East Bend Steam-2 | D1 | 2020-02-20 15:01 | 2020-02-20 15:23 | 0.367 | 16 |  | 250 | Pulverizer feeders | 2-2 Lighter Trip
East Bend Steam-2 | U1 | 2020-03-02 15:20 | 2020-03-03 07:02 | 15.7 | 9420 |  | 3420 | Feedwater piping and supports | 2-1 BFP Recirc. Flange Leak
East Bend Steam-2 | D1 | 2020-03-05 12:09 | 2020-03-05 12:14 | 0.083 | 5 |  | 310 | Pulverizer mills | 2-1 Pulverizer Loss of Coal Flow
East Bend Steam-2 | U1 | 2020-06-01 21:45 | 2020-06-03 01:00 | 27.25 | 16350 |  | 8261 | Scrubber booster I.D. fan drive | 2-2 IDBF VIV
East Bend Steam-2 | D1 | 2020-06-06 00:33 | 2020-06-06 23:00 | 22.45 | 5941.17 |  | 8010 | Crushers/mills | Vertimill Cleaning and 2-2 IDBF VIV
East Bend Steam-2 | D1 | 2020-06-06 23:00 | 2020-06-11 15:48 | 112.8 | 4536.82 |  | 8261 | Scrubber booster I.D. fan drive | IDBF VIV
East Bend Steam-2 | D4 | 2020-06-11 09:00 | 2020-06-11 17:20 | 8.333 | 1120.83 |  | 8261 | Scrubber booster I.D. fan drive | IDBF VIV
East Bend Steam-2 | D4 | 2020-06-24 10:00 | 2020-06-24 17:05 | 7.083 | 1062.5 |  | 1471 | Induced draft fan motors - variable speed | 2-2 ID Fan Coolant Leak
East Bend Steam-2 | D1 | 2020-07-01 15:40 | 2020-07-01 16:55 | 1.25 | 154 |  | 250 | Pulverizer feeders | 2-6 Coal Feeder Tripped
East Bend Steam-2 | D1 | 2020-07-09 18:05 | 2020-07-10 01:44 | 7.65 | 951.28 |  | 8399 | Solids conveying and mixing system problems | Lime Feed Conveyor Power
East Bend Steam-2 | D1 | 2020-07-22 11:56 | 2020-07-22 16:20 | 4.4 | 1047.07 |  | 3410 | Feedwater pump | 2-2 BFPT Replace MOOG and duplex filters
East Bend Steam-2 | D1 | 2020-07-22 18:29 | 2020-07-23 01:30 | 7.017 | 576.56 |  | 360 | Burners | 2-1 Mill 12R Burner Line Fire
East Bend Steam-2 | D4 | 2020-07-25 09:00 | 2020-07-25 12:00 | 3 | 750 |  | 3410 | Feedwater pump | 2-2 BFPT MOOG Replacement
East Bend Steam-2 | U1 | 2020-07-25 23:18 | 2020-07-26 06:02 | 6.733 | 4040 |  | 1450 | Other air supply problems | High furnace pressure swing from slag fall.
East Bend Steam-2 | D4 | 2020-08-08 05:29 | 2020-08-08 11:15 | 5.767 | 1037.65 |  | 8210 | Valves | C Module Repairs - Replace CRW Makeup Bypass Valve
East Bend Steam-2 | D1 | 2020-08-14 23:27 | 2020-08-14 23:33 | 0.1 | 2 |  | 250 | Pulverizer feeders | Lost coal on 2-4
East Bend Steam-2 | D4 | 2020-08-15 01:53 | 2020-08-15 08:25 | 6.533 | 1140.39 |  | 920 | Other slag and ash removal problems | DESLAG
East Bend Steam-2 | D4 | 2020-08-15 10:00 | 2020-08-15 11:20 | 1.333 | 66.67 |  | 250 | Pulverizer feeders | Replacement of 2-1 Feed Cleanout Conveyor
East Bend Steam-2 | D1 | 2020-08-20 13:30 | 2020-08-20 15:35 | 2.083 | 41.67 |  | 3499 | Other feedwater system problems | Feedwater Pressure Transmitter - Sent flow into bad quality
East Bend Steam-2 | D4 | 2020-08-29 08:00 | 2020-08-29 19:30 | 11.5 | 550.05 |  | 250 | Pulverizer feeders | 2-3 Feeder Belt Replacement
East Bend Steam-2 | D1 | 2020-09-14 17:42 | 2020-09-14 18:08 | 0.433 | 16 |  | 250 | Pulverizer feeders | Pulverizer feeder 480V breaker would not close.
East Bend Steam-2 | D1 | 2020-09-17 14:13 | 2020-09-17 17:38 | 3.417 | 872.34 |  | 360 | Burners | Burner Fire
East Bend Steam-2 | D1 | 2020-09-18 10:10 | 2020-09-18 10:46 | 0.6 | 182 |  | 250 | Pulverizer feeders | Bunker rundown for outage
East Bend Steam-2 | D4 | 2020-09-18 16:50 | 2020-09-18 21:11 | 4.35 | 1327.66 |  | 250 | Pulverizer feeders | Bunker rundown for outage
East Bend Steam-2 | D1 | 2020-11-24 01:00 | 2020-11-25 04:15 | 27.25 | 4802.27 |  | 1850 | Boiler water condition (not feedwater water quality) | Startup Chemistry Issues
East Bend Steam-2 | D1 | 2020-11-25 04:15 | 2020-11-28 05:44 | 73.483 | 2939.33 |  | 260 | Primary air fan | 2-4 Mill Trip on Low PA Flow
East Bend Steam-2 | D4 | 2020-11-28 04:33 | 2020-11-28 05:44 | 1.183 | 456.79 |  | 4040 | Bearings | High Vibration on HP Turbine
East Bend Steam-2 | D1 | 2020-12-02 20:16 | 2020-12-02 22:27 | 2.183 | 109.17 |  | 253 | Pulverizer feeder motor | 2-4 Pulverizer Issues
East Bend Steam-2 | D1 | 2020-12-06 14:12 | 2020-12-06 16:22 | 2.167 | 201 |  | 253 | Pulverizer feeder motor | 2-4 Feeder Motor Stopped
East Bend Steam-2 | D4 | 2020-12-10 04:00 | 2020-12-10 11:00 | 7 | 1820 |  | 8010 | Crushers/mills | Vertimill Heat Exchanger Tuning
East Bend Steam-2 | D4 | 2020-12-11 03:40 | 2020-12-11 11:00 | 7.333 | 194.99 |  | 8010 | Crushers/mills | Vertimill Heat Exchanger Tuning
East Bend Steam-2 | D1 | 2020-12-24 16:20 | 2020-12-24 16:35 | 0.25 | 7.5 |  | 310 | Pulverizer mills | 2-4 Pulverizer Mill
East Bend Steam-2 | D4 | 2020-12-31 02:50 | 2020-12-31 10:53 | 8.05 | 1610 |  | 920 | Other slag and ash removal problems | DESLAG
East Bend Steam-2 | D1 | 2021-01-01 19:49 | 2021-01-01 20:00 | 0.183 | 2 |  | 310 | Pulverizer mills | Starting 2-2 Pulv. Needed 6 mills in service to maintain load.
East Bend Steam-2 | D1 | 2021-01-08 13:00 | 2021-01-08 16:05 | 3.083 | 418.99 |  | 8010 | Crushers/mills | 2-1 Vertimill Cleaning, 2-2 Vertimill Lime Slurry Transfer Pump Belt Replacement
East Bend Steam-2 | D1 | 2021-01-18 18:43 | 2021-01-20 06:22 | 35.65 | 10435.47 |  | 1150 | Second superheater | Boiler Slag, could not pull enough air
East Bend Steam-2 | U1 | 2021-01-25 20:38 | 2021-01-26 00:18 | 3.667 | 2200 |  | 800 | Drums and drum internals (single drum only) | Tripped due to drum level
East Bend Steam-2 | U1 | 2021-01-26 00:19 | 2021-01-26 01:42 | 1.383 | 830 |  | 800 | Drums and drum internals (single drum only) | Tripped due to drum level
East Bend Steam-2 | D1 | 2021-01-26 04:00 | 2021-01-27 08:20 | 28.333 | 9281.72 |  | 3352 | Feedwater chemistry (not specific to condenser, polishers, or chemical addition) | Startup Chemistry Issues
East Bend Steam-2 | U1 | 2021-01-27 08:20 | 2021-01-29 16:44 | 56.4 | 33840 |  | 3110 | Condenser tube leaks | Condenser Tube Leak
East Bend Steam-2 | D1 | 2021-02-05 10:25 | 2021-02-05 13:17 | 2.867 | 544.67 |  | 8010 | Crushers/mills | Vertimill Screw Failure
East Bend Steam-2 | D4 | 2021-02-06 05:01 | 2021-02-06 09:00 | 3.983 | 1195 |  | 920 | Other slag and ash removal problems | DESLAG
East Bend Steam-2 | D4 | 2021-02-06 11:30 | 2021-02-06 20:38 | 9.133 | 456.67 |  | 335 | Pulverizer lube oil system | Pulverizer Lube Oil Pump Replacement
East Bend Steam-2 | D4 | 2021-02-07 03:00 | 2021-02-07 08:15 | 5.25 | 1575 |  | 920 | Other slag and ash removal problems | DESLAG
East Bend Steam-2 | D1 | 2021-02-11 17:00 | 2021-02-11 18:14 | 1.233 | 44.01 |  | 250 | Pulverizer feeders | 2-1 Feeder Lost Coal
East Bend Steam-2 | D4 | 2021-02-27 04:00 | 2021-03-01 04:59 | 48.983 | 9796.67 |  | 8230 | Ducting | FGD C Module Ductwork Leak Repairs
East Bend Steam-2 | D1 | 2021-03-08 08:03 | 2021-03-08 08:08 | 0.083 | 23 |  | 250 | Pulverizer feeders | Lost coal on 2-3 Pulverizer
East Bend Steam-2 | D4 | 2021-03-09 05:01 | 2021-03-09 07:08 | 2.117 | 635 |  | 8499 | Other miscellaneous wet scrubber problems | FGD Chemistry
East Bend Steam-2 | D1 | 2021-03-16 13:51 | 2021-03-16 22:46 | 8.917 | 2896.04 |  | 30 | Coal conveyors and feeders | F Conv. Fluid Drive
East Bend Steam-2 | D1 | 2021-03-17 15:49 | 2021-03-17 15:57 | 0.133 | 40.52 |  | 264 | Other primary air fan problems | 2-4 PA Damper
East Bend Steam-2 | D1 | 2021-03-18 11:03 | 2021-03-18 11:04 | 0.017 | 4 |  | 264 | Other primary air fan problems | 2-4 PA Damper
East Bend Steam-2 | D1 | 2021-03-19 17:43 | 2021-03-19 17:52 | 0.15 | 3 |  | 264 | Other primary air fan problems | 2-4 PA Damper
East Bend Steam-2 | D1 | 2021-03-19 18:20 | 2021-03-19 21:00 | 2.667 | 26.67 |  | 264 | Other primary air fan problems | 2-4 PA Damper
East Bend Steam-2 | D4 | 2021-03-20 06:46 | 2021-03-20 19:00 | 12.233 | 2327.88 |  | 8230 | Ducting | C Module Outage to Repair Duct Leaks
East Bend Steam-2 | D1 | 2021-04-03 08:55 | 2021-04-03 12:18 | 3.383 | 284 |  | 1480 | Other induced draft fan problems | 2-4 ID Fan Conductivity High
East Bend Steam-2 | D1 | 2021-04-18 20:19 | 2021-04-18 20:55 | 0.6 | 25 |  | 335 | Pulverizer lube oil system | 2-1 Pulv. Oil Leak, Removed From Service
East Bend Steam-2 | D1 | 2021-04-19 19:56 | 2021-04-24 03:14 | 103.3 | 24334.38 |  | 260 | Primary air fan | 2-2 PA Fan Shaft and Bearings
East Bend Steam-2 | D1 | 2021-04-20 10:00 | 2021-04-21 14:45 | 28.75 | 1597.35 |  | 1489 | Air heater (heat pipe, plate-type) | Secondary Air Heater Baskets
East Bend Steam-2 | D1 | 2021-04-21 17:20 | 2021-04-21 19:30 | 2.167 | 182.93 |  | 310 | Pulverizer mills | 2-2 Mill out for Flame Scanner Tuning
East Bend Steam-2 | D1 | 2021-05-11 23:10 | 2021-05-12 04:01 | 4.85 | 834.01 |  | 1457 | Induced draft fan lubrication systems | 2-1 ID Fan Tripped, No Coolant
East Bend Steam-2 | D1 | 2021-05-15 15:12 | 2021-05-15 21:10 | 5.967 | 1283.31 |  | 1480 | Other induced draft fan problems | ID Fan Maintenance
East Bend Steam-2 | D4 | 2021-05-22 09:30 | 2021-05-22 15:02 | 5.533 | 553.33 |  | 1457 | Induced draft fan lubrication systems | 2-4 ID Fan, Replace Molded Case Breaker for Coolant Pump #1
East Bend Steam-2 | D4 | 2021-05-29 06:00 | 2021-05-29 17:52 | 11.867 | 2590.37 |  | 260 | Primary air fan | 2-2 PA Fan Vibration - Replace Outboard Bearing
East Bend Steam-2 | D1 | 2021-05-30 00:53 | 2021-05-30 02:26 | 1.55 | 471.99 |  | 1455 | Induced draft fans | 2-4 ID Fan Spinning Backwards
East Bend Steam-2 | D1 | 2021-06-08 09:47 | 2021-06-08 10:13 | 0.433 | 138 | OMC | 9270 | Wet coal (OMC) | OMC - Lost 2-6 Mill - High Pulv. Outlet Temp - Plugged with Wet Coal
East Bend Steam-2 | D1 | 2021-06-08 12:30 | 2021-06-09 02:54 | 14.4 | 792 | OMC | 9270 | Wet coal (OMC) | OMC - Cleaning wet coal out of 2-6 Mill
East Bend Steam-2 | D1 | 2021-06-08 16:37 | 2021-06-08 17:48 | 1.183 | 42.9 |  | 310 | Pulverizer mills | Lost 2-3 Mill
East Bend Steam-2 | D1 | 2021-06-08 18:26 | 2021-06-08 18:55 | 0.483 | 9 |  | 310 | Pulverizer mills | Lost 2-5 Mill
East Bend Steam-2 | D1 | 2021-06-11 14:05 | 2021-06-11 14:47 | 0.7 | 21 |  | 250 | Pulverizer feeders | Lost coal on 2-3 Feeder
East Bend Steam-2 | D4 | 2021-06-13 02:01 | 2021-06-13 10:30 | 8.483 | 2088.68 |  | 260 | Primary air fan | 2-2 PA Fan Bearing Work
East Bend Steam-2 | D1 | 2021-06-21 14:35 | 2021-06-21 22:17 | 7.7 | 2082 |  | 260 | Primary air fan | 2-2 PA Fan Inboard Bearing Cooler Line Leak Repair
East Bend Steam-2 | D4 | 2021-06-26 02:00 | 2021-06-26 08:30 | 6.5 | 1950 |  | 1480 | Other induced draft fan problems | 2-4 ID Fan #1 Coolant Pump Repairs and Test
East Bend Steam-2 | D4 | 2021-07-01 04:01 | 2021-07-01 10:15 | 6.233 | 1904.6 |  | 260 | Primary air fan | Remove 2-2 PA Fan from Service to Tighten Bearing Bolts
East Bend Steam-2 | D1 | 2021-07-18 03:45 | 2021-07-18 04:19 | 0.567 | 185 |  | 335 | Pulverizer lube oil system | 2-4 Pulv. Trip - Lost Lube Oil Pump
East Bend Steam-2 | D4 | 2021-07-18 08:00 | 2021-07-18 12:00 | 4 | 800 |  | 8210 | Valves | Replace C Module Slurry Feed Control Valve
East Bend Steam-2 | D1 | 2021-07-24 18:05 | 2021-07-24 18:44 | 0.65 | 122 |  | 340 | Other pulverizer problems | 2-4 Pulv. Trip
East Bend Steam-2 | D1 | 2021-07-24 20:52 | 2021-07-24 21:21 | 0.483 | 17 |  | 340 | Other pulverizer problems | 2-4 Pulv Unavailable - Fans Maxed
East Bend Steam-2 | D1 | 2021-07-25 00:39 | 2021-07-25 02:00 | 1.35 | 10 |  | 340 | Other pulverizer problems | 2-4 Pulv Unavailable
East Bend Steam-2 | D1 | 2021-07-25 19:20 | 2021-07-26 16:40 | 21.333 | 866.13 |  | 338 | Pulverizer control systems (temperature and pressure) | 2-4 Pulv Trip due to PA Damper
East Bend Steam-2 | D1 | 2021-07-27 13:53 | 2021-07-27 17:16 | 3.383 | 796 |  | 340 | Other pulverizer problems | 2-4 Mill Unavailable - Swapping Mills
East Bend Steam-2 | D1 | 2021-07-27 19:20 | 2021-07-27 21:15 | 1.917 | 38.33 |  | 340 | Other pulverizer problems | 2-4 Mill Unavailable - Bad Fuel Quality
East Bend Steam-2 | D1 | 2021-07-29 01:30 | 2021-07-29 07:14 | 5.733 | 1560.04 |  | 920 | Other slag and ash removal problems | SFC Unable to Pull Ash
East Bend Steam-2 | U1 | 2021-07-29 07:14 | 2021-07-30 23:50 | 40.6 | 24360 |  | 890 | Bottom ash systems (wet or dry) | SFC Unable to Pull Ash
East Bend Steam-2 | D1 | 2021-08-01 14:10 | 2021-08-02 22:07 | 31.95 | 11182.5 |  | 8030 | Classifiers | FGD - Thickener Upsets
East Bend Steam-2 | U1 | 2021-08-02 23:06 | 2021-08-05 14:14 | 63.133 | 37880 |  | 3416 | Other feedwater pump problems | 2-1 BFPT Manual Valve Leaking
East Bend Steam-2 | D1 | 2021-08-08 18:52 | 2021-08-08 21:00 | 2.133 | 21.33 |  | 1400 | Forced draft fans | Ran Out of FD Fan
East Bend Steam-2 | D1 | 2021-08-10 22:40 | 2021-08-11 03:00 | 4.333 | 43.33 |  | 1400 | Forced draft fans | 2-2 FD Fan Maxed Out
East Bend Steam-2 | D4 | 2021-08-17 10:00 | 2021-08-17 10:01 | 0.017 | 3.5 |  | 8399 | Solids conveying and mixing system problems | Replace Radial Stacker Belt
East Bend Steam-2 | D1 | 2021-08-26 06:34 | 2021-08-26 07:58 | 1.4 | 171.99 |  | 340 | Other pulverizer problems | Dropped Load to Swap Mills
East Bend Steam-2 | D1 | 2021-08-28 19:43 | 2021-08-28 23:00 | 3.283 | 775 |  | 4520 | Stator windings, bushings, and terminals | Generator Flex Links and A-phase Bushing
East Bend Steam-2 | U1 | 2021-08-28 23:00 | 2021-09-05 14:30 | 183.5 | 110100 |  | 4520 | Stator windings, bushings, and terminals | Generator Flex Links and A-phase Bushing
East Bend Steam-2 | U1 | 2021-09-05 15:14 | 2021-09-05 16:58 | 1.733 | 1040 |  | 1740 | Boiler drum gage glasses / level indicator | Trip on boiler drum level.
East Bend Steam-2 | U1 | 2021-09-05 17:06 | 2021-09-05 18:42 | 1.6 | 960 |  | 1740 | Boiler drum gage glasses / level indicator | Trip on boiler drum level.
East Bend Steam-2 | D1 | 2021-09-08 10:40 | 2021-09-11 03:03 | 64.383 | 643.67 |  | 1700 | Feedwater controls (report local controls - feedwater pump, feedwater regulator valve, etc., - with component or system) | Governor Valve
East Bend Steam-2 | D1 | 2021-09-09 01:42 | 2021-09-09 02:28 | 0.767 | 126.66 |  | 310 | Pulverizer mills | Lost coal on 2-4 mill
East Bend Steam-2 | D1 | 2021-09-09 07:53 | 2021-09-09 09:42 | 1.817 | 372.67 |  | 310 | Pulverizer mills | Swapping mills
East Bend Steam-2 | D1 | 2021-09-10 14:16 | 2021-09-11 03:03 | 12.783 | 2402.18 |  | 95 | Bunker flow problems | Bunker Rundown for Fall 2021 Planned Outage
East Bend Steam-2 | U1 | 2021-12-19 02:28 | 2021-12-26 02:40 | 168.2 | 100920 |  | 4609 | Other exciter problems | Exciter repairs
East Bend Steam-2 | U1 | 2021-12-26 14:54 | 2021-12-27 04:08 | 13.233 | 7940 |  | 1700 | Feedwater controls (report local controls - feedwater pump, feedwater regulator valve, etc., - with component or system) | Lost drop 25/75 Feedwater Controls
East Bend Steam-2 | U1 | 2021-12-27 08:46 | 2021-12-27 19:00 | 10.233 | 6140 |  | 4420 | Vibration of the turbine generator unit that cannot be attributed to a specific cause such as bearings or blades (use this code for balance moves) | turbine vibration trip
East Bend Steam-2 | D1 | 2021-12-29 20:00 | 2021-12-31 02:14 | 30.233 | 6514.68 |  | 4560 | Generator vibration (excluding vibration due to failed bearing and other components) | Generator Vibration
East Bend Steam-2 | D1 | 2022-01-02 22:00 | 2022-01-03 03:01 | 5.017 | 1265 |  | 4560 | Generator vibration (excluding vibration due to failed bearing and other components) | Derate due to #9 bearing vibration
East Bend Steam-2 | D1 | 2022-01-08 00:13 | 2022-01-08 01:08 | 0.917 | 32 |  | 250 | Pulverizer feeders | 2-6 chute pluggage
East Bend Steam-2 | D1 | 2022-01-08 11:30 | 2022-01-08 12:54 | 1.4 | 61.99 |  | 310 | Pulverizer mills | 5 mill runback
East Bend Steam-2 | D1 | 2022-01-09 23:54 | 2022-01-10 03:00 | 3.1 | 298 |  | 250 | Pulverizer feeders | 2-2 feeder loss of coal
East Bend Steam-2 | D1 | 2022-01-10 03:00 | 2022-01-10 23:45 | 20.75 | 1062.81 |  | 1424 | Secondary air fan/blower controls | Secondary Air control issue
East Bend Steam-2 | D1 | 2022-01-11 21:16 | 2022-01-13 00:30 | 27.233 | 2236.67 |  | 310 | Pulverizer mills | 2-6 mill trip
East Bend Steam-2 | D1 | 2022-01-12 19:57 | 2022-01-12 20:25 | 0.467 | 0 |  | 310 | Pulverizer mills | swapping mills 2-6 pulverizer
East Bend Steam-2 | D1 | 2022-01-12 23:54 | 2022-01-13 00:07 | 0.217 | 0 |  | 310 | Pulverizer mills | swapping mills, 2-6 pulverizer
East Bend Steam-2 | D1 | 2022-01-13 07:55 | 2022-01-15 19:10 | 59.25 | 4394.57 | OMC | 9270 | Wet coal (OMC) | 2-6 pulverizer pluggage- Wet Coal
East Bend Steam-2 | D1 | 2022-01-13 23:52 | 2022-01-14 04:55 | 5.05 | 0 |  | 3630 | 400-700 volt transformers | 2A-2 transformer failure
East Bend Steam-2 | U1 | 2022-01-18 21:59 | 2022-01-20 04:59 | 31 | 18600 |  | 4293 | Hydraulic system pipes and valves | Loss of EH due to pipe failure on Governor valves
East Bend Steam-2 | U1 | 2022-01-20 05:04 | 2022-01-20 05:40 | 0.6 | 360 |  | 3401 | Startup feedwater pump | Feedwater trip
East Bend Steam-2 | D1 | 2022-01-21 20:22 | 2022-02-01 04:23 | 248.017 | 6044.17 |  | 4301 | Turbine governing system | #5 Governor valve
East Bend Steam-2 | D1 | 2022-01-25 20:10 | 2022-01-25 20:58 | 0.8 | 10.5 |  | 8010 | Crushers/mills | Lost vertimill
East Bend Steam-2 | D4 | 2022-02-04 22:09 | 2022-02-08 07:29 | 81.333 | 1588.11 |  | 4301 | Turbine governing system | Governor Valves 5&8
East Bend Steam-2 | D1 | 2022-02-05 19:12 | 2022-02-05 20:09 | 0.95 | 17.44 |  | 1440 | Air supply dampers | 2-5 pulverizer secondary air damper flow
East Bend Steam-2 | D1 | 2022-02-06 20:49 | 2022-02-08 07:29 | 34.667 | 3774.42 |  | 1470 | Induced draft fan motors and drives | 2-3 ID fan VFD trip
East Bend Steam-2 | D4 | 2022-02-08 04:00 | 2022-02-08 07:29 | 3.483 | 373.74 |  | 1470 | Induced draft fan motors and drives | load drop to start 2-3 ID fan VFD
East Bend Steam-2 | U1 | 2022-02-08 07:28 | 2022-02-08 17:36 | 10.133 | 6080 |  | 250 | Pulverizer feeders | 2-2 preheat coil pump failure caused low voltage and tripped 2 out of 3 feeders
East Bend Steam-2 | D1 | 2022-02-09 06:32 | 2022-02-10 09:20 | 26.8 | 1340 |  | 350 | Pulverized fuel and air piping (from pulverizer to wind box) (see code 0898 for pulverizer reject system problems) | 2-4 pulv damper issue
East Bend Steam-2 | D1 | 2022-02-10 03:00 | 2022-02-10 03:11 | 0.183 | 0 |  | 350 | Pulverized fuel and air piping (from pulverizer to wind box) (see code 0898 for pulverizer reject system problems) | 2-4 pulv swing valve
East Bend Steam-2 | D4 | 2022-02-10 03:00 | 2022-02-10 09:20 | 6.333 | 253.33 |  | 350 | Pulverized fuel and air piping (from pulverizer to wind box) (see code 0898 for pulverizer reject system problems) | Maintenance derate to replace 2-4 pulv damper beckdrive
East Bend Steam-2 | D1 | 2022-02-11 12:30 | 2022-02-14 14:06 | 73.6 | 2447.2 | OMC | 9250 | Low BTU coal (OMC) | Coal Quality
East Bend Steam-2 | D1 | 2022-02-12 05:08 | 2022-02-12 05:32 | 0.4 | 54.7 |  | 250 | Pulverizer feeders | Lost 2-4 coal feeder
East Bend Steam-2 | D1 | 2022-02-12 09:49 | 2022-02-12 11:13 | 1.4 | 177.45 |  | 250 | Pulverizer feeders | 2 Lost 2-3 coal feeder
East Bend Steam-2 | D1 | 2022-02-15 01:18 | 2022-02-16 00:11 | 22.883 | 686.5 | OMC | 9250 | Low BTU coal (OMC) | Coal Quality
East Bend Steam-2 | D4 | 2022-02-15 04:41 | 2022-02-16 00:18 | 19.617 | 4832.57 |  | 260 | Primary air fan | PA fan issue/inspection
East Bend Steam-2 | D1 | 2022-02-17 03:14 | 2022-02-17 04:06 | 0.867 | 167.99 |  | 250 | Pulverizer feeders | 2-2 Pulverizer feeder trip
East Bend Steam-2 | D4 | 2022-02-18 03:00 | 2022-02-18 05:34 | 2.567 | 282.33 |  | 550 | Reheat steam relief/safety valves | Setting safety valves
East Bend Steam-2 | D4 | 2022-02-19 04:04 | 2022-02-23 01:30 | 93.433 | 28030 |  | 260 | Primary air fan | 2-2 PA fan motor and inspect bearings
East Bend Steam-2 | D1 | 2022-02-26 00:12 | 2022-02-26 00:40 | 0.467 | 12 | OMC | 9270 | Wet coal (OMC) | 2-6 pulverizer-wet coal
East Bend Steam-2 | D4 | 2022-03-05 08:00 | 2022-03-05 15:00 | 7 | 2100 |  | 270 | Primary air duct and dampers | PA fan inlet vanes
East Bend Steam-2 | D4 | 2022-03-12 09:00 | 2022-03-12 21:00 | 12 | 600 |  | 898 | Bottom ash pyrite hopper (pulverizer reject) system | Planned derate- pyrite hopper knife gate
East Bend Steam-2 | U1 | 2022-05-07 04:20 | 2022-05-07 06:00 | 1.667 | 1000 |  | 260 | Primary air fan | PA fan vibration
East Bend Steam-2 | U1 | 2022-05-08 03:24 | 2022-05-09 17:28 | 38.067 | 22840 |  | 3410 | Feedwater pump | Unit Trip-Boiler Feed Pump recirc line repairs
East Bend Steam-2 | D1 | 2022-05-11 09:00 | 2022-05-11 11:00 | 2 | 97 |  | 8020 | Mill slurry tanks supply problems | Vertimill loss of grinding water
East Bend Steam-2 | D4 | 2022-05-16 10:00 | 2022-05-16 16:00 | 6 | 1200 |  | 1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler optimization tuning, mid-load off AGC
East Bend Steam-2 | U1 | 2022-05-31 02:16 | 2022-06-01 06:33 | 28.283 | 16970 |  | 4700 | Generator voltage control | Voltage regulator
East Bend Steam-2 | U1 | 2022-06-01 07:16 | 2022-06-02 08:34 | 25.3 | 15180 |  | 3410 | Feedwater pump | 2-2 BFPT Trip - Unit trip on Low Drum Level
East Bend Steam-2 | D1 | 2022-06-22 18:17 | 2022-06-22 21:35 | 3.3 | 52.11 |  | 1470 | Induced draft fan motors and drives | 2-1, 2-2 and 2-4 ID Fan VFDs temperature high
East Bend Steam-2 | D1 | 2022-06-24 10:47 | 2022-06-24 11:03 | 0.267 | 44 |  | 370 | Burner instruments and controls (except light off) | 2-5 Pulverizer tripped due to burner flames not detected
East Bend Steam-2 | D1 | 2022-07-01 19:53 | 2022-07-01 21:26 | 1.55 | 21.28 |  | 1400 | Forced draft fans | FD Fans Max Capability
East Bend Steam-2 | D1 | 2022-07-02 19:20 | 2022-07-03 10:49 | 15.483 | 154.83 |  | 1400 | Forced draft fans | FD Fan Max Capacity
East Bend Steam-2 | D1 | 2022-07-04 21:00 | 2022-07-04 21:30 | 0.5 | 6 |  | 1400 | Forced draft fans | FD Fan Max Capacity
East Bend Steam-2 | D1 | 2022-07-05 | 2022-07-05 06:20 | 6.333 | 107.98 |  | 1400 | Forced draft fans | FD Fan Max Capacity
East Bend Steam-2 | D1 | 2022-07-05 17:25 | 2022-07-05 19:43 | 2.3 | 136.99 |  | 1470 | Induced draft fan motors and drives | ID Fan VFDs at maximum temperature
East Bend Steam-2 | D1 | 2022-07-05 21:00 | 2022-07-06 03:00 | 6 | 144 |  | 1400 | Forced draft fans | FD Fan Max Capacity
East Bend Steam-2 | D1 | 2022-07-06 16:00 | 2022-07-08 01:55 | 33.917 | 747.52 |  | 1400 | Forced draft fans | FD Fan Max Capacity
East Bend Steam-2 | D1 | 2022-07-07 22:52 | 2022-07-07 23:35 | 0.717 | 6.2 |  | 1400 | Forced draft fans | FD Fan Max Capacity
East Bend Steam-2 | D1 | 2022-07-08 01:55 | 2022-07-09 16:00 | 38.083 | 761.67 |  | 1400 | Forced draft fans | FD Fan Max Capacity
East Bend Steam-2 | D1 | 2022-07-11 19:30 | 2022-07-14 11:35 | 64.083 | 15658.12 |  | 8330 | Dewatering equipment (thickener, centrifuge, etc.) | FGD Thickener Chemistry
East Bend Steam-2 | D1 | 2022-07-19 19:00 | 2022-07-21 03:21 | 32.35 | 942.36 |  | 1400 | Forced draft fans | FD Fan Max Capacity
East Bend Steam-2 | D1 | 2022-07-20 19:21 | 2022-07-20 19:37 | 0.267 | 0 |  | 4240 | Bearings | LP Turbine #7 Bearing Vibration
East Bend Steam-2 | D1 | 2022-07-21 03:21 | 2022-07-24 01:20 | 69.983 | 2068.01 |  | 1400 | Forced draft fans | FD Fan Max Capacity
East Bend Steam-2 | D1 | 2022-07-23 04:23 | 2022-07-23 05:10 | 0.783 | 35.85 |  | 1400 | Forced draft fans | FD Fan Max Capacity
East Bend Steam-2 | D1 | 2022-07-24 15:20 | 2022-07-26 15:28 | 48.133 | 1404.53 |  | 1400 | Forced draft fans | FD Fan Max Capacity
East Bend Steam-2 | D1 | 2022-07-26 20:50 | 2022-07-27 03:30 | 6.667 | 66.67 |  | 1400 | Forced draft fans | FD Fan Max Capacity
East Bend Steam-2 | D1 | 2022-07-27 05:29 | 2022-07-27 05:42 | 0.217 | 8 |  | 1400 | Forced draft fans | FD Fan Max Capacity
East Bend Steam-2 | D1 | 2022-07-27 18:30 | 2022-07-27 20:00 | 1.5 | 75 |  | 1400 | Forced draft fans | FD Fan Max Capacity
East Bend Steam-2 | D1 | 2022-07-27 20:00 | 2022-07-29 05:47 | 33.783 | 959.78 |  | 1400 | Forced draft fans | FD Fan Max Capacity
East Bend Steam-2 | D1 | 2022-08-01 17:00 | 2022-08-02 14:15 | 21.25 | 784.13 |  | 8260 | Scrubber booster I.D. fan (fan specific to the scrubber) | ID Booster Fan Breaker Single Phase
East Bend Steam-2 | D1 | 2022-08-02 04:00 | 2022-08-04 12:50 | 56.833 | 1000.14 |  | 8260 | Scrubber booster I.D. fan (fan specific to the scrubber) | ID Booster Fan Breaker Single Phase
East Bend Steam-2 | D1 | 2022-08-04 14:20 | 2022-08-05 17:58 | 27.633 | 552.67 |  | 8260 | Scrubber booster I.D. fan (fan specific to the scrubber) | ID Booster Fan Breaker Single Phase
East Bend Steam-2 | D1 | 2022-08-05 17:55 | 2022-08-05 17:58 | 0.05 | 7 |  | 3844 | Soot blowing air compressor and system | SBAC Trip
East Bend Steam-2 | U1 | 2022-08-05 17:58 | 2022-08-06 03:36 | 9.633 | 5780 |  | 3844 | Soot blowing air compressor and system | Station air compressor tripped due to damaged seal air piping.
East Bend Steam-2 | U1 | 2022-08-06 03:41 | 2022-08-06 04:55 | 1.233 | 740 |  | 3414 | Feedwater pump local controls | Drum Level trip
East Bend Steam-2 | D1 | 2022-08-06 20:00 | 2022-08-06 22:30 | 2.5 | 12.5 |  | 8260 | Scrubber booster I.D. fan (fan specific to the scrubber) | ID Booster Fan Breaker Single Phase
East Bend Steam-2 | U1 | 2022-08-07 00:21 | 2022-08-07 10:22 | 10.017 | 6010 |  | 3970 | Distributive Control System (DCS) - process computer | DCS Drop 25 Failure - MFT
East Bend Steam-2 | U1 | 2022-08-07 10:28 | 2022-08-07 12:01 | 1.55 | 930 |  | 3414 | Feedwater pump local controls | Drum Level trip
East Bend Steam-2 | D1 | 2022-08-10 15:40 | 2022-08-12 04:50 | 37.167 | 11369.28 | OMC | 9130 | Lack of fuel: Physical failures of fuel supply or delivery/transportation of fuel | Reclaim System flooding and coal supply delayed due to heavy rain and river conditions
East Bend Steam-2 | D4 | 2022-09-14 04:01 | 2022-09-17 12:15 | 80.233 | 23978.53 |  | 260 | Primary air fan | PA Fan Motor oil Leak
East Bend Steam-2 | D1 | 2022-09-21 11:10 | 2022-09-21 12:20 | 1.167 | 211.17 |  | 350 | Pulverized fuel and air piping (from pulverizer to wind box) (see code 0898 for pulverizer reject system problems) | 2-2 Pulverizer 8R Burner Line Hot Spot
East Bend Steam-2 | D1 | 2022-09-21 20:25 | 2022-09-21 21:41 | 1.267 | 12.67 |  | 1470 | Induced draft fan motors and drives | 2-2 ID Fan VFD Cooling Fan failed limiting cooling
East Bend Steam-2 | D1 | 2022-09-22 06:43 | 2022-09-22 07:38 | 0.917 | 167.67 |  | 350 | Pulverized fuel and air piping (from pulverizer to wind box) (see code 0898 for pulverizer reject system problems) | 2-2 Pulverizer 1R burner line hot spot.
East Bend Steam-2 | D4 | 2022-09-22 23:26 | 2022-09-23 01:47 | 2.35 | 907.99 |  | 95 | Bunker flow problems | Bunker Rundown to empty prior to outage.
East Bend Steam-2 | D1 | 2022-11-04 07:00 | 2022-11-05 01:06 | 18.1 | 4206.08 |  | 3620 | Main transformer | Main power transformer cooling
East Bend Steam-2 | D1 | 2022-11-16 14:10 | 2022-11-18 18:00 | 51.833 | 9848.33 |  | 1510 | Flue gas ducts (except recirculation) | FGD Ductwork
East Bend Steam-2 | D4 | 2022-11-18 21:00 | 2022-11-18 21:46 | 0.767 | 76.67 |  | 1510 | Flue gas ducts (except recirculation) | FGD Ductwork
East Bend Steam-2 | D4 | 2022-11-23 05:00 | 2022-11-23 22:32 | 17.533 | 3331.33 |  | 1510 | Flue gas ducts (except recirculation) | FGD Ductwork
East Bend Steam-2 | D1 | 2022-12-03 01:11 | 2022-12-03 02:37 | 1.433 | 414.99 |  | 250 | Pulverizer feeders | Lost coal on 2-4 Feeder
East Bend Steam-2 | D1 | 2022-12-05 15:44 | 2022-12-08 04:56 | 61.2 | 11646.97 |  | 8100 | Scrubber/absorber tower or module | C Module Mixer Failure
East Bend Steam-2 | U1 | 2022-12-09 06:10 | 2022-12-09 08:34 | 2.4 | 1440 |  | 1700 | Feedwater controls (report local controls - feedwater pump, feedwater regulator valve, etc., - with component or system) | Drum Level control trip
East Bend Steam-2 | U1 | 2022-12-09 10:30 | 2022-12-10 02:08 | 15.633 | 9380 |  | 1700 | Feedwater controls (report local controls - feedwater pump, feedwater regulator valve, etc., - with component or system) | Feedwater control trip
East Bend Steam-2 | U1 | 2022-12-10 03:08 | 2022-12-10 04:22 | 1.233 | 740 |  | 1700 | Feedwater controls (report local controls - feedwater pump, feedwater regulator valve, etc., - with component or system) | Feedwater control trip
East Bend Steam-2 | D1 | 2022-12-10 15:23 | 2022-12-14 21:18 | 101.917 | 22358.48 |  | 260 | Primary air fan | 2-1 Primary air fan motor failure
East Bend Steam-2 | D1 | 2022-12-16 14:22 | 2022-12-16 17:00 | 2.633 | 184.41 |  | 250 | Pulverizer feeders | Lost coal on 2-3 Feeder
East Bend Steam-2 | D1 | 2022-12-21 11:27 | 2022-12-21 23:00 | 11.55 | 2889.58 |  | 1470 | Induced draft fan motors and drives | 2-1 ID Fan VFD Trip
East Bend Steam-2 | D1 | 2022-12-26 00:34 | 2022-12-26 22:00 | 21.433 | 3921.87 |  | 1470 | Induced draft fan motors and drives | 2-1 ID Fan VFD
East Bend Steam-2 | D4 | 2023-01-19 11:00 | 2023-01-19 23:00 | 12 | 2160 |  | 270 | Primary air duct and dampers | 2-4 Pulverizer PA Damper Control
East Bend Steam-2 | U1 | 2023-03-15 08:32 | 2023-03-15 11:18 | 2.767 | 1660 |  | 1700 | Feedwater controls (report local controls - feedwater pump, feedwater regulator valve, etc., - with component or system) | Feedwater drum level control trip
East Bend Steam-2 | D1 | 2023-03-16 10:20 | 2023-03-16 19:00 | 8.667 | 1213.33 |  | 250 | Pulverizer feeders | 2-3 Coal Feeder Belt Failure
East Bend Steam-2 | D1 | 2023-03-17 00:45 | 2023-03-18 01:10 | 24.417 | 4395 |  | 250 | Pulverizer feeders | 2-5 Coal Feeder Belt Failure
East Bend Steam-2 | D1 | 2023-03-22 04:01 | 2023-04-01 04:00 | 239.983 | 45596.83 |  | 8260 | Scrubber booster I.D. fan (fan specific to the scrubber) | 2-1 IDBF Coupling Failure
East Bend Steam-2 | D1 | 2023-03-27 10:05 | 2023-03-27 11:00 | 0.917 | 0 |  | 95 | Bunker flow problems | 2-5 Coal feed plugged.
East Bend Steam-2 | D1 | 2023-03-27 15:01 | 2023-03-27 20:00 | 4.983 | 645.54 |  | 95 | Bunker flow problems | 2-6 Coal flow plugged
East Bend Steam-2 | D4 | 2023-04-01 04:01 | 2023-04-15 23:59 | 355.967 | 40368.67 |  | 8260 | Scrubber booster I.D. fan (fan specific to the scrubber) | 2-1 IDBF Sole Plate Repairs
East Bend Steam-2 | U1 | 2023-04-05 07:30 | 2023-04-11 07:00 | 143.5 | 86100 |  | 3662 | 4000-7000 volt conductors and buses | 24SR1 & 24SR2 Bus Failure
East Bend Steam-2 | D4 | 2023-04-16 | 2023-04-20 03:39 | 99.65 | 18933.5 |  | 8260 | Scrubber booster I.D. fan (fan specific to the scrubber) | 2-1 IDBF Sole Plate Repairs
East Bend Steam-2 | D1 | 2023-05-08 12:00 | 2023-05-15 04:21 | 160.35 | 29664.75 |  | 1480 | Other induced draft fan problems | Vibration on motor IB bearing, cause found to be coupling issue
East Bend Steam-2 | D1 | 2023-05-29 22:50 | 2023-06-07 06:05 | 199.25 | 5578.53 |  | 4301 | Turbine governing system | Govenor valve number 8
East Bend Steam-2 | D1 | 2023-06-02 06:56 | 2023-06-02 07:00 | 0.067 | 1.56 |  | 95 | Bunker flow problems | 2-3 pulv coal flow issues
East Bend Steam-2 | D4 | 2023-06-08 04:00 | 2023-06-10 03:50 | 47.833 | 14924 |  | 260 | Primary air fan | Motor Replacement
East Bend Steam-2 | D1 | 2023-06-19 18:01 | 2023-06-19 19:00 | 0.983 | 53.81 |  | 95 | Bunker flow problems | 2-3 pulv coal flow issues
East Bend Steam-2 | D1 | 2023-07-28 19:30 | 2023-07-28 23:20 | 3.833 | 76.67 | OMC | 9270 | Wet coal (OMC) | 2-6 Pulverizer Plugged
East Bend Steam-2 | D1 | 2023-07-31 16:35 | 2023-07-31 20:47 | 4.2 | 756 |  | 280 | Pulverizer fires | 2-2 Burner Line Fire
East Bend Steam-2 | D1 | 2023-08-23 07:57 | 2023-08-23 08:00 | 0.05 | 1.06 |  | 250 | Pulverizer feeders | 2-5 Pulverizer Coal Plugged
East Bend Steam-2 | D1 | 2023-08-25 17:19 | 2023-08-26 07:28 | 14.15 | 367.48 |  | 1400 | Forced draft fans | FD Fan MAXED
East Bend Steam-2 | D1 | 2023-09-05 17:30 | 2023-09-06 21:37 | 28.117 | 281.17 |  | 4301 | Turbine governing system | Turbine Governor Valve Control
East Bend Steam-2 | D1 | 2023-11-16 22:28 | 2023-11-16 23:00 | 0.533 | 86.63 |  | 250 | Pulverizer feeders | Loss of coal on 2-6 pulverizer
East Bend Steam-2 | D1 | 2023-11-17 10:31 | 2023-11-17 11:00 | 0.483 | 70.7 |  | 250 | Pulverizer feeders | Loss of coal on 2-6 pulverizer
East Bend Steam-2 | D1 | 2023-11-17 20:38 | 2023-11-17 22:00 | 1.367 | 206.82 |  | 250 | Pulverizer feeders | Loss of coal on 2-6 pulverizer
East Bend Steam-2 | D1 | 2023-11-22 12:39 | 2023-11-22 13:00 | 0.35 | 23.04 |  | 250 | Pulverizer feeders | Loss of coal on top mills (2-2 and 2-4)
East Bend Steam-2 | D1 | 2023-11-23 15:03 | 2023-11-23 16:00 | 0.95 | 279.43 |  | 250 | Pulverizer feeders | Loss of coal on 2-6 pulverizer
East Bend Steam-2 | D1 | 2023-12-01 17:11 | 2023-12-02 07:56 | 14.75 | 3017.26 |  | 891 | Bottom ash hoppers (including gates) | Economizer ash hoppers and submerged flight conveyor, too much slag at once
East Bend Steam-2 | D4 | 2023-12-02 07:57 | 2023-12-02 22:37 | 14.667 | 3813.33 |  | 1510 | Flue gas ducts (except recirculation) | A Module Ductwork Repairs
East Bend Steam-2 | D1 | 2023-12-05 00:26 | 2023-12-05 03:00 | 2.567 | 252.48 |  | 250 | Pulverizer feeders | Lost coal on 2-6 pulverizer
East Bend Steam-2 | D4 | 2023-12-09 06:00 | 2023-12-10 00:15 | 18.25 | 4562.5 |  | 1510 | Flue gas ducts (except recirculation) | A Module Ductwork Repairs
East Bend Steam-2 | D1 | 2023-12-15 14:00 | 2023-12-15 18:57 | 4.95 | 123.75 |  | 95 | Bunker flow problems | 2-6 bunker to coal chute clogged
East Bend Steam-2 | D4 | 2023-12-16 05:01 | 2023-12-18 03:00 | 45.983 | 11495.83 |  | 1510 | Flue gas ducts (except recirculation) | C Module Ductwork Repairs
East Bend Steam-2 | D1 | 2023-12-27 10:01 | 2023-12-28 20:50 | 34.817 | 8060.06 |  | 260 | Primary air fan | 2-1 PA Fan Outboard Bearing Wiped
East Bend Steam-2 | D1 | 2024-01-13 05:37 | 2024-01-13 06:00 | 0.383 | 45.98 | OMC | 9270 | Wet coal (OMC) | 2-6 mill, wet coal causing feeder plugging
East Bend Steam-2 | D1 | 2024-01-14 18:01 | 2024-01-14 21:00 | 2.983 | 581.33 | OMC | 9270 | Wet coal (OMC) | 2-5 mill, wet coal causing feeder and burner line plugging
East Bend Steam-2 | D1 | 2024-01-15 05:09 | 2024-01-15 07:00 | 1.85 | 97.75 |  | 360 | Burners | 23R burner line fire
East Bend Steam-2 | D1 | 2024-01-16 08:28 | 2024-01-16 09:00 | 0.533 | 53.91 | OMC | 9270 | Wet coal (OMC) | 2-2 mill, wet coal causing feeder plugging
East Bend Steam-2 | D1 | 2024-01-16 09:40 | 2024-01-16 14:00 | 4.333 | 801.67 | OMC | 9270 | Wet coal (OMC) | 2-2 mill, wet coal causing belt tracking
East Bend Steam-2 | D1 | 2024-01-16 14:01 | 2024-01-16 16:00 | 1.983 | 617.51 | OMC | 9270 | Wet coal (OMC) | 2-2 mill, wet coal causing belt tracking
East Bend Steam-2 | D1 | 2024-01-16 16:01 | 2024-01-16 17:45 | 1.733 | 320.67 | OMC | 9270 | Wet coal (OMC) | 2-2 mill, wet coal causing belt tracking
East Bend Steam-2 | D1 | 2024-01-16 19:41 | 2024-01-17 01:37 | 5.933 | 433.9 | OMC | 9270 | Wet coal (OMC) | 2-6 mill, wet coal causing feeder and chute plugging
East Bend Steam-2 | D1 | 2024-01-17 10:28 | 2024-01-17 14:00 | 3.533 | 493.82 | OMC | 9270 | Wet coal (OMC) | 2-3 and 2-6 mill, wet coal causing feeder build up and belt tracking
East Bend Steam-2 | D1 | 2024-01-17 20:19 | 2024-01-18 | 3.683 | 556.22 | OMC | 9270 | Wet coal (OMC) | 2-6 mill, wet coal causing feeder plugging
East Bend Steam-2 | D1 | 2024-01-19 00:12 | 2024-01-19 01:00 | 0.8 | 115.82 | OMC | 9270 | Wet coal (OMC) | 2-3 mill, wet coal causing chute plugging
East Bend Steam-2 | D1 | 2024-01-20 15:05 | 2024-01-20 18:00 | 2.917 | 373.57 |  | 3295 | Other waste water (zero discharge) problems | FGD Chemistry
East Bend Steam-2 | U1 | 2024-01-31 05:32 | 2024-01-31 09:16 | 3.733 | 2240 | OMC | 9270 | Wet coal (OMC) | 2-1 mill, wet coal causing feeder plugging and drum level to trip
East Bend Steam-2 | D1 | 2024-02-01 05:01 | 2024-02-05 23:40 | 114.65 | 27302.75 | OMC | 9270 | Wet coal (OMC) | Start-up ran long due to wet coal causing mill runbacks and could not stabilize Unit
East Bend Steam-2 | D1 | 2024-02-09 06:43 | 2024-02-09 07:00 | 0.283 | 26.38 | OMC | 9270 | Wet coal (OMC) | 2-4 Pulverizer feeder tripped from wet coal
East Bend Steam-2 | D1 | 2024-02-11 23:56 | 2024-02-12 01:00 | 1.067 | 280.23 | OMC | 9270 | Wet coal (OMC) | 2-1 pulverizer mill tripped twice on wet coal
East Bend Steam-2 | D1 | 2024-02-13 00:01 | 2024-02-13 01:00 | 0.983 | 297.23 |  | 270 | Primary air duct and dampers | 2-1 PA Fan tripped out, causing runback on 2-1 mill.
East Bend Steam-2 | D1 | 2024-02-13 01:00 | 2024-02-15 00:02 | 47.033 | 10347.33 |  | 270 | Primary air duct and dampers | 2-1 PA Fan IB VIVs found broken, made repairs
East Bend Steam-2 | D1 | 2024-02-20 17:54 | 2024-02-20 18:00 | 0.1 | 3.58 |  | 250 | Pulverizer feeders | 2-1 Pulverizer plugged
East Bend Steam-2 | D4 | 2024-02-27 11:00 | 2024-02-27 22:00 | 11 | 2530 |  | 270 | Primary air duct and dampers | 2-2 PA Fan VIVs inspected to verify condition, all looked good
East Bend Steam-2 | D1 | 2024-03-08 22:58 | 2024-03-08 23:00 | 0.033 | 0.36 |  | 1999 | Boiler, miscellaneous | SH temps high due to spray valve regulator stuck at 13%
East Bend Steam-2 | D1 | 2024-03-19 04:01 | 2024-03-19 06:24 | 2.383 | 429 |  | 8710 | SO2 analyzer problems | Troubleshooting transmitter issues on SO2
East Bend Steam-2 | D1 | 2024-03-19 06:25 | 2024-03-19 17:25 | 11 | 2200 |  | 8710 | SO2 analyzer problems | Working through transmitter issues and repairs
East Bend Steam-2 | D1 | 2024-04-02 22:45 | 2024-04-03 03:10 | 4.417 | 44.17 |  | 4301 | Turbine governing system | Turbine Valves opened at 100% and back pressure spiked
East Bend Steam-2 | D4 | 2024-04-03 11:00 | 2024-04-03 18:35 | 7.583 | 2275 |  | 590 | Desuperheater/attemperator valves | PSH Valve Repumping
East Bend Steam-2 | D1 | 2024-04-10 01:15 | 2024-04-10 01:45 | 0.5 | 2.5 |  | 4301 | Turbine governing system | Governor valves maxed out
East Bend Steam-2 | D1 | 2024-04-12 16:01 | 2024-04-12 17:00 | 0.983 | 204.1 |  | 400 | Burner wind box fires | 2-6 14R Burner Line
East Bend Steam-2 | D4 | 2024-05-07 20:21 | 2024-05-09 | 27.65 | 9636.3 |  | 4300 | Turbine supervisory system (use codes 4290 to 4299 for hydraulic oil) | Tuning
East Bend Steam-2 | D1 | 2024-05-09 17:01 | 2024-05-09 19:00 | 1.983 | 460.65 |  | 340 | Other pulverizer problems | Received alarm for not normal fuel block, took 2-4 mill out of service to investigate
East Bend Steam-2 | D4 | 2024-05-23 18:21 | 2024-05-27 20:00 | 97.65 | 23289.53 |  | 4300 | Turbine supervisory system (use codes 4290 to 4299 for hydraulic oil) | Tuning
East Bend Steam-2 | D1 | 2024-06-03 23:50 | 2024-06-04 04:00 | 4.167 | 41.67 |  | 8265 | Scrubber booster I.D. fan dampers | ID Booster Fan VIVs sticking
East Bend Steam-2 | D1 | 2024-06-14 18:01 | 2024-06-14 20:00 | 1.983 | 16.38 |  | 8265 | Scrubber booster I.D. fan dampers | ID Booster Fan VIVs sticking
East Bend Steam-2 | D1 | 2024-06-17 18:38 | 2024-06-17 21:00 | 2.367 | 207.56 |  | 400 | Burner wind box fires | 2-2 8R burner line, had to switch pulverizers
East Bend Steam-2 | D4 | 2024-06-27 10:00 | 2024-06-27 21:00 | 11 | 2860 |  | 8261 | Scrubber booster I.D. fan drive | Repaired beck drive, which caused for VIVs sticking
East Bend Steam-2 | D1 | 2024-08-29 00:05 | 2024-08-29 19:00 | 18.917 | 4161.67 |  | 8506 | Slurry pipelines | Slurry line plugged, dropped load until issue was resolved so as to not impact PH and