## Planning Parameters
2026-2027 RPM Base Residual Auction Planning Parameters |  |  | 2024-08-26
| RTO | Notes:
Installed Reserve Margin (IRM) | 18.6% | endorsed at the July 24, 2024 MRC meeting https://www.pjm.com/-/media/committees-groups/committees/mrc/2024/20240724/20240724-item-05---irm-fpr-and-elcc-for-26-27-bra---presentation.ashx
Pool-Wide Accredited UCAP Factor | 78.98% | endorsed at the July 24, 2024 MRC meeting.
Forecast Pool Requirement (FPR) | 0.9367 | endorsed at the July 24, 2024 MRC meeting.
Preliminary Forecast Peak Load | 157196.9787 | 2024 Load Report with adjustments for load served outside PJM.
Locational Deliverability Area
| RTO | MAAC | EMAAC | SWMAAC | PS | PS NORTH | DPL SOUTH | PEPCO | ATSI | ATSI-Cleveland | COMED | BGE | PL | DAYTON | DEOK | DOM | JCPL
CETO | NA | -745 | 5756 | 6882 | 6458 | 2918 | 1646 | 4385 | 3481 | 3328 | -1477 | 4654 | -120 | 2565 | 2826 | 5813 | 3812
CETL | NA | 3023 | 7645 | 7286 | 8839 | 4126 | 1846 | 6096 | 9209 | 4955 | 6012 | 5720 | 4356 | 4568 | 5524 | 6610 | 4098
Reliability Requirement | 147246.4 | 53166.7 | 30999.7 | 13457.6 | 10718 | 5390 | 2645.2 | 6474.8 | 11963.9 | 5066.9 | 21094.9 | 6952.8 | 8663.7 | 3475.4 | 5636.8 | 26664.8 | 6376.8
Total Peak Load of FRR Entities | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Preliminary FRR Obligation | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Reliability Requirement adjusted for FRR | 147246.4 | 53166.7 | 30999.7 | 13457.6 | 10718 | 5390 | 2645.2 | 6474.8 | 11963.9 | 5066.9 | 21094.9 | 6952.8 | 8663.7 | 3475.4 | 5636.8 | 26664.8 | 6376.8
Gross CONE, $/MW-Day (UCAP Price) | 695.83 | 694.35 | 696.17 | 678.26 | 696.17 | 696.17 | 696.17 | 678.26 | 694.77 | 694.77 | 708.51 | 678.26 | 701.44 | 694.77 | 694.77 | 694.77 | 696.17
Net CONE, $/MW-Day (UCAP Price) | 0 | 145.69 | 230.18 | 0 | 297.12 | 297.12 | 117.24 | 0 | 14.72 | 14.72 | 224.26 | 0 | 149.86 | 0 | 0 | 0 | 265.2
EE Addback (UCAP) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Variable Resource Requirement Curve:
Point (a) UCAP Price, $/MW-Day | 695.83 | 694.35 | 696.17 | 678.26 | 696.17 | 696.17 | 696.17 | 678.26 | 694.77 | 694.77 | 708.51 | 678.26 | 701.44 | 694.77 | 694.77 | 694.77 | 696.17
Point (b) UCAP Price, $/MW-Day | 0 | 109.27 | 172.64 | 0 | 222.84 | 222.84 | 87.93 | 0 | 11.04 | 11.04 | 168.2 | 0 | 112.4 | 0 | 0 | 0 | 198.9
Point (c) UCAP Price, $/MW-Day | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Point (a) UCAP Level, MW | 145773.9 | 52635 | 30689.7 | 13323 | 10610.8 | 5336.1 | 2618.7 | 6410.1 | 11844.3 | 5016.2 | 20884 | 6883.3 | 8577.1 | 3440.6 | 5580.4 | 26398.2 | 6313
Point (b) UCAP Level, MW | 149455.1 | 53964.2 | 31464.7 | 13659.5 | 10878.8 | 5470.9 | 2684.9 | 6571.9 | 12143.4 | 5142.9 | 21411.3 | 7057.1 | 8793.7 | 3527.5 | 5721.4 | 27064.8 | 6472.5
Point (c) UCAP Level, MW | 153872.5 | 55559.2 | 32394.7 | 14063.2 | 11200.3 | 5632.6 | 2764.2 | 6766.2 | 12502.3 | 5294.9 | 22044.2 | 7265.7 | 9053.6 | 3631.8 | 5890.5 | 27864.7 | 6663.8
Nominated PRD Value, MW | 165 | 165 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 0
VRR Curve adjusted for PRD:
Point (a1) UCAP Price, $/MW-Day | 695.83 | 694.35 |  | 678.26 | [7 empty] | 678.26
Point (b1) UCAP Price, $/MW-Day |  | 109.27
Point (prd1) UCAP Price, $/MW-Day | 0.01 | 0.01 |  | 0.01 | [7 empty] | 0.01
Point (prd2) UCAP Price, $/MW-Day | 0.01 | 0.01 |  | 0.01 | [7 empty] | 0.01
Point (b) UCAP Price, $/MW-Day | 0 |  |  | 0 | [7 empty] | 0
Point (c) UCAP Price, $/MW-Day | 0 | 0 |  | 0 | [7 empty] | 0
Point (a1) UCAP Level, MW | 145619.3 | 52480.4 |  | 13168.4 | [7 empty] | 6728.7
Point (b1) UCAP Level, MW |  | 53809.6
Point (prd1) UCAP Level, MW | 149300.4 | 55404.5 |  | 13504.9 | [7 empty] | 6902.5
Point (prd2) UCAP Level, MW | 149455 | 55559.1 |  | 13659.5 | [7 empty] | 7057.1
Point (b) UCAP Level, MW | 149455.1 |  |  | 13659.5 | [7 empty] | 7057.1
Point (c) UCAP Level, MW | 153872.5 | 55559.2 |  | 14063.2 | [7 empty] | 7265.7
Pre-Auction Credit Rate, $/MW | 7300 | 26588.43 | 42007.85 | 7300 | 54224.4 | 54224.4 | 21396.3 | 7300 | 7300 | 7300 | 40927.45 | 7300 | 27349.45 | 7300 | 7300 | 7300 | 48399
Participant-Funded ICTRs Awarded*
FRR Load Requirement (% Obligation):
Minimum Internal Resource Requirement | NA | 97.5% | 83.3% | 54.3% | 20.8% | NA | NA | NA | 24.5% | NA | 85.6% | 20.9% | NA | NA | 2.4% | 85.9% | 42.4%
* - Participant Funded ICTRs will be updated on final Planning Parameters posting after the completion of the 26/27 BRA
LDA CETO/CETL Data; Zonal Peak Loads, Base Zonal FRR Scaling Factors, and FRR load.
LDA/Zone | CETO (Capacity Emergency Transfer Objective) | CETL (Capacity Emergency Transfer Limit) | CETL to CETO Ratio % | 2023 Zonal W/N Coincident Peak Loads | Preliminary Zonal Peak Load Forecast | Base Zonal FRR Scaling Factor | FRR Portion of the Preliminary Peak Load Forecast | Preliminary Zonal Peak Load Forecast less FRR load | LDA/Zone
RTO | NA | NA | NA | 148659.4 | 157196.9787 | NA | 0 | 157196.9787 | RTO
AE | 2059 | >2,367.9 | >115% | 2310 | 2357 | 1.0203 | 0 | 2357 | AE
AEP | -1586 | * | * | 21723 | 24038 | 1.1066 | 0 | 24038 | AEP
APS | 1994 | >2,293.1 | >115% | 8452.2 | 9209 | 1.0895 | 0 | 9209 | APS
ATSI | 3481 | 9209 | 264.6% | 11550 | 11998 | 1.0388 | 0 | 11998 | ATSI
ATSI-CLEVELAND | 3328 | 4955 | 148.9% | NA | 4019.33 | NA | 0 | NA | ATSI-CLEVELAND
BGE | 4654 | 5720 | 122.9% | 6200 | 6285 | 1.0137 | 0 | 6285 | BGE
COMED | -1477 | 6012 | * | 18720 | 18807 | 1.0046 | 0 | 18807 | COMED
DAYTON | 2565 | 4568 | 178.1% | 3140 | 3148 | 1.0025 | 0 | 3148 | DAYTON
DEOK | 2826 | 5524 | 195.5% | 5030 | 5094 | 1.0127 | 0 | 5094 | DEOK
DLCO | 1888 | >2,171.2 | >115% | 2620 | 2634 | 1.0053 | 0 | 2634 | DLCO
DOM | 5813 | 6610 | 113.7% | 21200 | 24915 | 1.1752 | 0 | 24915 | DOM
DPL | 1570 | >1,805.5 | >115% | 3660 | 3654 | 0.99836 | 0 | 3654 | DPL
DPL SOUTH | 1646 | 1846 | 112.2% | NA | 2225.286 | NA | 0 | 2225.286 | DPL SOUTH
EKPC | 897 | >1,031.6 | >115% | 1950 | 2385.9787 | 1.2236 | 0 | 2385.9787 | EKPC
JCPL | 3812 | 4098 | 107.5% | 5730 | 5742 | 1.0021 | 0 | 5742 | JCPL
METED | 1518 | >1,745.7 | >115% | 2900 | 3019 | 1.041 | 0 | 3019 | METED
OVEC | NA | NA | NA | 60 | 60 | 1 | 0 | 60 | OVEC
PECO | 2912 | >3,348.8 | >115% | 8030 | 8146 | 1.0144 | 0 | 8146 | PECO
PENLC | 320 | >368.0 | >115% | 2730 | 2755 | 1.0092 | 0 | 2755 | PENLC
PEPCO | 4385 | 6096 | 139% | 5810 | 5851 | 1.0071 | 0 | 5851 | PEPCO
PL (incl. UGI) | -120 | * | * | 7034.2 | 7074 | 1.0057 | 0 | 7074 | PL (incl. UGI)
PS | 6458 | 8839 | 136.9% | 9420 | 9638 | 1.0231 | 0 | 9638 | PS
PS NORTH | 2918 | 4126 | 141.4% | NA | 4905.742 | NA | 0 | 4905.742 | PS NORTH
RECO | NA | NA | NA | 390 | 387 | 0.99231 | 0 | 387 | RECO
EMAAC | 5756 | 7645 | 132.8% | NA | 29924 | NA | 0 |  | EMAAC
SWMAAC | 6882 | 7286 | 105.9% | NA | 12136 | NA | 0 |  | SWMAAC
Western MAAC | -7296 | * | * | NA | 12848 | NA | 0 |  | Western MAAC
MAAC | -745 | 3023 | * | NA | 54908 | NA | 0 |  | MAAC
Western PJM | -1346 | * | * | NA | 77373.9787 | NA | 0 |  | Western PJM
* LDA has adequate internal resources to meet the reliability criterion.
Limiting conditions at the CETL for modeled LDAs:
LDA | Violation |  | Limiting Facility
MAAC | Mean Voltage |  | Voltage collapse and low voltage in Dominion 500 kV transmission systems
EMAAC | Mean Voltage |  | Low voltage at Brister 500 kV and srounding buses for the loss of Mt. Storm - Bismark 500 kV or Bismark - Doubs 500 kV
SWMAAC | Mean Voltage |  | Voltage collapse due to the loss of Brighton - Conastone 500 kV line
PS | Mean Thermal |  | Brunswick - Meadow Road 230 kV ckt Z2331 for the loss of Metuchen -Pierson Ave - Meadow Rd- Deans 230 kV ckt s2219 Roseland - Williams PIPE 230 kV for the loss of Roseland - Cedar Grove 230 kV Peach Bottom - Limerick 500 kV for the loss of Keeney - Rock Springs 500 kV
PSNORTH | Discrete Thermal |  | Roseland - Williams PIPE 230 kV for the loss of Roseland - Cedar Grove 230 kV Stanley Terrance - McCarther 230kV for the loss of WEST ORANGE - ORANGE HEIGHTS 230 kV Kitattiny - Bush 230 kVline for the loss of Portland - Martins Creek 230 kV
DPLSOUTH | Mean Thermal |  | Silver Run - Cedar Creek 230 kV line for the loss of Silver Run - Cartanza 230 kV line
PEPCO | Mean/Discrete Voltage |  | Voltage collapse for the loss of Mt. Storm - Bismark 500 kV or Bismark - Doubs 500 kV circuit
ATSI | Mean Thermal |  | Sporn - Muskingum River 345 kV line for the loss of Muskingum River - Waterford 345 kV line
ATSI-CLEVELAND | Mean/Discrete thermal |  | Conastone - Peach Bottom 500 kV pre-contingency
COMED | Mean Thermal |  | Dumont - Stillwell 345 kV for the loss of Dumont - Wilton 765 kV line Olive - University Park 345 kV for the loss of Dumont - Wilton 765 kV line
BGE | Mean/Discrete Voltage |  | Voltage collapse for the loss of Conastone - Brighton 500 kV
PL | Mean Thermal |  | Wescosville 500/138 kV transformer pre-contingency Loudoun - Morrisville 500 kV line for the loss of Brister - Ox 500 kV line
DAYTON | Mean/Discrete Voltage |  | Low voltage on Overlook 138 kV for the loss of Greene 345/138 KV transformer, or loss of Greene - Knollwood 138 kV or Sugar - Foster 345 kV line
DEOK | Mean Thermal |  | Conastone - Peach Bottom 500 kV pre-contingency
DOM | Discrete Voltage |  | Low voltage on Bismark 500 kV for the loss of Bedington - Black Oak 500 kV
JCPL | Discrete Thermal |  | Smithburg - East Windsor 230 kV for the loss of Deans - Smithburg 500 kV

## Net CONE
RPM CONE and E&AS Values for 2026/2027 Base Residual Auction
ICAP to UCAP Conversion Factor:
UCAP Price = ICAP Price / Pool-Wide Average Accredited UCAP Factor
Reference Resource Accredited UCAP Factor | [6 empty] | 78% | Based on reference resource AUCAPF
CONE Area 1: AE, DPL, JCPL, PECO, PS, RECO
CONE Area 2: BGE, PEPCO
CONE Area 3: AEP, APS, ATSI, Dayton, DEOK, Dominion, Duquesne (DLCo), EKPC, OVEC
CONE Area 4: MetEd, Penelec, PPL
CONE Area 5: ComEd
Zone/LDA | 2026/2027 BRA CONE: Levelized Revenue Requirement, $/MW-Year * | Escalation | 2026/2027 BRA CONE: Levelized Revenue Requirement, $/MW-Year | Gross CONE, $/MW-Day, UCAP Price | Forward Net E&AS Revenue Offset, $/MW-Year | Reactive Services Offset, $/MW-Year per Tariff | Total Net E&AS Revenue Offset, $/MW-Year | Net CONE, $/MW-Day, ICAP Price | Net CONE, $/MW-Day, UCAP Price | LDA Modeled with VRR Curve
CONE Area 1 | 198200 | 1 | 198200 | 696.17
AE |  |  |  | 696.17 | 116325.5 | 2546 | 118871.5 | 217.3384 | 278.64
DPL |  |  |  | 696.17 | 162276.5667 | 2546 | 164822.5667 | 91.445 | 117.24 | DPL SOUTH
JCPL |  |  |  | 696.17 | 120151.9167 | 2546 | 122697.9167 | 206.855 | 265.2 | JCPL
PE |  |  |  | 696.17 | 142766.1 | 2546 | 145312.1 | 144.8984 | 185.77
PSEG |  |  |  | 696.17 | 111063.4167 | 2546 | 113609.4167 | 231.755 | 297.12 | PS, PSEG NORTH
RECO |  |  |  | 696.17 | 128149.0667 | 2546 | 130695.0667 | 184.945 | 237.11
EMAAC |  |  |  | 696.17 |  |  |  | 179.54 | 230.18 | EMAAC
CONE Area 2 | 193100 | 1 | 193100 | 678.26
BGE |  |  |  | 678.26 | 259578.2667 | 2546 | 262124.2667 | 0 | 0 | BGE
PEPCO |  |  |  | 678.26 | 192413.4 | 2546 | 194959.4 | 0 | 0 | PEPCO
SWMAAC |  |  |  | 678.26 |  |  |  | 0 | 0 | SWMAAC
CONE Area 4 | 199700 | 1 | 199700 | 701.44
METED |  |  |  | 701.44 | 176765.85 | 2546 | 179311.85 | 55.8579 | 71.61
PENELEC |  |  |  | 701.44 | 237313.2667 | 2546 | 239859.2667 | 0 | 0
PPL |  |  |  | 701.44 | 154487.4667 | 2546 | 157033.4667 | 116.8946 | 149.86 | PPL
MAAC |  |  |  | 694.35 |  |  |  | 113.64 | 145.69 | MAAC
CONE Area 3 | 197800 | 1 | 197800 | 694.77
AEP |  |  |  | 694.77 | 212735.3833 | 2546 | 215281.3833 | 0 | 0
APS |  |  |  | 694.77 | 250057.85 | 2546 | 252603.85 | 0 | 0
ATSI |  |  |  | 694.77 | 191062.9 | 2546 | 193608.9 | 11.4825 | 14.72 | ATSI, ATSI CLEVELAND
DAYTON |  |  |  | 694.77 | 209777.6667 | 2546 | 212323.6667 | 0 | 0 | DAYTON
DEOK |  |  |  | 694.77 | 199262.0167 | 2546 | 201808.0167 | 0 | 0 | DEOK
DLCO |  |  |  | 694.77 | 179620.15 | 2546 | 182166.15 | 42.8325 | 54.91
DOM |  |  |  | 694.77 | 233182.6833 | 2546 | 235728.6833 | 0 | 0 | DOM
EKPC |  |  |  | 694.77 | 191229.5833 | 2546 | 193775.5833 | 11.0258 | 14.14
OVEC |  |  |  | 694.77 | 200719.5833 | 2546 | 203265.5833 | 0 | 0
CONE Area 5 | 201714 | NA | 201714 | 708.51
COMED |  |  |  | 708.51 | 135322.5333 | 2546 | 137868.5333 | 174.9191 | 224.26 | COMED
RTO | 198102.8 |  | 198102.8 | 695.83 | 196315.25 | 2546 | 198861.25 | 0 | 0 | RTO
CONE Area 5 based on asset life factor of CONE Area 3. 25/26: 1.0069; 27/28: 1.0376; 28/29: 1.0581; 29/30: 1.0818
* The 2026/2027 BRA CONE values are based on PJM’s Quadrennial Review filing (Docket No. ER22-2984) which was FERC approved on February 14, 2023.

## Key Transmission Upgrades
New Key Transmission Upgrades included for 2026/2027 model
Upgrade ID | Description | Transmission Owner
b3718.3 | Construct a new 500 kV transmission line for ~ 3.5 miles along with substation upgrades at Wishing Star and Mars. New right-of-way will be needed and will share same structures with the line. New conductor to have a minimum summer normal rating of 4357 MVA. | Dominion
b3718.1 | Install one 500/230kV 1440MVA transformer at a new substation called Wishing Star. Cut and extend 500 kV Line #546 (Brambleton-Mosby) and 500 kV Line #590 (Brambleton-Mosby) to the proposed Wishing Star substation. Lines to terminate in a 500 kV breaker and a half configuration. | Dominion
s2738 | *Obtain land and build a new 500/230kV Finneywood switching station at the intersection of 500kV Line #556 (Clover-Rawlings) and 230kV Line #235 (Cloud – Farmville). | Dominion
* Cut and terminate 500kV Line #556 into Finneywood 500/230kV switching station. Cut and terminate 230kV Line #235 into Finneywood 500/230kV switching station. In the new Finneywood switching station, install two 840 MVA 500/230kV transformers, a 230kV breaker and half bus with 12 breakers and a 500kV ring bus with 6 breakers.
* Construct Butler Farm 230kV substation with four 230kV breaker ring bus to terminate two 230kV lines. Construct one new 230kV transmission line for approximately 20 miles from Clover Sub to Butler Farm Substation. Construct one new 230kV transmission line for approximately 10 miles from Finneywood Sub to Butler Farm Substation.
* New right-of-way will be needed for both transmission lines. New conductor to have a minimum summer normal rating of 1573 MVA.
b3211 | Rebuild the 1.3 mile section of 500 kV Line No.569 (Loudoun - Morrisville) with single-circuit 500 kV structures at the current 500 kV standard. This will increase the rating of the line to 3424 MVA. | Dominion
b2443.6 | Install a second 500/230 kV transformer at Possum Point substation and replace bus work and associated equipment as needed. | Dominion
b3020 | Rebuild 500kV Line #574 Ladysmith to Elmont - 26.2 miles long | Dominion
b3326.0 | Rebuild the 13707 Vienna-Nelson 138 kV line | DPL
Key Transmission Upgrades included for 2025/2026 model but not included for 2026/2027 model
Upgrade ID | Description | Transmission Owner
None