## Only SF
Unit | Primary Fuel Type | Event Start | Event End | Event Type | Event Duration Hours | Equiv MWh Lost | Derate | Cause Code | Cause Description | Event Description
Woodsdale CT-3 | Natural Gas | 2019-01-30 16:55 | 2019-01-30 20:50 | SF | 3.917 | 368.17 | 93.9929 | 5130 | Starting system (including motor) | Starting device failure
Woodsdale CT-1 | Natural Gas | 2019-01-30 17:02 | 2019-02-02 20:58 | SF | 75.933 | 7137.73 | 94.0004 | 5130 | Starting system (including motor) | starting breaker failed to open
Woodsdale CT-3 | Natural Gas | 2019-03-27 10:45 | 2019-03-27 12:15 | SF | 1.5 | 141 | 94 | 3621 | Unit auxiliaries transformer | RAT Transformer 13 Tripped while starting
Woodsdale CT-4 | Natural Gas | 2019-03-27 10:45 | 2019-03-27 12:15 | SF | 1.5 | 141 | 94 | 3621 | Unit auxiliaries transformer | RAT Transformer 13 Tripped while starting
Woodsdale CT-6 | Natural Gas | 2019-06-19 12:27 | 2019-06-19 17:24 | SF | 4.95 | 465.3 | 94 | 5050 | Ignition system | FLAME OUT
Woodsdale CT-5 | Natural Gas | 2019-06-26 19:20 | 2019-06-26 20:12 | SF | 0.867 | 81.47 | 93.9677 | 5041 | Fuel piping and valves | Air supply to 2nd stage reg off
Woodsdale CT-6 | Natural Gas | 2019-06-26 19:35 | 2019-06-26 20:01 | SF | 0.433 | 40.73 | 94.0647 | 5041 | Fuel piping and valves | MAIN GAS SHUT OFF VALVE BREAKER TRIPPED
Woodsdale CT-1 | Natural Gas | 2019-07-13 21:02 | 2019-07-13 21:22 | SF | 0.333 | 31.33 | 94.0841 | 5050 | Ignition system | Trip on flame out
Woodsdale CT-6 | Natural Gas | 2019-07-29 13:55 | 2019-07-29 14:38 | SF | 0.717 | 67.37 | 93.9609 | 5150 | Turning gear and motor | Jacking Oil Pump Failure
Woodsdale CT-1 | Natural Gas | 2019-09-09 19:20 | 2019-09-09 20:16 | SF | 0.933 | 87.73 | 94.03 | 5041 | Fuel piping and valves | Gas valve went closed
Woodsdale CT-5 | Natural Gas | 2019-10-19 12:00 | 2019-10-19 13:00 | SF | 1 | 94 | 94 | 5130 | Starting system (including motor) | Remote start-breaker did not close.
Woodsdale CT-5 | Natural Gas | 2019-11-13 13:44 | 2019-11-15 22:42 | SF | 56.967 | 5354.87 | 93.9995 | 4810 | Generator output breaker | SF6 Gas in Gen Breaker low
Woodsdale CT-6 | Natural Gas | 2019-12-12 11:33 | 2019-12-12 13:32 | SF | 1.983 | 186.43 | 94.0141 | 9130 | Lack of fuel: Physical failures of fuel supply or delivery/transportation of fuel | Main gas reg. not working
Woodsdale CT-3 | Natural Gas | 2019-12-12 11:38 | 2019-12-12 13:32 | SF | 1.9 | 178.6 | 94 | 9130 | Lack of fuel: Physical failures of fuel supply or delivery/transportation of fuel | Shut down 0648, gas reg not working
Woodsdale CT-2 | Natural Gas | 2019-12-12 11:40 | 2019-12-12 13:32 | SF | 1.867 | 175.47 | 93.985 | 9130 | Lack of fuel: Physical failures of fuel supply or delivery/transportation of fuel | Main NG regulator failed
Woodsdale CT-6 | Natural Gas | 2019-12-20 12:44 | 2019-12-20 13:44 | SF | 1 | 94 | 94 | 5150 | Turning gear and motor | High level in fuel/water pump
Woodsdale CT-3 | Natural Gas | 2020-07-03 21:12 | 2020-07-03 23:16 | SF | 2.067 | 194.27 | 93.9865 | 4700 | Generator voltage control | Remote start. AVR fault unit did not start.
Woodsdale CT-4 | Natural Gas | 2020-08-14 17:34 | 2020-08-14 19:20 | SF | 1.767 | 166.07 | 93.9842 | 4720 | Generator synchronization equipment | Sync control issue
Woodsdale CT-3 | Natural Gas | 2020-12-07 21:09 | 2020-12-07 21:41 | SF | 0.533 | 50.13 | 94.0525 | 5130 | Starting system (including motor) | Undervoltage Relay for Starting Breaker failed.
Woodsdale CT-3 | Natural Gas | 2020-12-08 10:30 | 2020-12-08 10:59 | SF | 0.483 | 45.43 | 94.058 | 5130 | Starting system (including motor) | Undervoltage Relay for Starting Breaker failed. (Remote Start)
Woodsdale CT-2 | Natural Gas | 2021-02-16 13:20 | 2021-02-16 13:44 | SF | 0.4 | 37.6 | 94 | 5130 | Starting system (including motor) | Unit tripped due to starting bkr. Reset/installed & reracked starting bkr.
Woodsdale CT-4 | Natural Gas | 2021-02-17 10:52 | 2021-02-17 11:22 | SF | 0.5 | 47 | 94 | 5050 | Ignition system | Flame out 2200RPM
Woodsdale CT-4 | Natural Gas | 2021-03-22 08:39 | 2021-03-22 17:15 | SF | 8.6 | 808.4 | 94 | 5049 | Other fuel system problems | Remote start, trip on burner cooling air
Woodsdale CT-2 | Natural Gas | 2021-04-09 00:04 | 2021-04-22 17:35 | SF | 329.517 | 30974.57 | 93.9999 | 5130 | Starting system (including motor) | Switch over device for SFC failed-Arc-over when switchover device went to GT1
Woodsdale CT-1 | Natural Gas | 2021-04-09 00:07 | 2021-04-13 22:19 | SF | 118.2 | 11110.8 | 94 | 5130 | Starting system (including motor) | GT2 SFC Switch over device failed; GT1 out to repair switchover device
Woodsdale CT-2 | Natural Gas | 2021-06-04 19:56 | 2021-06-04 20:40 | SF | 0.733 | 68.93 | 94.0382 | 5130 | Starting system (including motor) | Syncronizer Failure
Woodsdale CT-5 | Natural Gas | 2021-06-27 20:47 | 2021-06-27 21:44 | SF | 0.95 | 89.3 | 94 | 4810 | Generator output breaker | Gen Breaker SF6 Gas Low
Woodsdale CT-2 | Natural Gas | 2021-08-17 17:50 | 2021-08-18 15:18 | SF | 21.467 | 2017.87 | 93.9987 | 5120 | Hydraulic oil system | Power Oil Breaker won`t close
Woodsdale CT-6 | Natural Gas | 2021-10-18 23:04 | 2021-10-19 14:09 | SF | 15.083 | 1417.83 | 94.0019 | 4720 | Generator synchronization equipment | Failed start; Synchronizer blocked
Woodsdale CT-6 | Natural Gas | 2021-11-05 09:55 | 2021-11-05 13:50 | SF | 3.917 | 368.17 | 93.9929 | 4720 | Generator synchronization equipment | Synchronizer problem
Woodsdale CT-2 | Natural Gas | 2022-01-07 12:45 | 2022-01-07 14:15 | SF | 1.5 | 141 | 94 | 5130 | Starting system (including motor) | Starting Breaker would not close.
Woodsdale CT-4 | Natural Gas | 2022-01-23 08:30 | 2022-01-23 10:11 | SF | 1.683 | 158.23 | 94.0166 | 4720 | Generator synchronization equipment | Gen Exciter Synchronizer blocked.
Woodsdale CT-2 | Natural Gas | 2022-05-13 19:22 | 2022-05-13 22:02 | SF | 2.667 | 250.67 | 93.9895 | 5130 | Starting system (including motor) | Starting Breaker Failure.
Woodsdale CT-5 | Natural Gas | 2022-06-15 15:44 | 2022-06-16 14:29 | SF | 22.75 | 2138.5 | 94 | 5001 | Inlet air vanes/nozzles | TRIP during start up; Variable Inlet Guide Vanes Problem.
Woodsdale CT-5 | Natural Gas | 2022-10-13 23:06 | 2022-10-14 00:23 | SF | 1.283 | 120.63 | 94.0218 | 5250 | Other controls and instrumentation problems | Flame out due to bad Thermocouple.
Woodsdale CT-6 | Natural Gas | 2023-01-10 12:04 | 2023-01-10 12:30 | SF | 0.433 | 40.73 | 94.0647 | 5050 | Ignition system | Start up trip during ignition
Woodsdale CT-6 | Natural Gas | 2023-05-07 10:16 | 2023-05-07 11:00 | SF | 0.733 | 68.93 | 94.0382 | 5050 | Ignition system | Start Fail; tripped on flame, RS at 0700, Load Desk didn't want to restart.
Woodsdale CT-3 | Natural Gas | 2023-07-26 19:02 | 2023-07-26 21:37 | SF | 2.583 | 242.83 | 94.0108 | 5050 | Ignition system | Would not light off; propane ignition pressure too high
Woodsdale CT-2 | Natural Gas | 2023-10-10 17:10 | 2023-10-10 20:28 | SF | 3.3 | 310.2 | 94 | 4750 | Other generator controls and metering problems | Start up fail; AVR Fault
Woodsdale CT-6 | Natural Gas | 2023-12-04 11:10 | 2023-12-07 15:23 | SF | 76.217 | 7164.37 | 93.9996 | 4720 | Generator synchronization equipment | Unit Sync. Not giving Close command to BKR
Woodsdale CT-6 | Natural Gas | 2023-12-12 10:58 | 2023-12-12 13:48 | SF | 2.833 | 266.33 | 94.0099 | 4720 | Generator synchronization equipment | Unit back Available After Sync work, 12/12/23 8:48
Woodsdale CT-4 | Natural Gas | 2024-01-08 11:58 | 2024-01-08 15:01 | SF | 3.05 | 286.7 | 94 | 3661 | 4000-7000 volt circuit breakers | Unit back available after FO breaker calibration
Woodsdale CT-1 | Natural Gas | 2024-01-08 12:01 | 2024-01-08 15:01 | SF | 3 | 282 | 94 | 3661 | 4000-7000 volt circuit breakers | Unit back available after FO breaker calibration
Woodsdale CT-3 | Natural Gas | 2024-01-08 12:01 | 2024-01-08 15:01 | SF | 3 | 282 | 94 | 3661 | 4000-7000 volt circuit breakers | Unit back available after FO breaker calibration
Woodsdale CT-4 | Natural Gas | 2024-01-15 11:45 | 2024-01-15 20:17 | SF | 8.533 | 802.13 | 94.0033 | 3661 | 4000-7000 volt circuit breakers | Unit back available after ignition system trouble
Woodsdale CT-3 | Natural Gas | 2024-01-15 11:50 | 2024-01-15 13:04 | SF | 1.233 | 115.93 | 94.0227 | 5050 | Ignition system | Unit back available after ignition system trouble
Woodsdale CT-4 | Natural Gas | 2024-01-30 11:58 | 2024-01-30 20:45 | SF | 8.783 | 825.63 | 94.0032 | 5042 | Fuel nozzles/vanes | Replaced bad card on FO control valve.
Woodsdale CT-5 | Natural Gas | 2024-04-23 08:25 | 2024-04-23 12:43 | SF | 4.3 | 404.2 | 94 | 4810 | Generator output breaker | Unit would not sync due to low SF6 gas pressure, raised gas pressure, test ran, return
Woodsdale CT-2 | Natural Gas | 2024-05-19 17:15 | 2024-05-19 23:04 | SF | 5.817 | 546.77 | 93.9952 | 5130 | Starting system (including motor) | SFC fail to start
Woodsdale CT-5 | Natural Gas | 2024-11-05 10:39 | 2024-11-05 18:10 | SF | 7.517 | 706.57 | 93.9963 | 4720 | Generator synchronization equipment | Generator breaker air pressure contact stuck open, reset.