## Branch Flow
BRANCH | [6 empty] | CONTINGENCY | CONTINGENCY | MVAFLOW | AMPFLOW | RATE RATE1/RATE2 | % FLOW | OWNER | ANALYSIS
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BASE CASE | BASE CASE | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE |  | BASE VOLTS is pu base case voltage.
342000 | 5GAS | 161 | 342703 | 5CASEY CO | 161 | 1 | SINGLE OPN LIN 409 342000-342760(1) | OPEN LINE FROM BUS 342000 [5GAS 161.00] TO BUS 342760 [5LIBERTY J 161.00] CKT 1 | 214.157 | 214.157 | 153 | 139.9719 | EKPC |  | CONT VOLTS is pu contingency case voltage.
DEVIATION is difference between contingency case and base case voltage.
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1 339206-342769(1) | OPEN LINE FROM BUS 339206 [AE1-143 C 161.00] TO BUS 342769 [5MARION CO 161.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE |  | RANGE VIO is range violations calculated as bus voltage - minimum range limit or bus voltage - maximum range limit.
DEV VIO is deviation violations calculated as DEVIATION - minimum deviation limit or DEVIATION - maximum deviation limit.
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2 339206-939132(1) | OPEN LINE FROM BUS 339206 [AE1-143 C 161.00] TO BUS 939132 [AE1-143 E 161.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3983 | LGEE |  | Report Options Used:
Solution type = contingency
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 3 341002-341443(1) | OPEN LINE FROM BUS 341002 [2AIRPORT RD 69.000] TO BUS 341443 [2ELLIO CO PT69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE |  | Rating to use to calculate Base Case percentage overload = RATE1
Rating to use to calculate Contingency Case percentage overload = RATE2
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 4 341002-341752(1) | OPEN LINE FROM BUS 341002 [2AIRPORT RD 69.000] TO BUS 341752 [2LEON 69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.398 | LGEE |  | Exclude elements with base case loading violations from contingency reports = False
Exclude buses with base case voltage range violations from contingency reports = False
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 5 341005-342181(1) | OPEN LINE FROM BUS 341005 [2ALBANY 69.000] TO BUS 342181 [2S ALBANY 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE |  | Exclude elements with base case SWD loading violations from contingency reports = False
Exclude buses with base case node voltage range violations from contingency reports = False
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 6 341005-342283(1) | OPEN LINE FROM BUS 341005 [2ALBANY 69.000] TO BUS 342283 [2SNOW T 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE |  | Percent of flow rating = 95
Minimum contingency case flow change = 0.0 MVA, filter criteria ignored
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 7 341005-342397(1) | OPEN LINE FROM BUS 341005 [2ALBANY 69.000] TO BUS 342397 [2UPCHURCH T 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE |  | Minimum contingency case voltage change = 0.0 pu, filter criteria ignored
Exclude islanded buses from contingency reports = True
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 8 341008-342106(1) | OPEN LINE FROM BUS 341008 [2ALCAN 69.000] TO BUS 342106 [2PPG J 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE |  | Bus mismatch tolerance = 0.5 MVA
System mismatch tolerance = 5 MVA
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 9 341008-342430(1) | OPEN LINE FROM BUS 341008 [2ALCAN 69.000] TO BUS 342430 [2W BEREA 69.000] CKT 1 | -31.4812 | 31.4812 | 33 | 95.3976 | LGEE
Note: RATE column label is Base Case Rating/Contingency case rating.
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 10 341014-341017(1) | OPEN LINE FROM BUS 341014 [2ANNVILLE 69.000] TO BUS 341017 [2ANNVILLE T 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 11 341017-341428(1) | OPEN LINE FROM BUS 341017 [2ANNVILLE T 69.000] TO BUS 341428 [2EBERLE T 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 12 341017-342391(1) | OPEN LINE FROM BUS 341017 [2ANNVILLE T 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 13 341020-341782(1) | OPEN LINE FROM BUS 341020 [2ARGENTUM 69.000] TO BUS 341782 [2LOW GAP T 69.000] CKT 1 | -31.483 | 31.483 | 33 | 95.403 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 14 341020-342538(1) | OPEN LINE FROM BUS 341020 [2ARGENTUM 69.000] TO BUS 342538 [4ARGENTUM 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 15 341029-341032(1) | OPEN LINE FROM BUS 341029 [2ASAHI M W 69.000] TO BUS 341032 [2ASAHI M W T69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 16 341032-341379(1) | OPEN LINE FROM BUS 341032 [2ASAHI M W T69.000] TO BUS 341379 [2DAHL ROAD 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 17 341032-342472(1) | OPEN LINE FROM BUS 341032 [2ASAHI M W T69.000] TO BUS 342472 [2WALNUT GROV69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 18 341035-341038(1) | OPEN LINE FROM BUS 341035 [2BACON CRK 69.000] TO BUS 341038 [2BACON CRK T69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 19 341038-341755(1) | OPEN LINE FROM BUS 341038 [2BACON CRK T69.000] TO BUS 341755 [2LIBER CH T 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 20 341038-342187(1) | OPEN LINE FROM BUS 341038 [2BACON CRK T69.000] TO BUS 342187 [2S CORBIN 69.000] CKT 1 | -31.4812 | 31.4812 | 33 | 95.3976 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 21 341041-341635(1) | OPEN LINE FROM BUS 341041 [2BAKER LN 69.000] TO BUS 341635 [2HOLLOWAY 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 22 341041-341638(1) | OPEN LINE FROM BUS 341041 [2BAKER LN 69.000] TO BUS 341638 [2HOLLOWAY J 69.000] CKT 1 | -31.4811 | 31.4811 | 33 | 95.3972 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 23 341041-342547(1) | OPEN LINE FROM BUS 341041 [2BAKER LN 69.000] TO BUS 342547 [4BAKER LN 138.00] CKT 1 | -31.4806 | 31.4806 | 33 | 95.3959 | LGEE
342000 | 5GAS | 161 | 342760 | 5LIBERTY J | 161 | 1 | SINGLE OPN LIN 408 342000-342703(1) | OPEN LINE FROM BUS 342000 [5GAS 161.00] TO BUS 342703 [5CASEY CO 161.00] CKT 1 | 212.8308 | 212.8308 | 153 | 139.1051 | EKPC
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 24 341044-341671(1) | OPEN LINE FROM BUS 341044 [2BALLARD 69.000] TO BUS 341671 [2HUNT FARM J69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 25 341044-342361(1) | OPEN LINE FROM BUS 341044 [2BALLARD 69.000] TO BUS 342361 [2TODDVILLE T69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 26 341047-342424(1) | OPEN LINE FROM BUS 341047 [2BALLTOWN 69.000] TO BUS 342424 [2W BARDST J 69.000] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 27 341050-342295(1) | OPEN LINE FROM BUS 341050 [2BANK LCK 69.000] TO BUS 342295 [2STANLY P J169.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 28 341053-341056(1) | OPEN LINE FROM BUS 341053 [2BARD SHOP 69.000] TO BUS 341056 [2BARD SHOP T69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 29 341056-341407(1) | OPEN LINE FROM BUS 341056 [2BARD SHOP T69.000] TO BUS 341407 [2E BARDSTOWN69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 30 341056-342424(1) | OPEN LINE FROM BUS 341056 [2BARD SHOP T69.000] TO BUS 342424 [2W BARDST J 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 31 341059-341275(1) | OPEN LINE FROM BUS 341059 [2BARREN CO 69.000] TO BUS 341275 [2CAVE CITY J69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 32 341059-341542(1) | OPEN LINE FROM BUS 341059 [2BARREN CO 69.000] TO BUS 341542 [2GOODNIGHT 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 33 341059-341651(1) | OPEN LINE FROM BUS 341059 [2BARREN CO 69.000] TO BUS 341651 [2HORSECAVE J69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.398 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 34 341059-342694(1) | OPEN LINE FROM BUS 341059 [2BARREN CO 69.000] TO BUS 342694 [5BARREN CO 161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 35 341062-341269(1) | OPEN LINE FROM BUS 341062 [2BASS 69.000] TO BUS 341269 [2CASEY CO 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 36 341065-341068(1) | OPEN LINE FROM BUS 341065 [2BEAM 69.000] TO BUS 341068 [2BEAM T 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 37 341068-341215(1) | OPEN LINE FROM BUS 341068 [2BEAM T 69.000] TO BUS 341215 [2BULLITT CO 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 38 341068-342253(1) | OPEN LINE FROM BUS 341068 [2BEAM T 69.000] TO BUS 342253 [2SHEPHEVIL J69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 39 341071-341074(1) | OPEN LINE FROM BUS 341071 [2BEATTYV 69.000] TO BUS 341074 [2BEATTYV D 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 40 341071-341077(1) | OPEN LINE FROM BUS 341071 [2BEATTYV 69.000] TO BUS 341077 [2BEATTYV J 69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3978 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 41 341071-342520(1) | OPEN LINE FROM BUS 341071 [2BEATTYV 69.000] TO BUS 342520 [2ZACHARIAH 69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3979 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 42 341074-341992(1) | OPEN LINE FROM BUS 341074 [2BEATTYV D 69.000] TO BUS 341992 [2OAKDALE 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 43 341077-341173(1) | OPEN LINE FROM BUS 341077 [2BEATTYV J 69.000] TO BUS 341173 [2BOONEVIL T 69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3978 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 44 341080-341149(1) | OPEN LINE FROM BUS 341080 [2BECKTON 69.000] TO BUS 341149 [2BON AYR 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 45 341080-342445(1) | OPEN LINE FROM BUS 341080 [2BECKTON 69.000] TO BUS 342445 [2W GLASGOW T69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 46 341089-342500(1) | OPEN LINE FROM BUS 341089 [2BEKAERT 69.000] TO BUS 342500 [2WIELAND 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 47 341092-341095(1) | OPEN LINE FROM BUS 341092 [2BELLVIEW 69.000] TO BUS 341095 [2BELLVIEW T 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 48 341095-341164(1) | OPEN LINE FROM BUS 341095 [2BELLVIEW T 69.000] TO BUS 341164 [2BOONE CO 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 49 341095-341227(1) | OPEN LINE FROM BUS 341095 [2BELLVIEW T 69.000] TO BUS 341227 [2BURLINGTN T69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 50 341098-342433(1) | OPEN LINE FROM BUS 341098 [2BEREAKU T 69.000] TO BUS 342433 [2W BEREA J 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 51 341104-341107(1) | OPEN LINE FROM BUS 341104 [2BIG BONE 69.000] TO BUS 341107 [2BIG BONE T 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 52 341107-341164(1) | OPEN LINE FROM BUS 341107 [2BIG BONE T 69.000] TO BUS 341164 [2BOONE CO 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 53 341107-341917(1) | OPEN LINE FROM BUS 341107 [2BIG BONE T 69.000] TO BUS 341917 [2MUNK 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 54 341110-341113(1) | OPEN LINE FROM BUS 341110 [2BIG CREEK 69.000] TO BUS 341113 [2BIG CREEK T69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 55 341110-341439(1) | OPEN LINE FROM BUS 341110 [2BIG CREEK 69.000] TO BUS 341439 [2ELK MT IP 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 56 341113-341464(1) | OPEN LINE FROM BUS 341113 [2BIG CREEK T69.000] TO BUS 341464 [2FALL ROCK 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 57 341113-342001(1) | OPEN LINE FROM BUS 341113 [2BIG CREEK T69.000] TO BUS 342001 [2ONEIDA 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 58 341114-341115(1) | OPEN LINE FROM BUS 341114 [2BIG HILL 69.000] TO BUS 341115 [2BIG HILL T 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 59 341115-342223(1) | OPEN LINE FROM BUS 341115 [2BIG HILL T 69.000] TO BUS 342223 [2SAND GAP T 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 60 341115-342346(1) | OPEN LINE FROM BUS 341115 [2BIG HILL T 69.000] TO BUS 342346 [2THREE LINKS69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 61 341116-341119(1) | OPEN LINE FROM BUS 341116 [2BIG WOODS 69.000] TO BUS 341119 [2BIG WOODS J69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 62 341119-341620(1) | OPEN LINE FROM BUS 341119 [2BIG WOODS J69.000] TO BUS 341620 [2HILDA 69.000] CKT 1 | -31.4811 | 31.481 | 33 | 95.3971 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 63 341119-342088(1) | OPEN LINE FROM BUS 341119 [2BIG WOODS J69.000] TO BUS 342088 [2PLUMMR L T 69.000] CKT 1 | -31.4806 | 31.4806 | 33 | 95.3958 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 64 341122-341125(1) | OPEN LINE FROM BUS 341122 [2BILL WELL T69.000] TO BUS 341125 [2BILL WELLS 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 65 341122-341692(1) | OPEN LINE FROM BUS 341122 [2BILL WELL T69.000] TO BUS 341692 [2JENNY WIL T69.000] CKT 1 | -31.4811 | 31.4811 | 33 | 95.3972 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 66 341122-341860(1) | OPEN LINE FROM BUS 341122 [2BILL WELL T69.000] TO BUS 341860 [2MIDDL CRK T69.000] CKT 1 | -31.4812 | 31.4812 | 33 | 95.3974 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 67 341131-341134(1) | OPEN LINE FROM BUS 341131 [2BLEVINS V T69.000] TO BUS 341134 [2BLEVINS VAL69.000] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 69 341131-342112(1) | OPEN LINE FROM BUS 341131 [2BLEVINS V T69.000] TO BUS 342112 [2PRESTON T 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 70 341137-341296(1) | OPEN LINE FROM BUS 341137 [2BLOOMFLD 69.000] TO BUS 341296 [2CHAPLIN T 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 71 341137-341935(1) | OPEN LINE FROM BUS 341137 [2BLOOMFLD 69.000] TO BUS 341935 [2N SPRINGFLD69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 72 341140-341143(1) | OPEN LINE FROM BUS 341140 [2BLUE G PW 69.000] TO BUS 341143 [2BLUE G PW T69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 73 341143-342019(1) | OPEN LINE FROM BUS 341143 [2BLUE G PW T69.000] TO BUS 342019 [2OWENS IL J 69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3978 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 74 341143-342508(1) | OPEN LINE FROM BUS 341143 [2BLUE G PW T69.000] TO BUS 342508 [2WOODLAWN 69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3978 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 75 341149-341272(1) | OPEN LINE FROM BUS 341149 [2BON AYR 69.000] TO BUS 341272 [2CAVE CITY 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 76 341152-341155(1) | OPEN LINE FROM BUS 341152 [2BONANZA 69.000] TO BUS 341155 [2BONANZA T 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 77 341155-341803(1) | OPEN LINE FROM BUS 341155 [2BONANZA T 69.000] TO BUS 341803 [2MAGOFFIN CO69.000] CKT 1 | -31.4822 | 31.4822 | 33 | 95.4005 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 78 341155-341860(1) | OPEN LINE FROM BUS 341155 [2BONANZA T 69.000] TO BUS 341860 [2MIDDL CRK T69.000] CKT 1 | -31.4811 | 31.4811 | 33 | 95.3974 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 79 341158-341161(1) | OPEN LINE FROM BUS 341158 [2BONNIV DIST69.000] TO BUS 341161 [2BONNIV EK 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 80 341158-341908(1) | OPEN LINE FROM BUS 341158 [2BONNIV DIST69.000] TO BUS 341908 [2MUNFVIL EK 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 81 341161-342403(1) | OPEN LINE FROM BUS 341161 [2BONNIV EK 69.000] TO BUS 342403 [2UPTON T 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 82 341164-341167(1) | OPEN LINE FROM BUS 341164 [2BOONE CO 69.000] TO BUS 341167 [2BOONE DIST 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 83 341164-342388(1) | OPEN LINE FROM BUS 341164 [2BOONE CO 69.000] TO BUS 342388 [2TURKEY FT J69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 84 341164-342466(1) | OPEN LINE FROM BUS 341164 [2BOONE CO 69.000] TO BUS 342466 [2W R SMOOT 69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3979 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 85 341164-342559(1) | OPEN LINE FROM BUS 341164 [2BOONE CO 69.000] TO BUS 342559 [4BOONE CO 138.00] CKT 1 | -31.4809 | 31.4809 | 33 | 95.3965 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 86 341170-341173(1) | OPEN LINE FROM BUS 341170 [2BOONEVIL 69.000] TO BUS 341173 [2BOONEVIL T 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 87 341173-342196(1) | OPEN LINE FROM BUS 341173 [2BOONEVIL T 69.000] TO BUS 342196 [2WHITE OAK 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 88 341179-341746(1) | OPEN LINE FROM BUS 341179 [2BOSTONKU 69.000] TO BUS 341746 [2LEBANON J 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 89 341179-342514(1) | OPEN LINE FROM BUS 341179 [2BOSTONKU 69.000] TO BUS 342514 [2WOOSLEY 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 90 341185-341614(1) | OPEN LINE FROM BUS 341185 [2BOWEN 69.000] TO BUS 341614 [2HIGH ROCK 69.000] CKT 1 | -31.4812 | 31.4812 | 33 | 95.3975 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 91 341185-342100(1) | OPEN LINE FROM BUS 341185 [2BOWEN 69.000] TO BUS 342100 [2POWELL CO 69.000] CKT 1 | -31.4811 | 31.4811 | 33 | 95.3973 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 92 341188-341488(1) | OPEN LINE FROM BUS 341188 [2BRACKEN CO 69.000] TO BUS 341488 [2FOUR OAKS T69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.398 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 93 341188-341587(1) | OPEN LINE FROM BUS 341188 [2BRACKEN CO 69.000] TO BUS 341587 [2GRIFFIN J 69.000] CKT 1 | -31.481 | 31.481 | 33 | 95.3969 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 94 341194-342385(1) | OPEN LINE FROM BUS 341194 [2BRISTOW 69.000] TO BUS 342385 [2TURKEY FT 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 95 341194-342388(1) | OPEN LINE FROM BUS 341194 [2BRISTOW 69.000] TO BUS 342388 [2TURKEY FT J69.000] CKT 1 | -31.481 | 31.481 | 33 | 95.3969 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 96 341197-341818(1) | OPEN LINE FROM BUS 341197 [2BRODHEAD 69.000] TO BUS 341818 [2MARETBURG T69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 97 341197-342349(1) | OPEN LINE FROM BUS 341197 [2BRODHEAD 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 98 341200-341920(1) | OPEN LINE FROM BUS 341200 [2BROMLEYEK 69.000] TO BUS 341920 [2MUNK J 69.000] CKT 1 | -31.4809 | 31.4809 | 33 | 95.3966 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 99 341200-342010(1) | OPEN LINE FROM BUS 341200 [2BROMLEYEK 69.000] TO BUS 342010 [2OWEN CO J1 69.000] CKT 1 | -31.481 | 31.481 | 33 | 95.397 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 100 341203-341206(1) | OPEN LINE FROM BUS 341203 [2BRONSTON 69.000] TO BUS 341206 [2BRONSTON T 69.000] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 101 341206-341347(1) | OPEN LINE FROM BUS 341206 [2BRONSTON T 69.000] TO BUS 341347 [2COOPER DIST69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 102 341206-341392(1) | OPEN LINE FROM BUS 341206 [2BRONSTON T 69.000] TO BUS 341392 [2DENNY 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 103 341209-341210(1) | OPEN LINE FROM BUS 341209 [2BROUGTWN T 69.000] TO BUS 341210 [2BROUGHT TWN69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 104 341209-341617(1) | OPEN LINE FROM BUS 341209 [2BROUGTWN T 69.000] TO BUS 341617 [2HIGHLAND EK69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 105 341209-342367(1) | OPEN LINE FROM BUS 341209 [2BROUGTWN T 69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 106 341212-341774(1) | OPEN LINE FROM BUS 341212 [2BUDD 69.000] TO BUS 341774 [2LOGAN 2 T 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
342000 | 5GAS | 161 | 342760 | 5LIBERTY J | 161 | 1 | EKPC_P1-2_LIB-CAS-GAS-MAR161 | EKPC_P1-2_LIB-CAS-GAS-MAR161 | 212.5774 | 212.5774 | 153 | 138.9395 | EKPC
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 107 341212-342500(1) | OPEN LINE FROM BUS 341212 [2BUDD 69.000] TO BUS 342500 [2WIELAND 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 108 341215-341281(1) | OPEN LINE FROM BUS 341215 [2BULLITT CO 69.000] TO BUS 341281 [2CEDAR GR 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 109 341215-341389(1) | OPEN LINE FROM BUS 341215 [2BULLITT CO 69.000] TO BUS 341389 [2DEATSVILL T69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 110 341215-342700(1) | OPEN LINE FROM BUS 341215 [2BULLITT CO 69.000] TO BUS 342700 [5BULLITT CO 161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
342000 | 5GAS | 161 | 342760 | 5LIBERTY J | 161 | 1 | SINGLE OPN LIN 572 342703-342769(1) | OPEN LINE FROM BUS 342703 [5CASEY CO 161.00] TO BUS 342769 [5MARION CO 161.00] CKT 1 | 183.4648 | 183.4648 | 153 | 119.9117 | EKPC
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 111 341218-341227(1) | OPEN LINE FROM BUS 341218 [2BULLITTSVIL69.000] TO BUS 341227 [2BURLINGTN T69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 112 341218-341605(1) | OPEN LINE FROM BUS 341218 [2BULLITTSVIL69.000] TO BUS 341605 [2HEBRON 69.000] CKT 1 | -31.4809 | 31.4809 | 33 | 95.3967 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 113 341224-341227(1) | OPEN LINE FROM BUS 341224 [2BURLINGTN 69.000] TO BUS 341227 [2BURLINGTN T69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 114 341233-341974(1) | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 341974 [2NORWOOD T 69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3979 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 115 341233-342286(1) | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 116 341248-341608(1) | OPEN LINE FROM BUS 341248 [2CAMPTON 69.000] TO BUS 341608 [2HELECHAW 69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3978 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 117 341248-342520(1) | OPEN LINE FROM BUS 341248 [2CAMPTON 69.000] TO BUS 342520 [2ZACHARIAH 69.000] CKT 1 | -31.481 | 31.481 | 33 | 95.397 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 118 341251-341254(1) | OPEN LINE FROM BUS 341251 [2CANE RIDG 69.000] TO BUS 341254 [2CANE RIDG T69.000] CKT 1 | -31.4821 | 31.4821 | 33 | 95.4004 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 119 341254-341872(1) | OPEN LINE FROM BUS 341254 [2CANE RIDG T69.000] TO BUS 341872 [2MILLB-CRL J69.000] CKT 1 | -31.482 | 31.482 | 33 | 95.4 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 120 341254-342259(1) | OPEN LINE FROM BUS 341254 [2CANE RIDG T69.000] TO BUS 342259 [2SIDEVIEW 69.000] CKT 1 | -31.482 | 31.482 | 33 | 95.4 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 121 341260-342013(1) | OPEN LINE FROM BUS 341260 [2CARSON 69.000] TO BUS 342013 [2OWEN CO J2 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 122 341263-341266(1) | OPEN LINE FROM BUS 341263 [2CARTER CTY 69.000] TO BUS 341266 [2CARTER CY T69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 123 341266-342034(1) | OPEN LINE FROM BUS 341266 [2CARTER CY T69.000] TO BUS 342034 [2PACTOLUS T 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 124 341266-342475(1) | OPEN LINE FROM BUS 341266 [2CARTER CY T69.000] TO BUS 342475 [2WARNOCK 69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3979 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 125 341269-342064(1) | OPEN LINE FROM BUS 341269 [2CASEY CO 69.000] TO BUS 342064 [2PEYTONS ST 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324718 | 2SHELBY CO T | 69 | 324726 | 2SHELBYVIL S | 69 | 1 | SINGLE OPN LIN 342 341774-341775(1) | OPEN LINE FROM BUS 341774 [2LOGAN 2 T 69.000] TO BUS 341775 [2LOGAN TAP 69.000] CKT 1 | 58.219 | 58.219 | 49 | 118.8142 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 126 341269-342703(1) | OPEN LINE FROM BUS 341269 [2CASEY CO 69.000] TO BUS 342703 [5CASEY CO 161.00] CKT 1 | -31.4813 | 31.4813 | 33 | 95.398 | LGEE
324718 | 2SHELBY CO T | 69 | 324726 | 2SHELBYVIL S | 69 | 1 | SINGLE OPN LIN 343 341775-342247(1) | OPEN LINE FROM BUS 341775 [2LOGAN TAP 69.000] TO BUS 342247 [2SHELBY CO 69.000] CKT 1 | 58.2175 | 58.2175 | 49 | 118.8111 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 127 341272-341275(1) | OPEN LINE FROM BUS 341272 [2CAVE CITY 69.000] TO BUS 341275 [2CAVE CITY J69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 128 341275-342241(1) | OPEN LINE FROM BUS 341275 [2CAVE CITY J69.000] TO BUS 342241 [2SEYMOUR T 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 129 341281-342082(1) | OPEN LINE FROM BUS 341281 [2CEDAR GR 69.000] TO BUS 342082 [2PLEAS GRV 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 130 341287-341713(1) | OPEN LINE FROM BUS 341287 [2CENT HARDIN69.000] TO BUS 341713 [2KARGLE 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 131 341287-342307(1) | OPEN LINE FROM BUS 341287 [2CENT HARDIN69.000] TO BUS 342307 [2STEPHENSBRG69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.398 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 132 341287-342568(1) | OPEN LINE FROM BUS 341287 [2CENT HARDIN69.000] TO BUS 342568 [4CENT HARDIN138.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 133 341293-341296(1) | OPEN LINE FROM BUS 341293 [2CHAPLIN 69.000] TO BUS 341296 [2CHAPLIN T 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 134 341296-342262(1) | OPEN LINE FROM BUS 341296 [2CHAPLIN T 69.000] TO BUS 342262 [2SINAI 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 135 341299-341989(1) | OPEN LINE FROM BUS 341299 [2CHARTERS 69.000] TO BUS 341989 [2OAK RIDGE T69.000] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 136 341299-342124(1) | OPEN LINE FROM BUS 341299 [2CHARTERS 69.000] TO BUS 342124 [2RECTORVILLE69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 137 341302-341305(1) | OPEN LINE FROM BUS 341302 [2CLAY CITY 69.000] TO BUS 341305 [2CLAY CITY T69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 138 341305-341593(1) | OPEN LINE FROM BUS 341305 [2CLAY CITY T69.000] TO BUS 341593 [2HARDWCRK T 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 139 341305-341599(1) | OPEN LINE FROM BUS 341305 [2CLAY CITY T69.000] TO BUS 341599 [2HARGETT T 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 140 341308-341314(1) | OPEN LINE FROM BUS 341308 [2CLAY LCK 69.000] TO BUS 341314 [2CLAY LCK SW69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 141 341311-341314(1) | OPEN LINE FROM BUS 341311 [2CLAY LCK J 69.000] TO BUS 341314 [2CLAY LCK SW69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 142 341311-342184(1) | OPEN LINE FROM BUS 341311 [2CLAY LCK J 69.000] TO BUS 342184 [2S ANDERSON 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 143 341311-342406(1) | OPEN LINE FROM BUS 341311 [2CLAY LCK J 69.000] TO BUS 342406 [2VAN ARSDELL69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 144 341317-341390(1) | OPEN LINE FROM BUS 341317 [2CLAY VILLAG69.000] TO BUS 341390 [2DEFOE TAP 69.000] CKT 1 | -31.4809 | 31.4809 | 33 | 95.3965 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 145 341320-341512(1) | OPEN LINE FROM BUS 341320 [2COBURG 69.000] TO BUS 341512 [2GARLIN T 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 146 341323-341335(1) | OPEN LINE FROM BUS 341323 [2COBURG J 69.000] TO BUS 341335 [2COLUMBIA 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 147 341323-341512(1) | OPEN LINE FROM BUS 341323 [2COBURG J 69.000] TO BUS 341512 [2GARLIN T 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 148 341323-342235(1) | OPEN LINE FROM BUS 341323 [2COBURG J 69.000] TO BUS 342235 [2SEWELTN J 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 149 341326-341488(1) | OPEN LINE FROM BUS 341326 [2COLEMANSVIL69.000] TO BUS 341488 [2FOUR OAKS T69.000] CKT 1 | -31.4805 | 31.4805 | 33 | 95.3955 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 150 341326-342133(1) | OPEN LINE FROM BUS 341326 [2COLEMANSVIL69.000] TO BUS 342133 [2RENAKER 69.000] CKT 1 | -31.4802 | 31.4802 | 33 | 95.3944 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 151 341329-341332(1) | OPEN LINE FROM BUS 341329 [2COLESBURG 69.000] TO BUS 341332 [2COLESBURG J69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 152 341332-341944(1) | OPEN LINE FROM BUS 341332 [2COLESBURG J69.000] TO BUS 341944 [2NELSON CO 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 153 341332-342155(1) | OPEN LINE FROM BUS 341332 [2COLESBURG J69.000] TO BUS 342155 [2ROANOKE T 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 154 341335-341370(1) | OPEN LINE FROM BUS 341335 [2COLUMBIA 69.000] TO BUS 341370 [2COLUMB S KU69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 155 341335-342436(1) | OPEN LINE FROM BUS 341335 [2COLUMBIA 69.000] TO BUS 342436 [2W COLUMBI T69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 156 341338-341341(1) | OPEN LINE FROM BUS 341338 [2CONWAY 69.000] TO BUS 341341 [2CONWAY T 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 157 341341-342346(1) | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342346 [2THREE LINKS69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 158 341341-342349(1) | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 159 341342-341343(1) | OPEN LINE FROM BUS 341342 [2CONTOWN T 69.000] TO BUS 341343 [2CONTOWN 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 160 341342-341761(1) | OPEN LINE FROM BUS 341342 [2CONTOWN T 69.000] TO BUS 341761 [2LIBERTY J 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 161 341342-342067(1) | OPEN LINE FROM BUS 341342 [2CONTOWN T 69.000] TO BUS 342067 [2PHIL 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 162 341344-341347(1) | OPEN LINE FROM BUS 341344 [2COOPER 69.000] TO BUS 341347 [2COOPER DIST69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 163 341344-342286(1) | OPEN LINE FROM BUS 341344 [2COOPER 69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 164 341344-342286(2) | OPEN LINE FROM BUS 341344 [2COOPER 69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 2 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 165 341344-342715(1) | OPEN LINE FROM BUS 341344 [2COOPER 69.000] TO BUS 342715 [5COOPER1 161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 166 341350-342067(1) | OPEN LINE FROM BUS 341350 [2CRESTON 69.000] TO BUS 342067 [2PHIL 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 167 341353-341356(1) | OPEN LINE FROM BUS 341353 [2CROCKETT 69.000] TO BUS 341356 [2CROCKETT T 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 168 341356-341653(1) | OPEN LINE FROM BUS 341356 [2CROCKETT T 69.000] TO BUS 341653 [2HOT MIX R T69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 169 341356-342265(1) | OPEN LINE FROM BUS 341356 [2CROCKETT T 69.000] TO BUS 342265 [2SKAGGS 69.000] CKT 1 | -31.4812 | 31.4812 | 33 | 95.3975 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 170 341359-341362(1) | OPEN LINE FROM BUS 341359 [2CROOKSVIL 69.000] TO BUS 341362 [2CROOKSVIL T69.000] CKT 1 | -31.4814 | 31.4815 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 171 341359-342288(1) | OPEN LINE FROM BUS 341359 [2CROOKSVIL 69.000] TO BUS 342288 [2SPEEDWELL 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 172 341362-341406(1) | OPEN LINE FROM BUS 341362 [2CROOKSVIL T69.000] TO BUS 341406 [2DUNCAN LN T69.000] CKT 1 | -31.4809 | 31.4809 | 33 | 95.3967 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 173 341362-341611(1) | OPEN LINE FROM BUS 341362 [2CROOKSVIL T69.000] TO BUS 341611 [2HICKORY PL 69.000] CKT 1 | -31.4811 | 31.4811 | 33 | 95.3972 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 174 341366-341370(1) | OPEN LINE FROM BUS 341366 [2COLUMB KU 69.000] TO BUS 341370 [2COLUMB S KU69.000] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 175 341377-341602(1) | OPEN LINE FROM BUS 341377 [2CYNTHIA TIE69.000] TO BUS 341602 [2HEADQTRS 69.000] CKT 1 | -31.4804 | 31.4804 | 33 | 95.3953 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 176 341377-342355(1) | OPEN LINE FROM BUS 341377 [2CYNTHIA TIE69.000] TO BUS 342355 [2THREE M T 69.000] CKT 1 | -31.4801 | 31.48 | 33 | 95.3941 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 177 341379-342256(1) | OPEN LINE FROM BUS 341379 [2DAHL ROAD 69.000] TO BUS 342256 [2SHOPVILLE 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 178 341380-341959(1) | OPEN LINE FROM BUS 341380 [2DALE 69.000] TO BUS 341959 [2NEWBY 1 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 179 341380-341962(1) | OPEN LINE FROM BUS 341380 [2DALE 69.000] TO BUS 341962 [2NEWBY 2 69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3979 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 180 341380-342574(1) | OPEN LINE FROM BUS 341380 [2DALE 69.000] TO BUS 342574 [4DALE 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 181 341381-341382(1) | OPEN LINE FROM BUS 341381 [2DAV LANE 69.000] TO BUS 341382 [2DAV LANE T 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 182 341382-341734(1) | OPEN LINE FROM BUS 341382 [2DAV LANE T 69.000] TO BUS 341734 [2LAUR C IP T69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 183 341382-342451(1) | OPEN LINE FROM BUS 341382 [2DAV LANE T 69.000] TO BUS 342451 [2W LONDON 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 184 341383-341467(1) | OPEN LINE FROM BUS 341383 [2DAVIS 69.000] TO BUS 341467 [2FAYETTE 69.000] CKT 1 | -31.4811 | 31.4811 | 33 | 95.3974 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 185 341383-341965(1) | OPEN LINE FROM BUS 341383 [2DAVIS 69.000] TO BUS 341965 [2NICHOLASVIL69.000] CKT 1 | -31.4812 | 31.4812 | 33 | 95.3976 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 186 341386-341389(1) | OPEN LINE FROM BUS 341386 [2DEATSVIL 69.000] TO BUS 341389 [2DEATSVILL T69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 187 341389-341707(1) | OPEN LINE FROM BUS 341389 [2DEATSVILL T69.000] TO BUS 341707 [2JOE TICH T 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 188 341390-341391(1) | OPEN LINE FROM BUS 341390 [2DEFOE TAP 69.000] TO BUS 341391 [2DEFOE 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 189 341390-341950(1) | OPEN LINE FROM BUS 341390 [2DEFOE TAP 69.000] TO BUS 341950 [2NEW CASTLE 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 190 341392-341578(1) | OPEN LINE FROM BUS 341392 [2DENNY 69.000] TO BUS 341578 [2GREGORY R T69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 191 341392-342499(1) | OPEN LINE FROM BUS 341392 [2DENNY 69.000] TO BUS 342499 [2WIBORG T 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 192 341392-342727(1) | OPEN LINE FROM BUS 341392 [2DENNY 69.000] TO BUS 342727 [5DENNY 161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 193 341394-341479(1) | OPEN LINE FROM BUS 341394 [2PATRIOT PW 69.000] TO BUS 341479 [2S BOUND RD 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 194 341394-342151(1) | OPEN LINE FROM BUS 341394 [2PATRIOT PW 69.000] TO BUS 342151 [2RINEYVILLE 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 195 341394-342157(1) | OPEN LINE FROM BUS 341394 [2PATRIOT PW 69.000] TO BUS 342157 [2ROGERSVIL J69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 196 341394-342274(1) | OPEN LINE FROM BUS 341394 [2PATRIOT PW 69.000] TO BUS 342274 [2SMITHRVIL T69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 197 341398-341605(1) | OPEN LINE FROM BUS 341398 [2DOWNING 69.000] TO BUS 341605 [2HEBRON 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 198 341398-341880(1) | OPEN LINE FROM BUS 341398 [2DOWNING 69.000] TO BUS 341880 [2MINEOLA PKE69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 199 341400-342091(1) | OPEN LINE FROM BUS 341400 [2DRAVO 69.000] TO BUS 342091 [2PLUMVILLE 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 200 341401-341842(1) | OPEN LINE FROM BUS 341401 [2DURO 69.000] TO BUS 341842 [2MBUSA T 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 201 341404-341842(1) | OPEN LINE FROM BUS 341404 [2DURO T 69.000] TO BUS 341842 [2MBUSA T 69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3977 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 202 341404-342295(1) | OPEN LINE FROM BUS 341404 [2DURO T 69.000] TO BUS 342295 [2STANLY P J169.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 203 341404-342388(1) | OPEN LINE FROM BUS 341404 [2DURO T 69.000] TO BUS 342388 [2TURKEY FT J69.000] CKT 1 | -31.4812 | 31.4812 | 33 | 95.3976 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 204 341405-341406(1) | OPEN LINE FROM BUS 341405 [2DUNCANNO LN69.000] TO BUS 341406 [2DUNCAN LN T69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 205 341407-342019(1) | OPEN LINE FROM BUS 341407 [2E BARDSTOWN69.000] TO BUS 342019 [2OWENS IL J 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 206 341410-341929(1) | OPEN LINE FROM BUS 341410 [2E BERNSTADT69.000] TO BUS 341929 [2N LONDON 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 207 341416-342076(1) | OPEN LINE FROM BUS 341416 [2E PINE KNOT69.000] TO BUS 342076 [2PINE KNOT 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 208 341419-341422(1) | OPEN LINE FROM BUS 341419 [2E SOMERSE T69.000] TO BUS 341422 [2E SOMERSET 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 209 341419-341941(1) | OPEN LINE FROM BUS 341419 [2E SOMERSE T69.000] TO BUS 341941 [2NELSN VAL T69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 210 341419-341974(1) | OPEN LINE FROM BUS 341419 [2E SOMERSE T69.000] TO BUS 341974 [2NORWOOD T 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 211 341425-341428(1) | OPEN LINE FROM BUS 341425 [2EBERLE 69.000] TO BUS 341428 [2EBERLE T 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 212 341428-341809(1) | OPEN LINE FROM BUS 341428 [2EBERLE T 69.000] TO BUS 341809 [2MAPLESVIL T69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 213 341431-341434(1) | OPEN LINE FROM BUS 341431 [2EDM-JBGAL J69.000] TO BUS 341434 [2EDM-JBGAL T69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 214 341431-341728(1) | OPEN LINE FROM BUS 341431 [2EDM-JBGAL J69.000] TO BUS 341728 [2KNOB LICK 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 215 341431-342322(1) | OPEN LINE FROM BUS 341431 [2EDM-JBGAL J69.000] TO BUS 342322 [2SUMM SHADE 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 216 341434-341437(1) | OPEN LINE FROM BUS 341434 [2EDM-JBGAL T69.000] TO BUS 341437 [2EDMON IND P69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 217 341434-341680(1) | OPEN LINE FROM BUS 341434 [2EDM-JBGAL T69.000] TO BUS 341680 [2JB GALLOWAY69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 218 341443-341446(1) | OPEN LINE FROM BUS 341443 [2ELLIO CO PT69.000] TO BUS 341446 [2ELLIOT CO P69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 219 341443-341953(1) | OPEN LINE FROM BUS 341443 [2ELLIO CO PT69.000] TO BUS 341953 [2NEW FOUNDL 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 220 341449-342163(1) | OPEN LINE FROM BUS 341449 [2ELLIOTTVILL69.000] TO BUS 342163 [2ROWAN CO 69.000] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 221 341455-341458(1) | OPEN LINE FROM BUS 341455 [2ETOWN EK1 69.000] TO BUS 341458 [2ETOWN EK2 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 222 341455-342274(1) | OPEN LINE FROM BUS 341455 [2ETOWN EK1 69.000] TO BUS 342274 [2SMITHRVIL T69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 223 341455-342379(1) | OPEN LINE FROM BUS 341455 [2ETOWN EK1 69.000] TO BUS 342379 [2TUNNEL H T 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 224 341458-342340(1) | OPEN LINE FROM BUS 341458 [2ETOWN EK2 69.000] TO BUS 342340 [2THARP T 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 225 341461-341797(1) | OPEN LINE FROM BUS 341461 [2FALCON EK 69.000] TO BUS 341797 [2MAGGARD 69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3978 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 226 341461-342310(1) | OPEN LINE FROM BUS 341461 [2FALCON EK 69.000] TO BUS 342310 [2SUBLETT 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 227 341464-341569(1) | OPEN LINE FROM BUS 341464 [2FALL ROCK 69.000] TO BUS 341569 [2GREENBRIA T69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 228 341464-342391(1) | OPEN LINE FROM BUS 341464 [2FALL ROCK 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 229 341464-342730(1) | OPEN LINE FROM BUS 341464 [2FALL ROCK 69.000] TO BUS 342730 [5FALL ROCK 161.00] CKT 1 | -31.4808 | 31.4808 | 33 | 95.3964 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 230 341467-342580(1) | OPEN LINE FROM BUS 341467 [2FAYETTE 69.000] TO BUS 342580 [4FAYETTE 138.00] CKT 1 | -31.481 | 31.481 | 33 | 95.397 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 231 341470-341473(1) | OPEN LINE FROM BUS 341470 [2FLOYD EK 69.000] TO BUS 341473 [2FLOYD-SFL T69.000] CKT 1 | -31.4807 | 31.4807 | 33 | 95.3961 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 232 341470-342511(1) | OPEN LINE FROM BUS 341470 [2FLOYD EK 69.000] TO BUS 342511 [2WOODSTOCK 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 233 341473-342115(1) | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 234 341473-342193(1) | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342193 [2S FLOYD 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 235 341476-341899(1) | OPEN LINE FROM BUS 341476 [2FOGG PIKE 69.000] TO BUS 341899 [2MT STERLING69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 236 341476-342130(1) | OPEN LINE FROM BUS 341476 [2FOGG PIKE 69.000] TO BUS 342130 [2REID VILLAG69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 237 341485-341488(1) | OPEN LINE FROM BUS 341485 [2FOUR OAKS 69.000] TO BUS 341488 [2FOUR OAKS T69.000] CKT 1 | -31.4812 | 31.4812 | 33 | 95.3976 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 238 341485-341550(1) | OPEN LINE FROM BUS 341485 [2FOUR OAKS 69.000] TO BUS 341550 [2FALMOUTH KU69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 239 341491-341548(1) | OPEN LINE FROM BUS 341491 [2FOX HOLLOW 69.000] TO BUS 341548 [2GORIN PRK J69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 240 341491-342037(1) | OPEN LINE FROM BUS 341491 [2FOX HOLLOW 69.000] TO BUS 342037 [2PARKWAY 1 69.000] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 241 341491-342043(1) | OPEN LINE FROM BUS 341491 [2FOX HOLLOW 69.000] TO BUS 342043 [2PARKWAY 2 T69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 242 341491-342049(1) | OPEN LINE FROM BUS 341491 [2FOX HOLLOW 69.000] TO BUS 342049 [2PATTON RD J69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 243 341491-342732(1) | OPEN LINE FROM BUS 341491 [2FOX HOLLOW 69.000] TO BUS 342732 [5FOX HOLLOW 161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 244 341494-341497(1) | OPEN LINE FROM BUS 341494 [2FREDRIKBG T69.000] TO BUS 341497 [2FREDRIKBRG 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 245 341494-341935(1) | OPEN LINE FROM BUS 341494 [2FREDRIKBG T69.000] TO BUS 341935 [2N SPRINGFLD69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3978 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 246 341494-342508(1) | OPEN LINE FROM BUS 341494 [2FREDRIKBG T69.000] TO BUS 342508 [2WOODLAWN 69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3978 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 247 341500-341644(1) | OPEN LINE FROM BUS 341500 [2FRENCHBURG 69.000] TO BUS 341644 [2HOPE 69.000] CKT 1 | -31.4808 | 31.4808 | 33 | 95.3963 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 248 341500-341824(1) | OPEN LINE FROM BUS 341500 [2FRENCHBURG 69.000] TO BUS 341824 [2MARIBA T 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 249 341503-341506(1) | OPEN LINE FROM BUS 341503 [2GAP OF RG T69.000] TO BUS 341506 [2GAP OF RIDG69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 250 341503-341578(1) | OPEN LINE FROM BUS 341503 [2GAP OF RG T69.000] TO BUS 341578 [2GREGORY R T69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 251 341503-341887(1) | OPEN LINE FROM BUS 341503 [2GAP OF RG T69.000] TO BUS 341887 [2MONTICELLO 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 252 341509-341512(1) | OPEN LINE FROM BUS 341509 [2GARLIN 69.000] TO BUS 341512 [2GARLIN T 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 253 341515-341732(1) | OPEN LINE FROM BUS 341515 [2GARRARD CO 69.000] TO BUS 341732 [2LANCASTER T69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 254 341515-942410(1) | OPEN LINE FROM BUS 341515 [2GARRARD CO 69.000] TO BUS 942410 [AE2-254 TAP 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 255 341518-341521(1) | OPEN LINE FROM BUS 341518 [2GARRARD KU 69.000] TO BUS 341521 [2GARRARDKU T69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 256 341521-341806(1) | OPEN LINE FROM BUS 341521 [2GARRARDKU T69.000] TO BUS 341806 [2MANCHESTER 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 257 341530-342043(1) | OPEN LINE FROM BUS 341530 [2GLASGO-CLEV69.000] TO BUS 342043 [2PARKWAY 2 T69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 258 341530-342445(1) | OPEN LINE FROM BUS 341530 [2GLASGO-CLEV69.000] TO BUS 342445 [2W GLASGOW T69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 259 341533-341632(1) | OPEN LINE FROM BUS 341533 [2GLENDALE 69.000] TO BUS 341632 [2HODGENVILLE69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 260 341533-342307(1) | OPEN LINE FROM BUS 341533 [2GLENDALE 69.000] TO BUS 342307 [2STEPHENSBRG69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 261 341536-341623(1) | OPEN LINE FROM BUS 341536 [2GODDARD 69.000] TO BUS 341623 [2HILLSBORO 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 262 341536-341989(1) | OPEN LINE FROM BUS 341536 [2GODDARD 69.000] TO BUS 341989 [2OAK RIDGE T69.000] CKT 1 | -31.4812 | 31.4812 | 33 | 95.3975 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 263 341536-342088(1) | OPEN LINE FROM BUS 341536 [2GODDARD 69.000] TO BUS 342088 [2PLUMMR L T 69.000] CKT 1 | -31.4832 | 31.4832 | 33 | 95.4035 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 264 341536-342589(1) | OPEN LINE FROM BUS 341536 [2GODDARD 69.000] TO BUS 342589 [4GODDARD 138.00] CKT 1 | -31.481 | 31.481 | 33 | 95.397 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 265 341539-341686(1) | OPEN LINE FROM BUS 341539 [2GOLDBUG 69.000] TO BUS 341686 [2JELLICO C T69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 266 341542-341548(1) | OPEN LINE FROM BUS 341542 [2GOODNIGHT 69.000] TO BUS 341548 [2GORIN PRK J69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 267 341551-341587(1) | OPEN LINE FROM BUS 341551 [2GRANTS LICK69.000] TO BUS 341587 [2GRIFFIN J 69.000] CKT 1 | -31.4819 | 31.4819 | 33 | 95.3997 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 268 341551-342298(1) | OPEN LINE FROM BUS 341551 [2GRANTS LICK69.000] TO BUS 342298 [2STANLY P J269.000] CKT 1 | -31.4798 | 31.4798 | 33 | 95.3934 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 269 341554-341752(1) | OPEN LINE FROM BUS 341554 [2GRAYSON J 69.000] TO BUS 341752 [2LEON 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 270 341554-342034(1) | OPEN LINE FROM BUS 341554 [2GRAYSON J 69.000] TO BUS 342034 [2PACTOLUS T 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 271 341563-341575(1) | OPEN LINE FROM BUS 341563 [2GREEN CO 69.000] TO BUS 341575 [2GREENSBURG 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 272 341563-342325(1) | OPEN LINE FROM BUS 341563 [2GREEN CO 69.000] TO BUS 342325 [2SUMMERSVIL 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 273 341563-342733(1) | OPEN LINE FROM BUS 341563 [2GREEN CO 69.000] TO BUS 342733 [5GREEN CO 161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 274 341569-341572(1) | OPEN LINE FROM BUS 341569 [2GREENBRIA T69.000] TO BUS 341572 [2GREENBRIAR 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 275 341569-341806(1) | OPEN LINE FROM BUS 341569 [2GREENBRIA T69.000] TO BUS 341806 [2MANCHESTER 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 276 341575-341854(1) | OPEN LINE FROM BUS 341575 [2GREENSBURG 69.000] TO BUS 341854 [2MCKINNY T 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 277 341578-341581(1) | OPEN LINE FROM BUS 341578 [2GREGORY R T69.000] TO BUS 341581 [2GREGORY RD 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 278 341584-341587(1) | OPEN LINE FROM BUS 341584 [2GRIFFIN 69.000] TO BUS 341587 [2GRIFFIN J 69.000] CKT 1 | -31.4812 | 31.4812 | 33 | 95.3977 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 279 341590-341593(1) | OPEN LINE FROM BUS 341590 [2HARDWCRK 69.000] TO BUS 341593 [2HARDWCRK T 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 280 341593-342301(1) | OPEN LINE FROM BUS 341593 [2HARDWCRK T 69.000] TO BUS 342301 [2STANTON 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 281 341596-341599(1) | OPEN LINE FROM BUS 341596 [2HARGETT 69.000] TO BUS 341599 [2HARGETT T 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 282 341599-342370(1) | OPEN LINE FROM BUS 341599 [2HARGETT T 69.000] TO BUS 342370 [2TRAPP 69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.398 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 283 341602-341872(1) | OPEN LINE FROM BUS 341602 [2HEADQTRS 69.000] TO BUS 341872 [2MILLB-CRL J69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3979 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 284 341602-342280(1) | OPEN LINE FROM BUS 341602 [2HEADQTRS 69.000] TO BUS 342280 [2SNOW HILL 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 285 341605-342595(1) | OPEN LINE FROM BUS 341605 [2HEBRON 69.000] TO BUS 342595 [4HEBRON 138.00] CKT 1 | -31.481 | 31.481 | 33 | 95.397 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 286 341608-342313(1) | OPEN LINE FROM BUS 341608 [2HELECHAW 69.000] TO BUS 342313 [2SUBLETT J 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 287 341611-342103(1) | OPEN LINE FROM BUS 341611 [2HICKORY PL 69.000] TO BUS 342103 [2PPG 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 288 341614-342520(1) | OPEN LINE FROM BUS 341614 [2HIGH ROCK 69.000] TO BUS 342520 [2ZACHARIAH 69.000] CKT 1 | -31.4812 | 31.4812 | 33 | 95.3975 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 289 341617-341896(1) | OPEN LINE FROM BUS 341617 [2HIGHLAND EK69.000] TO BUS 341896 [2MT OLIVE J 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 290 341620-342163(1) | OPEN LINE FROM BUS 341620 [2HILDA 69.000] TO BUS 342163 [2ROWAN CO 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 291 341623-342052(1) | OPEN LINE FROM BUS 341623 [2HILLSBORO 69.000] TO BUS 342052 [2PEASTICKS 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 292 341632-341800(1) | OPEN LINE FROM BUS 341632 [2HODGENVILLE69.000] TO BUS 341800 [2MAGNOLIA 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 293 341632-342316(1) | OPEN LINE FROM BUS 341632 [2HODGENVILLE69.000] TO BUS 342316 [2SULPHUR CRK69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3979 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 294 341638-342199(1) | OPEN LINE FROM BUS 341638 [2HOLLOWAY J 69.000] TO BUS 342199 [2S JESSAM J 69.000] CKT 1 | -31.4818 | 31.4818 | 33 | 95.3993 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 295 341638-342463(1) | OPEN LINE FROM BUS 341638 [2HOLLOWAY J 69.000] TO BUS 342463 [2W NICHVIL T69.000] CKT 1 | -31.4811 | 31.4811 | 33 | 95.3972 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 296 341641-341887(1) | OPEN LINE FROM BUS 341641 [2HOMESTEAD S69.000] TO BUS 341887 [2MONTICELLO 69.000] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 297 341644-341683(1) | OPEN LINE FROM BUS 341644 [2HOPE 69.000] TO BUS 341683 [2JEFFERSNVIL69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 298 341647-341650(1) | OPEN LINE FROM BUS 341647 [2HORSE CV KU69.000] TO BUS 341650 [2HORSECAVE T69.000] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3988 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 299 341650-341651(Z1) | OPEN LINE FROM BUS 341650 [2HORSECAVE T69.000] TO BUS 341651 [2HORSECAVE J69.000] CKT Z1 | -31.4816 | 31.4816 | 33 | 95.3988 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 300 341651-341914(1) | OPEN LINE FROM BUS 341651 [2HORSECAVE J69.000] TO BUS 341914 [2MUNFVILKU T69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 301 341653-341656(1) | OPEN LINE FROM BUS 341653 [2HOT MIX R T69.000] TO BUS 341656 [2HOT MIX RD 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 302 341653-341890(1) | OPEN LINE FROM BUS 341653 [2HOT MIX R T69.000] TO BUS 341890 [2MORGAN CO 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 303 341659-341662(1) | OPEN LINE FROM BUS 341659 [2HT ADAMS 69.000] TO BUS 341662 [2HT ADAMS T 69.000] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3989 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 304 341662-341671(1) | OPEN LINE FROM BUS 341662 [2HT ADAMS T 69.000] TO BUS 341671 [2HUNT FARM J69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 306 341665-341701(1) | OPEN LINE FROM BUS 341665 [2HUNT 69.000] TO BUS 341701 [2JK SMITH 69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3979 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 307 341665-341869(1) | OPEN LINE FROM BUS 341665 [2HUNT 69.000] TO BUS 341869 [2MILL HUNT T69.000] CKT 1 | -31.4803 | 31.4803 | 33 | 95.3949 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 308 341665-342596(1) | OPEN LINE FROM BUS 341665 [2HUNT 69.000] TO BUS 342596 [4HUNT 138.00] CKT 1 | -31.4801 | 31.48 | 33 | 95.3941 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 309 341671-342061(1) | OPEN LINE FROM BUS 341671 [2HUNT FARM J69.000] TO BUS 342061 [2PERRYVILLE 69.000] CKT 1 | -31.4812 | 31.4812 | 33 | 95.3975 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 310 341677-341890(1) | OPEN LINE FROM BUS 341677 [2INDEX 69.000] TO BUS 341890 [2MORGAN CO 69.000] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 311 341683-342100(1) | OPEN LINE FROM BUS 341683 [2JEFFERSNVIL69.000] TO BUS 342100 [2POWELL CO 69.000] CKT 1 | -31.481 | 31.481 | 33 | 95.3971 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 312 341686-341689(1) | OPEN LINE FROM BUS 341686 [2JELLICO C T69.000] TO BUS 341689 [2JELLICO CRK69.000] CKT 1 | -31.4814 | 31.4815 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 313 341686-342076(1) | OPEN LINE FROM BUS 341686 [2JELLICO C T69.000] TO BUS 342076 [2PINE KNOT 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 314 341692-341695(1) | OPEN LINE FROM BUS 341692 [2JENNY WIL T69.000] TO BUS 341695 [2JENNY WILEY69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 315 341692-342343(1) | OPEN LINE FROM BUS 341692 [2JENNY WIL T69.000] TO BUS 342343 [2THELMA 69.000] CKT 1 | -31.4812 | 31.4812 | 33 | 95.3976 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 316 341701-342370(1) | OPEN LINE FROM BUS 341701 [2JK SMITH 69.000] TO BUS 342370 [2TRAPP 69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3979 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 317 341704-341707(1) | OPEN LINE FROM BUS 341704 [2JOE TICH 69.000] TO BUS 341707 [2JOE TICH T 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 318 341707-342427(1) | OPEN LINE FROM BUS 341707 [2JOE TICH T 69.000] TO BUS 342427 [2W BARDSTWN 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 319 341716-341722(1) | OPEN LINE FROM BUS 341716 [2KEAVY 69.000] TO BUS 341722 [2KEAVY 2 T 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 320 341719-341740(1) | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.398 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 321 341719-342073(1) | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.398 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 322 341722-341740(1) | OPEN LINE FROM BUS 341722 [2KEAVY 2 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 323 341722-342187(1) | OPEN LINE FROM BUS 341722 [2KEAVY 2 T 69.000] TO BUS 342187 [2S CORBIN 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 324 341725-342007(1) | OPEN LINE FROM BUS 341725 [2KEITH 69.000] TO BUS 342007 [2OWEN CO 69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3978 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 325 341725-342058(1) | OPEN LINE FROM BUS 341725 [2KEITH 69.000] TO BUS 342058 [2PENN 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 326 341728-341854(1) | OPEN LINE FROM BUS 341728 [2KNOB LICK 69.000] TO BUS 341854 [2MCKINNY T 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 327 341731-341732(1) | OPEN LINE FROM BUS 341731 [2LANCASTER 69.000] TO BUS 341732 [2LANCASTER T69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 328 341732-341959(1) | OPEN LINE FROM BUS 341732 [2LANCASTER T69.000] TO BUS 341959 [2NEWBY 1 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 329 341734-341737(1) | OPEN LINE FROM BUS 341734 [2LAUR C IP T69.000] TO BUS 341737 [2LAUR CO IP 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 330 341734-341929(1) | OPEN LINE FROM BUS 341734 [2LAUR C IP T69.000] TO BUS 341929 [2N LONDON 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 331 341740-342754(1) | OPEN LINE FROM BUS 341740 [2LAUREL CO 69.000] TO BUS 342754 [5LAUREL CO 161.00] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3978 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 332 341746-342253(1) | OPEN LINE FROM BUS 341746 [2LEBANON J 69.000] TO BUS 342253 [2SHEPHEVIL J69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 333 341749-342058(1) | OPEN LINE FROM BUS 341749 [2LEES LICK 69.000] TO BUS 342058 [2PENN 69.000] CKT 1 | -31.4821 | 31.4821 | 33 | 95.4002 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 334 341749-342133(1) | OPEN LINE FROM BUS 341749 [2LEES LICK 69.000] TO BUS 342133 [2RENAKER 69.000] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 335 341755-341758(1) | OPEN LINE FROM BUS 341755 [2LIBER CH T 69.000] TO BUS 341758 [2LIBERT CHUR69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 336 341761-341767(1) | OPEN LINE FROM BUS 341761 [2LIBERTY J 69.000] TO BUS 341767 [2LIBERTYKU T69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
341611 | 2HICKORY PL | 69 | 342103 | 2PPG | 69 | 1 | SINGLE OPN LIN 502 342430-342691(1) | OPEN LINE FROM BUS 342430 [2W BEREA 69.000] TO BUS 342691 [4W BEREA 138.00] CKT 1 | 52.9497 | 52.9497 | 46 | 115.1081 | EKPC
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 337 341761-341896(1) | OPEN LINE FROM BUS 341761 [2LIBERTY J 69.000] TO BUS 341896 [2MT OLIVE J 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 338 341761-342760(1) | OPEN LINE FROM BUS 341761 [2LIBERTY J 69.000] TO BUS 342760 [5LIBERTY J 161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 339 341764-341767(1) | OPEN LINE FROM BUS 341764 [2LIBERTY KU 69.000] TO BUS 341767 [2LIBERTYKU T69.000] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3988 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 340 341767-342064(1) | OPEN LINE FROM BUS 341767 [2LIBERTYKU T69.000] TO BUS 342064 [2PEYTONS ST 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
341611 | 2HICKORY PL | 69 | 342103 | 2PPG | 69 | 1 | SINGLE OPN LIN 536 342577-342691(1) | OPEN LINE FROM BUS 342577 [4FAWKES EK 138.00] TO BUS 342691 [4W BEREA 138.00] CKT 1 | 52.9492 | 52.9492 | 46 | 115.107 | EKPC
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 341 341772-341774(1) | OPEN LINE FROM BUS 341772 [2LOGAN 69.000] TO BUS 341774 [2LOGAN 2 T 69.000] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 342 341774-341775(1) | OPEN LINE FROM BUS 341774 [2LOGAN 2 T 69.000] TO BUS 341775 [2LOGAN TAP 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
341611 | 2HICKORY PL | 69 | 342103 | 2PPG | 69 | 1 | EKPC_P1-2_FAW-W BER 138 | EKPC_P1-2_FAW-W BER 138 | 52.9289 | 52.9289 | 46 | 115.0628 | EKPC
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 343 341775-342247(1) | OPEN LINE FROM BUS 341775 [2LOGAN TAP 69.000] TO BUS 342247 [2SHELBY CO 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324536 | 2FINCHVILLE | 69 | 324718 | 2SHELBY CO T | 69 | 1 | SINGLE OPN LIN 571 342700-342819(1) | OPEN LINE FROM BUS 342700 [5BULLITT CO 161.00] TO BUS 342819 [5TAYLORSV T 161.00] CKT 1 | 60.0021 | 60.0021 | 53 | 113.2115 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 344 341776-342208(1) | OPEN LINE FROM BUS 341776 [2LORETTO 69.000] TO BUS 342208 [2S SPRINGF T69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 345 341776-342316(1) | OPEN LINE FROM BUS 341776 [2LORETTO 69.000] TO BUS 342316 [2SULPHUR CRK69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.398 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 346 341779-341782(1) | OPEN LINE FROM BUS 341779 [2LOW GAP 69.000] TO BUS 341782 [2LOW GAP T 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 347 341782-342475(1) | OPEN LINE FROM BUS 341782 [2LOW GAP T 69.000] TO BUS 342475 [2WARNOCK 69.000] CKT 1 | -31.4829 | 31.4829 | 33 | 95.4027 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 348 341785-341788(1) | OPEN LINE FROM BUS 341785 [2LYMAN BW 69.000] TO BUS 341788 [2LYMAN BW T 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 349 341788-342155(1) | OPEN LINE FROM BUS 341788 [2LYMAN BW T 69.000] TO BUS 342155 [2ROANOKE T 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 350 341788-342379(1) | OPEN LINE FROM BUS 341788 [2LYMAN BW T 69.000] TO BUS 342379 [2TUNNEL H T 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 351 341791-341794(1) | OPEN LINE FROM BUS 341791 [2MACKVIL KU 69.000] TO BUS 341794 [2MACKVILKU T69.000] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3988 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 352 341794-341935(1) | OPEN LINE FROM BUS 341794 [2MACKVILKU T69.000] TO BUS 341935 [2N SPRINGFLD69.000] CKT 1 | -31.4812 | 31.4812 | 33 | 95.3976 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 353 341794-342061(1) | OPEN LINE FROM BUS 341794 [2MACKVILKU T69.000] TO BUS 342061 [2PERRYVILLE 69.000] CKT 1 | -31.4812 | 31.4812 | 33 | 95.3976 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 354 341797-342265(1) | OPEN LINE FROM BUS 341797 [2MAGGARD 69.000] TO BUS 342265 [2SKAGGS 69.000] CKT 1 | -31.4812 | 31.4812 | 33 | 95.3975 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 355 341800-342325(1) | OPEN LINE FROM BUS 341800 [2MAGNOLIA 69.000] TO BUS 342325 [2SUMMERSVIL 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 356 341803-342310(1) | OPEN LINE FROM BUS 341803 [2MAGOFFIN CO69.000] TO BUS 342310 [2SUBLETT 69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3979 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 357 341803-342313(1) | OPEN LINE FROM BUS 341803 [2MAGOFFIN CO69.000] TO BUS 342313 [2SUBLETT J 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 358 341809-341812(1) | OPEN LINE FROM BUS 341809 [2MAPLESVIL T69.000] TO BUS 341812 [2MAPLESVILLE69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 359 341809-341929(1) | OPEN LINE FROM BUS 341809 [2MAPLESVIL T69.000] TO BUS 341929 [2N LONDON 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 360 341815-341818(1) | OPEN LINE FROM BUS 341815 [2MARETBURG 69.000] TO BUS 341818 [2MARETBURG T69.000] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 361 341818-342472(1) | OPEN LINE FROM BUS 341818 [2MARETBURG T69.000] TO BUS 342472 [2WALNUT GROV69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 362 341821-341824(1) | OPEN LINE FROM BUS 341821 [2MARIBA 69.000] TO BUS 341824 [2MARIBA T 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 363 341824-341833(1) | OPEN LINE FROM BUS 341824 [2MARIBA T 69.000] TO BUS 341833 [2MAYTOWN T 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 364 341827-342343(1) | OPEN LINE FROM BUS 341827 [2MARTIN CO 69.000] TO BUS 342343 [2THELMA 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 365 341830-341833(1) | OPEN LINE FROM BUS 341830 [2MAYTOWN 69.000] TO BUS 341833 [2MAYTOWN T 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 366 341833-341890(1) | OPEN LINE FROM BUS 341833 [2MAYTOWN T 69.000] TO BUS 341890 [2MORGAN CO 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 367 341836-341953(1) | OPEN LINE FROM BUS 341836 [2MAZIE 69.000] TO BUS 341953 [2NEW FOUNDL 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 368 341836-342265(1) | OPEN LINE FROM BUS 341836 [2MAZIE 69.000] TO BUS 342265 [2SKAGGS 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 369 341839-341842(1) | OPEN LINE FROM BUS 341839 [2MBUSA 69.000] TO BUS 341842 [2MBUSA T 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 371 341845-342490(1) | OPEN LINE FROM BUS 341845 [2MCCREARY CO69.000] TO BUS 342490 [2WHITLEY CTY69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 372 341845-342778(1) | OPEN LINE FROM BUS 341845 [2MCCREARY CO69.000] TO BUS 342778 [5MCCREARY CO161.00] CKT 1 | -31.4813 | 31.4813 | 33 | 95.398 | LGEE
342000 | 5GAS | 161 | 342760 | 5LIBERTY J | 161 | 1 | SINGLE OPN LIN 597 342769-342775(1) | OPEN LINE FROM BUS 342769 [5MARION CO 161.00] TO BUS 342775 [5MARION IP T161.00] CKT 1 | 169.5256 | 169.5256 | 153 | 110.801 | EKPC
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 373 341848-342223(1) | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342223 [2SAND GAP T 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 374 341848-342391(1) | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | -31.4828 | 31.4828 | 33 | 95.4023 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 375 341851-341854(1) | OPEN LINE FROM BUS 341851 [2MCKINNEY 69.000] TO BUS 341854 [2MCKINNY T 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 376 341857-342406(1) | OPEN LINE FROM BUS 341857 [2MERCR IND 69.000] TO BUS 342406 [2VAN ARSDELL69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3979 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 377 341860-341863(1) | OPEN LINE FROM BUS 341860 [2MIDDL CRK T69.000] TO BUS 341863 [2MIDDLE CRK 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 378 341869-341875(1) | OPEN LINE FROM BUS 341869 [2MILL HUNT T69.000] TO BUS 341875 [2MILLER HUNT69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 379 341869-342259(1) | OPEN LINE FROM BUS 341869 [2MILL HUNT T69.000] TO BUS 342259 [2SIDEVIEW 69.000] CKT 1 | -31.4802 | 31.4802 | 33 | 95.3946 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 380 341872-341878(1) | OPEN LINE FROM BUS 341872 [2MILLB-CRL J69.000] TO BUS 341878 [2MILLERSB EK69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.398 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 381 341887-342268(1) | OPEN LINE FROM BUS 341887 [2MONTICELLO 69.000] TO BUS 342268 [2SLAT 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 382 341893-341896(1) | OPEN LINE FROM BUS 341893 [2MT OLIVE 69.000] TO BUS 341896 [2MT OLIVE J 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 383 341908-341914(1) | OPEN LINE FROM BUS 341908 [2MUNFVIL EK 69.000] TO BUS 341914 [2MUNFVILKU T69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 384 341911-341914(1) | OPEN LINE FROM BUS 341911 [2MUNFVIL KU 69.000] TO BUS 341914 [2MUNFVILKU T69.000] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 385 341917-341998(1) | OPEN LINE FROM BUS 341917 [2MUNK 69.000] TO BUS 341998 [2OAKLEY NOEL69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 386 341920-341998(1) | OPEN LINE FROM BUS 341920 [2MUNK J 69.000] TO BUS 341998 [2OAKLEY NOEL69.000] CKT 1 | -31.4809 | 31.4809 | 33 | 95.3967 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 387 341920-342502(1) | OPEN LINE FROM BUS 341920 [2MUNK J 69.000] TO BUS 342502 [2WILLIAMSTWN69.000] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 388 341923-342091(1) | OPEN LINE FROM BUS 341923 [2MURPHYSVIL 69.000] TO BUS 342091 [2PLUMVILLE 69.000] CKT 1 | -31.4812 | 31.4812 | 33 | 95.3975 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 389 341923-342280(1) | OPEN LINE FROM BUS 341923 [2MURPHYSVIL 69.000] TO BUS 342280 [2SNOW HILL 69.000] CKT 1 | -31.4807 | 31.4807 | 33 | 95.396 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 390 341935-342208(1) | OPEN LINE FROM BUS 341935 [2N SPRINGFLD69.000] TO BUS 342208 [2S SPRINGF T69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 391 341938-342505(1) | OPEN LINE FROM BUS 341938 [2NANCY 69.000] TO BUS 342505 [2WINDSOR 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 392 341938-342526(1) | OPEN LINE FROM BUS 341938 [2NANCY 69.000] TO BUS 342526 [2ZOLLICOF T 69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.398 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 393 341941-341947(1) | OPEN LINE FROM BUS 341941 [2NELSN VAL T69.000] TO BUS 341947 [2NELSON VAL 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 394 341941-341971(1) | OPEN LINE FROM BUS 341941 [2NELSN VAL T69.000] TO BUS 341971 [2NORWOOD 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 395 341944-342424(1) | OPEN LINE FROM BUS 341944 [2NELSON CO 69.000] TO BUS 342424 [2W BARDST J 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 396 341944-342514(1) | OPEN LINE FROM BUS 341944 [2NELSON CO 69.000] TO BUS 342514 [2WOOSLEY 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 397 341950-342007(1) | OPEN LINE FROM BUS 341950 [2NEW CASTLE 69.000] TO BUS 342007 [2OWEN CO 69.000] CKT 1 | -31.4819 | 31.4819 | 33 | 95.3998 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 398 341953-342229(1) | OPEN LINE FROM BUS 341953 [2NEW FOUNDL 69.000] TO BUS 342229 [2SANDY HOOK 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 399 341962-342361(1) | OPEN LINE FROM BUS 341962 [2NEWBY 2 69.000] TO BUS 342361 [2TODDVILLE T69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3979 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 400 341965-342199(1) | OPEN LINE FROM BUS 341965 [2NICHOLASVIL69.000] TO BUS 342199 [2S JESSAM J 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 401 341971-342115(1) | OPEN LINE FROM BUS 341971 [2NORWOOD 69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | -31.4812 | 31.4812 | 33 | 95.3975 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 402 341974-342256(1) | OPEN LINE FROM BUS 341974 [2NORWOOD T 69.000] TO BUS 342256 [2SHOPVILLE 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 403 341977-341983(1) | OPEN LINE FROM BUS 341977 [2OAK HILL 69.000] TO BUS 341983 [2OAK HILL T 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 404 341980-341983(1) | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 341983 [2OAK HILL T 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 405 341980-342286(1) | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 406 341983-342469(1) | OPEN LINE FROM BUS 341983 [2OAK HILL T 69.000] TO BUS 342469 [2W SOMERSET 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 407 341986-341989(1) | OPEN LINE FROM BUS 341986 [2OAK RIDGE 69.000] TO BUS 341989 [2OAK RIDGE T69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 408 342000-342703(1) | OPEN LINE FROM BUS 342000 [5GAS 161.00] TO BUS 342703 [5CASEY CO 161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
342000 | 5GAS | 161 | 342760 | 5LIBERTY J | 161 | 1 | B-161-128 | B-161-128 | 168.7386 | 168.7386 | 153 | 110.2866 | EKPC
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 409 342000-342760(1) | OPEN LINE FROM BUS 342000 [5GAS 161.00] TO BUS 342760 [5LIBERTY J 161.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
342000 | 5GAS | 161 | 342760 | 5LIBERTY J | 161 | 1 | EKPC_P1-2_GRE-TAY-MAR161 | EKPC_P1-2_GRE-TAY-MAR161 | 168.737 | 168.737 | 153 | 110.2856 | EKPC
342000 | 5GAS | 161 | 342760 | 5LIBERTY J | 161 | 1 | B-345-100 | B-345-100 | 167.9485 | 167.9485 | 153 | 109.7703 | EKPC
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 410 342007-342008(1) | OPEN LINE FROM BUS 342007 [2OWEN CO 69.000] TO BUS 342008 [4OWEN CO 138.00] CKT 1 | -31.4806 | 31.4806 | 33 | 95.3959 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 411 342007-342010(1) | OPEN LINE FROM BUS 342007 [2OWEN CO 69.000] TO BUS 342010 [2OWEN CO J1 69.000] CKT 1 | -31.481 | 31.481 | 33 | 95.397 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 412 342007-342013(1) | OPEN LINE FROM BUS 342007 [2OWEN CO 69.000] TO BUS 342013 [2OWEN CO J2 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 413 342016-342019(1) | OPEN LINE FROM BUS 342016 [2OWENS IL 69.000] TO BUS 342019 [2OWENS IL J 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 414 342022-342025(1) | OPEN LINE FROM BUS 342022 [2OWINGSVIL T69.000] TO BUS 342025 [2OWINGVIL KU69.000] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3988 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 415 342022-342052(1) | OPEN LINE FROM BUS 342022 [2OWINGSVIL T69.000] TO BUS 342052 [2PEASTICKS 69.000] CKT 1 | -31.4817 | 31.4817 | 33 | 95.3989 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 416 342022-342112(1) | OPEN LINE FROM BUS 342022 [2OWINGSVIL T69.000] TO BUS 342112 [2PRESTON T 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 417 342031-342034(1) | OPEN LINE FROM BUS 342031 [2PACTOLUS 69.000] TO BUS 342034 [2PACTOLUS T 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 418 342037-342040(1) | OPEN LINE FROM BUS 342037 [2PARKWAY 1 69.000] TO BUS 342040 [2PARKWAY 2 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 419 342049-342161(1) | OPEN LINE FROM BUS 342049 [2PATTON RD J69.000] TO BUS 342161 [2ROSEVILLE T69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 420 342049-342319(1) | OPEN LINE FROM BUS 342049 [2PATTON RD J69.000] TO BUS 342319 [2SUMM SHAD J69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 421 342067-342505(1) | OPEN LINE FROM BUS 342067 [2PHIL 69.000] TO BUS 342505 [2WINDSOR 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 422 342070-342073(1) | OPEN LINE FROM BUS 342070 [2PINE GROVE 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 423 342073-342451(1) | OPEN LINE FROM BUS 342073 [2PINE GRV T 69.000] TO BUS 342451 [2W LONDON 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 425 342085-342088(1) | OPEN LINE FROM BUS 342085 [2PLUMMR L 69.000] TO BUS 342088 [2PLUMMR L T 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 426 342091-342124(1) | OPEN LINE FROM BUS 342091 [2PLUMVILLE 69.000] TO BUS 342124 [2RECTORVILLE69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.398 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 427 342091-342634(1) | OPEN LINE FROM BUS 342091 [2PLUMVILLE 69.000] TO BUS 342634 [4PLUMVILLE 138.00] CKT 1 | -31.4813 | 31.4813 | 33 | 95.398 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 428 342097-342184(1) | OPEN LINE FROM BUS 342097 [2POWEL TAYL 69.000] TO BUS 342184 [2S ANDERSON 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 429 342100-342301(1) | OPEN LINE FROM BUS 342100 [2POWELL CO 69.000] TO BUS 342301 [2STANTON 69.000] CKT 1 | -31.4817 | 31.4817 | 33 | 95.399 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 430 342100-342637(1) | OPEN LINE FROM BUS 342100 [2POWELL CO 69.000] TO BUS 342637 [4POWELL CO 138.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 431 342103-342106(1) | OPEN LINE FROM BUS 342103 [2PPG 69.000] TO BUS 342106 [2PPG J 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 432 342109-342112(1) | OPEN LINE FROM BUS 342109 [2PRESTON 69.000] TO BUS 342112 [2PRESTON T 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 433 342115-342787(1) | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 434 342118-342121(1) | OPEN LINE FROM BUS 342118 [2RADCLIFF 69.000] TO BUS 342121 [2T BROWN L T69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 435 342121-342328(1) | OPEN LINE FROM BUS 342121 [2T BROWN L T69.000] TO BUS 342328 [2T BROWN LOG69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 436 342121-342415(1) | OPEN LINE FROM BUS 342121 [2T BROWN L T69.000] TO BUS 342415 [2VINE GROV J69.000] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3988 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 437 342127-342265(1) | OPEN LINE FROM BUS 342127 [2REDBUSH 69.000] TO BUS 342265 [2SKAGGS 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 438 342127-342421(1) | OPEN LINE FROM BUS 342127 [2REDBUSH 69.000] TO BUS 342421 [2VOLGA 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 439 342130-342259(1) | OPEN LINE FROM BUS 342130 [2REID VILLAG69.000] TO BUS 342259 [2SIDEVIEW 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 441 342133-342640(1) | OPEN LINE FROM BUS 342133 [2RENAKER 69.000] TO BUS 342640 [4RENAKER 138.00] CKT 1 | -31.4779 | 31.4779 | 33 | 95.3877 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 442 342136-342139(1) | OPEN LINE FROM BUS 342136 [2REVELO KU 69.000] TO BUS 342139 [2REVELO KU T69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 443 342145-342487(1) | OPEN LINE FROM BUS 342145 [2RICHARDSON 69.000] TO BUS 342487 [2WEBSTER RD 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 444 342154-342155(1) | OPEN LINE FROM BUS 342154 [2ROANOKE 69.000] TO BUS 342155 [2ROANOKE T 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 445 342157-342418(1) | OPEN LINE FROM BUS 342157 [2ROGERSVIL J69.000] TO BUS 342418 [2VINE GROVE 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 446 342160-342161(1) | OPEN LINE FROM BUS 342160 [2ROSEVILLE 69.000] TO BUS 342161 [2ROSEVILLE T69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 447 342161-342334(1) | OPEN LINE FROM BUS 342161 [2ROSEVILLE T69.000] TO BUS 342334 [2TEMPLE HILL69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 448 342163-342649(1) | OPEN LINE FROM BUS 342163 [2ROWAN CO 69.000] TO BUS 342649 [4ROWAN CO 138.00] CKT 1 | -31.4813 | 31.4813 | 33 | 95.398 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 449 342166-342169(1) | OPEN LINE FROM BUS 342166 [2RUSS SPEK T69.000] TO BUS 342169 [2RUSS SPKU T69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 450 342166-342172(1) | OPEN LINE FROM BUS 342166 [2RUSS SPEK T69.000] TO BUS 342172 [2RUSS SPR EK69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 451 342166-342235(1) | OPEN LINE FROM BUS 342166 [2RUSS SPEK T69.000] TO BUS 342235 [2SEWELTN J 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 452 342169-342175(1) | OPEN LINE FROM BUS 342169 [2RUSS SPKU T69.000] TO BUS 342175 [2RUSS SPR KU69.000] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 453 342169-342178(1) | OPEN LINE FROM BUS 342169 [2RUSS SPKU T69.000] TO BUS 342178 [2RUSSEL CO 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 454 342178-342232(1) | OPEN LINE FROM BUS 342178 [2RUSSEL CO 69.000] TO BUS 342232 [2SEWELLTON 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 455 342178-342793(1) | OPEN LINE FROM BUS 342178 [2RUSSEL CO 69.000] TO BUS 342793 [5RUSSEL CO 161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.398 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 456 342184-342262(1) | OPEN LINE FROM BUS 342184 [2S ANDERSON 69.000] TO BUS 342262 [2SINAI 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 457 342186-342424(1) | OPEN LINE FROM BUS 342186 [2S BARDSTWN 69.000] TO BUS 342424 [2W BARDST J 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 458 342186-342427(1) | OPEN LINE FROM BUS 342186 [2S BARDSTWN 69.000] TO BUS 342427 [2W BARDSTWN 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 459 342196-342391(1) | OPEN LINE FROM BUS 342196 [2WHITE OAK 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 460 342199-342202(1) | OPEN LINE FROM BUS 342199 [2S JESSAM J 69.000] TO BUS 342202 [2S JESSAMINE69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3979 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 461 342208-342211(1) | OPEN LINE FROM BUS 342208 [2S SPRINGF T69.000] TO BUS 342211 [2S SPRINGFLD69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 462 342214-342217(1) | OPEN LINE FROM BUS 342214 [2SALEM EK 69.000] TO BUS 342217 [2SALEM EK T 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 463 342217-342481(1) | OPEN LINE FROM BUS 342217 [2SALEM EK T 69.000] TO BUS 342481 [2WEBB CR R T69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 464 342217-342505(1) | OPEN LINE FROM BUS 342217 [2SALEM EK T 69.000] TO BUS 342505 [2WINDSOR 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 465 342220-342223(1) | OPEN LINE FROM BUS 342220 [2SAND GAP 69.000] TO BUS 342223 [2SAND GAP T 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 466 342235-342481(1) | OPEN LINE FROM BUS 342235 [2SEWELTN J 69.000] TO BUS 342481 [2WEBB CR R T69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 467 342238-342241(1) | OPEN LINE FROM BUS 342238 [2SEYMOUR 69.000] TO BUS 342241 [2SEYMOUR T 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 468 342247-342248(1) | OPEN LINE FROM BUS 342247 [2SHELBY CO 69.000] TO BUS 342248 [2SHELBY TAP 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 469 342247-342410(1) | OPEN LINE FROM BUS 342247 [2SHELBY CO 69.000] TO BUS 342410 [2VEECHDALE 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 470 342247-342808(1) | OPEN LINE FROM BUS 342247 [2SHELBY CO 69.000] TO BUS 342808 [5SHELBY CO 161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 471 342250-342253(1) | OPEN LINE FROM BUS 342250 [2SHEPHEVIL 69.000] TO BUS 342253 [2SHEPHEVIL J69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 472 342265-342658(1) | OPEN LINE FROM BUS 342265 [2SKAGGS 69.000] TO BUS 342658 [4SKAGGS 138.00] CKT 1 | -31.4811 | 31.4811 | 33 | 95.3973 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 473 342268-342478(1) | OPEN LINE FROM BUS 342268 [2SLAT 69.000] TO BUS 342478 [2WAYNE CO 69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.398 | LGEE
324536 | 2FINCHVILLE | 69 | 324718 | 2SHELBY CO T | 69 | 1 | SINGLE OPN LIN 768 324101-324134(1) | OPEN LINE FROM BUS 324101 [7BLUE LICK 345.00] TO BUS 324134 [5BLUE LICK 161.00] CKT 1 | 58.0081 | 58.0081 | 53 | 109.4492 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 474 342271-342274(1) | OPEN LINE FROM BUS 342271 [2SMITHRSVIL 69.000] TO BUS 342274 [2SMITHRVIL T69.000] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 475 342277-342283(1) | OPEN LINE FROM BUS 342277 [2SNOW 69.000] TO BUS 342283 [2SNOW T 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 476 342283-342322(1) | OPEN LINE FROM BUS 342283 [2SNOW T 69.000] TO BUS 342322 [2SUMM SHADE 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 477 342286-342287(1) | OPEN LINE FROM BUS 342286 [2SOMERSET 69.000] TO BUS 342287 [2SOMERSET KU69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 478 342292-342295(1) | OPEN LINE FROM BUS 342292 [2STANLEY PRK69.000] TO BUS 342295 [2STANLY P J169.000] CKT 1 | -31.481 | 31.481 | 33 | 95.3971 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 479 342292-342298(1) | OPEN LINE FROM BUS 342292 [2STANLEY PRK69.000] TO BUS 342298 [2STANLY P J269.000] CKT 1 | -31.4798 | 31.4798 | 33 | 95.3934 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 480 342292-342667(1) | OPEN LINE FROM BUS 342292 [2STANLEY PRK69.000] TO BUS 342667 [4STANLEY PRK138.00] CKT 1 | -31.4802 | 31.4802 | 33 | 95.3947 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 481 342307-342403(1) | OPEN LINE FROM BUS 342307 [2STEPHENSBRG69.000] TO BUS 342403 [2UPTON T 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 482 342307-342412(1) | OPEN LINE FROM BUS 342307 [2STEPHENSBRG69.000] TO BUS 342412 [2VERTREES 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 483 342319-342322(1) | OPEN LINE FROM BUS 342319 [2SUMM SHAD J69.000] TO BUS 342322 [2SUMM SHADE 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 484 342319-342334(1) | OPEN LINE FROM BUS 342319 [2SUMM SHAD J69.000] TO BUS 342334 [2TEMPLE HILL69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 485 342322-342436(1) | OPEN LINE FROM BUS 342322 [2SUMM SHADE 69.000] TO BUS 342436 [2W COLUMBI T69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 486 342322-342814(1) | OPEN LINE FROM BUS 342322 [2SUMM SHADE 69.000] TO BUS 342814 [5SUMM SHADE 161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 487 342337-342340(1) | OPEN LINE FROM BUS 342337 [2THARP 69.000] TO BUS 342340 [2THARP T 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 488 342343-342421(1) | OPEN LINE FROM BUS 342343 [2THELMA 69.000] TO BUS 342421 [2VOLGA 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 489 342349-342433(1) | OPEN LINE FROM BUS 342349 [2THREE LNK J69.000] TO BUS 342433 [2W BEREA J 69.000] CKT 1 | -31.4822 | 31.4822 | 33 | 95.4005 | LGEE
324536 | 2FINCHVILLE | 69 | 324718 | 2SHELBY CO T | 69 | 1 | SINGLE OPN LIN 817 324134-326975(1) | OPEN LINE FROM BUS 324134 [5BLUE LICK 161.00] TO BUS 326975 [5CEDAR GRV 161.00] CKT 1 | 57.9979 | 57.9979 | 53 | 109.4301 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 490 342352-342355(1) | OPEN LINE FROM BUS 342352 [2THREE M 69.000] TO BUS 342355 [2THREE M T 69.000] CKT 1 | -31.4806 | 31.4806 | 33 | 95.3957 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 491 342358-342361(1) | OPEN LINE FROM BUS 342358 [2TODDVILLE 69.000] TO BUS 342361 [2TODDVILLE T69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 492 342364-342367(1) | OPEN LINE FROM BUS 342364 [2TOMM GOOC 69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 493 342367-942410(1) | OPEN LINE FROM BUS 342367 [2TOMM GOOC T69.000] TO BUS 942410 [AE2-254 TAP 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324536 | 2FINCHVILLE | 69 | 324718 | 2SHELBY CO T | 69 | 1 | B-345-102 | B-345-102 | 57.6329 | 57.6329 | 53 | 108.7413 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 494 342379-342382(1) | OPEN LINE FROM BUS 342379 [2TUNNEL H T 69.000] TO BUS 342382 [2TUNNEL HILL69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 495 342385-342487(1) | OPEN LINE FROM BUS 342385 [2TURKEY FT 69.000] TO BUS 342487 [2WEBSTER RD 69.000] CKT 1 | -31.4812 | 31.4812 | 33 | 95.3976 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 496 342391-342820(1) | OPEN LINE FROM BUS 342391 [2TYNER 69.000] TO BUS 342820 [5TYNER 161.00] CKT 1 | -31.481 | 31.481 | 33 | 95.3971 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 497 342394-342397(1) | OPEN LINE FROM BUS 342394 [2UPCHURCH 69.000] TO BUS 342397 [2UPCHURCH T 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 498 342397-342532(1) | OPEN LINE FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 499 342400-342403(1) | OPEN LINE FROM BUS 342400 [2UPTON 69.000] TO BUS 342403 [2UPTON T 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 500 342415-342418(1) | OPEN LINE FROM BUS 342415 [2VINE GROV J69.000] TO BUS 342418 [2VINE GROVE 69.000] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3988 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 501 342430-342433(1) | OPEN LINE FROM BUS 342430 [2W BEREA 69.000] TO BUS 342433 [2W BEREA J 69.000] CKT 1 | -31.4822 | 31.4822 | 33 | 95.4005 | LGEE
342000 | 5GAS | 161 | 342760 | 5LIBERTY J | 161 | 1 | SINGLE OPN LIN 765 324100-324130(1) | OPEN LINE FROM BUS 324100 [7ALCALDE 345.00] TO BUS 324130 [5ALCALDE 161.00] CKT 1 | 164.8475 | 164.8475 | 153 | 107.7435 | EKPC
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 502 342430-342691(1) | OPEN LINE FROM BUS 342430 [2W BEREA 69.000] TO BUS 342691 [4W BEREA 138.00] CKT 1 | -31.4809 | 31.4809 | 33 | 95.3968 | LGEE
324788 | 2BROOKS EK T | 69 | 324809 | 2BROOKS EKPC | 69 | 1 | B-69-316A | B-69-316A | 62.329 | 62.329 | 58 | 107.4638 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 503 342436-342439(1) | OPEN LINE FROM BUS 342436 [2W COLUMBI T69.000] TO BUS 342439 [2W COLUMBIA 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 504 342442-342445(1) | OPEN LINE FROM BUS 342442 [2W GLASGOW 69.000] TO BUS 342445 [2W GLASGOW T69.000] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 505 342460-342463(1) | OPEN LINE FROM BUS 342460 [2W NICHVIL 69.000] TO BUS 342463 [2W NICHVIL T69.000] CKT 1 | -31.4811 | 31.4811 | 33 | 95.3972 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 506 342469-342526(1) | OPEN LINE FROM BUS 342469 [2W SOMERSET 69.000] TO BUS 342526 [2ZOLLICOF T 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 507 342472-342511(1) | OPEN LINE FROM BUS 342472 [2WALNUT GROV69.000] TO BUS 342511 [2WOODSTOCK 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 508 342478-342532(1) | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 509 342478-342535(1) | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342535 [2ZULA T 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 510 342478-342823(1) | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | -31.4813 | 31.4813 | 33 | 95.398 | LGEE
342000 | 5GAS | 161 | 342760 | 5LIBERTY J | 161 | 1 | SINGLE OPN LIN 807 324130-324141(1) | OPEN LINE FROM BUS 324130 [5ALCALDE 161.00] TO BUS 324141 [5ELIHU 161.00] CKT 1 | 163.316 | 163.316 | 153 | 106.7425 | EKPC
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 511 342481-342484(1) | OPEN LINE FROM BUS 342481 [2WEBB CR R T69.000] TO BUS 342484 [2WEBB CR RDS69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 512 342490-342493(1) | OPEN LINE FROM BUS 342490 [2WHITLEY CTY69.000] TO BUS 342493 [2WHITLY C KU69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 513 342490-342499(1) | OPEN LINE FROM BUS 342490 [2WHITLEY CTY69.000] TO BUS 342499 [2WIBORG T 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 514 342496-342499(1) | OPEN LINE FROM BUS 342496 [2WIBORG 69.000] TO BUS 342499 [2WIBORG T 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 515 342523-342526(1) | OPEN LINE FROM BUS 342523 [2ZOLLICOF 69.000] TO BUS 342526 [2ZOLLICOF T 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 516 342529-342535(1) | OPEN LINE FROM BUS 342529 [2ZULA 69.000] TO BUS 342535 [2ZULA T 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 517 342538-342616(1) | OPEN LINE FROM BUS 342538 [4ARGENTUM 138.00] TO BUS 342616 [4LOVE HYDRO 138.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 518 342541-342544(1) | OPEN LINE FROM BUS 342541 [4AVON 138.00] TO BUS 342544 [4AVON-R 138.00] CKT 1 | -31.481 | 31.481 | 33 | 95.3969 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 519 342541-342556(1) | OPEN LINE FROM BUS 342541 [4AVON 138.00] TO BUS 342556 [4BECKNERV T 138.00] CKT 1 | -31.4833 | 31.4833 | 33 | 95.4039 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 520 342541-342580(1) | OPEN LINE FROM BUS 342541 [4AVON 138.00] TO BUS 342580 [4FAYETTE 138.00] CKT 1 | -31.4811 | 31.4811 | 33 | 95.3971 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 521 342541-342631(1) | OPEN LINE FROM BUS 342541 [4AVON 138.00] TO BUS 342631 [4PARIS T 138.00] CKT 1 | -31.485 | 31.485 | 33 | 95.4092 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 522 342541-342829(1) | OPEN LINE FROM BUS 342541 [4AVON 138.00] TO BUS 342829 [7AVON 345.00] CKT 1 | -31.4859 | 31.4859 | 33 | 95.4117 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 523 342550-342559(1) | OPEN LINE FROM BUS 342550 [4BAVARIAN LF138.00] TO BUS 342559 [4BOONE CO 138.00] CKT 1 | -31.4803 | 31.4803 | 33 | 95.3949 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 524 342550-342640(1) | OPEN LINE FROM BUS 342550 [4BAVARIAN LF138.00] TO BUS 342640 [4RENAKER 138.00] CKT 1 | -31.4803 | 31.4803 | 33 | 95.395 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 525 342553-342556(1) | OPEN LINE FROM BUS 342553 [4BECKNERV 138.00] TO BUS 342556 [4BECKNERV T 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 526 342556-342565(1) | OPEN LINE FROM BUS 342556 [4BECKNERV T 138.00] TO BUS 342565 [4BOONESBOR T138.00] CKT 1 | -31.4833 | 31.4833 | 33 | 95.4038 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 527 342559-342646(1) | OPEN LINE FROM BUS 342559 [4BOONE CO 138.00] TO BUS 342646 [4RICHWOOD T 138.00] CKT 1 | -31.4825 | 31.4825 | 33 | 95.4017 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 528 342559-342673(1) | OPEN LINE FROM BUS 342559 [4BOONE CO 138.00] TO BUS 342673 [4STERLNG T 138.00] CKT 1 | -31.4812 | 31.4812 | 33 | 95.3976 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 529 342565-342574(1) | OPEN LINE FROM BUS 342565 [4BOONESBOR T138.00] TO BUS 342574 [4DALE 138.00] CKT 1 | -31.4824 | 31.4824 | 33 | 95.4012 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 530 342571-342589(1) | OPEN LINE FROM BUS 342571 [4CRANSTON 138.00] TO BUS 342589 [4GODDARD 138.00] CKT 1 | -31.4818 | 31.4818 | 33 | 95.3992 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 531 342571-342649(1) | OPEN LINE FROM BUS 342571 [4CRANSTON 138.00] TO BUS 342649 [4ROWAN CO 138.00] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 532 342574-342596(1) | OPEN LINE FROM BUS 342574 [4DALE 138.00] TO BUS 342596 [4HUNT 138.00] CKT 1 | -31.4823 | 31.4823 | 33 | 95.401 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 533 342574-342676(1) | OPEN LINE FROM BUS 342574 [4DALE 138.00] TO BUS 342676 [4THREE FK T 138.00] CKT 1 | -31.4812 | 31.4812 | 33 | 95.3975 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 534 342577-342607(1) | OPEN LINE FROM BUS 342577 [4FAWKES EK 138.00] TO BUS 342607 [4JK SMITH 138.00] CKT 1 | -31.4819 | 31.4819 | 33 | 95.3996 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 535 342577-342676(1) | OPEN LINE FROM BUS 342577 [4FAWKES EK 138.00] TO BUS 342676 [4THREE FK T 138.00] CKT 1 | -31.4812 | 31.4812 | 33 | 95.3976 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 536 342577-342691(1) | OPEN LINE FROM BUS 342577 [4FAWKES EK 138.00] TO BUS 342691 [4W BEREA 138.00] CKT 1 | -31.481 | 31.481 | 33 | 95.3969 | LGEE
324536 | 2FINCHVILLE | 69 | 324718 | 2SHELBY CO T | 69 | 1 | SINGLE OPN LIN 595 342766-342819(1) | OPEN LINE FROM BUS 342766 [5LITTLE MT T161.00] TO BUS 342819 [5TAYLORSV T 161.00] CKT 1 | 56.3541 | 56.3541 | 53 | 106.3286 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 537 342583-342589(1) | OPEN LINE FROM BUS 342583 [4FLEMINGSBRG138.00] TO BUS 342589 [4GODDARD 138.00] CKT 1 | -31.4816 | 31.4817 | 33 | 95.3989 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 538 342583-342664(1) | OPEN LINE FROM BUS 342583 [4FLEMINGSBRG138.00] TO BUS 342664 [4SPURLOCK 138.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 539 342586-342587(1) | OPEN LINE FROM BUS 342586 [4GALLATIN CO138.00] TO BUS 342587 [1GALLATIN CO34.500] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 540 342586-342673(1) | OPEN LINE FROM BUS 342586 [4GALLATIN CO138.00] TO BUS 342673 [4STERLNG T 138.00] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3977 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 541 342589-342634(1) | OPEN LINE FROM BUS 342589 [4GODDARD 138.00] TO BUS 342634 [4PLUMVILLE 138.00] CKT 1 | -31.4812 | 31.4812 | 33 | 95.3977 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 542 342596-342607(1) | OPEN LINE FROM BUS 342596 [4HUNT 138.00] TO BUS 342607 [4JK SMITH 138.00] CKT 1 | -31.4828 | 31.4828 | 33 | 95.4023 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 543 342598-342664(1) | OPEN LINE FROM BUS 342598 [4INLAND C T 138.00] TO BUS 342664 [4SPURLOCK 138.00] CKT 1 | -31.4812 | 31.4812 | 33 | 95.3976 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 544 342601-342604(1) | OPEN LINE FROM BUS 342601 [4JACKSNVIL 138.00] TO BUS 342604 [4JACKSNVIL T138.00] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3979 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 545 342604-342631(1) | OPEN LINE FROM BUS 342604 [4JACKSNVIL T138.00] TO BUS 342631 [4PARIS T 138.00] CKT 1 | -31.4811 | 31.4811 | 33 | 95.3973 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 546 342604-342640(1) | OPEN LINE FROM BUS 342604 [4JACKSNVIL T138.00] TO BUS 342640 [4RENAKER 138.00] CKT 1 | -31.4812 | 31.4812 | 33 | 95.3976 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 547 342607-342610(1) | OPEN LINE FROM BUS 342607 [4JK SMITH 138.00] TO BUS 342610 [4JK SMITH 21138.00] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3979 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 548 342607-342613(1) | OPEN LINE FROM BUS 342607 [4JK SMITH 138.00] TO BUS 342613 [4JK SMITH 22138.00] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3979 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 549 342607-342637(1) | OPEN LINE FROM BUS 342607 [4JK SMITH 138.00] TO BUS 342637 [4POWELL CO 138.00] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 550 342607-342688(1) | OPEN LINE FROM BUS 342607 [4JK SMITH 138.00] TO BUS 342688 [4UNION CTY T138.00] CKT 1 | -31.4819 | 31.4819 | 33 | 95.3997 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 551 342610-342832(1) | OPEN LINE FROM BUS 342610 [4JK SMITH 21138.00] TO BUS 342832 [7JK SMITH 345.00] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3979 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 552 342613-342832(1) | OPEN LINE FROM BUS 342613 [4JK SMITH 22138.00] TO BUS 342832 [7JK SMITH 345.00] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3979 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 553 342622-342625(1) | OPEN LINE FROM BUS 342622 [4MAYSVIL I T138.00] TO BUS 342625 [4MAYSVIL IND138.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 554 342622-342634(1) | OPEN LINE FROM BUS 342622 [4MAYSVIL I T138.00] TO BUS 342634 [4PLUMVILLE 138.00] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3989 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 555 342622-342664(1) | OPEN LINE FROM BUS 342622 [4MAYSVIL I T138.00] TO BUS 342664 [4SPURLOCK 138.00] CKT 1 | -31.4817 | 31.4817 | 33 | 95.3992 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 556 342637-342784(1) | OPEN LINE FROM BUS 342637 [4POWELL CO 138.00] TO BUS 342784 [5POWELL CO 161.00] CKT 1 | -31.4813 | 31.4813 | 33 | 95.398 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 557 342640-342664(1) | OPEN LINE FROM BUS 342640 [4RENAKER 138.00] TO BUS 342664 [4SPURLOCK 138.00] CKT 1 | -31.4819 | 31.4819 | 33 | 95.3998 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 558 342643-342646(1) | OPEN LINE FROM BUS 342643 [4RICHWOOD 138.00] TO BUS 342646 [4RICHWOOD T 138.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 559 342646-342667(1) | OPEN LINE FROM BUS 342646 [4RICHWOOD T 138.00] TO BUS 342667 [4STANLEY PRK138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 560 342649-342658(1) | OPEN LINE FROM BUS 342649 [4ROWAN CO 138.00] TO BUS 342658 [4SKAGGS 138.00] CKT 1 | -31.4812 | 31.4812 | 33 | 95.3976 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 561 342661-342664(1) | OPEN LINE FROM BUS 342661 [4SPUR-KENT-R138.00] TO BUS 342664 [4SPURLOCK 138.00] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3977 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 562 342664-342667(1) | OPEN LINE FROM BUS 342664 [4SPURLOCK 138.00] TO BUS 342667 [4STANLEY PRK138.00] CKT 1 | -31.4811 | 31.4811 | 33 | 95.3974 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 563 342664-342838(1) | OPEN LINE FROM BUS 342664 [4SPURLOCK 138.00] TO BUS 342838 [7SPURLOCK 345.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 564 342664-342838(2) | OPEN LINE FROM BUS 342664 [4SPURLOCK 138.00] TO BUS 342838 [7SPURLOCK 345.00] CKT 2 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 565 342664-342838(3) | OPEN LINE FROM BUS 342664 [4SPURLOCK 138.00] TO BUS 342838 [7SPURLOCK 345.00] CKT 3 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 566 342670-342673(1) | OPEN LINE FROM BUS 342670 [4STERLING 138.00] TO BUS 342673 [4STERLNG T 138.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 567 342676-342679(1) | OPEN LINE FROM BUS 342676 [4THREE FK T 138.00] TO BUS 342679 [4THREE FORKS138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 568 342685-342688(1) | OPEN LINE FROM BUS 342685 [4UNION CITY 138.00] TO BUS 342688 [4UNION CTY T138.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 569 342694-342814(1) | OPEN LINE FROM BUS 342694 [5BARREN CO 161.00] TO BUS 342814 [5SUMM SHADE 161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 570 342697-342780(1) | OPEN LINE FROM BUS 342697 [5BEATTYV J 161.00] TO BUS 342780 [5MILL CRK T 161.00] CKT 1 | -31.4813 | 31.4813 | 33 | 95.398 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 571 342700-342819(1) | OPEN LINE FROM BUS 342700 [5BULLITT CO 161.00] TO BUS 342819 [5TAYLORSV T 161.00] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3979 | LGEE
342000 | 5GAS | 161 | 342760 | 5LIBERTY J | 161 | 1 | SINGLE OPN LIN 596 342769-342770(1) | OPEN LINE FROM BUS 342769 [5MARION CO 161.00] TO BUS 342770 [4MARION CO 138.00] CKT 1 | 161.7478 | 161.7478 | 153 | 105.7175 | EKPC
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 572 342703-342769(1) | OPEN LINE FROM BUS 342703 [5CASEY CO 161.00] TO BUS 342769 [5MARION CO 161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
342000 | 5GAS | 161 | 342760 | 5LIBERTY J | 161 | 1 | SINGLE OPN TIE 695 342770-324271(1) | OPEN LINE FROM BUS 342770 [4MARION CO 138.00] TO BUS 324271 [4LEBANON 138.00] CKT 1 | 161.7404 | 161.7404 | 153 | 105.7127 | EKPC
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 573 342715-342718(1) | OPEN LINE FROM BUS 342715 [5COOPER1 161.00] TO BUS 342718 [5COOPER2 161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 574 342715-342790(1) | OPEN LINE FROM BUS 342715 [5COOPER1 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | -31.4813 | 31.4813 | 33 | 95.398 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 575 342715-342799(1) | OPEN LINE FROM BUS 342715 [5COOPER1 161.00] TO BUS 342799 [5S OAKHILL 161.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
342000 | 5GAS | 161 | 342760 | 5LIBERTY J | 161 | 1 | B-69-25 | B-69-25 | 160.9766 | 160.9767 | 153 | 105.2135 | EKPC
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 576 342718-342727(1) | OPEN LINE FROM BUS 342718 [5COOPER2 161.00] TO BUS 342727 [5DENNY 161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 577 342718-342757(1) | OPEN LINE FROM BUS 342718 [5COOPER2 161.00] TO BUS 342757 [5LAUREL DAM 161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 578 342721-342724(1) | OPEN LINE FROM BUS 342721 [5DARWIN TH 161.00] TO BUS 342724 [5DARWIN TH T161.00] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3988 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 579 342724-342766(1) | OPEN LINE FROM BUS 342724 [5DARWIN TH T161.00] TO BUS 342766 [5LITTLE MT T161.00] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3979 | LGEE
324536 | 2FINCHVILLE | 69 | 324718 | 2SHELBY CO T | 69 | 1 | EKPC_P1-2_BULL-BLUE L161 | EKPC_P1-2_BULL-BLUE L161 | 55.5281 | 55.5281 | 53 | 104.77 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 580 342724-342808(1) | OPEN LINE FROM BUS 342724 [5DARWIN TH T161.00] TO BUS 342808 [5SHELBY CO 161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 581 342730-342820(1) | OPEN LINE FROM BUS 342730 [5FALL ROCK 161.00] TO BUS 342820 [5TYNER 161.00] CKT 1 | -31.4809 | 31.4809 | 33 | 95.3966 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 582 342733-342814(1) | OPEN LINE FROM BUS 342733 [5GREEN CO 161.00] TO BUS 342814 [5SUMM SHADE 161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 583 342733-342817(1) | OPEN LINE FROM BUS 342733 [5GREEN CO 161.00] TO BUS 342817 [5TAYLOR CO J161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 584 342736-342739(1) | OPEN LINE FROM BUS 342736 [5GREEN HAL T161.00] TO BUS 342739 [5GREEN HALL 161.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 585 342736-342820(1) | OPEN LINE FROM BUS 342736 [5GREEN HAL T161.00] TO BUS 342820 [5TYNER 161.00] CKT 1 | -31.4811 | 31.4811 | 33 | 95.3974 | LGEE
324536 | 2FINCHVILLE | 69 | 324718 | 2SHELBY CO T | 69 | 1 | SINGLE OPN TIE 689 342700-326975(1) | OPEN LINE FROM BUS 342700 [5BULLITT CO 161.00] TO BUS 326975 [5CEDAR GRV 161.00] CKT 1 | 55.3678 | 55.3678 | 53 | 104.4675 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 586 342742-342745(1) | OPEN LINE FROM BUS 342742 [5JABEZ 161.00] TO BUS 342745 [5JABEZ T 161.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 587 342745-342751(1) | OPEN LINE FROM BUS 342745 [5JABEZ T 161.00] TO BUS 342751 [5JAMESTOWN T161.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
342000 | 5GAS | 161 | 342760 | 5LIBERTY J | 161 | 1 | SINGLE OPN LIN 126 341269-342703(1) | OPEN LINE FROM BUS 341269 [2CASEY CO 69.000] TO BUS 342703 [5CASEY CO 161.00] CKT 1 | 159.4585 | 159.4585 | 153 | 104.2212 | EKPC
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 588 342745-342799(1) | OPEN LINE FROM BUS 342745 [5JABEZ T 161.00] TO BUS 342799 [5S OAKHILL 161.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324434 | 2BEREA TAP | 69 | 324612 | 2LAKE REBA | 69 | 1 | SINGLE OPN LIN 1603 324700-324938(1) | OPEN LINE FROM BUS 324700 [2RICHMND SO 69.000] TO BUS 324938 [2RICHMND 3 69.000] CKT 1 | -85.0828 | 85.0828 | 82 | 103.7595 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 589 342748-342751(1) | OPEN LINE FROM BUS 342748 [5JAMESTOWN 161.00] TO BUS 342751 [5JAMESTOWN T161.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 590 342751-342796(1) | OPEN LINE FROM BUS 342751 [5JAMESTOWN T161.00] TO BUS 342796 [5RUSSEL CO J161.00] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
342000 | 5GAS | 161 | 342760 | 5LIBERTY J | 161 | 1 | SINGLE OPN LIN 600 342775-342805(1) | OPEN LINE FROM BUS 342775 [5MARION IP T161.00] TO BUS 342805 [5SALOMA T 161.00] CKT 1 | 158.4776 | 158.4776 | 153 | 103.5802 | EKPC
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 591 342754-342757(1) | OPEN LINE FROM BUS 342754 [5LAUREL CO 161.00] TO BUS 342757 [5LAUREL DAM 161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 592 342754-342781(1) | OPEN LINE FROM BUS 342754 [5LAUREL CO 161.00] TO BUS 342781 [5PITTSBURG 161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 593 342760-342790(1) | OPEN LINE FROM BUS 342760 [5LIBERTY J 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
342000 | 5GAS | 161 | 342760 | 5LIBERTY J | 161 | 1 | SINGLE OPN TIE 700 342796-360448(1) | OPEN LINE FROM BUS 342796 [5RUSSEL CO J161.00] TO BUS 360448 [5WOLF CRK HP161.00] CKT 1 | 157.9974 | 157.9974 | 153 | 103.2662 | EKPC
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 594 342763-342766(1) | OPEN LINE FROM BUS 342763 [5LITTLE MT 161.00] TO BUS 342766 [5LITTLE MT T161.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 595 342766-342819(1) | OPEN LINE FROM BUS 342766 [5LITTLE MT T161.00] TO BUS 342819 [5TAYLORSV T 161.00] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3979 | LGEE
324536 | 2FINCHVILLE | 69 | 324718 | 2SHELBY CO T | 69 | 1 | SINGLE OPN LIN 579 342724-342766(1) | OPEN LINE FROM BUS 342724 [5DARWIN TH T161.00] TO BUS 342766 [5LITTLE MT T161.00] CKT 1 | 54.5225 | 54.5225 | 53 | 102.8727 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 596 342769-342770(1) | OPEN LINE FROM BUS 342769 [5MARION CO 161.00] TO BUS 342770 [4MARION CO 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
342000 | 5GAS | 161 | 342760 | 5LIBERTY J | 161 | 1 | SINGLE OPN LIN 125 341269-342064(1) | OPEN LINE FROM BUS 341269 [2CASEY CO 69.000] TO BUS 342064 [2PEYTONS ST 69.000] CKT 1 | 156.3129 | 156.3129 | 153 | 102.1653 | EKPC
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 597 342769-342775(1) | OPEN LINE FROM BUS 342769 [5MARION CO 161.00] TO BUS 342775 [5MARION IP T161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
342000 | 5GAS | 161 | 342760 | 5LIBERTY J | 161 | 1 | SINGLE OPN LIN 763 324100-324102(1) | OPEN LINE FROM BUS 324100 [7ALCALDE 345.00] TO BUS 324102 [7BROWN NORTH345.00] CKT 1 | 155.7938 | 155.7938 | 153 | 101.826 | EKPC
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 598 342772-342797(1) | OPEN LINE FROM BUS 342772 [5MARION IP 161.00] TO BUS 342797 [5S MARION IT161.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 599 342775-342797(1) | OPEN LINE FROM BUS 342775 [5MARION IP T161.00] TO BUS 342797 [5S MARION IT161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
342000 | 5GAS | 161 | 342760 | 5LIBERTY J | 161 | 1 | B-69-18 | B-69-18 | 155.0387 | 155.0387 | 153 | 101.3325 | EKPC
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 600 342775-342805(1) | OPEN LINE FROM BUS 342775 [5MARION IP T161.00] TO BUS 342805 [5SALOMA T 161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
342000 | 5GAS | 161 | 342760 | 5LIBERTY J | 161 | 1 | SINGLE OPN LIN 608 342805-342817(1) | OPEN LINE FROM BUS 342805 [5SALOMA T 161.00] TO BUS 342817 [5TAYLOR CO J161.00] CKT 1 | 154.9729 | 154.9729 | 153 | 101.2895 | EKPC
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 601 342779-342780(1) | OPEN LINE FROM BUS 342779 [5MILLER CRK 161.00] TO BUS 342780 [5MILL CRK T 161.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 602 342780-342784(1) | OPEN LINE FROM BUS 342780 [5MILL CRK T 161.00] TO BUS 342784 [5POWELL CO 161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 603 342781-342820(1) | OPEN LINE FROM BUS 342781 [5PITTSBURG 161.00] TO BUS 342820 [5TYNER 161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 604 342787-342790(1) | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 605 342793-342796(1) | OPEN LINE FROM BUS 342793 [5RUSSEL CO 161.00] TO BUS 342796 [5RUSSEL CO J161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 606 342797-342798(1) | OPEN LINE FROM BUS 342797 [5S MARION IT161.00] TO BUS 342798 [5S MARION IP161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
342703 | 5CASEY CO | 161 | 342769 | 5MARION CO | 161 | 1 | SINGLE OPN LIN 409 342000-342760(1) | OPEN LINE FROM BUS 342000 [5GAS 161.00] TO BUS 342760 [5LIBERTY J 161.00] CKT 1 | -154.7204 | 154.7204 | 153 | 101.1244 | EKPC
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 607 342802-342805(1) | OPEN LINE FROM BUS 342802 [5SALOMA 161.00] TO BUS 342805 [5SALOMA T 161.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 608 342805-342817(1) | OPEN LINE FROM BUS 342805 [5SALOMA T 161.00] TO BUS 342817 [5TAYLOR CO J161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324718 | 2SHELBY CO T | 69 | 324726 | 2SHELBYVIL S | 69 | 1 | SINGLE OPN LIN 106 341212-341774(1) | OPEN LINE FROM BUS 341212 [2BUDD 69.000] TO BUS 341774 [2LOGAN 2 T 69.000] CKT 1 | 49.3507 | 49.3507 | 49 | 100.7158 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 609 342818-342819(1) | OPEN LINE FROM BUS 342818 [5TAYLORSVILL161.00] TO BUS 342819 [5TAYLORSV T 161.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 610 342829-342835(1) | OPEN LINE FROM BUS 342829 [7AVON 345.00] TO BUS 342835 [7N CLARK 345.00] CKT 1 | -31.486 | 31.486 | 33 | 95.4121 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 611 342832-342835(1) | OPEN LINE FROM BUS 342832 [7JK SMITH 345.00] TO BUS 342835 [7N CLARK 345.00] CKT 1 | -31.4811 | 31.4811 | 33 | 95.3971 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 612 342832-342841(1) | OPEN LINE FROM BUS 342832 [7JK SMITH 345.00] TO BUS 342841 [7W GARRARDEK345.00] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3989 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 613 342835-342838(1) | OPEN LINE FROM BUS 342835 [7N CLARK 345.00] TO BUS 342838 [7SPURLOCK 345.00] CKT 1 | -31.4837 | 31.4837 | 33 | 95.4052 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 614 942410-942411(1) | OPEN LINE FROM BUS 942410 [AE2-254 TAP 69.000] TO BUS 942411 [AE2-254 C O169.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 615 942411-942412(1) | OPEN LINE FROM BUS 942411 [AE2-254 C O169.000] TO BUS 942412 [AE2-254 E O169.000] CKT 1 | -31.4814 | 31.4815 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 616 341020-243725(1) | OPEN LINE FROM BUS 341020 [2ARGENTUM 69.000] TO BUS 243725 [05GRAYSB 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 617 341071-324430(1) | OPEN LINE FROM BUS 341071 [2BEATTYV 69.000] TO BUS 324430 [2BEATTYVI KU69.000] CKT 1 | -31.4812 | 31.4812 | 33 | 95.3977 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 618 341089-325102(1) | OPEN LINE FROM BUS 341089 [2BEKAERT 69.000] TO BUS 325102 [2W SHELBY 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 619 341161-324213(1) | OPEN LINE FROM BUS 341161 [2BONNIV EK 69.000] TO BUS 324213 [4BONNIEVILLE138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 620 341188-324463(1) | OPEN LINE FROM BUS 341188 [2BRACKEN CO 69.000] TO BUS 324463 [2CARNTOWN 69.000] CKT 1 | -31.4805 | 31.4805 | 33 | 95.3955 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 621 341188-324722(1) | OPEN LINE FROM BUS 341188 [2BRACKEN CO 69.000] TO BUS 324722 [2SHARON KU 69.000] CKT 1 | -31.4812 | 31.4812 | 33 | 95.3974 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 622 341317-324474(1) | OPEN LINE FROM BUS 341317 [2CLAY VILLAG69.000] TO BUS 324474 [2CLAY VILG T69.000] CKT 1 | -31.4827 | 31.4827 | 33 | 95.402 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 623 341320-324830(1) | OPEN LINE FROM BUS 341320 [2COBURG 69.000] TO BUS 324830 [2CAMPBELV EK69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 624 341406-324530(1) | OPEN LINE FROM BUS 341406 [2DUNCAN LN T69.000] TO BUS 324530 [2FAWKES 69.000] CKT 1 | -31.4809 | 31.4809 | 33 | 95.3968 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 625 341407-324425(1) | OPEN LINE FROM BUS 341407 [2E BARDSTOWN69.000] TO BUS 324425 [2BARDT IND T69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 626 341461-243721(Z1) | OPEN LINE FROM BUS 341461 [2FALCON EK 69.000] TO BUS 243721 [05FALCON 69.000] CKT Z1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 627 341515-324600(1) | OPEN LINE FROM BUS 341515 [2GARRARD CO 69.000] TO BUS 324600 [2LANCASTR KU69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 628 341539-324784(1) | OPEN LINE FROM BUS 341539 [2GOLDBUG 69.000] TO BUS 324784 [2WOFFORD 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 629 341554-243726(1) | OPEN LINE FROM BUS 341554 [2GRAYSON J 69.000] TO BUS 243726 [05GRAYSO 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 630 341563-324554(1) | OPEN LINE FROM BUS 341563 [2GREEN CO 69.000] TO BUS 324554 [2GRENSBRG KU69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 631 341605-251579(1) | OPEN LINE FROM BUS 341605 [2HEBRON 69.000] TO BUS 251579 [08HEBRON 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 632 341608-243812(Z1) | OPEN LINE FROM BUS 341608 [2HELECHAW 69.000] TO BUS 243812 [05LEE C 69.000] CKT Z1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 633 341632-324575(1) | OPEN LINE FROM BUS 341632 [2HODGENVILLE69.000] TO BUS 324575 [2HODGENV KU 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 634 341632-324660(1) | OPEN LINE FROM BUS 341632 [2HODGENVILLE69.000] TO BUS 324660 [2NEW HAVEN 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 635 341713-324519(1) | OPEN LINE FROM BUS 341713 [2KARGLE 69.000] TO BUS 324519 [2ETOWN KU 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 636 341740-324576(1) | OPEN LINE FROM BUS 341740 [2LAUREL CO 69.000] TO BUS 324576 [2HOPEWELL 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 637 341752-243737(Z1) | OPEN LINE FROM BUS 341752 [2LEON 69.000] TO BUS 243737 [05LEONKY 69.000] CKT Z1 | -31.4813 | 31.4813 | 33 | 95.3978 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 638 341755-324527(1) | OPEN LINE FROM BUS 341755 [2LIBER CH T 69.000] TO BUS 324527 [2FARLEY KU 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.398 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 639 341890-246973(Z1) | OPEN LINE FROM BUS 341890 [2MORGAN CO 69.000] TO BUS 246973 [05MORGCO 69.000] CKT Z1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 640 341923-324717(1) | OPEN LINE FROM BUS 341923 [2MURPHYSVIL 69.000] TO BUS 324717 [2SARDIS TAP 69.000] CKT 1 | -31.4791 | 31.4791 | 33 | 95.3911 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 641 341923-325019(1) | OPEN LINE FROM BUS 341923 [2MURPHYSVIL 69.000] TO BUS 325019 [2KENTON-6 69.000] CKT 1 | -31.4808 | 31.4808 | 33 | 95.3964 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 642 341929-324662(1) | OPEN LINE FROM BUS 341929 [2N LONDON 69.000] TO BUS 324662 [2N LONDON KU69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 643 341935-324736(1) | OPEN LINE FROM BUS 341935 [2N SPRINGFLD69.000] TO BUS 324736 [2SPRINGFL KU69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.398 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 644 341944-324288(1) | OPEN LINE FROM BUS 341944 [2NELSON CO 69.000] TO BUS 324288 [4NELSON CO 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 645 342007-324455(1) | OPEN LINE FROM BUS 342007 [2OWEN CO 69.000] TO BUS 324455 [2BROMLEY 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 646 342008-324290(1) | OPEN LINE FROM BUS 342008 [4OWEN CO 138.00] TO BUS 324290 [4OWEN CO TAP138.00] CKT 1 | -31.4806 | 31.4806 | 33 | 95.3959 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 647 342055-243742(1) | OPEN LINE FROM BUS 342055 [2PELFREY 69.000] TO BUS 243742 [05CORYSS 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 648 342058-324951(1) | OPEN LINE FROM BUS 342058 [2PENN 69.000] TO BUS 324951 [2SCOTT CO 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 649 342133-324492(1) | OPEN LINE FROM BUS 342133 [2RENAKER 69.000] TO BUS 324492 [2CYNTHIAN SW69.000] CKT 1 | -31.478 | 31.478 | 33 | 95.3879 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 650 342157-324708(1) | OPEN LINE FROM BUS 342157 [2ROGERSVIL J69.000] TO BUS 324708 [2ROGERSVILLE69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 651 342184-324445(1) | OPEN LINE FROM BUS 342184 [2S ANDERSON 69.000] TO BUS 324445 [2BONDS MILL 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 652 342184-324445(2) | OPEN LINE FROM BUS 342184 [2S ANDERSON 69.000] TO BUS 324445 [2BONDS MILL 69.000] CKT 2 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 653 342218-247897(Z1) | OPEN LINE FROM BUS 342218 [2SALT LICK 138.00] TO BUS 247897 [05SNAG FK SS138.00] CKT Z1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 654 342232-324787(1) | OPEN LINE FROM BUS 342232 [2SEWELLTON 69.000] TO BUS 324787 [2UNION UNDWR69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 655 342248-324718(1) | OPEN LINE FROM BUS 342248 [2SHELBY TAP 69.000] TO BUS 324718 [2SHELBY CO T69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 656 342287-324531(1) | OPEN LINE FROM BUS 342287 [2SOMERSET KU69.000] TO BUS 324531 [2FERGUSON SO69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 657 342287-324737(1) | OPEN LINE FROM BUS 342287 [2SOMERSET KU69.000] TO BUS 324737 [2SOMERSET SO69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 658 342307-324509(1) | OPEN LINE FROM BUS 342307 [2STEPHENSBRG69.000] TO BUS 324509 [2EASTVIEW 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 659 342340-324519(1) | OPEN LINE FROM BUS 342340 [2THARP T 69.000] TO BUS 324519 [2ETOWN KU 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 660 342343-246971(1) | OPEN LINE FROM BUS 342343 [2THELMA 69.000] TO BUS 246971 [05THELM2 69.000] CKT 1 | -31.4812 | 31.4812 | 33 | 95.3976 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 661 342454-251315(1) | OPEN LINE FROM BUS 342454 [2W M SMITH 69.000] TO BUS 251315 [08EKSMTH 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 662 342487-250148(1) | OPEN LINE FROM BUS 342487 [2WEBSTER RD 69.000] TO BUS 250148 [08EKPWEB 138.00] CKT 1 | -31.481 | 31.481 | 33 | 95.3971 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 663 342538-243688(1) | OPEN LINE FROM BUS 342538 [4ARGENTUM 138.00] TO BUS 243688 [05S.PORT MTR138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 664 342544-324275(1) | OPEN LINE FROM BUS 342544 [4AVON-R 138.00] TO BUS 324275 [4LOUDON AVE 138.00] CKT 1 | -31.481 | 31.481 | 33 | 95.397 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 665 342547-324210(1) | OPEN LINE FROM BUS 342547 [4BAKER LN 138.00] TO BUS 324210 [4BAKER LANE 138.00] CKT 1 | -31.4807 | 31.4807 | 33 | 95.3959 | LGEE
342000 | 5GAS | 161 | 342760 | 5LIBERTY J | 161 | 1 | EKPC_P1-2_CASEY-LIB J69 | EKPC_P1-2_CASEY-LIB J69 | 153.5589 | 153.5589 | 153 | 100.3653 | EKPC
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 666 342559-250054(1) | OPEN LINE FROM BUS 342559 [4BOONE CO 138.00] TO BUS 250054 [08LONGBR 138.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 667 342565-325925(1) | OPEN LINE FROM BUS 342565 [4BOONESBOR T138.00] TO BUS 325925 [4BOONSBORO N138.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 668 342568-324047(1) | OPEN LINE FROM BUS 342568 [4CENT HARDIN138.00] TO BUS 324047 [4BLACKBRANCH138.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 669 342568-324261(1) | OPEN LINE FROM BUS 342568 [4CENT HARDIN138.00] TO BUS 324261 [4HARDIN CO 138.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 670 342577-324247(1) | OPEN LINE FROM BUS 342577 [4FAWKES EK 138.00] TO BUS 324247 [4FAWKES TAP 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 671 342577-324248(1) | OPEN LINE FROM BUS 342577 [4FAWKES EK 138.00] TO BUS 324248 [4FAWKES KU 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 672 342586-324253(1) | OPEN LINE FROM BUS 342586 [4GALLATIN CO138.00] TO BUS 324253 [4GHENT 138.00] CKT 1 | -31.4808 | 31.4808 | 33 | 95.3965 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 673 342595-250152(1) | OPEN LINE FROM BUS 342595 [4HEBRON 138.00] TO BUS 250152 [08HEBRNG 138.00] CKT 1 | -31.481 | 31.481 | 33 | 95.397 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 674 342607-342918(1) | OPEN LINE FROM BUS 342607 [4JK SMITH 138.00] TO BUS 342918 [1JKCT 1G 13.800] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 675 342607-342921(1) | OPEN LINE FROM BUS 342607 [4JK SMITH 138.00] TO BUS 342921 [1JKCT 2G 13.800] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 676 342607-342924(1) | OPEN LINE FROM BUS 342607 [4JK SMITH 138.00] TO BUS 342924 [1JKCT 3G 13.800] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 677 342607-342927(1) | OPEN LINE FROM BUS 342607 [4JK SMITH 138.00] TO BUS 342927 [1JKCT 4G 13.800] CKT 1 | -31.4817 | 31.4817 | 33 | 95.399 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 678 342607-342930(1) | OPEN LINE FROM BUS 342607 [4JK SMITH 138.00] TO BUS 342930 [1JKCT 5G 13.800] CKT 1 | -31.4817 | 31.4817 | 33 | 95.399 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 679 342607-342933(1) | OPEN LINE FROM BUS 342607 [4JK SMITH 138.00] TO BUS 342933 [1JKCT 6G 13.800] CKT 1 | -31.4817 | 31.4817 | 33 | 95.3989 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 680 342607-342936(1) | OPEN LINE FROM BUS 342607 [4JK SMITH 138.00] TO BUS 342936 [1JKCT 7G 13.800] CKT 1 | -31.4817 | 31.4817 | 33 | 95.3989 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 681 342616-342948(1) | OPEN LINE FROM BUS 342616 [4LOVE HYDRO 138.00] TO BUS 342948 [1LOVE HYDRO 4.1600] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 682 342631-324328(1) | OPEN LINE FROM BUS 342631 [4PARIS T 138.00] TO BUS 324328 [4PARIS 138.00] CKT 1 | -31.4917 | 31.4917 | 33 | 95.4294 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 683 342649-324302(1) | OPEN LINE FROM BUS 342649 [4ROWAN CO 138.00] TO BUS 324302 [4RODBURN 138.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 684 342661-324267(1) | OPEN LINE FROM BUS 342661 [4SPUR-KENT-R138.00] TO BUS 324267 [4KENTON 138.00] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3978 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 685 342664-342957(1) | OPEN LINE FROM BUS 342664 [4SPURLOCK 138.00] TO BUS 342957 [1SPURLK1G 22.000] CKT 1 | -31.4819 | 31.4819 | 33 | 95.3997 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 686 342688-324276(1) | OPEN LINE FROM BUS 342688 [4UNION CTY T138.00] TO BUS 324276 [4LAKE REBA T138.00] CKT 1 | -31.4819 | 31.4819 | 33 | 95.3996 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 687 342697-324138(1) | OPEN LINE FROM BUS 342697 [5BEATTYV J 161.00] TO BUS 324138 [5DELVINTA 161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 688 342697-324430(1) | OPEN LINE FROM BUS 342697 [5BEATTYV J 161.00] TO BUS 324430 [2BEATTYVI KU69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.398 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 689 342700-326975(1) | OPEN LINE FROM BUS 342700 [5BULLITT CO 161.00] TO BUS 326975 [5CEDAR GRV 161.00] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3979 | LGEE
342000 | 5GAS | 161 | 342760 | 5LIBERTY J | 161 | 1 | EKPC_P1-2_COP-RUS-WLF161 | EKPC_P1-2_COP-RUS-WLF161 | 153.1705 | 153.1705 | 153 | 100.1114 | EKPC
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 690 342700-326998(1) | OPEN LINE FROM BUS 342700 [5BULLITT CO 161.00] TO BUS 326998 [5BULLITT TAP161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 691 342718-324141(1) | OPEN LINE FROM BUS 342718 [5COOPER2 161.00] TO BUS 324141 [5ELIHU 161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
342000 | 5GAS | 161 | 342760 | 5LIBERTY J | 161 | 1 | SINGLE OPN LIN 340 341767-342064(1) | OPEN LINE FROM BUS 341767 [2LIBERTYKU T69.000] TO BUS 342064 [2PEYTONS ST 69.000] CKT 1 | 152.1743 | 152.1743 | 153 | 99.4604 | EKPC
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 692 342732-361603(1) | OPEN LINE FROM BUS 342732 [5FOX HOLLOW 161.00] TO BUS 361603 [5E GLASGOW T161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 693 342736-324138(1) | OPEN LINE FROM BUS 342736 [5GREEN HAL T161.00] TO BUS 324138 [5DELVINTA 161.00] CKT 1 | -31.4811 | 31.4811 | 33 | 95.3974 | LGEE
342000 | 5GAS | 161 | 342760 | 5LIBERTY J | 161 | 1 | EKPC_P1-2_GREEN-KUTAY69 | EKPC_P1-2_GREEN-KUTAY69 | 151.9168 | 151.9168 | 153 | 99.292 | EKPC
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 694 342757-342945(1) | OPEN LINE FROM BUS 342757 [5LAUREL DAM 161.00] TO BUS 342945 [1LAUREL 1G 13.800] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 695 342770-324271(1) | OPEN LINE FROM BUS 342770 [4MARION CO 138.00] TO BUS 324271 [4LEBANON 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
342000 | 5GAS | 161 | 342760 | 5LIBERTY J | 161 | 1 | BB-1403 | BB-1403 | 151.9065 | 151.9065 | 153 | 99.2853 | EKPC
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 696 342778-360473(1) | OPEN LINE FROM BUS 342778 [5MCCREARY CO161.00] TO BUS 360473 [5JELLICO TN 161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 697 342778-360486(1) | OPEN LINE FROM BUS 342778 [5MCCREARY CO161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 698 342778-361579(1) | OPEN LINE FROM BUS 342778 [5MCCREARY CO161.00] TO BUS 361579 [5WINFIELD TN161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 699 342781-324688(1) | OPEN LINE FROM BUS 342781 [5PITTSBURG 161.00] TO BUS 324688 [2PITTSBRG KU69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 700 342796-360448(1) | OPEN LINE FROM BUS 342796 [5RUSSEL CO J161.00] TO BUS 360448 [5WOLF CRK HP161.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
342000 | 5GAS | 161 | 342760 | 5LIBERTY J | 161 | 1 | BB-1402 | BB-1402 | 151.5574 | 151.5574 | 153 | 99.0571 | EKPC
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 701 342814-360334(1) | OPEN LINE FROM BUS 342814 [5SUMM SHADE 161.00] TO BUS 360334 [5SUMMER SHAD161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 702 342814-361788(1) | OPEN LINE FROM BUS 342814 [5SUMM SHADE 161.00] TO BUS 361788 [5SUM SHAD TP161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 703 342817-325921(1) | OPEN LINE FROM BUS 342817 [5TAYLOR CO J161.00] TO BUS 325921 [5TAYLOR CO 161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
342000 | 5GAS | 161 | 342760 | 5LIBERTY J | 161 | 1 | SINGLE OPN LIN 599 342775-342797(1) | OPEN LINE FROM BUS 342775 [5MARION IP T161.00] TO BUS 342797 [5S MARION IT161.00] CKT 1 | 151.0272 | 151.0272 | 153 | 98.7106 | EKPC
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 704 342823-360486(1) | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | -31.4813 | 31.4813 | 33 | 95.398 | LGEE
342000 | 5GAS | 161 | 342760 | 5LIBERTY J | 161 | 1 | SINGLE OPN LIN 590 342751-342796(1) | OPEN LINE FROM BUS 342751 [5JAMESTOWN T161.00] TO BUS 342796 [5RUSSEL CO J161.00] CKT 1 | 150.4326 | 150.4326 | 153 | 98.322 | EKPC
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 705 342832-342939-342942(1) | OPEN LINE FROM BUS 342832 [7JK SMITH 345.00] TO BUS 342939 [1JKCT 9G 13.800] TO BUS 342942 [1JKCT 10G 13.800] CKT 1 | -31.4823 | 31.4823 | 33 | 95.401 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 706 342838-249581(1) | OPEN LINE FROM BUS 342838 [7SPURLOCK 345.00] TO BUS 249581 [08MELDAL 345.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 707 342838-253077(1) | OPEN LINE FROM BUS 342838 [7SPURLOCK 345.00] TO BUS 253077 [09STUART 345.00] CKT 1 | -31.4809 | 31.4809 | 33 | 95.3968 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 708 342838-342960(1) | OPEN LINE FROM BUS 342838 [7SPURLOCK 345.00] TO BUS 342960 [1SPURLK2G 22.000] CKT 1 | -31.4819 | 31.4819 | 33 | 95.3998 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 709 342838-342963(1) | OPEN LINE FROM BUS 342838 [7SPURLOCK 345.00] TO BUS 342963 [1SPURLK3G 18.000] CKT 1 | -31.4817 | 31.4817 | 33 | 95.3992 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 710 342838-342966(1) | OPEN LINE FROM BUS 342838 [7SPURLOCK 345.00] TO BUS 342966 [1SPURLK4G 18.000] CKT 1 | -31.4817 | 31.4817 | 33 | 95.3992 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 711 342841-325074(Z1) | OPEN LINE FROM BUS 342841 [7W GARRARDEK345.00] TO BUS 325074 [7W GARRARDKU345.00] CKT Z1 | -31.4812 | 31.4812 | 33 | 95.3976 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 712 342844-384157(1) | OPEN LINE FROM BUS 342844 [8SOUTHGEN 500.00] TO BUS 384157 [8MILLER8 500.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 713 342847-243205(1) | OPEN LINE FROM BUS 342847 [9NORTHGEN 765.00] TO BUS 243205 [05COOK 765.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BARREN CO - HORSECAVE 69 SS | BARREN CO - HORSECAVE 69 SS | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | CAVE CITY J-SEYMOUR T 69 SS | CAVE CITY J-SEYMOUR T 69 SS | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | CAVE CITY - CAVE CITY JCT 69 SS | CAVE CITY - CAVE CITY JCT 69 SS | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | FOX HOLLOW - PARKWAY1 69 SS | FOX HOLLOW - PARKWAY1 69 SS | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | WAYNE CO - ZULA TAP 69 SS | WAYNE CO - ZULA TAP 69 SS | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | KU GARRARD T-MANCHESTER 69 SS | KU GARRARD T-MANCHESTER 69 SS | -31.4815 | 31.4815 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | GREEN BRIAR T-MANCHESTER 69 SS | GREEN BRIAR T-MANCHESTER 69 SS | -31.4815 | 31.4815 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | FALL ROCK-GREEN BRIAR T 69 SS | FALL ROCK-GREEN BRIAR T 69 SS | -31.4813 | 31.4813 | 33 | 95.3979 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BIG CREEK - BIG CREEK TAP 69 SS | BIG CREEK - BIG CREEK TAP 69 SS | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | FALL ROCK - BIG CREEK TAP 69 SS | FALL ROCK - BIG CREEK TAP 69 SS | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BIG CREEK - ELK MT 69 SS | BIG CREEK - ELK MT 69 SS | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | CLAY LICK JCT - S ANDERSON 69 SS | CLAY LICK JCT - S ANDERSON 69 SS | -31.4819 | 31.4819 | 33 | 95.3996 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | CLAY LICK J-CLAY LICK SW 69 SS | CLAY LICK J-CLAY LICK SW 69 SS | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | OWEN CO - OWEN CO JCT 2 69 SS | OWEN CO - OWEN CO JCT 2 69 SS | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | OWEN CO JCT 1 - BROMLEY EK 69 SS | OWEN CO JCT 1 - BROMLEY EK 69 SS | -31.4811 | 31.4811 | 33 | 95.3972 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BROMLEY EK - MUNK JCT 69 SS | BROMLEY EK - MUNK JCT 69 SS | -31.4811 | 31.4811 | 33 | 95.3972 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | MUNK JCT - WILLIAMSTOWN 69 SS | MUNK JCT - WILLIAMSTOWN 69 SS | -31.4811 | 31.4811 | 33 | 95.3972 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | RENAKER - THREE M 69 SS | RENAKER - THREE M 69 SS | -31.4827 | 31.4827 | 33 | 95.4022 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | KU W FRANKFORT BRDGPT1 69 SS | KU W FRANKFORT BRDGPT1 69 SS | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BRIDGEPORT J-BRDGPT2 69 SS | BRIDGEPORT J-BRDGPT2 69 SS | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | STANLEY PARKER - BANK LICK 69 SS | STANLEY PARKER - BANK LICK 69 SS | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BEATTYVILLE-BEATTYVLLE D SS | BEATTYVILLE-BEATTYVLLE D SS | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BEATTYVILLE DIST - OAKDALE 69 SS | BEATTYVILLE DIST - OAKDALE 69 SS | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SHELBY CO BUS SS | SHELBY CO BUS SS | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_OWEN-PENN69 | EKPC_P1-2_OWEN-PENN69 | -31.4812 | 31.4812 | 33 | 95.3975 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_PENN-RENAKER69 | EKPC_P1-2_PENN-RENAKER69 | -31.4816 | 31.4816 | 33 | 95.3989 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_BOONE-HEBRON69 | EKPC_P1-2_BOONE-HEBRON69 | -31.4812 | 31.4812 | 33 | 95.3977 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_BOON-OWN-REN69 | EKPC_P1-2_BOON-OWN-REN69 | -31.4813 | 31.4813 | 33 | 95.3979 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_T FTJ-WEB RD69 | EKPC_P1-2_T FTJ-WEB RD69 | -31.481 | 31.481 | 33 | 95.397 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_TFTJ- ST PRK69 | EKPC_P1-2_TFTJ- ST PRK69 | -31.4812 | 31.4812 | 33 | 95.3974 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_ST PRK-BRAK 69 | EKPC_P1-2_ST PRK-BRAK 69 | -31.4809 | 31.4809 | 33 | 95.3967 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_OWN-CARSON 69 | EKPC_P1-2_OWN-CARSON 69 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_OWN-CLY VILL69 | EKPC_P1-2_OWN-CLY VILL69 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_BRAK- REN 69 | EKPC_P1-2_BRAK- REN 69 | -31.4804 | 31.4804 | 33 | 95.3952 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_BRAK- KU KEN69 | EKPC_P1-2_BRAK- KU KEN69 | -31.4811 | 31.4811 | 33 | 95.3973 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_PLUM-GODDARD69 | EKPC_P1-2_PLUM-GODDARD69 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_MURPH - HQ 69 | EKPC_P1-2_MURPH - HQ 69 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_MURPH-MILLBG69 | EKPC_P1-2_MURPH-MILLBG69 | -31.4804 | 31.4804 | 33 | 95.3952 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_MURPH-KU KEN69 | EKPC_P1-2_MURPH-KU KEN69 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_ARGEN - LEON69 | EKPC_P1-2_ARGEN - LEON69 | -31.4813 | 31.4813 | 33 | 95.3979 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_LEON-SKAGGS 69 | EKPC_P1-2_LEON-SKAGGS 69 | -31.4812 | 31.4812 | 33 | 95.3977 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_FIN-SHL-SHBV69 | EKPC_P1-2_FIN-SHL-SHBV69 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_SHL-BUD-BKRT69 | EKPC_P1-2_SHL-BUD-BKRT69 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_REN - HQ 69 | EKPC_P1-2_REN - HQ 69 | -31.4808 | 31.4808 | 33 | 95.3963 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_GODD - HOPE 69 | EKPC_P1-2_GODD - HOPE 69 | -31.4816 | 31.4816 | 33 | 95.3988 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_GODD - ROW 69 | EKPC_P1-2_GODD - ROW 69 | -31.4812 | 31.4812 | 33 | 95.3975 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_BULL-W BARDJ69 | EKPC_P1-2_BULL-W BARDJ69 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_BULL - NELS 69 | EKPC_P1-2_BULL - NELS 69 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_N SPR -S AND69 | EKPC_P1-2_N SPR -S AND69 | -31.4813 | 31.4813 | 33 | 95.398 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_HNTFMJ-S AND69 | EKPC_P1-2_HNTFMJ-S AND69 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_BKR LN-FAY 69 | EKPC_P1-2_BKR LN-FAY 69 | -31.4806 | 31.4806 | 33 | 95.3956 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_HQ-HUNT 69 | EKPC_P1-2_HQ-HUNT 69 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_HUNT-POWELL 69 | EKPC_P1-2_HUNT-POWELL 69 | -31.4812 | 31.4812 | 33 | 95.3975 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_DALE-HTFRMJ69 | EKPC_P1-2_DALE-HTFRMJ69 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_DALE-GARRD 69 | EKPC_P1-2_DALE-GARRD 69 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_HOPE - POW 69 | EKPC_P1-2_HOPE - POW 69 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_HOPE - MORG 69 | EKPC_P1-2_HOPE - MORG 69 | -31.4813 | 31.4813 | 33 | 95.3979 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_MORG-SKAGGS69 | EKPC_P1-2_MORG-SKAGGS69 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_SKAGGS-FALC69 | EKPC_P1-2_SKAGGS-FALC69 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_SKAGGS-THELM69 | EKPC_P1-2_SKAGGS-THELM69 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_C HAR-KU ETN69 | EKPC_P1-2_C HAR-KU ETN69 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_STEPH-HODG 69 | EKPC_P1-2_STEPH-HODG 69 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_STEPH-BONN 69 | EKPC_P1-2_STEPH-BONN 69 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_ETOWN-KU ETN69 | EKPC_P1-2_ETOWN-KU ETN69 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_ETWN-ROG-RAD69 | EKPC_P1-2_ETWN-ROG-RAD69 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_ETOWN-NELSN 69 | EKPC_P1-2_ETOWN-NELSN 69 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_W BARDJ-EBRD69 | EKPC_P1-2_W BARDJ-EBRD69 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_HODG-GREEN 69 | EKPC_P1-2_HODG-GREEN 69 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_HODG-N SPR 69 | EKPC_P1-2_HODG-N SPR 69 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_E BARD-N SPR69 | EKPC_P1-2_E BARD-N SPR69 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_E BRD-KU BRD69 | EKPC_P1-2_E BRD-KU BRD69 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_HNTFMJ-N SPR69 | EKPC_P1-2_HNTFMJ-N SPR69 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_W BER-THRLJ 69 | EKPC_P1-2_W BER-THRLJ 69 | -31.4822 | 31.4822 | 33 | 95.4005 | LGEE
324757 | 2UPR MIL CRK | 69 | 324941 | 2RIVERPORT | 69 | 1 | SINGLE OPN LIN 1520 324619-324998(1) | OPEN LINE FROM BUS 324619 [2LOWER MIL C69.000] TO BUS 324998 [2WEST CO 2 69.000] CKT 1 | 61.8488 | 61.8487 | 63 | 98.1726 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_W BER-KU FAW69 | EKPC_P1-2_W BER-KU FAW69 | -31.4807 | 31.4807 | 33 | 95.3962 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_POW - ZACH 69 | EKPC_P1-2_POW - ZACH 69 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_ZACH-HELECH69 | EKPC_P1-2_ZACH-HELECH69 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_BETYV - OAK 69 | EKPC_P1-2_BETYV - OAK 69 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_BETYV - TYN 69 | EKPC_P1-2_BETYV - TYN 69 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_HELECH-MAG 69 | EKPC_P1-2_HELECH-MAG 69 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_FALC - MAG 69 | EKPC_P1-2_FALC - MAG 69 | -31.4816 | 31.4816 | 33 | 95.3988 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_MAG - THELM 69 | EKPC_P1-2_MAG - THELM 69 | -31.4813 | 31.4813 | 33 | 95.3979 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_BONN - BARR 69 | EKPC_P1-2_BONN - BARR 69 | -31.4816 | 31.4816 | 33 | 95.3989 | LGEE
324757 | 2UPR MIL CRK | 69 | 324941 | 2RIVERPORT | 69 | 1 | B-69-337 | B-69-337 | 61.8284 | 61.8284 | 63 | 98.1403 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_GREEN-SUM SH69 | EKPC_P1-2_GREEN-SUM SH69 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_CASEY-LIB J69 | EKPC_P1-2_CASEY-LIB J69 | -31.4817 | 31.4817 | 33 | 95.399 | LGEE
324536 | 2FINCHVILLE | 69 | 324718 | 2SHELBY CO T | 69 | 1 | BB-1272 | BB-1272 | 51.8685 | 51.8685 | 53 | 97.8651 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_LIB J-GARR69 | EKPC_P1-2_LIB J-GARR69 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_LIB J-WIND 69 | EKPC_P1-2_LIB J-WIND 69 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_PUL-WAL-SSET69 | EKPC_P1-2_PUL-WAL-SSET69 | -31.4813 | 31.4813 | 33 | 95.3978 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_PUL - WOODSTOCK 69 | EKPC_P1-2_PUL - WOODSTOCK 69 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_THREELJ- WAL69 | EKPC_P1-2_THREELJ- WAL69 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_TYN - N LON 69 | EKPC_P1-2_TYN - N LON 69 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_FALL R-GARR69 | EKPC_P1-2_FALL R-GARR69 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_FALL R-GOOS 69 | EKPC_P1-2_FALL R-GOOS 69 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_BARR- FOX H 69 | EKPC_P1-2_BARR- FOX H 69 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_FOX H-SUMMSH69 | EKPC_P1-2_FOX H-SUMMSH69 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_SUMMSH-SEWJ 69 | EKPC_P1-2_SUMMSH-SEWJ 69 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_SUMMSH-WAYNE69 | EKPC_P1-2_SUMMSH-WAYNE69 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_WAYNE-ZULA 69 | EKPC_P1-2_WAYNE-ZULA 69 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_SEWJ - RUSS 69 | EKPC_P1-2_SEWJ - RUSS 69 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_SEWJ - WIND 69 | EKPC_P1-2_SEWJ - WIND 69 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_RUSS-KU SSET69 | EKPC_P1-2_RUSS-KU SSET69 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_WIND - SSET 69 | EKPC_P1-2_WIND - SSET 69 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_SSET-KU ELI 69 | EKPC_P1-2_SSET-KU ELI 69 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_COOP-DENNY 69 | EKPC_P1-2_COOP-DENNY 69 | -31.4816 | 31.4816 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_LAUR-KU FAR69 | EKPC_P1-2_LAUR-KU FAR69 | -31.4813 | 31.4813 | 33 | 95.398 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_LAUR-KU SWTH69 | EKPC_P1-2_LAUR-KU SWTH69 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_WAYNE-DENNY69 | EKPC_P1-2_WAYNE-DENNY69 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_DENNY-MCCRRY69 | EKPC_P1-2_DENNY-MCCRRY69 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_MCCRY-KUWOFF69 | EKPC_P1-2_MCCRY-KUWOFF69 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_CLYV-SHL-FRK69 | EKPC_P1-2_CLYV-SHL-FRK69 | -31.4813 | 31.4813 | 33 | 95.3978 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_BULL- PLENTG69 | EKPC_P1-2_BULL- PLENTG69 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_AEPMORG- MOR69 | EKPC_P1-2_AEPMORG- MOR69 | -31.4813 | 31.4813 | 33 | 95.3979 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_AEPMORG-INDX69 | EKPC_P1-2_AEPMORG-INDX69 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_HODG-KU BARD69 | EKPC_P1-2_HODG-KU BARD69 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_HODG-KU ETWN69 | EKPC_P1-2_HODG-KU ETWN69 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_N SPR-KU LEB69 | EKPC_P1-2_N SPR-KU LEB69 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
342000 | 5GAS | 161 | 342760 | 5LIBERTY J | 161 | 1 | SINGLE OPN LIN 587 342745-342751(1) | OPEN LINE FROM BUS 342745 [5JABEZ T 161.00] TO BUS 342751 [5JAMESTOWN T161.00] CKT 1 | 149.602 | 149.602 | 153 | 97.7791 | EKPC
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_BAR-BON-FHOL69 | EKPC_P1-2_BAR-BON-FHOL69 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_FHOL-PARK69 | EKPC_P1-2_FHOL-PARK69 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_GREEN-KUTAY69 | EKPC_P1-2_GREEN-KUTAY69 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
342000 | 5GAS | 161 | 342760 | 5LIBERTY J | 161 | 1 | SINGLE OPN LIN 606 342797-342798(1) | OPEN LINE FROM BUS 342797 [5S MARION IT161.00] TO BUS 342798 [5S MARION IP161.00] CKT 1 | 149.4557 | 149.4557 | 153 | 97.6835 | EKPC
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_NLON-KU NLON69 | EKPC_P1-2_NLON-KU NLON69 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_DK HEB-HEB 138 | EKPC_P1-2_DK HEB-HEB 138 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_BOONE-BUFF138 | EKPC_P1-2_BOONE-BUFF138 | -31.4813 | 31.4813 | 33 | 95.3979 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_BOONE-STANP138 | EKPC_P1-2_BOONE-STANP138 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_BOONE-GALL138 | EKPC_P1-2_BOONE-GALL138 | -31.4813 | 31.4813 | 33 | 95.3978 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_BOONE-REN 138 | EKPC_P1-2_BOONE-REN 138 | -31.4806 | 31.4806 | 33 | 95.3957 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_OWEN 138/69 | EKPC_P1-2_OWEN 138/69 | -31.4816 | 31.4816 | 33 | 95.3988 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_SPUR-KUKEN 138 | EKPC_P1-2_SPUR-KUKEN 138 | -31.4813 | 31.4813 | 33 | 95.3978 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_SPUR-PLUM 138 | EKPC_P1-2_SPUR-PLUM 138 | -31.4817 | 31.4817 | 33 | 95.3991 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_SPUR-GODD 138 | EKPC_P1-2_SPUR-GODD 138 | -31.4818 | 31.4818 | 33 | 95.3993 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_GODD - ROW138 | EKPC_P1-2_GODD - ROW138 | -31.4817 | 31.4817 | 33 | 95.399 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_AVN-PAR-REN138 | EKPC_P1-2_AVN-PAR-REN138 | -31.4915 | 31.4915 | 33 | 95.4287 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_AVN-BBN-DLE138 | EKPC_P1-2_AVN-BBN-DLE138 | -31.4819 | 31.4819 | 33 | 95.3998 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_AVON-FAY 138 | EKPC_P1-2_AVON-FAY 138 | -31.4811 | 31.4811 | 33 | 95.3971 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_AVON-LOUD 138 | EKPC_P1-2_AVON-LOUD 138 | -31.481 | 31.481 | 33 | 95.397 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_DALE-JKSMIT138 | EKPC_P1-2_DALE-JKSMIT138 | -31.4812 | 31.4812 | 33 | 95.3977 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_DALE-FAWK 138 | EKPC_P1-2_DALE-FAWK 138 | -31.4812 | 31.4812 | 33 | 95.3976 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_FAW-W BER 138 | EKPC_P1-2_FAW-W BER 138 | -31.481 | 31.481 | 33 | 95.3969 | LGEE
324757 | 2UPR MIL CRK | 69 | 324941 | 2RIVERPORT | 69 | 1 | SINGLE OPN LIN 1790 324997-324998(1) | OPEN LINE FROM BUS 324997 [2WEST CO 1 69.000] TO BUS 324998 [2WEST CO 2 69.000] CKT 1 | 61.3867 | 61.3867 | 63 | 97.4392 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_JKS 345/138 1 | EKPC_P1-2_JKS 345/138 1 | -31.4813 | 31.4813 | 33 | 95.3979 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_JKS 345/138 2 | EKPC_P1-2_JKS 345/138 2 | -31.4813 | 31.4813 | 33 | 95.3979 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_JKSMTH-REBA138 | EKPC_P1-2_JKSMTH-REBA138 | -31.4819 | 31.4819 | 33 | 95.3998 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_ROW-SKAG138 | EKPC_P1-2_ROW-SKAG138 | -31.4811 | 31.4811 | 33 | 95.3973 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_CHARD-HRDBG138 | EKPC_P1-2_CHARD-HRDBG138 | -31.4812 | 31.4812 | 33 | 95.3977 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_COP-RUS-WLF161 | EKPC_P1-2_COP-RUS-WLF161 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
342000 | 5GAS | 161 | 342760 | 5LIBERTY J | 161 | 1 | SINGLE OPN LIN 588 342745-342799(1) | OPEN LINE FROM BUS 342745 [5JABEZ T 161.00] TO BUS 342799 [5S OAKHILL 161.00] CKT 1 | 149.0683 | 149.0683 | 153 | 97.4302 | EKPC
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_COOP-DEN161 | EKPC_P1-2_COOP-DEN161 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_COP-LIBJ-PU161 | EKPC_P1-2_COP-LIBJ-PU161 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
341407 | 2E BARDSTOWN | 69 | 324425 | 2BARDT IND T | 69 | 1 | SINGLE OPN LIN 110 341215-342700(1) | OPEN LINE FROM BUS 341215 [2BULLITT CO 69.000] TO BUS 342700 [5BULLITT CO 161.00] CKT 1 | -65.2526 | 65.2526 | 67 | 97.3919 | TIE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_LIB-CAS-GAS-MAR161 | EKPC_P1-2_LIB-CAS-GAS-MAR161 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
342000 | 5GAS | 161 | 342703 | 5CASEY CO | 161 | 1 | SINGLE OPN LIN 593 342760-342790(1) | OPEN LINE FROM BUS 342760 [5LIBERTY J 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 148.3912 | 148.3912 | 153 | 96.9877 | EKPC
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_MCCR-WAYNE161 | EKPC_P1-2_MCCR-WAYNE161 | -31.4814 | 31.4814 | 33 | 95.398 | LGEE
324271 | 4LEBANON | 138 | 324606 | 2LEBANON | 69 | 1 | SINGLE OPN LIN 1044 324271-324606(2) | OPEN LINE FROM BUS 324271 [4LEBANON 138.00] TO BUS 324606 [2LEBANON 69.000] CKT 2 | 58.099 | 58.099 | 60 | 96.8317 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_LAUR-PIT-TY161 | EKPC_P1-2_LAUR-PIT-TY161 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_TYN-DELV161 | EKPC_P1-2_TYN-DELV161 | -31.4812 | 31.4812 | 33 | 95.3974 | LGEE
342000 | 5GAS | 161 | 342703 | 5CASEY CO | 161 | 1 | EKPC_P1-2_COP-LIBJ-PU161 | EKPC_P1-2_COP-LIBJ-PU161 | 148.07 | 148.07 | 153 | 96.7778 | EKPC
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_TYN-FALLR161 | EKPC_P1-2_TYN-FALLR161 | -31.4807 | 31.4807 | 33 | 95.3961 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_GRE-TAY-MAR161 | EKPC_P1-2_GRE-TAY-MAR161 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
342000 | 5GAS | 161 | 342760 | 5LIBERTY J | 161 | 1 | B-500-97 | B-500-97 | 148.0658 | 148.0658 | 153 | 96.775 | EKPC
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_BARR-SUMSH161 | EKPC_P1-2_BARR-SUMSH161 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_BULL-SUMSH161 | EKPC_P1-2_BULL-SUMSH161 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_BULL-BLUE L161 | EKPC_P1-2_BULL-BLUE L161 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
342000 | 5GAS | 161 | 342760 | 5LIBERTY J | 161 | 1 | SINGLE OPN LIN 770 324102-324106(1) | OPEN LINE FROM BUS 324102 [7BROWN NORTH345.00] TO BUS 324106 [7HARDIN CO 345.00] CKT 1 | 148.0017 | 148.0017 | 153 | 96.7331 | EKPC
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_BULL-SHEL161 | EKPC_P1-2_BULL-SHEL161 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_POW-BTV-DEL161 | EKPC_P1-2_POW-BTV-DEL161 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | TVA SS-GLASGOW & LAFAYETTE 161 | TVA SS-GLASGOW & LAFAYETTE 161 | -31.4813 | 31.4813 | 33 | 95.398 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EK-TVA SSHD & SSHD 161 XFMR | EK-TVA SSHD & SSHD 161 XFMR | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | EKPC_P1-2_AVON-NCLA345 | EKPC_P1-2_AVON-NCLA345 | -31.4859 | 31.4859 | 33 | 95.4119 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 714 324010-324114(1) | OPEN LINE FROM BUS 324010 [7TRIMBL REAC345.00] TO BUS 324114 [7TRIMBLE CO 345.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 715 324021-324103(Z1) | OPEN LINE FROM BUS 324021 [7BLUEGRASS12345.00] TO BUS 324103 [7BUCKNER 345.00] CKT Z1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 716 324022-324103(Z1) | OPEN LINE FROM BUS 324022 [7BLUEGRASS 3345.00] TO BUS 324103 [7BUCKNER 345.00] CKT Z1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 717 324029-324030(1) | OPEN LINE FROM BUS 324029 [7TRIMBLE CTA345.00] TO BUS 324030 [7TRIMBLE CTB345.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 718 324029-324114(1) | OPEN LINE FROM BUS 324029 [7TRIMBLE CTA345.00] TO BUS 324114 [7TRIMBLE CO 345.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 719 324030-324114(1) | OPEN LINE FROM BUS 324030 [7TRIMBLE CTB345.00] TO BUS 324114 [7TRIMBLE CO 345.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 720 324047-325055(1) | OPEN LINE FROM BUS 324047 [4BLACKBRANCH138.00] TO BUS 325055 [4RHUDES TP 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 721 324048-324437(1) | OPEN LINE FROM BUS 324048 [2PARKWY MINE69.000] TO BUS 324437 [2BEVIER KU 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 722 324048-324584(1) | OPEN LINE FROM BUS 324048 [2PARKWY MINE69.000] TO BUS 324584 [2INDIAN HILL69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 723 324049-324572(1) | OPEN LINE FROM BUS 324049 [2OXFORD COAL69.000] TO BUS 324572 [2HILLSIDE 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 724 324049-324745(1) | OPEN LINE FROM BUS 324049 [2OXFORD COAL69.000] TO BUS 324745 [2STRINGTOWN 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 725 324050-324362(1) | OPEN LINE FROM BUS 324050 [2JONESVILLE 69.000] TO BUS 324362 [2RIO 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 726 324050-324447(1) | OPEN LINE FROM BUS 324050 [2JONESVILLE 69.000] TO BUS 324447 [2BONNIE KU 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 727 324051-324173(1) | OPEN LINE FROM BUS 324051 [4MATANZAS 138.00] TO BUS 324173 [5MATANZAS 161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 728 324051-324173(2) | OPEN LINE FROM BUS 324051 [4MATANZAS 138.00] TO BUS 324173 [5MATANZAS 161.00] CKT 2 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 729 324051-324255(1) | OPEN LINE FROM BUS 324051 [4MATANZAS 138.00] TO BUS 324255 [4GREEN RIVER138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 730 324051-324291(1) | OPEN LINE FROM BUS 324051 [4MATANZAS 138.00] TO BUS 324291 [4OHIO COUNTY138.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 731 324058-324059(1) | OPEN LINE FROM BUS 324058 [2BEAVER DAM 69.000] TO BUS 324059 [2BEAVER DM N69.000] CKT 1 | -31.4817 | 31.4817 | 33 | 95.3991 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 732 324058-324667(1) | OPEN LINE FROM BUS 324058 [2BEAVER DAM 69.000] TO BUS 324667 [2OHIO COUNTY69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 733 324059-324080(1) | OPEN LINE FROM BUS 324059 [2BEAVER DM N69.000] TO BUS 324080 [2HARTFORD 69.000] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 734 324061-324079(1) | OPEN LINE FROM BUS 324061 [2BORG-WARNER69.000] TO BUS 324079 [2HANSON 69.000] CKT 1 | -31.4817 | 31.4817 | 33 | 95.399 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 735 324061-324873(1) | OPEN LINE FROM BUS 324061 [2BORG-WARNER69.000] TO BUS 324873 [2HANSON JCT 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 736 324065-324843(1) | OPEN LINE FROM BUS 324065 [2DAWSON 764 69.000] TO BUS 324843 [2DAWSON IND 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 737 324067-324512(1) | OPEN LINE FROM BUS 324067 [2EDDYV PRIS 69.000] TO BUS 324512 [2EDDYV PR TP69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 738 324068-324349(1) | OPEN LINE FROM BUS 324068 [2E CAMPBELVL69.000] TO BUS 324349 [2CAMPBELVIL269.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 739 324069-324687(1) | OPEN LINE FROM BUS 324069 [2PAYNES ML 69.000] TO BUS 324687 [2PISGAH 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 740 324069-324763(1) | OPEN LINE FROM BUS 324069 [2PAYNES ML 69.000] TO BUS 324763 [2VERSAILLES 69.000] CKT 1 | -31.4812 | 31.4812 | 33 | 95.3977 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 741 324075-324702(1) | OPEN LINE FROM BUS 324075 [2GRAHAM 69.000] TO BUS 324702 [2RIVER QUEEN69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 742 324077-326594(1) | OPEN LINE FROM BUS 324077 [2GREENVILE W69.000] TO BUS 326594 [2GREENVL 12 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 743 324081-326587(1) | OPEN LINE FROM BUS 324081 [2MADSNV GE 69.000] TO BUS 326587 [2MADSNV W TP69.000] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 747 324083-326587(1) | OPEN LINE FROM BUS 324083 [2MADSNV W 69.000] TO BUS 326587 [2MADSNV W TP69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 748 324085-324629(1) | OPEN LINE FROM BUS 324085 [2MARION 4 69.000] TO BUS 324629 [2MARION KU 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 749 324086-324096(1) | OPEN LINE FROM BUS 324086 [2MORGANF IND69.000] TO BUS 324096 [2PEA WSH TAP69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 750 324086-324671(1) | OPEN LINE FROM BUS 324086 [2MORGANF IND69.000] TO BUS 324671 [2OVERLAD S T69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 751 324087-324913(1) | OPEN LINE FROM BUS 324087 [2MT VERN SO 69.000] TO BUS 324913 [2MT VERNON 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 752 324087-324927(1) | OPEN LINE FROM BUS 324087 [2MT VERN SO 69.000] TO BUS 324927 [2PINE HILL T69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 753 324090-324095(1) | OPEN LINE FROM BUS 324090 [2OVERLAND NO69.000] TO BUS 324095 [2UNIONTOWN 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 754 324091-324096(1) | OPEN LINE FROM BUS 324091 [2OVERLAND SO69.000] TO BUS 324096 [2PEA WSH TAP69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 755 324092-324702(1) | OPEN LINE FROM BUS 324092 [2PEABODY RVR69.000] TO BUS 324702 [2RIVER QUEEN69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 756 324093-324711(1) | OPEN LINE FROM BUS 324093 [2SPEN CHEMIC69.000] TO BUS 324711 [2SPEN CHEM T69.000] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 757 324094-324562(1) | OPEN LINE FROM BUS 324094 [2TURTLE CK T69.000] TO BUS 324562 [2HARLAN KU 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 758 324094-324761(1) | OPEN LINE FROM BUS 324094 [2TURTLE CK T69.000] TO BUS 324761 [2VERDA 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 759 324094-325045(1) | OPEN LINE FROM BUS 324094 [2TURTLE CK T69.000] TO BUS 325045 [2TURTLE CRK 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 760 324095-326572(1) | OPEN LINE FROM BUS 324095 [2UNIONTOWN 69.000] TO BUS 326572 [2RIVRVW COAL69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 761 324096-324097(1) | OPEN LINE FROM BUS 324096 [2PEA WSH TAP69.000] TO BUS 324097 [2PEAB WASH 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 762 324098-324779(1) | OPEN LINE FROM BUS 324098 [2WEST VACO 69.000] TO BUS 324779 [2WICKLIFFE 69.000] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 763 324100-324102(1) | OPEN LINE FROM BUS 324100 [7ALCALDE 345.00] TO BUS 324102 [7BROWN NORTH345.00] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3989 | LGEE
342000 | 5GAS | 161 | 342760 | 5LIBERTY J | 161 | 1 | SINGLE OPN LIN 575 342715-342799(1) | OPEN LINE FROM BUS 342715 [5COOPER1 161.00] TO BUS 342799 [5S OAKHILL 161.00] CKT 1 | 147.8018 | 147.8018 | 153 | 96.6025 | EKPC
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 764 324100-324112(1) | OPEN LINE FROM BUS 324100 [7ALCALDE 345.00] TO BUS 324112 [7PINEVILLE 345.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 765 324100-324130(1) | OPEN LINE FROM BUS 324100 [7ALCALDE 345.00] TO BUS 324130 [5ALCALDE 161.00] CKT 1 | -31.481 | 31.481 | 33 | 95.3971 | LGEE
342000 | 5GAS | 161 | 342760 | 5LIBERTY J | 161 | 1 | BASE CASE | BASE CASE | 142.8948 | 142.8948 | 148 | 96.5505 | EKPC
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 766 324101-324107(1) | OPEN LINE FROM BUS 324101 [7BLUE LICK 345.00] TO BUS 324107 [7MIDDLETOWN 345.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 767 324101-324108(1) | OPEN LINE FROM BUS 324101 [7BLUE LICK 345.00] TO BUS 324108 [7MILL CREEK 345.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 768 324101-324134(1) | OPEN LINE FROM BUS 324101 [7BLUE LICK 345.00] TO BUS 324134 [5BLUE LICK 161.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3983 | LGEE
324530 | 2FAWKES | 69 | 324656 | 2N MADISON T | 69 | 1 | SINGLE OPN LIN 1630 324735-324794(1) | OPEN LINE FROM BUS 324735 [2SOUTH POINT69.000] TO BUS 324794 [2ASHLND PIPE69.000] CKT 1 | 47.2585 | 47.2585 | 49 | 96.4459 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 769 324101-324212(1) | OPEN LINE FROM BUS 324101 [7BLUE LICK 345.00] TO BUS 324212 [4BLUE LICK 138.00] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3979 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 770 324102-324106(1) | OPEN LINE FROM BUS 324102 [7BROWN NORTH345.00] TO BUS 324106 [7HARDIN CO 345.00] CKT 1 | -31.4817 | 31.4817 | 33 | 95.3991 | LGEE
342000 | 5GAS | 161 | 342760 | 5LIBERTY J | 161 | 1 | EKPC_P1-2_N SPR-KU LEB69 | EKPC_P1-2_N SPR-KU LEB69 | 147.0192 | 147.0192 | 153 | 96.091 | EKPC
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 771 324102-324116(1) | OPEN LINE FROM BUS 324102 [7BROWN NORTH345.00] TO BUS 324116 [7W LEXINGTON345.00] CKT 1 | -31.4821 | 31.4821 | 33 | 95.4004 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 772 324102-325074(1) | OPEN LINE FROM BUS 324102 [7BROWN NORTH345.00] TO BUS 325074 [7W GARRARDKU345.00] CKT 1 | -31.4812 | 31.4812 | 33 | 95.3977 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 773 324102-325956(1) | OPEN LINE FROM BUS 324102 [7BROWN NORTH345.00] TO BUS 325956 [4BROWN N 2 138.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 774 324102-325957(2) | OPEN LINE FROM BUS 324102 [7BROWN NORTH345.00] TO BUS 325957 [4BROWN N 1 138.00] CKT 2 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 775 324103-324107(1) | OPEN LINE FROM BUS 324103 [7BUCKNER 345.00] TO BUS 324107 [7MIDDLETOWN 345.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 776 324103-324114(1) | OPEN LINE FROM BUS 324103 [7BUCKNER 345.00] TO BUS 324114 [7TRIMBLE CO 345.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 777 324104-324106(1) | OPEN LINE FROM BUS 324104 [7DAVIESS 345.00] TO BUS 324106 [7HARDIN CO 345.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 778 324105-324115(1) | OPEN LINE FROM BUS 324105 [7GHENT 345.00] TO BUS 324115 [7W FRANKFORT345.00] CKT 1 | -31.4822 | 31.4822 | 33 | 95.4006 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 779 324105-324116(1) | OPEN LINE FROM BUS 324105 [7GHENT 345.00] TO BUS 324116 [7W LEXINGTON345.00] CKT 1 | -31.4828 | 31.4828 | 33 | 95.4023 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 780 324105-324253(1) | OPEN LINE FROM BUS 324105 [7GHENT 345.00] TO BUS 324253 [4GHENT 138.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 781 324105-324253(2) | OPEN LINE FROM BUS 324105 [7GHENT 345.00] TO BUS 324253 [4GHENT 138.00] CKT 2 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 782 324105-326536(1) | OPEN LINE FROM BUS 324105 [7GHENT 345.00] TO BUS 326536 [7GALLATIN 345.00] CKT 1 | -31.4817 | 31.4817 | 33 | 95.3991 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 783 324106-324261(1) | OPEN LINE FROM BUS 324106 [7HARDIN CO 345.00] TO BUS 324261 [4HARDIN CO 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 784 324106-324261(2) | OPEN LINE FROM BUS 324106 [7HARDIN CO 345.00] TO BUS 324261 [4HARDIN CO 138.00] CKT 2 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 785 324106-325073(1) | OPEN LINE FROM BUS 324106 [7HARDIN CO 345.00] TO BUS 325073 [7REDMON RD 345.00] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 786 324107-324108(1) | OPEN LINE FROM BUS 324107 [7MIDDLETOWN 345.00] TO BUS 324108 [7MILL CREEK 345.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 787 324107-324114(1) | OPEN LINE FROM BUS 324107 [7MIDDLETOWN 345.00] TO BUS 324114 [7TRIMBLE CO 345.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 788 324107-324281(3) | OPEN LINE FROM BUS 324107 [7MIDDLETOWN 345.00] TO BUS 324281 [4MIDDLETOWN 138.00] CKT 3 | -31.4815 | 31.4815 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 789 324107-324281(4) | OPEN LINE FROM BUS 324107 [7MIDDLETOWN 345.00] TO BUS 324281 [4MIDDLETOWN 138.00] CKT 4 | -31.4815 | 31.4815 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 790 324107-324281(5) | OPEN LINE FROM BUS 324107 [7MIDDLETOWN 345.00] TO BUS 324281 [4MIDDLETOWN 138.00] CKT 5 | -31.4815 | 31.4815 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 791 324107-324281(7) | OPEN LINE FROM BUS 324107 [7MIDDLETOWN 345.00] TO BUS 324281 [4MIDDLETOWN 138.00] CKT 7 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 792 324108-325073(1) | OPEN LINE FROM BUS 324108 [7MILL CREEK 345.00] TO BUS 325073 [7REDMON RD 345.00] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 793 324108-326001(1) | OPEN LINE FROM BUS 324108 [7MILL CREEK 345.00] TO BUS 326001 [7CANE RUN TP345.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 794 324109-324565(1) | OPEN LINE FROM BUS 324109 [7NAS 345.00] TO BUS 324565 [7NAS TAP 345.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 795 324110-324289(1) | OPEN LINE FROM BUS 324110 [7NORTHSIDE 345.00] TO BUS 324289 [4NORTHSIDE 138.00] CKT 1 | -31.4813 | 31.4813 | 33 | 95.398 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 796 324110-326569(1) | OPEN LINE FROM BUS 324110 [7NORTHSIDE 345.00] TO BUS 326569 [7KENZIG ROAD345.00] CKT 1 | -31.4813 | 31.4813 | 33 | 95.398 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 797 324111-324294(1) | OPEN LINE FROM BUS 324111 [7PADDYS WEST345.00] TO BUS 324294 [4PADDYS WEST138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 798 324111-326001(1) | OPEN LINE FROM BUS 324111 [7PADDYS WEST345.00] TO BUS 326001 [7CANE RUN TP345.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 799 324111-326569(1) | OPEN LINE FROM BUS 324111 [7PADDYS WEST345.00] TO BUS 326569 [7KENZIG ROAD345.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 800 324112-324167(1) | OPEN LINE FROM BUS 324112 [7PINEVILLE 345.00] TO BUS 324167 [5PINEVILLE 2161.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 801 324112-325074(1) | OPEN LINE FROM BUS 324112 [7PINEVILLE 345.00] TO BUS 325074 [7W GARRARDKU345.00] CKT 1 | -31.4817 | 31.4817 | 33 | 95.3991 | LGEE
342000 | 5GAS | 161 | 342760 | 5LIBERTY J | 161 | 1 | SINGLE OPN LIN 336 341761-341767(1) | OPEN LINE FROM BUS 341761 [2LIBERTY J 69.000] TO BUS 341767 [2LIBERTYKU T69.000] CKT 1 | 146.9839 | 146.9839 | 153 | 96.0679 | EKPC
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 802 324114-324314(5) | OPEN LINE FROM BUS 324114 [7TRIMBLE CO 345.00] TO BUS 324314 [4TRIMBLE CO 138.00] CKT 5 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 803 324114-324314(6) | OPEN LINE FROM BUS 324114 [7TRIMBLE CO 345.00] TO BUS 324314 [4TRIMBLE CO 138.00] CKT 6 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 804 324115-324319(1) | OPEN LINE FROM BUS 324115 [7W FRANKFORT345.00] TO BUS 324319 [4W FRANKFORT138.00] CKT 1 | -31.482 | 31.482 | 33 | 95.4 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 805 324116-324320(1) | OPEN LINE FROM BUS 324116 [7W LEXINGTON345.00] TO BUS 324320 [4W LEXINGTON138.00] CKT 1 | -31.4856 | 31.4856 | 33 | 95.4108 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 806 324124-326564(1) | OPEN LINE FROM BUS 324124 [2CENTRTOWN S69.000] TO BUS 326564 [2LEW BREC 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 807 324130-324141(1) | OPEN LINE FROM BUS 324130 [5ALCALDE 161.00] TO BUS 324141 [5ELIHU 161.00] CKT 1 | -31.4812 | 31.4812 | 33 | 95.3975 | LGEE
342000 | 5GAS | 161 | 342760 | 5LIBERTY J | 161 | 1 | SINGLE OPN LIN 493 342367-942410(1) | OPEN LINE FROM BUS 342367 [2TOMM GOOC T69.000] TO BUS 942410 [AE2-254 TAP 69.000] CKT 1 | 146.9688 | 146.9688 | 153 | 96.058 | EKPC
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 808 324130-324143(1) | OPEN LINE FROM BUS 324130 [5ALCALDE 161.00] TO BUS 324143 [5FARLEY 161.00] CKT 1 | -31.4813 | 31.4813 | 33 | 95.398 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 809 324131-324139(1) | OPEN LINE FROM BUS 324131 [5ARNOLD 161.00] TO BUS 324139 [5DORCHESTER 161.00] CKT 1 | -31.4813 | 31.4813 | 33 | 95.398 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 810 324131-324146(1) | OPEN LINE FROM BUS 324131 [5ARNOLD 161.00] TO BUS 324146 [5HARLAN WYE 161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 811 324131-324148(1) | OPEN LINE FROM BUS 324131 [5ARNOLD 161.00] TO BUS 324148 [5WOOTON TAP 161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 812 324131-324416(1) | OPEN LINE FROM BUS 324131 [5ARNOLD 161.00] TO BUS 324416 [2ARNOLD 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 813 324132-324133(1) | OPEN LINE FROM BUS 324132 [5ARTEMUS TAP161.00] TO BUS 324133 [5ARTEMUS 161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 814 324132-324143(1) | OPEN LINE FROM BUS 324132 [5ARTEMUS TAP161.00] TO BUS 324143 [5FARLEY 161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 815 324132-324156(1) | OPEN LINE FROM BUS 324132 [5ARTEMUS TAP161.00] TO BUS 324156 [5PINEVILE SW161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 816 324133-324417(1) | OPEN LINE FROM BUS 324133 [5ARTEMUS 161.00] TO BUS 324417 [2ARTEMUS 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 817 324134-326975(1) | OPEN LINE FROM BUS 324134 [5BLUE LICK 161.00] TO BUS 326975 [5CEDAR GRV 161.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3983 | LGEE
324941 | 2RIVERPORT | 69 | 324975 | 2TERRY | 69 | 1 | SINGLE OPN LIN 1520 324619-324998(1) | OPEN LINE FROM BUS 324619 [2LOWER MIL C69.000] TO BUS 324998 [2WEST CO 2 69.000] CKT 1 | 60.5093 | 60.5093 | 63 | 96.0465 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 818 324135-324136(1) | OPEN LINE FROM BUS 324135 [5CORYDON TAP161.00] TO BUS 324136 [5CORYDON 161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 819 324135-324144(1) | OPEN LINE FROM BUS 324135 [5CORYDON TAP161.00] TO BUS 324144 [5GREEN RIVER161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 820 324135-324153(1) | OPEN LINE FROM BUS 324135 [5CORYDON TAP161.00] TO BUS 324153 [5MORGANFIELD161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 821 324136-324484(1) | OPEN LINE FROM BUS 324136 [5CORYDON 161.00] TO BUS 324484 [2CORYDON 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 822 324137-324151(1) | OPEN LINE FROM BUS 324137 [5CRITTENDEN 161.00] TO BUS 324151 [5LIVNGSTN CO161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 823 324137-324153(1) | OPEN LINE FROM BUS 324137 [5CRITTENDEN 161.00] TO BUS 324153 [5MORGANFIELD161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 824 324137-324486(1) | OPEN LINE FROM BUS 324137 [5CRITTENDEN 161.00] TO BUS 324486 [2CRITTENDEN 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 825 324138-324148(1) | OPEN LINE FROM BUS 324138 [5DELVINTA 161.00] TO BUS 324148 [5WOOTON TAP 161.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 826 324138-324165(1) | OPEN LINE FROM BUS 324138 [5DELVINTA 161.00] TO BUS 324165 [5W IRVINE T 161.00] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3979 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 827 324139-324149(1) | OPEN LINE FROM BUS 324139 [5DORCHESTER 161.00] TO BUS 324149 [5IMBODEN 161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 828 324139-324503(1) | OPEN LINE FROM BUS 324139 [5DORCHESTER 161.00] TO BUS 324503 [2DORCHESTER 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 829 324139-324503(2) | OPEN LINE FROM BUS 324139 [5DORCHESTER 161.00] TO BUS 324503 [2DORCHESTER 69.000] CKT 2 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 830 324140-324160(1) | OPEN LINE FROM BUS 324140 [5EARLINGTN N161.00] TO BUS 324160 [5RIVER QN T 161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 831 324140-324164(1) | OPEN LINE FROM BUS 324140 [5EARLINGTN N161.00] TO BUS 324164 [5WALKER 161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 832 324140-324506(1) | OPEN LINE FROM BUS 324140 [5EARLINGTN N161.00] TO BUS 324506 [2EARLINGTN N69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 833 324140-325079(1) | OPEN LINE FROM BUS 324140 [5EARLINGTN N161.00] TO BUS 325079 [5N PRINCETON161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 834 324141-324514(1) | OPEN LINE FROM BUS 324141 [5ELIHU 161.00] TO BUS 324514 [2ELIHU 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 835 324141-324514(2) | OPEN LINE FROM BUS 324141 [5ELIHU 161.00] TO BUS 324514 [2ELIHU 69.000] CKT 2 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 836 324143-324527(1) | OPEN LINE FROM BUS 324143 [5FARLEY 161.00] TO BUS 324527 [2FARLEY KU 69.000] CKT 1 | -31.4812 | 31.4812 | 33 | 95.3977 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 837 324144-324160(1) | OPEN LINE FROM BUS 324144 [5GREEN RIVER161.00] TO BUS 324160 [5RIVER QN T 161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 838 324144-324255(1) | OPEN LINE FROM BUS 324144 [5GREEN RIVER161.00] TO BUS 324255 [4GREEN RIVER138.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 839 324144-324255(2) | OPEN LINE FROM BUS 324144 [5GREEN RIVER161.00] TO BUS 324255 [4GREEN RIVER138.00] CKT 2 | -31.4815 | 31.4815 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 840 324144-324255(3) | OPEN LINE FROM BUS 324144 [5GREEN RIVER161.00] TO BUS 324255 [4GREEN RIVER138.00] CKT 3 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 841 324145-324171(1) | OPEN LINE FROM BUS 324145 [5GRAHAMVILLE161.00] TO BUS 324171 [5GRAHMVILE 1161.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 842 324145-324172(1) | OPEN LINE FROM BUS 324145 [5GRAHAMVILLE161.00] TO BUS 324172 [5GRAHMVILE 2161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 843 324145-324553(1) | OPEN LINE FROM BUS 324145 [5GRAHAMVILLE161.00] TO BUS 324553 [2GRAHAMVILLE69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 844 324145-325069(1) | OPEN LINE FROM BUS 324145 [5GRAHAMVILLE161.00] TO BUS 325069 [5SONG SP TP 161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 845 324145-325077(1) | OPEN LINE FROM BUS 324145 [5GRAHAMVILLE161.00] TO BUS 325077 [5COLEMAN TAP161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 846 324146-324147(1) | OPEN LINE FROM BUS 324146 [5HARLAN WYE 161.00] TO BUS 324147 [5HOWARDS BR 161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 847 324146-324155(1) | OPEN LINE FROM BUS 324146 [5HARLAN WYE 161.00] TO BUS 324155 [5PINEVILLE 1161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 848 324146-324157(1) | OPEN LINE FROM BUS 324146 [5HARLAN WYE 161.00] TO BUS 324157 [5POCKET N 161.00] CKT 1 | -31.4812 | 31.4812 | 33 | 95.3976 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 849 324146-324564(1) | OPEN LINE FROM BUS 324146 [5HARLAN WYE 161.00] TO BUS 324564 [2HARLAN WYE 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 850 324147-324155(1) | OPEN LINE FROM BUS 324147 [5HOWARDS BR 161.00] TO BUS 324155 [5PINEVILLE 1161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 851 324149-324157(1) | OPEN LINE FROM BUS 324149 [5IMBODEN 161.00] TO BUS 324157 [5POCKET N 161.00] CKT 1 | -31.4813 | 31.4813 | 33 | 95.398 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 852 324149-324583(1) | OPEN LINE FROM BUS 324149 [5IMBODEN 161.00] TO BUS 324583 [2IMBODEN 69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3979 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 853 324150-324154(1) | OPEN LINE FROM BUS 324150 [5LEBANON JCT161.00] TO BUS 324154 [5PADDYS RUN 161.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 854 324151-324161(1) | OPEN LINE FROM BUS 324151 [5LIVNGSTN CO161.00] TO BUS 324161 [5S PADUCAH 161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 855 324151-325028(1) | OPEN LINE FROM BUS 324151 [5LIVNGSTN CO161.00] TO BUS 325028 [5ASHWD SL TP161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 856 324152-324165(1) | OPEN LINE FROM BUS 324152 [5LAKE REBA T161.00] TO BUS 324165 [5W IRVINE T 161.00] CKT 1 | -31.4812 | 31.4812 | 33 | 95.3976 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 857 324152-324276(1) | OPEN LINE FROM BUS 324152 [5LAKE REBA T161.00] TO BUS 324276 [4LAKE REBA T138.00] CKT 1 | -31.4812 | 31.4812 | 33 | 95.3976 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 858 324153-324645(1) | OPEN LINE FROM BUS 324153 [5MORGANFIELD161.00] TO BUS 324645 [2MORGANFIELD69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 859 324155-324156(1) | OPEN LINE FROM BUS 324155 [5PINEVILLE 1161.00] TO BUS 324156 [5PINEVILE SW161.00] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3979 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 860 324155-324167(Z1) | OPEN LINE FROM BUS 324155 [5PINEVILLE 1161.00] TO BUS 324167 [5PINEVILLE 2161.00] CKT Z1 | -31.4813 | 31.4813 | 33 | 95.3977 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 861 324155-324686(1) | OPEN LINE FROM BUS 324155 [5PINEVILLE 1161.00] TO BUS 324686 [2PINEVILLE 69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3978 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 862 324157-324158(1) | OPEN LINE FROM BUS 324157 [5POCKET N 161.00] TO BUS 324158 [5POCKET 161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 863 324158-324689(1) | OPEN LINE FROM BUS 324158 [5POCKET 161.00] TO BUS 324689 [2POCKET 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 864 324159-324160(1) | OPEN LINE FROM BUS 324159 [5RIVER QUEEN161.00] TO BUS 324160 [5RIVER QN T 161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 865 324159-324702(1) | OPEN LINE FROM BUS 324159 [5RIVER QUEEN161.00] TO BUS 324702 [2RIVER QUEEN69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 866 324161-324712(1) | OPEN LINE FROM BUS 324161 [5S PADUCAH 161.00] TO BUS 324712 [2SO PADUCAH 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 867 324161-325078(1) | OPEN LINE FROM BUS 324161 [5S PADUCAH 161.00] TO BUS 325078 [5PADUCAH PRI161.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 868 324163-324165(1) | OPEN LINE FROM BUS 324163 [5WEST IRVINE161.00] TO BUS 324165 [5W IRVINE T 161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 869 324163-324767(1) | OPEN LINE FROM BUS 324163 [5WEST IRVINE161.00] TO BUS 324767 [2WEST IRVINE69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 870 324164-324769(1) | OPEN LINE FROM BUS 324164 [5WALKER 161.00] TO BUS 324769 [2WALKER KU 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 871 324166-324779(1) | OPEN LINE FROM BUS 324166 [5WICKLIFFE 161.00] TO BUS 324779 [2WICKLIFFE 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 872 324166-325069(1) | OPEN LINE FROM BUS 324166 [5WICKLIFFE 161.00] TO BUS 325069 [5SONG SP TP 161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 873 324167-324686(2) | OPEN LINE FROM BUS 324167 [5PINEVILLE 2161.00] TO BUS 324686 [2PINEVILLE 69.000] CKT 2 | -31.4812 | 31.4812 | 33 | 95.3976 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 874 324191-324603(1) | OPEN LINE FROM BUS 324191 [2LEBANON E T69.000] TO BUS 324603 [2LEBANON CIT69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 875 324191-324606(1) | OPEN LINE FROM BUS 324191 [2LEBANON E T69.000] TO BUS 324606 [2LEBANON 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 876 324192-324240(1) | OPEN LINE FROM BUS 324192 [4DAYTON-WALT138.00] TO BUS 324240 [4DAY-WALT TP138.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 877 324193-324251(1) | OPEN LINE FROM BUS 324193 [4FLEMINGB KU138.00] TO BUS 324251 [4FLEMNB KU T138.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 878 324195-324722(1) | OPEN LINE FROM BUS 324195 [2AUGUSTA 69.000] TO BUS 324722 [2SHARON KU 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 879 324196-324224(1) | OPEN LINE FROM BUS 324196 [2BOONESB PRK69.000] TO BUS 324224 [2RED HOUSE 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 880 324196-324449(1) | OPEN LINE FROM BUS 324196 [2BOONESB PRK69.000] TO BUS 324449 [2BOONSBORO N69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 881 324198-324878(1) | OPEN LINE FROM BUS 324198 [2HUNT BOTTOM69.000] TO BUS 324878 [2HUNT BTM TP69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 882 324199-324252(1) | OPEN LINE FROM BUS 324199 [2OWENTON 69.000] TO BUS 324252 [2SCHOLLS 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 883 324200-324205(1) | OPEN LINE FROM BUS 324200 [4PLSUR RDG T138.00] TO BUS 324205 [4ASHBOTTOM 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 884 324200-324237(1) | OPEN LINE FROM BUS 324200 [4PLSUR RDG T138.00] TO BUS 324237 [4CANE RUN SW138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 885 324200-324299(1) | OPEN LINE FROM BUS 324200 [4PLSUR RDG T138.00] TO BUS 324299 [4PLEASUR RDG138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 886 324201-324305(1) | OPEN LINE FROM BUS 324201 [4ADAMS 138.00] TO BUS 324305 [4SCOTT CO 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 887 324201-324313(1) | OPEN LINE FROM BUS 324201 [4ADAMS 138.00] TO BUS 324313 [4TOYOTA S 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 888 324201-324315(1) | OPEN LINE FROM BUS 324201 [4ADAMS 138.00] TO BUS 324315 [4TYRONE 138.00] CKT 1 | -31.4819 | 31.4819 | 33 | 95.3998 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 889 324201-324335(1) | OPEN LINE FROM BUS 324201 [4ADAMS 138.00] TO BUS 324335 [4INNOVATION 138.00] CKT 1 | -31.4811 | 31.4811 | 33 | 95.3972 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 890 324201-324405(1) | OPEN LINE FROM BUS 324201 [4ADAMS 138.00] TO BUS 324405 [2ADAMS 69.000] CKT 1 | -31.4806 | 31.4806 | 33 | 95.3956 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 891 324201-324405(2) | OPEN LINE FROM BUS 324201 [4ADAMS 138.00] TO BUS 324405 [2ADAMS 69.000] CKT 2 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 892 324202-324241(1) | OPEN LINE FROM BUS 324202 [4ALGONQUIN 138.00] TO BUS 324241 [4DIXIE 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 893 324202-324408(1) | OPEN LINE FROM BUS 324202 [4ALGONQUIN 138.00] TO BUS 324408 [2ALGONQUIN 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 894 324203-324258(1) | OPEN LINE FROM BUS 324203 [4AMERICAN AV138.00] TO BUS 324258 [4HAEFLING 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 895 324203-324301(1) | OPEN LINE FROM BUS 324203 [4AMERICAN AV138.00] TO BUS 324301 [4REYNOLDS 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 896 324203-324409(1) | OPEN LINE FROM BUS 324203 [4AMERICAN AV138.00] TO BUS 324409 [2AMERICAN AV69.000] CKT 1 | -31.4817 | 31.4817 | 33 | 95.3991 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 897 324204-324205(1) | OPEN LINE FROM BUS 324204 [4APPLIANC PK138.00] TO BUS 324205 [4ASHBOTTOM 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 898 324204-324243(1) | OPEN LINE FROM BUS 324204 [4APPLIANC PK138.00] TO BUS 324243 [4ETHEL 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 899 324204-324281(1) | OPEN LINE FROM BUS 324204 [4APPLIANC PK138.00] TO BUS 324281 [4MIDDLETOWN 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 900 324205-324237(1) | OPEN LINE FROM BUS 324205 [4ASHBOTTOM 138.00] TO BUS 324237 [4CANE RUN SW138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 901 324205-324257(1) | OPEN LINE FROM BUS 324205 [4ASHBOTTOM 138.00] TO BUS 324257 [4GRADE LANE 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 902 324205-324279(1) | OPEN LINE FROM BUS 324205 [4ASHBOTTOM 138.00] TO BUS 324279 [4MANSLICK 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 903 324205-324419(1) | OPEN LINE FROM BUS 324205 [4ASHBOTTOM 138.00] TO BUS 324419 [2ASHBOT WEST69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 904 324205-325023(2) | OPEN LINE FROM BUS 324205 [4ASHBOTTOM 138.00] TO BUS 325023 [2ASHBOT EAST69.000] CKT 2 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 905 324206-324284(1) | OPEN LINE FROM BUS 324206 [4ASHBY 138.00] TO BUS 324284 [4MILL CREEK 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 906 324206-324299(1) | OPEN LINE FROM BUS 324206 [4ASHBY 138.00] TO BUS 324299 [4PLEASUR RDG138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 907 324207-324218(1) | OPEN LINE FROM BUS 324207 [4BARDSTOWN 138.00] TO BUS 324218 [4BROWN CT 138.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 908 324207-324288(1) | OPEN LINE FROM BUS 324207 [4BARDSTOWN 138.00] TO BUS 324288 [4NELSON CO 138.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 909 324207-324426(1) | OPEN LINE FROM BUS 324207 [4BARDSTOWN 138.00] TO BUS 324426 [2BARDSTOWN 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 910 324208-324265(1) | OPEN LINE FROM BUS 324208 [4BEARGRASS 138.00] TO BUS 324265 [4JEFFRSONV T138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 911 324208-324277(1) | OPEN LINE FROM BUS 324208 [4BEARGRASS 138.00] TO BUS 324277 [4LYNDON SO 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 912 324208-324289(1) | OPEN LINE FROM BUS 324208 [4BEARGRASS 138.00] TO BUS 324289 [4NORTHSIDE 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 913 324208-324298(1) | OPEN LINE FROM BUS 324208 [4BEARGRASS 138.00] TO BUS 324298 [4PLAINVIEW T138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 914 324208-324321(1) | OPEN LINE FROM BUS 324208 [4BEARGRASS 138.00] TO BUS 324321 [4WATERSIDE 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 915 324208-324321(2) | OPEN LINE FROM BUS 324208 [4BEARGRASS 138.00] TO BUS 324321 [4WATERSIDE 138.00] CKT 2 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 916 324208-324429(1) | OPEN LINE FROM BUS 324208 [4BEARGRASS 138.00] TO BUS 324429 [2BEARGRASS 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 917 324209-324263(1) | OPEN LINE FROM BUS 324209 [4BG PARKWAY 138.00] TO BUS 324263 [4HURSTBORNE 138.00] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3989 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 918 324210-324262(1) | OPEN LINE FROM BUS 324210 [4BAKER LANE 138.00] TO BUS 324262 [4HIGBY MILL 138.00] CKT 1 | -31.4818 | 31.4818 | 33 | 95.3993 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 919 324210-324334(1) | OPEN LINE FROM BUS 324210 [4BAKER LANE 138.00] TO BUS 324334 [4BROWN N 2-R138.00] CKT 1 | -31.4828 | 31.4828 | 33 | 95.4024 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 920 324211-324221(1) | OPEN LINE FROM BUS 324211 [4BLACKWELL 138.00] TO BUS 324221 [4BUTLER 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 921 324211-324253(1) | OPEN LINE FROM BUS 324211 [4BLACKWELL 138.00] TO BUS 324253 [4GHENT 138.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 922 324212-324285(1) | OPEN LINE FROM BUS 324212 [4BLUE LICK 138.00] TO BUS 324285 [4MUD LANE 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 923 324213-324270(1) | OPEN LINE FROM BUS 324213 [4BONNIEVILLE138.00] TO BUS 324270 [4LEBANON WES138.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 924 324213-324447(1) | OPEN LINE FROM BUS 324213 [4BONNIEVILLE138.00] TO BUS 324447 [2BONNIE KU 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 925 324213-324800(1) | OPEN LINE FROM BUS 324213 [4BONNIEVILLE138.00] TO BUS 324800 [4MERE TVA 138.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 926 324214-324243(1) | OPEN LINE FROM BUS 324214 [4BRECKNRIDGE138.00] TO BUS 324243 [4ETHEL 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 927 324214-324263(1) | OPEN LINE FROM BUS 324214 [4BRECKNRIDGE138.00] TO BUS 324263 [4HURSTBORNE 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 928 324214-324451(1) | OPEN LINE FROM BUS 324214 [4BRECKNRIDGE138.00] TO BUS 324451 [2BRECKNRIDGE69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 929 324215-324237(1) | OPEN LINE FROM BUS 324215 [4BRIDGPOR HE138.00] TO BUS 324237 [4CANE RUN SW138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 930 324215-324284(1) | OPEN LINE FROM BUS 324215 [4BRIDGPOR HE138.00] TO BUS 324284 [4MILL CREEK 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 931 324217-324219(1) | OPEN LINE FROM BUS 324217 [4BROWN PLANT138.00] TO BUS 324219 [4BROWN T1 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 932 324217-324220(1) | OPEN LINE FROM BUS 324217 [4BROWN PLANT138.00] TO BUS 324220 [4BROWN T2 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 933 324217-324239(1) | OPEN LINE FROM BUS 324217 [4BROWN PLANT138.00] TO BUS 324239 [4DANVILE N T138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 934 324217-324248(1) | OPEN LINE FROM BUS 324217 [4BROWN PLANT138.00] TO BUS 324248 [4FAWKES KU 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 935 324218-324219(1) | OPEN LINE FROM BUS 324218 [4BROWN CT 138.00] TO BUS 324219 [4BROWN T1 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 936 324218-324220(1) | OPEN LINE FROM BUS 324218 [4BROWN CT 138.00] TO BUS 324220 [4BROWN T2 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 937 324218-325957(1) | OPEN LINE FROM BUS 324218 [4BROWN CT 138.00] TO BUS 325957 [4BROWN N 1 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 938 324219-325957(1) | OPEN LINE FROM BUS 324219 [4BROWN T1 138.00] TO BUS 325957 [4BROWN N 1 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 939 324220-325956(1) | OPEN LINE FROM BUS 324220 [4BROWN T2 138.00] TO BUS 325956 [4BROWN N 2 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 940 324221-324225(1) | OPEN LINE FROM BUS 324221 [4BUTLER 138.00] TO BUS 324225 [4CARNTOWN TP138.00] CKT 1 | -31.4813 | 31.4813 | 33 | 95.398 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 941 324222-324237(1) | OPEN LINE FROM BUS 324222 [4CAMPGROUND 138.00] TO BUS 324237 [4CANE RUN SW138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 942 324222-324295(1) | OPEN LINE FROM BUS 324222 [4CAMPGROUND 138.00] TO BUS 324295 [4PADDYS RUN 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 943 324223-324294(1) | OPEN LINE FROM BUS 324223 [4CANAL 138.00] TO BUS 324294 [4PADDYS WEST138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 944 324223-324321(1) | OPEN LINE FROM BUS 324223 [4CANAL 138.00] TO BUS 324321 [4WATERSIDE 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 945 324223-324462(1) | OPEN LINE FROM BUS 324223 [4CANAL 138.00] TO BUS 324462 [2CANAL 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 946 324225-324226(1) | OPEN LINE FROM BUS 324225 [4CARNTOWN TP138.00] TO BUS 324226 [4CARNTOWN 138.00] CKT 1 | -31.4808 | 31.4808 | 33 | 95.3962 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 947 324225-324267(1) | OPEN LINE FROM BUS 324225 [4CARNTOWN TP138.00] TO BUS 324267 [4KENTON 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 948 324226-324463(1) | OPEN LINE FROM BUS 324226 [4CARNTOWN 138.00] TO BUS 324463 [2CARNTOWN 69.000] CKT 1 | -31.4807 | 31.4807 | 33 | 95.3962 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 949 324227-324274(1) | OPEN LINE FROM BUS 324227 [4CARROLLTON 138.00] TO BUS 324274 [4LOCKPORT 138.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 950 324227-324466(1) | OPEN LINE FROM BUS 324227 [4CARROLLTON 138.00] TO BUS 324466 [2CARROLLTON 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 951 324227-324466(2) | OPEN LINE FROM BUS 324227 [4CARROLLTON 138.00] TO BUS 324466 [2CARROLLTON 69.000] CKT 2 | -31.4817 | 31.4817 | 33 | 95.399 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 952 324227-326512(1) | OPEN LINE FROM BUS 324227 [4CARROLLTON 138.00] TO BUS 326512 [4AIRGAS 138.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 953 324228-324281(1) | OPEN LINE FROM BUS 324228 [4CENTERFIELD138.00] TO BUS 324281 [4MIDDLETOWN 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 954 324228-324469(1) | OPEN LINE FROM BUS 324228 [4CENTERFIELD138.00] TO BUS 324469 [2CENTERFIELD69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 955 324228-326520(1) | OPEN LINE FROM BUS 324228 [4CENTERFIELD138.00] TO BUS 326520 [4TRIMBLE TR9138.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 956 324229-324236(1) | OPEN LINE FROM BUS 324229 [4CLARK CO 138.00] TO BUS 324236 [4RICHMND NO 138.00] CKT 1 | -31.4819 | 31.4819 | 33 | 95.3996 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 957 324229-324310(1) | OPEN LINE FROM BUS 324229 [4CLARK CO 138.00] TO BUS 324310 [4SPENCER RD 138.00] CKT 1 | -31.4812 | 31.4812 | 33 | 95.3975 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 958 324229-324472(1) | OPEN LINE FROM BUS 324229 [4CLARK CO 138.00] TO BUS 324472 [2CLARK CO 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 959 324230-324262(1) | OPEN LINE FROM BUS 324230 [4CLAYS MILL 138.00] TO BUS 324262 [4HIGBY MILL 138.00] CKT 1 | -31.4818 | 31.4818 | 33 | 95.3993 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 960 324230-325957(1) | OPEN LINE FROM BUS 324230 [4CLAYS MILL 138.00] TO BUS 325957 [4BROWN N 1 138.00] CKT 1 | -31.4823 | 31.4824 | 33 | 95.4011 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 961 324231-324256(1) | OPEN LINE FROM BUS 324231 [4CLOVERPORT 138.00] TO BUS 324256 [4GR RVR STL 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 962 324231-324260(1) | OPEN LINE FROM BUS 324231 [4CLOVERPORT 138.00] TO BUS 324260 [4HARDINSBURG138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 963 324231-325132(1) | OPEN LINE FROM BUS 324231 [4CLOVERPORT 138.00] TO BUS 325132 [4GREENSOL TP138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 964 324232-326574(1) | OPEN LINE FROM BUS 324232 [4CANE RN 11A138.00] TO BUS 326574 [4CR11 TAP 138.00] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 965 324236-324248(1) | OPEN LINE FROM BUS 324236 [4RICHMND NO 138.00] TO BUS 324248 [4FAWKES KU 138.00] CKT 1 | -31.4819 | 31.4819 | 33 | 95.3998 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 966 324237-324295(1) | OPEN LINE FROM BUS 324237 [4CANE RUN SW138.00] TO BUS 324295 [4PADDYS RUN 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 967 324237-324488(1) | OPEN LINE FROM BUS 324237 [4CANE RUN SW138.00] TO BUS 324488 [2CANE RUN SW69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 968 324237-324488(2) | OPEN LINE FROM BUS 324237 [4CANE RUN SW138.00] TO BUS 324488 [2CANE RUN SW69.000] CKT 2 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 969 324237-325096(22) | OPEN LINE FROM BUS 324237 [4CANE RUN SW138.00] TO BUS 325096 [4CANERN NGCC138.00] CKT 22 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 970 324237-325096(24) | OPEN LINE FROM BUS 324237 [4CANE RUN SW138.00] TO BUS 325096 [4CANERN NGCC138.00] CKT 24 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 971 324237-325096(25) | OPEN LINE FROM BUS 324237 [4CANE RUN SW138.00] TO BUS 325096 [4CANERN NGCC138.00] CKT 25 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
342000 | 5GAS | 161 | 342760 | 5LIBERTY J | 161 | 1 | SINGLE OPN TIE 693 342736-324138(1) | OPEN LINE FROM BUS 342736 [5GREEN HAL T161.00] TO BUS 324138 [5DELVINTA 161.00] CKT 1 | 146.9086 | 146.9086 | 153 | 96.0187 | EKPC
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 972 324237-326565(23) | OPEN LINE FROM BUS 324237 [4CANE RUN SW138.00] TO BUS 326565 [4INTRNTL TAP138.00] CKT 23 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 973 324237-326574(21) | OPEN LINE FROM BUS 324237 [4CANE RUN SW138.00] TO BUS 326574 [4CR11 TAP 138.00] CKT 21 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 974 324238-324239(1) | OPEN LINE FROM BUS 324238 [4DANVILLE N 138.00] TO BUS 324239 [4DANVILE N T138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324941 | 2RIVERPORT | 69 | 324975 | 2TERRY | 69 | 1 | B-69-337 | B-69-337 | 60.4907 | 60.4907 | 63 | 96.017 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 975 324238-324495(1) | OPEN LINE FROM BUS 324238 [4DANVILLE N 138.00] TO BUS 324495 [2DANVILLE N 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
342000 | 5GAS | 161 | 342760 | 5LIBERTY J | 161 | 1 | SINGLE OPN LIN 1499 324606-324736(1) | OPEN LINE FROM BUS 324606 [2LEBANON 69.000] TO BUS 324736 [2SPRINGFL KU69.000] CKT 1 | 146.8606 | 146.8606 | 153 | 95.9873 | EKPC
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 976 324239-325121(1) | OPEN LINE FROM BUS 324239 [4DANVILE N T138.00] TO BUS 325121 [4LOGAN TP 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 977 324240-324242(1) | OPEN LINE FROM BUS 324240 [4DAY-WALT TP138.00] TO BUS 324242 [4DOW CORN W 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 978 324240-324287(1) | OPEN LINE FROM BUS 324240 [4DAY-WALT TP138.00] TO BUS 324287 [4NAS TAP 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 979 324241-324295(1) | OPEN LINE FROM BUS 324241 [4DIXIE 138.00] TO BUS 324295 [4PADDYS RUN 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 980 324242-326512(1) | OPEN LINE FROM BUS 324242 [4DOW CORN W 138.00] TO BUS 326512 [4AIRGAS 138.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 981 324243-324518(1) | OPEN LINE FROM BUS 324243 [4ETHEL 138.00] TO BUS 324518 [2ETHEL 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 982 324244-324261(1) | OPEN LINE FROM BUS 324244 [4ETOWN 138.00] TO BUS 324261 [4HARDIN CO 138.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 983 324244-324288(1) | OPEN LINE FROM BUS 324244 [4ETOWN 138.00] TO BUS 324288 [4NELSON CO 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 984 324244-324519(1) | OPEN LINE FROM BUS 324244 [4ETOWN 138.00] TO BUS 324519 [2ETOWN KU 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 985 324245-324246(1) | OPEN LINE FROM BUS 324245 [4FARMERS TAP138.00] TO BUS 324246 [4FARMERS 138.00] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3978 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 986 324245-324307(1) | OPEN LINE FROM BUS 324245 [4FARMERS TAP138.00] TO BUS 324307 [4SHARKEY TAP138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 987 324245-324310(1) | OPEN LINE FROM BUS 324245 [4FARMERS TAP138.00] TO BUS 324310 [4SPENCER RD 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 988 324246-324528(1) | OPEN LINE FROM BUS 324246 [4FARMERS 138.00] TO BUS 324528 [2FARMERS 69.000] CKT 1 | -31.4811 | 31.4811 | 33 | 95.3974 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 989 324247-324248(1) | OPEN LINE FROM BUS 324247 [4FAWKES TAP 138.00] TO BUS 324248 [4FAWKES KU 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 990 324247-324276(1) | OPEN LINE FROM BUS 324247 [4FAWKES TAP 138.00] TO BUS 324276 [4LAKE REBA T138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 991 324248-324530(1) | OPEN LINE FROM BUS 324248 [4FAWKES KU 138.00] TO BUS 324530 [2FAWKES 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 992 324248-324530(2) | OPEN LINE FROM BUS 324248 [4FAWKES KU 138.00] TO BUS 324530 [2FAWKES 69.000] CKT 2 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 993 324249-324257(1) | OPEN LINE FROM BUS 324249 [4FERN VALLEY138.00] TO BUS 324257 [4GRADE LANE 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 994 324249-324292(1) | OPEN LINE FROM BUS 324249 [4FERN VALLEY138.00] TO BUS 324292 [4OKOLONA 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 995 324249-324322(1) | OPEN LINE FROM BUS 324249 [4FERN VALLEY138.00] TO BUS 324322 [4WATTERSON 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 996 324249-324532(1) | OPEN LINE FROM BUS 324249 [4FERN VALLEY138.00] TO BUS 324532 [2FERN VALLEY69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 997 324249-324532(2) | OPEN LINE FROM BUS 324249 [4FERN VALLEY138.00] TO BUS 324532 [2FERN VALLEY69.000] CKT 2 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 998 324250-324306(1) | OPEN LINE FROM BUS 324250 [4E FRANKFORT138.00] TO BUS 324306 [4SHADRACK 138.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 999 324250-324315(1) | OPEN LINE FROM BUS 324250 [4E FRANKFORT138.00] TO BUS 324315 [4TYRONE 138.00] CKT 1 | -31.4818 | 31.4818 | 33 | 95.3993 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1000 324250-324535(1) | OPEN LINE FROM BUS 324250 [4E FRANKFORT138.00] TO BUS 324535 [2E FRANKFORT69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1001 324250-324535(2) | OPEN LINE FROM BUS 324250 [4E FRANKFORT138.00] TO BUS 324535 [2E FRANKFORT69.000] CKT 2 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1002 324251-324254(1) | OPEN LINE FROM BUS 324251 [4FLEMNB KU T138.00] TO BUS 324254 [4GODDARD KU 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1003 324251-324323(1) | OPEN LINE FROM BUS 324251 [4FLEMNB KU T138.00] TO BUS 324323 [4WEDONIA 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1004 324252-324455(1) | OPEN LINE FROM BUS 324252 [2SCHOLLS 69.000] TO BUS 324455 [2BROMLEY 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1005 324253-324287(1) | OPEN LINE FROM BUS 324253 [4GHENT 138.00] TO BUS 324287 [4NAS TAP 138.00] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1006 324253-324290(1) | OPEN LINE FROM BUS 324253 [4GHENT 138.00] TO BUS 324290 [4OWEN CO TAP138.00] CKT 1 | -31.4818 | 31.4818 | 33 | 95.3993 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1007 324253-324831(1) | OPEN LINE FROM BUS 324253 [4GHENT 138.00] TO BUS 324831 [4WHITE SULPH138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1008 324254-324302(1) | OPEN LINE FROM BUS 324254 [4GODDARD KU 138.00] TO BUS 324302 [4RODBURN 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1009 324255-324291(1) | OPEN LINE FROM BUS 324255 [4GREEN RIVER138.00] TO BUS 324291 [4OHIO COUNTY138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1010 324255-324550(1) | OPEN LINE FROM BUS 324255 [4GREEN RIVER138.00] TO BUS 324550 [2GREEN RIVER69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1011 324255-324550(2) | OPEN LINE FROM BUS 324255 [4GREEN RIVER138.00] TO BUS 324550 [2GREEN RIVER69.000] CKT 2 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1012 324255-325015(1) | OPEN LINE FROM BUS 324255 [4GREEN RIVER138.00] TO BUS 325015 [4SMITH TAP 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1013 324256-324551(1) | OPEN LINE FROM BUS 324256 [4GR RVR STL 138.00] TO BUS 324551 [2GR RVR STL 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1014 324256-325015(1) | OPEN LINE FROM BUS 324256 [4GR RVR STL 138.00] TO BUS 325015 [4SMITH TAP 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1015 324258-324264(1) | OPEN LINE FROM BUS 324258 [4HAEFLING 138.00] TO BUS 324264 [4IBM NORTHTP138.00] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3988 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1016 324258-324317(1) | OPEN LINE FROM BUS 324258 [4HAEFLING 138.00] TO BUS 324317 [4VILEY ROAD 138.00] CKT 1 | -31.482 | 31.482 | 33 | 95.4 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1017 324258-324335(1) | OPEN LINE FROM BUS 324258 [4HAEFLING 138.00] TO BUS 324335 [4INNOVATION 138.00] CKT 1 | -31.481 | 31.481 | 33 | 95.397 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1018 324258-324558(1) | OPEN LINE FROM BUS 324258 [4HAEFLING 138.00] TO BUS 324558 [2HAEFLING 69.000] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1019 324258-325100(1) | OPEN LINE FROM BUS 324258 [4HAEFLING 138.00] TO BUS 325100 [4W LEX R1 138.00] CKT 1 | -31.4822 | 31.4822 | 33 | 95.4005 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1020 324259-324278(1) | OPEN LINE FROM BUS 324259 [4HANCOCK 138.00] TO BUS 324278 [4MAGAZINE 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1021 324259-324561(1) | OPEN LINE FROM BUS 324259 [4HANCOCK 138.00] TO BUS 324561 [2HANCOCK 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1022 324260-325055(1) | OPEN LINE FROM BUS 324260 [4HARDINSBURG138.00] TO BUS 325055 [4RHUDES TP 138.00] CKT 1 | -31.4814 | 31.4815 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1023 324261-324303(1) | OPEN LINE FROM BUS 324261 [4HARDIN CO 138.00] TO BUS 324303 [4ROGERSVILLE138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1024 324261-324563(1) | OPEN LINE FROM BUS 324261 [4HARDIN CO 138.00] TO BUS 324563 [2HARDIN CO 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1025 324261-324563(2) | OPEN LINE FROM BUS 324261 [4HARDIN CO 138.00] TO BUS 324563 [2HARDIN CO 69.000] CKT 2 | -31.4815 | 31.4815 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1026 324262-324269(1) | OPEN LINE FROM BUS 324262 [4HIGBY MILL 138.00] TO BUS 324269 [4LANSDOWNE 138.00] CKT 1 | -31.4818 | 31.4818 | 33 | 95.3994 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1027 324262-324333(1) | OPEN LINE FROM BUS 324262 [4HIGBY MILL 138.00] TO BUS 324333 [4BROWN N 1-R138.00] CKT 1 | -31.4826 | 31.4826 | 33 | 95.4017 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1028 324262-324568(1) | OPEN LINE FROM BUS 324262 [4HIGBY MILL 138.00] TO BUS 324568 [2HIGBY 618 69.000] CKT 1 | -31.4799 | 31.4799 | 33 | 95.3937 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1029 324262-324569(1) | OPEN LINE FROM BUS 324262 [4HIGBY MILL 138.00] TO BUS 324569 [2HIGBY 608 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1030 324262-324569(2) | OPEN LINE FROM BUS 324262 [4HIGBY MILL 138.00] TO BUS 324569 [2HIGBY 608 69.000] CKT 2 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1031 324262-325089(Z1) | OPEN LINE FROM BUS 324262 [4HIGBY MILL 138.00] TO BUS 325089 [4HIGBY MILL2138.00] CKT Z1 | -31.4813 | 31.4813 | 33 | 95.398 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1032 324263-324297(1) | OPEN LINE FROM BUS 324263 [4HURSTBORNE 138.00] TO BUS 324297 [4PLAINVIEW 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1033 324264-324275(1) | OPEN LINE FROM BUS 324264 [4IBM NORTHTP138.00] TO BUS 324275 [4LOUDON AVE 138.00] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1034 324264-326548(1) | OPEN LINE FROM BUS 324264 [4IBM NORTHTP138.00] TO BUS 326548 [4IBM NORTH 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1035 324265-324289(1) | OPEN LINE FROM BUS 324265 [4JEFFRSONV T138.00] TO BUS 324289 [4NORTHSIDE 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1036 324267-324323(1) | OPEN LINE FROM BUS 324267 [4KENTON 138.00] TO BUS 324323 [4WEDONIA 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1037 324267-324589(1) | OPEN LINE FROM BUS 324267 [4KENTON 138.00] TO BUS 324589 [2KENTON 688 69.000] CKT 1 | -31.4812 | 31.4812 | 33 | 95.3976 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1038 324267-324882(1) | OPEN LINE FROM BUS 324267 [4KENTON 138.00] TO BUS 324882 [2KENTON 698 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1039 324268-324284(1) | OPEN LINE FROM BUS 324268 [4KNOB CREEK 138.00] TO BUS 324284 [4MILL CREEK 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1040 324268-324300(1) | OPEN LINE FROM BUS 324268 [4KNOB CREEK 138.00] TO BUS 324300 [4POND CREEK 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1041 324269-324601(1) | OPEN LINE FROM BUS 324269 [4LANSDOWNE 138.00] TO BUS 324601 [2LANSDOWNE 69.000] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3988 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1042 324270-324271(1) | OPEN LINE FROM BUS 324270 [4LEBANON WES138.00] TO BUS 324271 [4LEBANON 138.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1043 324271-324606(1) | OPEN LINE FROM BUS 324271 [4LEBANON 138.00] TO BUS 324606 [2LEBANON 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1044 324271-324606(2) | OPEN LINE FROM BUS 324271 [4LEBANON 138.00] TO BUS 324606 [2LEBANON 69.000] CKT 2 | -31.4815 | 31.4815 | 33 | 95.3983 | LGEE
342000 | 5GAS | 161 | 342760 | 5LIBERTY J | 161 | 1 | SINGLE OPN LIN 585 342736-342820(1) | OPEN LINE FROM BUS 342736 [5GREEN HAL T161.00] TO BUS 342820 [5TYNER 161.00] CKT 1 | 146.7821 | 146.7821 | 153 | 95.936 | EKPC
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1045 324271-325121(1) | OPEN LINE FROM BUS 324271 [4LEBANON 138.00] TO BUS 325121 [4LOGAN TP 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1046 324272-324308(1) | OPEN LINE FROM BUS 324272 [4LEITCHFIELD138.00] TO BUS 324308 [4SHREWSBURY 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1047 324272-324609(1) | OPEN LINE FROM BUS 324272 [4LEITCHFIELD138.00] TO BUS 324609 [2LEITCHFIELD69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1048 324273-326559(Z1) | OPEN LINE FROM BUS 324273 [4LAKE REBA 138.00] TO BUS 326559 [4BGAD TAP 138.00] CKT Z1 | -31.4816 | 31.4816 | 33 | 95.3988 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1049 324274-324306(1) | OPEN LINE FROM BUS 324274 [4LOCKPORT 138.00] TO BUS 324306 [4SHADRACK 138.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1050 324275-324618(1) | OPEN LINE FROM BUS 324275 [4LOUDON AVE 138.00] TO BUS 324618 [2LOUDON 628 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1051 324276-326559(1) | OPEN LINE FROM BUS 324276 [4LAKE REBA T138.00] TO BUS 326559 [4BGAD TAP 138.00] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3989 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1052 324277-324281(1) | OPEN LINE FROM BUS 324277 [4LYNDON SO 138.00] TO BUS 324281 [4MIDDLETOWN 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1053 324277-324622(1) | OPEN LINE FROM BUS 324277 [4LYNDON SO 138.00] TO BUS 324622 [2LYNDON SO 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1054 324278-324321(1) | OPEN LINE FROM BUS 324278 [4MAGAZINE 138.00] TO BUS 324321 [4WATERSIDE 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1055 324279-324284(1) | OPEN LINE FROM BUS 324279 [4MANSLICK 138.00] TO BUS 324284 [4MILL CREEK 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1056 324281-324282(1) | OPEN LINE FROM BUS 324281 [4MIDDLETOWN 138.00] TO BUS 324282 [4MIDDLETWN-R138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.398 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1057 324281-324364(1) | OPEN LINE FROM BUS 324281 [4MIDDLETOWN 138.00] TO BUS 324364 [4OLD HENRY 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1058 324281-324637(1) | OPEN LINE FROM BUS 324281 [4MIDDLETOWN 138.00] TO BUS 324637 [2MIDDLETOWN 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1059 324281-324637(2) | OPEN LINE FROM BUS 324281 [4MIDDLETOWN 138.00] TO BUS 324637 [2MIDDLETOWN 69.000] CKT 2 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1060 324281-324637(6) | OPEN LINE FROM BUS 324281 [4MIDDLETOWN 138.00] TO BUS 324637 [2MIDDLETOWN 69.000] CKT 6 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1061 324281-325042(1) | OPEN LINE FROM BUS 324281 [4MIDDLETOWN 138.00] TO BUS 325042 [4JEFERSONTWN138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1062 324282-324298(1) | OPEN LINE FROM BUS 324282 [4MIDDLETWN-R138.00] TO BUS 324298 [4PLAINVIEW T138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.398 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1063 324283-324320(1) | OPEN LINE FROM BUS 324283 [4MIDWAY 138.00] TO BUS 324320 [4W LEXINGTON138.00] CKT 1 | -31.4813 | 31.4813 | 33 | 95.398 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1064 324283-324831(1) | OPEN LINE FROM BUS 324283 [4MIDWAY 138.00] TO BUS 324831 [4WHITE SULPH138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1065 324284-324640(7) | OPEN LINE FROM BUS 324284 [4MILL CREEK 138.00] TO BUS 324640 [2MILL CREEK 69.000] CKT 7 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1066 324284-324640(8) | OPEN LINE FROM BUS 324284 [4MILL CREEK 138.00] TO BUS 324640 [2MILL CREEK 69.000] CKT 8 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1067 324284-325088(1) | OPEN LINE FROM BUS 324284 [4MILL CREEK 138.00] TO BUS 325088 [4MIL CK YARD138.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1068 324285-324292(1) | OPEN LINE FROM BUS 324285 [4MUD LANE 138.00] TO BUS 324292 [4OKOLONA 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1069 324285-324651(1) | OPEN LINE FROM BUS 324285 [4MUD LANE 138.00] TO BUS 324651 [2MUD LANE 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1070 324286-324287(1) | OPEN LINE FROM BUS 324286 [4NAS 138.00] TO BUS 324287 [4NAS TAP 138.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1071 324289-325013(1) | OPEN LINE FROM BUS 324289 [4NORTHSIDE 138.00] TO BUS 325013 [4CLIFTY TAP1138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1072 324290-324305(1) | OPEN LINE FROM BUS 324290 [4OWEN CO TAP138.00] TO BUS 324305 [4SCOTT CO 138.00] CKT 1 | -31.4821 | 31.4821 | 33 | 95.4002 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1073 324291-324667(1) | OPEN LINE FROM BUS 324291 [4OHIO COUNTY138.00] TO BUS 324667 [2OHIO COUNTY69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1074 324294-324295(1) | OPEN LINE FROM BUS 324294 [4PADDYS WEST138.00] TO BUS 324295 [4PADDYS RUN 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1075 324296-324320(1) | OPEN LINE FROM BUS 324296 [4PISGAH 138.00] TO BUS 324320 [4W LEXINGTON138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1076 324296-324687(1) | OPEN LINE FROM BUS 324296 [4PISGAH 138.00] TO BUS 324687 [2PISGAH 69.000] CKT 1 | -31.4822 | 31.4822 | 33 | 95.4006 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1077 324296-325857(1) | OPEN LINE FROM BUS 324296 [4PISGAH 138.00] TO BUS 325857 [4BROWN N TIE138.00] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3988 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1078 324297-324298(1) | OPEN LINE FROM BUS 324297 [4PLAINVIEW 138.00] TO BUS 324298 [4PLAINVIEW T138.00] CKT 1 | -31.4813 | 31.4813 | 33 | 95.398 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1079 324300-324311(1) | OPEN LINE FROM BUS 324300 [4POND CREEK 138.00] TO BUS 324311 [4TIP TOP 138.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1080 324301-325089(1) | OPEN LINE FROM BUS 324301 [4REYNOLDS 138.00] TO BUS 325089 [4HIGBY MILL2138.00] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1081 324302-324307(1) | OPEN LINE FROM BUS 324302 [4RODBURN 138.00] TO BUS 324307 [4SHARKEY TAP138.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1082 324303-324708(1) | OPEN LINE FROM BUS 324303 [4ROGERSVILLE138.00] TO BUS 324708 [2ROGERSVILLE69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1083 324304-324762(1) | OPEN LINE FROM BUS 324304 [2VERSAILLE W69.000] TO BUS 324762 [2VERSAIL W T69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1084 324305-324951(1) | OPEN LINE FROM BUS 324305 [4SCOTT CO 138.00] TO BUS 324951 [2SCOTT CO 69.000] CKT 1 | -31.4812 | 31.4812 | 33 | 95.3977 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1085 324305-324991(1) | OPEN LINE FROM BUS 324305 [4SCOTT CO 138.00] TO BUS 324991 [4ROGERS GAP 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1086 324307-326556(1) | OPEN LINE FROM BUS 324307 [4SHARKEY TAP138.00] TO BUS 326556 [4N SHARKEY T138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1087 324310-324733(1) | OPEN LINE FROM BUS 324310 [4SPENCER RD 138.00] TO BUS 324733 [2SPENCER RD 69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3978 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1088 324310-325009(1) | OPEN LINE FROM BUS 324310 [4SPENCER RD 138.00] TO BUS 325009 [2SPENCER A 69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3978 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1089 324311-324976(3) | OPEN LINE FROM BUS 324311 [4TIP TOP 138.00] TO BUS 324976 [2TIP TOP 1 69.000] CKT 3 | -31.4816 | 31.4816 | 33 | 95.3988 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1090 324311-325132(1) | OPEN LINE FROM BUS 324311 [4TIP TOP 138.00] TO BUS 325132 [4GREENSOL TP138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1091 324312-324313(1) | OPEN LINE FROM BUS 324312 [4TOYOTA N 138.00] TO BUS 324313 [4TOYOTA S 138.00] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3979 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1092 324312-324991(1) | OPEN LINE FROM BUS 324312 [4TOYOTA N 138.00] TO BUS 324991 [4ROGERS GAP 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1093 324314-326520(Z1) | OPEN LINE FROM BUS 324314 [4TRIMBLE CO 138.00] TO BUS 326520 [4TRIMBLE TR9138.00] CKT Z1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1094 324315-324755(1) | OPEN LINE FROM BUS 324315 [4TYRONE 138.00] TO BUS 324755 [2TYRONE 69.000] CKT 1 | -31.4817 | 31.4817 | 33 | 95.3989 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1095 324315-325957(1) | OPEN LINE FROM BUS 324315 [4TYRONE 138.00] TO BUS 325957 [4BROWN N 1 138.00] CKT 1 | -31.4817 | 31.4817 | 33 | 95.399 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1096 324316-324759(1) | OPEN LINE FROM BUS 324316 [4VIRGINIA CI138.00] TO BUS 324759 [2VIRGINIA CI69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1097 324317-325101(1) | OPEN LINE FROM BUS 324317 [4VILEY ROAD 138.00] TO BUS 325101 [4W LEX R2 138.00] CKT 1 | -31.4822 | 31.4822 | 33 | 95.4006 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1098 324318-324764(1) | OPEN LINE FROM BUS 324318 [4WEST CLIFF 138.00] TO BUS 324764 [2WEST CLIFF 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1099 324318-324764(2) | OPEN LINE FROM BUS 324318 [4WEST CLIFF 138.00] TO BUS 324764 [2WEST CLIFF 69.000] CKT 2 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1100 324319-324765(1) | OPEN LINE FROM BUS 324319 [4W FRANKFORT138.00] TO BUS 324765 [2W FRANKFORT69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1101 324320-325089(1) | OPEN LINE FROM BUS 324320 [4W LEXINGTON138.00] TO BUS 325089 [4HIGBY MILL2138.00] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3988 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1102 324320-325100(1) | OPEN LINE FROM BUS 324320 [4W LEXINGTON138.00] TO BUS 325100 [4W LEX R1 138.00] CKT 1 | -31.4821 | 31.4821 | 33 | 95.4004 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1103 324320-325101(1) | OPEN LINE FROM BUS 324320 [4W LEXINGTON138.00] TO BUS 325101 [4W LEX R2 138.00] CKT 1 | -31.4822 | 31.4822 | 33 | 95.4006 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1104 324322-324771(1) | OPEN LINE FROM BUS 324322 [4WATTERSON 138.00] TO BUS 324771 [2WATTERSON 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1105 324322-324771(2) | OPEN LINE FROM BUS 324322 [4WATTERSON 138.00] TO BUS 324771 [2WATTERSON 69.000] CKT 2 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1106 324322-325042(1) | OPEN LINE FROM BUS 324322 [4WATTERSON 138.00] TO BUS 325042 [4JEFERSONTWN138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1107 324328-324680(1) | OPEN LINE FROM BUS 324328 [4PARIS 138.00] TO BUS 324680 [2PARIS KU 69.000] CKT 1 | -31.4917 | 31.4917 | 33 | 95.4293 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1108 324329-324364(1) | OPEN LINE FROM BUS 324329 [4COLLINS 138.00] TO BUS 324364 [4OLD HENRY 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1109 324329-324481(1) | OPEN LINE FROM BUS 324329 [4COLLINS 138.00] TO BUS 324481 [2COLLINS 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1110 324330-324783(1) | OPEN LINE FROM BUS 324330 [2WINCHES IND69.000] TO BUS 324783 [2WINCHSTR KU69.000] CKT 1 | -31.4808 | 31.4808 | 33 | 95.3963 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1111 324330-325063(1) | OPEN LINE FROM BUS 324330 [2WINCHES IND69.000] TO BUS 325063 [2CORPORAT DR69.000] CKT 1 | -31.481 | 31.481 | 33 | 95.3971 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1112 324331-324418(1) | OPEN LINE FROM BUS 324331 [2ASHLAND AVE69.000] TO BUS 324418 [2ASHLND AV T69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3979 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1113 324332-325059(1) | OPEN LINE FROM BUS 324332 [2LAKE SHORE 69.000] TO BUS 325059 [2BRYANT RD T69.000] CKT 1 | -31.4808 | 31.4808 | 33 | 95.3964 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1114 324333-325957(1) | OPEN LINE FROM BUS 324333 [4BROWN N 1-R138.00] TO BUS 325957 [4BROWN N 1 138.00] CKT 1 | -31.4825 | 31.4825 | 33 | 95.4016 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1115 324334-325956(1) | OPEN LINE FROM BUS 324334 [4BROWN N 2-R138.00] TO BUS 325956 [4BROWN N 2 138.00] CKT 1 | -31.4827 | 31.4827 | 33 | 95.4023 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1116 324337-324650(1) | OPEN LINE FROM BUS 324337 [2MOUNT TABOR69.000] TO BUS 324650 [2MT TBR T 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1117 324338-324339(1) | OPEN LINE FROM BUS 324338 [2SCOTT ST 4 69.000] TO BUS 324339 [2SCOTT ST 1269.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3978 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1118 324338-324952(1) | OPEN LINE FROM BUS 324338 [2SCOTT ST 4 69.000] TO BUS 324952 [2SCOTT ST TP69.000] CKT 1 | -31.4812 | 31.4812 | 33 | 95.3976 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1119 324340-324734(1) | OPEN LINE FROM BUS 324340 [2SPINDLETOP 69.000] TO BUS 324734 [2SPINDLETP T69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1120 324341-324781(1) | OPEN LINE FROM BUS 324341 [2WILMORE 69.000] TO BUS 324781 [2WILMORE T 69.000] CKT 1 | -31.4817 | 31.4817 | 33 | 95.399 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1121 324344-324421(1) | OPEN LINE FROM BUS 324344 [2ATOKA 69.000] TO BUS 324421 [2ATOKA TAP 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1122 324345-324425(1) | OPEN LINE FROM BUS 324345 [2BARDTWN IND69.000] TO BUS 324425 [2BARDT IND T69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1123 324346-324612(1) | OPEN LINE FROM BUS 324346 [2RICHMND E 69.000] TO BUS 324612 [2LAKE REBA 69.000] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3988 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1124 324347-325058(1) | OPEN LINE FROM BUS 324347 [2BEATTY 649 69.000] TO BUS 325058 [2BEATTY 614 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1125 324348-324808(1) | OPEN LINE FROM BUS 324348 [2BRODHEAD CI69.000] TO BUS 324808 [2BRODHEAD KU69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1126 324349-324479(1) | OPEN LINE FROM BUS 324349 [2CAMPBELVIL269.000] TO BUS 324479 [2CAMPBELVL T69.000] CKT 1 | -31.4817 | 31.4817 | 33 | 95.3991 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1127 324350-324485(1) | OPEN LINE FROM BUS 324350 [2CRAB ORCHAR69.000] TO BUS 324485 [2CRAB ORCH T69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1128 324351-324354(1) | OPEN LINE FROM BUS 324351 [2ETOWN 3 69.000] TO BUS 324354 [2GATES RUBBR69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1129 324351-324519(1) | OPEN LINE FROM BUS 324351 [2ETOWN 3 69.000] TO BUS 324519 [2ETOWN KU 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1130 324352-324563(1) | OPEN LINE FROM BUS 324352 [2ETOWN IND 69.000] TO BUS 324563 [2HARDIN CO 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1131 324353-324863(1) | OPEN LINE FROM BUS 324353 [2FLORDA TILE69.000] TO BUS 324863 [2FLA TILE T169.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.398 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1132 324354-326561(1) | OPEN LINE FROM BUS 324354 [2GATES RUBBR69.000] TO BUS 326561 [2ETOWN WEST 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1133 324355-325054(1) | OPEN LINE FROM BUS 324355 [2HARRDSBRG 469.000] TO BUS 325054 [2HARRDSBRG N69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1134 324355-326578(1) | OPEN LINE FROM BUS 324355 [2HARRDSBRG 469.000] TO BUS 326578 [2HARRDSBRG 169.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1135 324356-325054(1) | OPEN LINE FROM BUS 324356 [2HARRDSBRG1269.000] TO BUS 325054 [2HARRDSBRG N69.000] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3988 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1136 324357-324600(1) | OPEN LINE FROM BUS 324357 [2LANCASTER 169.000] TO BUS 324600 [2LANCASTR KU69.000] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1137 324358-324914(1) | OPEN LINE FROM BUS 324358 [2M-V CLARKSN69.000] TO BUS 324914 [2M-V CLARK T69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1138 324359-324913(1) | OPEN LINE FROM BUS 324359 [2MT VERN 58969.000] TO BUS 324913 [2MT VERNON 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1139 324360-324927(1) | OPEN LINE FROM BUS 324360 [2PINE HILL 69.000] TO BUS 324927 [2PINE HILL T69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1140 324361-324935(1) | OPEN LINE FROM BUS 324361 [2RADCLIFF KU69.000] TO BUS 324935 [2RADCLF KU T69.000] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3989 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1141 324363-324957(1) | OPEN LINE FROM BUS 324363 [2SHELB CI KU69.000] TO BUS 324957 [2SHELBY CI T69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1142 324363-326518(1) | OPEN LINE FROM BUS 324363 [2SHELB CI KU69.000] TO BUS 326518 [2SHELB CI EK69.000] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1143 324372-324514(1) | OPEN LINE FROM BUS 324372 [2BURNSIDE 69.000] TO BUS 324514 [2ELIHU 69.000] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1144 324373-324814(1) | OPEN LINE FROM BUS 324373 [2CATRON CRK 69.000] TO BUS 324814 [2CATRON CK T69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1145 324374-324376(1) | OPEN LINE FROM BUS 324374 [2CROCKETT KU69.000] TO BUS 324376 [2DEER BRANCH69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1146 324374-325083(1) | OPEN LINE FROM BUS 324374 [2CROCKETT KU69.000] TO BUS 325083 [2ALEX CK TAP69.000] CKT 1 | -31.4814 | 31.4815 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1147 324375-324442(1) | OPEN LINE FROM BUS 324375 [2DAYHOIT 69.000] TO BUS 324442 [2BLEDSOE TAP69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1148 324376-324813(1) | OPEN LINE FROM BUS 324376 [2DEER BRANCH69.000] TO BUS 324813 [2CARY 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1149 324377-325083(1) | OPEN LINE FROM BUS 324377 [2GARDNER 69.000] TO BUS 325083 [2ALEX CK TAP69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1150 324378-324636(1) | OPEN LINE FROM BUS 324378 [2MIDDLBO780 69.000] TO BUS 324636 [2MIDDLESBORO69.000] CKT 1 | -31.4817 | 31.4817 | 33 | 95.3991 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1151 324380-324393(1) | OPEN LINE FROM BUS 324380 [2DANIEL BRAN69.000] TO BUS 324393 [2ROSE HILL 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1152 324380-324945(1) | OPEN LINE FROM BUS 324380 [2DANIEL BRAN69.000] TO BUS 324945 [2ROSE HILL T69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1153 324381-325001(1) | OPEN LINE FROM BUS 324381 [2WILLAMSBURG69.000] TO BUS 325001 [2WILLMBRG SW69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1154 324382-325001(1) | OPEN LINE FROM BUS 324382 [2WILLMBRG SO69.000] TO BUS 325001 [2WILLMBRG SW69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1155 324384-324549(1) | OPEN LINE FROM BUS 324384 [2APPALACHIA 69.000] TO BUS 324549 [2GORGE 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1156 324385-324549(1) | OPEN LINE FROM BUS 324385 [2BIG STONE G69.000] TO BUS 324549 [2GORGE 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1157 324386-324388(1) | OPEN LINE FROM BUS 324386 [2DIXIANA 69.000] TO BUS 324388 [2CRITICAL FK69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1158 324387-324392(1) | OPEN LINE FROM BUS 324387 [2ADDINGTON 69.000] TO BUS 324392 [2ROCKY FORK 69.000] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1159 324387-325064(1) | OPEN LINE FROM BUS 324387 [2ADDINGTON 69.000] TO BUS 325064 [2LAUREL GROV69.000] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1160 324388-325031(1) | OPEN LINE FROM BUS 324388 [2CRITICAL FK69.000] TO BUS 325031 [2LIPPS 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1161 324389-324851(1) | OPEN LINE FROM BUS 324389 [2DWINA 69.000] TO BUS 324851 [2DWINA TAP 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1162 324390-324391(1) | OPEN LINE FROM BUS 324390 [2PENNINGTON 69.000] TO BUS 324391 [2POOR VALLEY69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1163 324391-324689(1) | OPEN LINE FROM BUS 324391 [2POOR VALLEY69.000] TO BUS 324689 [2POCKET 69.000] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1164 324392-325031(1) | OPEN LINE FROM BUS 324392 [2ROCKY FORK 69.000] TO BUS 325031 [2LIPPS 69.000] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1165 324394-324977(1) | OPEN LINE FROM BUS 324394 [2TOMS CREEK 69.000] TO BUS 324977 [2TOMS CRK TP69.000] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1166 324395-325005(1) | OPEN LINE FROM BUS 324395 [2WISE 69.000] TO BUS 325005 [2WISE TAP 69.000] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1167 324400-324510(1) | OPEN LINE FROM BUS 324400 [2WHAS TAP 69.000] TO BUS 324510 [2EASTWOOD 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
342000 | 5GAS | 161 | 342760 | 5LIBERTY J | 161 | 1 | EKPC_P1-2_TYN-DELV161 | EKPC_P1-2_TYN-DELV161 | 146.7573 | 146.7573 | 153 | 95.9198 | EKPC
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1168 324400-324775(1) | OPEN LINE FROM BUS 324400 [2WHAS TAP 69.000] TO BUS 324775 [2WHAS 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1169 324400-325022(1) | OPEN LINE FROM BUS 324400 [2WHAS TAP 69.000] TO BUS 325022 [2EASTWOOD W 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1170 324401-324541(1) | OPEN LINE FROM BUS 324401 [2FREYS HIL J69.000] TO BUS 324541 [2FORD 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1171 324401-324545(1) | OPEN LINE FROM BUS 324401 [2FREYS HIL J69.000] TO BUS 324545 [2FREYS HILL 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1172 324401-324785(1) | OPEN LINE FROM BUS 324401 [2FREYS HIL J69.000] TO BUS 324785 [2WORTHINGTON69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.398 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1173 324402-324859(1) | OPEN LINE FROM BUS 324402 [2FAIRMOUNT T69.000] TO BUS 324859 [2FAIRMOUNT 169.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1174 324403-324469(1) | OPEN LINE FROM BUS 324403 [2CRESTWOOD T69.000] TO BUS 324469 [2CENTERFIELD69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1175 324403-324487(1) | OPEN LINE FROM BUS 324403 [2CRESTWOOD T69.000] TO BUS 324487 [2CRESTWOOD 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1176 324403-324616(1) | OPEN LINE FROM BUS 324403 [2CRESTWOOD T69.000] TO BUS 324616 [2LONG RUN 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1177 324404-324622(1) | OPEN LINE FROM BUS 324404 [2LYNDON TAP 69.000] TO BUS 324622 [2LYNDON SO 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1178 324404-324623(1) | OPEN LINE FROM BUS 324404 [2LYNDON TAP 69.000] TO BUS 324623 [2LYNDON 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1179 324404-324750(1) | OPEN LINE FROM BUS 324404 [2LYNDON TAP 69.000] TO BUS 324750 [2TAYLOR LG 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1180 324405-324547(1) | OPEN LINE FROM BUS 324405 [2ADAMS 69.000] TO BUS 324547 [2GEORGETOWN 69.000] CKT 1 | -31.482 | 31.482 | 33 | 95.4 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1181 324405-326989(1) | OPEN LINE FROM BUS 324405 [2ADAMS 69.000] TO BUS 326989 [2LONG LICK 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1182 324406-324637(1) | OPEN LINE FROM BUS 324406 [2AIKEN 69.000] TO BUS 324637 [2MIDDLETOWN 69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.398 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1183 324406-324673(1) | OPEN LINE FROM BUS 324406 [2AIKEN 69.000] TO BUS 324673 [2OXMOOR 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1184 324406-325022(1) | OPEN LINE FROM BUS 324406 [2AIKEN 69.000] TO BUS 325022 [2EASTWOOD W 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1185 324407-324755(1) | OPEN LINE FROM BUS 324407 [2ALEXANDER 69.000] TO BUS 324755 [2TYRONE 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1186 324407-324955(1) | OPEN LINE FROM BUS 324407 [2ALEXANDER 69.000] TO BUS 324955 [2SHANNON RUN69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.398 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1187 324408-324552(1) | OPEN LINE FROM BUS 324408 [2ALGONQUIN 69.000] TO BUS 324552 [2GRADY 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1188 324408-324625(1) | OPEN LINE FROM BUS 324408 [2ALGONQUIN 69.000] TO BUS 324625 [2MAGAZINE 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1189 324408-324649(1) | OPEN LINE FROM BUS 324408 [2ALGONQUIN 69.000] TO BUS 324649 [2MORRIS FORM69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1190 324408-324719(1) | OPEN LINE FROM BUS 324408 [2ALGONQUIN 69.000] TO BUS 324719 [2SEMINOLE 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1191 324408-324739(1) | OPEN LINE FROM BUS 324408 [2ALGONQUIN 69.000] TO BUS 324739 [2STEWART 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1192 324409-324632(1) | OPEN LINE FROM BUS 324409 [2AMERICAN AV69.000] TO BUS 324632 [2UK MED CENT69.000] CKT 1 | -31.4812 | 31.4812 | 33 | 95.3976 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1193 324409-324683(1) | OPEN LINE FROM BUS 324409 [2AMERICAN AV69.000] TO BUS 324683 [2PICADOME 69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3978 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1194 324409-324772(1) | OPEN LINE FROM BUS 324409 [2AMERICAN AV69.000] TO BUS 324772 [2UK WEST 2 69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3979 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1195 324411-324440(1) | OPEN LINE FROM BUS 324411 [2ANDOVER TAP69.000] TO BUS 324440 [2BLACK MOUNT69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1196 324411-324583(1) | OPEN LINE FROM BUS 324411 [2ANDOVER TAP69.000] TO BUS 324583 [2IMBODEN 69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.398 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1197 324411-324670(1) | OPEN LINE FROM BUS 324411 [2ANDOVER TAP69.000] TO BUS 324670 [2OSAKA EAST 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1198 324412-324670(1) | OPEN LINE FROM BUS 324412 [2ANDOVER 69.000] TO BUS 324670 [2OSAKA EAST 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1199 324413-324414(1) | OPEN LINE FROM BUS 324413 [2AO SMITH TP69.000] TO BUS 324414 [2AO SMITH 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1200 324413-324461(1) | OPEN LINE FROM BUS 324413 [2AO SMITH TP69.000] TO BUS 324461 [2CAMARGO 69.000] CKT 1 | -31.4811 | 31.4811 | 33 | 95.3972 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1201 324413-324733(1) | OPEN LINE FROM BUS 324413 [2AO SMITH TP69.000] TO BUS 324733 [2SPENCER RD 69.000] CKT 1 | -31.4811 | 31.4811 | 33 | 95.3972 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1202 324414-326531(1) | OPEN LINE FROM BUS 324414 [2AO SMITH 69.000] TO BUS 326531 [2HINKSTON 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1203 324415-324593(1) | OPEN LINE FROM BUS 324415 [2APPOLO FUEL69.000] TO BUS 324593 [2KU PARK 69.000] CKT 1 | -31.4812 | 31.4812 | 33 | 95.3976 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1204 324415-324636(1) | OPEN LINE FROM BUS 324415 [2APPOLO FUEL69.000] TO BUS 324636 [2MIDDLESBORO69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1205 324416-324433(1) | OPEN LINE FROM BUS 324416 [2ARNOLD 69.000] TO BUS 324433 [2BENHAM 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1206 324416-324490(1) | OPEN LINE FROM BUS 324416 [2ARNOLD 69.000] TO BUS 324490 [2CUMBERLAND 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1207 324417-324423(1) | OPEN LINE FROM BUS 324417 [2ARTEMUS 69.000] TO BUS 324423 [2BARBOURVILE69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1208 324418-324632(1) | OPEN LINE FROM BUS 324418 [2ASHLND AV T69.000] TO BUS 324632 [2UK MED CENT69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3979 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1209 324418-324934(1) | OPEN LINE FROM BUS 324418 [2ASHLND AV T69.000] TO BUS 324934 [2RACE STREET69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3977 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1210 324419-325024(1) | OPEN LINE FROM BUS 324419 [2ASHBOT WEST69.000] TO BUS 325024 [2ASHBOT SPRK69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1211 324421-324450(1) | OPEN LINE FROM BUS 324421 [2ATOKA TAP 69.000] TO BUS 324450 [2BOYLE CO 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1212 324421-324495(1) | OPEN LINE FROM BUS 324421 [2ATOKA TAP 69.000] TO BUS 324495 [2DANVILLE N 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1213 324422-324508(1) | OPEN LINE FROM BUS 324422 [2AVON T2 69.000] TO BUS 324508 [2EASTLAND 69.000] CKT 1 | -31.4853 | 31.4853 | 33 | 95.41 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1214 324422-324680(1) | OPEN LINE FROM BUS 324422 [2AVON T2 69.000] TO BUS 324680 [2PARIS KU 69.000] CKT 1 | -31.4834 | 31.4834 | 33 | 95.4043 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1215 324422-325081(1) | OPEN LINE FROM BUS 324422 [2AVON T2 69.000] TO BUS 325081 [2BRIAR HILL 69.000] CKT 1 | -31.4811 | 31.4811 | 33 | 95.3973 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1216 324423-324438(1) | OPEN LINE FROM BUS 324423 [2BARBOURVILE69.000] TO BUS 324438 [2BIMBLE 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1217 324424-324801(1) | OPEN LINE FROM BUS 324424 [2BARDTWN CTY69.000] TO BUS 324801 [2BARTON 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1218 324424-326537(1) | OPEN LINE FROM BUS 324424 [2BARDTWN CTY69.000] TO BUS 326537 [2WOODLAWN KU69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1219 324425-324426(1) | OPEN LINE FROM BUS 324425 [2BARDT IND T69.000] TO BUS 324426 [2BARDSTOWN 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1220 324426-324525(1) | OPEN LINE FROM BUS 324426 [2BARDSTOWN 69.000] TO BUS 324525 [2FAIRFIELD 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1221 324426-326537(Z1) | OPEN LINE FROM BUS 324426 [2BARDSTOWN 69.000] TO BUS 326537 [2WOODLAWN KU69.000] CKT Z1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1222 324427-324779(1) | OPEN LINE FROM BUS 324427 [2BARDWELL 69.000] TO BUS 324779 [2WICKLIFFE 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1223 324427-324823(1) | OPEN LINE FROM BUS 324427 [2BARDWELL 69.000] TO BUS 324823 [2CLINTON 58169.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1224 324428-324778(1) | OPEN LINE FROM BUS 324428 [2BARLOW 69.000] TO BUS 324778 [2WICKLIFE CI69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1225 324428-324864(1) | OPEN LINE FROM BUS 324428 [2BARLOW 69.000] TO BUS 324864 [2FORRESTDALE69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1226 324429-324453(1) | OPEN LINE FROM BUS 324429 [2BEARGRASS 69.000] TO BUS 324453 [2BEARGRS PMP69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1227 324429-324475(1) | OPEN LINE FROM BUS 324429 [2BEARGRASS 69.000] TO BUS 324475 [2CLIFTON 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1228 324429-324624(1) | OPEN LINE FROM BUS 324429 [2BEARGRASS 69.000] TO BUS 324624 [2MADISON LGE69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1229 324429-324710(1) | OPEN LINE FROM BUS 324429 [2BEARGRASS 69.000] TO BUS 324710 [2RVR CITY SH69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1230 324430-325058(1) | OPEN LINE FROM BUS 324430 [2BEATTYVI KU69.000] TO BUS 325058 [2BEATTY 614 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1231 324432-324558(1) | OPEN LINE FROM BUS 324432 [2BELT LINE 69.000] TO BUS 324558 [2HAEFLING 69.000] CKT 1 | -31.4825 | 31.4825 | 33 | 95.4014 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1232 324432-324879(1) | OPEN LINE FROM BUS 324432 [2BELT LINE 69.000] TO BUS 324879 [2IBM 998 69.000] CKT 1 | -31.4823 | 31.4823 | 33 | 95.4011 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1233 324433-324621(1) | OPEN LINE FROM BUS 324433 [2BENHAM 69.000] TO BUS 324621 [2LYNCH 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1234 324434-324435(1) | OPEN LINE FROM BUS 324434 [2BEREA TAP 69.000] TO BUS 324435 [2BEREA NORTH69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1235 324434-324668(1) | OPEN LINE FROM BUS 324434 [2BEREA TAP 69.000] TO BUS 324668 [2OKONITE 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1236 324435-324805(1) | OPEN LINE FROM BUS 324435 [2BEREA NORTH69.000] TO BUS 324805 [2BEREA 2 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1237 324436-324676(1) | OPEN LINE FROM BUS 324436 [2BEREA EK TP69.000] TO BUS 324676 [2PAINT LICK 69.000] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1238 324436-324805(1) | OPEN LINE FROM BUS 324436 [2BEREA EK TP69.000] TO BUS 324805 [2BEREA 2 69.000] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1239 324437-324745(1) | OPEN LINE FROM BUS 324437 [2BEVIER KU 69.000] TO BUS 324745 [2STRINGTOWN 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1240 324438-324515(1) | OPEN LINE FROM BUS 324438 [2BIMBLE 69.000] TO BUS 324515 [2EMANUEL TAP69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1241 324438-324573(1) | OPEN LINE FROM BUS 324438 [2BIMBLE 69.000] TO BUS 324573 [2HINKLE 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1242 324439-324518(1) | OPEN LINE FROM BUS 324439 [2BISHOP 69.000] TO BUS 324518 [2ETHEL 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1243 324439-324532(1) | OPEN LINE FROM BUS 324439 [2BISHOP 69.000] TO BUS 324532 [2FERN VALLEY69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1244 324440-324621(1) | OPEN LINE FROM BUS 324440 [2BLACK MOUNT69.000] TO BUS 324621 [2LYNCH 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1245 324441-324503(1) | OPEN LINE FROM BUS 324441 [2BLACKWOOD 69.000] TO BUS 324503 [2DORCHESTER 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1246 324441-324802(1) | OPEN LINE FROM BUS 324441 [2BLACKWOOD 69.000] TO BUS 324802 [2BEAR BRANCH69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1247 324442-324497(1) | OPEN LINE FROM BUS 324442 [2BLEDSOE TAP69.000] TO BUS 324497 [2DAYHOIT TAP69.000] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1248 324442-325008(1) | OPEN LINE FROM BUS 324442 [2BLEDSOE TAP69.000] TO BUS 325008 [2BLEDSOE 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1249 324443-324789(1) | OPEN LINE FROM BUS 324443 [2BLUE LICK 69.000] TO BUS 324789 [2BLUE LCK TP69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1250 324444-324651(1) | OPEN LINE FROM BUS 324444 [2BLUELICK EK69.000] TO BUS 324651 [2MUD LANE 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1251 324444-324788(1) | OPEN LINE FROM BUS 324444 [2BLUELICK EK69.000] TO BUS 324788 [2BROOKS EK T69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1252 324445-324620(1) | OPEN LINE FROM BUS 324445 [2BONDS MILL 69.000] TO BUS 324620 [2LAWRENCEBRG69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3978 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1253 324445-324732(1) | OPEN LINE FROM BUS 324445 [2BONDS MILL 69.000] TO BUS 324732 [2SOUTHVILLE 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1254 324445-324863(1) | OPEN LINE FROM BUS 324445 [2BONDS MILL 69.000] TO BUS 324863 [2FLA TILE T169.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3978 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1255 324445-325087(1) | OPEN LINE FROM BUS 324445 [2BONDS MILL 69.000] TO BUS 325087 [2CLAY LICK T69.000] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3989 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1256 324446-324824(1) | OPEN LINE FROM BUS 324446 [2BOND 69.000] TO BUS 324824 [2CLINCH VALL69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1257 324446-324977(1) | OPEN LINE FROM BUS 324446 [2BOND 69.000] TO BUS 324977 [2TOMS CRK TP69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1258 324447-324731(1) | OPEN LINE FROM BUS 324447 [2BONNIE KU 69.000] TO BUS 324731 [2SONORA TAP 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1259 324448-324782(1) | OPEN LINE FROM BUS 324448 [2BOONE AVE 69.000] TO BUS 324782 [2WINCHEST SO69.000] CKT 1 | -31.4817 | 31.4817 | 33 | 95.3991 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1260 324448-325004(1) | OPEN LINE FROM BUS 324448 [2BOONE AVE 69.000] TO BUS 325004 [2WINCHES WTR69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1261 324449-325004(1) | OPEN LINE FROM BUS 324449 [2BOONSBORO N69.000] TO BUS 325004 [2WINCHES WTR69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1262 324449-325925(1) | OPEN LINE FROM BUS 324449 [2BOONSBORO N69.000] TO BUS 325925 [4BOONSBORO N138.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1263 324450-324494(1) | OPEN LINE FROM BUS 324450 [2BOYLE CO 69.000] TO BUS 324494 [2DANVILLE 1 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1264 324451-324574(1) | OPEN LINE FROM BUS 324451 [2BRECKNRIDGE69.000] TO BUS 324574 [2HILLCREST 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1265 324451-324673(1) | OPEN LINE FROM BUS 324451 [2BRECKNRIDGE69.000] TO BUS 324673 [2OXMOOR 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1266 324453-324475(1) | OPEN LINE FROM BUS 324453 [2BEARGRS PMP69.000] TO BUS 324475 [2CLIFTON 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1267 324455-324966(1) | OPEN LINE FROM BUS 324455 [2BROMLEY 69.000] TO BUS 324966 [2SPARTA KU 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1268 324456-324465(1) | OPEN LINE FROM BUS 324456 [2BRUSH CREEK69.000] TO BUS 324465 [2CARPENTER T69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1269 324456-324593(1) | OPEN LINE FROM BUS 324456 [2BRUSH CREEK69.000] TO BUS 324593 [2KU PARK 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1270 324457-324610(1) | OPEN LINE FROM BUS 324457 [2BUCHANAN 69.000] TO BUS 324610 [2LEX PLANT 69.000] CKT 1 | -31.4811 | 31.4811 | 33 | 95.3971 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1271 324457-324986(1) | OPEN LINE FROM BUS 324457 [2BUCHANAN 69.000] TO BUS 324986 [2W HIGH T2 69.000] CKT 1 | -31.4811 | 31.4811 | 33 | 95.3973 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1272 324458-324501(1) | OPEN LINE FROM BUS 324458 [2BUENA VISTA69.000] TO BUS 324501 [2DIX DAM 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1273 324458-324546(1) | OPEN LINE FROM BUS 324458 [2BUENA VISTA69.000] TO BUS 324546 [2GARRARD CT 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1274 324459-324626(1) | OPEN LINE FROM BUS 324459 [2BUSH TAP 69.000] TO BUS 324626 [2MANCHEST SO69.000] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3989 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1275 324459-326533(1) | OPEN LINE FROM BUS 324459 [2BUSH TAP 69.000] TO BUS 326533 [2BUSH EKPC 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1276 324460-324686(1) | OPEN LINE FROM BUS 324460 [2CALLOWAY 69.000] TO BUS 324686 [2PINEVILLE 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1277 324460-324706(1) | OPEN LINE FROM BUS 324460 [2CALLOWAY 69.000] TO BUS 324706 [2ROCKY BRNCH69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1278 324461-324912(1) | OPEN LINE FROM BUS 324461 [2CAMARGO 69.000] TO BUS 324912 [2MT STERL KU69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1279 324462-324499(1) | OPEN LINE FROM BUS 324462 [2CANAL 69.000] TO BUS 324499 [2DEL PARK 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1280 324462-324624(1) | OPEN LINE FROM BUS 324462 [2CANAL 69.000] TO BUS 324624 [2MADISON LGE69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1281 324462-324625(1) | OPEN LINE FROM BUS 324462 [2CANAL 69.000] TO BUS 324625 [2MAGAZINE 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1282 324462-324665(1) | OPEN LINE FROM BUS 324462 [2CANAL 69.000] TO BUS 324665 [2OHIO FALL 169.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3978 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1283 324462-324666(1) | OPEN LINE FROM BUS 324462 [2CANAL 69.000] TO BUS 324666 [2OHIO FALL 269.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3978 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1284 324464-324615(1) | OPEN LINE FROM BUS 324464 [2CARON 69.000] TO BUS 324615 [2LONDON 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1285 324464-324860(1) | OPEN LINE FROM BUS 324464 [2CARON 69.000] TO BUS 324860 [2FARISTON 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1286 324465-324784(1) | OPEN LINE FROM BUS 324465 [2CARPENTER T69.000] TO BUS 324784 [2WOFFORD 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1287 324465-326535(1) | OPEN LINE FROM BUS 324465 [2CARPENTER T69.000] TO BUS 326535 [2CARPENTER 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1288 324466-324602(1) | OPEN LINE FROM BUS 324466 [2CARROLLTON 69.000] TO BUS 324602 [2LAWRENCE TP69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1289 324466-324634(1) | OPEN LINE FROM BUS 324466 [2CARROLLTON 69.000] TO BUS 324634 [2METAL+THERM69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3978 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1290 324467-324528(1) | OPEN LINE FROM BUS 324467 [2CAVE RUN TP69.000] TO BUS 324528 [2FARMERS 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1291 324467-324714(1) | OPEN LINE FROM BUS 324467 [2CAVE RUN TP69.000] TO BUS 324714 [2SALT LICK 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1292 324467-326538(1) | OPEN LINE FROM BUS 324467 [2CAVE RUN TP69.000] TO BUS 326538 [2CAVE RUN 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1293 324468-324572(1) | OPEN LINE FROM BUS 324468 [2CENTRL CI S69.000] TO BUS 324572 [2HILLSIDE 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1294 324468-324817(1) | OPEN LINE FROM BUS 324468 [2CENTRL CI S69.000] TO BUS 324817 [2CENTRAL CIT69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1295 324469-324681(1) | OPEN LINE FROM BUS 324469 [2CENTERFIELD69.000] TO BUS 324681 [2PENAL FARM 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1296 324469-324682(1) | OPEN LINE FROM BUS 324469 [2CENTERFIELD69.000] TO BUS 324682 [2PENAL TAP 69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.398 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1297 324470-324486(1) | OPEN LINE FROM BUS 324470 [2CERRO-SALEM69.000] TO BUS 324486 [2CRITTENDEN 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1298 324470-324948(1) | OPEN LINE FROM BUS 324470 [2CERRO-SALEM69.000] TO BUS 324948 [2SALEM KU 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1299 324471-324777(1) | OPEN LINE FROM BUS 324471 [2CHRISTIAN 69.000] TO BUS 324777 [2WHEATCROFT 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1300 324471-324822(1) | OPEN LINE FROM BUS 324471 [2CHRISTIAN 69.000] TO BUS 324822 [2CLAY KU 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1301 324472-324540(1) | OPEN LINE FROM BUS 324472 [2CLARK CO 69.000] TO BUS 324540 [2FOGG PIKE T69.000] CKT 1 | -31.4805 | 31.4805 | 33 | 95.3956 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1302 324472-324749(1) | OPEN LINE FROM BUS 324472 [2CLARK CO 69.000] TO BUS 324749 [2SYLVANIA 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1303 324473-324561(1) | OPEN LINE FROM BUS 324473 [2CLAY LGE 69.000] TO BUS 324561 [2HANCOCK 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1304 324473-324570(1) | OPEN LINE FROM BUS 324473 [2CLAY LGE 69.000] TO BUS 324570 [2HIGHLAND 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1305 324473-324624(1) | OPEN LINE FROM BUS 324473 [2CLAY LGE 69.000] TO BUS 324624 [2MADISON LGE69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1306 324474-324725(1) | OPEN LINE FROM BUS 324474 [2CLAY VILG T69.000] TO BUS 324725 [2SHELBYVIL E69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1307 324474-324765(1) | OPEN LINE FROM BUS 324474 [2CLAY VILG T69.000] TO BUS 324765 [2W FRANKFORT69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1308 324475-324574(1) | OPEN LINE FROM BUS 324475 [2CLIFTON 69.000] TO BUS 324574 [2HILLCREST 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1309 324476-324581(1) | OPEN LINE FROM BUS 324476 [2CMC TAP 69.000] TO BUS 324581 [2HUGHES LANE69.000] CKT 1 | -31.4889 | 31.4889 | 33 | 95.4209 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1310 324476-324680(1) | OPEN LINE FROM BUS 324476 [2CMC TAP 69.000] TO BUS 324680 [2PARIS KU 69.000] CKT 1 | -31.497 | 31.497 | 33 | 95.4454 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1311 324477-324502(1) | OPEN LINE FROM BUS 324477 [2CAMP BRECKN69.000] TO BUS 324502 [2DIXON KU 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1312 324477-324645(1) | OPEN LINE FROM BUS 324477 [2CAMP BRECKN69.000] TO BUS 324645 [2MORGANFIELD69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1313 324478-324516(1) | OPEN LINE FROM BUS 324478 [2CAMPBELBURG69.000] TO BUS 324516 [2EMINENCE KU69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1314 324478-324828(1) | OPEN LINE FROM BUS 324478 [2CAMPBELBURG69.000] TO BUS 324828 [2CAMPBBRG KU69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1315 324479-324751(1) | OPEN LINE FROM BUS 324479 [2CAMPBELVL T69.000] TO BUS 324751 [2TAYLOR CO 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1316 324479-324889(1) | OPEN LINE FROM BUS 324479 [2CAMPBELVL T69.000] TO BUS 324889 [2LEBANON SO 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1317 324480-324515(1) | OPEN LINE FROM BUS 324480 [2CMPGND EK T69.000] TO BUS 324515 [2EMANUEL TAP69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1318 324480-324615(1) | OPEN LINE FROM BUS 324480 [2CMPGND EK T69.000] TO BUS 324615 [2LONDON 69.000] CKT 1 | -31.4812 | 31.4812 | 33 | 95.3976 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1319 324480-326521(1) | OPEN LINE FROM BUS 324480 [2CMPGND EK T69.000] TO BUS 326521 [2CAMPGRND EK69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1320 324481-324487(1) | OPEN LINE FROM BUS 324481 [2COLLINS 69.000] TO BUS 324487 [2CRESTWOOD 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1321 324481-324541(1) | OPEN LINE FROM BUS 324481 [2COLLINS 69.000] TO BUS 324541 [2FORD 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1322 324482-324748(1) | OPEN LINE FROM BUS 324482 [2CORBIN EAST69.000] TO BUS 324748 [2SWEET HOLLO69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1323 324482-324832(1) | OPEN LINE FROM BUS 324482 [2CORBIN EAST69.000] TO BUS 324832 [2CORBIN 1 69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.398 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1324 324484-324571(1) | OPEN LINE FROM BUS 324484 [2CORYDON 69.000] TO BUS 324571 [2HIGHLAND MI69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1325 324484-324711(1) | OPEN LINE FROM BUS 324484 [2CORYDON 69.000] TO BUS 324711 [2SPEN CHEM T69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1326 324485-324600(1) | OPEN LINE FROM BUS 324485 [2CRAB ORCH T69.000] TO BUS 324600 [2LANCASTR KU69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1327 324485-324808(1) | OPEN LINE FROM BUS 324485 [2CRAB ORCH T69.000] TO BUS 324808 [2BRODHEAD KU69.000] CKT 1 | -31.4811 | 31.4811 | 33 | 95.3974 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1328 324486-324628(1) | OPEN LINE FROM BUS 324486 [2CRITTENDEN 69.000] TO BUS 324628 [2MARION SO 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1329 324488-324529(1) | OPEN LINE FROM BUS 324488 [2CANE RUN SW69.000] TO BUS 324529 [2FARNSLEY 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1330 324488-324724(1) | OPEN LINE FROM BUS 324488 [2CANE RUN SW69.000] TO BUS 324724 [2SHIVELY 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1331 324488-324739(1) | OPEN LINE FROM BUS 324488 [2CANE RUN SW69.000] TO BUS 324739 [2STEWART 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1332 324489-324654(1) | OPEN LINE FROM BUS 324489 [2CUMB FALL T69.000] TO BUS 324654 [2MT VIC EK J69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.398 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1333 324489-324784(1) | OPEN LINE FROM BUS 324489 [2CUMB FALL T69.000] TO BUS 324784 [2WOFFORD 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1334 324489-325034(1) | OPEN LINE FROM BUS 324489 [2CUMB FALL T69.000] TO BUS 325034 [2CUMBER FALL69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1335 324490-324827(1) | OPEN LINE FROM BUS 324490 [2CUMBERLAND 69.000] TO BUS 324827 [2CLOVERLICK 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1336 324491-324837(1) | OPEN LINE FROM BUS 324491 [2CYNTHIAN SO69.000] TO BUS 324837 [2CYNTHIAN KU69.000] CKT 1 | -31.4779 | 31.4779 | 33 | 95.3875 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1337 324491-325085(1) | OPEN LINE FROM BUS 324491 [2CYNTHIAN SO69.000] TO BUS 325085 [2CYNTHI EK T69.000] CKT 1 | -31.4853 | 31.4853 | 33 | 95.41 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1338 324492-324595(1) | OPEN LINE FROM BUS 324492 [2CYNTHIAN SW69.000] TO BUS 324595 [2KAWNEER 69.000] CKT 1 | -31.478 | 31.478 | 33 | 95.3879 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1339 324493-324518(1) | OPEN LINE FROM BUS 324493 [2DAHLIA 69.000] TO BUS 324518 [2ETHEL 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1340 324493-324570(1) | OPEN LINE FROM BUS 324493 [2DAHLIA 69.000] TO BUS 324570 [2HIGHLAND 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1341 324494-324840(1) | OPEN LINE FROM BUS 324494 [2DANVILLE 1 69.000] TO BUS 324840 [2DANVILLE E 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1342 324495-326579(1) | OPEN LINE FROM BUS 324495 [2DANVILLE N 69.000] TO BUS 326579 [2HARRDSBRG 269.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1343 324496-324767(1) | OPEN LINE FROM BUS 324496 [2DARK HOLLOW69.000] TO BUS 324767 [2WEST IRVINE69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1344 324496-324880(1) | OPEN LINE FROM BUS 324496 [2DARK HOLLOW69.000] TO BUS 324880 [2IRVINE 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1345 324497-324564(1) | OPEN LINE FROM BUS 324497 [2DAYHOIT TAP69.000] TO BUS 324564 [2HARLAN WYE 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1346 324497-324588(1) | OPEN LINE FROM BUS 324497 [2DAYHOIT TAP69.000] TO BUS 324588 [2KENTENIA 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1347 324498-324621(1) | OPEN LINE FROM BUS 324498 [2DAYS BRANCH69.000] TO BUS 324621 [2LYNCH 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1348 324498-324876(1) | OPEN LINE FROM BUS 324498 [2DAYS BRANCH69.000] TO BUS 324876 [2HOLMES MILL69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1349 324499-324552(1) | OPEN LINE FROM BUS 324499 [2DEL PARK 69.000] TO BUS 324552 [2GRADY 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1350 324500-324924(1) | OPEN LINE FROM BUS 324500 [2DELAPLAIN T69.000] TO BUS 324924 [2OXFORD 69.000] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1351 324501-324764(1) | OPEN LINE FROM BUS 324501 [2DIX DAM 69.000] TO BUS 324764 [2WEST CLIFF 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1352 324502-324658(1) | OPEN LINE FROM BUS 324502 [2DIXON KU 69.000] TO BUS 324658 [2NEBO 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1353 324503-325064(1) | OPEN LINE FROM BUS 324503 [2DORCHESTER 69.000] TO BUS 325064 [2LAUREL GROV69.000] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1354 324504-324662(1) | OPEN LINE FROM BUS 324504 [2E BERNST KU69.000] TO BUS 324662 [2N LONDON KU69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1355 324504-324927(1) | OPEN LINE FROM BUS 324504 [2E BERNST KU69.000] TO BUS 324927 [2PINE HILL T69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1356 324505-324506(1) | OPEN LINE FROM BUS 324505 [2E DIAMOND 69.000] TO BUS 324506 [2EARLINGTN N69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1357 324505-324947(1) | OPEN LINE FROM BUS 324505 [2E DIAMOND 69.000] TO BUS 324947 [2RUMSEY 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1358 324506-324769(1) | OPEN LINE FROM BUS 324506 [2EARLINGTN N69.000] TO BUS 324769 [2WALKER KU 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1359 324506-324954(1) | OPEN LINE FROM BUS 324506 [2EARLINGTN N69.000] TO BUS 324954 [2SENTRY TAP 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1360 324507-324769(1) | OPEN LINE FROM BUS 324507 [2EARLINGTON 69.000] TO BUS 324769 [2WALKER KU 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1361 324507-324850(1) | OPEN LINE FROM BUS 324507 [2EARLINGTON 69.000] TO BUS 324850 [2DOZIER H 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1362 324508-324617(1) | OPEN LINE FROM BUS 324508 [2EASTLAND 69.000] TO BUS 324617 [2LOUDON 618 69.000] CKT 1 | -31.4866 | 31.4866 | 33 | 95.4138 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1363 324509-324914(1) | OPEN LINE FROM BUS 324509 [2EASTVIEW 69.000] TO BUS 324914 [2M-V CLARK T69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1364 324510-324729(1) | OPEN LINE FROM BUS 324510 [2EASTWOOD 69.000] TO BUS 324729 [2SIMPSONVILL69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
342000 | 5GAS | 161 | 342760 | 5LIBERTY J | 161 | 1 | BB-1509 | BB-1509 | 146.7573 | 146.7573 | 153 | 95.9198 | EKPC
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1365 324511-324584(1) | OPEN LINE FROM BUS 324511 [2ECHOLS 69.000] TO BUS 324584 [2INDIAN HILL69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1366 324511-324959(1) | OPEN LINE FROM BUS 324511 [2ECHOLS 69.000] TO BUS 324959 [2SIMMONS 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1367 324512-324693(1) | OPEN LINE FROM BUS 324512 [2EDDYV PR TP69.000] TO BUS 324693 [2PRINCETON 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1368 324513-324693(1) | OPEN LINE FROM BUS 324513 [2EDDYVILLE 69.000] TO BUS 324693 [2PRINCETON 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1369 324513-324885(1) | OPEN LINE FROM BUS 324513 [2EDDYVILLE 69.000] TO BUS 324885 [2KUTTAWA 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1370 324514-324531(1) | OPEN LINE FROM BUS 324514 [2ELIHU 69.000] TO BUS 324531 [2FERGUSON SO69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1371 324514-324654(1) | OPEN LINE FROM BUS 324514 [2ELIHU 69.000] TO BUS 324654 [2MT VIC EK J69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3979 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1372 324514-324962(1) | OPEN LINE FROM BUS 324514 [2ELIHU 69.000] TO BUS 324962 [2SOMERSET 1 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1373 324515-326530(1) | OPEN LINE FROM BUS 324515 [2EMANUEL TAP69.000] TO BUS 326530 [2EMANUEL 69.000] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3988 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1374 324516-324585(1) | OPEN LINE FROM BUS 324516 [2EMINENCE KU69.000] TO BUS 324585 [2JERICHO 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1375 324516-324727(1) | OPEN LINE FROM BUS 324516 [2EMINENCE KU69.000] TO BUS 324727 [2SHELBYVILLE69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1376 324517-325005(1) | OPEN LINE FROM BUS 324517 [2ESSERVILLE 69.000] TO BUS 325005 [2WISE TAP 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1377 324518-324657(1) | OPEN LINE FROM BUS 324518 [2ETHEL 69.000] TO BUS 324657 [2NACHAND 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1378 324519-324520(1) | OPEN LINE FROM BUS 324519 [2ETOWN KU 69.000] TO BUS 324520 [2ETOWN 2 TAP69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1379 324519-324521(1) | OPEN LINE FROM BUS 324519 [2ETOWN KU 69.000] TO BUS 324521 [2ETOWN 4 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1380 324519-324563(1) | OPEN LINE FROM BUS 324519 [2ETOWN KU 69.000] TO BUS 324563 [2HARDIN CO 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1381 324519-324563(2) | OPEN LINE FROM BUS 324519 [2ETOWN KU 69.000] TO BUS 324563 [2HARDIN CO 69.000] CKT 2 | -31.4815 | 31.4815 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1382 324520-326555(1) | OPEN LINE FROM BUS 324520 [2ETOWN 2 TAP69.000] TO BUS 326555 [2RINEYVIL RD69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1383 324521-324575(1) | OPEN LINE FROM BUS 324521 [2ETOWN 4 69.000] TO BUS 324575 [2HODGENV KU 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1384 324522-324523(1) | OPEN LINE FROM BUS 324522 [2EVARTS TAP 69.000] TO BUS 324523 [2EVARTS 69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3979 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1385 324522-324692(1) | OPEN LINE FROM BUS 324522 [2EVARTS TAP 69.000] TO BUS 324692 [2POWELL MTN 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1386 324522-324761(1) | OPEN LINE FROM BUS 324522 [2EVARTS TAP 69.000] TO BUS 324761 [2VERDA 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1387 324523-324798(1) | OPEN LINE FROM BUS 324523 [2EVARTS 69.000] TO BUS 324798 [2BAILEY CRK 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.398 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1388 324524-325009(1) | OPEN LINE FROM BUS 324524 [2EWINGTON 69.000] TO BUS 325009 [2SPENCER A 69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3978 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1389 324525-324974(1) | OPEN LINE FROM BUS 324525 [2FAIRFIELD 69.000] TO BUS 324974 [2TAYLRV EK T69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1390 324526-324730(1) | OPEN LINE FROM BUS 324526 [2FAIRMOUNT 269.000] TO BUS 324730 [2SMYRNA 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1391 324527-324704(1) | OPEN LINE FROM BUS 324527 [2FARLEY KU 69.000] TO BUS 324704 [2ROCKHOLD 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1392 324527-324758(1) | OPEN LINE FROM BUS 324527 [2FARLEY KU 69.000] TO BUS 324758 [2US STEEL 69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.398 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1393 324528-324647(1) | OPEN LINE FROM BUS 324528 [2FARMERS 69.000] TO BUS 324647 [2MOREHEAD W 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1394 324529-324675(1) | OPEN LINE FROM BUS 324529 [2FARNSLEY 69.000] TO BUS 324675 [2PADDYS RUN 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1395 324529-324724(1) | OPEN LINE FROM BUS 324529 [2FARNSLEY 69.000] TO BUS 324724 [2SHIVELY 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1396 324530-324701(1) | OPEN LINE FROM BUS 324530 [2FAWKES 69.000] TO BUS 324701 [2RICHMND 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1397 324533-324535(1) | OPEN LINE FROM BUS 324533 [2FRANKFORT 169.000] TO BUS 324535 [2E FRANKFORT69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1398 324534-324535(1) | OPEN LINE FROM BUS 324534 [2FRANKFORT 269.000] TO BUS 324535 [2E FRANKFORT69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1399 324534-324762(1) | OPEN LINE FROM BUS 324534 [2FRANKFORT 269.000] TO BUS 324762 [2VERSAIL W T69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1400 324535-326528(1) | OPEN LINE FROM BUS 324535 [2E FRANKFORT69.000] TO BUS 326528 [2BRIDGEPORT 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1401 324536-324653(1) | OPEN LINE FROM BUS 324536 [2FINCHVILLE 69.000] TO BUS 324653 [2M-V SIMPSON69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1402 324536-324718(1) | OPEN LINE FROM BUS 324536 [2FINCHVILLE 69.000] TO BUS 324718 [2SHELBY CO T69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1403 324536-324752(1) | OPEN LINE FROM BUS 324536 [2FINCHVILLE 69.000] TO BUS 324752 [2TAYLORSV KU69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1404 324537-324620(1) | OPEN LINE FROM BUS 324537 [2FLA TILE T269.000] TO BUS 324620 [2LAWRENCEBRG69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1405 324537-324755(1) | OPEN LINE FROM BUS 324537 [2FLA TILE T269.000] TO BUS 324755 [2TYRONE 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1406 324538-324561(1) | OPEN LINE FROM BUS 324538 [2FLOYD 69.000] TO BUS 324561 [2HANCOCK 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1407 324538-324614(1) | OPEN LINE FROM BUS 324538 [2FLOYD 69.000] TO BUS 324614 [2LOCUST TAP 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1408 324539-324601(1) | OPEN LINE FROM BUS 324539 [2FMC 69.000] TO BUS 324601 [2LANSDOWNE 69.000] CKT 1 | -31.481 | 31.481 | 33 | 95.3971 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1409 324539-324613(1) | OPEN LINE FROM BUS 324539 [2FMC 69.000] TO BUS 324613 [2LK SHORE TP69.000] CKT 1 | -31.4845 | 31.4845 | 33 | 95.4075 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1410 324540-324912(1) | OPEN LINE FROM BUS 324540 [2FOGG PIKE T69.000] TO BUS 324912 [2MT STERL KU69.000] CKT 1 | -31.4806 | 31.4806 | 33 | 95.3958 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1411 324541-324637(1) | OPEN LINE FROM BUS 324541 [2FORD 69.000] TO BUS 324637 [2MIDDLETOWN 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1412 324542-324588(1) | OPEN LINE FROM BUS 324542 [2FORESTER CR69.000] TO BUS 324588 [2KENTENIA 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1413 324542-324706(1) | OPEN LINE FROM BUS 324542 [2FORESTER CR69.000] TO BUS 324706 [2ROCKY BRNCH69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1414 324543-324686(1) | OPEN LINE FROM BUS 324543 [2FOUR MILE 69.000] TO BUS 324686 [2PINEVILLE 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1415 324543-324813(1) | OPEN LINE FROM BUS 324543 [2FOUR MILE 69.000] TO BUS 324813 [2CARY 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1416 324544-324693(1) | OPEN LINE FROM BUS 324544 [2FREDONIA QU69.000] TO BUS 324693 [2PRINCETON 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1417 324544-324865(1) | OPEN LINE FROM BUS 324544 [2FREDONIA QU69.000] TO BUS 324865 [2FREDONIA 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1418 324545-324623(1) | OPEN LINE FROM BUS 324545 [2FREYS HILL 69.000] TO BUS 324623 [2LYNDON 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1419 324546-324600(1) | OPEN LINE FROM BUS 324546 [2GARRARD CT 69.000] TO BUS 324600 [2LANCASTR KU69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1420 324547-324890(1) | OPEN LINE FROM BUS 324547 [2GEORGETOWN 69.000] TO BUS 324890 [2LEMONS MILL69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1421 324549-324583(1) | OPEN LINE FROM BUS 324549 [2GORGE 69.000] TO BUS 324583 [2IMBODEN 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1422 324549-324894(1) | OPEN LINE FROM BUS 324549 [2GORGE 69.000] TO BUS 324894 [2E STONE G T69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1423 324550-324652(1) | OPEN LINE FROM BUS 324550 [2GREEN RIVER69.000] TO BUS 324652 [2MUHLENBRG P69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1424 324550-324709(1) | OPEN LINE FROM BUS 324550 [2GREEN RIVER69.000] TO BUS 324709 [2RVR QUEEN T69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1425 324550-324723(1) | OPEN LINE FROM BUS 324550 [2GREEN RIVER69.000] TO BUS 324723 [2SHAVER CHAP69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1426 324550-325082(1) | OPEN LINE FROM BUS 324550 [2GREEN RIVER69.000] TO BUS 325082 [2ARMSTR BREC69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1427 324550-326513(1) | OPEN LINE FROM BUS 324550 [2GREEN RIVER69.000] TO BUS 326513 [2EQAL M BREC69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1428 324551-324786(1) | OPEN LINE FROM BUS 324551 [2GR RVR STL 69.000] TO BUS 324786 [2ZION 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1429 324551-324947(1) | OPEN LINE FROM BUS 324551 [2GR RVR STL 69.000] TO BUS 324947 [2RUMSEY 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1430 324552-324675(1) | OPEN LINE FROM BUS 324552 [2GRADY 69.000] TO BUS 324675 [2PADDYS RUN 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1431 324553-324864(1) | OPEN LINE FROM BUS 324553 [2GRAHAMVILLE69.000] TO BUS 324864 [2FORRESTDALE69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1432 324554-324830(1) | OPEN LINE FROM BUS 324554 [2GRENSBRG KU69.000] TO BUS 324830 [2CAMPBELV EK69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1433 324555-324716(1) | OPEN LINE FROM BUS 324555 [2VA CTY REAC69.000] TO BUS 324716 [2SANDY RIDGE69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3979 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1434 324555-324759(1) | OPEN LINE FROM BUS 324555 [2VA CTY REAC69.000] TO BUS 324759 [2VIRGINIA CI69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3979 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1435 324556-324702(1) | OPEN LINE FROM BUS 324556 [2GREENV W TP69.000] TO BUS 324702 [2RIVER QUEEN69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1436 324556-324870(1) | OPEN LINE FROM BUS 324556 [2GREENV W TP69.000] TO BUS 324870 [2GREENVILLE 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1437 324556-326593(1) | OPEN LINE FROM BUS 324556 [2GREENV W TP69.000] TO BUS 326593 [2GREENVIL N 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1438 324557-324829(1) | OPEN LINE FROM BUS 324557 [2GR RVR PLAZ69.000] TO BUS 324829 [2CAMPBELVIL169.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1439 324557-324830(1) | OPEN LINE FROM BUS 324557 [2GR RVR PLAZ69.000] TO BUS 324830 [2CAMPBELV EK69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1440 324558-324734(1) | OPEN LINE FROM BUS 324558 [2HAEFLING 69.000] TO BUS 324734 [2SPINDLETP T69.000] CKT 1 | -31.481 | 31.481 | 33 | 95.397 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1441 324558-324766(1) | OPEN LINE FROM BUS 324558 [2HAEFLING 69.000] TO BUS 324766 [2W HIGH T1 69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.398 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1442 324559-324797(1) | OPEN LINE FROM BUS 324559 [2HALEY 69.000] TO BUS 324797 [2AVON T1 69.000] CKT 1 | -31.4818 | 31.4818 | 33 | 95.3993 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1443 324559-326586(1) | OPEN LINE FROM BUS 324559 [2HALEY 69.000] TO BUS 326586 [2HUME RD TAP69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3979 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1444 324560-324689(1) | OPEN LINE FROM BUS 324560 [2HAMBLIN TAP69.000] TO BUS 324689 [2POCKET 69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3979 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1445 324560-324815(1) | OPEN LINE FROM BUS 324560 [2HAMBLIN TAP69.000] TO BUS 324815 [2CAWOOD 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1446 324560-325041(1) | OPEN LINE FROM BUS 324560 [2HAMBLIN TAP69.000] TO BUS 325041 [2STONE TVA 69.000] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1447 324562-324564(1) | OPEN LINE FROM BUS 324562 [2HARLAN KU 69.000] TO BUS 324564 [2HARLAN WYE 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1448 324563-324731(1) | OPEN LINE FROM BUS 324563 [2HARDIN CO 69.000] TO BUS 324731 [2SONORA TAP 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1449 324565-324566(1) | OPEN LINE FROM BUS 324565 [7NAS TAP 345.00] TO BUS 324566 [7NAS 222 345.00] CKT 1 | -31.4812 | 31.4812 | 33 | 95.3977 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1450 324567-324780(1) | OPEN LINE FROM BUS 324567 [2HIGBY MIL 269.000] TO BUS 324780 [2WIL DOWN T169.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1451 324568-324569(1) | OPEN LINE FROM BUS 324568 [2HIGBY 618 69.000] TO BUS 324569 [2HIGBY 608 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1452 324568-324713(1) | OPEN LINE FROM BUS 324568 [2HIGBY 618 69.000] TO BUS 324713 [2SO ELKHORN 69.000] CKT 1 | -31.4811 | 31.4811 | 33 | 95.3973 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1453 324568-324742(1) | OPEN LINE FROM BUS 324568 [2HIGBY 618 69.000] TO BUS 324742 [2STONEWALL T69.000] CKT 1 | -31.4805 | 31.4805 | 33 | 95.3954 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1454 324569-324632(1) | OPEN LINE FROM BUS 324569 [2HIGBY 608 69.000] TO BUS 324632 [2UK MED CENT69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1455 324571-324671(1) | OPEN LINE FROM BUS 324571 [2HIGHLAND MI69.000] TO BUS 324671 [2OVERLAD S T69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1456 324572-324691(1) | OPEN LINE FROM BUS 324572 [2HILLSIDE 69.000] TO BUS 324691 [2POWDERLY 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1457 324573-324741(1) | OPEN LINE FROM BUS 324573 [2HINKLE 69.000] TO BUS 324741 [2STINKIN CRK69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1458 324576-324748(1) | OPEN LINE FROM BUS 324576 [2HOPEWELL 69.000] TO BUS 324748 [2SWEET HOLLO69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1459 324577-324693(1) | OPEN LINE FROM BUS 324577 [2HARDESTY A 69.000] TO BUS 324693 [2PRINCETON 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1460 324577-324769(1) | OPEN LINE FROM BUS 324577 [2HARDESTY A 69.000] TO BUS 324769 [2WALKER KU 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1461 324578-324690(1) | OPEN LINE FROM BUS 324578 [2HARDESTY B 69.000] TO BUS 324690 [2DAWSON TAP 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1462 324578-324769(1) | OPEN LINE FROM BUS 324578 [2HARDESTY B 69.000] TO BUS 324769 [2WALKER KU 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1463 324579-324580(1) | OPEN LINE FROM BUS 324579 [2HARMNY LAND69.000] TO BUS 324580 [2HARRODS CRK69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1464 324579-324960(1) | OPEN LINE FROM BUS 324579 [2HARMNY LAND69.000] TO BUS 324960 [2SKYLIGHT 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1465 324580-324750(1) | OPEN LINE FROM BUS 324580 [2HARRODS CRK69.000] TO BUS 324750 [2TAYLOR LG 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1466 324580-324785(1) | OPEN LINE FROM BUS 324580 [2HARRODS CRK69.000] TO BUS 324785 [2WORTHINGTON69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1467 324581-324586(1) | OPEN LINE FROM BUS 324581 [2HUGHES LANE69.000] TO BUS 324586 [2JOYLAND 69.000] CKT 1 | -31.4796 | 31.4796 | 33 | 95.3927 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1468 324582-324610(1) | OPEN LINE FROM BUS 324582 [2IBM 69.000] TO BUS 324610 [2LEX PLANT 69.000] CKT 1 | -31.4821 | 31.4821 | 33 | 95.4003 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1469 324582-324879(1) | OPEN LINE FROM BUS 324582 [2IBM 69.000] TO BUS 324879 [2IBM 998 69.000] CKT 1 | -31.4823 | 31.4823 | 33 | 95.4009 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1470 324583-324591(1) | OPEN LINE FROM BUS 324583 [2IMBODEN 69.000] TO BUS 324591 [2KEOKEE TAP 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1471 324584-324659(1) | OPEN LINE FROM BUS 324584 [2INDIAN HILL69.000] TO BUS 324659 [2NELSON 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1472 324585-324598(1) | OPEN LINE FROM BUS 324585 [2JERICHO 69.000] TO BUS 324598 [2LA GRANGE E69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1473 324586-324610(1) | OPEN LINE FROM BUS 324586 [2JOYLAND 69.000] TO BUS 324610 [2LEX PLANT 69.000] CKT 1 | -31.4846 | 31.4846 | 33 | 95.4079 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1474 324587-324702(1) | OPEN LINE FROM BUS 324587 [2KEN AMERICA69.000] TO BUS 324702 [2RIVER QUEEN69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1475 324587-324709(1) | OPEN LINE FROM BUS 324587 [2KEN AMERICA69.000] TO BUS 324709 [2RVR QUEEN T69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1476 324589-324722(1) | OPEN LINE FROM BUS 324589 [2KENTON 688 69.000] TO BUS 324722 [2SHARON KU 69.000] CKT 1 | -31.4805 | 31.4805 | 33 | 95.3954 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1477 324589-324899(1) | OPEN LINE FROM BUS 324589 [2KENTON 688 69.000] TO BUS 324899 [2MAYSVILLE E69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1478 324589-325019(1) | OPEN LINE FROM BUS 324589 [2KENTON 688 69.000] TO BUS 325019 [2KENTON-6 69.000] CKT 1 | -31.4799 | 31.4799 | 33 | 95.3937 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1479 324590-324719(1) | OPEN LINE FROM BUS 324590 [2KENWOOD 69.000] TO BUS 324719 [2SEMINOLE 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1480 324590-325023(1) | OPEN LINE FROM BUS 324590 [2KENWOOD 69.000] TO BUS 325023 [2ASHBOT EAST69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1481 324591-324592(1) | OPEN LINE FROM BUS 324591 [2KEOKEE TAP 69.000] TO BUS 324592 [2KEOKEE TVA 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1482 324592-324689(1) | OPEN LINE FROM BUS 324592 [2KEOKEE TVA 69.000] TO BUS 324689 [2POCKET 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1483 324593-324686(1) | OPEN LINE FROM BUS 324593 [2KU PARK 69.000] TO BUS 324686 [2PINEVILLE 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1484 324593-324741(1) | OPEN LINE FROM BUS 324593 [2KU PARK 69.000] TO BUS 324741 [2STINKIN CRK69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.398 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1485 324595-324837(1) | OPEN LINE FROM BUS 324595 [2KAWNEER 69.000] TO BUS 324837 [2CYNTHIAN KU69.000] CKT 1 | -31.4778 | 31.4778 | 33 | 95.3873 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1486 324597-324764(1) | OPEN LINE FROM BUS 324597 [2KY ST HOSP 69.000] TO BUS 324764 [2WEST CLIFF 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1487 324597-324840(1) | OPEN LINE FROM BUS 324597 [2KY ST HOSP 69.000] TO BUS 324840 [2DANVILLE E 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1488 324598-324682(1) | OPEN LINE FROM BUS 324598 [2LA GRANGE E69.000] TO BUS 324682 [2PENAL TAP 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1489 324599-324600(1) | OPEN LINE FROM BUS 324599 [2LANCASTER 269.000] TO BUS 324600 [2LANCASTR KU69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1490 324599-324971(1) | OPEN LINE FROM BUS 324599 [2LANCASTER 269.000] TO BUS 324971 [2STANFORD NO69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1491 324601-324650(1) | OPEN LINE FROM BUS 324601 [2LANSDOWNE 69.000] TO BUS 324650 [2MT TBR T 69.000] CKT 1 | -31.4817 | 31.4817 | 33 | 95.3991 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1492 324601-324780(1) | OPEN LINE FROM BUS 324601 [2LANSDOWNE 69.000] TO BUS 324780 [2WIL DOWN T169.000] CKT 1 | -31.4811 | 31.4811 | 33 | 95.3974 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1493 324602-324828(1) | OPEN LINE FROM BUS 324602 [2LAWRENCE TP69.000] TO BUS 324828 [2CAMPBBRG KU69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1494 324602-324888(1) | OPEN LINE FROM BUS 324602 [2LAWRENCE TP69.000] TO BUS 324888 [2LAWRENCE 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1495 324603-324605(1) | OPEN LINE FROM BUS 324603 [2LEBANON CIT69.000] TO BUS 324605 [2LEBANON EK 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1496 324604-324606(1) | OPEN LINE FROM BUS 324604 [2LEBANON IND69.000] TO BUS 324606 [2LEBANON 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1497 324604-325020(1) | OPEN LINE FROM BUS 324604 [2LEBANON IND69.000] TO BUS 325020 [2LEBANON E 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1498 324605-324889(1) | OPEN LINE FROM BUS 324605 [2LEBANON EK 69.000] TO BUS 324889 [2LEBANON SO 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1499 324606-324736(1) | OPEN LINE FROM BUS 324606 [2LEBANON 69.000] TO BUS 324736 [2SPRINGFL KU69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
341383 | 2DAVIS | 69 | 341965 | 2NICHOLASVIL | 69 | 1 | SINGLE OPN TIE 665 342547-324210(1) | OPEN LINE FROM BUS 342547 [4BAKER LN 138.00] TO BUS 324210 [4BAKER LANE 138.00] CKT 1 | 60.421 | 60.421 | 63 | 95.9064 | EKPC
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1500 324607-324608(1) | OPEN LINE FROM BUS 324607 [2LEITCHF CIT69.000] TO BUS 324608 [2LEITCHF E 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1501 324607-324609(1) | OPEN LINE FROM BUS 324607 [2LEITCHF CIT69.000] TO BUS 324609 [2LEITCHFIELD69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1502 324608-324992(1) | OPEN LINE FROM BUS 324608 [2LEITCHF E 69.000] TO BUS 324992 [2WARREN TIE 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1503 324609-324643(1) | OPEN LINE FROM BUS 324609 [2LEITCHFIELD69.000] TO BUS 324643 [2MILL WOOD 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1504 324609-325040(1) | OPEN LINE FROM BUS 324609 [2LEITCHFIELD69.000] TO BUS 325040 [2LEITCHF TVA69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1505 324609-325040(2) | OPEN LINE FROM BUS 324609 [2LEITCHFIELD69.000] TO BUS 325040 [2LEITCHF TVA69.000] CKT 2 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1506 324610-324617(1) | OPEN LINE FROM BUS 324610 [2LEX PLANT 69.000] TO BUS 324617 [2LOUDON 618 69.000] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3988 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1507 324610-324674(1) | OPEN LINE FROM BUS 324610 [2LEX PLANT 69.000] TO BUS 324674 [2PROC & GAMB69.000] CKT 1 | -31.4811 | 31.4811 | 33 | 95.3972 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1508 324611-324618(1) | OPEN LINE FROM BUS 324611 [2LIBERTY RD 69.000] TO BUS 324618 [2LOUDON 628 69.000] CKT 1 | -31.4812 | 31.4812 | 33 | 95.3976 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1509 324611-324891(1) | OPEN LINE FROM BUS 324611 [2LIBERTY RD 69.000] TO BUS 324891 [2LEX WATER 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1510 324612-324701(1) | OPEN LINE FROM BUS 324612 [2LAKE REBA 69.000] TO BUS 324701 [2RICHMND 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1511 324612-324768(1) | OPEN LINE FROM BUS 324612 [2LAKE REBA 69.000] TO BUS 324768 [2WACO 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1512 324613-324618(1) | OPEN LINE FROM BUS 324613 [2LK SHORE TP69.000] TO BUS 324618 [2LOUDON 628 69.000] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1513 324613-325059(1) | OPEN LINE FROM BUS 324613 [2LK SHORE TP69.000] TO BUS 325059 [2BRYANT RD T69.000] CKT 1 | -31.4801 | 31.4801 | 33 | 95.3943 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1514 324614-324719(1) | OPEN LINE FROM BUS 324614 [2LOCUST TAP 69.000] TO BUS 324719 [2SEMINOLE 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1515 324614-326545(1) | OPEN LINE FROM BUS 324614 [2LOCUST TAP 69.000] TO BUS 326545 [2LOCUST LGE 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1516 324615-324688(1) | OPEN LINE FROM BUS 324615 [2LONDON 69.000] TO BUS 324688 [2PITTSBRG KU69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.398 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1517 324616-324775(1) | OPEN LINE FROM BUS 324616 [2LONG RUN 69.000] TO BUS 324775 [2WHAS 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1518 324617-324618(1) | OPEN LINE FROM BUS 324617 [2LOUDON 618 69.000] TO BUS 324618 [2LOUDON 628 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1519 324618-326586(1) | OPEN LINE FROM BUS 324618 [2LOUDON 628 69.000] TO BUS 326586 [2HUME RD TAP69.000] CKT 1 | -31.481 | 31.481 | 33 | 95.3969 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1520 324619-324998(1) | OPEN LINE FROM BUS 324619 [2LOWER MIL C69.000] TO BUS 324998 [2WEST CO 2 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
342000 | 5GAS | 161 | 342760 | 5LIBERTY J | 161 | 1 | SINGLE OPN LIN 1540 324641-324751(1) | OPEN LINE FROM BUS 324641 [2MILE LAN TP69.000] TO BUS 324751 [2TAYLOR CO 69.000] CKT 1 | 146.695 | 146.695 | 153 | 95.8791 | EKPC
341383 | 2DAVIS | 69 | 341965 | 2NICHOLASVIL | 69 | 1 | SINGLE OPN LIN 23 341041-342547(1) | OPEN LINE FROM BUS 341041 [2BAKER LN 69.000] TO BUS 342547 [4BAKER LN 138.00] CKT 1 | 60.4019 | 60.4019 | 63 | 95.8761 | EKPC
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1521 324621-326523(1) | OPEN LINE FROM BUS 324621 [2LYNCH 69.000] TO BUS 326523 [2ARKLAND JCT69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1522 324622-324637(1) | OPEN LINE FROM BUS 324622 [2LYNDON SO 69.000] TO BUS 324637 [2MIDDLETOWN 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1523 324622-324673(1) | OPEN LINE FROM BUS 324622 [2LYNDON SO 69.000] TO BUS 324673 [2OXMOOR 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1524 324623-324637(1) | OPEN LINE FROM BUS 324623 [2LYNDON 69.000] TO BUS 324637 [2MIDDLETOWN 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1525 324626-324627(1) | OPEN LINE FROM BUS 324626 [2MANCHEST SO69.000] TO BUS 324627 [2MANCHEST KU69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1526 324628-324629(1) | OPEN LINE FROM BUS 324628 [2MARION SO 69.000] TO BUS 324629 [2MARION KU 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1527 324629-324904(1) | OPEN LINE FROM BUS 324629 [2MARION KU 69.000] TO BUS 324904 [2MEXICO KU 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1528 324630-324862(1) | OPEN LINE FROM BUS 324630 [2MADSNV LP E69.000] TO BUS 324862 [2FIES CITY 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1529 324631-324658(1) | OPEN LINE FROM BUS 324631 [2MADSNV LP W69.000] TO BUS 324658 [2NEBO 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1530 324633-324636(1) | OPEN LINE FROM BUS 324633 [2MELDRUM 69.000] TO BUS 324636 [2MIDDLESBORO69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1531 324633-324684(1) | OPEN LINE FROM BUS 324633 [2MELDRUM 69.000] TO BUS 324684 [2PINEVIL 72269.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1532 324634-324849(1) | OPEN LINE FROM BUS 324634 [2METAL+THERM69.000] TO BUS 324849 [2DOW CORNING69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.398 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1533 324636-324874(1) | OPEN LINE FROM BUS 324636 [2MIDDLESBORO69.000] TO BUS 324874 [2HARROGATE 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1534 324637-324653(1) | OPEN LINE FROM BUS 324637 [2MIDDLETOWN 69.000] TO BUS 324653 [2M-V SIMPSON69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1535 324638-324706(1) | OPEN LINE FROM BUS 324638 [2MILL CRK KU69.000] TO BUS 324706 [2ROCKY BRNCH69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1536 324638-324813(1) | OPEN LINE FROM BUS 324638 [2MILL CRK KU69.000] TO BUS 324813 [2CARY 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1537 324639-324642(1) | OPEN LINE FROM BUS 324639 [2MILLRSB624 69.000] TO BUS 324642 [2MILLERSBURG69.000] CKT 1 | -31.4834 | 31.4834 | 33 | 95.4043 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1538 324639-324812(1) | OPEN LINE FROM BUS 324639 [2MILLRSB624 69.000] TO BUS 324812 [2CARLISLE 69.000] CKT 1 | -31.481 | 31.4809 | 33 | 95.3968 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1539 324639-325035(1) | OPEN LINE FROM BUS 324639 [2MILLRSB624 69.000] TO BUS 325035 [2BLUE SOL TP69.000] CKT 1 | -31.4853 | 31.4853 | 33 | 95.4101 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1540 324641-324751(1) | OPEN LINE FROM BUS 324641 [2MILE LAN TP69.000] TO BUS 324751 [2TAYLOR CO 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
341383 | 2DAVIS | 69 | 341965 | 2NICHOLASVIL | 69 | 1 | B-138-117 | B-138-117 | 60.3857 | 60.3857 | 63 | 95.8503 | EKPC
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1541 324641-324829(1) | OPEN LINE FROM BUS 324641 [2MILE LAN TP69.000] TO BUS 324829 [2CAMPBELVIL169.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
342000 | 5GAS | 161 | 342760 | 5LIBERTY J | 161 | 1 | SINGLE OPN LIN 974 324238-324239(1) | OPEN LINE FROM BUS 324238 [4DANVILLE N 138.00] TO BUS 324239 [4DANVILE N T138.00] CKT 1 | 146.5529 | 146.5529 | 153 | 95.7862 | EKPC
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1542 324641-326970(1) | OPEN LINE FROM BUS 324641 [2MILE LAN TP69.000] TO BUS 326970 [2MILE LAN EK69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1543 324642-324677(1) | OPEN LINE FROM BUS 324642 [2MILLERSBURG69.000] TO BUS 324677 [2PARIS 12 69.000] CKT 1 | -31.482 | 31.482 | 33 | 95.3999 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1544 324642-324679(1) | OPEN LINE FROM BUS 324642 [2MILLERSBURG69.000] TO BUS 324679 [2PARIS 3 69.000] CKT 1 | -31.4821 | 31.4821 | 33 | 95.4002 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1545 324642-324717(1) | OPEN LINE FROM BUS 324642 [2MILLERSBURG69.000] TO BUS 324717 [2SARDIS TAP 69.000] CKT 1 | -31.479 | 31.479 | 33 | 95.3908 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1546 324643-324811(1) | OPEN LINE FROM BUS 324643 [2MILL WOOD 69.000] TO BUS 324811 [2CANEYVL JCT69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1547 324644-324645(1) | OPEN LINE FROM BUS 324644 [2MORGANFLD 469.000] TO BUS 324645 [2MORGANFIELD69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1548 324644-324776(1) | OPEN LINE FROM BUS 324644 [2MORGANFLD 469.000] TO BUS 324776 [2WHEATCROF T69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1549 324645-324671(1) | OPEN LINE FROM BUS 324645 [2MORGANFIELD69.000] TO BUS 324671 [2OVERLAD S T69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1550 324645-326546(1) | OPEN LINE FROM BUS 324645 [2MORGANFIELD69.000] TO BUS 326546 [2SUNOCO TAP 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1551 324645-326572(1) | OPEN LINE FROM BUS 324645 [2MORGANFIELD69.000] TO BUS 326572 [2RIVRVW COAL69.000] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1552 324646-324707(1) | OPEN LINE FROM BUS 324646 [2MOREHEAD E 69.000] TO BUS 324707 [2RODBURN 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1553 324646-324910(1) | OPEN LINE FROM BUS 324646 [2MOREHEAD E 69.000] TO BUS 324910 [2MOREHEAD 69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3977 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1554 324647-324910(1) | OPEN LINE FROM BUS 324647 [2MOREHEAD W 69.000] TO BUS 324910 [2MOREHEAD 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1555 324648-324664(1) | OPEN LINE FROM BUS 324648 [2MORTONS GAP69.000] TO BUS 324664 [2OAK HILL KU69.000] CKT 1 | -31.4817 | 31.4817 | 33 | 95.399 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1556 324648-324769(1) | OPEN LINE FROM BUS 324648 [2MORTONS GAP69.000] TO BUS 324769 [2WALKER KU 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1557 324649-324675(1) | OPEN LINE FROM BUS 324649 [2MORRIS FORM69.000] TO BUS 324675 [2PADDYS RUN 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1558 324650-324891(1) | OPEN LINE FROM BUS 324650 [2MT TBR T 69.000] TO BUS 324891 [2LEX WATER 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1559 324652-324817(1) | OPEN LINE FROM BUS 324652 [2MUHLENBRG P69.000] TO BUS 324817 [2CENTRAL CIT69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1560 324655-324748(1) | OPEN LINE FROM BUS 324655 [2N CORBIN T 69.000] TO BUS 324748 [2SWEET HOLLO69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.398 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1561 324655-324791(1) | OPEN LINE FROM BUS 324655 [2N CORBIN T 69.000] TO BUS 324791 [2AISIN 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1562 324655-326542(1) | OPEN LINE FROM BUS 324655 [2N CORBIN T 69.000] TO BUS 326542 [2N CORBIN 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1563 324656-324968(1) | OPEN LINE FROM BUS 324656 [2N MADISON T69.000] TO BUS 324968 [2SPEAR STA B69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1564 324657-324771(1) | OPEN LINE FROM BUS 324657 [2NACHAND 69.000] TO BUS 324771 [2WATTERSON 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1565 324658-324774(1) | OPEN LINE FROM BUS 324658 [2NEBO 69.000] TO BUS 324774 [2WEBCOAL 4 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1566 324658-324776(1) | OPEN LINE FROM BUS 324658 [2NEBO 69.000] TO BUS 324776 [2WHEATCROF T69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1567 324658-324931(1) | OPEN LINE FROM BUS 324658 [2NEBO 69.000] TO BUS 324931 [2PROVIDNCE E69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1568 324659-326513(1) | OPEN LINE FROM BUS 324659 [2NELSON 69.000] TO BUS 326513 [2EQAL M BREC69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1569 324660-324801(1) | OPEN LINE FROM BUS 324660 [2NEW HAVEN 69.000] TO BUS 324801 [2BARTON 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1570 324661-324989(1) | OPEN LINE FROM BUS 324661 [2NICHLSV 7 69.000] TO BUS 324989 [2W NICHSV T 69.000] CKT 1 | -31.4809 | 31.4809 | 33 | 95.3968 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1571 324662-324688(1) | OPEN LINE FROM BUS 324662 [2N LONDON KU69.000] TO BUS 324688 [2PITTSBRG KU69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1572 324663-324826(1) | OPEN LINE FROM BUS 324663 [2NORTON EAST69.000] TO BUS 324826 [2CLINCH V SW69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1573 324667-324703(1) | OPEN LINE FROM BUS 324667 [2OHIO COUNTY69.000] TO BUS 324703 [2RIVERVIEW 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1574 324667-324770(1) | OPEN LINE FROM BUS 324667 [2OHIO COUNTY69.000] TO BUS 324770 [2WARREN 4 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1575 324668-324936(1) | OPEN LINE FROM BUS 324668 [2OKONITE 69.000] TO BUS 324936 [2RICHMND IND69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1576 324672-324916(1) | OPEN LINE FROM BUS 324672 [2OXFORD EK T69.000] TO BUS 324916 [2NEWTOWN TAP69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1577 324674-324934(1) | OPEN LINE FROM BUS 324674 [2PROC & GAMB69.000] TO BUS 324934 [2RACE STREET69.000] CKT 1 | -31.4812 | 31.4812 | 33 | 95.3976 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1578 324677-324680(1) | OPEN LINE FROM BUS 324677 [2PARIS 12 69.000] TO BUS 324680 [2PARIS KU 69.000] CKT 1 | -31.4783 | 31.4783 | 33 | 95.3887 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1579 324678-324679(1) | OPEN LINE FROM BUS 324678 [2PARIS CITY 69.000] TO BUS 324679 [2PARIS 3 69.000] CKT 1 | -31.4857 | 31.4857 | 33 | 95.4113 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1580 324678-324680(1) | OPEN LINE FROM BUS 324678 [2PARIS CITY 69.000] TO BUS 324680 [2PARIS KU 69.000] CKT 1 | -31.481 | 31.481 | 33 | 95.397 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1581 324681-324960(1) | OPEN LINE FROM BUS 324681 [2PENAL FARM 69.000] TO BUS 324960 [2SKYLIGHT 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1582 324682-324887(1) | OPEN LINE FROM BUS 324682 [2PENAL TAP 69.000] TO BUS 324887 [2LA GRANG PE69.000] CKT 1 | -31.4817 | 31.4817 | 33 | 95.399 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1583 324683-324866(1) | OPEN LINE FROM BUS 324683 [2PICADOME 69.000] TO BUS 324866 [2GE LAMP 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1584 324684-324686(1) | OPEN LINE FROM BUS 324684 [2PINEVIL 72269.000] TO BUS 324686 [2PINEVILLE 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1585 324687-324694(1) | OPEN LINE FROM BUS 324687 [2PISGAH 69.000] TO BUS 324694 [2PARKR MIL T69.000] CKT 1 | -31.4819 | 31.4819 | 33 | 95.3997 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1586 324689-324738(1) | OPEN LINE FROM BUS 324689 [2POCKET 69.000] TO BUS 324738 [2SAINT CHARL69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1587 324689-324744(1) | OPEN LINE FROM BUS 324689 [2POCKET 69.000] TO BUS 324744 [2STRAGHT CRK69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1588 324690-324747(1) | OPEN LINE FROM BUS 324690 [2DAWSON TAP 69.000] TO BUS 324747 [2SUNSET MINE69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1589 324690-324843(1) | OPEN LINE FROM BUS 324690 [2DAWSON TAP 69.000] TO BUS 324843 [2DAWSON IND 69.000] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1590 324691-324870(1) | OPEN LINE FROM BUS 324691 [2POWDERLY 69.000] TO BUS 324870 [2GREENVILLE 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1591 324692-324738(1) | OPEN LINE FROM BUS 324692 [2POWELL MTN 69.000] TO BUS 324738 [2SAINT CHARL69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1592 324693-324747(1) | OPEN LINE FROM BUS 324693 [2PRINCETON 69.000] TO BUS 324747 [2SUNSET MINE69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1593 324694-324884(1) | OPEN LINE FROM BUS 324694 [2PARKR MIL T69.000] TO BUS 324884 [2KUNKEL 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1594 324694-324930(1) | OPEN LINE FROM BUS 324694 [2PARKR MIL T69.000] TO BUS 324930 [2PARKER MILL69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.398 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1595 324695-324749(1) | OPEN LINE FROM BUS 324695 [2PARKER SEAL69.000] TO BUS 324749 [2SYLVANIA 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1596 324695-324783(1) | OPEN LINE FROM BUS 324695 [2PARKER SEAL69.000] TO BUS 324783 [2WINCHSTR KU69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1597 324696-324706(1) | OPEN LINE FROM BUS 324696 [2PUCKETT CRK69.000] TO BUS 324706 [2ROCKY BRNCH69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1598 324696-324792(1) | OPEN LINE FROM BUS 324696 [2PUCKETT CRK69.000] TO BUS 324792 [2ALVA 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1599 324698-324708(1) | OPEN LINE FROM BUS 324698 [2RADCLIFF SO69.000] TO BUS 324708 [2ROGERSVILLE69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1600 324698-326555(1) | OPEN LINE FROM BUS 324698 [2RADCLIFF SO69.000] TO BUS 326555 [2RINEYVIL RD69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1601 324699-324768(1) | OPEN LINE FROM BUS 324699 [2RICE STA TP69.000] TO BUS 324768 [2WACO 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1602 324699-326552(1) | OPEN LINE FROM BUS 324699 [2RICE STA TP69.000] TO BUS 326552 [2SE COAL TP 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1603 324700-324938(1) | OPEN LINE FROM BUS 324700 [2RICHMND SO 69.000] TO BUS 324938 [2RICHMND 3 69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3979 | LGEE
342000 | 5GAS | 161 | 342760 | 5LIBERTY J | 161 | 1 | SINGLE OPN LIN 975 324238-324495(1) | OPEN LINE FROM BUS 324238 [4DANVILLE N 138.00] TO BUS 324495 [2DANVILLE N 69.000] CKT 1 | 146.5496 | 146.5496 | 153 | 95.784 | EKPC
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1604 324703-324959(1) | OPEN LINE FROM BUS 324703 [2RIVERVIEW 69.000] TO BUS 324959 [2SIMMONS 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1605 324704-324784(1) | OPEN LINE FROM BUS 324704 [2ROCKHOLD 69.000] TO BUS 324784 [2WOFFORD 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1606 324705-324783(1) | OPEN LINE FROM BUS 324705 [2ROCKWELL 69.000] TO BUS 324783 [2WINCHSTR KU69.000] CKT 1 | -31.4817 | 31.4817 | 33 | 95.399 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1607 324705-324855(1) | OPEN LINE FROM BUS 324705 [2ROCKWELL 69.000] TO BUS 324855 [2EKPC OFF TP69.000] CKT 1 | -31.4824 | 31.4824 | 33 | 95.4012 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1608 324708-324944(1) | OPEN LINE FROM BUS 324708 [2ROGERSVILLE69.000] TO BUS 324944 [2ROGERSV 60569.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1609 324709-324981(1) | OPEN LINE FROM BUS 324709 [2RVR QUEEN T69.000] TO BUS 324981 [2TEXAS GAS T69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1610 324710-324750(1) | OPEN LINE FROM BUS 324710 [2RVR CITY SH69.000] TO BUS 324750 [2TAYLOR LG 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1611 324711-324790(1) | OPEN LINE FROM BUS 324711 [2SPEN CHEM T69.000] TO BUS 324790 [2AIRLINE RD 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1612 324712-324825(1) | OPEN LINE FROM BUS 324712 [2SO PADUCAH 69.000] TO BUS 324825 [2CLINTON KU 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1613 324713-324955(1) | OPEN LINE FROM BUS 324713 [2SO ELKHORN 69.000] TO BUS 324955 [2SHANNON RUN69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3979 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1614 324714-324733(1) | OPEN LINE FROM BUS 324714 [2SALT LICK 69.000] TO BUS 324733 [2SPENCER RD 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1615 324715-324721(1) | OPEN LINE FROM BUS 324715 [2SALVISA 69.000] TO BUS 324721 [2SHAKERTOWN 69.000] CKT 1 | -31.4817 | 31.4817 | 33 | 95.399 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1616 324715-325087(1) | OPEN LINE FROM BUS 324715 [2SALVISA 69.000] TO BUS 325087 [2CLAY LICK T69.000] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3989 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1617 324716-324977(1) | OPEN LINE FROM BUS 324716 [2SANDY RIDGE69.000] TO BUS 324977 [2TOMS CRK TP69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.398 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1618 324717-326549(1) | OPEN LINE FROM BUS 324717 [2SARDIS TAP 69.000] TO BUS 326549 [2SARDIS 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1619 324718-324726(1) | OPEN LINE FROM BUS 324718 [2SHELBY CO T69.000] TO BUS 324726 [2SHELBYVIL S69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1620 324719-324724(1) | OPEN LINE FROM BUS 324719 [2SEMINOLE 69.000] TO BUS 324724 [2SHIVELY 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1621 324721-324764(1) | OPEN LINE FROM BUS 324721 [2SHAKERTOWN 69.000] TO BUS 324764 [2WEST CLIFF 69.000] CKT 1 | -31.4817 | 31.4817 | 33 | 95.399 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1622 324723-325086(1) | OPEN LINE FROM BUS 324723 [2SHAVER CHAP69.000] TO BUS 325086 [2KEN AMERI 269.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1623 324725-324727(1) | OPEN LINE FROM BUS 324725 [2SHELBYVIL E69.000] TO BUS 324727 [2SHELBYVILLE69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1624 324726-324727(1) | OPEN LINE FROM BUS 324726 [2SHELBYVIL S69.000] TO BUS 324727 [2SHELBYVILLE69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1625 324727-325102(1) | OPEN LINE FROM BUS 324727 [2SHELBYVILLE69.000] TO BUS 325102 [2W SHELBY 69.000] CKT 1 | -31.4814 | 31.4815 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1626 324728-324781(1) | OPEN LINE FROM BUS 324728 [2SHUN PIKE 69.000] TO BUS 324781 [2WILMORE T 69.000] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3989 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1627 324729-325102(1) | OPEN LINE FROM BUS 324729 [2SIMPSONVILL69.000] TO BUS 325102 [2W SHELBY 69.000] CKT 1 | -31.4819 | 31.4819 | 33 | 95.3998 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1628 324731-326547(1) | OPEN LINE FROM BUS 324731 [2SONORA TAP 69.000] TO BUS 326547 [2SONORA 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1629 324734-324848(1) | OPEN LINE FROM BUS 324734 [2SPINDLETP T69.000] TO BUS 324848 [2DONERAIL 69.000] CKT 1 | -31.481 | 31.481 | 33 | 95.397 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1630 324735-324794(1) | OPEN LINE FROM BUS 324735 [2SOUTH POINT69.000] TO BUS 324794 [2ASHLND PIPE69.000] CKT 1 | -31.4809 | 31.4809 | 33 | 95.3967 | LGEE
342000 | 5GAS | 161 | 342760 | 5LIBERTY J | 161 | 1 | SINGLE OPN LIN 372 341845-342778(1) | OPEN LINE FROM BUS 341845 [2MCCREARY CO69.000] TO BUS 342778 [5MCCREARY CO161.00] CKT 1 | 146.242 | 146.242 | 153 | 95.583 | EKPC
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1631 324737-324969(1) | OPEN LINE FROM BUS 324737 [2SOMERSET SO69.000] TO BUS 324969 [2SMRST 615KU69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1632 324740-324788(1) | OPEN LINE FROM BUS 324740 [2SOUTH PARK 69.000] TO BUS 324788 [2BROOKS EK T69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1633 324740-325024(1) | OPEN LINE FROM BUS 324740 [2SOUTH PARK 69.000] TO BUS 325024 [2ASHBOT SPRK69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
342000 | 5GAS | 161 | 342760 | 5LIBERTY J | 161 | 1 | EKPC_P1-2_BONN - BARR 69 | EKPC_P1-2_BONN - BARR 69 | 146.2271 | 146.2271 | 153 | 95.5732 | EKPC
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1634 324742-324866(1) | OPEN LINE FROM BUS 324742 [2STONEWALL T69.000] TO BUS 324866 [2GE LAMP 69.000] CKT 1 | -31.4812 | 31.4812 | 33 | 95.3975 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1635 324742-324972(1) | OPEN LINE FROM BUS 324742 [2STONEWALL T69.000] TO BUS 324972 [2STONEWALL 69.000] CKT 1 | -31.4808 | 31.4808 | 33 | 95.3964 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1636 324743-324759(1) | OPEN LINE FROM BUS 324743 [2SAINT PAUL 69.000] TO BUS 324759 [2VIRGINIA CI69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1637 324743-324851(1) | OPEN LINE FROM BUS 324743 [2SAINT PAUL 69.000] TO BUS 324851 [2DWINA TAP 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1638 324744-324876(1) | OPEN LINE FROM BUS 324744 [2STRAGHT CRK69.000] TO BUS 324876 [2HOLMES MILL69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1639 324746-326546(1) | OPEN LINE FROM BUS 324746 [2SUNOCO 69.000] TO BUS 326546 [2SUNOCO TAP 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1640 324751-325921(1) | OPEN LINE FROM BUS 324751 [2TAYLOR CO 69.000] TO BUS 325921 [5TAYLOR CO 161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
342000 | 5GAS | 161 | 342760 | 5LIBERTY J | 161 | 1 | SINGLE OPN TIE 691 342718-324141(1) | OPEN LINE FROM BUS 342718 [5COOPER2 161.00] TO BUS 324141 [5ELIHU 161.00] CKT 1 | 146.2205 | 146.2205 | 153 | 95.569 | EKPC
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1641 324752-324974(1) | OPEN LINE FROM BUS 324752 [2TAYLORSV KU69.000] TO BUS 324974 [2TAYLRV EK T69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1642 324754-324928(1) | OPEN LINE FROM BUS 324754 [2TUNNEL H KU69.000] TO BUS 324928 [2POOLE 69.000] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1643 324755-324762(1) | OPEN LINE FROM BUS 324755 [2TYRONE 69.000] TO BUS 324762 [2VERSAIL W T69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1644 324755-324920(1) | OPEN LINE FROM BUS 324755 [2TYRONE 69.000] TO BUS 324920 [2NINEVAH TAP69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1645 324755-324985(1) | OPEN LINE FROM BUS 324755 [2TYRONE 69.000] TO BUS 324985 [2VSAIL BYPAS69.000] CKT 1 | -31.4821 | 31.4821 | 33 | 95.4003 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1646 324756-324772(1) | OPEN LINE FROM BUS 324756 [2UK WEST 1 69.000] TO BUS 324772 [2UK WEST 2 69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3978 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1647 324756-324952(1) | OPEN LINE FROM BUS 324756 [2UK WEST 1 69.000] TO BUS 324952 [2SCOTT ST TP69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3977 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1648 324757-324941(1) | OPEN LINE FROM BUS 324757 [2UPR MIL CRK69.000] TO BUS 324941 [2RIVERPORT 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1649 324758-324833(1) | OPEN LINE FROM BUS 324758 [2US STEEL 69.000] TO BUS 324833 [2CORBIN 2 69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3979 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1650 324760-324838(1) | OPEN LINE FROM BUS 324760 [2VAKSDAHL AV69.000] TO BUS 324838 [2DANV IND TP69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1651 324763-324985(1) | OPEN LINE FROM BUS 324763 [2VERSAILLES 69.000] TO BUS 324985 [2VSAIL BYPAS69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3978 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1652 324764-326578(1) | OPEN LINE FROM BUS 324764 [2WEST CLIFF 69.000] TO BUS 326578 [2HARRDSBRG 169.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1653 324765-326528(1) | OPEN LINE FROM BUS 324765 [2W FRANKFORT69.000] TO BUS 326528 [2BRIDGEPORT 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1654 324765-326973(1) | OPEN LINE FROM BUS 324765 [2W FRANKFORT69.000] TO BUS 326973 [2BRIDGPRT 1 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1655 324766-324952(1) | OPEN LINE FROM BUS 324766 [2W HIGH T1 69.000] TO BUS 324952 [2SCOTT ST TP69.000] CKT 1 | -31.4812 | 31.4812 | 33 | 95.3976 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1656 324767-326552(Z1) | OPEN LINE FROM BUS 324767 [2WEST IRVINE69.000] TO BUS 326552 [2SE COAL TP 69.000] CKT Z1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1657 324770-324946(1) | OPEN LINE FROM BUS 324770 [2WARREN 4 69.000] TO BUS 324946 [2ROSINE JCT 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1658 324774-324993(1) | OPEN LINE FROM BUS 324774 [2WEBCOAL 4 69.000] TO BUS 324993 [2WARRIOR CL 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1659 324776-324777(1) | OPEN LINE FROM BUS 324776 [2WHEATCROF T69.000] TO BUS 324777 [2WHEATCROFT 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1660 324777-324973(1) | OPEN LINE FROM BUS 324777 [2WHEATCROFT 69.000] TO BUS 324973 [2STURGIS 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1661 324778-324779(1) | OPEN LINE FROM BUS 324778 [2WICKLIFE CI69.000] TO BUS 324779 [2WICKLIFFE 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1662 324782-324783(1) | OPEN LINE FROM BUS 324782 [2WINCHEST SO69.000] TO BUS 324783 [2WINCHSTR KU69.000] CKT 1 | -31.4817 | 31.4817 | 33 | 95.3991 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1663 324784-325001(1) | OPEN LINE FROM BUS 324784 [2WOFFORD 69.000] TO BUS 325001 [2WILLMBRG SW69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1664 324786-324790(1) | OPEN LINE FROM BUS 324786 [2ZION 69.000] TO BUS 324790 [2AIRLINE RD 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1665 324787-324990(1) | OPEN LINE FROM BUS 324787 [2UNION UNDWR69.000] TO BUS 324990 [2WAITSBORO 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1666 324788-324809(1) | OPEN LINE FROM BUS 324788 [2BROOKS EK T69.000] TO BUS 324809 [2BROOKS EKPC69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1667 324789-324806(1) | OPEN LINE FROM BUS 324789 [2BLUE LCK TP69.000] TO BUS 324806 [2BEULAH EKPC69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1668 324789-325021(1) | OPEN LINE FROM BUS 324789 [2BLUE LCK TP69.000] TO BUS 325021 [2CONESTOGA 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1669 324791-324860(1) | OPEN LINE FROM BUS 324791 [2AISIN 69.000] TO BUS 324860 [2FARISTON 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1670 324792-324819(1) | OPEN LINE FROM BUS 324792 [2ALVA 69.000] TO BUS 324819 [2CHUNKLIC BR69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1671 324794-324987(1) | OPEN LINE FROM BUS 324794 [2ASHLND PIPE69.000] TO BUS 324987 [2W HICKMAN 69.000] CKT 1 | -31.4812 | 31.4812 | 33 | 95.3975 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1672 324795-324922(1) | OPEN LINE FROM BUS 324795 [2ASHBYBRG PU69.000] TO BUS 324922 [2ONTON 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1673 324797-324855(1) | OPEN LINE FROM BUS 324797 [2AVON T1 69.000] TO BUS 324855 [2EKPC OFF TP69.000] CKT 1 | -31.4818 | 31.4818 | 33 | 95.3994 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1674 324798-324875(1) | OPEN LINE FROM BUS 324798 [2BAILEY CRK 69.000] TO BUS 324875 [2HIGHSPLINT 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1675 324799-324931(1) | OPEN LINE FROM BUS 324799 [2BARNHILL 69.000] TO BUS 324931 [2PROVIDNCE E69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1676 324799-324932(1) | OPEN LINE FROM BUS 324799 [2BARNHILL 69.000] TO BUS 324932 [2PROVIDENCE 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1677 324802-324871(1) | OPEN LINE FROM BUS 324802 [2BEAR BRANCH69.000] TO BUS 324871 [2HAMER 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1678 324803-324907(1) | OPEN LINE FROM BUS 324803 [2BEAR TRACK 69.000] TO BUS 324907 [2MILLER CRK 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1679 324803-325058(1) | OPEN LINE FROM BUS 324803 [2BEAR TRACK 69.000] TO BUS 325058 [2BEATTY 614 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1680 324804-324908(1) | OPEN LINE FROM BUS 324804 [2BEDFORD TAP69.000] TO BUS 324908 [2MILTON 69.000] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1681 324804-325033(1) | OPEN LINE FROM BUS 324804 [2BEDFORD TAP69.000] TO BUS 325033 [2BEDFORD KU 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1682 324806-324925(1) | OPEN LINE FROM BUS 324806 [2BEULAH EKPC69.000] TO BUS 324925 [2PLEAS GRV T69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1683 324808-324913(1) | OPEN LINE FROM BUS 324808 [2BRODHEAD KU69.000] TO BUS 324913 [2MT VERNON 69.000] CKT 1 | -31.4812 | 31.4812 | 33 | 95.3975 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1684 324809-324958(1) | OPEN LINE FROM BUS 324809 [2BROOKS EKPC69.000] TO BUS 324958 [2SHEPHRDSV T69.000] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3989 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1685 324810-324947(1) | OPEN LINE FROM BUS 324810 [2CALHOUN 69.000] TO BUS 324947 [2RUMSEY 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1686 324811-324946(1) | OPEN LINE FROM BUS 324811 [2CANEYVL JCT69.000] TO BUS 324946 [2ROSINE JCT 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1687 324814-324956(1) | OPEN LINE FROM BUS 324814 [2CATRON CK T69.000] TO BUS 324956 [2SHAWNEE GAS69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1688 324815-325007(1) | OPEN LINE FROM BUS 324815 [2CAWOOD 69.000] TO BUS 325007 [2YANCY TAP 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1689 324816-324970(1) | OPEN LINE FROM BUS 324816 [2CEMETARY RD69.000] TO BUS 324970 [2STANFORD KU69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1690 324818-324827(1) | OPEN LINE FROM BUS 324818 [2CHAD TAP 69.000] TO BUS 324827 [2CLOVERLICK 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1691 324818-324978(1) | OPEN LINE FROM BUS 324818 [2CHAD TAP 69.000] TO BUS 324978 [2TOTZ 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1692 324819-324945(1) | OPEN LINE FROM BUS 324819 [2CHUNKLIC BR69.000] TO BUS 324945 [2ROSE HILL T69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1693 324820-324850(1) | OPEN LINE FROM BUS 324820 [2ISLAND MINE69.000] TO BUS 324850 [2DOZIER H 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1694 324820-324981(1) | OPEN LINE FROM BUS 324820 [2ISLAND MINE69.000] TO BUS 324981 [2TEXAS GAS T69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1695 324821-324914(1) | OPEN LINE FROM BUS 324821 [2CLARKSON 69.000] TO BUS 324914 [2M-V CLARK T69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1696 324821-324992(1) | OPEN LINE FROM BUS 324821 [2CLARKSON 69.000] TO BUS 324992 [2WARREN TIE 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1697 324822-324996(1) | OPEN LINE FROM BUS 324822 [2CLAY KU 69.000] TO BUS 324996 [2DOTIKI TAP 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1698 324823-324825(1) | OPEN LINE FROM BUS 324823 [2CLINTON 58169.000] TO BUS 324825 [2CLINTON KU 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1699 324824-325005(1) | OPEN LINE FROM BUS 324824 [2CLINCH VALL69.000] TO BUS 325005 [2WISE TAP 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1700 324826-324999(1) | OPEN LINE FROM BUS 324826 [2CLINCH V SW69.000] TO BUS 324999 [2WHTE OAK KU69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1701 324832-324833(1) | OPEN LINE FROM BUS 324832 [2CORBIN 1 69.000] TO BUS 324833 [2CORBIN 2 69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3979 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1702 324836-324853(1) | OPEN LINE FROM BUS 324836 [2BENS BRANCH69.000] TO BUS 324853 [2E STONE GAP69.000] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3988 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1703 324836-324894(1) | OPEN LINE FROM BUS 324836 [2BENS BRANCH69.000] TO BUS 324894 [2E STONE G T69.000] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3988 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1704 324838-324957(1) | OPEN LINE FROM BUS 324838 [2DANV IND TP69.000] TO BUS 324957 [2SHELBY CI T69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1705 324839-324909(1) | OPEN LINE FROM BUS 324839 [2DANVILE IND69.000] TO BUS 324909 [2MINR FARM T69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1706 324841-324909(1) | OPEN LINE FROM BUS 324841 [2DANVILLE W 69.000] TO BUS 324909 [2MINR FARM T69.000] CKT 1 | -31.4816 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1707 324842-324967(1) | OPEN LINE FROM BUS 324842 [2DAVIS TAP 69.000] TO BUS 324967 [2SPEAR STA A69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1708 324842-324987(1) | OPEN LINE FROM BUS 324842 [2DAVIS TAP 69.000] TO BUS 324987 [2W HICKMAN 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1709 324844-324943(1) | OPEN LINE FROM BUS 324844 [2DELAPLAIN 69.000] TO BUS 324943 [2ROGERS GAP 69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3977 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1710 324845-324962(1) | OPEN LINE FROM BUS 324845 [2DENHAM ST 69.000] TO BUS 324962 [2SOMERSET 1 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1711 324845-324963(1) | OPEN LINE FROM BUS 324845 [2DENHAM ST 69.000] TO BUS 324963 [2SOMERSET 2 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1712 324846-324932(1) | OPEN LINE FROM BUS 324846 [2DIAMOND 69.000] TO BUS 324932 [2PROVIDENCE 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1713 324846-324996(1) | OPEN LINE FROM BUS 324846 [2DIAMOND 69.000] TO BUS 324996 [2DOTIKI TAP 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1714 324847-324973(1) | OPEN LINE FROM BUS 324847 [2DODGE HILL 69.000] TO BUS 324973 [2STURGIS 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1715 324847-326546(1) | OPEN LINE FROM BUS 324847 [2DODGE HILL 69.000] TO BUS 326546 [2SUNOCO TAP 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1716 324848-324877(1) | OPEN LINE FROM BUS 324848 [2DONERAIL 69.000] TO BUS 324877 [2HOOVER KU 69.000] CKT 1 | -31.4811 | 31.4811 | 33 | 95.3971 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1717 324849-324867(1) | OPEN LINE FROM BUS 324849 [2DOW CORNING69.000] TO BUS 324867 [2GHENT 69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.398 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1718 324851-324999(1) | OPEN LINE FROM BUS 324851 [2DWINA TAP 69.000] TO BUS 324999 [2WHTE OAK KU69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1719 324852-324885(1) | OPEN LINE FROM BUS 324852 [2DYCUSBURG 69.000] TO BUS 324885 [2KUTTAWA 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1720 324852-324949(1) | OPEN LINE FROM BUS 324852 [2DYCUSBURG 69.000] TO BUS 324949 [2SALEM 673 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1721 324855-326541(1) | OPEN LINE FROM BUS 324855 [2EKPC OFF TP69.000] TO BUS 326541 [2EKPC OFFICE69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3978 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1722 324856-324880(1) | OPEN LINE FROM BUS 324856 [2ESTIL ST CO69.000] TO BUS 324880 [2IRVINE 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1723 324856-324907(1) | OPEN LINE FROM BUS 324856 [2ESTIL ST CO69.000] TO BUS 324907 [2MILLER CRK 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1724 324857-324858(1) | OPEN LINE FROM BUS 324857 [2ETOWN 2 69.000] TO BUS 324858 [2ETOWN 5 69.000] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1725 324862-325086(1) | OPEN LINE FROM BUS 324862 [2FIES CITY 69.000] TO BUS 325086 [2KEN AMERI 269.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1726 324863-324920(1) | OPEN LINE FROM BUS 324863 [2FLA TILE T169.000] TO BUS 324920 [2NINEVAH TAP69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1727 324865-324904(1) | OPEN LINE FROM BUS 324865 [2FREDONIA 69.000] TO BUS 324904 [2MEXICO KU 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1728 324867-324911(1) | OPEN LINE FROM BUS 324867 [2GHENT 69.000] TO BUS 324911 [2MARKLAND DM69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1729 324871-324894(1) | OPEN LINE FROM BUS 324871 [2HAMER 69.000] TO BUS 324894 [2E STONE G T69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1730 324873-324896(1) | OPEN LINE FROM BUS 324873 [2HANSON JCT 69.000] TO BUS 324896 [2MADSNV E 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1731 324875-324942(1) | OPEN LINE FROM BUS 324875 [2HIGHSPLINT 69.000] TO BUS 324942 [2ROBBINS 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1732 324877-324890(1) | OPEN LINE FROM BUS 324877 [2HOOVER KU 69.000] TO BUS 324890 [2LEMONS MILL69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1733 324878-324908(1) | OPEN LINE FROM BUS 324878 [2HUNT BTM TP69.000] TO BUS 324908 [2MILTON 69.000] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3989 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1734 324881-324942(1) | OPEN LINE FROM BUS 324881 [2JACKS CREEK69.000] TO BUS 324942 [2ROBBINS 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1735 324881-324978(1) | OPEN LINE FROM BUS 324881 [2JACKS CREEK69.000] TO BUS 324978 [2TOTZ 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1736 324884-324979(1) | OPEN LINE FROM BUS 324884 [2KUNKEL 69.000] TO BUS 324979 [2TRAFTON AVE69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.398 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1737 324886-324967(1) | OPEN LINE FROM BUS 324886 [2KY RIVER 69.000] TO BUS 324967 [2SPEAR STA A69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1738 324886-324968(1) | OPEN LINE FROM BUS 324886 [2KY RIVER 69.000] TO BUS 324968 [2SPEAR STA B69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1739 324892-324945(1) | OPEN LINE FROM BUS 324892 [2LIGGETT 69.000] TO BUS 324945 [2ROSE HILL T69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1740 324892-325007(1) | OPEN LINE FROM BUS 324892 [2LIGGETT 69.000] TO BUS 325007 [2YANCY TAP 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1741 324893-324897(1) | OPEN LINE FROM BUS 324893 [2MADSNV GE T69.000] TO BUS 324897 [2MADSNV N 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1742 324893-326587(1) | OPEN LINE FROM BUS 324893 [2MADSNV GE T69.000] TO BUS 326587 [2MADSNV W TP69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1743 324895-324897(1) | OPEN LINE FROM BUS 324895 [2MADSNV HO 69.000] TO BUS 324897 [2MADSNV N 69.000] CKT 1 | -31.4817 | 31.4817 | 33 | 95.399 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1744 324896-324902(1) | OPEN LINE FROM BUS 324896 [2MADSNV E 69.000] TO BUS 324902 [2MCCOY AVE 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1745 324898-324954(1) | OPEN LINE FROM BUS 324898 [2MANITOU 69.000] TO BUS 324954 [2SENTRY TAP 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1746 324898-324993(1) | OPEN LINE FROM BUS 324898 [2MANITOU 69.000] TO BUS 324993 [2WARRIOR CL 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1747 324899-324900(1) | OPEN LINE FROM BUS 324899 [2MAYSVILLE E69.000] TO BUS 324900 [2MAYSVILLE M69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1748 324903-324964(1) | OPEN LINE FROM BUS 324903 [2MCKEE ROAD 69.000] TO BUS 324964 [2SOMERSET 3 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1749 324903-324965(1) | OPEN LINE FROM BUS 324903 [2MCKEE ROAD 69.000] TO BUS 324965 [2SOMERSET NO69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1750 324909-325032(1) | OPEN LINE FROM BUS 324909 [2MINR FARM T69.000] TO BUS 325032 [2MINOR FARM 69.000] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1751 324911-324994(1) | OPEN LINE FROM BUS 324911 [2MARKLAND DM69.000] TO BUS 324994 [2WARSAW KU 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.398 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1752 324915-325006(1) | OPEN LINE FROM BUS 324915 [2MT WAS EK J69.000] TO BUS 325006 [2W MT WSH EK69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1753 324916-324924(1) | OPEN LINE FROM BUS 324916 [2NEWTOWN TAP69.000] TO BUS 324924 [2OXFORD 69.000] CKT 1 | -31.4819 | 31.4819 | 33 | 95.3998 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1754 324916-325027(1) | OPEN LINE FROM BUS 324916 [2NEWTOWN TAP69.000] TO BUS 325027 [2NEWTOWN 69.000] CKT 1 | -31.4819 | 31.4819 | 33 | 95.3998 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1755 324917-324918(1) | OPEN LINE FROM BUS 324917 [2NICHLSV 3 69.000] TO BUS 324918 [2NICHLSV 4&569.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1756 324917-324980(1) | OPEN LINE FROM BUS 324917 [2NICHLSV 3 69.000] TO BUS 324980 [2RJ CORMAN 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1757 324918-324919(1) | OPEN LINE FROM BUS 324918 [2NICHLSV 4&569.000] TO BUS 324919 [2NICHLSV 6&869.000] CKT 1 | -31.4811 | 31.4811 | 33 | 95.3972 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1758 324919-324989(1) | OPEN LINE FROM BUS 324919 [2NICHLSV 6&869.000] TO BUS 324989 [2W NICHSV T 69.000] CKT 1 | -31.4809 | 31.4809 | 33 | 95.3968 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1759 324920-326529(1) | OPEN LINE FROM BUS 324920 [2NINEVAH TAP69.000] TO BUS 326529 [2NINEVAH 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1760 324922-326563(1) | OPEN LINE FROM BUS 324922 [2ONTON 69.000] TO BUS 326563 [2ADVENT MINE69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1761 324925-325006(1) | OPEN LINE FROM BUS 324925 [2PLEAS GRV T69.000] TO BUS 325006 [2W MT WSH EK69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1762 324928-324953(1) | OPEN LINE FROM BUS 324928 [2POOLE 69.000] TO BUS 324953 [2SEBREE 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1763 324930-324972(1) | OPEN LINE FROM BUS 324930 [2PARKER MILL69.000] TO BUS 324972 [2STONEWALL 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1764 324934-324984(1) | OPEN LINE FROM BUS 324934 [2RACE STREET69.000] TO BUS 324984 [2VINE STREET69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1765 324935-324944(1) | OPEN LINE FROM BUS 324935 [2RADCLF KU T69.000] TO BUS 324944 [2ROGERSV 60569.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1766 324935-324982(1) | OPEN LINE FROM BUS 324935 [2RADCLF KU T69.000] TO BUS 324982 [2VINE GRV KU69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1767 324936-324940(1) | OPEN LINE FROM BUS 324936 [2RICHMND IND69.000] TO BUS 324940 [2RICHMND J 69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3979 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1768 324937-324939(1) | OPEN LINE FROM BUS 324937 [2RICHMND 2 69.000] TO BUS 324939 [2RICHMND 4 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1769 324938-324940(1) | OPEN LINE FROM BUS 324938 [2RICHMND 3 69.000] TO BUS 324940 [2RICHMND J 69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.398 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1770 324941-324975(1) | OPEN LINE FROM BUS 324941 [2RIVERPORT 69.000] TO BUS 324975 [2TERRY 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1771 324948-324949(1) | OPEN LINE FROM BUS 324948 [2SALEM KU 69.000] TO BUS 324949 [2SALEM 673 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1772 324950-325084(1) | OPEN LINE FROM BUS 324950 [2SCIENC HILL69.000] TO BUS 325084 [2FLOYD EKP T69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1773 324951-326989(1) | OPEN LINE FROM BUS 324951 [2SCOTT CO 69.000] TO BUS 326989 [2LONG LICK 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1774 324953-326563(1) | OPEN LINE FROM BUS 324953 [2SEBREE 69.000] TO BUS 326563 [2ADVENT MINE69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1775 324954-325762(1) | OPEN LINE FROM BUS 324954 [2SENTRY TAP 69.000] TO BUS 325762 [2WARRIOR TAP69.000] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3988 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1776 324957-324970(1) | OPEN LINE FROM BUS 324957 [2SHELBY CI T69.000] TO BUS 324970 [2STANFORD KU69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1777 324958-325043(1) | OPEN LINE FROM BUS 324958 [2SHEPHRDSV T69.000] TO BUS 325043 [2SHEPHERDSV 69.000] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3989 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1778 324959-326564(1) | OPEN LINE FROM BUS 324959 [2SIMMONS 69.000] TO BUS 326564 [2LEW BREC 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1779 324961-324963(1) | OPEN LINE FROM BUS 324961 [2SOMERSET GE69.000] TO BUS 324963 [2SOMERSET 2 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1780 324966-324994(1) | OPEN LINE FROM BUS 324966 [2SPARTA KU 69.000] TO BUS 324994 [2WARSAW KU 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1781 324969-324990(1) | OPEN LINE FROM BUS 324969 [2SMRST 615KU69.000] TO BUS 324990 [2WAITSBORO 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1782 324970-324971(1) | OPEN LINE FROM BUS 324970 [2STANFORD KU69.000] TO BUS 324971 [2STANFORD NO69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1783 324975-324997(1) | OPEN LINE FROM BUS 324975 [2TERRY 69.000] TO BUS 324997 [2WEST CO 1 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1784 324979-324986(1) | OPEN LINE FROM BUS 324979 [2TRAFTON AVE69.000] TO BUS 324986 [2W HIGH T2 69.000] CKT 1 | -31.4811 | 31.4811 | 33 | 95.3973 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1785 324981-325062(1) | OPEN LINE FROM BUS 324981 [2TEXAS GAS T69.000] TO BUS 325062 [2TEXAS GAS 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1786 324984-324988(1) | OPEN LINE FROM BUS 324984 [2VINE STREET69.000] TO BUS 324988 [2WEST HIGH 69.000] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3988 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1787 324994-325025(1) | OPEN LINE FROM BUS 324994 [2WARSAW KU 69.000] TO BUS 325025 [2WARSAW EAST69.000] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3989 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1788 324995-325084(1) | OPEN LINE FROM BUS 324995 [2WAYNESBURG 69.000] TO BUS 325084 [2FLOYD EKP T69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1789 324996-325010(1) | OPEN LINE FROM BUS 324996 [2DOTIKI TAP 69.000] TO BUS 325010 [2WEBCOAL 2 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1790 324997-324998(1) | OPEN LINE FROM BUS 324997 [2WEST CO 1 69.000] TO BUS 324998 [2WEST CO 2 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
342000 | 5GAS | 161 | 342760 | 5LIBERTY J | 161 | 1 | SINGLE OPN LIN 1640 324751-325921(1) | OPEN LINE FROM BUS 324751 [2TAYLOR CO 69.000] TO BUS 325921 [5TAYLOR CO 161.00] CKT 1 | 146.1412 | 146.1412 | 153 | 95.5171 | EKPC
342000 | 5GAS | 161 | 342760 | 5LIBERTY J | 161 | 1 | SINGLE OPN TIE 703 342817-325921(1) | OPEN LINE FROM BUS 342817 [5TAYLOR CO J161.00] TO BUS 325921 [5TAYLOR CO 161.00] CKT 1 | 146.1401 | 146.1401 | 153 | 95.5164 | EKPC
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1791 325002-325003(Z1) | OPEN LINE FROM BUS 325002 [2WILS DOWN 169.000] TO BUS 325003 [2WILS DOWN 269.000] CKT Z1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1792 325008-325026(1) | OPEN LINE FROM BUS 325008 [2BLEDSOE 69.000] TO BUS 325026 [2PINE MOUNTN69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1793 325010-325011(1) | OPEN LINE FROM BUS 325010 [2WEBCOAL 2 69.000] TO BUS 325011 [2DOTIKI 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1796 325023-325024(1) | OPEN LINE FROM BUS 325023 [2ASHBOT EAST69.000] TO BUS 325024 [2ASHBOT SPRK69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1797 325028-325047(1) | OPEN LINE FROM BUS 325028 [5ASHWD SL TP161.00] TO BUS 325047 [5ASHWOOD 161.00] CKT 1 | -31.4812 | 31.4812 | 33 | 95.3977 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1798 325028-326589(1) | OPEN LINE FROM BUS 325028 [5ASHWD SL TP161.00] TO BUS 326589 [5N PRN LIV R161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1799 325035-325050(1) | OPEN LINE FROM BUS 325035 [2BLUE SOL TP69.000] TO BUS 325050 [2BLUE SOLAR 69.000] CKT 1 | -31.4812 | 31.4812 | 33 | 95.3976 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1800 325035-325085(1) | OPEN LINE FROM BUS 325035 [2BLUE SOL TP69.000] TO BUS 325085 [2CYNTHI EK T69.000] CKT 1 | -31.4853 | 31.4853 | 33 | 95.41 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1801 325041-325068(1) | OPEN LINE FROM BUS 325041 [2STONE TVA 69.000] TO BUS 325068 [2HAMBLIN 69.000] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1802 325044-326565(1) | OPEN LINE FROM BUS 325044 [4INTRNTL 138.00] TO BUS 326565 [4INTRNTL TAP138.00] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1803 325045-325092(1) | OPEN LINE FROM BUS 325045 [2TURTLE CRK 69.000] TO BUS 325092 [2COAL GOOD 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1804 325055-325116(1) | OPEN LINE FROM BUS 325055 [4RHUDES TP 138.00] TO BUS 325116 [4RHUDES CR 138.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1805 325057-325088(1) | OPEN LINE FROM BUS 325057 [4KOSMOS CEME138.00] TO BUS 325088 [4MIL CK YARD138.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1806 325059-325060(1) | OPEN LINE FROM BUS 325059 [2BRYANT RD T69.000] TO BUS 325060 [2BRYANT ROAD69.000] CKT 1 | -31.4807 | 31.4807 | 33 | 95.3959 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1807 325075-325077(Z1) | OPEN LINE FROM BUS 325075 [5KMPA COLEMN161.00] TO BUS 325077 [5COLEMAN TAP161.00] CKT Z1 | -31.4817 | 31.4817 | 33 | 95.3991 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1808 325077-325078(1) | OPEN LINE FROM BUS 325077 [5COLEMAN TAP161.00] TO BUS 325078 [5PADUCAH PRI161.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1809 325078-326562(1) | OPEN LINE FROM BUS 325078 [5PADUCAH PRI161.00] TO BUS 326562 [2PAD PRI 62469.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1810 325078-326596(1) | OPEN LINE FROM BUS 325078 [5PADUCAH PRI161.00] TO BUS 326596 [2PAD PRI 61469.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1811 325079-326589(1) | OPEN LINE FROM BUS 325079 [5N PRINCETON161.00] TO BUS 326589 [5N PRN LIV R161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1812 325079-326591(1) | OPEN LINE FROM BUS 325079 [5N PRINCETON161.00] TO BUS 326591 [5W PRINCETON161.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1813 325083-326544(1) | OPEN LINE FROM BUS 325083 [2ALEX CK TAP69.000] TO BUS 326544 [2ALEX CREEK 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1814 325096-326002(1) | OPEN LINE FROM BUS 325096 [4CANERN NGCC138.00] TO BUS 326002 [7CANERN NGCC345.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1815 325096-326565(23) | OPEN LINE FROM BUS 325096 [4CANERN NGCC138.00] TO BUS 326565 [4INTRNTL TAP138.00] CKT 23 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1816 325096-326566(71) | OPEN LINE FROM BUS 325096 [4CANERN NGCC138.00] TO BUS 326566 [4CANE RUN 71138.00] CKT 71 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1817 325096-326567(72) | OPEN LINE FROM BUS 325096 [4CANERN NGCC138.00] TO BUS 326567 [4CANE RUN 72138.00] CKT 72 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1818 325096-326568(7S) | OPEN LINE FROM BUS 325096 [4CANERN NGCC138.00] TO BUS 326568 [4CANE RUN 7S138.00] CKT 7S | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1819 325096-326574(21) | OPEN LINE FROM BUS 325096 [4CANERN NGCC138.00] TO BUS 326574 [4CR11 TAP 138.00] CKT 21 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1820 325761-325762(1) | OPEN LINE FROM BUS 325761 [2WARRIOR PRP69.000] TO BUS 325762 [2WARRIOR TAP69.000] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1821 325762-325767(1) | OPEN LINE FROM BUS 325762 [2WARRIOR TAP69.000] TO BUS 325767 [2SENTRY 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1822 325857-325956(Z1) | OPEN LINE FROM BUS 325857 [4BROWN N TIE138.00] TO BUS 325956 [4BROWN N 2 138.00] CKT Z1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1823 325857-325957(Z1) | OPEN LINE FROM BUS 325857 [4BROWN N TIE138.00] TO BUS 325957 [4BROWN N 1 138.00] CKT Z1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1824 326001-326002(1) | OPEN LINE FROM BUS 326001 [7CANE RUN TP345.00] TO BUS 326002 [7CANERN NGCC345.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1825 326517-326523(1) | OPEN LINE FROM BUS 326517 [2OVEN FORK 69.000] TO BUS 326523 [2ARKLAND JCT69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1826 326523-326534(1) | OPEN LINE FROM BUS 326523 [2ARKLAND JCT69.000] TO BUS 326534 [2ARKLAND 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1827 326524-326527(1) | OPEN LINE FROM BUS 326524 [2VAN METER 69.000] TO BUS 326527 [2TREEHAVEN T69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1828 326525-326527(1) | OPEN LINE FROM BUS 326525 [2TREEHAVEN 69.000] TO BUS 326527 [2TREEHAVEN T69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1829 326526-326556(1) | OPEN LINE FROM BUS 326526 [4N SHARKEY 138.00] TO BUS 326556 [4N SHARKEY T138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1830 326527-326541(1) | OPEN LINE FROM BUS 326527 [2TREEHAVEN T69.000] TO BUS 326541 [2EKPC OFFICE69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1831 326528-326974(1) | OPEN LINE FROM BUS 326528 [2BRIDGEPORT 69.000] TO BUS 326974 [2BRIDGPRT 2 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1832 326530-326539(1) | OPEN LINE FROM BUS 326530 [2EMANUEL 69.000] TO BUS 326539 [2GIRDLER 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1833 326532-326556(1) | OPEN LINE FROM BUS 326532 [4SHARKEY 138.00] TO BUS 326556 [4N SHARKEY T138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1834 326552-326553(1) | OPEN LINE FROM BUS 326552 [2SE COAL TP 69.000] TO BUS 326553 [2SE COAL 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1835 326559-326560(1) | OPEN LINE FROM BUS 326559 [4BGAD TAP 138.00] TO BUS 326560 [4BG ARMY DEP138.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1836 326562-326596(Z1) | OPEN LINE FROM BUS 326562 [2PAD PRI 62469.000] TO BUS 326596 [2PAD PRI 61469.000] CKT Z1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1837 326571-326586(1) | OPEN LINE FROM BUS 326571 [2HUME RD 69.000] TO BUS 326586 [2HUME RD TAP69.000] CKT 1 | -31.4811 | 31.4811 | 33 | 95.3972 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1838 326578-326579(1) | OPEN LINE FROM BUS 326578 [2HARRDSBRG 169.000] TO BUS 326579 [2HARRDSBRG 269.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1839 326578-326584(1) | OPEN LINE FROM BUS 326578 [2HARRDSBRG 169.000] TO BUS 326584 [2CORNG7462_369.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1840 326579-326580(1) | OPEN LINE FROM BUS 326579 [2HARRDSBRG 269.000] TO BUS 326580 [2CORNIG 825369.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1841 326582-326583(1) | OPEN LINE FROM BUS 326582 [2CORNG8251_269.000] TO BUS 326583 [2CORNIG 746169.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1842 326583-326584(1) | OPEN LINE FROM BUS 326583 [2CORNIG 746169.000] TO BUS 326584 [2CORNG7462_369.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1843 326591-326592(1) | OPEN LINE FROM BUS 326591 [5W PRINCETON161.00] TO BUS 326592 [5E PRINCETON161.00] CKT 1 | -31.4817 | 31.4817 | 33 | 95.399 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1844 326593-326594(1) | OPEN LINE FROM BUS 326593 [2GREENVIL N 69.000] TO BUS 326594 [2GREENVL 12 69.000] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3989 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 1845 324010-248000(1) | OPEN LINE FROM BUS 324010 [7TRIMBL REAC345.00] TO BUS 248000 [06CLIFTY 345.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 1846 324021-324044(1) | OPEN LINE FROM BUS 324021 [7BLUEGRASS12345.00] TO BUS 324044 [1BLUEGRASS 118.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 1847 324021-324045(1) | OPEN LINE FROM BUS 324021 [7BLUEGRASS12345.00] TO BUS 324045 [1BLUEGRASS 218.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 1848 324022-324046(1) | OPEN LINE FROM BUS 324022 [7BLUEGRASS 3345.00] TO BUS 324046 [1BLUEGRASS 318.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 1850 324104-324113(1) | OPEN LINE FROM BUS 324104 [7DAVIESS 345.00] TO BUS 324113 [7SMITH 345.00] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3978 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 1851 324104-340561(1) | OPEN LINE FROM BUS 324104 [7DAVIESS 345.00] TO BUS 340561 [7WILSON 345.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 1852 324104-340563(1) | OPEN LINE FROM BUS 324104 [7DAVIESS 345.00] TO BUS 340563 [7COLEMAN 345.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 1853 324105-249501(1) | OPEN LINE FROM BUS 324105 [7GHENT 345.00] TO BUS 249501 [08BATESV 345.00] CKT 1 | -31.4812 | 31.4812 | 33 | 95.3977 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 1854 324105-249532(1) | OPEN LINE FROM BUS 324105 [7GHENT 345.00] TO BUS 249532 [08TRIMBL 345.00] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3978 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 1855 324108-324284-326550(5) | OPEN LINE FROM BUS 324108 [7MILL CREEK 345.00] TO BUS 324284 [4MILL CREEK 138.00] TO BUS 326550 [1MC TR5 TERT13.800] CKT 5 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 1856 324108-324284-326551(6) | OPEN LINE FROM BUS 324108 [7MILL CREEK 345.00] TO BUS 324284 [4MILL CREEK 138.00] TO BUS 326551 [1MC TR6 TERT13.800] CKT 6 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 1857 324112-324072(1) | OPEN LINE FROM BUS 324112 [7PINEVILLE 345.00] TO BUS 324072 [8PINEVILLE 500.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 1858 324114-249520(1) | OPEN LINE FROM BUS 324114 [7TRIMBLE CO 345.00] TO BUS 249520 [08SPEED 345.00] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3979 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 1859 324114-249532(1) | OPEN LINE FROM BUS 324114 [7TRIMBLE CO 345.00] TO BUS 249532 [08TRIMBL 345.00] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3979 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 1863 324144-340553(1) | OPEN LINE FROM BUS 324144 [5GREEN RIVER161.00] TO BUS 340553 [5WLSNBR 161.00] CKT 1 | -31.4813 | 31.4813 | 33 | 95.398 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 1864 324148-243668(1) | OPEN LINE FROM BUS 324148 [5WOOTON TAP 161.00] TO BUS 243668 [05WOOTON 161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 1865 324150-360334(1) | OPEN LINE FROM BUS 324150 [5LEBANON JCT161.00] TO BUS 360334 [5SUMMER SHAD161.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 1866 324151-360125(1) | OPEN LINE FROM BUS 324151 [5LIVNGSTN CO161.00] TO BUS 360125 [5CALVERT KY 161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 1867 324151-360127(1) | OPEN LINE FROM BUS 324151 [5LIVNGSTN CO161.00] TO BUS 360127 [5KENTUCKY HP161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 1868 324156-360452(1) | OPEN LINE FROM BUS 324156 [5PINEVILE SW161.00] TO BUS 360452 [5PINEVILL KY161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 1869 324157-324073(1) | OPEN LINE FROM BUS 324157 [5POCKET N 161.00] TO BUS 324073 [8POCKET N 500.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 1870 324171-351003(1) | OPEN LINE FROM BUS 324171 [5GRAHMVILE 1161.00] TO BUS 351003 [5JOPPA TS 161.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 1871 324172-351002(1) | OPEN LINE FROM BUS 324172 [5GRAHMVILE 2161.00] TO BUS 351002 [5JOPPA S 161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 1872 324173-340553(1) | OPEN LINE FROM BUS 324173 [5MATANZAS 161.00] TO BUS 340553 [5WLSNBR 161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 1873 324173-340624(1) | OPEN LINE FROM BUS 324173 [5MATANZAS 161.00] TO BUS 340624 [5BRTAP 161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 1875 324211-251561(1) | OPEN LINE FROM BUS 324211 [4BLACKWELL 138.00] TO BUS 251561 [08BLACKW 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 1877 324217-325012(1) | OPEN LINE FROM BUS 324217 [4BROWN PLANT138.00] TO BUS 325012 [1BROWN SOLAR13.200] CKT 1 | -31.4812 | 31.4812 | 33 | 95.3977 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 1878 324227-248009(1) | OPEN LINE FROM BUS 324227 [4CARROLLTON 138.00] TO BUS 248009 [06CLIFTY 138.00] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3988 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 1879 324231-253623(1) | OPEN LINE FROM BUS 324231 [4CLOVERPORT 138.00] TO BUS 253623 [10CANTAP 138.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 1880 324231-340615(1) | OPEN LINE FROM BUS 324231 [4CLOVERPORT 138.00] TO BUS 340615 [4N.HARD 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 1881 324232-324399(1) | OPEN LINE FROM BUS 324232 [4CANE RN 11A138.00] TO BUS 324399 [1CANERN11 14.000] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 1884 324253-249723(1) | OPEN LINE FROM BUS 324253 [4GHENT 138.00] TO BUS 249723 [08FAIRVW 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 1886 324256-324309(1) | OPEN LINE FROM BUS 324256 [4GR RVR STL 138.00] TO BUS 324309 [4SMITH 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 1887 324260-340615(1) | OPEN LINE FROM BUS 324260 [4HARDINSBURG138.00] TO BUS 340615 [4N.HARD 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 1889 324265-249763(1) | OPEN LINE FROM BUS 324265 [4JEFFRSONV T138.00] TO BUS 249763 [08JEFF 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 1890 324267-247508(1) | OPEN LINE FROM BUS 324267 [4KENTON 138.00] TO BUS 247508 [05SARDINIA 138.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 1892 324268-324170(1) | OPEN LINE FROM BUS 324268 [4KNOB CREEK 138.00] TO BUS 324170 [1KNOB CRK 34.500] CKT 1 | -31.4817 | 31.4817 | 33 | 95.3991 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 1899 324289-249789(1) | OPEN LINE FROM BUS 324289 [4NORTHSIDE 138.00] TO BUS 249789 [08LOUCMJ 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 1901 324294-249730(1) | OPEN LINE FROM BUS 324294 [4PADDYS WEST138.00] TO BUS 249730 [08GALAGH 138.00] CKT 1 | -31.4813 | 31.4813 | 33 | 95.398 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 1902 324295-324431(4A) | OPEN LINE FROM BUS 324295 [4PADDYS RUN 138.00] TO BUS 324431 [1PADDYR1 14.000] CKT 4A | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 1903 324295-324596(5) | OPEN LINE FROM BUS 324295 [4PADDYS RUN 138.00] TO BUS 324596 [1PADDYR2A 14.000] CKT 5 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 1904 324295-324675-324635(3) | OPEN LINE FROM BUS 324295 [4PADDYS RUN 138.00] TO BUS 324675 [2PADDYS RUN 69.000] TO BUS 324635 [1PADDYR2B 14.000] CKT 3 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 1906 324311-324366(1) | OPEN LINE FROM BUS 324311 [4TIP TOP 138.00] TO BUS 324366 [1TIPTOP 1 34.500] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3989 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 1907 324311-324753-326511(2) | OPEN LINE FROM BUS 324311 [4TIP TOP 138.00] TO BUS 324753 [2TIP TOP 2 69.000] TO BUS 326511 [1TIPTOP 34.500] CKT 2 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 1908 324316-242605(1) | OPEN LINE FROM BUS 324316 [4VIRGINIA CI138.00] TO BUS 242605 [05CLNCHR 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 1910 324405-326500(1) | OPEN LINE FROM BUS 324405 [2ADAMS 69.000] TO BUS 326500 [1ADAMS 34.500] CKT 1 | -31.4813 | 31.4813 | 33 | 95.398 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 1911 324412-326501(1) | OPEN LINE FROM BUS 324412 [2ANDOVER 69.000] TO BUS 326501 [1ANDOVE 34.500] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 1915 324437-324063(1) | OPEN LINE FROM BUS 324437 [2BEVIER KU 69.000] TO BUS 324063 [1BEVIER 34.500] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 1918 324446-324397(1) | OPEN LINE FROM BUS 324446 [2BOND 69.000] TO BUS 324397 [1BOND 23.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 1923 324503-324398(1) | OPEN LINE FROM BUS 324503 [2DORCHESTER 69.000] TO BUS 324398 [1DORCHEST 23.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 1924 324503-326504(1) | OPEN LINE FROM BUS 324503 [2DORCHESTER 69.000] TO BUS 326504 [1DORCHE 34.500] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 1925 324507-324123(1) | OPEN LINE FROM BUS 324507 [2EARLINGTON 69.000] TO BUS 324123 [1EARLINGT 34.500] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 1927 324512-362916(1) | OPEN LINE FROM BUS 324512 [2EDDYV PR TP69.000] TO BUS 362916 [2KY DAM 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 1933 324533-326505(1) | OPEN LINE FROM BUS 324533 [2FRANKFORT 169.000] TO BUS 326505 [1FFRT 34.500] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 1934 324550-324128(1) | OPEN LINE FROM BUS 324550 [2GREEN RIVER69.000] TO BUS 324128 [1GREEN RIVER34.500] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 1935 324551-324669(1) | OPEN LINE FROM BUS 324551 [2GR RVR STL 69.000] TO BUS 324669 [2OMU 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 1937 324574-324043(1) | OPEN LINE FROM BUS 324574 [2HILLCREST 69.000] TO BUS 324043 [1ZORN 13.800] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 1940 324578-324142(1) | OPEN LINE FROM BUS 324578 [2HARDESTY B 69.000] TO BUS 324142 [1HARDSTY 34.500] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 1941 324583-324168(1) | OPEN LINE FROM BUS 324583 [2IMBODEN 69.000] TO BUS 324168 [1IMBODEN 34.500] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 1945 324664-326507(1) | OPEN LINE FROM BUS 324664 [2OAK HILL KU69.000] TO BUS 326507 [1OAK HI 34.500] CKT 1 | -31.4817 | 31.4817 | 33 | 95.399 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 1948 324689-324184(1) | OPEN LINE FROM BUS 324689 [2POCKET 69.000] TO BUS 324184 [1POCKET 34.500] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 1949 324693-326509(1) | OPEN LINE FROM BUS 324693 [2PRINCETON 69.000] TO BUS 326509 [1PRINCE 34.500] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 1950 324707-243740(Z1) | OPEN LINE FROM BUS 324707 [2RODBURN 69.000] TO BUS 243740 [05MOREHE 69.000] CKT Z1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 1952 324712-362116(1) | OPEN LINE FROM BUS 324712 [2SO PADUCAH 69.000] TO BUS 362116 [2KY HYDRO 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 1959 324764-324368(1) | OPEN LINE FROM BUS 324764 [2WEST CLIFF 69.000] TO BUS 324368 [1W CLIFF 34.500] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 1962 324803-324057(1) | OPEN LINE FROM BUS 324803 [2BEAR TRACK 69.000] TO BUS 324057 [1BEAR TRA 34.500] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 1964 324947-324190(1) | OPEN LINE FROM BUS 324947 [2RUMSEY 69.000] TO BUS 324190 [1RUMSEY 34.500] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 1965 324948-324883(1) | OPEN LINE FROM BUS 324948 [2SALEM KU 69.000] TO BUS 324883 [1SALEM 34.500] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 1967 325013-248009(1) | OPEN LINE FROM BUS 325013 [4CLIFTY TAP1138.00] TO BUS 248009 [06CLIFTY 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 1968 325014-248009(1) | OPEN LINE FROM BUS 325014 [4CLIFTY TAP2138.00] TO BUS 248009 [06CLIFTY 138.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 1969 325014-250057(1) | OPEN LINE FROM BUS 325014 [4CLIFTY TAP2138.00] TO BUS 250057 [08M.FORT 138.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 1970 325015-324309(1) | OPEN LINE FROM BUS 325015 [4SMITH TAP 138.00] TO BUS 324309 [4SMITH 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 1972 325047-325046(1) | OPEN LINE FROM BUS 325047 [5ASHWOOD 161.00] TO BUS 325046 [1ASHWOOD COL34.500] CKT 1 | -31.4812 | 31.4812 | 33 | 95.3977 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 1973 325073-340651(1) | OPEN LINE FROM BUS 325073 [7REDMON RD 345.00] TO BUS 340651 [OTTERCRK345 345.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 1976 325116-325117(1) | OPEN LINE FROM BUS 325116 [4RHUDES CR 138.00] TO BUS 325117 [1RHUDES COL 34.500] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 1979 326569-248830(1) | OPEN LINE FROM BUS 326569 [7KENZIG ROAD345.00] TO BUS 248830 [07RAMSY5 345.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 1980 326569-249520(1) | OPEN LINE FROM BUS 326569 [7KENZIG ROAD345.00] TO BUS 249520 [08SPEED 345.00] CKT 1 | -31.4814 | 31.4815 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 1981 326596-324697(1) | OPEN LINE FROM BUS 326596 [2PAD PRI 61469.000] TO BUS 324697 [1KMPA PAD2 13.800] CKT 1 | -31.4813 | 31.4813 | 33 | 95.398 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 1982 326596-324933(1) | OPEN LINE FROM BUS 326596 [2PAD PRI 61469.000] TO BUS 324933 [1KMPA PAD1 13.800] CKT 1 | -31.4813 | 31.4813 | 33 | 95.398 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 1985 326998-361788(1) | OPEN LINE FROM BUS 326998 [5BULLITT TAP161.00] TO BUS 361788 [5SUM SHAD TP161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | MERE SWS | MERE SWS | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-69-51 | B-69-51 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-69-446 | B-69-446 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-69-65 | B-69-65 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-69-63 | B-69-63 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-69-66 | B-69-66 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-69-53 | B-69-53 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-69-36 | B-69-36 | -31.4831 | 31.4831 | 33 | 95.4033 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-69-49 | B-69-49 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-69-37 | B-69-37 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-69-11 | B-69-11 | -31.4816 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-69-50 | B-69-50 | -31.4816 | 31.4816 | 33 | 95.3988 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-69-316A | B-69-316A | -31.4815 | 31.4815 | 33 | 95.3983 | LGEE
342000 | 5GAS | 161 | 342760 | 5LIBERTY J | 161 | 1 | SINGLE OPN LIN 801 324112-325074(1) | OPEN LINE FROM BUS 324112 [7PINEVILLE 345.00] TO BUS 325074 [7W GARRARDKU345.00] CKT 1 | 146.0939 | 146.0939 | 153 | 95.4862 | EKPC
342000 | 5GAS | 161 | 342760 | 5LIBERTY J | 161 | 1 | SINGLE OPN LIN 473 342268-342478(1) | OPEN LINE FROM BUS 342268 [2SLAT 69.000] TO BUS 342478 [2WAYNE CO 69.000] CKT 1 | 146.0729 | 146.0729 | 153 | 95.4725 | EKPC
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-69-9 | B-69-9 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SW-1000 | SW-1000 | -31.4821 | 31.4821 | 33 | 95.4002 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-69-47 | B-69-47 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-69-48 | B-69-48 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-69-52 | B-69-52 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-69-56 | B-69-56 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-69-57 | B-69-57 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-69-58 | B-69-58 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-69-60 | B-69-60 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-69-61 | B-69-61 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-69-62 | B-69-62 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-69-318 | B-69-318 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-69-319 | B-69-319 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-69-67 | B-69-67 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-69-693 | B-69-693 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-69-69 | B-69-69 | -31.4812 | 31.4812 | 33 | 95.3977 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-69-72 | B-69-72 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-69-74 | B-69-74 | -31.4817 | 31.4817 | 33 | 95.3991 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-69-76 | B-69-76 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-69-77 | B-69-77 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-69-73 | B-69-73 | -31.4817 | 31.4817 | 33 | 95.399 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-69-10 | B-69-10 | -31.4812 | 31.4812 | 33 | 95.3977 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-345-449 | B-345-449 | -31.4816 | 31.4816 | 33 | 95.3988 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-138-123 | B-138-123 | -31.482 | 31.482 | 33 | 95.4 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-69-322 | B-69-322 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-69-324 | B-69-324 | -31.4811 | 31.4811 | 33 | 95.3974 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-69-79 | B-69-79 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-69-80 | B-69-80 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-69-325 | B-69-325 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-69-327 | B-69-327 | -31.4817 | 31.4817 | 33 | 95.399 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-138-115 | B-138-115 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-69-448 | B-69-448 | -31.4816 | 31.4816 | 33 | 95.3989 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-161-131 | B-161-131 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-69-334 | B-69-334 | -31.4808 | 31.4808 | 33 | 95.3963 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-69-335 | B-69-335 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-138-447 | B-138-447 | -31.4815 | 31.4815 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-69-330 | B-69-330 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-69-332 | B-69-332 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-69-337 | B-69-337 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324941 | 2RIVERPORT | 69 | 324975 | 2TERRY | 69 | 1 | SINGLE OPN LIN 1790 324997-324998(1) | OPEN LINE FROM BUS 324997 [2WEST CO 1 69.000] TO BUS 324998 [2WEST CO 2 69.000] CKT 1 | 60.07 | 60.07 | 63 | 95.3491 | LGEE
324237 | 4CANE RUN SW | 138 | 326565 | 4INTRNTL TAP | 138 | 23 | SINGLE OPN LIN 971 324237-325096(25) | OPEN LINE FROM BUS 324237 [4CANE RUN SW138.00] TO BUS 325096 [4CANERN NGCC138.00] CKT 25 | -198.3008 | 198.3008 | 208 | 95.3369 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-69-338 | B-69-338 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-69-450 | B-69-450 | -31.4813 | 31.4813 | 33 | 95.398 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-500-97 | B-500-97 | -31.4817 | 31.4817 | 33 | 95.3992 | LGEE
342000 | 5GAS | 161 | 342760 | 5LIBERTY J | 161 | 1 | SINGLE OPN LIN 501 342430-342433(1) | OPEN LINE FROM BUS 342430 [2W BEREA 69.000] TO BUS 342433 [2W BEREA J 69.000] CKT 1 | 145.8425 | 145.8425 | 153 | 95.3219 | EKPC
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-69-339 | B-69-339 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-69-340 | B-69-340 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-2000 | BB-2000 | -31.4821 | 31.4821 | 33 | 95.4003 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1366 | BB-1366 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1452 | BB-1452 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1386 | BB-1386 | -31.4816 | 31.4816 | 33 | 95.3988 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1456 | BB-1456 | -31.4813 | 31.4813 | 33 | 95.398 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1280 | BB-1280 | -31.4806 | 31.4806 | 33 | 95.3957 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1479 | BB-1479 | -31.4818 | 31.4818 | 33 | 95.3993 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1317 | BB-1317 | -31.4811 | 31.4811 | 33 | 95.3973 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1225 | BB-1225 | -31.4816 | 31.4816 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1373 | BB-1373 | -31.484 | 31.484 | 33 | 95.4059 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1073 | BB-1073 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1493 | BB-1493 | -31.4801 | 31.4801 | 33 | 95.3941 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1494 | BB-1494 | -31.4806 | 31.4806 | 33 | 95.3957 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1495 | BB-1495 | -31.4804 | 31.4804 | 33 | 95.3952 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1318 | BB-1318 | -31.4807 | 31.4807 | 33 | 95.396 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1352 | BB-1352 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1405 | BB-1405 | -31.4808 | 31.4808 | 33 | 95.3963 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1301 | BB-1301 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1387 | BB-1387 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1443 | BB-1443 | -31.4813 | 31.4813 | 33 | 95.398 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1335 | BB-1335 | -31.4816 | 31.4816 | 33 | 95.3988 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1298 | BB-1298 | -31.4806 | 31.4806 | 33 | 95.3958 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1369 | BB-1369 | -31.4813 | 31.4813 | 33 | 95.3979 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1297 | BB-1297 | -31.4804 | 31.4804 | 33 | 95.3953 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1288 | BB-1288 | -31.4809 | 31.4809 | 33 | 95.3968 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1468 | BB-1468 | -31.481 | 31.481 | 33 | 95.3971 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1315 | BB-1315 | -31.4806 | 31.4806 | 33 | 95.3956 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1482 | BB-1482 | -31.4809 | 31.4809 | 33 | 95.3966 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1368 | BB-1368 | -31.4823 | 31.4823 | 33 | 95.401 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1312 | BB-1312 | -31.4812 | 31.4812 | 33 | 95.3975 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1313 | BB-1313 | -31.481 | 31.481 | 33 | 95.397 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1319 | BB-1319 | -31.4828 | 31.4828 | 33 | 95.4025 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1323 | BB-1323 | -31.4816 | 31.4816 | 33 | 95.3989 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1325 | BB-1325 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1407 | BB-1407 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1356 | BB-1356 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1316 | BB-1316 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1370 | BB-1370 | -31.4817 | 31.4817 | 33 | 95.399 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1349 | BB-1349 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1320 | BB-1320 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1434 | BB-1434 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1285 | BB-1285 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1401 | BB-1401 | -31.4816 | 31.4816 | 33 | 95.3988 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | MORG-WHT-NEB | MORG-WHT-NEB | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1302 | BB-1302 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1400 | BB-1400 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1344 | BB-1344 | -31.4816 | 31.4816 | 33 | 95.3988 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1473 | BB-1473 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1420 | BB-1420 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1306 | BB-1306 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1307 | BB-1307 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1415 | BB-1415 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1342 | BB-1342 | -31.4816 | 31.4816 | 33 | 95.3988 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1287 | BB-1287 | -31.4816 | 31.4816 | 33 | 95.3988 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1491 | BB-1491 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1303 | BB-1303 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1374 | BB-1374 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1367 | BB-1367 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1339 | BB-1339 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1308 | BB-1308 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1338 | BB-1338 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1404 | BB-1404 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1442 | BB-1442 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1513 | BB-1513 | -31.4813 | 31.4813 | 33 | 95.398 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1408 | BB-1408 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1286 | BB-1286 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1365 | BB-1365 | -31.4816 | 31.4816 | 33 | 95.3989 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1486 | BB-1486 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1322 | BB-1322 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1379 | BB-1379 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1391 | BB-1391 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1403 | BB-1403 | -31.4816 | 31.4816 | 33 | 95.3988 | LGEE
342000 | 5GAS | 161 | 342760 | 5LIBERTY J | 161 | 1 | SINGLE OPN LIN 489 342349-342433(1) | OPEN LINE FROM BUS 342349 [2THREE LNK J69.000] TO BUS 342433 [2W BEREA J 69.000] CKT 1 | 145.8373 | 145.8373 | 153 | 95.3185 | EKPC
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1390 | BB-1390 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1425 | BB-1425 | -31.4816 | 31.4816 | 33 | 95.3989 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1436 | BB-1436 | -31.4816 | 31.4816 | 33 | 95.3989 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1321 | BB-1321 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1343 | BB-1343 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1300 | BB-1300 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1294 | BB-1294 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1327 | BB-1327 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1336 | BB-1336 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1446 | BB-1446 | -31.4812 | 31.4812 | 33 | 95.3975 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1514 | BB-1514 | -31.4813 | 31.4813 | 33 | 95.3978 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1345 | BB-1345 | -31.4817 | 31.4817 | 33 | 95.3992 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1361 | BB-1361 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-3000 | BB-3000 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1337 | BB-1337 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1432 | BB-1432 | -31.4815 | 31.4815 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1461 | BB-1461 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1353 | BB-1353 | -31.4816 | 31.4816 | 33 | 95.3989 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1457 | BB-1457 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-69-41 | B-69-41 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1299 | BB-1299 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1428 | BB-1428 | -31.4816 | 31.4816 | 33 | 95.3989 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1428A | BB-1428A | -31.4816 | 31.4816 | 33 | 95.3989 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-69-40 | B-69-40 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1464 | BB-1464 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1410 | BB-1410 | -31.4817 | 31.4817 | 33 | 95.399 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1326 | BB-1326 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1406 | BB-1406 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-69-42 | B-69-42 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1399 | BB-1399 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1346 | BB-1346 | -31.4813 | 31.4813 | 33 | 95.398 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-69-78 | B-69-78 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1332 | BB-1332 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1402 | BB-1402 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
342000 | 5GAS | 161 | 342760 | 5LIBERTY J | 161 | 1 | EKPC_P1-2_W BER-THRLJ 69 | EKPC_P1-2_W BER-THRLJ 69 | 145.8372 | 145.8372 | 153 | 95.3184 | EKPC
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1398 | BB-1398 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1453 | BB-1453 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1274 | BB-1274 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1277 | BB-1277 | -31.4816 | 31.4816 | 33 | 95.3988 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1289 | BB-1289 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1328 | BB-1328 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1272 | BB-1272 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324285 | 4MUD LANE | 138 | 324651 | 2MUD LANE | 69 | 1 | SINGLE OPN LIN 1633 324740-325024(1) | OPEN LINE FROM BUS 324740 [2SOUTH PARK 69.000] TO BUS 325024 [2ASHBOT SPRK69.000] CKT 1 | 131.512 | 131.512 | 138 | 95.2986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-69-45 | B-69-45 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1512 | BB-1512 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1470 | BB-1470 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1430 | BB-1430 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1450 | BB-1450 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1424 | BB-1424 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1393 | BB-1393 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1392 | BB-1392 | -31.4816 | 31.4816 | 33 | 95.3988 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1375 | BB-1375 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-69-136 | B-69-136 | -31.4816 | 31.4816 | 33 | 95.3989 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-69-137 | B-69-137 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-69-140 | B-69-140 | -31.4813 | 31.4813 | 33 | 95.398 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-69-141 | B-69-141 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1364 | BB-1364 | -31.4817 | 31.4817 | 33 | 95.3991 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1355 | BB-1355 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1354 | BB-1354 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1270 | BB-1270 | -31.4813 | 31.4813 | 33 | 95.3978 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1271 | BB-1271 | -31.4813 | 31.4813 | 33 | 95.3978 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1275 | BB-1275 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | PRIN-KYD-PAD | PRIN-KYD-PAD | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-69-46 | B-69-46 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | P1-1000 | P1-1000 | -31.4819 | 31.4819 | 33 | 95.3996 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | P1-1001 | P1-1001 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-69-25 | B-69-25 | -31.4812 | 31.4812 | 33 | 95.3975 | LGEE
341281 | 2CEDAR GR | 69 | 342082 | 2PLEAS GRV | 69 | 1 | B-69-316A | B-69-316A | 43.8274 | 43.8274 | 46 | 95.2769 | EKPC
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1164 | BB-1164 | -31.4816 | 31.4816 | 33 | 95.3989 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1097 | BB-1097 | -31.4817 | 31.4817 | 33 | 95.399 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-138-114 | B-138-114 | -31.4816 | 31.4816 | 33 | 95.3988 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-138-119 | B-138-119 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-138-113 | B-138-113 | -31.4816 | 31.4816 | 33 | 95.3988 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-138-118 | B-138-118 | -31.4809 | 31.4809 | 33 | 95.3967 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1179 | BB-1179 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1192 | BB-1192 | -31.4816 | 31.4816 | 33 | 95.3989 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1201 | BB-1201 | -31.4816 | 31.4816 | 33 | 95.3988 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1203 | BB-1203 | -31.482 | 31.482 | 33 | 95.4 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1240 | BB-1240 | -31.4817 | 31.4817 | 33 | 95.399 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-138-122 | B-138-122 | -31.4824 | 31.4824 | 33 | 95.4012 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1143 | BB-1143 | -31.4822 | 31.4822 | 33 | 95.4007 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1049 | BB-1049 | -31.4817 | 31.4817 | 33 | 95.3991 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-138-111 | B-138-111 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-161-125 | B-161-125 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-138-21 | B-138-21 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1133 | BB-1133 | -31.4816 | 31.4816 | 33 | 95.3989 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-161-126 | B-161-126 | -31.4813 | 31.4813 | 33 | 95.3979 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1063 | BB-1063 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-161-24 | B-161-24 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-161-23 | B-161-23 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-161-124 | B-161-124 | -31.4812 | 31.4812 | 33 | 95.3977 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1509 | BB-1509 | -31.4812 | 31.4812 | 33 | 95.3974 | LGEE
342000 | 5GAS | 161 | 342760 | 5LIBERTY J | 161 | 1 | SINGLE OPN LIN 1541 324641-324829(1) | OPEN LINE FROM BUS 324641 [2MILE LAN TP69.000] TO BUS 324829 [2CAMPBELVIL169.000] CKT 1 | 145.6459 | 145.6459 | 153 | 95.1934 | EKPC
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-138-112 | B-138-112 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1239 | BB-1239 | -31.4819 | 31.4819 | 33 | 95.3998 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1216 | BB-1216 | -31.4818 | 31.4818 | 33 | 95.3993 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1019 | BB-1019 | -31.4822 | 31.4822 | 33 | 95.4006 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-138-97 | B-138-97 | -31.4819 | 31.4819 | 33 | 95.3998 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-161-108 | B-161-108 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1057 | BB-1057 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-161-106 | B-161-106 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-161-128 | B-161-128 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324536 | 2FINCHVILLE | 69 | 324718 | 2SHELBY CO T | 69 | 1 | SINGLE OPN LIN 1364 324510-324729(1) | OPEN LINE FROM BUS 324510 [2EASTWOOD 69.000] TO BUS 324729 [2SIMPSONVILL69.000] CKT 1 | 50.4375 | 50.4375 | 53 | 95.1652 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-69-18 | B-69-18 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324536 | 2FINCHVILLE | 69 | 324718 | 2SHELBY CO T | 69 | 1 | SINGLE OPN LIN 1167 324400-324510(1) | OPEN LINE FROM BUS 324400 [2WHAS TAP 69.000] TO BUS 324510 [2EASTWOOD 69.000] CKT 1 | 50.4305 | 50.4305 | 53 | 95.152 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-69-19 | B-69-19 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-138-28 | B-138-28 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1228 | BB-1228 | -31.4817 | 31.4817 | 33 | 95.3991 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1229 | BB-1229 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1066 | BB-1066 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1026 | BB-1026 | -31.4813 | 31.4813 | 33 | 95.398 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-345-475 | B-345-475 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1139 | BB-1139 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-138-130 | B-138-130 | -31.4816 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-138-12 | B-138-12 | -31.4915 | 31.4915 | 33 | 95.4287 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-69-13 | B-69-13 | -31.4818 | 31.4818 | 33 | 95.3994 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-69-15 | B-69-15 | -31.4818 | 31.4818 | 33 | 95.3995 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-69-20 | B-69-20 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-69-26 | B-69-26 | -31.4813 | 31.4813 | 33 | 95.3978 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-69-29 | B-69-29 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-69-30 | B-69-30 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-69-31 | B-69-31 | -31.4817 | 31.4817 | 33 | 95.399 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1205 | BB-1205 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1187 | BB-1187 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1136 | BB-1136 | -31.4815 | 31.4815 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1112 | BB-1112 | -31.4816 | 31.4816 | 33 | 95.3988 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1098 | BB-1098 | -31.4816 | 31.4816 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1075 | BB-1075 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1062 | BB-1062 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1060 | BB-1060 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1061 | BB-1061 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-69-135 | B-69-135 | -31.4813 | 31.4813 | 33 | 95.398 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-69-132 | B-69-132 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-138-120 | B-138-120 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-138-121 | B-138-121 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-138-109 | B-138-109 | -31.4813 | 31.4813 | 33 | 95.398 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1226 | BB-1226 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1001 | BB-1001 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-345-100 | B-345-100 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
342000 | 5GAS | 161 | 342760 | 5LIBERTY J | 161 | 1 | SINGLE OPN TIE 704 342823-360486(1) | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 145.3873 | 145.3873 | 153 | 95.0244 | EKPC
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-161-107 | B-161-107 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-138-110 | B-138-110 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-138-117 | B-138-117 | -31.4816 | 31.4816 | 33 | 95.3988 | LGEE
342000 | 5GAS | 161 | 342760 | 5LIBERTY J | 161 | 1 | SINGLE OPN LIN 510 342478-342823(1) | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 145.3865 | 145.3865 | 153 | 95.0238 | EKPC
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-161-84 | B-161-84 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-138-116 | B-138-116 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-345-101 | B-345-101 | -31.4813 | 31.4813 | 33 | 95.3979 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-345-102 | B-345-102 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
342000 | 5GAS | 161 | 342760 | 5LIBERTY J | 161 | 1 | EKPC_P1-2_MCCR-WAYNE161 | EKPC_P1-2_MCCR-WAYNE161 | 145.3687 | 145.3687 | 153 | 95.0122 | EKPC
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-69-133 | B-69-133 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1074 | BB-1074 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1132 | BB-1132 | -31.4826 | 31.4826 | 33 | 95.4017 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1218 | BB-1218 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-2021 | BB-2021 | -31.4813 | 31.4813 | 33 | 95.3978 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | BB-1245B | BB-1245B | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-69-35 | B-69-35 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-69-32 | B-69-32 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | B-69-33 | B-69-33 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | P1-1002 | P1-1002 | -31.4854 | 31.4854 | 33 | 95.4102 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | P1-2-1004 | P1-2-1004 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | P1-2-1005 | P1-2-1005 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1986 242691-243088(1) | OPEN LINE FROM BUS 242691 [05KENOVA 138.00] TO BUS 243088 [05S.POINT1 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1987 242927-242938(1) | OPEN LINE FROM BUS 242927 [05MARQUI 765.00] TO BUS 242938 [05MARQUI 345.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1988 242938-243034(2) | OPEN LINE FROM BUS 242938 [05MARQUI 345.00] TO BUS 243034 [05MARQUI 138.00] CKT 2 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1989 242938-243034(3) | OPEN LINE FROM BUS 242938 [05MARQUI 345.00] TO BUS 243034 [05MARQUI 138.00] CKT 3 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1990 242938-246888(1) | OPEN LINE FROM BUS 242938 [05MARQUI 345.00] TO BUS 246888 [05BIERSR 345.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1991 242982-243047(1) | OPEN LINE FROM BUS 242982 [05CENPOR 138.00] TO BUS 243047 [05N PORT 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1992 242988-242992(1) | OPEN LINE FROM BUS 242988 [05DOGWOO 138.00] TO BUS 242992 [05E WHEE 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1993 242988-243042(1) | OPEN LINE FROM BUS 242988 [05DOGWOO 138.00] TO BUS 243042 [05MILLBR PK1138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1994 243013-243069(1) | OPEN LINE FROM BUS 243013 [05GAVIN1 138.00] TO BUS 243069 [05FIREBR 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1995 243019-243102(1) | OPEN LINE FROM BUS 243019 [05HILLSB 138.00] TO BUS 243102 [05SINK SP8SS138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1996 243042-243047(1) | OPEN LINE FROM BUS 243042 [05MILLBR PK1138.00] TO BUS 243047 [05N PORT 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1997 243042-243069(1) | OPEN LINE FROM BUS 243042 [05MILLBR PK1138.00] TO BUS 243069 [05FIREBR 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1998 243042-243173(5) | OPEN LINE FROM BUS 243042 [05MILLBR PK1138.00] TO BUS 243173 [05MILLBRK 69.000] CKT 5 | -31.4815 | 31.4815 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 1999 243047-243087(1) | OPEN LINE FROM BUS 243047 [05N PORT 138.00] TO BUS 243087 [05S LUCA 138.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2000 243047-243819(1) | OPEN LINE FROM BUS 243047 [05N PORT 138.00] TO BUS 243819 [05N PORTSM 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2001 243069-246782(1) | OPEN LINE FROM BUS 243069 [05FIREBR 138.00] TO BUS 246782 [05FIREBRCK 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2002 243088-243184(2) | OPEN LINE FROM BUS 243088 [05S.POINT1 138.00] TO BUS 243184 [05S POINT 34.500] CKT 2 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2003 243167-243171(1) | OPEN LINE FROM BUS 243167 [05FRANKLIN 69.000] TO BUS 243171 [05HAYPRTRDSS69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3979 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2004 243167-243178(1) | OPEN LINE FROM BUS 243167 [05FRANKLIN 69.000] TO BUS 243178 [05GINAT C SS69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2005 243167-243725(1) | OPEN LINE FROM BUS 243167 [05FRANKLIN 69.000] TO BUS 243725 [05GRAYSB 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2006 243171-243183(1) | OPEN LINE FROM BUS 243171 [05HAYPRTRDSS69.000] TO BUS 243183 [05WHEELRBR 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2007 243173-243181(1) | OPEN LINE FROM BUS 243173 [05MILLBRK 69.000] TO BUS 243181 [05SCIOTOVI 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2008 243173-243597(1) | OPEN LINE FROM BUS 243173 [05MILLBRK 69.000] TO BUS 243597 [05ASHLEY 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2009 243173-246916(1) | OPEN LINE FROM BUS 243173 [05MILLBRK 69.000] TO BUS 246916 [05CORNRSTN 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2010 243173-246917(1) | OPEN LINE FROM BUS 243173 [05MILLBRK 69.000] TO BUS 246917 [05RUHLMAN 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2011 243176-243178(1) | OPEN LINE FROM BUS 243176 [05N HAVERH 69.000] TO BUS 243178 [05GINAT C SS69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2012 243178-247476(1) | OPEN LINE FROM BUS 243178 [05GINAT C SS69.000] TO BUS 247476 [05PLYMOUTHHT69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2013 243181-243183(1) | OPEN LINE FROM BUS 243181 [05SCIOTOVI 69.000] TO BUS 243183 [05WHEELRBR 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2014 243618-247072(1) | OPEN LINE FROM BUS 243618 [05STUART 69.000] TO BUS 247072 [05RAVNSS 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2015 243656-243808(1) | OPEN LINE FROM BUS 243656 [05BEAVC1EQ 999.00] TO BUS 243808 [05BEAVERCR 46.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2016 243657-243808(1) | OPEN LINE FROM BUS 243657 [05BEAVC2EQ 999.00] TO BUS 243808 [05BEAVERCR 46.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2017 243663-243702(1) | OPEN LINE FROM BUS 243663 [05THELMAEQ 999.00] TO BUS 243702 [05THELMA 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2018 243663-243750(1) | OPEN LINE FROM BUS 243663 [05THELMAEQ 999.00] TO BUS 243750 [05THELM1 69.000] CKT 1 | -31.481 | 31.481 | 33 | 95.397 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2020 243678-243679(1) | OPEN LINE FROM BUS 243678 [05BSANDX 138.00] TO BUS 243679 [05BUSSYV 138.00] CKT 1 | -31.4817 | 31.4817 | 33 | 95.3991 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2021 243679-243702(1) | OPEN LINE FROM BUS 243679 [05BUSSYV 138.00] TO BUS 243702 [05THELMA 138.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2022 243684-243702(1) | OPEN LINE FROM BUS 243684 [05DEWEY 138.00] TO BUS 243702 [05THELMA 138.00] CKT 1 | -31.4808 | 31.4808 | 33 | 95.3962 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2023 243684-243804(1) | OPEN LINE FROM BUS 243684 [05DEWEY 138.00] TO BUS 243804 [05DEWEY 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2024 243684-244008(1) | OPEN LINE FROM BUS 243684 [05DEWEY 138.00] TO BUS 244008 [05STANVILLE1138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2025 243688-244686(Z1) | OPEN LINE FROM BUS 243688 [05S.PORT MTR138.00] TO BUS 244686 [05VANCEBURG 138.00] CKT Z1 | -31.4815 | 31.4815 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2026 243702-246971(1) | OPEN LINE FROM BUS 243702 [05THELMA 138.00] TO BUS 246971 [05THELM2 69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.398 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2027 243712-243716(1) | OPEN LINE FROM BUS 243712 [05CANNONSB 69.000] TO BUS 243716 [05COALTON 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2028 243714-243727(1) | OPEN LINE FROM BUS 243714 [05CHAVIES 69.000] TO BUS 243727 [05HADDIX 69.000] CKT 1 | -31.4823 | 31.4823 | 33 | 95.4009 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2029 243716-243732(1) | OPEN LINE FROM BUS 243716 [05COALTON 69.000] TO BUS 243732 [05HITCHI 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2030 243716-243743(1) | OPEN LINE FROM BUS 243716 [05COALTON 69.000] TO BUS 243743 [05PRINCESS 69.000] CKT 1 | -31.481 | 31.481 | 33 | 95.397 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2031 243724-243737(1) | OPEN LINE FROM BUS 243724 [05GRAHN 69.000] TO BUS 243737 [05LEONKY 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2032 243724-243742(1) | OPEN LINE FROM BUS 243724 [05GRAHN 69.000] TO BUS 243742 [05CORYSS 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2033 243727-243734(1) | OPEN LINE FROM BUS 243727 [05HADDIX 69.000] TO BUS 243734 [05JACKSON 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2034 243728-243740(1) | OPEN LINE FROM BUS 243728 [05HAYWAR 69.000] TO BUS 243740 [05MOREHE 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2035 243728-243741(1) | OPEN LINE FROM BUS 243728 [05HAYWAR 69.000] TO BUS 243741 [05OLIVEHIL 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2036 243732-243737(1) | OPEN LINE FROM BUS 243732 [05HITCHI 69.000] TO BUS 243737 [05LEONKY 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2037 243733-243812(1) | OPEN LINE FROM BUS 243733 [05INDEX 69.000] TO BUS 243812 [05LEE C 69.000] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2039 243734-243812(1) | OPEN LINE FROM BUS 243734 [05JACKSON 69.000] TO BUS 243812 [05LEE C 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2041 243741-243742(1) | OPEN LINE FROM BUS 243741 [05OLIVEHIL 69.000] TO BUS 243742 [05CORYSS 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2042 243750-244632(1) | OPEN LINE FROM BUS 243750 [05THELM1 69.000] TO BUS 244632 [05W.PNTSVL 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2043 243758-243759(1) | OPEN LINE FROM BUS 243758 [05MIDDLECR 46.000] TO BUS 243759 [05PRESTNSB 46.000] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3988 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2044 243808-244592(1) | OPEN LINE FROM BUS 243808 [05BEAVERCR 46.000] TO BUS 244592 [05BURTON 46.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2045 243808-244616(1) | OPEN LINE FROM BUS 243808 [05BEAVERCR 46.000] TO BUS 244616 [05MCKINNEY 46.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.398 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2046 244632-246970(1) | OPEN LINE FROM BUS 244632 [05W.PNTSVL 69.000] TO BUS 246970 [05MAYOTRL 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2047 246970-246971(1) | OPEN LINE FROM BUS 246970 [05MAYOTRL 69.000] TO BUS 246971 [05THELM2 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2048 242691-242835(1) | OPEN LINE FROM BUS 242691 [05KENOVA 138.00] TO BUS 242835 [05TRISTA 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2049 242691-244720(1) | OPEN LINE FROM BUS 242691 [05KENOVA 138.00] TO BUS 244720 [05KENOVA H 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2050 242918-244965(EQ) | OPEN LINE FROM BUS 242918 [05SPOIN4EQ 999.00] TO BUS 244965 [05S POINT 69.000] CKT EQ | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2051 242918-245615(4) | OPEN LINE FROM BUS 242918 [05SPOIN4EQ 999.00] TO BUS 245615 [05S.POINT2 138.00] CKT 4 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2052 242927-242924(1) | OPEN LINE FROM BUS 242927 [05MARQUI 765.00] TO BUS 242924 [05HANG R 765.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2053 242938-248005(1) | OPEN LINE FROM BUS 242938 [05MARQUI 345.00] TO BUS 248005 [06KYGER 345.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2054 242938-248005(2) | OPEN LINE FROM BUS 242938 [05MARQUI 345.00] TO BUS 248005 [06KYGER 345.00] CKT 2 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2055 242938-248013(1) | OPEN LINE FROM BUS 242938 [05MARQUI 345.00] TO BUS 248013 [06PIERCE 345.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2056 242938-253077(1) | OPEN LINE FROM BUS 242938 [05MARQUI 345.00] TO BUS 253077 [09STUART 345.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2057 242982-243815(2) | OPEN LINE FROM BUS 242982 [05CENPOR 138.00] TO BUS 243815 [05CENPORTS 69.000] CKT 2 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2058 242992-243124(1) | OPEN LINE FROM BUS 242992 [05E WHEE 138.00] TO BUS 243124 [05TEXEAS 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2059 242992-243968(1) | OPEN LINE FROM BUS 242992 [05E WHEE 138.00] TO BUS 243968 [05IRONWOODSS138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2060 243013-242698(1) | OPEN LINE FROM BUS 243013 [05GAVIN1 138.00] TO BUS 242698 [05LAKIN 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2061 243013-242807(1) | OPEN LINE FROM BUS 243013 [05GAVIN1 138.00] TO BUS 242807 [05SPORN 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2062 243013-243611(1) | OPEN LINE FROM BUS 243013 [05GAVIN1 138.00] TO BUS 243611 [05CARTWRT SS138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2063 243013-243766(ZC) | OPEN LINE FROM BUS 243013 [05GAVIN1 138.00] TO BUS 243766 [05LIGHTSTONL138.00] CKT ZC | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2064 243013-243766(ZD) | OPEN LINE FROM BUS 243013 [05GAVIN1 138.00] TO BUS 243766 [05LIGHTSTONL138.00] CKT ZD | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2065 243013-244949(1) | OPEN LINE FROM BUS 243013 [05GAVIN1 138.00] TO BUS 244949 [05GAVIN 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2066 243013-244949(2) | OPEN LINE FROM BUS 243013 [05GAVIN1 138.00] TO BUS 244949 [05GAVIN 69.000] CKT 2 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2067 243013-246324(Z1) | OPEN LINE FROM BUS 243013 [05GAVIN1 138.00] TO BUS 246324 [05GAVIN_CAP 138.00] CKT Z1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2068 243019-242787(1) | OPEN LINE FROM BUS 243019 [05HILLSB 138.00] TO BUS 242787 [05MIDDLEB SS138.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2069 243019-246911(1) | OPEN LINE FROM BUS 243019 [05HILLSB 138.00] TO BUS 246911 [05HIGHLA 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2070 243019-246946(1) | OPEN LINE FROM BUS 243019 [05HILLSB 138.00] TO BUS 246946 [05WLDCAT 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2071 243019-249995(1) | OPEN LINE FROM BUS 243019 [05HILLSB 138.00] TO BUS 249995 [08CLINCO 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2072 243034-243501(1) | OPEN LINE FROM BUS 243034 [05MARQUI 138.00] TO BUS 243501 [05E.BEAV 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2073 243034-243544(2) | OPEN LINE FROM BUS 243034 [05MARQUI 138.00] TO BUS 243544 [05MILPRD 138.00] CKT 2 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2074 243034-245632(1) | OPEN LINE FROM BUS 243034 [05MARQUI 138.00] TO BUS 245632 [05ARBOLES 138.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2075 243042-245948(Z1) | OPEN LINE FROM BUS 243042 [05MILLBR PK1138.00] TO BUS 245948 [05MILLBR PK2138.00] CKT Z1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2076 243042-245949(Z1) | OPEN LINE FROM BUS 243042 [05MILLBR PK1138.00] TO BUS 245949 [05MLBRPK_ARG138.00] CKT Z1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2077 243064-242929(2) | OPEN LINE FROM BUS 243064 [05NPROCT 138.00] TO BUS 242929 [05NPROCT 765.00] CKT 2 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2078 243064-242999(1) | OPEN LINE FROM BUS 243064 [05NPROCT 138.00] TO BUS 242999 [05EPROCT 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2079 243064-243193(1) | OPEN LINE FROM BUS 243064 [05NPROCT 138.00] TO BUS 243193 [05VIKING SS 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2080 243064-243675(1) | OPEN LINE FROM BUS 243064 [05NPROCT 138.00] TO BUS 243675 [05BELLF1 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2081 243064-245615(1) | OPEN LINE FROM BUS 243064 [05NPROCT 138.00] TO BUS 245615 [05S.POINT2 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2082 243064-245664(1) | OPEN LINE FROM BUS 243064 [05NPROCT 138.00] TO BUS 245664 [05E.HUNTING1138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2083 243064-290186(2) | OPEN LINE FROM BUS 243064 [05NPROCT 138.00] TO BUS 290186 [05N.CHESPK 138.00] CKT 2 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2084 243087-243140(1) | OPEN LINE FROM BUS 243087 [05S LUCA 138.00] TO BUS 243140 [05WAKEFL 138.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2085 243088-245615(Z1) | OPEN LINE FROM BUS 243088 [05S.POINT1 138.00] TO BUS 245615 [05S.POINT2 138.00] CKT Z1 | -31.4815 | 31.4815 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2086 243088-245948(1) | OPEN LINE FROM BUS 243088 [05S.POINT1 138.00] TO BUS 245948 [05MILLBR PK2138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2087 243102-244942(Z1) | OPEN LINE FROM BUS 243102 [05SINK SP8SS138.00] TO BUS 244942 [05SINK SP8 138.00] CKT Z1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2088 243102-245948(1) | OPEN LINE FROM BUS 243102 [05SINK SP8SS138.00] TO BUS 245948 [05MILLBR PK2138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2089 243171-290138(1) | OPEN LINE FROM BUS 243171 [05HAYPRTRDSS69.000] TO BUS 290138 [05KOT COAL 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2090 243173-246850(1) | OPEN LINE FROM BUS 243173 [05MILLBRK 69.000] TO BUS 246850 [05TYGART 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2091 243176-243164(1) | OPEN LINE FROM BUS 243176 [05N HAVERH 69.000] TO BUS 243164 [05DCHEMTAP 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2092 243176-243827(1) | OPEN LINE FROM BUS 243176 [05N HAVERH 69.000] TO BUS 243827 [05SUNCOKE 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2093 243176-247033(1) | OPEN LINE FROM BUS 243176 [05N HAVERH 69.000] TO BUS 247033 [05HAVERHSS 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2094 243184-244719(1) | OPEN LINE FROM BUS 243184 [05S POINT 34.500] TO BUS 244719 [05VIRGINIA 34.500] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2095 243184-244968(1) | OPEN LINE FROM BUS 243184 [05S POINT 34.500] TO BUS 244968 [05SPTETHNO 34.500] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2096 243184-244968(2) | OPEN LINE FROM BUS 243184 [05S POINT 34.500] TO BUS 244968 [05SPTETHNO 34.500] CKT 2 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2097 243453-243454(1) | OPEN LINE FROM BUS 243453 [05BEATTY 345.00] TO BUS 243454 [05BIXBY 345.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2098 243453-243469(3) | OPEN LINE FROM BUS 243453 [05BEATTY 345.00] TO BUS 243469 [05BEATTY 138.00] CKT 3 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2099 243453-243469(4) | OPEN LINE FROM BUS 243453 [05BEATTY 345.00] TO BUS 243469 [05BEATTY 138.00] CKT 4 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2100 243453-244022(1) | OPEN LINE FROM BUS 243453 [05BEATTY 345.00] TO BUS 244022 [05COLE 345.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2101 243453-245769(1) | OPEN LINE FROM BUS 243453 [05BEATTY 345.00] TO BUS 245769 [05ADKINS 345.00] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2102 243453-253248(1) | OPEN LINE FROM BUS 243453 [05BEATTY 345.00] TO BUS 253248 [09MDISON 345.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2103 243597-246741(1) | OPEN LINE FROM BUS 243597 [05ASHLEY 69.000] TO BUS 246741 [05PEDRO 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2104 243618-253076(1) | OPEN LINE FROM BUS 243618 [05STUART 69.000] TO BUS 253076 [09STUART 138.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2105 243656-243671(1) | OPEN LINE FROM BUS 243656 [05BEAVC1EQ 999.00] TO BUS 243671 [05BEAVER CR1138.00] CKT 1 | -31.4813 | 31.4813 | 33 | 95.398 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2106 243657-243708(1) | OPEN LINE FROM BUS 243657 [05BEAVC2EQ 999.00] TO BUS 243708 [05BEAVERCR 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2107 243657-244688(1) | OPEN LINE FROM BUS 243657 [05BEAVC2EQ 999.00] TO BUS 244688 [05BEAVER CR2138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2108 243678-243669(SR) | OPEN LINE FROM BUS 243678 [05BSANDX 138.00] TO BUS 243669 [05B SAND 138.00] CKT SR | -31.4817 | 31.4817 | 33 | 95.3991 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2109 243688-245949(1) | OPEN LINE FROM BUS 243688 [05S.PORT MTR138.00] TO BUS 245949 [05MLBRPK_ARG138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2111 243712-244727(1) | OPEN LINE FROM BUS 243712 [05CANNONSB 69.000] TO BUS 244727 [05S.NEAL 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2119 243743-244670(1) | OPEN LINE FROM BUS 243743 [05PRINCESS 69.000] TO BUS 244670 [05HOODSCRK 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.398 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2120 243759-243753(1) | OPEN LINE FROM BUS 243759 [05PRESTNSB 46.000] TO BUS 243753 [05ALLEN 46.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2121 243759-243754(1) | OPEN LINE FROM BUS 243759 [05PRESTNSB 46.000] TO BUS 243754 [05EPRESTNS 46.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2122 243759-247415(1) | OPEN LINE FROM BUS 243759 [05PRESTNSB 46.000] TO BUS 247415 [05JENWILEYSS46.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.398 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2123 243804-244575(1) | OPEN LINE FROM BUS 243804 [05DEWEY 69.000] TO BUS 244575 [05PEVLER 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2126 243819-243822(1) | OPEN LINE FROM BUS 243819 [05N PORTSM 69.000] TO BUS 243822 [05ROSEMNT SS69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2127 243819-243826(1) | OPEN LINE FROM BUS 243819 [05N PORTSM 69.000] TO BUS 243826 [05ORTELCRN 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2128 244008-242915(Z1) | OPEN LINE FROM BUS 244008 [05STANVILLE1138.00] TO BUS 242915 [05STANVILLE2138.00] CKT Z1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2129 244592-244599(1) | OPEN LINE FROM BUS 244592 [05BURTON 46.000] TO BUS 244599 [05ELWOOD 46.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2130 244616-244626(1) | OPEN LINE FROM BUS 244616 [05MCKINNEY 46.000] TO BUS 244626 [05SALSBURY 46.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2131 246782-247061(1) | OPEN LINE FROM BUS 246782 [05FIREBRCK 69.000] TO BUS 247061 [05JEFFERSNSS69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2132 246782-247062(1) | OPEN LINE FROM BUS 246782 [05FIREBRCK 69.000] TO BUS 247062 [05BLOOM SS 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2133 246888-243454(1) | OPEN LINE FROM BUS 246888 [05BIERSR 345.00] TO BUS 243454 [05BIXBY 345.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2134 246888-246889(1) | OPEN LINE FROM BUS 246888 [05BIERSR 345.00] TO BUS 246889 [05BIERSR 138.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2135 246916-243815(1) | OPEN LINE FROM BUS 246916 [05CORNRSTN 69.000] TO BUS 243815 [05CENPORTS 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2136 246917-243815(1) | OPEN LINE FROM BUS 246917 [05RUHLMAN 69.000] TO BUS 243815 [05CENPORTS 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2139 247072-246790(1) | OPEN LINE FROM BUS 247072 [05RAVNSS 69.000] TO BUS 246790 [05BROWNHLS 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2140 247072-247073(1) | OPEN LINE FROM BUS 247072 [05RAVNSS 69.000] TO BUS 247073 [05RAVEN 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2141 249564-249991(1) | OPEN LINE FROM BUS 249564 [08BUFTN1 345.00] TO BUS 249991 [08BUFTN1 138.00] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3979 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2142 249564-249991(46) | OPEN LINE FROM BUS 249564 [08BUFTN1 345.00] TO BUS 249991 [08BUFTN1 138.00] CKT 46 | -31.4813 | 31.4813 | 33 | 95.398 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2143 249566-249570(1) | OPEN LINE FROM BUS 249566 [08FOSTER 345.00] TO BUS 249570 [08P.UNON 345.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2144 249566-249578(1) | OPEN LINE FROM BUS 249566 [08FOSTER 345.00] TO BUS 249578 [08HILCRT 345.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2145 249566-249582(1) | OPEN LINE FROM BUS 249566 [08FOSTER 345.00] TO BUS 249582 [08GARVER 345.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2146 249567-249575(1) | OPEN LINE FROM BUS 249567 [08M.FORT 345.00] TO BUS 249575 [08TERMNL 345.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2147 249567-250057(10) | OPEN LINE FROM BUS 249567 [08M.FORT 345.00] TO BUS 250057 [08M.FORT 138.00] CKT 10 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2148 249567-250057(9) | OPEN LINE FROM BUS 249567 [08M.FORT 345.00] TO BUS 250057 [08M.FORT 138.00] CKT 9 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2149 249570-249575(1) | OPEN LINE FROM BUS 249570 [08P.UNON 345.00] TO BUS 249575 [08TERMNL 345.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2150 249570-249577(1) | OPEN LINE FROM BUS 249570 [08P.UNON 345.00] TO BUS 249577 [08ZIMER 345.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2151 249570-250082(1) | OPEN LINE FROM BUS 249570 [08P.UNON 345.00] TO BUS 250082 [08P.UN1 138.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2152 249570-250083(1) | OPEN LINE FROM BUS 249570 [08P.UNON 345.00] TO BUS 250083 [08P.UN2 138.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2153 249571-249573(1) | OPEN LINE FROM BUS 249571 [08REDBK1 345.00] TO BUS 249573 [08SGROVE 345.00] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3979 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2154 249571-249575(1) | OPEN LINE FROM BUS 249571 [08REDBK1 345.00] TO BUS 249575 [08TERMNL 345.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2155 249573-249577(1) | OPEN LINE FROM BUS 249573 [08SGROVE 345.00] TO BUS 249577 [08ZIMER 345.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2156 249573-250097(1) | OPEN LINE FROM BUS 249573 [08SGROVE 345.00] TO BUS 250097 [08SGROVE 138.00] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3979 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2157 249577-249580(Z1) | OPEN LINE FROM BUS 249577 [08ZIMER 345.00] TO BUS 249580 [08ZIMERG 345.00] CKT Z1 | -31.4813 | 31.4813 | 33 | 95.398 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2158 249577-249581(1) | OPEN LINE FROM BUS 249577 [08ZIMER 345.00] TO BUS 249581 [08MELDAL 345.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2159 249578-250136(1) | OPEN LINE FROM BUS 249578 [08HILCRT 345.00] TO BUS 250136 [08HILCRT 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2160 249580-251968(1H) | OPEN LINE FROM BUS 249580 [08ZIMERG 345.00] TO BUS 251968 [08ZIMRHP 26.000] CKT 1H | -31.4813 | 31.4813 | 33 | 95.3979 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2161 249580-251969(1L) | OPEN LINE FROM BUS 249580 [08ZIMERG 345.00] TO BUS 251969 [08ZIMRLP 22.000] CKT 1L | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2162 249581-250145(1) | OPEN LINE FROM BUS 249581 [08MELDAL 345.00] TO BUS 250145 [08MELDAL 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2163 249990-250021(1) | OPEN LINE FROM BUS 249990 [08BROWN 138.00] TO BUS 250021 [08ESTWD2 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2164 249991-250028(1) | OPEN LINE FROM BUS 249991 [08BUFTN1 138.00] TO BUS 250028 [08FLRNC2 138.00] CKT 1 | -31.4811 | 31.4811 | 33 | 95.3973 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2165 249991-250077(1) | OPEN LINE FROM BUS 249991 [08BUFTN1 138.00] TO BUS 250077 [08MTZION 138.00] CKT 1 | -31.4812 | 31.4812 | 33 | 95.3977 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2166 249991-250148(1) | OPEN LINE FROM BUS 249991 [08BUFTN1 138.00] TO BUS 250148 [08EKPWEB 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2167 249991-251279(2) | OPEN LINE FROM BUS 249991 [08BUFTN1 138.00] TO BUS 251279 [08BUFTN2 69.000] CKT 2 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2168 249999-250007(1) | OPEN LINE FROM BUS 249999 [08CNSTNC 138.00] TO BUS 250007 [08CRSNT1 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2169 249999-250044(1) | OPEN LINE FROM BUS 249999 [08CNSTNC 138.00] TO BUS 250044 [08HEBRN2 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2170 250016-250057(1) | OPEN LINE FROM BUS 250016 [08EBNZR 138.00] TO BUS 250057 [08M.FORT 138.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2171 250044-250152(Z1) | OPEN LINE FROM BUS 250044 [08HEBRN2 138.00] TO BUS 250152 [08HEBRNG 138.00] CKT Z1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2172 250045-250151(Z1) | OPEN LINE FROM BUS 250045 [08HEBRN1 138.00] TO BUS 250151 [08HEBTAP 138.00] CKT Z1 | -31.4818 | 31.4818 | 33 | 95.3995 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2173 250054-250077(1) | OPEN LINE FROM BUS 250054 [08LONGBR 138.00] TO BUS 250077 [08MTZION 138.00] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3988 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2174 250057-250058(1) | OPEN LINE FROM BUS 250057 [08M.FORT 138.00] TO BUS 250058 [08M.FTGT 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2175 250057-250060(1) | OPEN LINE FROM BUS 250057 [08M.FORT 138.00] TO BUS 250060 [08MDWAY1 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2176 250057-250070(1) | OPEN LINE FROM BUS 250057 [08M.FORT 138.00] TO BUS 250070 [08MRGAN1 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2177 250057-250131(1) | OPEN LINE FROM BUS 250057 [08M.FORT 138.00] TO BUS 250131 [08WILEY2 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2178 250057-250151(1) | OPEN LINE FROM BUS 250057 [08M.FORT 138.00] TO BUS 250151 [08HEBTAP 138.00] CKT 1 | -31.4809 | 31.4809 | 33 | 95.3968 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2179 250058-251378(1) | OPEN LINE FROM BUS 250058 [08M.FTGT 138.00] TO BUS 251378 [08M.FTGT 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2180 250136-250141(1) | OPEN LINE FROM BUS 250136 [08HILCRT 138.00] TO BUS 250141 [08SCEAST 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2181 250145-250154(1) | OPEN LINE FROM BUS 250145 [08MELDAL 138.00] TO BUS 250154 [08MELDLS 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2182 250151-250152(Z1) | OPEN LINE FROM BUS 250151 [08HEBTAP 138.00] TO BUS 250152 [08HEBRNG 138.00] CKT Z1 | -31.4809 | 31.4809 | 33 | 95.3968 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2183 250154-251970(T1) | OPEN LINE FROM BUS 250154 [08MELDLS 138.00] TO BUS 251970 [08MELDL1 13.800] CKT T1 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2184 250154-251971(T2) | OPEN LINE FROM BUS 250154 [08MELDLS 138.00] TO BUS 251971 [08MELDL2 13.800] CKT T2 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2185 250154-251972(T3) | OPEN LINE FROM BUS 250154 [08MELDLS 138.00] TO BUS 251972 [08MELDL3 13.800] CKT T3 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2186 251276-251469(1) | OPEN LINE FROM BUS 251276 [08BROWER 69.000] TO BUS 251469 [08T28652 69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2187 251291-251301(1) | OPEN LINE FROM BUS 251291 [08CNSTNC 69.000] TO BUS 251301 [08CWW-BN 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2188 251291-251315(1) | OPEN LINE FROM BUS 251291 [08CNSTNC 69.000] TO BUS 251315 [08EKSMTH 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2189 251301-251310(1) | OPEN LINE FROM BUS 251301 [08CWW-BN 69.000] TO BUS 251310 [08DRYCRK 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2190 251314-251315(1) | OPEN LINE FROM BUS 251314 [08EKDOWN 69.000] TO BUS 251315 [08EKSMTH 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2191 251314-251467(1) | OPEN LINE FROM BUS 251314 [08EKDOWN 69.000] TO BUS 251467 [08T15268 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2192 251367-251368(Z1) | OPEN LINE FROM BUS 251367 [08LEVIA 69.000] TO BUS 251368 [08LEVIB 69.000] CKT Z1 | -31.4813 | 31.4813 | 33 | 95.398 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2193 251367-251467(1) | OPEN LINE FROM BUS 251367 [08LEVIA 69.000] TO BUS 251467 [08T15268 69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3979 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2194 251378-251406(1) | OPEN LINE FROM BUS 251378 [08M.FTGT 69.000] TO BUS 251406 [08MONSTW 69.000] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3988 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2195 251378-251469(1) | OPEN LINE FROM BUS 251378 [08M.FTGT 69.000] TO BUS 251469 [08T28652 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2196 251378-251579(1) | OPEN LINE FROM BUS 251378 [08M.FTGT 69.000] TO BUS 251579 [08HEBRON 69.000] CKT 1 | -31.481 | 31.481 | 33 | 95.3969 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2197 251467-251579(1) | OPEN LINE FROM BUS 251467 [08T15268 69.000] TO BUS 251579 [08HEBRON 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2198 251468-251469(1) | OPEN LINE FROM BUS 251468 [08T28651 69.000] TO BUS 251469 [08T28652 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2199 249564-248002(1) | OPEN LINE FROM BUS 249564 [08BUFTN1 345.00] TO BUS 248002 [06DEARB2 345.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2200 249564-248013(1) | OPEN LINE FROM BUS 249564 [08BUFTN1 345.00] TO BUS 248013 [06PIERCE 345.00] CKT 1 | -31.4812 | 31.4812 | 33 | 95.3975 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2201 249566-248013(1) | OPEN LINE FROM BUS 249566 [08FOSTER 345.00] TO BUS 248013 [06PIERCE 345.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2202 249566-250029(1) | OPEN LINE FROM BUS 249566 [08FOSTER 345.00] TO BUS 250029 [08FOSTER 138.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2203 249566-253006(1) | OPEN LINE FROM BUS 249566 [08FOSTER 345.00] TO BUS 253006 [09BATH 345.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2204 249566-253079(1) | OPEN LINE FROM BUS 249566 [08FOSTER 345.00] TO BUS 253079 [09SUGRCK 345.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2205 249567-243233(1) | OPEN LINE FROM BUS 249567 [08M.FORT 345.00] TO BUS 243233 [05TANNER 345.00] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3978 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2206 249567-249576(1) | OPEN LINE FROM BUS 249567 [08M.FORT 345.00] TO BUS 249576 [08WODSDL 345.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2207 249567-251950(7) | OPEN LINE FROM BUS 249567 [08M.FORT 345.00] TO BUS 251950 [08M.FRT7 22.000] CKT 7 | -31.4817 | 31.4817 | 33 | 95.399 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2208 249567-251951(8) | OPEN LINE FROM BUS 249567 [08M.FORT 345.00] TO BUS 251951 [08M.FRT8 22.000] CKT 8 | -31.4817 | 31.4817 | 33 | 95.399 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2209 249567-253090(1) | OPEN LINE FROM BUS 249567 [08M.FORT 345.00] TO BUS 253090 [09WMILTN 345.00] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2210 249571-250092(1) | OPEN LINE FROM BUS 249571 [08REDBK1 345.00] TO BUS 250092 [08REDBK1 138.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2211 249571-250093(1) | OPEN LINE FROM BUS 249571 [08REDBK1 345.00] TO BUS 250093 [08REDBK2 138.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2212 249575-249565(1) | OPEN LINE FROM BUS 249575 [08TERMNL 345.00] TO BUS 249565 [08EBEND 345.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2213 249575-250117(1) | OPEN LINE FROM BUS 249575 [08TERMNL 345.00] TO BUS 250117 [08TRMNL1 138.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2214 249575-250118(1) | OPEN LINE FROM BUS 249575 [08TERMNL 345.00] TO BUS 250118 [08TRMNL2 138.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2215 249578-253077(1) | OPEN LINE FROM BUS 249578 [08HILCRT 345.00] TO BUS 253077 [09STUART 345.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2217 249582-249574(1) | OPEN LINE FROM BUS 249582 [08GARVER 345.00] TO BUS 249574 [08TDHNTR 345.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2218 249582-249583(1) | OPEN LINE FROM BUS 249582 [08GARVER 345.00] TO BUS 249583 [08NTEGEN 345.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2219 249582-250162(1) | OPEN LINE FROM BUS 249582 [08GARVER 345.00] TO BUS 250162 [08GARVER 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2220 249990-253076(1) | OPEN LINE FROM BUS 249990 [08BROWN 138.00] TO BUS 253076 [09STUART 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2221 249990-251277-251792(1) | OPEN LINE FROM BUS 249990 [08BROWN 138.00] TO BUS 251277 [08BROWN 69.000] TO BUS 251792 [08BROWN 34.500] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2222 249991-251278(1) | OPEN LINE FROM BUS 249991 [08BUFTN1 138.00] TO BUS 251278 [08BUFTN1 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2223 249991-251278-252039(1) | OPEN LINE FROM BUS 249991 [08BUFTN1 138.00] TO BUS 251278 [08BUFTN1 69.000] TO BUS 252039 [08BUFTN1 12.470] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2224 250007-250014(1) | OPEN LINE FROM BUS 250007 [08CRSNT1 138.00] TO BUS 250014 [08DNLSN1 138.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2225 250007-250124(1) | OPEN LINE FROM BUS 250007 [08CRSNT1 138.00] TO BUS 250124 [08WENDEA 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2226 250016-250061(1) | OPEN LINE FROM BUS 250016 [08EBNZR 138.00] TO BUS 250061 [08MDWAY2 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2227 250016-251311(1) | OPEN LINE FROM BUS 250016 [08EBNZR 138.00] TO BUS 251311 [08EBNZR1 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2228 250016-251312(1) | OPEN LINE FROM BUS 250016 [08EBNZR 138.00] TO BUS 251312 [08EBNZR2 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2229 250016-251793(1) | OPEN LINE FROM BUS 250016 [08EBNZR 138.00] TO BUS 251793 [08EBNZR6 34.500] CKT 1 | -31.4813 | 31.4813 | 33 | 95.398 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2230 250021-250020(Z1) | OPEN LINE FROM BUS 250021 [08ESTWD2 138.00] TO BUS 250020 [08ESTWD1 138.00] CKT Z1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2231 250028-250027(Z1) | OPEN LINE FROM BUS 250028 [08FLRNC2 138.00] TO BUS 250027 [08FLRNC1 138.00] CKT Z1 | -31.4813 | 31.4813 | 33 | 95.3979 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2233 250057-249736(1) | OPEN LINE FROM BUS 250057 [08M.FORT 138.00] TO BUS 249736 [08GRDALE 138.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3986 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2235 250058-251960-251961(18) | OPEN LINE FROM BUS 250058 [08M.FTGT 138.00] TO BUS 251960 [08MFTGT1 13.800] TO BUS 251961 [08MFTGT2 13.800] CKT 18 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2236 250060-250048(1) | OPEN LINE FROM BUS 250060 [08MDWAY1 138.00] TO BUS 250048 [08KLEMN1 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2237 250070-250032(1) | OPEN LINE FROM BUS 250070 [08MRGAN1 138.00] TO BUS 250032 [08FRFLD1 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2238 250082-249985(1) | OPEN LINE FROM BUS 250082 [08P.UN1 138.00] TO BUS 249985 [08BECKET 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2239 250082-250050(1) | OPEN LINE FROM BUS 250082 [08P.UN1 138.00] TO BUS 250050 [08KMPER1 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2240 250082-250067(1) | OPEN LINE FROM BUS 250082 [08P.UN1 138.00] TO BUS 250067 [08MLHSR2 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2241 250082-250096(1) | OPEN LINE FROM BUS 250082 [08P.UN1 138.00] TO BUS 250096 [08SEWARD 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2242 250082-250157(1) | OPEN LINE FROM BUS 250082 [08P.UN1 138.00] TO BUS 250157 [08CORNTP 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2243 250082-251428-251798(1) | OPEN LINE FROM BUS 250082 [08P.UN1 138.00] TO BUS 251428 [08P.UNN1 69.000] TO BUS 251798 [08PORTU6 34.500] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2244 250083-250013(1) | OPEN LINE FROM BUS 250083 [08P.UN2 138.00] TO BUS 250013 [08DIMICK 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2245 250083-250065(1) | OPEN LINE FROM BUS 250083 [08P.UN2 138.00] TO BUS 250065 [08MILIKN 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2246 250083-250160(1) | OPEN LINE FROM BUS 250083 [08P.UN2 138.00] TO BUS 250160 [08PROVID 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2247 250083-251429(1) | OPEN LINE FROM BUS 250083 [08P.UN2 138.00] TO BUS 251429 [08P.UNN2 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2248 250083-251798(1) | OPEN LINE FROM BUS 250083 [08P.UN2 138.00] TO BUS 251798 [08PORTU6 34.500] CKT 1 | -31.4814 | 31.4814 | 33 | 95.398 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2249 250083-252045(5) | OPEN LINE FROM BUS 250083 [08P.UN2 138.00] TO BUS 252045 [08PORTU2 12.470] CKT 5 | -31.4814 | 31.4814 | 33 | 95.398 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2250 250083-251428-252045(1) | OPEN LINE FROM BUS 250083 [08P.UN2 138.00] TO BUS 251428 [08P.UNN1 69.000] TO BUS 252045 [08PORTU2 12.470] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2251 250097-249988(1) | OPEN LINE FROM BUS 250097 [08SGROVE 138.00] TO BUS 249988 [08BKJ135 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2252 250097-250042(1) | OPEN LINE FROM BUS 250097 [08SGROVE 138.00] TO BUS 250042 [08HANDS1 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2253 250097-250052(1) | OPEN LINE FROM BUS 250097 [08SGROVE 138.00] TO BUS 250052 [08KYUNIV 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2254 250097-250053(1) | OPEN LINE FROM BUS 250097 [08SGROVE 138.00] TO BUS 250053 [08LAFARG 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2255 250131-250032(1) | OPEN LINE FROM BUS 250131 [08WILEY2 138.00] TO BUS 250032 [08FRFLD1 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2256 250131-250068(1) | OPEN LINE FROM BUS 250131 [08WILEY2 138.00] TO BUS 250068 [08MPLKL1 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2257 250131-250155(1) | OPEN LINE FROM BUS 250131 [08WILEY2 138.00] TO BUS 250155 [08WILCAP 138.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2258 250131-251826(1) | OPEN LINE FROM BUS 250131 [08WILEY2 138.00] TO BUS 251826 [WILLEY 1 34.500] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3978 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2259 250136-250166(Z1) | OPEN LINE FROM BUS 250136 [08HILCRT 138.00] TO BUS 250166 [08HLCRTC 138.00] CKT Z1 | -31.4816 | 31.4816 | 33 | 95.3989 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2260 250141-250020(1) | OPEN LINE FROM BUS 250141 [08SCEAST 138.00] TO BUS 250020 [08ESTWD1 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2261 250148-250043(1) | OPEN LINE FROM BUS 250148 [08EKPWEB 138.00] TO BUS 250043 [08HANDS2 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2264 251279-251527(1) | OPEN LINE FROM BUS 251279 [08BUFTN2 69.000] TO BUS 251527 [08TP6763 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2265 251279-251543(1) | OPEN LINE FROM BUS 251279 [08BUFTN2 69.000] TO BUS 251543 [08VILLA 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2266 251310-251284(1) | OPEN LINE FROM BUS 251310 [08DRYCRK 69.000] TO BUS 251284 [08ATLAS 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2268 251368-251373(1) | OPEN LINE FROM BUS 251368 [08LEVIB 69.000] TO BUS 251373 [08LMBRG1 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2269 251405-251449(1) | OPEN LINE FROM BUS 251405 [08MONSTE 69.000] TO BUS 251449 [08SAYLPK 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2270 251468-251414(1) | OPEN LINE FROM BUS 251468 [08T28651 69.000] TO BUS 251414 [08NEUMAN 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2272 360112-360450(1) | OPEN LINE FROM BUS 360112 [5RUGBY TN 161.00] TO BUS 360450 [5HUNTSVL TN 161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2273 360145-360473(1) | OPEN LINE FROM BUS 360145 [5ROYAL BLUE 161.00] TO BUS 360473 [5JELLICO TN 161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2274 360145-361771(1) | OPEN LINE FROM BUS 360145 [5ROYAL BLUE 161.00] TO BUS 361771 [5ROYL BLU SS161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2275 360333-361113(1) | OPEN LINE FROM BUS 360333 [5GLASGOW KY 161.00] TO BUS 361113 [5GLASGOW TP 161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2276 360334-360354(1) | OPEN LINE FROM BUS 360334 [5SUMMER SHAD161.00] TO BUS 360354 [5LAFAYETT TN161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2277 360334-360448(1) | OPEN LINE FROM BUS 360334 [5SUMMER SHAD161.00] TO BUS 360448 [5WOLF CRK HP161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2278 360334-361064(1) | OPEN LINE FROM BUS 360334 [5SUMMER SHAD161.00] TO BUS 361064 [5TOMPKNSV TP161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2279 360334-361788(1) | OPEN LINE FROM BUS 360334 [5SUMMER SHAD161.00] TO BUS 361788 [5SUM SHAD TP161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2280 360338-361139(1) | OPEN LINE FROM BUS 360338 [5SCOTTSVL KY161.00] TO BUS 361139 [5S SCOTTSVLE161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2281 360342-362499(1) | OPEN LINE FROM BUS 360342 [5LIVINGST TN161.00] TO BUS 362499 [2LIVINGST TN69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2282 360354-361139(1) | OPEN LINE FROM BUS 360354 [5LAFAYETT TN161.00] TO BUS 361139 [5S SCOTTSVLE161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2283 360354-361265(1) | OPEN LINE FROM BUS 360354 [5LAFAYETT TN161.00] TO BUS 361265 [5HARTSVLE TP161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2284 360354-361558(1) | OPEN LINE FROM BUS 360354 [5LAFAYETT TN161.00] TO BUS 361558 [5E SUMNER TP161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2285 360445-360450(1) | OPEN LINE FROM BUS 360445 [5BRAYTOWN TN161.00] TO BUS 360450 [5HUNTSVL TN 161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2286 360448-360486(1) | OPEN LINE FROM BUS 360448 [5WOLF CRK HP161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2287 360448-361618(1) | OPEN LINE FROM BUS 360448 [5WOLF CRK HP161.00] TO BUS 361618 [5KELSEY RD 161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2288 360448-361666(1) | OPEN LINE FROM BUS 360448 [5WOLF CRK HP161.00] TO BUS 361666 [5BURKSVLTP 161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2289 360448-364620(1) | OPEN LINE FROM BUS 360448 [5WOLF CRK HP161.00] TO BUS 364620 [1WOLFCR H1-213.800] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2290 360448-364621(2) | OPEN LINE FROM BUS 360448 [5WOLF CRK HP161.00] TO BUS 364621 [1WOLFCR H3-413.800] CKT 2 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2291 360448-364622(3) | OPEN LINE FROM BUS 360448 [5WOLF CRK HP161.00] TO BUS 364622 [1WOLFCR H5-613.800] CKT 3 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2292 360450-361580(1) | OPEN LINE FROM BUS 360450 [5HUNTSVL TN 161.00] TO BUS 361580 [5ONEIDA TN 161.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2293 360450-361618(1) | OPEN LINE FROM BUS 360450 [5HUNTSVL TN 161.00] TO BUS 361618 [5KELSEY RD 161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2294 360454-361771(1) | OPEN LINE FROM BUS 360454 [5CARYVILL TN161.00] TO BUS 361771 [5ROYL BLU SS161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2295 360509-361246(1) | OPEN LINE FROM BUS 360509 [5W TOMPKINSV161.00] TO BUS 361246 [5W TOMPKINST161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2296 361064-361246(1) | OPEN LINE FROM BUS 361064 [5TOMPKNSV TP161.00] TO BUS 361246 [5W TOMPKINST161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2297 361064-361666(1) | OPEN LINE FROM BUS 361064 [5TOMPKNSV TP161.00] TO BUS 361666 [5BURKSVLTP 161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2298 361113-361735(1) | OPEN LINE FROM BUS 361113 [5GLASGOW TP 161.00] TO BUS 361735 [5TRANSPARK 161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.398 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2299 361114-361735(1) | OPEN LINE FROM BUS 361114 [5BRISTOW TAP161.00] TO BUS 361735 [5TRANSPARK 161.00] CKT 1 | -31.4813 | 31.4813 | 33 | 95.398 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2300 361117-361246(1) | OPEN LINE FROM BUS 361117 [5TOMPKNSV PS161.00] TO BUS 361246 [5W TOMPKINST161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2301 361265-361266(1) | OPEN LINE FROM BUS 361265 [5HARTSVLE TP161.00] TO BUS 361266 [5HARTSVLE TN161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2302 361267-361558(1) | OPEN LINE FROM BUS 361267 [5WESTMORELD 161.00] TO BUS 361558 [5E SUMNER TP161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2303 361558-361559(1) | OPEN LINE FROM BUS 361558 [5E SUMNER TP161.00] TO BUS 361559 [5E SUMNER TN161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2304 361579-361580(1) | OPEN LINE FROM BUS 361579 [5WINFIELD TN161.00] TO BUS 361580 [5ONEIDA TN 161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2305 361603-361604(1) | OPEN LINE FROM BUS 361603 [5E GLASGOW T161.00] TO BUS 361604 [5E GLASGOW 161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2306 361618-361619(1) | OPEN LINE FROM BUS 361618 [5KELSEY RD 161.00] TO BUS 361619 [5BYRDSTOWN 161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2307 361666-361667(1) | OPEN LINE FROM BUS 361666 [5BURKSVLTP 161.00] TO BUS 361667 [5BURKESVL KY161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2308 362058-362059(1) | OPEN LINE FROM BUS 362058 [2MOSS TN TAP69.000] TO BUS 362059 [2TOMPKINSVL 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2309 362058-362061(1) | OPEN LINE FROM BUS 362058 [2MOSS TN TAP69.000] TO BUS 362061 [2DALE HOLLOW69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2310 362058-363060(1) | OPEN LINE FROM BUS 362058 [2MOSS TN TAP69.000] TO BUS 363060 [2MOSS TN 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2311 362059-362060(1) | OPEN LINE FROM BUS 362059 [2TOMPKINSVL 69.000] TO BUS 362060 [2SUMMER SHAD69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2312 362060-362061(1) | OPEN LINE FROM BUS 362060 [2SUMMER SHAD69.000] TO BUS 362061 [2DALE HOLLOW69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2313 362061-364614(1) | OPEN LINE FROM BUS 362061 [2DALE HOLLOW69.000] TO BUS 364614 [1DALE HOL H113.800] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2314 362061-364615(2) | OPEN LINE FROM BUS 362061 [2DALE HOLLOW69.000] TO BUS 364615 [1DALE HOL H213.800] CKT 2 | -31.4815 | 31.4815 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2315 362061-364616(3) | OPEN LINE FROM BUS 362061 [2DALE HOLLOW69.000] TO BUS 364616 [1DALE HOL H313.800] CKT 3 | -31.4815 | 31.4815 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2316 360112-361287(1) | OPEN LINE FROM BUS 360112 [5RUGBY TN 161.00] TO BUS 361287 [5JAMESTWN TN161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2319 360334-360607(1) | OPEN LINE FROM BUS 360334 [5SUMMER SHAD161.00] TO BUS 360607 [5S GLASGOW 161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2320 360334-362060-362483(2) | OPEN LINE FROM BUS 360334 [5SUMMER SHAD161.00] TO BUS 362060 [2SUMMER SHAD69.000] TO BUS 362483 [1SUMMER SHAD13.200] CKT 2 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2321 360338-361553(1) | OPEN LINE FROM BUS 360338 [5SCOTTSVL KY161.00] TO BUS 361553 [5N SCOTTSVLE161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2322 360338-361621(1) | OPEN LINE FROM BUS 360338 [5SCOTTSVL KY161.00] TO BUS 361621 [5ALVATON TP 161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2323 360342-361617(1) | OPEN LINE FROM BUS 360342 [5LIVINGST TN161.00] TO BUS 361617 [5MONROE TAP 161.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2324 360342-361731(1) | OPEN LINE FROM BUS 360342 [5LIVINGST TN161.00] TO BUS 361731 [5RICKMAN TAP161.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2325 360352-360349(2) | OPEN LINE FROM BUS 360352 [5GALLATIN F1161.00] TO BUS 360349 [5LEBANON TN 161.00] CKT 2 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2326 360352-360382(1) | OPEN LINE FROM BUS 360352 [5GALLATIN F1161.00] TO BUS 360382 [5HOEGANAES 161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2327 360352-360773(1) | OPEN LINE FROM BUS 360352 [5GALLATIN F1161.00] TO BUS 360773 [5WILSON #2 161.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2328 360352-361128(1) | OPEN LINE FROM BUS 360352 [5GALLATIN F1161.00] TO BUS 361128 [5LEBANON IPT161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2329 360352-361714(1) | OPEN LINE FROM BUS 360352 [5GALLATIN F1161.00] TO BUS 361714 [5GAL SCRB TP161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2330 360352-361827(1) | OPEN LINE FROM BUS 360352 [5GALLATIN F1161.00] TO BUS 361827 [5W TROUSDALE161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2331 360352-364121(1) | OPEN LINE FROM BUS 360352 [5GALLATIN F1161.00] TO BUS 364121 [1GALLATIN F124.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2332 360352-364122(2) | OPEN LINE FROM BUS 360352 [5GALLATIN F1161.00] TO BUS 364122 [1GALLATIN F224.000] CKT 2 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2333 360352-364221-364222(T1) | OPEN LINE FROM BUS 360352 [5GALLATIN F1161.00] TO BUS 364221 [1GALLATIN T113.800] TO BUS 364222 [1GALLATIN T213.800] CKT T1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2334 360352-364223-364224(T2) | OPEN LINE FROM BUS 360352 [5GALLATIN F1161.00] TO BUS 364223 [1GALLATIN T313.800] TO BUS 364224 [1GALLATIN T413.800] CKT T2 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2335 360445-361542(1) | OPEN LINE FROM BUS 360445 [5BRAYTOWN TN161.00] TO BUS 361542 [5WINDROCK 161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3982 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2337 360454-361330(1) | OPEN LINE FROM BUS 360454 [5CARYVILL TN161.00] TO BUS 361330 [5JACKSBRO TP161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2341 361113-360607(1) | OPEN LINE FROM BUS 361113 [5GLASGOW TP 161.00] TO BUS 360607 [5S GLASGOW 161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2342 361114-360332(1) | OPEN LINE FROM BUS 361114 [5BRISTOW TAP161.00] TO BUS 360332 [5E BOWLGREEN161.00] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3979 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2343 361114-360335(1) | OPEN LINE FROM BUS 361114 [5BRISTOW TAP161.00] TO BUS 360335 [5BRISTOW KY 161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2344 361265-361827(1) | OPEN LINE FROM BUS 361265 [5HARTSVLE TP161.00] TO BUS 361827 [5W TROUSDALE161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2345 361267-360530(1) | OPEN LINE FROM BUS 361267 [5WESTMORELD 161.00] TO BUS 360530 [5ANGELTOWN 161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2348 361603-360607(1) | OPEN LINE FROM BUS 361603 [5E GLASGOW T161.00] TO BUS 360607 [5S GLASGOW 161.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.398 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2352 253006-253027(1) | OPEN LINE FROM BUS 253006 [09BATH 345.00] TO BUS 253027 [09GREENE 345.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2353 253013-253014(1) | OPEN LINE FROM BUS 253013 [09CLINTO 69.000] TO BUS 253014 [09CLINTO 345.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2354 253013-253014(2) | OPEN LINE FROM BUS 253013 [09CLINTO 69.000] TO BUS 253014 [09CLINTO 345.00] CKT 2 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2355 253013-253094(1) | OPEN LINE FROM BUS 253013 [09CLINTO 69.000] TO BUS 253094 [09WILMNG 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2356 253013-253094(2) | OPEN LINE FROM BUS 253013 [09CLINTO 69.000] TO BUS 253094 [09WILMNG 69.000] CKT 2 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2357 253014-253027(1) | OPEN LINE FROM BUS 253014 [09CLINTO 345.00] TO BUS 253027 [09GREENE 345.00] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2358 253026-253027(1) | OPEN LINE FROM BUS 253026 [09GREENE 138.00] TO BUS 253027 [09GREENE 345.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2359 253026-253027(2) | OPEN LINE FROM BUS 253026 [09GREENE 138.00] TO BUS 253027 [09GREENE 345.00] CKT 2 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2360 253027-253079(1) | OPEN LINE FROM BUS 253027 [09GREENE 345.00] TO BUS 253079 [09SUGRCK 345.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2361 253076-253077(1) | OPEN LINE FROM BUS 253076 [09STUART 138.00] TO BUS 253077 [09STUART 345.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2362 253077-253100(1) | OPEN LINE FROM BUS 253077 [09STUART 345.00] TO BUS 253100 [09ATLNTA 345.00] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3988 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2363 253099-253100(1) | OPEN LINE FROM BUS 253099 [09ATLNTA 69.000] TO BUS 253100 [09ATLNTA 345.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2364 253099-253181(1) | OPEN LINE FROM BUS 253099 [09ATLNTA 69.000] TO BUS 253181 [09NHOLLN 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2366 253006-253005(1) | OPEN LINE FROM BUS 253006 [09BATH 345.00] TO BUS 253005 [09BATH 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2367 253006-253005(2) | OPEN LINE FROM BUS 253006 [09BATH 345.00] TO BUS 253005 [09BATH 138.00] CKT 2 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2368 253006-253047(1) | OPEN LINE FROM BUS 253006 [09BATH 345.00] TO BUS 253047 [09MIAMI 345.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2369 253014-253310(1) | OPEN LINE FROM BUS 253014 [09CLINTO 345.00] TO BUS 253310 [AC1-085 POI 345.00] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3989 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2370 253026-238623(1) | OPEN LINE FROM BUS 253026 [09GREENE 138.00] TO BUS 238623 [02CLARK 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2371 253026-253002(1) | OPEN LINE FROM BUS 253026 [09GREENE 138.00] TO BUS 253002 [09AIRWAY 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2372 253026-253040(1) | OPEN LINE FROM BUS 253026 [09GREENE 138.00] TO BUS 253040 [09KNOLLW 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2373 253026-253062(1) | OPEN LINE FROM BUS 253026 [09GREENE 138.00] TO BUS 253062 [09OVERL1 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2374 253026-253083(1) | OPEN LINE FROM BUS 253026 [09GREENE 138.00] TO BUS 253083 [09TREBEI 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2375 253026-253107(1) | OPEN LINE FROM BUS 253026 [09GREENE 138.00] TO BUS 253107 [09ALPHA 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2376 253027-253248(1) | OPEN LINE FROM BUS 253027 [09GREENE 345.00] TO BUS 253248 [09MDISON 345.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2381 253077-253310(1) | OPEN LINE FROM BUS 253077 [09STUART 345.00] TO BUS 253310 [AC1-085 POI 345.00] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2382 253077-253352(1) | OPEN LINE FROM BUS 253077 [09STUART 345.00] TO BUS 253352 [AB1-169 MAIN345.00] CKT 1 | -31.4806 | 31.4806 | 33 | 95.3959 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2385 253079-253078(1) | OPEN LINE FROM BUS 253079 [09SUGRCK 345.00] TO BUS 253078 [09SUGRCK 138.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2386 253079-253078(2) | OPEN LINE FROM BUS 253079 [09SUGRCK 345.00] TO BUS 253078 [09SUGRCK 138.00] CKT 2 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2387 253094-253043(1) | OPEN LINE FROM BUS 253094 [09WILMNG 69.000] TO BUS 253043 [09MRTNSV 69.000] CKT 1 | -31.4813 | 31.4813 | 33 | 95.3979 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2388 253094-253115(1) | OPEN LINE FROM BUS 253094 [09WILMNG 69.000] TO BUS 253115 [09AIRPRK 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2389 253094-253131(1) | OPEN LINE FROM BUS 253094 [09WILMNG 69.000] TO BUS 253131 [09COL ST 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3981 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2390 253094-253237(1) | OPEN LINE FROM BUS 253094 [09WILMNG 69.000] TO BUS 253237 [09WEBBRD 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2391 253099-253322(1) | OPEN LINE FROM BUS 253099 [09ATLNTA 69.000] TO BUS 253322 [AC1-069 MAIN69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2392 253099-253330(1) | OPEN LINE FROM BUS 253099 [09ATLNTA 69.000] TO BUS 253330 [AC1-068 MAIN69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2393 253099-253335(1) | OPEN LINE FROM BUS 253099 [09ATLNTA 69.000] TO BUS 253335 [AC1-165 MAIN69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2394 253099-253340(1) | OPEN LINE FROM BUS 253099 [09ATLNTA 69.000] TO BUS 253340 [AC1-166 MAIN69.000] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2395 253100-245769(1) | OPEN LINE FROM BUS 253100 [09ATLNTA 345.00] TO BUS 245769 [05ADKINS 345.00] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3988 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2396 253181-253201(1) | OPEN LINE FROM BUS 253181 [09NHOLLN 69.000] TO BUS 253201 [09ROBINS 69.000] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN LIN 2397 248005-248013(1) | OPEN LINE FROM BUS 248005 [06KYGER 345.00] TO BUS 248013 [06PIERCE 345.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2398 248005-242528(1) | OPEN LINE FROM BUS 248005 [06KYGER 345.00] TO BUS 242528 [05SPORN 345.00] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2401 248005-248027-248026(1) | OPEN LINE FROM BUS 248005 [06KYGER 345.00] TO BUS 248027 [06KYGER 1LP 15.500] TO BUS 248026 [06KYGER 1HP 15.500] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2402 248005-248029-248028(1) | OPEN LINE FROM BUS 248005 [06KYGER 345.00] TO BUS 248029 [06KYGER 2LP 15.500] TO BUS 248028 [06KYGER 2HP 15.500] CKT 1 | -31.4814 | 31.4814 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2403 248005-248031-248030(1) | OPEN LINE FROM BUS 248005 [06KYGER 345.00] TO BUS 248031 [06KYGER 3LP 15.500] TO BUS 248030 [06KYGER 3HP 15.500] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2404 248005-248033-248032(1) | OPEN LINE FROM BUS 248005 [06KYGER 345.00] TO BUS 248033 [06KYGER 4LP 15.500] TO BUS 248032 [06KYGER 4HP 15.500] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2405 248005-248035-248034(1) | OPEN LINE FROM BUS 248005 [06KYGER 345.00] TO BUS 248035 [06KYGER 5LP 15.500] TO BUS 248034 [06KYGER 5HP 15.500] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2406 248009-248008(SR) | OPEN LINE FROM BUS 248009 [06CLIFTY 138.00] TO BUS 248008 [06CLIFTX 138.00] CKT SR | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2411 248013-248000(1) | OPEN LINE FROM BUS 248013 [06PIERCE 345.00] TO BUS 248000 [06CLIFTY 345.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2412 248013-248000(2) | OPEN LINE FROM BUS 248013 [06PIERCE 345.00] TO BUS 248000 [06CLIFTY 345.00] CKT 2 | -31.4815 | 31.4815 | 33 | 95.3985 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2413 248013-248001(1) | OPEN LINE FROM BUS 248013 [06PIERCE 345.00] TO BUS 248001 [06DEARB1 345.00] CKT 1 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2416 248013-250086(17) | OPEN LINE FROM BUS 248013 [06PIERCE 345.00] TO BUS 250086 [08PIERCE 138.00] CKT 17 | -31.4815 | 31.4815 | 33 | 95.3983 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2417 248013-250143(18) | OPEN LINE FROM BUS 248013 [06PIERCE 345.00] TO BUS 250143 [08PRCE18 138.00] CKT 18 | -31.4815 | 31.4815 | 33 | 95.3984 | LGEE
324082 | 2PARIS 4 | 69 | 324476 | 2CMC TAP | 69 | 1 | SINGLE OPN TIE 2418 249736-249754(1) | OPEN LINE FROM BUS 249736 [08GRDALE 138.00] TO BUS 249754 [08HEHIDN 138.00] CKT 1 | -31.4816 | 31.4816 | 33 | 95.3987 | LGEE

## Bus Voltage
BUS |  |  | RECORD | TYPE | MIN | MAX | CONTINGENCY | CONTINGENCY | BASE VOLTS | VOLTAGE | CONT VOLTS | VOLTAGE | DEVIATION | RANGE VIO | DEV VIO | Analysis
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BASE CASE | BASE CASE | 0.93965 | 64.8362 |  |  |  | -0.00034559 |  |  | BASE VOLTS is pu base case voltage.
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BASE CASE | BASE CASE | 1.05 | 525 |  |  |  | 0 |  |  | CONT VOLTS is pu contingency case voltage.
DEVIATION is difference between contingency case and base case voltage.
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1 339206-342769(1) | OPEN LINE FROM BUS 339206 [AE1-143 C 161.00] TO BUS 342769 [5MARION CO 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8358 | -5.424e-06 | -0.00035101 |  |  | RANGE VIO is range violations calculated as bus voltage - minimum range limit or bus voltage - maximum range limit.
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1 339206-342769(1) | OPEN LINE FROM BUS 339206 [AE1-143 C 161.00] TO BUS 342769 [5MARION CO 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0 |  |  | DEV VIO is deviation violations calculated as DEVIATION - minimum deviation limit or DEVIATION - maximum deviation limit.
Report Options Used:
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2 339206-939132(1) | OPEN LINE FROM BUS 339206 [AE1-143 C 161.00] TO BUS 939132 [AE1-143 E 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 1.5497e-06 | -0.00034404 |  |  | Solution type = contingency
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2 339206-939132(1) | OPEN LINE FROM BUS 339206 [AE1-143 C 161.00] TO BUS 939132 [AE1-143 E 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0 |  |  | Rating to use to calculate Base Case percentage overload = RATE1
Rating to use to calculate Contingency Case percentage overload = RATE2
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 3 341002-341443(1) | OPEN LINE FROM BUS 341002 [2AIRPORT RD 69.000] TO BUS 341443 [2ELLIO CO PT69.000] CKT 1 | 0.93965 | 64.8362 | 0.9395 | 64.8253 | -0.00015718 | -0.00050277 |  |  | Exclude elements with base case loading violations from contingency reports = False
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 3 341002-341443(1) | OPEN LINE FROM BUS 341002 [2AIRPORT RD 69.000] TO BUS 341443 [2ELLIO CO PT69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0 |  |  | Exclude buses with base case voltage range violations from contingency reports = False
Exclude elements with base case SWD loading violations from contingency reports = False
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 4 341002-341752(1) | OPEN LINE FROM BUS 341002 [2AIRPORT RD 69.000] TO BUS 341752 [2LEON 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93943 | 64.8206 | -0.00022537 | -0.00057095 |  |  | Exclude buses with base case node voltage range violations from contingency reports = False
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 4 341002-341752(1) | OPEN LINE FROM BUS 341002 [2AIRPORT RD 69.000] TO BUS 341752 [2LEON 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0 |  |  | Percent of flow rating = 95
Minimum contingency case flow change = 0.0 MVA, filter criteria ignored
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 5 341005-342181(1) | OPEN LINE FROM BUS 341005 [2ALBANY 69.000] TO BUS 342181 [2S ALBANY 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 1.1325e-06 | -0.00034446 |  |  | Minimum contingency case voltage change = 0.0 pu, filter criteria ignored
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 5 341005-342181(1) | OPEN LINE FROM BUS 341005 [2ALBANY 69.000] TO BUS 342181 [2S ALBANY 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0 |  |  | Exclude islanded buses from contingency reports = True
Bus mismatch tolerance = 0.5 MVA
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 6 341005-342283(1) | OPEN LINE FROM BUS 341005 [2ALBANY 69.000] TO BUS 342283 [2SNOW T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8358 | -5.2452e-06 | -0.00035083 |  |  | System mismatch tolerance = 5 MVA
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 6 341005-342283(1) | OPEN LINE FROM BUS 341005 [2ALBANY 69.000] TO BUS 342283 [2SNOW T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 7 341005-342397(1) | OPEN LINE FROM BUS 341005 [2ALBANY 69.000] TO BUS 342397 [2UPCHURCH T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 4.1723e-07 | -0.00034517
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 7 341005-342397(1) | OPEN LINE FROM BUS 341005 [2ALBANY 69.000] TO BUS 342397 [2UPCHURCH T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 8 341008-342106(1) | OPEN LINE FROM BUS 341008 [2ALCAN 69.000] TO BUS 342106 [2PPG J 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8367 | 7.8082e-06 | -0.00033778
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 8 341008-342106(1) | OPEN LINE FROM BUS 341008 [2ALCAN 69.000] TO BUS 342106 [2PPG J 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 9 341008-342430(1) | OPEN LINE FROM BUS 341008 [2ALCAN 69.000] TO BUS 342430 [2W BEREA 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93988 | 64.8515 | 0.00022256 | -0.00012302
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 9 341008-342430(1) | OPEN LINE FROM BUS 341008 [2ALCAN 69.000] TO BUS 342430 [2W BEREA 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 10 341014-341017(1) | OPEN LINE FROM BUS 341014 [2ANNVILLE 69.000] TO BUS 341017 [2ANNVILLE T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93968 | 64.838 | 2.6941e-05 | -0.00031865
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 10 341014-341017(1) | OPEN LINE FROM BUS 341014 [2ANNVILLE 69.000] TO BUS 341017 [2ANNVILLE T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 11 341017-341428(1) | OPEN LINE FROM BUS 341017 [2ANNVILLE T 69.000] TO BUS 341428 [2EBERLE T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.9397 | 64.8391 | 4.3273e-05 | -0.00030231
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 11 341017-341428(1) | OPEN LINE FROM BUS 341017 [2ANNVILLE T 69.000] TO BUS 341428 [2EBERLE T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 12 341017-342391(1) | OPEN LINE FROM BUS 341017 [2ANNVILLE T 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93971 | 64.8398 | 5.2631e-05 | -0.00029296
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 12 341017-342391(1) | OPEN LINE FROM BUS 341017 [2ANNVILLE T 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 13 341020-341782(1) | OPEN LINE FROM BUS 341020 [2ARGENTUM 69.000] TO BUS 341782 [2LOW GAP T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93955 | 64.8288 | -0.00010622 | -0.0004518
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 13 341020-341782(1) | OPEN LINE FROM BUS 341020 [2ARGENTUM 69.000] TO BUS 341782 [2LOW GAP T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 14 341020-342538(1) | OPEN LINE FROM BUS 341020 [2ARGENTUM 69.000] TO BUS 342538 [4ARGENTUM 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93958 | 64.8313 | -7.0512e-05 | -0.0004161
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 14 341020-342538(1) | OPEN LINE FROM BUS 341020 [2ARGENTUM 69.000] TO BUS 342538 [4ARGENTUM 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 15 341029-341032(1) | OPEN LINE FROM BUS 341029 [2ASAHI M W 69.000] TO BUS 341032 [2ASAHI M W T69.000] CKT 1 | 0.93965 | 64.8362 | 0.9397 | 64.839 | 4.0829e-05 | -0.00030476
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 15 341029-341032(1) | OPEN LINE FROM BUS 341029 [2ASAHI M W 69.000] TO BUS 341032 [2ASAHI M W T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 16 341032-341379(1) | OPEN LINE FROM BUS 341032 [2ASAHI M W T69.000] TO BUS 341379 [2DAHL ROAD 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.835 | -1.651e-05 | -0.0003621
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 16 341032-341379(1) | OPEN LINE FROM BUS 341032 [2ASAHI M W T69.000] TO BUS 341379 [2DAHL ROAD 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 17 341032-342472(1) | OPEN LINE FROM BUS 341032 [2ASAHI M W T69.000] TO BUS 342472 [2WALNUT GROV69.000] CKT 1 | 0.93965 | 64.8362 | 0.93968 | 64.8377 | 2.2292e-05 | -0.0003233
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 17 341032-342472(1) | OPEN LINE FROM BUS 341032 [2ASAHI M W T69.000] TO BUS 342472 [2WALNUT GROV69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 18 341035-341038(1) | OPEN LINE FROM BUS 341035 [2BACON CRK 69.000] TO BUS 341038 [2BACON CRK T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8371 | 1.4007e-05 | -0.00033158
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 18 341035-341038(1) | OPEN LINE FROM BUS 341035 [2BACON CRK 69.000] TO BUS 341038 [2BACON CRK T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 19 341038-341755(1) | OPEN LINE FROM BUS 341038 [2BACON CRK T69.000] TO BUS 341755 [2LIBER CH T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93963 | 64.8345 | -2.4021e-05 | -0.00036961
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 19 341038-341755(1) | OPEN LINE FROM BUS 341038 [2BACON CRK T69.000] TO BUS 341755 [2LIBER CH T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 20 341038-342187(1) | OPEN LINE FROM BUS 341038 [2BACON CRK T69.000] TO BUS 342187 [2S CORBIN 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8351 | -1.5616e-05 | -0.0003612
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 20 341038-342187(1) | OPEN LINE FROM BUS 341038 [2BACON CRK T69.000] TO BUS 342187 [2S CORBIN 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 21 341041-341635(1) | OPEN LINE FROM BUS 341041 [2BAKER LN 69.000] TO BUS 341635 [2HOLLOWAY 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93973 | 64.8412 | 7.3612e-05 | -0.00027198
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 21 341041-341635(1) | OPEN LINE FROM BUS 341041 [2BAKER LN 69.000] TO BUS 341635 [2HOLLOWAY 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 22 341041-341638(1) | OPEN LINE FROM BUS 341041 [2BAKER LN 69.000] TO BUS 341638 [2HOLLOWAY J 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93972 | 64.8409 | 6.8605e-05 | -0.00027698
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 22 341041-341638(1) | OPEN LINE FROM BUS 341041 [2BAKER LN 69.000] TO BUS 341638 [2HOLLOWAY J 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 23 341041-342547(1) | OPEN LINE FROM BUS 341041 [2BAKER LN 69.000] TO BUS 342547 [4BAKER LN 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93995 | 64.8568 | 0.00029993 | -4.5657e-05
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 23 341041-342547(1) | OPEN LINE FROM BUS 341041 [2BAKER LN 69.000] TO BUS 342547 [4BAKER LN 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 1.1921e-07 | 1.1921e-07
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 24 341044-341671(1) | OPEN LINE FROM BUS 341044 [2BALLARD 69.000] TO BUS 341671 [2HUNT FARM J69.000] CKT 1 | 0.93965 | 64.8362 | 0.93961 | 64.833 | -4.6194e-05 | -0.00039178
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 24 341044-341671(1) | OPEN LINE FROM BUS 341044 [2BALLARD 69.000] TO BUS 341671 [2HUNT FARM J69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 25 341044-342361(1) | OPEN LINE FROM BUS 341044 [2BALLARD 69.000] TO BUS 342361 [2TODDVILLE T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8348 | -1.9252e-05 | -0.00036484
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 25 341044-342361(1) | OPEN LINE FROM BUS 341044 [2BALLARD 69.000] TO BUS 342361 [2TODDVILLE T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 26 341047-342424(1) | OPEN LINE FROM BUS 341047 [2BALLTOWN 69.000] TO BUS 342424 [2W BARDST J 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -4.7684e-07 | -0.00034606
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 26 341047-342424(1) | OPEN LINE FROM BUS 341047 [2BALLTOWN 69.000] TO BUS 342424 [2W BARDST J 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 27 341050-342295(1) | OPEN LINE FROM BUS 341050 [2BANK LCK 69.000] TO BUS 342295 [2STANLY P J169.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 28 341053-341056(1) | OPEN LINE FROM BUS 341053 [2BARD SHOP 69.000] TO BUS 341056 [2BARD SHOP T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 1.3709e-06 | -0.00034422
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 28 341053-341056(1) | OPEN LINE FROM BUS 341053 [2BARD SHOP 69.000] TO BUS 341056 [2BARD SHOP T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 29 341056-341407(1) | OPEN LINE FROM BUS 341056 [2BARD SHOP T69.000] TO BUS 341407 [2E BARDSTOWN69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8368 | 9.0599e-06 | -0.00033653
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 29 341056-341407(1) | OPEN LINE FROM BUS 341056 [2BARD SHOP T69.000] TO BUS 341407 [2E BARDSTOWN69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 30 341056-342424(1) | OPEN LINE FROM BUS 341056 [2BARD SHOP T69.000] TO BUS 342424 [2W BARDST J 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 4.1723e-06 | -0.00034142
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 30 341056-342424(1) | OPEN LINE FROM BUS 341056 [2BARD SHOP T69.000] TO BUS 342424 [2W BARDST J 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 31 341059-341275(1) | OPEN LINE FROM BUS 341059 [2BARREN CO 69.000] TO BUS 341275 [2CAVE CITY J69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 2.1458e-06 | -0.00034344
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 31 341059-341275(1) | OPEN LINE FROM BUS 341059 [2BARREN CO 69.000] TO BUS 341275 [2CAVE CITY J69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 32 341059-341542(1) | OPEN LINE FROM BUS 341059 [2BARREN CO 69.000] TO BUS 341542 [2GOODNIGHT 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 2.9802e-07 | -0.00034529
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 32 341059-341542(1) | OPEN LINE FROM BUS 341059 [2BARREN CO 69.000] TO BUS 341542 [2GOODNIGHT 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 33 341059-341651(1) | OPEN LINE FROM BUS 341059 [2BARREN CO 69.000] TO BUS 341651 [2HORSECAVE J69.000] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8373 | 1.7047e-05 | -0.00032854
341647 | 2HORSE CV KU | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 33 341059-341651(1) | OPEN LINE FROM BUS 341059 [2BARREN CO 69.000] TO BUS 341651 [2HORSECAVE J69.000] CKT 1 | 0.98114 | 67.6986 | 0.86507 | 59.6898 | -0.11607 | -0.07493
341650 | 2HORSECAVE T | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 33 341059-341651(1) | OPEN LINE FROM BUS 341059 [2BARREN CO 69.000] TO BUS 341651 [2HORSECAVE J69.000] CKT 1 | 0.98399 | 67.895 | 0.8683 | 59.9128 | -0.11569 | -0.071699
341651 | 2HORSECAVE J | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 33 341059-341651(1) | OPEN LINE FROM BUS 341059 [2BARREN CO 69.000] TO BUS 341651 [2HORSECAVE J69.000] CKT 1 | 0.98399 | 67.895 | 0.8683 | 59.9128 | -0.11569 | -0.071699
341908 | 2MUNFVIL EK | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 33 341059-341651(1) | OPEN LINE FROM BUS 341059 [2BARREN CO 69.000] TO BUS 341651 [2HORSECAVE J69.000] CKT 1 | 0.98826 | 68.1902 | 0.92118 | 63.5616 | -0.06708 | -0.018817
341911 | 2MUNFVIL KU | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 33 341059-341651(1) | OPEN LINE FROM BUS 341059 [2BARREN CO 69.000] TO BUS 341651 [2HORSECAVE J69.000] CKT 1 | 0.98589 | 68.0265 | 0.90692 | 62.5773 | -0.078974 | -0.033083
341914 | 2MUNFVILKU T | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 33 341059-341651(1) | OPEN LINE FROM BUS 341059 [2BARREN CO 69.000] TO BUS 341651 [2HORSECAVE J69.000] CKT 1 | 0.98641 | 68.062 | 0.90748 | 62.6158 | -0.078929 | -0.032524
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 33 341059-341651(1) | OPEN LINE FROM BUS 341059 [2BARREN CO 69.000] TO BUS 341651 [2HORSECAVE J69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 34 341059-342694(1) | OPEN LINE FROM BUS 341059 [2BARREN CO 69.000] TO BUS 342694 [5BARREN CO 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 3.3975e-06 | -0.00034219
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 34 341059-342694(1) | OPEN LINE FROM BUS 341059 [2BARREN CO 69.000] TO BUS 342694 [5BARREN CO 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 35 341062-341269(1) | OPEN LINE FROM BUS 341062 [2BASS 69.000] TO BUS 341269 [2CASEY CO 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -5.3644e-07 | -0.00034612
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 35 341062-341269(1) | OPEN LINE FROM BUS 341062 [2BASS 69.000] TO BUS 341269 [2CASEY CO 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 36 341065-341068(1) | OPEN LINE FROM BUS 341065 [2BEAM 69.000] TO BUS 341068 [2BEAM T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -1.7881e-06 | -0.00034738
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 36 341065-341068(1) | OPEN LINE FROM BUS 341065 [2BEAM 69.000] TO BUS 341068 [2BEAM T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 37 341068-341215(1) | OPEN LINE FROM BUS 341068 [2BEAM T 69.000] TO BUS 341215 [2BULLITT CO 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8357 | -6.8545e-06 | -0.00035244
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 37 341068-341215(1) | OPEN LINE FROM BUS 341068 [2BEAM T 69.000] TO BUS 341215 [2BULLITT CO 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 38 341068-342253(1) | OPEN LINE FROM BUS 341068 [2BEAM T 69.000] TO BUS 342253 [2SHEPHEVIL J69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8358 | -4.4107e-06 | -0.00035
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 38 341068-342253(1) | OPEN LINE FROM BUS 341068 [2BEAM T 69.000] TO BUS 342253 [2SHEPHEVIL J69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 39 341071-341074(1) | OPEN LINE FROM BUS 341071 [2BEATTYV 69.000] TO BUS 341074 [2BEATTYV D 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93976 | 64.8432 | 0.00010186 | -0.00024372
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 40 341071-341077(1) | OPEN LINE FROM BUS 341071 [2BEATTYV 69.000] TO BUS 341077 [2BEATTYV J 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8366 | 7.093e-06 | -0.00033849
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 40 341071-341077(1) | OPEN LINE FROM BUS 341071 [2BEATTYV 69.000] TO BUS 341077 [2BEATTYV J 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 41 341071-342520(1) | OPEN LINE FROM BUS 341071 [2BEATTYV 69.000] TO BUS 342520 [2ZACHARIAH 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93963 | 64.8342 | -2.7716e-05 | -0.0003733
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 41 341071-342520(1) | OPEN LINE FROM BUS 341071 [2BEATTYV 69.000] TO BUS 342520 [2ZACHARIAH 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 42 341074-341992(1) | OPEN LINE FROM BUS 341074 [2BEATTYV D 69.000] TO BUS 341992 [2OAKDALE 69.000] CKT 1 | 0.93965 | 64.8362 | 0.9397 | 64.8392 | 4.4584e-05 | -0.000301
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 42 341074-341992(1) | OPEN LINE FROM BUS 341074 [2BEATTYV D 69.000] TO BUS 341992 [2OAKDALE 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 43 341077-341173(1) | OPEN LINE FROM BUS 341077 [2BEATTYV J 69.000] TO BUS 341173 [2BOONEVIL T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8366 | 6.4373e-06 | -0.00033915
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 43 341077-341173(1) | OPEN LINE FROM BUS 341077 [2BEATTYV J 69.000] TO BUS 341173 [2BOONEVIL T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 44 341080-341149(1) | OPEN LINE FROM BUS 341080 [2BECKTON 69.000] TO BUS 341149 [2BON AYR 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 1.7881e-07 | -0.00034541
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 44 341080-341149(1) | OPEN LINE FROM BUS 341080 [2BECKTON 69.000] TO BUS 341149 [2BON AYR 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 45 341080-342445(1) | OPEN LINE FROM BUS 341080 [2BECKTON 69.000] TO BUS 342445 [2W GLASGOW T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 2.9206e-06 | -0.00034267
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 45 341080-342445(1) | OPEN LINE FROM BUS 341080 [2BECKTON 69.000] TO BUS 342445 [2W GLASGOW T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 46 341089-342500(1) | OPEN LINE FROM BUS 341089 [2BEKAERT 69.000] TO BUS 342500 [2WIELAND 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.2517e-06 | -0.00034684
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 46 341089-342500(1) | OPEN LINE FROM BUS 341089 [2BEKAERT 69.000] TO BUS 342500 [2WIELAND 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 47 341092-341095(1) | OPEN LINE FROM BUS 341092 [2BELLVIEW 69.000] TO BUS 341095 [2BELLVIEW T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 48 341095-341164(1) | OPEN LINE FROM BUS 341095 [2BELLVIEW T 69.000] TO BUS 341164 [2BOONE CO 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 49 341095-341227(1) | OPEN LINE FROM BUS 341095 [2BELLVIEW T 69.000] TO BUS 341227 [2BURLINGTN T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 50 341098-342433(1) | OPEN LINE FROM BUS 341098 [2BEREAKU T 69.000] TO BUS 342433 [2W BEREA J 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | -5.9605e-08 | -0.00034565
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 50 341098-342433(1) | OPEN LINE FROM BUS 341098 [2BEREAKU T 69.000] TO BUS 342433 [2W BEREA J 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 51 341104-341107(1) | OPEN LINE FROM BUS 341104 [2BIG BONE 69.000] TO BUS 341107 [2BIG BONE T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93988 | 64.8515 | 0.0002225 | -0.00012308
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 51 341104-341107(1) | OPEN LINE FROM BUS 341104 [2BIG BONE 69.000] TO BUS 341107 [2BIG BONE T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 52 341107-341164(1) | OPEN LINE FROM BUS 341107 [2BIG BONE T 69.000] TO BUS 341164 [2BOONE CO 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93989 | 64.8523 | 0.00023353 | -0.00011206
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 52 341107-341164(1) | OPEN LINE FROM BUS 341107 [2BIG BONE T 69.000] TO BUS 341164 [2BOONE CO 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 53 341107-341917(1) | OPEN LINE FROM BUS 341107 [2BIG BONE T 69.000] TO BUS 341917 [2MUNK 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93968 | 64.8376 | 2.0742e-05 | -0.00032485
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 53 341107-341917(1) | OPEN LINE FROM BUS 341107 [2BIG BONE T 69.000] TO BUS 341917 [2MUNK 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 54 341110-341113(1) | OPEN LINE FROM BUS 341110 [2BIG CREEK 69.000] TO BUS 341113 [2BIG CREEK T69.000] CKT 1 | 0.93965 | 64.8362 | 0.9397 | 64.8395 | 4.8697e-05 | -0.00029689
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 54 341110-341113(1) | OPEN LINE FROM BUS 341110 [2BIG CREEK 69.000] TO BUS 341113 [2BIG CREEK T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 55 341110-341439(1) | OPEN LINE FROM BUS 341110 [2BIG CREEK 69.000] TO BUS 341439 [2ELK MT IP 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93968 | 64.8379 | 2.5928e-05 | -0.00031966
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 55 341110-341439(1) | OPEN LINE FROM BUS 341110 [2BIG CREEK 69.000] TO BUS 341439 [2ELK MT IP 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 56 341113-341464(1) | OPEN LINE FROM BUS 341113 [2BIG CREEK T69.000] TO BUS 341464 [2FALL ROCK 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93971 | 64.8402 | 5.8591e-05 | -0.000287
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 56 341113-341464(1) | OPEN LINE FROM BUS 341113 [2BIG CREEK T69.000] TO BUS 341464 [2FALL ROCK 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 57 341113-342001(1) | OPEN LINE FROM BUS 341113 [2BIG CREEK T69.000] TO BUS 342001 [2ONEIDA 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.837 | 1.2577e-05 | -0.00033301
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 57 341113-342001(1) | OPEN LINE FROM BUS 341113 [2BIG CREEK T69.000] TO BUS 342001 [2ONEIDA 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 1.1921e-07 | 1.1921e-07
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 58 341114-341115(1) | OPEN LINE FROM BUS 341114 [2BIG HILL 69.000] TO BUS 341115 [2BIG HILL T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93969 | 64.8387 | 3.6657e-05 | -0.00030893
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 58 341114-341115(1) | OPEN LINE FROM BUS 341114 [2BIG HILL 69.000] TO BUS 341115 [2BIG HILL T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 59 341115-342223(1) | OPEN LINE FROM BUS 341115 [2BIG HILL T 69.000] TO BUS 342223 [2SAND GAP T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8359 | -4.0531e-06 | -0.00034964
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 59 341115-342223(1) | OPEN LINE FROM BUS 341115 [2BIG HILL T 69.000] TO BUS 342223 [2SAND GAP T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 60 341115-342346(1) | OPEN LINE FROM BUS 341115 [2BIG HILL T 69.000] TO BUS 342346 [2THREE LINKS69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 3.2783e-06 | -0.00034231
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 60 341115-342346(1) | OPEN LINE FROM BUS 341115 [2BIG HILL T 69.000] TO BUS 342346 [2THREE LINKS69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 61 341116-341119(1) | OPEN LINE FROM BUS 341116 [2BIG WOODS 69.000] TO BUS 341119 [2BIG WOODS J69.000] CKT 1 | 0.93965 | 64.8362 | 0.93979 | 64.8455 | 0.00013477 | -0.00021082
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 61 341116-341119(1) | OPEN LINE FROM BUS 341116 [2BIG WOODS 69.000] TO BUS 341119 [2BIG WOODS J69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 62 341119-341620(1) | OPEN LINE FROM BUS 341119 [2BIG WOODS J69.000] TO BUS 341620 [2HILDA 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93956 | 64.8299 | -9.1314e-05 | -0.0004369
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 62 341119-341620(1) | OPEN LINE FROM BUS 341119 [2BIG WOODS J69.000] TO BUS 341620 [2HILDA 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 63 341119-342088(1) | OPEN LINE FROM BUS 341119 [2BIG WOODS J69.000] TO BUS 342088 [2PLUMMR L T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93949 | 64.8247 | -0.00016552 | -0.00051111
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 63 341119-342088(1) | OPEN LINE FROM BUS 341119 [2BIG WOODS J69.000] TO BUS 342088 [2PLUMMR L T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 64 341122-341125(1) | OPEN LINE FROM BUS 341122 [2BILL WELL T69.000] TO BUS 341125 [2BILL WELLS 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93976 | 64.8436 | 0.00010818 | -0.00023741
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 64 341122-341125(1) | OPEN LINE FROM BUS 341122 [2BILL WELL T69.000] TO BUS 341125 [2BILL WELLS 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 1.1921e-07 | 1.1921e-07
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 65 341122-341692(1) | OPEN LINE FROM BUS 341122 [2BILL WELL T69.000] TO BUS 341692 [2JENNY WIL T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93949 | 64.8247 | -0.0001657 | -0.00051129
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 65 341122-341692(1) | OPEN LINE FROM BUS 341122 [2BILL WELL T69.000] TO BUS 341692 [2JENNY WIL T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 66 341122-341860(1) | OPEN LINE FROM BUS 341122 [2BILL WELL T69.000] TO BUS 341860 [2MIDDL CRK T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8366 | 6.9737e-06 | -0.00033861
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 66 341122-341860(1) | OPEN LINE FROM BUS 341122 [2BILL WELL T69.000] TO BUS 341860 [2MIDDL CRK T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 67 341131-341134(1) | OPEN LINE FROM BUS 341131 [2BLEVINS V T69.000] TO BUS 341134 [2BLEVINS VAL69.000] CKT 1 | 0.93965 | 64.8362 | 0.93938 | 64.8172 | -0.0002746 | -0.00062019
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 67 341131-341134(1) | OPEN LINE FROM BUS 341131 [2BLEVINS V T69.000] TO BUS 341134 [2BLEVINS VAL69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 69 341131-342112(1) | OPEN LINE FROM BUS 341131 [2BLEVINS V T69.000] TO BUS 342112 [2PRESTON T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93974 | 64.8419 | 8.291e-05 | -0.00026268
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 69 341131-342112(1) | OPEN LINE FROM BUS 341131 [2BLEVINS V T69.000] TO BUS 342112 [2PRESTON T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 70 341137-341296(1) | OPEN LINE FROM BUS 341137 [2BLOOMFLD 69.000] TO BUS 341296 [2CHAPLIN T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8365 | 4.2915e-06 | -0.0003413
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 70 341137-341296(1) | OPEN LINE FROM BUS 341137 [2BLOOMFLD 69.000] TO BUS 341296 [2CHAPLIN T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 71 341137-341935(1) | OPEN LINE FROM BUS 341137 [2BLOOMFLD 69.000] TO BUS 341935 [2N SPRINGFLD69.000] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8349 | -1.7822e-05 | -0.00036341
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 71 341137-341935(1) | OPEN LINE FROM BUS 341137 [2BLOOMFLD 69.000] TO BUS 341935 [2N SPRINGFLD69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 72 341140-341143(1) | OPEN LINE FROM BUS 341140 [2BLUE G PW 69.000] TO BUS 341143 [2BLUE G PW T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8365 | 4.3511e-06 | -0.00034124
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 72 341140-341143(1) | OPEN LINE FROM BUS 341140 [2BLUE G PW 69.000] TO BUS 341143 [2BLUE G PW T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 73 341143-342019(1) | OPEN LINE FROM BUS 341143 [2BLUE G PW T69.000] TO BUS 342019 [2OWENS IL J 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93963 | 64.8344 | -2.5868e-05 | -0.00037146
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 73 341143-342019(1) | OPEN LINE FROM BUS 341143 [2BLUE G PW T69.000] TO BUS 342019 [2OWENS IL J 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 74 341143-342508(1) | OPEN LINE FROM BUS 341143 [2BLUE G PW T69.000] TO BUS 342508 [2WOODLAWN 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8368 | 9.7752e-06 | -0.00033581
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 74 341143-342508(1) | OPEN LINE FROM BUS 341143 [2BLUE G PW T69.000] TO BUS 342508 [2WOODLAWN 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 75 341149-341272(1) | OPEN LINE FROM BUS 341149 [2BON AYR 69.000] TO BUS 341272 [2CAVE CITY 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 5.9605e-08 | -0.00034553
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 75 341149-341272(1) | OPEN LINE FROM BUS 341149 [2BON AYR 69.000] TO BUS 341272 [2CAVE CITY 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 76 341152-341155(1) | OPEN LINE FROM BUS 341152 [2BONANZA 69.000] TO BUS 341155 [2BONANZA T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93971 | 64.8401 | 5.7459e-05 | -0.00028813
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 76 341152-341155(1) | OPEN LINE FROM BUS 341152 [2BONANZA 69.000] TO BUS 341155 [2BONANZA T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 77 341155-341803(1) | OPEN LINE FROM BUS 341155 [2BONANZA T 69.000] TO BUS 341803 [2MAGOFFIN CO69.000] CKT 1 | 0.93965 | 64.8362 | 0.93993 | 64.8553 | 0.00027788 | -6.7711e-05
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 77 341155-341803(1) | OPEN LINE FROM BUS 341155 [2BONANZA T 69.000] TO BUS 341803 [2MAGOFFIN CO69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 78 341155-341860(1) | OPEN LINE FROM BUS 341155 [2BONANZA T 69.000] TO BUS 341860 [2MIDDL CRK T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93977 | 64.8441 | 0.0001145 | -0.00023109
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 78 341155-341860(1) | OPEN LINE FROM BUS 341155 [2BONANZA T 69.000] TO BUS 341860 [2MIDDL CRK T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 79 341158-341161(1) | OPEN LINE FROM BUS 341158 [2BONNIV DIST69.000] TO BUS 341161 [2BONNIV EK 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8357 | -6.8545e-06 | -0.00035244
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 79 341158-341161(1) | OPEN LINE FROM BUS 341158 [2BONNIV DIST69.000] TO BUS 341161 [2BONNIV EK 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 80 341158-341908(1) | OPEN LINE FROM BUS 341158 [2BONNIV DIST69.000] TO BUS 341908 [2MUNFVIL EK 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8357 | -6.0797e-06 | -0.00035167
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 80 341158-341908(1) | OPEN LINE FROM BUS 341158 [2BONNIV DIST69.000] TO BUS 341908 [2MUNFVIL EK 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 81 341161-342403(1) | OPEN LINE FROM BUS 341161 [2BONNIV EK 69.000] TO BUS 342403 [2UPTON T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8359 | -2.9802e-06 | -0.00034857
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 81 341161-342403(1) | OPEN LINE FROM BUS 341161 [2BONNIV EK 69.000] TO BUS 342403 [2UPTON T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 82 341164-341167(1) | OPEN LINE FROM BUS 341164 [2BOONE CO 69.000] TO BUS 341167 [2BOONE DIST 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 83 341164-342388(1) | OPEN LINE FROM BUS 341164 [2BOONE CO 69.000] TO BUS 342388 [2TURKEY FT J69.000] CKT 1 | 0.93965 | 64.8362 | 0.93991 | 64.8541 | 0.00025994 | -8.5652e-05
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 83 341164-342388(1) | OPEN LINE FROM BUS 341164 [2BOONE CO 69.000] TO BUS 342388 [2TURKEY FT J69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 84 341164-342466(1) | OPEN LINE FROM BUS 341164 [2BOONE CO 69.000] TO BUS 342466 [2W R SMOOT 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 85 341164-342559(1) | OPEN LINE FROM BUS 341164 [2BOONE CO 69.000] TO BUS 342559 [4BOONE CO 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 86 341170-341173(1) | OPEN LINE FROM BUS 341170 [2BOONEVIL 69.000] TO BUS 341173 [2BOONEVIL T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93968 | 64.8381 | 2.8849e-05 | -0.00031674
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 86 341170-341173(1) | OPEN LINE FROM BUS 341170 [2BOONEVIL 69.000] TO BUS 341173 [2BOONEVIL T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 87 341173-342196(1) | OPEN LINE FROM BUS 341173 [2BOONEVIL T 69.000] TO BUS 342196 [2WHITE OAK 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 3.3975e-06 | -0.00034219
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 87 341173-342196(1) | OPEN LINE FROM BUS 341173 [2BOONEVIL T 69.000] TO BUS 342196 [2WHITE OAK 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 88 341179-341746(1) | OPEN LINE FROM BUS 341179 [2BOSTONKU 69.000] TO BUS 341746 [2LEBANON J 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 2.9802e-07 | -0.00034529
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 88 341179-341746(1) | OPEN LINE FROM BUS 341179 [2BOSTONKU 69.000] TO BUS 341746 [2LEBANON J 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 89 341179-342514(1) | OPEN LINE FROM BUS 341179 [2BOSTONKU 69.000] TO BUS 342514 [2WOOSLEY 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 4.1723e-07 | -0.00034517
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 89 341179-342514(1) | OPEN LINE FROM BUS 341179 [2BOSTONKU 69.000] TO BUS 342514 [2WOOSLEY 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 90 341185-341614(1) | OPEN LINE FROM BUS 341185 [2BOWEN 69.000] TO BUS 341614 [2HIGH ROCK 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93954 | 64.8283 | -0.00011396 | -0.00045955
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 90 341185-341614(1) | OPEN LINE FROM BUS 341185 [2BOWEN 69.000] TO BUS 341614 [2HIGH ROCK 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 91 341185-342100(1) | OPEN LINE FROM BUS 341185 [2BOWEN 69.000] TO BUS 342100 [2POWELL CO 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93952 | 64.8266 | -0.00013864 | -0.00048423
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 91 341185-342100(1) | OPEN LINE FROM BUS 341185 [2BOWEN 69.000] TO BUS 342100 [2POWELL CO 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 92 341188-341488(1) | OPEN LINE FROM BUS 341188 [2BRACKEN CO 69.000] TO BUS 341488 [2FOUR OAKS T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 93 341188-341587(1) | OPEN LINE FROM BUS 341188 [2BRACKEN CO 69.000] TO BUS 341587 [2GRIFFIN J 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93511 | 64.5224 | -0.0045477 | -0.0048933
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 93 341188-341587(1) | OPEN LINE FROM BUS 341188 [2BRACKEN CO 69.000] TO BUS 341587 [2GRIFFIN J 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 94 341194-342385(1) | OPEN LINE FROM BUS 341194 [2BRISTOW 69.000] TO BUS 342385 [2TURKEY FT 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 95 341194-342388(1) | OPEN LINE FROM BUS 341194 [2BRISTOW 69.000] TO BUS 342388 [2TURKEY FT J69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 96 341197-341818(1) | OPEN LINE FROM BUS 341197 [2BRODHEAD 69.000] TO BUS 341818 [2MARETBURG T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93963 | 64.8343 | -2.7299e-05 | -0.00037289
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 96 341197-341818(1) | OPEN LINE FROM BUS 341197 [2BRODHEAD 69.000] TO BUS 341818 [2MARETBURG T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 97 341197-342349(1) | OPEN LINE FROM BUS 341197 [2BRODHEAD 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.93965 | 64.8362 | 0.93968 | 64.8376 | 2.0802e-05 | -0.00032479
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 97 341197-342349(1) | OPEN LINE FROM BUS 341197 [2BRODHEAD 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 98 341200-341920(1) | OPEN LINE FROM BUS 341200 [2BROMLEYEK 69.000] TO BUS 341920 [2MUNK J 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341200 | 2BROMLEYEK | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 99 341200-342010(1) | OPEN LINE FROM BUS 341200 [2BROMLEYEK 69.000] TO BUS 342010 [2OWEN CO J1 69.000] CKT 1 | 0.99203 | 68.4498 | 0.92118 | 63.5616 | -0.070844 | -0.018817
341917 | 2MUNK | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 99 341200-342010(1) | OPEN LINE FROM BUS 341200 [2BROMLEYEK 69.000] TO BUS 342010 [2OWEN CO J1 69.000] CKT 1 | 0.96446 | 66.5477 | 0.93678 | 64.6378 | -0.027679 | -0.0032203
341920 | 2MUNK J | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 99 341200-342010(1) | OPEN LINE FROM BUS 341200 [2BROMLEYEK 69.000] TO BUS 342010 [2OWEN CO J1 69.000] CKT 1 | 0.97761 | 67.4549 | 0.92594 | 63.8901 | -0.051664 | -0.014057
341998 | 2OAKLEY NOEL | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 99 341200-342010(1) | OPEN LINE FROM BUS 341200 [2BROMLEYEK 69.000] TO BUS 342010 [2OWEN CO J1 69.000] CKT 1 | 0.96812 | 66.8005 | 0.92965 | 64.1456 | -0.038478 | -0.010354
342502 | 2WILLIAMSTWN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 99 341200-342010(1) | OPEN LINE FROM BUS 341200 [2BROMLEYEK 69.000] TO BUS 342010 [2OWEN CO J1 69.000] CKT 1 | 0.97778 | 67.467 | 0.92546 | 63.857 | -0.052318 | -0.014536
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 99 341200-342010(1) | OPEN LINE FROM BUS 341200 [2BROMLEYEK 69.000] TO BUS 342010 [2OWEN CO J1 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 100 341203-341206(1) | OPEN LINE FROM BUS 341203 [2BRONSTON 69.000] TO BUS 341206 [2BRONSTON T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8372 | 1.5557e-05 | -0.00033003
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 100 341203-341206(1) | OPEN LINE FROM BUS 341203 [2BRONSTON 69.000] TO BUS 341206 [2BRONSTON T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 101 341206-341347(1) | OPEN LINE FROM BUS 341206 [2BRONSTON T 69.000] TO BUS 341347 [2COOPER DIST69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 3.0398e-06 | -0.00034255
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 101 341206-341347(1) | OPEN LINE FROM BUS 341206 [2BRONSTON T 69.000] TO BUS 341347 [2COOPER DIST69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 102 341206-341392(1) | OPEN LINE FROM BUS 341206 [2BRONSTON T 69.000] TO BUS 341392 [2DENNY 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8359 | -2.9802e-06 | -0.00034857
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 102 341206-341392(1) | OPEN LINE FROM BUS 341206 [2BRONSTON T 69.000] TO BUS 341392 [2DENNY 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 103 341209-341210(1) | OPEN LINE FROM BUS 341209 [2BROUGTWN T 69.000] TO BUS 341210 [2BROUGHT TWN69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 1.7881e-07 | -0.00034541
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 103 341209-341210(1) | OPEN LINE FROM BUS 341209 [2BROUGTWN T 69.000] TO BUS 341210 [2BROUGHT TWN69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 104 341209-341617(1) | OPEN LINE FROM BUS 341209 [2BROUGTWN T 69.000] TO BUS 341617 [2HIGHLAND EK69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.3709e-06 | -0.00034696
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 104 341209-341617(1) | OPEN LINE FROM BUS 341209 [2BROUGTWN T 69.000] TO BUS 341617 [2HIGHLAND EK69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 105 341209-342367(1) | OPEN LINE FROM BUS 341209 [2BROUGTWN T 69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -2.6226e-06 | -0.00034821
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 105 341209-342367(1) | OPEN LINE FROM BUS 341209 [2BROUGTWN T 69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341089 | 2BEKAERT | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 106 341212-341774(1) | OPEN LINE FROM BUS 341212 [2BUDD 69.000] TO BUS 341774 [2LOGAN 2 T 69.000] CKT 1 | 0.96341 | 66.4751 | 0.93179 | 64.2932 | -0.031622 | -0.0082148
341212 | 2BUDD | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 106 341212-341774(1) | OPEN LINE FROM BUS 341212 [2BUDD 69.000] TO BUS 341774 [2LOGAN 2 T 69.000] CKT 1 | 0.96804 | 66.7948 | 0.92522 | 63.8402 | -0.042821 | -0.01478
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 106 341212-341774(1) | OPEN LINE FROM BUS 341212 [2BUDD 69.000] TO BUS 341774 [2LOGAN 2 T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8351 | -1.5676e-05 | -0.00036126
342500 | 2WIELAND | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 106 341212-341774(1) | OPEN LINE FROM BUS 341212 [2BUDD 69.000] TO BUS 341774 [2LOGAN 2 T 69.000] CKT 1 | 0.96309 | 66.453 | 0.9261 | 63.901 | -0.036986 | -0.013898
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 106 341212-341774(1) | OPEN LINE FROM BUS 341212 [2BUDD 69.000] TO BUS 341774 [2LOGAN 2 T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341089 | 2BEKAERT | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 107 341212-342500(1) | OPEN LINE FROM BUS 341212 [2BUDD 69.000] TO BUS 342500 [2WIELAND 69.000] CKT 1 | 0.96341 | 66.4751 | 0.93683 | 64.6411 | -0.02658 | -0.003173
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 107 341212-342500(1) | OPEN LINE FROM BUS 341212 [2BUDD 69.000] TO BUS 342500 [2WIELAND 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8353 | -1.2279e-05 | -0.00035787
342500 | 2WIELAND | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 107 341212-342500(1) | OPEN LINE FROM BUS 341212 [2BUDD 69.000] TO BUS 342500 [2WIELAND 69.000] CKT 1 | 0.96309 | 66.453 | 0.93196 | 64.305 | -0.031131 | -0.0080435
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 107 341212-342500(1) | OPEN LINE FROM BUS 341212 [2BUDD 69.000] TO BUS 342500 [2WIELAND 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 108 341215-341281(1) | OPEN LINE FROM BUS 341215 [2BULLITT CO 69.000] TO BUS 341281 [2CEDAR GR 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8354 | -1.1384e-05 | -0.00035697
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 108 341215-341281(1) | OPEN LINE FROM BUS 341215 [2BULLITT CO 69.000] TO BUS 341281 [2CEDAR GR 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 109 341215-341389(1) | OPEN LINE FROM BUS 341215 [2BULLITT CO 69.000] TO BUS 341389 [2DEATSVILL T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8356 | -7.6294e-06 | -0.00035322
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 109 341215-341389(1) | OPEN LINE FROM BUS 341215 [2BULLITT CO 69.000] TO BUS 341389 [2DEATSVILL T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 110 341215-342700(1) | OPEN LINE FROM BUS 341215 [2BULLITT CO 69.000] TO BUS 342700 [5BULLITT CO 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93961 | 64.8333 | -4.1842e-05 | -0.00038743
342082 | 2PLEAS GRV | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 110 341215-342700(1) | OPEN LINE FROM BUS 341215 [2BULLITT CO 69.000] TO BUS 342700 [5BULLITT CO 161.00] CKT 1 | 0.97663 | 67.3872 | 0.93562 | 64.558 | -0.041004 | -0.0043775
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 110 341215-342700(1) | OPEN LINE FROM BUS 341215 [2BULLITT CO 69.000] TO BUS 342700 [5BULLITT CO 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 111 341218-341227(1) | OPEN LINE FROM BUS 341218 [2BULLITTSVIL69.000] TO BUS 341227 [2BURLINGTN T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93937 | 64.8165 | -0.00028425 | -0.00062984
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 111 341218-341227(1) | OPEN LINE FROM BUS 341218 [2BULLITTSVIL69.000] TO BUS 341227 [2BURLINGTN T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 112 341218-341605(1) | OPEN LINE FROM BUS 341218 [2BULLITTSVIL69.000] TO BUS 341605 [2HEBRON 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 113 341224-341227(1) | OPEN LINE FROM BUS 341224 [2BURLINGTN 69.000] TO BUS 341227 [2BURLINGTN T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341029 | 2ASAHI M W | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 114 341233-341974(1) | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 341974 [2NORWOOD T 69.000] CKT 1 | 0.96833 | 66.8145 | 0.93652 | 64.6199 | -0.031806 | -0.0034798
341032 | 2ASAHI M W T | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 114 341233-341974(1) | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 341974 [2NORWOOD T 69.000] CKT 1 | 0.96914 | 66.8708 | 0.93736 | 64.678 | -0.031779 | -0.0026374
341379 | 2DAHL ROAD | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 114 341233-341974(1) | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 341974 [2NORWOOD T 69.000] CKT 1 | 0.96945 | 66.8919 | 0.93713 | 64.6618 | -0.03232 | -0.0028719
341422 | 2E SOMERSET | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 114 341233-341974(1) | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 341974 [2NORWOOD T 69.000] CKT 1 | 0.97448 | 67.2393 | 0.93974 | 64.8418 | -0.034746 | -0.00026441
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 114 341233-341974(1) | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 341974 [2NORWOOD T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93959 | 64.8318 | -6.3062e-05 | -0.00040865
341974 | 2NORWOOD T | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 114 341233-341974(1) | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 341974 [2NORWOOD T 69.000] CKT 1 | 0.97652 | 67.3799 | 0.93913 | 64.7997 | -0.037394 | -0.00087363
342256 | 2SHOPVILLE | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 114 341233-341974(1) | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 341974 [2NORWOOD T 69.000] CKT 1 | 0.97027 | 66.9485 | 0.93751 | 64.6879 | -0.032763 | -0.0024944
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 114 341233-341974(1) | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 341974 [2NORWOOD T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341029 | 2ASAHI M W | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 115 341233-342286(1) | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.96833 | 66.8145 | 0.9337 | 64.4254 | -0.034626 | -0.0062988
341032 | 2ASAHI M W T | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 115 341233-342286(1) | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.96914 | 66.8708 | 0.93455 | 64.4837 | -0.034595 | -0.0054534
341233 | 2CABIN HOLLW | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 115 341233-342286(1) | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.98348 | 67.8604 | 0.9295 | 64.1353 | -0.053987 | -0.010503
341379 | 2DAHL ROAD | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 115 341233-342286(1) | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.96945 | 66.8919 | 0.93398 | 64.4443 | -0.035473 | -0.0060245
341419 | 2E SOMERSE T | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 115 341233-342286(1) | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.97487 | 67.2661 | 0.93409 | 64.4523 | -0.04078 | -0.0059091
341422 | 2E SOMERSET | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 115 341233-342286(1) | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.97448 | 67.2393 | 0.93369 | 64.4243 | -0.040797 | -0.0063149
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 115 341233-342286(1) | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93972 | 64.8405 | 6.2704e-05 | -0.00028288
341947 | 2NELSON VAL | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 115 341233-342286(1) | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.97354 | 67.1742 | 0.93927 | 64.8093 | -0.034273 | -0.00073463
341974 | 2NORWOOD T | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 115 341233-342286(1) | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.97652 | 67.3799 | 0.93238 | 64.334 | -0.044143 | -0.007623
342256 | 2SHOPVILLE | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 115 341233-342286(1) | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.97027 | 66.9485 | 0.9341 | 64.4526 | -0.036174 | -0.0059049
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 115 341233-342286(1) | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 116 341248-341608(1) | OPEN LINE FROM BUS 341248 [2CAMPTON 69.000] TO BUS 341608 [2HELECHAW 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93953 | 64.8273 | -0.00012761 | -0.0004732
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 116 341248-341608(1) | OPEN LINE FROM BUS 341248 [2CAMPTON 69.000] TO BUS 341608 [2HELECHAW 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 117 341248-342520(1) | OPEN LINE FROM BUS 341248 [2CAMPTON 69.000] TO BUS 342520 [2ZACHARIAH 69.000] CKT 1 | 0.93965 | 64.8362 | 0.9395 | 64.8256 | -0.00015283 | -0.00049841
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 117 341248-342520(1) | OPEN LINE FROM BUS 341248 [2CAMPTON 69.000] TO BUS 342520 [2ZACHARIAH 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 118 341251-341254(1) | OPEN LINE FROM BUS 341251 [2CANE RIDG 69.000] TO BUS 341254 [2CANE RIDG T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93968 | 64.8378 | 2.3425e-05 | -0.00032216
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 118 341251-341254(1) | OPEN LINE FROM BUS 341251 [2CANE RIDG 69.000] TO BUS 341254 [2CANE RIDG T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 119 341254-341872(1) | OPEN LINE FROM BUS 341254 [2CANE RIDG T69.000] TO BUS 341872 [2MILLB-CRL J69.000] CKT 1 | 0.93965 | 64.8362 | 0.9396 | 64.8324 | -5.4002e-05 | -0.00039959
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 119 341254-341872(1) | OPEN LINE FROM BUS 341254 [2CANE RIDG T69.000] TO BUS 341872 [2MILLB-CRL J69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 120 341254-342259(1) | OPEN LINE FROM BUS 341254 [2CANE RIDG T69.000] TO BUS 342259 [2SIDEVIEW 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93959 | 64.832 | -6.032e-05 | -0.00040591
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 120 341254-342259(1) | OPEN LINE FROM BUS 341254 [2CANE RIDG T69.000] TO BUS 342259 [2SIDEVIEW 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 121 341260-342013(1) | OPEN LINE FROM BUS 341260 [2CARSON 69.000] TO BUS 342013 [2OWEN CO J2 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93971 | 64.8397 | 5.1975e-05 | -0.00029361
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 121 341260-342013(1) | OPEN LINE FROM BUS 341260 [2CARSON 69.000] TO BUS 342013 [2OWEN CO J2 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 122 341263-341266(1) | OPEN LINE FROM BUS 341263 [2CARTER CTY 69.000] TO BUS 341266 [2CARTER CY T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93968 | 64.8378 | 2.3842e-05 | -0.00032175
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 122 341263-341266(1) | OPEN LINE FROM BUS 341263 [2CARTER CTY 69.000] TO BUS 341266 [2CARTER CY T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 1.1921e-07 | 1.1921e-07
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 123 341266-342034(1) | OPEN LINE FROM BUS 341266 [2CARTER CY T69.000] TO BUS 342034 [2PACTOLUS T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93954 | 64.8286 | -0.00010949 | -0.00045508
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 123 341266-342034(1) | OPEN LINE FROM BUS 341266 [2CARTER CY T69.000] TO BUS 342034 [2PACTOLUS T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 124 341266-342475(1) | OPEN LINE FROM BUS 341266 [2CARTER CY T69.000] TO BUS 342475 [2WARNOCK 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93948 | 64.8238 | -0.00017893 | -0.00052452
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 124 341266-342475(1) | OPEN LINE FROM BUS 341266 [2CARTER CY T69.000] TO BUS 342475 [2WARNOCK 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 125 341269-342064(1) | OPEN LINE FROM BUS 341269 [2CASEY CO 69.000] TO BUS 342064 [2PEYTONS ST 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8358 | -4.5896e-06 | -0.00035018
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 125 341269-342064(1) | OPEN LINE FROM BUS 341269 [2CASEY CO 69.000] TO BUS 342064 [2PEYTONS ST 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 126 341269-342703(1) | OPEN LINE FROM BUS 341269 [2CASEY CO 69.000] TO BUS 342703 [5CASEY CO 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8357 | -6.9737e-06 | -0.00035256
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 126 341269-342703(1) | OPEN LINE FROM BUS 341269 [2CASEY CO 69.000] TO BUS 342703 [5CASEY CO 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 127 341272-341275(1) | OPEN LINE FROM BUS 341272 [2CAVE CITY 69.000] TO BUS 341275 [2CAVE CITY J69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 2.3246e-06 | -0.00034326
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 127 341272-341275(1) | OPEN LINE FROM BUS 341272 [2CAVE CITY 69.000] TO BUS 341275 [2CAVE CITY J69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 128 341275-342241(1) | OPEN LINE FROM BUS 341275 [2CAVE CITY J69.000] TO BUS 342241 [2SEYMOUR T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -7.7486e-07 | -0.00034636
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 128 341275-342241(1) | OPEN LINE FROM BUS 341275 [2CAVE CITY J69.000] TO BUS 342241 [2SEYMOUR T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 129 341281-342082(1) | OPEN LINE FROM BUS 341281 [2CEDAR GR 69.000] TO BUS 342082 [2PLEAS GRV 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8356 | -8.1062e-06 | -0.00035369
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 129 341281-342082(1) | OPEN LINE FROM BUS 341281 [2CEDAR GR 69.000] TO BUS 342082 [2PLEAS GRV 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 130 341287-341713(1) | OPEN LINE FROM BUS 341287 [2CENT HARDIN69.000] TO BUS 341713 [2KARGLE 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -8.3447e-07 | -0.00034642
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 130 341287-341713(1) | OPEN LINE FROM BUS 341287 [2CENT HARDIN69.000] TO BUS 341713 [2KARGLE 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 131 341287-342307(1) | OPEN LINE FROM BUS 341287 [2CENT HARDIN69.000] TO BUS 342307 [2STEPHENSBRG69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 3.5763e-07 | -0.00034523
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 131 341287-342307(1) | OPEN LINE FROM BUS 341287 [2CENT HARDIN69.000] TO BUS 342307 [2STEPHENSBRG69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 132 341287-342568(1) | OPEN LINE FROM BUS 341287 [2CENT HARDIN69.000] TO BUS 342568 [4CENT HARDIN138.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8356 | -7.5698e-06 | -0.00035316
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 132 341287-342568(1) | OPEN LINE FROM BUS 341287 [2CENT HARDIN69.000] TO BUS 342568 [4CENT HARDIN138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 133 341293-341296(1) | OPEN LINE FROM BUS 341293 [2CHAPLIN 69.000] TO BUS 341296 [2CHAPLIN T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 2.9802e-06 | -0.00034261
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 133 341293-341296(1) | OPEN LINE FROM BUS 341293 [2CHAPLIN 69.000] TO BUS 341296 [2CHAPLIN T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 134 341296-342262(1) | OPEN LINE FROM BUS 341296 [2CHAPLIN T 69.000] TO BUS 342262 [2SINAI 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8366 | 5.9605e-06 | -0.00033963
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 134 341296-342262(1) | OPEN LINE FROM BUS 341296 [2CHAPLIN T 69.000] TO BUS 342262 [2SINAI 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 135 341299-341989(1) | OPEN LINE FROM BUS 341299 [2CHARTERS 69.000] TO BUS 341989 [2OAK RIDGE T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93935 | 64.8155 | -0.00029951 | -0.0006451
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 135 341299-341989(1) | OPEN LINE FROM BUS 341299 [2CHARTERS 69.000] TO BUS 341989 [2OAK RIDGE T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 136 341299-342124(1) | OPEN LINE FROM BUS 341299 [2CHARTERS 69.000] TO BUS 342124 [2RECTORVILLE69.000] CKT 1 | 0.93965 | 64.8362 | 0.93933 | 64.8138 | -0.00032401 | -0.0006696
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 136 341299-342124(1) | OPEN LINE FROM BUS 341299 [2CHARTERS 69.000] TO BUS 342124 [2RECTORVILLE69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 137 341302-341305(1) | OPEN LINE FROM BUS 341302 [2CLAY CITY 69.000] TO BUS 341305 [2CLAY CITY T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93978 | 64.8451 | 0.00012952 | -0.00021607
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 137 341302-341305(1) | OPEN LINE FROM BUS 341302 [2CLAY CITY 69.000] TO BUS 341305 [2CLAY CITY T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 138 341305-341593(1) | OPEN LINE FROM BUS 341305 [2CLAY CITY T69.000] TO BUS 341593 [2HARDWCRK T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8353 | -1.2159e-05 | -0.00035775
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 138 341305-341593(1) | OPEN LINE FROM BUS 341305 [2CLAY CITY T69.000] TO BUS 341593 [2HARDWCRK T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 139 341305-341599(1) | OPEN LINE FROM BUS 341305 [2CLAY CITY T69.000] TO BUS 341599 [2HARGETT T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93974 | 64.8418 | 8.2195e-05 | -0.00026339
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 139 341305-341599(1) | OPEN LINE FROM BUS 341305 [2CLAY CITY T69.000] TO BUS 341599 [2HARGETT T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 140 341308-341314(1) | OPEN LINE FROM BUS 341308 [2CLAY LCK 69.000] TO BUS 341314 [2CLAY LCK SW69.000] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8373 | 1.6212e-05 | -0.00032938
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 140 341308-341314(1) | OPEN LINE FROM BUS 341308 [2CLAY LCK 69.000] TO BUS 341314 [2CLAY LCK SW69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 141 341311-341314(1) | OPEN LINE FROM BUS 341311 [2CLAY LCK J 69.000] TO BUS 341314 [2CLAY LCK SW69.000] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8373 | 1.6034e-05 | -0.00032955
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 141 341311-341314(1) | OPEN LINE FROM BUS 341311 [2CLAY LCK J 69.000] TO BUS 341314 [2CLAY LCK SW69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 142 341311-342184(1) | OPEN LINE FROM BUS 341311 [2CLAY LCK J 69.000] TO BUS 342184 [2S ANDERSON 69.000] CKT 1 | 0.93965 | 64.8362 | 0.9396 | 64.8327 | -4.9531e-05 | -0.00039512
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 142 341311-342184(1) | OPEN LINE FROM BUS 341311 [2CLAY LCK J 69.000] TO BUS 342184 [2S ANDERSON 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 143 341311-342406(1) | OPEN LINE FROM BUS 341311 [2CLAY LCK J 69.000] TO BUS 342406 [2VAN ARSDELL69.000] CKT 1 | 0.93965 | 64.8362 | 0.93963 | 64.8343 | -2.7537e-05 | -0.00037313
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 143 341311-342406(1) | OPEN LINE FROM BUS 341311 [2CLAY LCK J 69.000] TO BUS 342406 [2VAN ARSDELL69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 144 341317-341390(1) | OPEN LINE FROM BUS 341317 [2CLAY VILLAG69.000] TO BUS 341390 [2DEFOE TAP 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93963 | 64.8345 | -2.3961e-05 | -0.00036955
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 144 341317-341390(1) | OPEN LINE FROM BUS 341317 [2CLAY VILLAG69.000] TO BUS 341390 [2DEFOE TAP 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 145 341320-341512(1) | OPEN LINE FROM BUS 341320 [2COBURG 69.000] TO BUS 341512 [2GARLIN T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -2.3842e-06 | -0.00034797
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 145 341320-341512(1) | OPEN LINE FROM BUS 341320 [2COBURG 69.000] TO BUS 341512 [2GARLIN T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 146 341323-341335(1) | OPEN LINE FROM BUS 341323 [2COBURG J 69.000] TO BUS 341335 [2COLUMBIA 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8365 | 5.1856e-06 | -0.0003404
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 146 341323-341335(1) | OPEN LINE FROM BUS 341323 [2COBURG J 69.000] TO BUS 341335 [2COLUMBIA 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 147 341323-341512(1) | OPEN LINE FROM BUS 341323 [2COBURG J 69.000] TO BUS 341512 [2GARLIN T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 9.5367e-07 | -0.00034463
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 147 341323-341512(1) | OPEN LINE FROM BUS 341323 [2COBURG J 69.000] TO BUS 341512 [2GARLIN T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 148 341323-342235(1) | OPEN LINE FROM BUS 341323 [2COBURG J 69.000] TO BUS 342235 [2SEWELTN J 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8366 | 6.1393e-06 | -0.00033945
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 148 341323-342235(1) | OPEN LINE FROM BUS 341323 [2COBURG J 69.000] TO BUS 342235 [2SEWELTN J 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 149 341326-341488(1) | OPEN LINE FROM BUS 341326 [2COLEMANSVIL69.000] TO BUS 341488 [2FOUR OAKS T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 150 341326-342133(1) | OPEN LINE FROM BUS 341326 [2COLEMANSVIL69.000] TO BUS 342133 [2RENAKER 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 151 341329-341332(1) | OPEN LINE FROM BUS 341329 [2COLESBURG 69.000] TO BUS 341332 [2COLESBURG J69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -5.9605e-07 | -0.00034618
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 151 341329-341332(1) | OPEN LINE FROM BUS 341329 [2COLESBURG 69.000] TO BUS 341332 [2COLESBURG J69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 152 341332-341944(1) | OPEN LINE FROM BUS 341332 [2COLESBURG J69.000] TO BUS 341944 [2NELSON CO 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 3.6955e-06 | -0.00034189
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 152 341332-341944(1) | OPEN LINE FROM BUS 341332 [2COLESBURG J69.000] TO BUS 341944 [2NELSON CO 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 153 341332-342155(1) | OPEN LINE FROM BUS 341332 [2COLESBURG J69.000] TO BUS 342155 [2ROANOKE T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 3.2783e-06 | -0.00034231
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 153 341332-342155(1) | OPEN LINE FROM BUS 341332 [2COLESBURG J69.000] TO BUS 342155 [2ROANOKE T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 154 341335-341370(1) | OPEN LINE FROM BUS 341335 [2COLUMBIA 69.000] TO BUS 341370 [2COLUMB S KU69.000] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.837 | 1.1623e-05 | -0.00033396
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 154 341335-341370(1) | OPEN LINE FROM BUS 341335 [2COLUMBIA 69.000] TO BUS 341370 [2COLUMB S KU69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 155 341335-342436(1) | OPEN LINE FROM BUS 341335 [2COLUMBIA 69.000] TO BUS 342436 [2W COLUMBI T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8358 | -4.9472e-06 | -0.00035053
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 155 341335-342436(1) | OPEN LINE FROM BUS 341335 [2COLUMBIA 69.000] TO BUS 342436 [2W COLUMBI T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 156 341338-341341(1) | OPEN LINE FROM BUS 341338 [2CONWAY 69.000] TO BUS 341341 [2CONWAY T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93968 | 64.8381 | 2.8253e-05 | -0.00031734
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 156 341338-341341(1) | OPEN LINE FROM BUS 341338 [2CONWAY 69.000] TO BUS 341341 [2CONWAY T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 157 341341-342346(1) | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342346 [2THREE LINKS69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 2.861e-06 | -0.00034273
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 157 341341-342346(1) | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342346 [2THREE LINKS69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 158 341341-342349(1) | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 3.2187e-06 | -0.00034237
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 158 341341-342349(1) | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 159 341342-341343(1) | OPEN LINE FROM BUS 341342 [2CONTOWN T 69.000] TO BUS 341343 [2CONTOWN 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 4.7684e-07 | -0.00034511
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 159 341342-341343(1) | OPEN LINE FROM BUS 341342 [2CONTOWN T 69.000] TO BUS 341343 [2CONTOWN 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 160 341342-341761(1) | OPEN LINE FROM BUS 341342 [2CONTOWN T 69.000] TO BUS 341761 [2LIBERTY J 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8354 | -1.0252e-05 | -0.00035584
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 160 341342-341761(1) | OPEN LINE FROM BUS 341342 [2CONTOWN T 69.000] TO BUS 341761 [2LIBERTY J 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 161 341342-342067(1) | OPEN LINE FROM BUS 341342 [2CONTOWN T 69.000] TO BUS 342067 [2PHIL 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8356 | -7.8678e-06 | -0.00035346
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 161 341342-342067(1) | OPEN LINE FROM BUS 341342 [2CONTOWN T 69.000] TO BUS 342067 [2PHIL 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 162 341344-341347(1) | OPEN LINE FROM BUS 341344 [2COOPER 69.000] TO BUS 341347 [2COOPER DIST69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 3.3975e-06 | -0.00034219
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 162 341344-341347(1) | OPEN LINE FROM BUS 341344 [2COOPER 69.000] TO BUS 341347 [2COOPER DIST69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 163 341344-342286(1) | OPEN LINE FROM BUS 341344 [2COOPER 69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -2.2054e-06 | -0.00034779
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 163 341344-342286(1) | OPEN LINE FROM BUS 341344 [2COOPER 69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 164 341344-342286(2) | OPEN LINE FROM BUS 341344 [2COOPER 69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 2 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -2.2054e-06 | -0.00034779
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 164 341344-342286(2) | OPEN LINE FROM BUS 341344 [2COOPER 69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 2 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 165 341344-342715(1) | OPEN LINE FROM BUS 341344 [2COOPER 69.000] TO BUS 342715 [5COOPER1 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8356 | -8.3447e-06 | -0.00035393
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 165 341344-342715(1) | OPEN LINE FROM BUS 341344 [2COOPER 69.000] TO BUS 342715 [5COOPER1 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 166 341350-342067(1) | OPEN LINE FROM BUS 341350 [2CRESTON 69.000] TO BUS 342067 [2PHIL 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 2.2054e-06 | -0.00034338
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 166 341350-342067(1) | OPEN LINE FROM BUS 341350 [2CRESTON 69.000] TO BUS 342067 [2PHIL 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 167 341353-341356(1) | OPEN LINE FROM BUS 341353 [2CROCKETT 69.000] TO BUS 341356 [2CROCKETT T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93975 | 64.8424 | 9.0659e-05 | -0.00025493
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 167 341353-341356(1) | OPEN LINE FROM BUS 341353 [2CROCKETT 69.000] TO BUS 341356 [2CROCKETT T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 168 341356-341653(1) | OPEN LINE FROM BUS 341356 [2CROCKETT T 69.000] TO BUS 341653 [2HOT MIX R T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8359 | -3.159e-06 | -0.00034875
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 168 341356-341653(1) | OPEN LINE FROM BUS 341356 [2CROCKETT T 69.000] TO BUS 341653 [2HOT MIX R T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 169 341356-342265(1) | OPEN LINE FROM BUS 341356 [2CROCKETT T 69.000] TO BUS 342265 [2SKAGGS 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8355 | -1.0073e-05 | -0.00035566
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 169 341356-342265(1) | OPEN LINE FROM BUS 341356 [2CROCKETT T 69.000] TO BUS 342265 [2SKAGGS 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 170 341359-341362(1) | OPEN LINE FROM BUS 341359 [2CROOKSVIL 69.000] TO BUS 341362 [2CROOKSVIL T69.000] CKT 1 | 0.93965 | 64.8362 | 0.9397 | 64.8394 | 4.673e-05 | -0.00029886
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 171 341359-342288(1) | OPEN LINE FROM BUS 341359 [2CROOKSVIL 69.000] TO BUS 342288 [2SPEEDWELL 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8365 | 4.4703e-06 | -0.00034112
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 171 341359-342288(1) | OPEN LINE FROM BUS 341359 [2CROOKSVIL 69.000] TO BUS 342288 [2SPEEDWELL 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 172 341362-341406(1) | OPEN LINE FROM BUS 341362 [2CROOKSVIL T69.000] TO BUS 341406 [2DUNCAN LN T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 173 341362-341611(1) | OPEN LINE FROM BUS 341362 [2CROOKSVIL T69.000] TO BUS 341611 [2HICKORY PL 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93993 | 64.8553 | 0.00027817 | -6.7413e-05
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 173 341362-341611(1) | OPEN LINE FROM BUS 341362 [2CROOKSVIL T69.000] TO BUS 341611 [2HICKORY PL 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 174 341366-341370(1) | OPEN LINE FROM BUS 341366 [2COLUMB KU 69.000] TO BUS 341370 [2COLUMB S KU69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8366 | 6.0201e-06 | -0.00033957
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 174 341366-341370(1) | OPEN LINE FROM BUS 341366 [2COLUMB KU 69.000] TO BUS 341370 [2COLUMB S KU69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 175 341377-341602(1) | OPEN LINE FROM BUS 341377 [2CYNTHIA TIE69.000] TO BUS 341602 [2HEADQTRS 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 176 341377-342355(1) | OPEN LINE FROM BUS 341377 [2CYNTHIA TIE69.000] TO BUS 342355 [2THREE M T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341029 | 2ASAHI M W | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 177 341379-342256(1) | OPEN LINE FROM BUS 341379 [2DAHL ROAD 69.000] TO BUS 342256 [2SHOPVILLE 69.000] CKT 1 | 0.96833 | 66.8145 | 0.9308 | 64.2255 | -0.037523 | -0.0091963
341032 | 2ASAHI M W T | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 177 341379-342256(1) | OPEN LINE FROM BUS 341379 [2DAHL ROAD 69.000] TO BUS 342256 [2SHOPVILLE 69.000] CKT 1 | 0.96914 | 66.8708 | 0.93165 | 64.284 | -0.03749 | -0.0083484
341379 | 2DAHL ROAD | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 177 341379-342256(1) | OPEN LINE FROM BUS 341379 [2DAHL ROAD 69.000] TO BUS 342256 [2SHOPVILLE 69.000] CKT 1 | 0.96945 | 66.8919 | 0.9309 | 64.2324 | -0.038543 | -0.0090951
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 177 341379-342256(1) | OPEN LINE FROM BUS 341379 [2DAHL ROAD 69.000] TO BUS 342256 [2SHOPVILLE 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93959 | 64.8318 | -6.33e-05 | -0.00040889
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 177 341379-342256(1) | OPEN LINE FROM BUS 341379 [2DAHL ROAD 69.000] TO BUS 342256 [2SHOPVILLE 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 178 341380-341959(1) | OPEN LINE FROM BUS 341380 [2DALE 69.000] TO BUS 341959 [2NEWBY 1 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93971 | 64.8399 | 5.3942e-05 | -0.00029165
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 178 341380-341959(1) | OPEN LINE FROM BUS 341380 [2DALE 69.000] TO BUS 341959 [2NEWBY 1 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 179 341380-341962(1) | OPEN LINE FROM BUS 341380 [2DALE 69.000] TO BUS 341962 [2NEWBY 2 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8356 | -8.1062e-06 | -0.00035369
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 179 341380-341962(1) | OPEN LINE FROM BUS 341380 [2DALE 69.000] TO BUS 341962 [2NEWBY 2 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 180 341380-342574(1) | OPEN LINE FROM BUS 341380 [2DALE 69.000] TO BUS 342574 [4DALE 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93969 | 64.8384 | 3.2842e-05 | -0.00031275
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 180 341380-342574(1) | OPEN LINE FROM BUS 341380 [2DALE 69.000] TO BUS 342574 [4DALE 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 181 341381-341382(1) | OPEN LINE FROM BUS 341381 [2DAV LANE 69.000] TO BUS 341382 [2DAV LANE T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93973 | 64.8411 | 7.1466e-05 | -0.00027412
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 181 341381-341382(1) | OPEN LINE FROM BUS 341381 [2DAV LANE 69.000] TO BUS 341382 [2DAV LANE T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341381 | 2DAV LANE | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 182 341382-341734(1) | OPEN LINE FROM BUS 341382 [2DAV LANE T 69.000] TO BUS 341734 [2LAUR C IP T69.000] CKT 1 | 0.96406 | 66.5204 | 0.93735 | 64.677 | -0.026715 | -0.0026515
341382 | 2DAV LANE T | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 182 341382-341734(1) | OPEN LINE FROM BUS 341382 [2DAV LANE T 69.000] TO BUS 341734 [2LAUR C IP T69.000] CKT 1 | 0.96451 | 66.5509 | 0.9378 | 64.7085 | -0.026702 | -0.002196
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 182 341382-341734(1) | OPEN LINE FROM BUS 341382 [2DAV LANE T 69.000] TO BUS 341734 [2LAUR C IP T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8373 | 1.6928e-05 | -0.00032866
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 182 341382-341734(1) | OPEN LINE FROM BUS 341382 [2DAV LANE T 69.000] TO BUS 341734 [2LAUR C IP T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 183 341382-342451(1) | OPEN LINE FROM BUS 341382 [2DAV LANE T 69.000] TO BUS 342451 [2W LONDON 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 8.3447e-07 | -0.00034475
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 183 341382-342451(1) | OPEN LINE FROM BUS 341382 [2DAV LANE T 69.000] TO BUS 342451 [2W LONDON 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 184 341383-341467(1) | OPEN LINE FROM BUS 341383 [2DAVIS 69.000] TO BUS 341467 [2FAYETTE 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93985 | 64.8496 | 0.00019425 | -0.00015134
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 184 341383-341467(1) | OPEN LINE FROM BUS 341383 [2DAVIS 69.000] TO BUS 341467 [2FAYETTE 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 185 341383-341965(1) | OPEN LINE FROM BUS 341383 [2DAVIS 69.000] TO BUS 341965 [2NICHOLASVIL69.000] CKT 1 | 0.93965 | 64.8362 | 0.93982 | 64.8473 | 0.00016123 | -0.00018436
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 185 341383-341965(1) | OPEN LINE FROM BUS 341383 [2DAVIS 69.000] TO BUS 341965 [2NICHOLASVIL69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 186 341386-341389(1) | OPEN LINE FROM BUS 341386 [2DEATSVIL 69.000] TO BUS 341389 [2DEATSVILL T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -1.8477e-06 | -0.00034744
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 186 341386-341389(1) | OPEN LINE FROM BUS 341386 [2DEATSVIL 69.000] TO BUS 341389 [2DEATSVILL T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 187 341389-341707(1) | OPEN LINE FROM BUS 341389 [2DEATSVILL T69.000] TO BUS 341707 [2JOE TICH T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8359 | -4.0531e-06 | -0.00034964
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 187 341389-341707(1) | OPEN LINE FROM BUS 341389 [2DEATSVILL T69.000] TO BUS 341707 [2JOE TICH T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 188 341390-341391(1) | OPEN LINE FROM BUS 341390 [2DEFOE TAP 69.000] TO BUS 341391 [2DEFOE 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93968 | 64.8378 | 2.4557e-05 | -0.00032103
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 188 341390-341391(1) | OPEN LINE FROM BUS 341390 [2DEFOE TAP 69.000] TO BUS 341391 [2DEFOE 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 189 341390-341950(1) | OPEN LINE FROM BUS 341390 [2DEFOE TAP 69.000] TO BUS 341950 [2NEW CASTLE 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8372 | 1.4484e-05 | -0.0003311
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 189 341390-341950(1) | OPEN LINE FROM BUS 341390 [2DEFOE TAP 69.000] TO BUS 341950 [2NEW CASTLE 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 190 341392-341578(1) | OPEN LINE FROM BUS 341392 [2DENNY 69.000] TO BUS 341578 [2GREGORY R T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.837 | 1.2279e-05 | -0.00033331
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 190 341392-341578(1) | OPEN LINE FROM BUS 341392 [2DENNY 69.000] TO BUS 341578 [2GREGORY R T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 191 341392-342499(1) | OPEN LINE FROM BUS 341392 [2DENNY 69.000] TO BUS 342499 [2WIBORG T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | -5.9605e-08 | -0.00034565
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 191 341392-342499(1) | OPEN LINE FROM BUS 341392 [2DENNY 69.000] TO BUS 342499 [2WIBORG T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 192 341392-342727(1) | OPEN LINE FROM BUS 341392 [2DENNY 69.000] TO BUS 342727 [5DENNY 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93971 | 64.8401 | 5.6982e-05 | -0.00028861
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 192 341392-342727(1) | OPEN LINE FROM BUS 341392 [2DENNY 69.000] TO BUS 342727 [5DENNY 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 193 341394-341479(1) | OPEN LINE FROM BUS 341394 [2PATRIOT PW 69.000] TO BUS 341479 [2S BOUND RD 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -2.563e-06 | -0.00034815
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 193 341394-341479(1) | OPEN LINE FROM BUS 341394 [2PATRIOT PW 69.000] TO BUS 341479 [2S BOUND RD 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 194 341394-342151(1) | OPEN LINE FROM BUS 341394 [2PATRIOT PW 69.000] TO BUS 342151 [2RINEYVILLE 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -2.1458e-06 | -0.00034773
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 194 341394-342151(1) | OPEN LINE FROM BUS 341394 [2PATRIOT PW 69.000] TO BUS 342151 [2RINEYVILLE 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 195 341394-342157(1) | OPEN LINE FROM BUS 341394 [2PATRIOT PW 69.000] TO BUS 342157 [2ROGERSVIL J69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -5.3644e-07 | -0.00034612
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 195 341394-342157(1) | OPEN LINE FROM BUS 341394 [2PATRIOT PW 69.000] TO BUS 342157 [2ROGERSVIL J69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 196 341394-342274(1) | OPEN LINE FROM BUS 341394 [2PATRIOT PW 69.000] TO BUS 342274 [2SMITHRVIL T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 1.7881e-07 | -0.00034541
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 196 341394-342274(1) | OPEN LINE FROM BUS 341394 [2PATRIOT PW 69.000] TO BUS 342274 [2SMITHRVIL T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 197 341398-341605(1) | OPEN LINE FROM BUS 341398 [2DOWNING 69.000] TO BUS 341605 [2HEBRON 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 199 341400-342091(1) | OPEN LINE FROM BUS 341400 [2DRAVO 69.000] TO BUS 342091 [2PLUMVILLE 69.000] CKT 1 | 0.93965 | 64.8362 | 0.9397 | 64.8393 | 4.5061e-05 | -0.00030053
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 199 341400-342091(1) | OPEN LINE FROM BUS 341400 [2DRAVO 69.000] TO BUS 342091 [2PLUMVILLE 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 200 341401-341842(1) | OPEN LINE FROM BUS 341401 [2DURO 69.000] TO BUS 341842 [2MBUSA T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 201 341404-341842(1) | OPEN LINE FROM BUS 341404 [2DURO T 69.000] TO BUS 341842 [2MBUSA T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 202 341404-342295(1) | OPEN LINE FROM BUS 341404 [2DURO T 69.000] TO BUS 342295 [2STANLY P J169.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 203 341404-342388(1) | OPEN LINE FROM BUS 341404 [2DURO T 69.000] TO BUS 342388 [2TURKEY FT J69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 204 341405-341406(1) | OPEN LINE FROM BUS 341405 [2DUNCANNO LN69.000] TO BUS 341406 [2DUNCAN LN T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93969 | 64.8385 | 3.3975e-05 | -0.00031161
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 204 341405-341406(1) | OPEN LINE FROM BUS 341405 [2DUNCANNO LN69.000] TO BUS 341406 [2DUNCAN LN T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 205 341407-342019(1) | OPEN LINE FROM BUS 341407 [2E BARDSTOWN69.000] TO BUS 342019 [2OWENS IL J 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8366 | 6.9737e-06 | -0.00033861
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 205 341407-342019(1) | OPEN LINE FROM BUS 341407 [2E BARDSTOWN69.000] TO BUS 342019 [2OWENS IL J 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 206 341410-341929(1) | OPEN LINE FROM BUS 341410 [2E BERNSTADT69.000] TO BUS 341929 [2N LONDON 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93969 | 64.8385 | 3.463e-05 | -0.00031096
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 206 341410-341929(1) | OPEN LINE FROM BUS 341410 [2E BERNSTADT69.000] TO BUS 341929 [2N LONDON 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 207 341416-342076(1) | OPEN LINE FROM BUS 341416 [2E PINE KNOT69.000] TO BUS 342076 [2PINE KNOT 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 3.9935e-06 | -0.00034159
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 207 341416-342076(1) | OPEN LINE FROM BUS 341416 [2E PINE KNOT69.000] TO BUS 342076 [2PINE KNOT 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 208 341419-341422(1) | OPEN LINE FROM BUS 341419 [2E SOMERSE T69.000] TO BUS 341422 [2E SOMERSET 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8375 | 1.9133e-05 | -0.00032645
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 208 341419-341422(1) | OPEN LINE FROM BUS 341419 [2E SOMERSE T69.000] TO BUS 341422 [2E SOMERSET 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 209 341419-341941(1) | OPEN LINE FROM BUS 341419 [2E SOMERSE T69.000] TO BUS 341941 [2NELSN VAL T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -5.3644e-07 | -0.00034612
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 209 341419-341941(1) | OPEN LINE FROM BUS 341419 [2E SOMERSE T69.000] TO BUS 341941 [2NELSN VAL T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 210 341419-341974(1) | OPEN LINE FROM BUS 341419 [2E SOMERSE T69.000] TO BUS 341974 [2NORWOOD T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 2.0862e-06 | -0.0003435
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 210 341419-341974(1) | OPEN LINE FROM BUS 341419 [2E SOMERSE T69.000] TO BUS 341974 [2NORWOOD T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 211 341425-341428(1) | OPEN LINE FROM BUS 341425 [2EBERLE 69.000] TO BUS 341428 [2EBERLE T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93963 | 64.8344 | -2.5213e-05 | -0.0003708
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 211 341425-341428(1) | OPEN LINE FROM BUS 341425 [2EBERLE 69.000] TO BUS 341428 [2EBERLE T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 212 341428-341809(1) | OPEN LINE FROM BUS 341428 [2EBERLE T 69.000] TO BUS 341809 [2MAPLESVIL T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8365 | 4.4703e-06 | -0.00034112
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 212 341428-341809(1) | OPEN LINE FROM BUS 341428 [2EBERLE T 69.000] TO BUS 341809 [2MAPLESVIL T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 213 341431-341434(1) | OPEN LINE FROM BUS 341431 [2EDM-JBGAL J69.000] TO BUS 341434 [2EDM-JBGAL T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.0133e-06 | -0.0003466
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 213 341431-341434(1) | OPEN LINE FROM BUS 341431 [2EDM-JBGAL J69.000] TO BUS 341434 [2EDM-JBGAL T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 214 341431-341728(1) | OPEN LINE FROM BUS 341431 [2EDM-JBGAL J69.000] TO BUS 341728 [2KNOB LICK 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 2.9802e-07 | -0.00034529
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 214 341431-341728(1) | OPEN LINE FROM BUS 341431 [2EDM-JBGAL J69.000] TO BUS 341728 [2KNOB LICK 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 215 341431-342322(1) | OPEN LINE FROM BUS 341431 [2EDM-JBGAL J69.000] TO BUS 342322 [2SUMM SHADE 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 6.5565e-07 | -0.00034493
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 215 341431-342322(1) | OPEN LINE FROM BUS 341431 [2EDM-JBGAL J69.000] TO BUS 342322 [2SUMM SHADE 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 216 341434-341437(1) | OPEN LINE FROM BUS 341434 [2EDM-JBGAL T69.000] TO BUS 341437 [2EDMON IND P69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -2.9802e-07 | -0.00034589
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 216 341434-341437(1) | OPEN LINE FROM BUS 341434 [2EDM-JBGAL T69.000] TO BUS 341437 [2EDMON IND P69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 217 341434-341680(1) | OPEN LINE FROM BUS 341434 [2EDM-JBGAL T69.000] TO BUS 341680 [2JB GALLOWAY69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -8.9407e-07 | -0.00034648
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 217 341434-341680(1) | OPEN LINE FROM BUS 341434 [2EDM-JBGAL T69.000] TO BUS 341680 [2JB GALLOWAY69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 218 341443-341446(1) | OPEN LINE FROM BUS 341443 [2ELLIO CO PT69.000] TO BUS 341446 [2ELLIOT CO P69.000] CKT 1 | 0.93965 | 64.8362 | 0.93994 | 64.8559 | 0.00028682 | -5.877e-05
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 218 341443-341446(1) | OPEN LINE FROM BUS 341443 [2ELLIO CO PT69.000] TO BUS 341446 [2ELLIOT CO P69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 219 341443-341953(1) | OPEN LINE FROM BUS 341443 [2ELLIO CO PT69.000] TO BUS 341953 [2NEW FOUNDL 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93974 | 64.8419 | 8.3148e-05 | -0.00026244
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 219 341443-341953(1) | OPEN LINE FROM BUS 341443 [2ELLIO CO PT69.000] TO BUS 341953 [2NEW FOUNDL 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 220 341449-342163(1) | OPEN LINE FROM BUS 341449 [2ELLIOTTVILL69.000] TO BUS 342163 [2ROWAN CO 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93943 | 64.8207 | -0.00022453 | -0.00057012
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 220 341449-342163(1) | OPEN LINE FROM BUS 341449 [2ELLIOTTVILL69.000] TO BUS 342163 [2ROWAN CO 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 221 341455-341458(1) | OPEN LINE FROM BUS 341455 [2ETOWN EK1 69.000] TO BUS 341458 [2ETOWN EK2 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -2.7418e-06 | -0.00034833
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 221 341455-341458(1) | OPEN LINE FROM BUS 341455 [2ETOWN EK1 69.000] TO BUS 341458 [2ETOWN EK2 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 222 341455-342274(1) | OPEN LINE FROM BUS 341455 [2ETOWN EK1 69.000] TO BUS 342274 [2SMITHRVIL T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 5.3644e-07 | -0.00034505
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 222 341455-342274(1) | OPEN LINE FROM BUS 341455 [2ETOWN EK1 69.000] TO BUS 342274 [2SMITHRVIL T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 223 341455-342379(1) | OPEN LINE FROM BUS 341455 [2ETOWN EK1 69.000] TO BUS 342379 [2TUNNEL H T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -1.8477e-06 | -0.00034744
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 223 341455-342379(1) | OPEN LINE FROM BUS 341455 [2ETOWN EK1 69.000] TO BUS 342379 [2TUNNEL H T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 224 341458-342340(1) | OPEN LINE FROM BUS 341458 [2ETOWN EK2 69.000] TO BUS 342340 [2THARP T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8359 | -4.0531e-06 | -0.00034964
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 224 341458-342340(1) | OPEN LINE FROM BUS 341458 [2ETOWN EK2 69.000] TO BUS 342340 [2THARP T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 225 341461-341797(1) | OPEN LINE FROM BUS 341461 [2FALCON EK 69.000] TO BUS 341797 [2MAGGARD 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8375 | 1.8895e-05 | -0.00032669
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 225 341461-341797(1) | OPEN LINE FROM BUS 341461 [2FALCON EK 69.000] TO BUS 341797 [2MAGGARD 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 226 341461-342310(1) | OPEN LINE FROM BUS 341461 [2FALCON EK 69.000] TO BUS 342310 [2SUBLETT 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93955 | 64.8289 | -0.00010461 | -0.00045019
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 226 341461-342310(1) | OPEN LINE FROM BUS 341461 [2FALCON EK 69.000] TO BUS 342310 [2SUBLETT 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 227 341464-341569(1) | OPEN LINE FROM BUS 341464 [2FALL ROCK 69.000] TO BUS 341569 [2GREENBRIA T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93969 | 64.8389 | 3.9995e-05 | -0.00030559
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 227 341464-341569(1) | OPEN LINE FROM BUS 341464 [2FALL ROCK 69.000] TO BUS 341569 [2GREENBRIA T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 228 341464-342391(1) | OPEN LINE FROM BUS 341464 [2FALL ROCK 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -2.3246e-06 | -0.00034791
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 228 341464-342391(1) | OPEN LINE FROM BUS 341464 [2FALL ROCK 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 229 341464-342730(1) | OPEN LINE FROM BUS 341464 [2FALL ROCK 69.000] TO BUS 342730 [5FALL ROCK 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93963 | 64.8344 | -2.4974e-05 | -0.00037056
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 229 341464-342730(1) | OPEN LINE FROM BUS 341464 [2FALL ROCK 69.000] TO BUS 342730 [5FALL ROCK 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 230 341467-342580(1) | OPEN LINE FROM BUS 341467 [2FAYETTE 69.000] TO BUS 342580 [4FAYETTE 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93999 | 64.859 | 0.0003314 | -1.4186e-05
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 230 341467-342580(1) | OPEN LINE FROM BUS 341467 [2FAYETTE 69.000] TO BUS 342580 [4FAYETTE 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 231 341470-341473(1) | OPEN LINE FROM BUS 341470 [2FLOYD EK 69.000] TO BUS 341473 [2FLOYD-SFL T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93962 | 64.8336 | -3.7134e-05 | -0.00038272
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 231 341470-341473(1) | OPEN LINE FROM BUS 341470 [2FLOYD EK 69.000] TO BUS 341473 [2FLOYD-SFL T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 232 341470-342511(1) | OPEN LINE FROM BUS 341470 [2FLOYD EK 69.000] TO BUS 342511 [2WOODSTOCK 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93963 | 64.8347 | -2.1338e-05 | -0.00036693
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 232 341470-342511(1) | OPEN LINE FROM BUS 341470 [2FLOYD EK 69.000] TO BUS 342511 [2WOODSTOCK 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341470 | 2FLOYD EK | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 233 341473-342115(1) | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.978 | 67.4817 | 0.93454 | 64.483 | -0.04346 | -0.005464
341473 | 2FLOYD-SFL T | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 233 341473-342115(1) | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.98179 | 67.7435 | 0.93097 | 64.2366 | -0.050824 | -0.0090341
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 233 341473-342115(1) | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93959 | 64.8316 | -6.64e-05 | -0.00041199
342193 | 2S FLOYD | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 233 341473-342115(1) | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.98169 | 67.7367 | 0.93086 | 64.2295 | -0.05083 | -0.0091383
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 233 341473-342115(1) | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 234 341473-342193(1) | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342193 [2S FLOYD 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8371 | 1.353e-05 | -0.00033206
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 234 341473-342193(1) | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342193 [2S FLOYD 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 235 341476-341899(1) | OPEN LINE FROM BUS 341476 [2FOGG PIKE 69.000] TO BUS 341899 [2MT STERLING69.000] CKT 1 | 0.93965 | 64.8362 | 0.93993 | 64.8553 | 0.00027758 | -6.8009e-05
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 235 341476-341899(1) | OPEN LINE FROM BUS 341476 [2FOGG PIKE 69.000] TO BUS 341899 [2MT STERLING69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 236 341476-342130(1) | OPEN LINE FROM BUS 341476 [2FOGG PIKE 69.000] TO BUS 342130 [2REID VILLAG69.000] CKT 1 | 0.93965 | 64.8362 | 0.93993 | 64.8551 | 0.00027436 | -7.1228e-05
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 236 341476-342130(1) | OPEN LINE FROM BUS 341476 [2FOGG PIKE 69.000] TO BUS 342130 [2REID VILLAG69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 237 341485-341488(1) | OPEN LINE FROM BUS 341485 [2FOUR OAKS 69.000] TO BUS 341488 [2FOUR OAKS T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 238 341485-341550(1) | OPEN LINE FROM BUS 341485 [2FOUR OAKS 69.000] TO BUS 341550 [2FALMOUTH KU69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 239 341491-341548(1) | OPEN LINE FROM BUS 341491 [2FOX HOLLOW 69.000] TO BUS 341548 [2GORIN PRK J69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 5.3644e-07 | -0.00034505
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 239 341491-341548(1) | OPEN LINE FROM BUS 341491 [2FOX HOLLOW 69.000] TO BUS 341548 [2GORIN PRK J69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 240 341491-342037(1) | OPEN LINE FROM BUS 341491 [2FOX HOLLOW 69.000] TO BUS 342037 [2PARKWAY 1 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -1.6689e-06 | -0.00034726
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 240 341491-342037(1) | OPEN LINE FROM BUS 341491 [2FOX HOLLOW 69.000] TO BUS 342037 [2PARKWAY 1 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 241 341491-342043(1) | OPEN LINE FROM BUS 341491 [2FOX HOLLOW 69.000] TO BUS 342043 [2PARKWAY 2 T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 2.6822e-06 | -0.00034291
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 241 341491-342043(1) | OPEN LINE FROM BUS 341491 [2FOX HOLLOW 69.000] TO BUS 342043 [2PARKWAY 2 T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 242 341491-342049(1) | OPEN LINE FROM BUS 341491 [2FOX HOLLOW 69.000] TO BUS 342049 [2PATTON RD J69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 2.9802e-07 | -0.00034529
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 242 341491-342049(1) | OPEN LINE FROM BUS 341491 [2FOX HOLLOW 69.000] TO BUS 342049 [2PATTON RD J69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 243 341491-342732(1) | OPEN LINE FROM BUS 341491 [2FOX HOLLOW 69.000] TO BUS 342732 [5FOX HOLLOW 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 1.4305e-06 | -0.00034416
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 243 341491-342732(1) | OPEN LINE FROM BUS 341491 [2FOX HOLLOW 69.000] TO BUS 342732 [5FOX HOLLOW 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 244 341494-341497(1) | OPEN LINE FROM BUS 341494 [2FREDRIKBG T69.000] TO BUS 341497 [2FREDRIKBRG 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 2.861e-06 | -0.00034273
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 244 341494-341497(1) | OPEN LINE FROM BUS 341494 [2FREDRIKBG T69.000] TO BUS 341497 [2FREDRIKBRG 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 245 341494-341935(1) | OPEN LINE FROM BUS 341494 [2FREDRIKBG T69.000] TO BUS 341935 [2N SPRINGFLD69.000] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8375 | 1.8954e-05 | -0.00032663
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 245 341494-341935(1) | OPEN LINE FROM BUS 341494 [2FREDRIKBG T69.000] TO BUS 341935 [2N SPRINGFLD69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 246 341494-342508(1) | OPEN LINE FROM BUS 341494 [2FREDRIKBG T69.000] TO BUS 342508 [2WOODLAWN 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8368 | 9.5367e-06 | -0.00033605
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 246 341494-342508(1) | OPEN LINE FROM BUS 341494 [2FREDRIKBG T69.000] TO BUS 342508 [2WOODLAWN 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 247 341500-341644(1) | OPEN LINE FROM BUS 341500 [2FRENCHBURG 69.000] TO BUS 341644 [2HOPE 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93957 | 64.8302 | -8.6427e-05 | -0.00043201
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 247 341500-341644(1) | OPEN LINE FROM BUS 341500 [2FRENCHBURG 69.000] TO BUS 341644 [2HOPE 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 248 341500-341824(1) | OPEN LINE FROM BUS 341500 [2FRENCHBURG 69.000] TO BUS 341824 [2MARIBA T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93962 | 64.8337 | -3.5644e-05 | -0.00038123
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 248 341500-341824(1) | OPEN LINE FROM BUS 341500 [2FRENCHBURG 69.000] TO BUS 341824 [2MARIBA T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 249 341503-341506(1) | OPEN LINE FROM BUS 341503 [2GAP OF RG T69.000] TO BUS 341506 [2GAP OF RIDG69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8367 | 8.5235e-06 | -0.00033706
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 249 341503-341506(1) | OPEN LINE FROM BUS 341503 [2GAP OF RG T69.000] TO BUS 341506 [2GAP OF RIDG69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 250 341503-341578(1) | OPEN LINE FROM BUS 341503 [2GAP OF RG T69.000] TO BUS 341578 [2GREGORY R T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8369 | 1.0788e-05 | -0.0003348
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 250 341503-341578(1) | OPEN LINE FROM BUS 341503 [2GAP OF RG T69.000] TO BUS 341578 [2GREGORY R T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 251 341503-341887(1) | OPEN LINE FROM BUS 341503 [2GAP OF RG T69.000] TO BUS 341887 [2MONTICELLO 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8359 | -3.5167e-06 | -0.0003491
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 251 341503-341887(1) | OPEN LINE FROM BUS 341503 [2GAP OF RG T69.000] TO BUS 341887 [2MONTICELLO 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 252 341509-341512(1) | OPEN LINE FROM BUS 341509 [2GARLIN 69.000] TO BUS 341512 [2GARLIN T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 1.0133e-06 | -0.00034457
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 252 341509-341512(1) | OPEN LINE FROM BUS 341509 [2GARLIN 69.000] TO BUS 341512 [2GARLIN T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 253 341515-341732(1) | OPEN LINE FROM BUS 341515 [2GARRARD CO 69.000] TO BUS 341732 [2LANCASTER T69.000] CKT 1 | 0.93965 | 64.8362 | 0.9396 | 64.8325 | -5.3346e-05 | -0.00039893
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 253 341515-341732(1) | OPEN LINE FROM BUS 341515 [2GARRARD CO 69.000] TO BUS 341732 [2LANCASTER T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 254 341515-942410(1) | OPEN LINE FROM BUS 341515 [2GARRARD CO 69.000] TO BUS 942410 [AE2-254 TAP 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8373 | 1.7166e-05 | -0.00032842
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 254 341515-942410(1) | OPEN LINE FROM BUS 341515 [2GARRARD CO 69.000] TO BUS 942410 [AE2-254 TAP 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 255 341518-341521(1) | OPEN LINE FROM BUS 341518 [2GARRARD KU 69.000] TO BUS 341521 [2GARRARDKU T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 5.9605e-07 | -0.00034499
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 255 341518-341521(1) | OPEN LINE FROM BUS 341518 [2GARRARD KU 69.000] TO BUS 341521 [2GARRARDKU T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 256 341521-341806(1) | OPEN LINE FROM BUS 341521 [2GARRARDKU T69.000] TO BUS 341806 [2MANCHESTER 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 1.1921e-07 | -0.00034547
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 256 341521-341806(1) | OPEN LINE FROM BUS 341521 [2GARRARDKU T69.000] TO BUS 341806 [2MANCHESTER 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 257 341530-342043(1) | OPEN LINE FROM BUS 341530 [2GLASGO-CLEV69.000] TO BUS 342043 [2PARKWAY 2 T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 2.6822e-06 | -0.00034291
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 257 341530-342043(1) | OPEN LINE FROM BUS 341530 [2GLASGO-CLEV69.000] TO BUS 342043 [2PARKWAY 2 T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 258 341530-342445(1) | OPEN LINE FROM BUS 341530 [2GLASGO-CLEV69.000] TO BUS 342445 [2W GLASGOW T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 2.6822e-06 | -0.00034291
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 258 341530-342445(1) | OPEN LINE FROM BUS 341530 [2GLASGO-CLEV69.000] TO BUS 342445 [2W GLASGOW T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 259 341533-341632(1) | OPEN LINE FROM BUS 341533 [2GLENDALE 69.000] TO BUS 341632 [2HODGENVILLE69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.3709e-06 | -0.00034696
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 259 341533-341632(1) | OPEN LINE FROM BUS 341533 [2GLENDALE 69.000] TO BUS 341632 [2HODGENVILLE69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 260 341533-342307(1) | OPEN LINE FROM BUS 341533 [2GLENDALE 69.000] TO BUS 342307 [2STEPHENSBRG69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8359 | -3.3379e-06 | -0.00034893
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 260 341533-342307(1) | OPEN LINE FROM BUS 341533 [2GLENDALE 69.000] TO BUS 342307 [2STEPHENSBRG69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 261 341536-341623(1) | OPEN LINE FROM BUS 341536 [2GODDARD 69.000] TO BUS 341623 [2HILLSBORO 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93944 | 64.8212 | -0.00021601 | -0.00056159
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 261 341536-341623(1) | OPEN LINE FROM BUS 341536 [2GODDARD 69.000] TO BUS 341623 [2HILLSBORO 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 1.1921e-07 | 1.1921e-07
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 262 341536-341989(1) | OPEN LINE FROM BUS 341536 [2GODDARD 69.000] TO BUS 341989 [2OAK RIDGE T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 263 341536-342088(1) | OPEN LINE FROM BUS 341536 [2GODDARD 69.000] TO BUS 342088 [2PLUMMR L T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 264 341536-342589(1) | OPEN LINE FROM BUS 341536 [2GODDARD 69.000] TO BUS 342589 [4GODDARD 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 265 341539-341686(1) | OPEN LINE FROM BUS 341539 [2GOLDBUG 69.000] TO BUS 341686 [2JELLICO C T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8349 | -1.8477e-05 | -0.00036407
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 265 341539-341686(1) | OPEN LINE FROM BUS 341539 [2GOLDBUG 69.000] TO BUS 341686 [2JELLICO C T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 266 341542-341548(1) | OPEN LINE FROM BUS 341542 [2GOODNIGHT 69.000] TO BUS 341548 [2GORIN PRK J69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 4.7684e-07 | -0.00034511
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 266 341542-341548(1) | OPEN LINE FROM BUS 341542 [2GOODNIGHT 69.000] TO BUS 341548 [2GORIN PRK J69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 267 341551-341587(1) | OPEN LINE FROM BUS 341551 [2GRANTS LICK69.000] TO BUS 341587 [2GRIFFIN J 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 268 341551-342298(1) | OPEN LINE FROM BUS 341551 [2GRANTS LICK69.000] TO BUS 342298 [2STANLY P J269.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341554 | 2GRAYSON J | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 269 341554-341752(1) | OPEN LINE FROM BUS 341554 [2GRAYSON J 69.000] TO BUS 341752 [2LEON 69.000] CKT 1 | 0.97031 | 66.9514 | 0.92959 | 64.1414 | -0.040725 | -0.010415
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 269 341554-341752(1) | OPEN LINE FROM BUS 341554 [2GRAYSON J 69.000] TO BUS 341752 [2LEON 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93999 | 64.8595 | 0.00033891 | -6.6757e-06
342031 | 2PACTOLUS | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 269 341554-341752(1) | OPEN LINE FROM BUS 341554 [2GRAYSON J 69.000] TO BUS 341752 [2LEON 69.000] CKT 1 | 0.96876 | 66.8443 | 0.93008 | 64.1755 | -0.038679 | -0.0099207
342034 | 2PACTOLUS T | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 269 341554-341752(1) | OPEN LINE FROM BUS 341554 [2GRAYSON J 69.000] TO BUS 341752 [2LEON 69.000] CKT 1 | 0.96946 | 66.8928 | 0.93081 | 64.2259 | -0.03865 | -0.0091891
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 269 341554-341752(1) | OPEN LINE FROM BUS 341554 [2GRAYSON J 69.000] TO BUS 341752 [2LEON 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 270 341554-342034(1) | OPEN LINE FROM BUS 341554 [2GRAYSON J 69.000] TO BUS 342034 [2PACTOLUS T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93981 | 64.8466 | 0.00015193 | -0.00019366
342031 | 2PACTOLUS | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 270 341554-342034(1) | OPEN LINE FROM BUS 341554 [2GRAYSON J 69.000] TO BUS 342034 [2PACTOLUS T 69.000] CKT 1 | 0.96876 | 66.8443 | 0.93825 | 64.7394 | -0.030507 | -0.0017485
342034 | 2PACTOLUS T | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 270 341554-342034(1) | OPEN LINE FROM BUS 341554 [2GRAYSON J 69.000] TO BUS 342034 [2PACTOLUS T 69.000] CKT 1 | 0.96946 | 66.8928 | 0.93898 | 64.7894 | -0.030483 | -0.0010226
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 270 341554-342034(1) | OPEN LINE FROM BUS 341554 [2GRAYSON J 69.000] TO BUS 342034 [2PACTOLUS T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 271 341563-341575(1) | OPEN LINE FROM BUS 341563 [2GREEN CO 69.000] TO BUS 341575 [2GREENSBURG 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -9.5367e-07 | -0.00034654
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 271 341563-341575(1) | OPEN LINE FROM BUS 341563 [2GREEN CO 69.000] TO BUS 341575 [2GREENSBURG 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 272 341563-342325(1) | OPEN LINE FROM BUS 341563 [2GREEN CO 69.000] TO BUS 342325 [2SUMMERSVIL 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8366 | 5.7817e-06 | -0.00033981
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 272 341563-342325(1) | OPEN LINE FROM BUS 341563 [2GREEN CO 69.000] TO BUS 342325 [2SUMMERSVIL 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 273 341563-342733(1) | OPEN LINE FROM BUS 341563 [2GREEN CO 69.000] TO BUS 342733 [5GREEN CO 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93968 | 64.8377 | 2.2292e-05 | -0.0003233
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 273 341563-342733(1) | OPEN LINE FROM BUS 341563 [2GREEN CO 69.000] TO BUS 342733 [5GREEN CO 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 274 341569-341572(1) | OPEN LINE FROM BUS 341569 [2GREENBRIA T69.000] TO BUS 341572 [2GREENBRIAR 69.000] CKT 1 | 0.93965 | 64.8362 | 0.9397 | 64.839 | 4.1187e-05 | -0.0003044
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 274 341569-341572(1) | OPEN LINE FROM BUS 341569 [2GREENBRIA T69.000] TO BUS 341572 [2GREENBRIAR 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 275 341569-341806(1) | OPEN LINE FROM BUS 341569 [2GREENBRIA T69.000] TO BUS 341806 [2MANCHESTER 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -2.3842e-07 | -0.00034583
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 275 341569-341806(1) | OPEN LINE FROM BUS 341569 [2GREENBRIA T69.000] TO BUS 341806 [2MANCHESTER 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 276 341575-341854(1) | OPEN LINE FROM BUS 341575 [2GREENSBURG 69.000] TO BUS 341854 [2MCKINNY T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -4.1723e-07 | -0.000346
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 276 341575-341854(1) | OPEN LINE FROM BUS 341575 [2GREENSBURG 69.000] TO BUS 341854 [2MCKINNY T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 277 341578-341581(1) | OPEN LINE FROM BUS 341578 [2GREGORY R T69.000] TO BUS 341581 [2GREGORY RD 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 1.1325e-06 | -0.00034446
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 277 341578-341581(1) | OPEN LINE FROM BUS 341578 [2GREGORY R T69.000] TO BUS 341581 [2GREGORY RD 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 278 341584-341587(1) | OPEN LINE FROM BUS 341584 [2GRIFFIN 69.000] TO BUS 341587 [2GRIFFIN J 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 279 341590-341593(1) | OPEN LINE FROM BUS 341590 [2HARDWCRK 69.000] TO BUS 341593 [2HARDWCRK T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8369 | 1.1265e-05 | -0.00033432
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 279 341590-341593(1) | OPEN LINE FROM BUS 341590 [2HARDWCRK 69.000] TO BUS 341593 [2HARDWCRK T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 280 341593-342301(1) | OPEN LINE FROM BUS 341593 [2HARDWCRK T 69.000] TO BUS 342301 [2STANTON 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8348 | -1.9193e-05 | -0.00036478
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 280 341593-342301(1) | OPEN LINE FROM BUS 341593 [2HARDWCRK T 69.000] TO BUS 342301 [2STANTON 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 281 341596-341599(1) | OPEN LINE FROM BUS 341596 [2HARGETT 69.000] TO BUS 341599 [2HARGETT T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.9397 | 64.839 | 4.1127e-05 | -0.00030446
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 281 341596-341599(1) | OPEN LINE FROM BUS 341596 [2HARGETT 69.000] TO BUS 341599 [2HARGETT T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 282 341599-342370(1) | OPEN LINE FROM BUS 341599 [2HARGETT T 69.000] TO BUS 342370 [2TRAPP 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93975 | 64.8428 | 9.6977e-05 | -0.00024861
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 282 341599-342370(1) | OPEN LINE FROM BUS 341599 [2HARGETT T 69.000] TO BUS 342370 [2TRAPP 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 283 341602-341872(1) | OPEN LINE FROM BUS 341602 [2HEADQTRS 69.000] TO BUS 341872 [2MILLB-CRL J69.000] CKT 1 | 0.93965 | 64.8362 | 0.939 | 64.7907 | -0.00065875 | -0.0010043
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 283 341602-341872(1) | OPEN LINE FROM BUS 341602 [2HEADQTRS 69.000] TO BUS 341872 [2MILLB-CRL J69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 284 341602-342280(1) | OPEN LINE FROM BUS 341602 [2HEADQTRS 69.000] TO BUS 342280 [2SNOW HILL 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93933 | 64.8137 | -0.00032502 | -0.00067061
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 284 341602-342280(1) | OPEN LINE FROM BUS 341602 [2HEADQTRS 69.000] TO BUS 342280 [2SNOW HILL 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 285 341605-342595(1) | OPEN LINE FROM BUS 341605 [2HEBRON 69.000] TO BUS 342595 [4HEBRON 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93889 | 64.7834 | -0.00076389 | -0.0011095
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 285 341605-342595(1) | OPEN LINE FROM BUS 341605 [2HEBRON 69.000] TO BUS 342595 [4HEBRON 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 286 341608-342313(1) | OPEN LINE FROM BUS 341608 [2HELECHAW 69.000] TO BUS 342313 [2SUBLETT J 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8354 | -1.0908e-05 | -0.0003565
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 286 341608-342313(1) | OPEN LINE FROM BUS 341608 [2HELECHAW 69.000] TO BUS 342313 [2SUBLETT J 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 287 341611-342103(1) | OPEN LINE FROM BUS 341611 [2HICKORY PL 69.000] TO BUS 342103 [2PPG 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8369 | 1.0967e-05 | -0.00033462
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 287 341611-342103(1) | OPEN LINE FROM BUS 341611 [2HICKORY PL 69.000] TO BUS 342103 [2PPG 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 288 341614-342520(1) | OPEN LINE FROM BUS 341614 [2HIGH ROCK 69.000] TO BUS 342520 [2ZACHARIAH 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93954 | 64.8283 | -0.00011384 | -0.00045943
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 288 341614-342520(1) | OPEN LINE FROM BUS 341614 [2HIGH ROCK 69.000] TO BUS 342520 [2ZACHARIAH 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 289 341617-341896(1) | OPEN LINE FROM BUS 341617 [2HIGHLAND EK69.000] TO BUS 341896 [2MT OLIVE J 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -2.3842e-07 | -0.00034583
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 289 341617-341896(1) | OPEN LINE FROM BUS 341617 [2HIGHLAND EK69.000] TO BUS 341896 [2MT OLIVE J 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 290 341620-342163(1) | OPEN LINE FROM BUS 341620 [2HILDA 69.000] TO BUS 342163 [2ROWAN CO 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8375 | 1.955e-05 | -0.00032604
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 290 341620-342163(1) | OPEN LINE FROM BUS 341620 [2HILDA 69.000] TO BUS 342163 [2ROWAN CO 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 291 341623-342052(1) | OPEN LINE FROM BUS 341623 [2HILLSBORO 69.000] TO BUS 342052 [2PEASTICKS 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93944 | 64.8215 | -0.00021285 | -0.00055844
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 291 341623-342052(1) | OPEN LINE FROM BUS 341623 [2HILLSBORO 69.000] TO BUS 342052 [2PEASTICKS 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 292 341632-341800(1) | OPEN LINE FROM BUS 341632 [2HODGENVILLE69.000] TO BUS 341800 [2MAGNOLIA 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8358 | -5.5432e-06 | -0.00035113
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 292 341632-341800(1) | OPEN LINE FROM BUS 341632 [2HODGENVILLE69.000] TO BUS 341800 [2MAGNOLIA 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 293 341632-342316(1) | OPEN LINE FROM BUS 341632 [2HODGENVILLE69.000] TO BUS 342316 [2SULPHUR CRK69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8358 | -5.7817e-06 | -0.00035137
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 293 341632-342316(1) | OPEN LINE FROM BUS 341632 [2HODGENVILLE69.000] TO BUS 342316 [2SULPHUR CRK69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 294 341638-342199(1) | OPEN LINE FROM BUS 341638 [2HOLLOWAY J 69.000] TO BUS 342199 [2S JESSAM J 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93957 | 64.83 | -8.9049e-05 | -0.00043464
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 294 341638-342199(1) | OPEN LINE FROM BUS 341638 [2HOLLOWAY J 69.000] TO BUS 342199 [2S JESSAM J 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 295 341638-342463(1) | OPEN LINE FROM BUS 341638 [2HOLLOWAY J 69.000] TO BUS 342463 [2W NICHVIL T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93981 | 64.8471 | 0.00015932 | -0.00018626
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 295 341638-342463(1) | OPEN LINE FROM BUS 341638 [2HOLLOWAY J 69.000] TO BUS 342463 [2W NICHVIL T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 296 341641-341887(1) | OPEN LINE FROM BUS 341641 [2HOMESTEAD S69.000] TO BUS 341887 [2MONTICELLO 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8367 | 8.5235e-06 | -0.00033706
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 296 341641-341887(1) | OPEN LINE FROM BUS 341641 [2HOMESTEAD S69.000] TO BUS 341887 [2MONTICELLO 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 297 341644-341683(1) | OPEN LINE FROM BUS 341644 [2HOPE 69.000] TO BUS 341683 [2JEFFERSNVIL69.000] CKT 1 | 0.93965 | 64.8362 | 0.93961 | 64.8329 | -4.6909e-05 | -0.0003925
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 297 341644-341683(1) | OPEN LINE FROM BUS 341644 [2HOPE 69.000] TO BUS 341683 [2JEFFERSNVIL69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 298 341647-341650(1) | OPEN LINE FROM BUS 341647 [2HORSE CV KU69.000] TO BUS 341650 [2HORSECAVE T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93969 | 64.8386 | 3.4928e-05 | -0.00031066
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 298 341647-341650(1) | OPEN LINE FROM BUS 341647 [2HORSE CV KU69.000] TO BUS 341650 [2HORSECAVE T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 299 341650-341651(Z1) | OPEN LINE FROM BUS 341650 [2HORSECAVE T69.000] TO BUS 341651 [2HORSECAVE J69.000] CKT Z1 | 0.93965 | 64.8362 | 0.93969 | 64.8386 | 3.4928e-05 | -0.00031066
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 299 341650-341651(Z1) | OPEN LINE FROM BUS 341650 [2HORSECAVE T69.000] TO BUS 341651 [2HORSECAVE J69.000] CKT Z1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 300 341651-341914(1) | OPEN LINE FROM BUS 341651 [2HORSECAVE J69.000] TO BUS 341914 [2MUNFVILKU T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8358 | -4.9472e-06 | -0.00035053
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 300 341651-341914(1) | OPEN LINE FROM BUS 341651 [2HORSECAVE J69.000] TO BUS 341914 [2MUNFVILKU T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 301 341653-341656(1) | OPEN LINE FROM BUS 341653 [2HOT MIX R T69.000] TO BUS 341656 [2HOT MIX RD 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93976 | 64.8434 | 0.00010455 | -0.00024104
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 301 341653-341656(1) | OPEN LINE FROM BUS 341653 [2HOT MIX R T69.000] TO BUS 341656 [2HOT MIX RD 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 302 341653-341890(1) | OPEN LINE FROM BUS 341653 [2HOT MIX R T69.000] TO BUS 341890 [2MORGAN CO 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8358 | -4.828e-06 | -0.00035042
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 302 341653-341890(1) | OPEN LINE FROM BUS 341653 [2HOT MIX R T69.000] TO BUS 341890 [2MORGAN CO 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 303 341659-341662(1) | OPEN LINE FROM BUS 341659 [2HT ADAMS 69.000] TO BUS 341662 [2HT ADAMS T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93959 | 64.8316 | -6.6519e-05 | -0.00041211
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 303 341659-341662(1) | OPEN LINE FROM BUS 341659 [2HT ADAMS 69.000] TO BUS 341662 [2HT ADAMS T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 304 341662-341671(1) | OPEN LINE FROM BUS 341662 [2HT ADAMS T 69.000] TO BUS 341671 [2HUNT FARM J69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 4.2319e-06 | -0.00034136
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 304 341662-341671(1) | OPEN LINE FROM BUS 341662 [2HT ADAMS T 69.000] TO BUS 341671 [2HUNT FARM J69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 306 341665-341701(1) | OPEN LINE FROM BUS 341665 [2HUNT 69.000] TO BUS 341701 [2JK SMITH 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93976 | 64.8435 | 0.0001058 | -0.00023979
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 306 341665-341701(1) | OPEN LINE FROM BUS 341665 [2HUNT 69.000] TO BUS 341701 [2JK SMITH 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 307 341665-341869(1) | OPEN LINE FROM BUS 341665 [2HUNT 69.000] TO BUS 341869 [2MILL HUNT T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 308 341665-342596(1) | OPEN LINE FROM BUS 341665 [2HUNT 69.000] TO BUS 342596 [4HUNT 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 309 341671-342061(1) | OPEN LINE FROM BUS 341671 [2HUNT FARM J69.000] TO BUS 342061 [2PERRYVILLE 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93973 | 64.8411 | 7.23e-05 | -0.00027329
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 309 341671-342061(1) | OPEN LINE FROM BUS 341671 [2HUNT FARM J69.000] TO BUS 342061 [2PERRYVILLE 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 310 341677-341890(1) | OPEN LINE FROM BUS 341677 [2INDEX 69.000] TO BUS 341890 [2MORGAN CO 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93952 | 64.827 | -0.00013256 | -0.00047815
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 310 341677-341890(1) | OPEN LINE FROM BUS 341677 [2INDEX 69.000] TO BUS 341890 [2MORGAN CO 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 311 341683-342100(1) | OPEN LINE FROM BUS 341683 [2JEFFERSNVIL69.000] TO BUS 342100 [2POWELL CO 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93948 | 64.8244 | -0.00017065 | -0.00051624
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 311 341683-342100(1) | OPEN LINE FROM BUS 341683 [2JEFFERSNVIL69.000] TO BUS 342100 [2POWELL CO 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 312 341686-341689(1) | OPEN LINE FROM BUS 341686 [2JELLICO C T69.000] TO BUS 341689 [2JELLICO CRK69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 2.3842e-06 | -0.0003432
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 312 341686-341689(1) | OPEN LINE FROM BUS 341686 [2JELLICO C T69.000] TO BUS 341689 [2JELLICO CRK69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 313 341686-342076(1) | OPEN LINE FROM BUS 341686 [2JELLICO C T69.000] TO BUS 342076 [2PINE KNOT 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93963 | 64.8346 | -2.1994e-05 | -0.00036758
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 313 341686-342076(1) | OPEN LINE FROM BUS 341686 [2JELLICO C T69.000] TO BUS 342076 [2PINE KNOT 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 314 341692-341695(1) | OPEN LINE FROM BUS 341692 [2JENNY WIL T69.000] TO BUS 341695 [2JENNY WILEY69.000] CKT 1 | 0.93965 | 64.8362 | 0.93972 | 64.8405 | 6.3241e-05 | -0.00028235
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 314 341692-341695(1) | OPEN LINE FROM BUS 341692 [2JENNY WIL T69.000] TO BUS 341695 [2JENNY WILEY69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 315 341692-342343(1) | OPEN LINE FROM BUS 341692 [2JENNY WIL T69.000] TO BUS 342343 [2THELMA 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93963 | 64.8346 | -2.2888e-05 | -0.00036848
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 315 341692-342343(1) | OPEN LINE FROM BUS 341692 [2JENNY WIL T69.000] TO BUS 342343 [2THELMA 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 316 341701-342370(1) | OPEN LINE FROM BUS 341701 [2JK SMITH 69.000] TO BUS 342370 [2TRAPP 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93976 | 64.8437 | 0.00010884 | -0.00023675
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 316 341701-342370(1) | OPEN LINE FROM BUS 341701 [2JK SMITH 69.000] TO BUS 342370 [2TRAPP 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 317 341704-341707(1) | OPEN LINE FROM BUS 341704 [2JOE TICH 69.000] TO BUS 341707 [2JOE TICH T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.3113e-06 | -0.0003469
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 317 341704-341707(1) | OPEN LINE FROM BUS 341704 [2JOE TICH 69.000] TO BUS 341707 [2JOE TICH T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 318 341707-342427(1) | OPEN LINE FROM BUS 341707 [2JOE TICH T 69.000] TO BUS 342427 [2W BARDSTWN 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.2517e-06 | -0.00034684
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 318 341707-342427(1) | OPEN LINE FROM BUS 341707 [2JOE TICH T 69.000] TO BUS 342427 [2W BARDSTWN 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 319 341716-341722(1) | OPEN LINE FROM BUS 341716 [2KEAVY 69.000] TO BUS 341722 [2KEAVY 2 T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.9397 | 64.839 | 4.071e-05 | -0.00030488
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 319 341716-341722(1) | OPEN LINE FROM BUS 341716 [2KEAVY 69.000] TO BUS 341722 [2KEAVY 2 T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 320 341719-341740(1) | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93962 | 64.8337 | -3.618e-05 | -0.00038177
342070 | 2PINE GROVE | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 320 341719-341740(1) | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.96385 | 66.5058 | 0.93959 | 64.8316 | -0.024264 | -0.00041175
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 320 341719-341740(1) | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 321 341719-342073(1) | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93962 | 64.8336 | -3.6955e-05 | -0.00038254
342070 | 2PINE GROVE | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 321 341719-342073(1) | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 0.96385 | 66.5058 | 0.93927 | 64.8094 | -0.024586 | -0.00073373
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 321 341719-342073(1) | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 322 341722-341740(1) | OPEN LINE FROM BUS 341722 [2KEAVY 2 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8368 | 9.0003e-06 | -0.00033659
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 322 341722-341740(1) | OPEN LINE FROM BUS 341722 [2KEAVY 2 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 323 341722-342187(1) | OPEN LINE FROM BUS 341722 [2KEAVY 2 T 69.000] TO BUS 342187 [2S CORBIN 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8359 | -3.6955e-06 | -0.00034928
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 323 341722-342187(1) | OPEN LINE FROM BUS 341722 [2KEAVY 2 T 69.000] TO BUS 342187 [2S CORBIN 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 324 341725-342007(1) | OPEN LINE FROM BUS 341725 [2KEITH 69.000] TO BUS 342007 [2OWEN CO 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 325 341725-342058(1) | OPEN LINE FROM BUS 341725 [2KEITH 69.000] TO BUS 342058 [2PENN 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 326 341728-341854(1) | OPEN LINE FROM BUS 341728 [2KNOB LICK 69.000] TO BUS 341854 [2MCKINNY T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | -5.9605e-08 | -0.00034565
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 326 341728-341854(1) | OPEN LINE FROM BUS 341728 [2KNOB LICK 69.000] TO BUS 341854 [2MCKINNY T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 327 341731-341732(1) | OPEN LINE FROM BUS 341731 [2LANCASTER 69.000] TO BUS 341732 [2LANCASTER T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8366 | 6.3777e-06 | -0.00033921
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 327 341731-341732(1) | OPEN LINE FROM BUS 341731 [2LANCASTER 69.000] TO BUS 341732 [2LANCASTER T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 328 341732-341959(1) | OPEN LINE FROM BUS 341732 [2LANCASTER T69.000] TO BUS 341959 [2NEWBY 1 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8352 | -1.3471e-05 | -0.00035906
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 328 341732-341959(1) | OPEN LINE FROM BUS 341732 [2LANCASTER T69.000] TO BUS 341959 [2NEWBY 1 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 329 341734-341737(1) | OPEN LINE FROM BUS 341734 [2LAUR C IP T69.000] TO BUS 341737 [2LAUR CO IP 69.000] CKT 1 | 0.93965 | 64.8362 | 0.9397 | 64.8394 | 4.679e-05 | -0.0002988
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 329 341734-341737(1) | OPEN LINE FROM BUS 341734 [2LAUR C IP T69.000] TO BUS 341737 [2LAUR CO IP 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341381 | 2DAV LANE | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 330 341734-341929(1) | OPEN LINE FROM BUS 341734 [2LAUR C IP T69.000] TO BUS 341929 [2N LONDON 69.000] CKT 1 | 0.96406 | 66.5204 | 0.9222 | 63.632 | -0.04186 | -0.017797
341382 | 2DAV LANE T | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 330 341734-341929(1) | OPEN LINE FROM BUS 341734 [2LAUR C IP T69.000] TO BUS 341929 [2N LONDON 69.000] CKT 1 | 0.96451 | 66.5509 | 0.92267 | 63.6639 | -0.04184 | -0.017334
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 330 341734-341929(1) | OPEN LINE FROM BUS 341734 [2LAUR C IP T69.000] TO BUS 341929 [2N LONDON 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93968 | 64.8376 | 2.0921e-05 | -0.00032467
341734 | 2LAUR C IP T | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 330 341734-341929(1) | OPEN LINE FROM BUS 341734 [2LAUR C IP T69.000] TO BUS 341929 [2N LONDON 69.000] CKT 1 | 0.96462 | 66.5588 | 0.9226 | 63.6591 | -0.042024 | -0.017404
341737 | 2LAUR CO IP | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 330 341734-341929(1) | OPEN LINE FROM BUS 341734 [2LAUR C IP T69.000] TO BUS 341929 [2N LONDON 69.000] CKT 1 | 0.96087 | 66.2998 | 0.91867 | 63.3881 | -0.042197 | -0.021331
342070 | 2PINE GROVE | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 330 341734-341929(1) | OPEN LINE FROM BUS 341734 [2LAUR C IP T69.000] TO BUS 341929 [2N LONDON 69.000] CKT 1 | 0.96385 | 66.5058 | 0.93728 | 64.6721 | -0.026576 | -0.0027238
342073 | 2PINE GRV T | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 330 341734-341929(1) | OPEN LINE FROM BUS 341734 [2LAUR C IP T69.000] TO BUS 341929 [2N LONDON 69.000] CKT 1 | 0.96512 | 66.5936 | 0.93858 | 64.7623 | -0.02654 | -0.0014156
342451 | 2W LONDON | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 330 341734-341929(1) | OPEN LINE FROM BUS 341734 [2LAUR C IP T69.000] TO BUS 341929 [2N LONDON 69.000] CKT 1 | 0.96401 | 66.5166 | 0.93018 | 64.1823 | -0.033829 | -0.0098211
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 330 341734-341929(1) | OPEN LINE FROM BUS 341734 [2LAUR C IP T69.000] TO BUS 341929 [2N LONDON 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 331 341740-342754(1) | OPEN LINE FROM BUS 341740 [2LAUREL CO 69.000] TO BUS 342754 [5LAUREL CO 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93981 | 64.8472 | 0.00015986 | -0.00018573
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 331 341740-342754(1) | OPEN LINE FROM BUS 341740 [2LAUREL CO 69.000] TO BUS 342754 [5LAUREL CO 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 332 341746-342253(1) | OPEN LINE FROM BUS 341746 [2LEBANON J 69.000] TO BUS 342253 [2SHEPHEVIL J69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 0 | -0.00034559
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 332 341746-342253(1) | OPEN LINE FROM BUS 341746 [2LEBANON J 69.000] TO BUS 342253 [2SHEPHEVIL J69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 333 341749-342058(1) | OPEN LINE FROM BUS 341749 [2LEES LICK 69.000] TO BUS 342058 [2PENN 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93815 | 64.7327 | -0.0014997 | -0.0018452
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 333 341749-342058(1) | OPEN LINE FROM BUS 341749 [2LEES LICK 69.000] TO BUS 342058 [2PENN 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 334 341749-342133(1) | OPEN LINE FROM BUS 341749 [2LEES LICK 69.000] TO BUS 342133 [2RENAKER 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93903 | 64.7928 | -0.00062793 | -0.00097352
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 334 341749-342133(1) | OPEN LINE FROM BUS 341749 [2LEES LICK 69.000] TO BUS 342133 [2RENAKER 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 335 341755-341758(1) | OPEN LINE FROM BUS 341755 [2LIBER CH T 69.000] TO BUS 341758 [2LIBERT CHUR69.000] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8371 | 1.3709e-05 | -0.00033188
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 335 341755-341758(1) | OPEN LINE FROM BUS 341755 [2LIBER CH T 69.000] TO BUS 341758 [2LIBERT CHUR69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 336 341761-341767(1) | OPEN LINE FROM BUS 341761 [2LIBERTY J 69.000] TO BUS 341767 [2LIBERTYKU T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 1.7881e-06 | -0.0003438
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 336 341761-341767(1) | OPEN LINE FROM BUS 341761 [2LIBERTY J 69.000] TO BUS 341767 [2LIBERTYKU T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 337 341761-341896(1) | OPEN LINE FROM BUS 341761 [2LIBERTY J 69.000] TO BUS 341896 [2MT OLIVE J 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 3.5763e-07 | -0.00034523
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 337 341761-341896(1) | OPEN LINE FROM BUS 341761 [2LIBERTY J 69.000] TO BUS 341896 [2MT OLIVE J 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 338 341761-342760(1) | OPEN LINE FROM BUS 341761 [2LIBERTY J 69.000] TO BUS 342760 [5LIBERTY J 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -2.265e-06 | -0.00034785
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 338 341761-342760(1) | OPEN LINE FROM BUS 341761 [2LIBERTY J 69.000] TO BUS 342760 [5LIBERTY J 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 339 341764-341767(1) | OPEN LINE FROM BUS 341764 [2LIBERTY KU 69.000] TO BUS 341767 [2LIBERTYKU T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8367 | 7.4506e-06 | -0.00033814
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 339 341764-341767(1) | OPEN LINE FROM BUS 341764 [2LIBERTY KU 69.000] TO BUS 341767 [2LIBERTYKU T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 340 341767-342064(1) | OPEN LINE FROM BUS 341767 [2LIBERTYKU T69.000] TO BUS 342064 [2PEYTONS ST 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -1.9073e-06 | -0.0003475
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 340 341767-342064(1) | OPEN LINE FROM BUS 341767 [2LIBERTYKU T69.000] TO BUS 342064 [2PEYTONS ST 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 341 341772-341774(1) | OPEN LINE FROM BUS 341772 [2LOGAN 69.000] TO BUS 341774 [2LOGAN 2 T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8358 | -4.7684e-06 | -0.00035036
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 341 341772-341774(1) | OPEN LINE FROM BUS 341772 [2LOGAN 69.000] TO BUS 341774 [2LOGAN 2 T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341089 | 2BEKAERT | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 342 341774-341775(1) | OPEN LINE FROM BUS 341774 [2LOGAN 2 T 69.000] TO BUS 341775 [2LOGAN TAP 69.000] CKT 1 | 0.96341 | 66.4751 | 0.92599 | 63.8931 | -0.03742 | -0.014013
341212 | 2BUDD | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 342 341774-341775(1) | OPEN LINE FROM BUS 341774 [2LOGAN 2 T 69.000] TO BUS 341775 [2LOGAN TAP 69.000] CKT 1 | 0.96804 | 66.7948 | 0.91695 | 63.2694 | -0.051093 | -0.023052
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 342 341774-341775(1) | OPEN LINE FROM BUS 341774 [2LOGAN 2 T 69.000] TO BUS 341775 [2LOGAN TAP 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93968 | 64.838 | 2.6882e-05 | -0.00031871
341772 | 2LOGAN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 342 341774-341775(1) | OPEN LINE FROM BUS 341774 [2LOGAN 2 T 69.000] TO BUS 341775 [2LOGAN TAP 69.000] CKT 1 | 0.97051 | 66.965 | 0.91641 | 63.2322 | -0.054099 | -0.023591
341774 | 2LOGAN 2 T | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 342 341774-341775(1) | OPEN LINE FROM BUS 341774 [2LOGAN 2 T 69.000] TO BUS 341775 [2LOGAN TAP 69.000] CKT 1 | 0.97051 | 66.965 | 0.91641 | 63.2322 | -0.054099 | -0.023591
342500 | 2WIELAND | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 342 341774-341775(1) | OPEN LINE FROM BUS 341774 [2LOGAN 2 T 69.000] TO BUS 341775 [2LOGAN TAP 69.000] CKT 1 | 0.96309 | 66.453 | 0.91911 | 63.4187 | -0.043976 | -0.020889
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 342 341774-341775(1) | OPEN LINE FROM BUS 341774 [2LOGAN 2 T 69.000] TO BUS 341775 [2LOGAN TAP 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341089 | 2BEKAERT | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 343 341775-342247(1) | OPEN LINE FROM BUS 341775 [2LOGAN TAP 69.000] TO BUS 342247 [2SHELBY CO 69.000] CKT 1 | 0.96341 | 66.4751 | 0.92599 | 63.8931 | -0.03742 | -0.014013
341212 | 2BUDD | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 343 341775-342247(1) | OPEN LINE FROM BUS 341775 [2LOGAN TAP 69.000] TO BUS 342247 [2SHELBY CO 69.000] CKT 1 | 0.96804 | 66.7948 | 0.91695 | 63.2694 | -0.051093 | -0.023052
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 343 341775-342247(1) | OPEN LINE FROM BUS 341775 [2LOGAN TAP 69.000] TO BUS 342247 [2SHELBY CO 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93968 | 64.838 | 2.6882e-05 | -0.00031871
341772 | 2LOGAN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 343 341775-342247(1) | OPEN LINE FROM BUS 341775 [2LOGAN TAP 69.000] TO BUS 342247 [2SHELBY CO 69.000] CKT 1 | 0.97051 | 66.965 | 0.91641 | 63.2322 | -0.054099 | -0.023591
341774 | 2LOGAN 2 T | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 343 341775-342247(1) | OPEN LINE FROM BUS 341775 [2LOGAN TAP 69.000] TO BUS 342247 [2SHELBY CO 69.000] CKT 1 | 0.97051 | 66.965 | 0.91641 | 63.2322 | -0.054099 | -0.023591
341775 | 2LOGAN TAP | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 343 341775-342247(1) | OPEN LINE FROM BUS 341775 [2LOGAN TAP 69.000] TO BUS 342247 [2SHELBY CO 69.000] CKT 1 | 0.97064 | 66.9742 | 0.91641 | 63.2322 | -0.054231 | -0.023591
342500 | 2WIELAND | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 343 341775-342247(1) | OPEN LINE FROM BUS 341775 [2LOGAN TAP 69.000] TO BUS 342247 [2SHELBY CO 69.000] CKT 1 | 0.96309 | 66.453 | 0.91911 | 63.4187 | -0.043976 | -0.020889
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 343 341775-342247(1) | OPEN LINE FROM BUS 341775 [2LOGAN TAP 69.000] TO BUS 342247 [2SHELBY CO 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 344 341776-342208(1) | OPEN LINE FROM BUS 341776 [2LORETTO 69.000] TO BUS 342208 [2S SPRINGF T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8373 | 1.5914e-05 | -0.00032967
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 344 341776-342208(1) | OPEN LINE FROM BUS 341776 [2LORETTO 69.000] TO BUS 342208 [2S SPRINGF T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 345 341776-342316(1) | OPEN LINE FROM BUS 341776 [2LORETTO 69.000] TO BUS 342316 [2SULPHUR CRK69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 4.1723e-06 | -0.00034142
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 345 341776-342316(1) | OPEN LINE FROM BUS 341776 [2LORETTO 69.000] TO BUS 342316 [2SULPHUR CRK69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 346 341779-341782(1) | OPEN LINE FROM BUS 341779 [2LOW GAP 69.000] TO BUS 341782 [2LOW GAP T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93968 | 64.8379 | 2.4676e-05 | -0.00032091
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 346 341779-341782(1) | OPEN LINE FROM BUS 341779 [2LOW GAP 69.000] TO BUS 341782 [2LOW GAP T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 347 341782-342475(1) | OPEN LINE FROM BUS 341782 [2LOW GAP T 69.000] TO BUS 342475 [2WARNOCK 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 5.3644e-07 | -0.00034505
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 347 341782-342475(1) | OPEN LINE FROM BUS 341782 [2LOW GAP T 69.000] TO BUS 342475 [2WARNOCK 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 348 341785-341788(1) | OPEN LINE FROM BUS 341785 [2LYMAN BW 69.000] TO BUS 341788 [2LYMAN BW T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -2.3842e-06 | -0.00034797
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 348 341785-341788(1) | OPEN LINE FROM BUS 341785 [2LYMAN BW 69.000] TO BUS 341788 [2LYMAN BW T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 349 341788-342155(1) | OPEN LINE FROM BUS 341788 [2LYMAN BW T 69.000] TO BUS 342155 [2ROANOKE T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 2.861e-06 | -0.00034273
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 349 341788-342155(1) | OPEN LINE FROM BUS 341788 [2LYMAN BW T 69.000] TO BUS 342155 [2ROANOKE T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 350 341788-342379(1) | OPEN LINE FROM BUS 341788 [2LYMAN BW T 69.000] TO BUS 342379 [2TUNNEL H T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 1.8477e-06 | -0.00034374
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 350 341788-342379(1) | OPEN LINE FROM BUS 341788 [2LYMAN BW T 69.000] TO BUS 342379 [2TUNNEL H T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 351 341791-341794(1) | OPEN LINE FROM BUS 341791 [2MACKVIL KU 69.000] TO BUS 341794 [2MACKVILKU T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 1.0729e-06 | -0.00034451
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 351 341791-341794(1) | OPEN LINE FROM BUS 341791 [2MACKVIL KU 69.000] TO BUS 341794 [2MACKVILKU T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 352 341794-341935(1) | OPEN LINE FROM BUS 341794 [2MACKVILKU T69.000] TO BUS 341935 [2N SPRINGFLD69.000] CKT 1 | 0.93965 | 64.8362 | 0.93968 | 64.838 | 2.6703e-05 | -0.00031888
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 352 341794-341935(1) | OPEN LINE FROM BUS 341794 [2MACKVILKU T69.000] TO BUS 341935 [2N SPRINGFLD69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 353 341794-342061(1) | OPEN LINE FROM BUS 341794 [2MACKVILKU T69.000] TO BUS 342061 [2PERRYVILLE 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93968 | 64.8381 | 2.7835e-05 | -0.00031775
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 353 341794-342061(1) | OPEN LINE FROM BUS 341794 [2MACKVILKU T69.000] TO BUS 342061 [2PERRYVILLE 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 354 341797-342265(1) | OPEN LINE FROM BUS 341797 [2MAGGARD 69.000] TO BUS 342265 [2SKAGGS 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93968 | 64.8382 | 2.8968e-05 | -0.00031662
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 354 341797-342265(1) | OPEN LINE FROM BUS 341797 [2MAGGARD 69.000] TO BUS 342265 [2SKAGGS 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 355 341800-342325(1) | OPEN LINE FROM BUS 341800 [2MAGNOLIA 69.000] TO BUS 342325 [2SUMMERSVIL 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8358 | -5.6028e-06 | -0.00035119
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 355 341800-342325(1) | OPEN LINE FROM BUS 341800 [2MAGNOLIA 69.000] TO BUS 342325 [2SUMMERSVIL 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 356 341803-342310(1) | OPEN LINE FROM BUS 341803 [2MAGOFFIN CO69.000] TO BUS 342310 [2SUBLETT 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93963 | 64.8343 | -2.6941e-05 | -0.00037253
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 356 341803-342310(1) | OPEN LINE FROM BUS 341803 [2MAGOFFIN CO69.000] TO BUS 342310 [2SUBLETT 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 357 341803-342313(1) | OPEN LINE FROM BUS 341803 [2MAGOFFIN CO69.000] TO BUS 342313 [2SUBLETT J 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 5.9605e-07 | -0.00034499
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 357 341803-342313(1) | OPEN LINE FROM BUS 341803 [2MAGOFFIN CO69.000] TO BUS 342313 [2SUBLETT J 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 358 341809-341812(1) | OPEN LINE FROM BUS 341809 [2MAPLESVIL T69.000] TO BUS 341812 [2MAPLESVILLE69.000] CKT 1 | 0.93965 | 64.8362 | 0.93968 | 64.8381 | 2.7835e-05 | -0.00031775
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 358 341809-341812(1) | OPEN LINE FROM BUS 341809 [2MAPLESVIL T69.000] TO BUS 341812 [2MAPLESVILLE69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 359 341809-341929(1) | OPEN LINE FROM BUS 341809 [2MAPLESVIL T69.000] TO BUS 341929 [2N LONDON 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93971 | 64.8402 | 5.8174e-05 | -0.00028741
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 359 341809-341929(1) | OPEN LINE FROM BUS 341809 [2MAPLESVIL T69.000] TO BUS 341929 [2N LONDON 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 360 341815-341818(1) | OPEN LINE FROM BUS 341815 [2MARETBURG 69.000] TO BUS 341818 [2MARETBURG T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93961 | 64.8331 | -4.4167e-05 | -0.00038975
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 360 341815-341818(1) | OPEN LINE FROM BUS 341815 [2MARETBURG 69.000] TO BUS 341818 [2MARETBURG T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 361 341818-342472(1) | OPEN LINE FROM BUS 341818 [2MARETBURG T69.000] TO BUS 342472 [2WALNUT GROV69.000] CKT 1 | 0.93965 | 64.8362 | 0.93969 | 64.8389 | 3.9458e-05 | -0.00030613
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 361 341818-342472(1) | OPEN LINE FROM BUS 341818 [2MARETBURG T69.000] TO BUS 342472 [2WALNUT GROV69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 362 341821-341824(1) | OPEN LINE FROM BUS 341821 [2MARIBA 69.000] TO BUS 341824 [2MARIBA T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93977 | 64.8441 | 0.00011486 | -0.00023073
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 362 341821-341824(1) | OPEN LINE FROM BUS 341821 [2MARIBA 69.000] TO BUS 341824 [2MARIBA T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 363 341824-341833(1) | OPEN LINE FROM BUS 341824 [2MARIBA T 69.000] TO BUS 341833 [2MAYTOWN T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.835 | -1.7285e-05 | -0.00036287
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 363 341824-341833(1) | OPEN LINE FROM BUS 341824 [2MARIBA T 69.000] TO BUS 341833 [2MAYTOWN T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 364 341827-342343(1) | OPEN LINE FROM BUS 341827 [2MARTIN CO 69.000] TO BUS 342343 [2THELMA 69.000] CKT 1 | 0.93965 | 64.8362 | 0.9397 | 64.839 | 4.1246e-05 | -0.00030434
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 364 341827-342343(1) | OPEN LINE FROM BUS 341827 [2MARTIN CO 69.000] TO BUS 342343 [2THELMA 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 365 341830-341833(1) | OPEN LINE FROM BUS 341830 [2MAYTOWN 69.000] TO BUS 341833 [2MAYTOWN T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93975 | 64.8431 | 0.00010014 | -0.00024545
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 365 341830-341833(1) | OPEN LINE FROM BUS 341830 [2MAYTOWN 69.000] TO BUS 341833 [2MAYTOWN T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 366 341833-341890(1) | OPEN LINE FROM BUS 341833 [2MAYTOWN T 69.000] TO BUS 341890 [2MORGAN CO 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8353 | -1.2994e-05 | -0.00035858
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 366 341833-341890(1) | OPEN LINE FROM BUS 341833 [2MAYTOWN T 69.000] TO BUS 341890 [2MORGAN CO 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341443 | 2ELLIO CO PT | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 367 341836-341953(1) | OPEN LINE FROM BUS 341836 [2MAZIE 69.000] TO BUS 341953 [2NEW FOUNDL 69.000] CKT 1 | 0.96983 | 66.9181 | 0.93425 | 64.4631 | -0.03558 | -0.005752
341446 | 2ELLIOT CO P | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 367 341836-341953(1) | OPEN LINE FROM BUS 341836 [2MAZIE 69.000] TO BUS 341953 [2NEW FOUNDL 69.000] CKT 1 | 0.96946 | 66.8924 | 0.93386 | 64.4364 | -0.035594 | -0.0061387
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 367 341836-341953(1) | OPEN LINE FROM BUS 341836 [2MAZIE 69.000] TO BUS 341953 [2NEW FOUNDL 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93983 | 64.8482 | 0.00017494 | -0.00017065
341953 | 2NEW FOUNDL | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 367 341836-341953(1) | OPEN LINE FROM BUS 341836 [2MAZIE 69.000] TO BUS 341953 [2NEW FOUNDL 69.000] CKT 1 | 0.97094 | 66.995 | 0.93322 | 64.3923 | -0.03772 | -0.0067778
342229 | 2SANDY HOOK | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 367 341836-341953(1) | OPEN LINE FROM BUS 341836 [2MAZIE 69.000] TO BUS 341953 [2NEW FOUNDL 69.000] CKT 1 | 0.96886 | 66.8512 | 0.93105 | 64.2425 | -0.037807 | -0.0089498
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 367 341836-341953(1) | OPEN LINE FROM BUS 341836 [2MAZIE 69.000] TO BUS 341953 [2NEW FOUNDL 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341443 | 2ELLIO CO PT | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 368 341836-342265(1) | OPEN LINE FROM BUS 341836 [2MAZIE 69.000] TO BUS 342265 [2SKAGGS 69.000] CKT 1 | 0.96983 | 66.9181 | 0.92777 | 64.0159 | -0.042061 | -0.012233
341446 | 2ELLIOT CO P | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 368 341836-342265(1) | OPEN LINE FROM BUS 341836 [2MAZIE 69.000] TO BUS 342265 [2SKAGGS 69.000] CKT 1 | 0.96946 | 66.8924 | 0.92738 | 63.989 | -0.042078 | -0.012623
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 368 341836-342265(1) | OPEN LINE FROM BUS 341836 [2MAZIE 69.000] TO BUS 342265 [2SKAGGS 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93986 | 64.8505 | 0.00020742 | -0.00013816
341836 | 2MAZIE | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 368 341836-342265(1) | OPEN LINE FROM BUS 341836 [2MAZIE 69.000] TO BUS 342265 [2SKAGGS 69.000] CKT 1 | 0.98656 | 68.0729 | 0.92392 | 63.7506 | -0.062641 | -0.016078
341953 | 2NEW FOUNDL | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 368 341836-342265(1) | OPEN LINE FROM BUS 341836 [2MAZIE 69.000] TO BUS 342265 [2SKAGGS 69.000] CKT 1 | 0.97094 | 66.995 | 0.92642 | 63.9228 | -0.044524 | -0.013582
342229 | 2SANDY HOOK | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 368 341836-342265(1) | OPEN LINE FROM BUS 341836 [2MAZIE 69.000] TO BUS 342265 [2SKAGGS 69.000] CKT 1 | 0.96886 | 66.8512 | 0.92423 | 63.7718 | -0.044628 | -0.01577
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 368 341836-342265(1) | OPEN LINE FROM BUS 341836 [2MAZIE 69.000] TO BUS 342265 [2SKAGGS 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 369 341839-341842(1) | OPEN LINE FROM BUS 341839 [2MBUSA 69.000] TO BUS 341842 [2MBUSA T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 371 341845-342490(1) | OPEN LINE FROM BUS 341845 [2MCCREARY CO69.000] TO BUS 342490 [2WHITLEY CTY69.000] CKT 1 | 0.93965 | 64.8362 | 0.93971 | 64.8397 | 5.1975e-05 | -0.00029361
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 371 341845-342490(1) | OPEN LINE FROM BUS 341845 [2MCCREARY CO69.000] TO BUS 342490 [2WHITLEY CTY69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 372 341845-342778(1) | OPEN LINE FROM BUS 341845 [2MCCREARY CO69.000] TO BUS 342778 [5MCCREARY CO161.00] CKT 1 | 0.93965 | 64.8362 | 0.93969 | 64.8388 | 3.8505e-05 | -0.00030708
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 372 341845-342778(1) | OPEN LINE FROM BUS 341845 [2MCCREARY CO69.000] TO BUS 342778 [5MCCREARY CO161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 373 341848-342223(1) | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342223 [2SAND GAP T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8355 | -9.5963e-06 | -0.00035518
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 373 341848-342223(1) | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342223 [2SAND GAP T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 374 341848-342391(1) | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93978 | 64.8451 | 0.00012976 | -0.00021583
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 374 341848-342391(1) | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 375 341851-341854(1) | OPEN LINE FROM BUS 341851 [2MCKINNEY 69.000] TO BUS 341854 [2MCKINNY T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -7.1526e-07 | -0.0003463
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 375 341851-341854(1) | OPEN LINE FROM BUS 341851 [2MCKINNEY 69.000] TO BUS 341854 [2MCKINNY T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 376 341857-342406(1) | OPEN LINE FROM BUS 341857 [2MERCR IND 69.000] TO BUS 342406 [2VAN ARSDELL69.000] CKT 1 | 0.93965 | 64.8362 | 0.93955 | 64.8292 | -0.00010145 | -0.00044703
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 376 341857-342406(1) | OPEN LINE FROM BUS 341857 [2MERCR IND 69.000] TO BUS 342406 [2VAN ARSDELL69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 377 341860-341863(1) | OPEN LINE FROM BUS 341860 [2MIDDL CRK T69.000] TO BUS 341863 [2MIDDLE CRK 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93974 | 64.8424 | 9.0003e-05 | -0.00025558
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 377 341860-341863(1) | OPEN LINE FROM BUS 341860 [2MIDDL CRK T69.000] TO BUS 341863 [2MIDDLE CRK 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 378 341869-341875(1) | OPEN LINE FROM BUS 341869 [2MILL HUNT T69.000] TO BUS 341875 [2MILLER HUNT69.000] CKT 1 | 0.93965 | 64.8362 | 0.93973 | 64.8414 | 7.5579e-05 | -0.00027001
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 378 341869-341875(1) | OPEN LINE FROM BUS 341869 [2MILL HUNT T69.000] TO BUS 341875 [2MILLER HUNT69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 379 341869-342259(1) | OPEN LINE FROM BUS 341869 [2MILL HUNT T69.000] TO BUS 342259 [2SIDEVIEW 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 380 341872-341878(1) | OPEN LINE FROM BUS 341872 [2MILLB-CRL J69.000] TO BUS 341878 [2MILLERSB EK69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 381 341887-342268(1) | OPEN LINE FROM BUS 341887 [2MONTICELLO 69.000] TO BUS 342268 [2SLAT 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93969 | 64.8387 | 3.7491e-05 | -0.0003081
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 381 341887-342268(1) | OPEN LINE FROM BUS 341887 [2MONTICELLO 69.000] TO BUS 342268 [2SLAT 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 382 341893-341896(1) | OPEN LINE FROM BUS 341893 [2MT OLIVE 69.000] TO BUS 341896 [2MT OLIVE J 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 5.9605e-07 | -0.00034499
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 382 341893-341896(1) | OPEN LINE FROM BUS 341893 [2MT OLIVE 69.000] TO BUS 341896 [2MT OLIVE J 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 383 341908-341914(1) | OPEN LINE FROM BUS 341908 [2MUNFVIL EK 69.000] TO BUS 341914 [2MUNFVILKU T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8357 | -6.3777e-06 | -0.00035197
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 383 341908-341914(1) | OPEN LINE FROM BUS 341908 [2MUNFVIL EK 69.000] TO BUS 341914 [2MUNFVILKU T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 384 341911-341914(1) | OPEN LINE FROM BUS 341911 [2MUNFVIL KU 69.000] TO BUS 341914 [2MUNFVILKU T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 3.7551e-06 | -0.00034183
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 384 341911-341914(1) | OPEN LINE FROM BUS 341911 [2MUNFVIL KU 69.000] TO BUS 341914 [2MUNFVILKU T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 385 341917-341998(1) | OPEN LINE FROM BUS 341917 [2MUNK 69.000] TO BUS 341998 [2OAKLEY NOEL69.000] CKT 1 | 0.93965 | 64.8362 | 0.93894 | 64.7865 | -0.00071931 | -0.0010649
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 385 341917-341998(1) | OPEN LINE FROM BUS 341917 [2MUNK 69.000] TO BUS 341998 [2OAKLEY NOEL69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 386 341920-341998(1) | OPEN LINE FROM BUS 341920 [2MUNK J 69.000] TO BUS 341998 [2OAKLEY NOEL69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 387 341920-342502(1) | OPEN LINE FROM BUS 341920 [2MUNK J 69.000] TO BUS 342502 [2WILLIAMSTWN69.000] CKT 1 | 0.93965 | 64.8362 | 0.93961 | 64.8331 | -4.375e-05 | -0.00038934
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 387 341920-342502(1) | OPEN LINE FROM BUS 341920 [2MUNK J 69.000] TO BUS 342502 [2WILLIAMSTWN69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 388 341923-342091(1) | OPEN LINE FROM BUS 341923 [2MURPHYSVIL 69.000] TO BUS 342091 [2PLUMVILLE 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93987 | 64.851 | 0.00021547 | -0.00013012
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 388 341923-342091(1) | OPEN LINE FROM BUS 341923 [2MURPHYSVIL 69.000] TO BUS 342091 [2PLUMVILLE 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 389 341923-342280(1) | OPEN LINE FROM BUS 341923 [2MURPHYSVIL 69.000] TO BUS 342280 [2SNOW HILL 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93908 | 64.7965 | -0.00057411 | -0.0009197
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 389 341923-342280(1) | OPEN LINE FROM BUS 341923 [2MURPHYSVIL 69.000] TO BUS 342280 [2SNOW HILL 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 390 341935-342208(1) | OPEN LINE FROM BUS 341935 [2N SPRINGFLD69.000] TO BUS 342208 [2S SPRINGF T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93968 | 64.8382 | 2.9564e-05 | -0.00031602
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 390 341935-342208(1) | OPEN LINE FROM BUS 341935 [2N SPRINGFLD69.000] TO BUS 342208 [2S SPRINGF T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 391 341938-342505(1) | OPEN LINE FROM BUS 341938 [2NANCY 69.000] TO BUS 342505 [2WINDSOR 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8354 | -1.1563e-05 | -0.00035715
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 391 341938-342505(1) | OPEN LINE FROM BUS 341938 [2NANCY 69.000] TO BUS 342505 [2WINDSOR 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 392 341938-342526(1) | OPEN LINE FROM BUS 341938 [2NANCY 69.000] TO BUS 342526 [2ZOLLICOF T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -8.9407e-07 | -0.00034648
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 392 341938-342526(1) | OPEN LINE FROM BUS 341938 [2NANCY 69.000] TO BUS 342526 [2ZOLLICOF T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 393 341941-341947(1) | OPEN LINE FROM BUS 341941 [2NELSN VAL T69.000] TO BUS 341947 [2NELSON VAL 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8369 | 1.0848e-05 | -0.00033474
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 393 341941-341947(1) | OPEN LINE FROM BUS 341941 [2NELSN VAL T69.000] TO BUS 341947 [2NELSON VAL 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 394 341941-341971(1) | OPEN LINE FROM BUS 341941 [2NELSN VAL T69.000] TO BUS 341971 [2NORWOOD 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8359 | -3.0994e-06 | -0.00034869
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 394 341941-341971(1) | OPEN LINE FROM BUS 341941 [2NELSN VAL T69.000] TO BUS 341971 [2NORWOOD 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 395 341944-342424(1) | OPEN LINE FROM BUS 341944 [2NELSON CO 69.000] TO BUS 342424 [2W BARDST J 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8358 | -5.7817e-06 | -0.00035137
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 395 341944-342424(1) | OPEN LINE FROM BUS 341944 [2NELSON CO 69.000] TO BUS 342424 [2W BARDST J 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 396 341944-342514(1) | OPEN LINE FROM BUS 341944 [2NELSON CO 69.000] TO BUS 342514 [2WOOSLEY 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 2.9802e-07 | -0.00034529
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 396 341944-342514(1) | OPEN LINE FROM BUS 341944 [2NELSON CO 69.000] TO BUS 342514 [2WOOSLEY 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 397 341950-342007(1) | OPEN LINE FROM BUS 341950 [2NEW CASTLE 69.000] TO BUS 342007 [2OWEN CO 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93979 | 64.8457 | 0.0001384 | -0.00020719
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 397 341950-342007(1) | OPEN LINE FROM BUS 341950 [2NEW CASTLE 69.000] TO BUS 342007 [2OWEN CO 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 398 341953-342229(1) | OPEN LINE FROM BUS 341953 [2NEW FOUNDL 69.000] TO BUS 342229 [2SANDY HOOK 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93974 | 64.8419 | 8.291e-05 | -0.00026268
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 398 341953-342229(1) | OPEN LINE FROM BUS 341953 [2NEW FOUNDL 69.000] TO BUS 342229 [2SANDY HOOK 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 399 341962-342361(1) | OPEN LINE FROM BUS 341962 [2NEWBY 2 69.000] TO BUS 342361 [2TODDVILLE T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8358 | -5.3048e-06 | -0.00035089
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 399 341962-342361(1) | OPEN LINE FROM BUS 341962 [2NEWBY 2 69.000] TO BUS 342361 [2TODDVILLE T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 400 341965-342199(1) | OPEN LINE FROM BUS 341965 [2NICHOLASVIL69.000] TO BUS 342199 [2S JESSAM J 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93974 | 64.8423 | 8.9765e-05 | -0.00025582
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 400 341965-342199(1) | OPEN LINE FROM BUS 341965 [2NICHOLASVIL69.000] TO BUS 342199 [2S JESSAM J 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 401 341971-342115(1) | OPEN LINE FROM BUS 341971 [2NORWOOD 69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8355 | -9.7156e-06 | -0.0003553
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 401 341971-342115(1) | OPEN LINE FROM BUS 341971 [2NORWOOD 69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341029 | 2ASAHI M W | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 402 341974-342256(1) | OPEN LINE FROM BUS 341974 [2NORWOOD T 69.000] TO BUS 342256 [2SHOPVILLE 69.000] CKT 1 | 0.96833 | 66.8145 | 0.93477 | 64.4993 | -0.033555 | -0.005228
341032 | 2ASAHI M W T | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 402 341974-342256(1) | OPEN LINE FROM BUS 341974 [2NORWOOD T 69.000] TO BUS 342256 [2SHOPVILLE 69.000] CKT 1 | 0.96914 | 66.8708 | 0.93562 | 64.5575 | -0.033526 | -0.0043839
341379 | 2DAHL ROAD | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 402 341974-342256(1) | OPEN LINE FROM BUS 341974 [2NORWOOD T 69.000] TO BUS 342256 [2SHOPVILLE 69.000] CKT 1 | 0.96945 | 66.8919 | 0.93516 | 64.5259 | -0.03429 | -0.0048421
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 402 341974-342256(1) | OPEN LINE FROM BUS 341974 [2NORWOOD T 69.000] TO BUS 342256 [2SHOPVILLE 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93959 | 64.8316 | -6.6102e-05 | -0.00041169
342256 | 2SHOPVILLE | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 402 341974-342256(1) | OPEN LINE FROM BUS 341974 [2NORWOOD T 69.000] TO BUS 342256 [2SHOPVILLE 69.000] CKT 1 | 0.97027 | 66.9485 | 0.93528 | 64.5345 | -0.034986 | -0.0047171
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 402 341974-342256(1) | OPEN LINE FROM BUS 341974 [2NORWOOD T 69.000] TO BUS 342256 [2SHOPVILLE 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 403 341977-341983(1) | OPEN LINE FROM BUS 341977 [2OAK HILL 69.000] TO BUS 341983 [2OAK HILL T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8369 | 1.1027e-05 | -0.00033456
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 403 341977-341983(1) | OPEN LINE FROM BUS 341977 [2OAK HILL 69.000] TO BUS 341983 [2OAK HILL T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 404 341980-341983(1) | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 341983 [2OAK HILL T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8365 | 5.5432e-06 | -0.00034004
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 404 341980-341983(1) | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 341983 [2OAK HILL T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 405 341980-342286(1) | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8365 | 5.3644e-06 | -0.00034022
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 405 341980-342286(1) | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 406 341983-342469(1) | OPEN LINE FROM BUS 341983 [2OAK HILL T 69.000] TO BUS 342469 [2W SOMERSET 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8358 | -4.5896e-06 | -0.00035018
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 406 341983-342469(1) | OPEN LINE FROM BUS 341983 [2OAK HILL T 69.000] TO BUS 342469 [2W SOMERSET 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 407 341986-341989(1) | OPEN LINE FROM BUS 341986 [2OAK RIDGE 69.000] TO BUS 341989 [2OAK RIDGE T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93975 | 64.8426 | 9.3043e-05 | -0.00025254
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 407 341986-341989(1) | OPEN LINE FROM BUS 341986 [2OAK RIDGE 69.000] TO BUS 341989 [2OAK RIDGE T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 408 342000-342703(1) | OPEN LINE FROM BUS 342000 [5GAS 161.00] TO BUS 342703 [5CASEY CO 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.837 | 1.2577e-05 | -0.00033301
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 408 342000-342703(1) | OPEN LINE FROM BUS 342000 [5GAS 161.00] TO BUS 342703 [5CASEY CO 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 409 342000-342760(1) | OPEN LINE FROM BUS 342000 [5GAS 161.00] TO BUS 342760 [5LIBERTY J 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93957 | 64.8302 | -8.6188e-05 | -0.00043178
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 409 342000-342760(1) | OPEN LINE FROM BUS 342000 [5GAS 161.00] TO BUS 342760 [5LIBERTY J 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 410 342007-342008(1) | OPEN LINE FROM BUS 342007 [2OWEN CO 69.000] TO BUS 342008 [4OWEN CO 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341200 | 2BROMLEYEK | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 411 342007-342010(1) | OPEN LINE FROM BUS 342007 [2OWEN CO 69.000] TO BUS 342010 [2OWEN CO J1 69.000] CKT 1 | 0.99203 | 68.4498 | 0.92151 | 63.5842 | -0.070517 | -0.01849
341917 | 2MUNK | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 411 342007-342010(1) | OPEN LINE FROM BUS 342007 [2OWEN CO 69.000] TO BUS 342010 [2OWEN CO J1 69.000] CKT 1 | 0.96446 | 66.5477 | 0.93694 | 64.6487 | -0.027522 | -0.0030628
341920 | 2MUNK J | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 411 342007-342010(1) | OPEN LINE FROM BUS 342007 [2OWEN CO 69.000] TO BUS 342010 [2OWEN CO J1 69.000] CKT 1 | 0.97761 | 67.4549 | 0.92619 | 63.9074 | -0.051413 | -0.013806
341998 | 2OAKLEY NOEL | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 411 342007-342010(1) | OPEN LINE FROM BUS 342007 [2OWEN CO 69.000] TO BUS 342010 [2OWEN CO J1 69.000] CKT 1 | 0.96812 | 66.8005 | 0.92984 | 64.1593 | -0.038279 | -0.010155
342010 | 2OWEN CO J1 | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 411 342007-342010(1) | OPEN LINE FROM BUS 342007 [2OWEN CO 69.000] TO BUS 342010 [2OWEN CO J1 69.000] CKT 1 | 0.99637 | 68.7494 | 0.92152 | 63.5848 | -0.07485 | -0.018482
342502 | 2WILLIAMSTWN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 411 342007-342010(1) | OPEN LINE FROM BUS 342007 [2OWEN CO 69.000] TO BUS 342010 [2OWEN CO J1 69.000] CKT 1 | 0.97778 | 67.467 | 0.92572 | 63.8746 | -0.052064 | -0.014282
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 411 342007-342010(1) | OPEN LINE FROM BUS 342007 [2OWEN CO 69.000] TO BUS 342010 [2OWEN CO J1 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 412 342007-342013(1) | OPEN LINE FROM BUS 342007 [2OWEN CO 69.000] TO BUS 342013 [2OWEN CO J2 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93971 | 64.8397 | 5.12e-05 | -0.00029439
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 412 342007-342013(1) | OPEN LINE FROM BUS 342007 [2OWEN CO 69.000] TO BUS 342013 [2OWEN CO J2 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 413 342016-342019(1) | OPEN LINE FROM BUS 342016 [2OWENS IL 69.000] TO BUS 342019 [2OWENS IL J 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8365 | 4.6492e-06 | -0.00034094
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 413 342016-342019(1) | OPEN LINE FROM BUS 342016 [2OWENS IL 69.000] TO BUS 342019 [2OWENS IL J 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 414 342022-342025(1) | OPEN LINE FROM BUS 342022 [2OWINGSVIL T69.000] TO BUS 342025 [2OWINGVIL KU69.000] CKT 1 | 0.93965 | 64.8362 | 0.93989 | 64.8521 | 0.00023162 | -0.00011396
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 414 342022-342025(1) | OPEN LINE FROM BUS 342022 [2OWINGSVIL T69.000] TO BUS 342025 [2OWINGVIL KU69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 1.1921e-07 | 1.1921e-07
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 415 342022-342052(1) | OPEN LINE FROM BUS 342022 [2OWINGSVIL T69.000] TO BUS 342052 [2PEASTICKS 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93912 | 64.7995 | -0.00053149 | -0.00087708
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 415 342022-342052(1) | OPEN LINE FROM BUS 342022 [2OWINGSVIL T69.000] TO BUS 342052 [2PEASTICKS 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 416 342022-342112(1) | OPEN LINE FROM BUS 342022 [2OWINGSVIL T69.000] TO BUS 342112 [2PRESTON T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93976 | 64.8437 | 0.00010949 | -0.00023609
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 416 342022-342112(1) | OPEN LINE FROM BUS 342022 [2OWINGSVIL T69.000] TO BUS 342112 [2PRESTON T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 417 342031-342034(1) | OPEN LINE FROM BUS 342031 [2PACTOLUS 69.000] TO BUS 342034 [2PACTOLUS T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93984 | 64.8489 | 0.00018412 | -0.00016147
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 417 342031-342034(1) | OPEN LINE FROM BUS 342031 [2PACTOLUS 69.000] TO BUS 342034 [2PACTOLUS T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 418 342037-342040(1) | OPEN LINE FROM BUS 342037 [2PARKWAY 1 69.000] TO BUS 342040 [2PARKWAY 2 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -4.7684e-07 | -0.00034606
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 418 342037-342040(1) | OPEN LINE FROM BUS 342037 [2PARKWAY 1 69.000] TO BUS 342040 [2PARKWAY 2 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 419 342049-342161(1) | OPEN LINE FROM BUS 342049 [2PATTON RD J69.000] TO BUS 342161 [2ROSEVILLE T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -2.9802e-07 | -0.00034589
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 419 342049-342161(1) | OPEN LINE FROM BUS 342049 [2PATTON RD J69.000] TO BUS 342161 [2ROSEVILLE T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 420 342049-342319(1) | OPEN LINE FROM BUS 342049 [2PATTON RD J69.000] TO BUS 342319 [2SUMM SHAD J69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 3.5763e-07 | -0.00034523
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 420 342049-342319(1) | OPEN LINE FROM BUS 342049 [2PATTON RD J69.000] TO BUS 342319 [2SUMM SHAD J69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 421 342067-342505(1) | OPEN LINE FROM BUS 342067 [2PHIL 69.000] TO BUS 342505 [2WINDSOR 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 3.8147e-06 | -0.00034177
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 421 342067-342505(1) | OPEN LINE FROM BUS 342067 [2PHIL 69.000] TO BUS 342505 [2WINDSOR 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 422 342070-342073(1) | OPEN LINE FROM BUS 342070 [2PINE GROVE 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.9397 | 64.8391 | 4.2021e-05 | -0.00030357
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 422 342070-342073(1) | OPEN LINE FROM BUS 342070 [2PINE GROVE 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 423 342073-342451(1) | OPEN LINE FROM BUS 342073 [2PINE GRV T 69.000] TO BUS 342451 [2W LONDON 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8351 | -1.5736e-05 | -0.00036132
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 423 342073-342451(1) | OPEN LINE FROM BUS 342073 [2PINE GRV T 69.000] TO BUS 342451 [2W LONDON 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 425 342085-342088(1) | OPEN LINE FROM BUS 342085 [2PLUMMR L 69.000] TO BUS 342088 [2PLUMMR L T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93974 | 64.8418 | 8.1539e-05 | -0.00026405
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 425 342085-342088(1) | OPEN LINE FROM BUS 342085 [2PLUMMR L 69.000] TO BUS 342088 [2PLUMMR L T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 426 342091-342124(1) | OPEN LINE FROM BUS 342091 [2PLUMVILLE 69.000] TO BUS 342124 [2RECTORVILLE69.000] CKT 1 | 0.93965 | 64.8362 | 0.93991 | 64.8538 | 0.00025594 | -8.9645e-05
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 426 342091-342124(1) | OPEN LINE FROM BUS 342091 [2PLUMVILLE 69.000] TO BUS 342124 [2RECTORVILLE69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 427 342091-342634(1) | OPEN LINE FROM BUS 342091 [2PLUMVILLE 69.000] TO BUS 342634 [4PLUMVILLE 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93927 | 64.8098 | -0.00038177 | -0.00072736
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 427 342091-342634(1) | OPEN LINE FROM BUS 342091 [2PLUMVILLE 69.000] TO BUS 342634 [4PLUMVILLE 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 428 342097-342184(1) | OPEN LINE FROM BUS 342097 [2POWEL TAYL 69.000] TO BUS 342184 [2S ANDERSON 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8376 | 2.0385e-05 | -0.0003252
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 428 342097-342184(1) | OPEN LINE FROM BUS 342097 [2POWEL TAYL 69.000] TO BUS 342184 [2S ANDERSON 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 429 342100-342301(1) | OPEN LINE FROM BUS 342100 [2POWELL CO 69.000] TO BUS 342301 [2STANTON 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93947 | 64.8234 | -0.0001843 | -0.00052989
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 429 342100-342301(1) | OPEN LINE FROM BUS 342100 [2POWELL CO 69.000] TO BUS 342301 [2STANTON 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 430 342100-342637(1) | OPEN LINE FROM BUS 342100 [2POWELL CO 69.000] TO BUS 342637 [4POWELL CO 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93913 | 64.7999 | -0.00052613 | -0.00087172
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 430 342100-342637(1) | OPEN LINE FROM BUS 342100 [2POWELL CO 69.000] TO BUS 342637 [4POWELL CO 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 431 342103-342106(1) | OPEN LINE FROM BUS 342103 [2PPG 69.000] TO BUS 342106 [2PPG J 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8367 | 7.9274e-06 | -0.00033766
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 431 342103-342106(1) | OPEN LINE FROM BUS 342103 [2PPG 69.000] TO BUS 342106 [2PPG J 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 432 342109-342112(1) | OPEN LINE FROM BUS 342109 [2PRESTON 69.000] TO BUS 342112 [2PRESTON T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.9397 | 64.8394 | 4.6551e-05 | -0.00029904
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 432 342109-342112(1) | OPEN LINE FROM BUS 342109 [2PRESTON 69.000] TO BUS 342112 [2PRESTON T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 433 342115-342787(1) | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93963 | 64.8344 | -2.5451e-05 | -0.00037104
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 433 342115-342787(1) | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 434 342118-342121(1) | OPEN LINE FROM BUS 342118 [2RADCLIFF 69.000] TO BUS 342121 [2T BROWN L T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8359 | -3.159e-06 | -0.00034875
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 434 342118-342121(1) | OPEN LINE FROM BUS 342118 [2RADCLIFF 69.000] TO BUS 342121 [2T BROWN L T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 435 342121-342328(1) | OPEN LINE FROM BUS 342121 [2T BROWN L T69.000] TO BUS 342328 [2T BROWN LOG69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -2.9206e-06 | -0.00034851
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 435 342121-342328(1) | OPEN LINE FROM BUS 342121 [2T BROWN L T69.000] TO BUS 342328 [2T BROWN LOG69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 436 342121-342415(1) | OPEN LINE FROM BUS 342121 [2T BROWN L T69.000] TO BUS 342415 [2VINE GROV J69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8357 | -6.0201e-06 | -0.00035161
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 436 342121-342415(1) | OPEN LINE FROM BUS 342121 [2T BROWN L T69.000] TO BUS 342415 [2VINE GROV J69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 437 342127-342265(1) | OPEN LINE FROM BUS 342127 [2REDBUSH 69.000] TO BUS 342265 [2SKAGGS 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93977 | 64.8443 | 0.00011873 | -0.00022686
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 437 342127-342265(1) | OPEN LINE FROM BUS 342127 [2REDBUSH 69.000] TO BUS 342265 [2SKAGGS 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 438 342127-342421(1) | OPEN LINE FROM BUS 342127 [2REDBUSH 69.000] TO BUS 342421 [2VOLGA 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93975 | 64.8426 | 9.2924e-05 | -0.00025266
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 438 342127-342421(1) | OPEN LINE FROM BUS 342127 [2REDBUSH 69.000] TO BUS 342421 [2VOLGA 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 439 342130-342259(1) | OPEN LINE FROM BUS 342130 [2REID VILLAG69.000] TO BUS 342259 [2SIDEVIEW 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 441 342133-342640(1) | OPEN LINE FROM BUS 342133 [2RENAKER 69.000] TO BUS 342640 [4RENAKER 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 442 342136-342139(1) | OPEN LINE FROM BUS 342136 [2REVELO KU 69.000] TO BUS 342139 [2REVELO KU T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 2.9206e-06 | -0.00034267
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 442 342136-342139(1) | OPEN LINE FROM BUS 342136 [2REVELO KU 69.000] TO BUS 342139 [2REVELO KU T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 443 342145-342487(1) | OPEN LINE FROM BUS 342145 [2RICHARDSON 69.000] TO BUS 342487 [2WEBSTER RD 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 444 342154-342155(1) | OPEN LINE FROM BUS 342154 [2ROANOKE 69.000] TO BUS 342155 [2ROANOKE T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.1325e-06 | -0.00034672
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 444 342154-342155(1) | OPEN LINE FROM BUS 342154 [2ROANOKE 69.000] TO BUS 342155 [2ROANOKE T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 445 342157-342418(1) | OPEN LINE FROM BUS 342157 [2ROGERSVIL J69.000] TO BUS 342418 [2VINE GROVE 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8355 | -9.4771e-06 | -0.00035506
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 445 342157-342418(1) | OPEN LINE FROM BUS 342157 [2ROGERSVIL J69.000] TO BUS 342418 [2VINE GROVE 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 446 342160-342161(1) | OPEN LINE FROM BUS 342160 [2ROSEVILLE 69.000] TO BUS 342161 [2ROSEVILLE T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.0729e-06 | -0.00034666
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 446 342160-342161(1) | OPEN LINE FROM BUS 342160 [2ROSEVILLE 69.000] TO BUS 342161 [2ROSEVILLE T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 447 342161-342334(1) | OPEN LINE FROM BUS 342161 [2ROSEVILLE T69.000] TO BUS 342334 [2TEMPLE HILL69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 5.9605e-08 | -0.00034553
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 447 342161-342334(1) | OPEN LINE FROM BUS 342161 [2ROSEVILLE T69.000] TO BUS 342334 [2TEMPLE HILL69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 448 342163-342649(1) | OPEN LINE FROM BUS 342163 [2ROWAN CO 69.000] TO BUS 342649 [4ROWAN CO 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93962 | 64.8336 | -3.6418e-05 | -0.00038201
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 448 342163-342649(1) | OPEN LINE FROM BUS 342163 [2ROWAN CO 69.000] TO BUS 342649 [4ROWAN CO 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 449 342166-342169(1) | OPEN LINE FROM BUS 342166 [2RUSS SPEK T69.000] TO BUS 342169 [2RUSS SPKU T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8367 | 7.7486e-06 | -0.00033784
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 449 342166-342169(1) | OPEN LINE FROM BUS 342166 [2RUSS SPEK T69.000] TO BUS 342169 [2RUSS SPKU T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 450 342166-342172(1) | OPEN LINE FROM BUS 342166 [2RUSS SPEK T69.000] TO BUS 342172 [2RUSS SPR EK69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 3.8743e-06 | -0.00034171
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 450 342166-342172(1) | OPEN LINE FROM BUS 342166 [2RUSS SPEK T69.000] TO BUS 342172 [2RUSS SPR EK69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 451 342166-342235(1) | OPEN LINE FROM BUS 342166 [2RUSS SPEK T69.000] TO BUS 342235 [2SEWELTN J 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8358 | -4.828e-06 | -0.00035042
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 451 342166-342235(1) | OPEN LINE FROM BUS 342166 [2RUSS SPEK T69.000] TO BUS 342235 [2SEWELTN J 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 452 342169-342175(1) | OPEN LINE FROM BUS 342169 [2RUSS SPKU T69.000] TO BUS 342175 [2RUSS SPR KU69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8367 | 7.2122e-06 | -0.00033838
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 452 342169-342175(1) | OPEN LINE FROM BUS 342169 [2RUSS SPKU T69.000] TO BUS 342175 [2RUSS SPR KU69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 453 342169-342178(1) | OPEN LINE FROM BUS 342169 [2RUSS SPKU T69.000] TO BUS 342178 [2RUSSEL CO 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8369 | 1.1265e-05 | -0.00033432
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 453 342169-342178(1) | OPEN LINE FROM BUS 342169 [2RUSS SPKU T69.000] TO BUS 342178 [2RUSSEL CO 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 454 342178-342232(1) | OPEN LINE FROM BUS 342178 [2RUSSEL CO 69.000] TO BUS 342232 [2SEWELLTON 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8358 | -5.5432e-06 | -0.00035113
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 454 342178-342232(1) | OPEN LINE FROM BUS 342178 [2RUSSEL CO 69.000] TO BUS 342232 [2SEWELLTON 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 455 342178-342793(1) | OPEN LINE FROM BUS 342178 [2RUSSEL CO 69.000] TO BUS 342793 [5RUSSEL CO 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 3.159e-06 | -0.00034243
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 455 342178-342793(1) | OPEN LINE FROM BUS 342178 [2RUSSEL CO 69.000] TO BUS 342793 [5RUSSEL CO 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 456 342184-342262(1) | OPEN LINE FROM BUS 342184 [2S ANDERSON 69.000] TO BUS 342262 [2SINAI 69.000] CKT 1 | 0.93965 | 64.8362 | 0.9397 | 64.8394 | 4.7207e-05 | -0.00029838
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 456 342184-342262(1) | OPEN LINE FROM BUS 342184 [2S ANDERSON 69.000] TO BUS 342262 [2SINAI 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 457 342186-342424(1) | OPEN LINE FROM BUS 342186 [2S BARDSTWN 69.000] TO BUS 342424 [2W BARDST J 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 2.6226e-06 | -0.00034297
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 457 342186-342424(1) | OPEN LINE FROM BUS 342186 [2S BARDSTWN 69.000] TO BUS 342424 [2W BARDST J 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 458 342186-342427(1) | OPEN LINE FROM BUS 342186 [2S BARDSTWN 69.000] TO BUS 342427 [2W BARDSTWN 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 1.0133e-06 | -0.00034457
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 458 342186-342427(1) | OPEN LINE FROM BUS 342186 [2S BARDSTWN 69.000] TO BUS 342427 [2W BARDSTWN 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 459 342196-342391(1) | OPEN LINE FROM BUS 342196 [2WHITE OAK 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8353 | -1.1683e-05 | -0.00035727
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 459 342196-342391(1) | OPEN LINE FROM BUS 342196 [2WHITE OAK 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 460 342199-342202(1) | OPEN LINE FROM BUS 342199 [2S JESSAM J 69.000] TO BUS 342202 [2S JESSAMINE69.000] CKT 1 | 0.93965 | 64.8362 | 0.93978 | 64.8447 | 0.00012434 | -0.00022125
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 460 342199-342202(1) | OPEN LINE FROM BUS 342199 [2S JESSAM J 69.000] TO BUS 342202 [2S JESSAMINE69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 461 342208-342211(1) | OPEN LINE FROM BUS 342208 [2S SPRINGF T69.000] TO BUS 342211 [2S SPRINGFLD69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 2.8014e-06 | -0.00034279
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 461 342208-342211(1) | OPEN LINE FROM BUS 342208 [2S SPRINGF T69.000] TO BUS 342211 [2S SPRINGFLD69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 462 342214-342217(1) | OPEN LINE FROM BUS 342214 [2SALEM EK 69.000] TO BUS 342217 [2SALEM EK T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8367 | 8.4043e-06 | -0.00033718
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 462 342214-342217(1) | OPEN LINE FROM BUS 342214 [2SALEM EK 69.000] TO BUS 342217 [2SALEM EK T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 463 342217-342481(1) | OPEN LINE FROM BUS 342217 [2SALEM EK T 69.000] TO BUS 342481 [2WEBB CR R T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -9.5367e-07 | -0.00034654
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 463 342217-342481(1) | OPEN LINE FROM BUS 342217 [2SALEM EK T 69.000] TO BUS 342481 [2WEBB CR R T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 464 342217-342505(1) | OPEN LINE FROM BUS 342217 [2SALEM EK T 69.000] TO BUS 342505 [2WINDSOR 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.837 | 1.2219e-05 | -0.00033337
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 464 342217-342505(1) | OPEN LINE FROM BUS 342217 [2SALEM EK T 69.000] TO BUS 342505 [2WINDSOR 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 465 342220-342223(1) | OPEN LINE FROM BUS 342220 [2SAND GAP 69.000] TO BUS 342223 [2SAND GAP T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8373 | 1.6928e-05 | -0.00032866
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 465 342220-342223(1) | OPEN LINE FROM BUS 342220 [2SAND GAP 69.000] TO BUS 342223 [2SAND GAP T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 466 342235-342481(1) | OPEN LINE FROM BUS 342235 [2SEWELTN J 69.000] TO BUS 342481 [2WEBB CR R T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8356 | -8.4043e-06 | -0.00035399
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 466 342235-342481(1) | OPEN LINE FROM BUS 342235 [2SEWELTN J 69.000] TO BUS 342481 [2WEBB CR R T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 467 342238-342241(1) | OPEN LINE FROM BUS 342238 [2SEYMOUR 69.000] TO BUS 342241 [2SEYMOUR T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -7.7486e-07 | -0.00034636
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 467 342238-342241(1) | OPEN LINE FROM BUS 342238 [2SEYMOUR 69.000] TO BUS 342241 [2SEYMOUR T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 468 342247-342248(1) | OPEN LINE FROM BUS 342247 [2SHELBY CO 69.000] TO BUS 342248 [2SHELBY TAP 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 3.6955e-06 | -0.00034189
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 468 342247-342248(1) | OPEN LINE FROM BUS 342247 [2SHELBY CO 69.000] TO BUS 342248 [2SHELBY TAP 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 469 342247-342410(1) | OPEN LINE FROM BUS 342247 [2SHELBY CO 69.000] TO BUS 342410 [2VEECHDALE 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 1.2517e-06 | -0.00034434
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 469 342247-342410(1) | OPEN LINE FROM BUS 342247 [2SHELBY CO 69.000] TO BUS 342410 [2VEECHDALE 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 470 342247-342808(1) | OPEN LINE FROM BUS 342247 [2SHELBY CO 69.000] TO BUS 342808 [5SHELBY CO 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93971 | 64.8397 | 5.0902e-05 | -0.00029469
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 470 342247-342808(1) | OPEN LINE FROM BUS 342247 [2SHELBY CO 69.000] TO BUS 342808 [5SHELBY CO 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 471 342250-342253(1) | OPEN LINE FROM BUS 342250 [2SHEPHEVIL 69.000] TO BUS 342253 [2SHEPHEVIL J69.000] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.835 | -1.6809e-05 | -0.0003624
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 471 342250-342253(1) | OPEN LINE FROM BUS 342250 [2SHEPHEVIL 69.000] TO BUS 342253 [2SHEPHEVIL J69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 472 342265-342658(1) | OPEN LINE FROM BUS 342265 [2SKAGGS 69.000] TO BUS 342658 [4SKAGGS 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 473 342268-342478(1) | OPEN LINE FROM BUS 342268 [2SLAT 69.000] TO BUS 342478 [2WAYNE CO 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93971 | 64.8402 | 5.9307e-05 | -0.00028628
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 473 342268-342478(1) | OPEN LINE FROM BUS 342268 [2SLAT 69.000] TO BUS 342478 [2WAYNE CO 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 474 342271-342274(1) | OPEN LINE FROM BUS 342271 [2SMITHRSVIL 69.000] TO BUS 342274 [2SMITHRVIL T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8358 | -5.1856e-06 | -0.00035077
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 475 342277-342283(1) | OPEN LINE FROM BUS 342277 [2SNOW 69.000] TO BUS 342283 [2SNOW T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8359 | -3.2783e-06 | -0.00034887
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 475 342277-342283(1) | OPEN LINE FROM BUS 342277 [2SNOW 69.000] TO BUS 342283 [2SNOW T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 476 342283-342322(1) | OPEN LINE FROM BUS 342283 [2SNOW T 69.000] TO BUS 342322 [2SUMM SHADE 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8358 | -5.1856e-06 | -0.00035077
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 476 342283-342322(1) | OPEN LINE FROM BUS 342283 [2SNOW T 69.000] TO BUS 342322 [2SUMM SHADE 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 477 342286-342287(1) | OPEN LINE FROM BUS 342286 [2SOMERSET 69.000] TO BUS 342287 [2SOMERSET KU69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8358 | -5.5432e-06 | -0.00035113
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 477 342286-342287(1) | OPEN LINE FROM BUS 342286 [2SOMERSET 69.000] TO BUS 342287 [2SOMERSET KU69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 478 342292-342295(1) | OPEN LINE FROM BUS 342292 [2STANLEY PRK69.000] TO BUS 342295 [2STANLY P J169.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 479 342292-342298(1) | OPEN LINE FROM BUS 342292 [2STANLEY PRK69.000] TO BUS 342298 [2STANLY P J269.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 480 342292-342667(1) | OPEN LINE FROM BUS 342292 [2STANLEY PRK69.000] TO BUS 342667 [4STANLEY PRK138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 481 342307-342403(1) | OPEN LINE FROM BUS 342307 [2STEPHENSBRG69.000] TO BUS 342403 [2UPTON T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8359 | -3.4571e-06 | -0.00034904
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 481 342307-342403(1) | OPEN LINE FROM BUS 342307 [2STEPHENSBRG69.000] TO BUS 342403 [2UPTON T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 482 342307-342412(1) | OPEN LINE FROM BUS 342307 [2STEPHENSBRG69.000] TO BUS 342412 [2VERTREES 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -2.0862e-06 | -0.00034767
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 482 342307-342412(1) | OPEN LINE FROM BUS 342307 [2STEPHENSBRG69.000] TO BUS 342412 [2VERTREES 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 483 342319-342322(1) | OPEN LINE FROM BUS 342319 [2SUMM SHAD J69.000] TO BUS 342322 [2SUMM SHADE 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 1.1325e-06 | -0.00034446
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 483 342319-342322(1) | OPEN LINE FROM BUS 342319 [2SUMM SHAD J69.000] TO BUS 342322 [2SUMM SHADE 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 484 342319-342334(1) | OPEN LINE FROM BUS 342319 [2SUMM SHAD J69.000] TO BUS 342334 [2TEMPLE HILL69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 2.9802e-07 | -0.00034529
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 484 342319-342334(1) | OPEN LINE FROM BUS 342319 [2SUMM SHAD J69.000] TO BUS 342334 [2TEMPLE HILL69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 485 342322-342436(1) | OPEN LINE FROM BUS 342322 [2SUMM SHADE 69.000] TO BUS 342436 [2W COLUMBI T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 4.1723e-07 | -0.00034517
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 485 342322-342436(1) | OPEN LINE FROM BUS 342322 [2SUMM SHADE 69.000] TO BUS 342436 [2W COLUMBI T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 486 342322-342814(1) | OPEN LINE FROM BUS 342322 [2SUMM SHADE 69.000] TO BUS 342814 [5SUMM SHADE 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8366 | 6.9737e-06 | -0.00033861
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 486 342322-342814(1) | OPEN LINE FROM BUS 342322 [2SUMM SHADE 69.000] TO BUS 342814 [5SUMM SHADE 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 487 342337-342340(1) | OPEN LINE FROM BUS 342337 [2THARP 69.000] TO BUS 342340 [2THARP T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8359 | -3.7551e-06 | -0.00034934
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 487 342337-342340(1) | OPEN LINE FROM BUS 342337 [2THARP 69.000] TO BUS 342340 [2THARP T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 488 342343-342421(1) | OPEN LINE FROM BUS 342343 [2THELMA 69.000] TO BUS 342421 [2VOLGA 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93957 | 64.8307 | -7.9572e-05 | -0.00042516
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 488 342343-342421(1) | OPEN LINE FROM BUS 342343 [2THELMA 69.000] TO BUS 342421 [2VOLGA 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 489 342349-342433(1) | OPEN LINE FROM BUS 342349 [2THREE LNK J69.000] TO BUS 342433 [2W BEREA J 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93976 | 64.8434 | 0.00010544 | -0.00024015
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 489 342349-342433(1) | OPEN LINE FROM BUS 342349 [2THREE LNK J69.000] TO BUS 342433 [2W BEREA J 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 490 342352-342355(1) | OPEN LINE FROM BUS 342352 [2THREE M 69.000] TO BUS 342355 [2THREE M T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 491 342358-342361(1) | OPEN LINE FROM BUS 342358 [2TODDVILLE 69.000] TO BUS 342361 [2TODDVILLE T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93968 | 64.8376 | 2.0921e-05 | -0.00032467
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 491 342358-342361(1) | OPEN LINE FROM BUS 342358 [2TODDVILLE 69.000] TO BUS 342361 [2TODDVILLE T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 492 342364-342367(1) | OPEN LINE FROM BUS 342364 [2TOMM GOOC 69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 3.6955e-06 | -0.00034189
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 492 342364-342367(1) | OPEN LINE FROM BUS 342364 [2TOMM GOOC 69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 493 342367-942410(1) | OPEN LINE FROM BUS 342367 [2TOMM GOOC T69.000] TO BUS 942410 [AE2-254 TAP 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93969 | 64.8386 | 3.5524e-05 | -0.00031006
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 493 342367-942410(1) | OPEN LINE FROM BUS 342367 [2TOMM GOOC T69.000] TO BUS 942410 [AE2-254 TAP 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 494 342379-342382(1) | OPEN LINE FROM BUS 342379 [2TUNNEL H T 69.000] TO BUS 342382 [2TUNNEL HILL69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8358 | -5.424e-06 | -0.00035101
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 494 342379-342382(1) | OPEN LINE FROM BUS 342379 [2TUNNEL H T 69.000] TO BUS 342382 [2TUNNEL HILL69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 1.1921e-07 | 1.1921e-07
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 495 342385-342487(1) | OPEN LINE FROM BUS 342385 [2TURKEY FT 69.000] TO BUS 342487 [2WEBSTER RD 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 496 342391-342820(1) | OPEN LINE FROM BUS 342391 [2TYNER 69.000] TO BUS 342820 [5TYNER 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8352 | -1.3292e-05 | -0.00035888
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 496 342391-342820(1) | OPEN LINE FROM BUS 342391 [2TYNER 69.000] TO BUS 342820 [5TYNER 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 497 342394-342397(1) | OPEN LINE FROM BUS 342394 [2UPCHURCH 69.000] TO BUS 342397 [2UPCHURCH T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 1.5497e-06 | -0.00034404
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 497 342394-342397(1) | OPEN LINE FROM BUS 342394 [2UPCHURCH 69.000] TO BUS 342397 [2UPCHURCH T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 1.1921e-07 | 1.1921e-07
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 498 342397-342532(1) | OPEN LINE FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 2.4438e-06 | -0.00034314
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 498 342397-342532(1) | OPEN LINE FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 499 342400-342403(1) | OPEN LINE FROM BUS 342400 [2UPTON 69.000] TO BUS 342403 [2UPTON T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.1325e-06 | -0.00034672
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 499 342400-342403(1) | OPEN LINE FROM BUS 342400 [2UPTON 69.000] TO BUS 342403 [2UPTON T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 500 342415-342418(1) | OPEN LINE FROM BUS 342415 [2VINE GROV J69.000] TO BUS 342418 [2VINE GROVE 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8357 | -6.0201e-06 | -0.00035161
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 500 342415-342418(1) | OPEN LINE FROM BUS 342415 [2VINE GROV J69.000] TO BUS 342418 [2VINE GROVE 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 501 342430-342433(1) | OPEN LINE FROM BUS 342430 [2W BEREA 69.000] TO BUS 342433 [2W BEREA J 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93976 | 64.8434 | 0.00010532 | -0.00024027
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 501 342430-342433(1) | OPEN LINE FROM BUS 342430 [2W BEREA 69.000] TO BUS 342433 [2W BEREA J 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 502 342430-342691(1) | OPEN LINE FROM BUS 342430 [2W BEREA 69.000] TO BUS 342691 [4W BEREA 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 503 342436-342439(1) | OPEN LINE FROM BUS 342436 [2W COLUMBI T69.000] TO BUS 342439 [2W COLUMBIA 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 8.9407e-07 | -0.00034469
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 503 342436-342439(1) | OPEN LINE FROM BUS 342436 [2W COLUMBI T69.000] TO BUS 342439 [2W COLUMBIA 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 504 342442-342445(1) | OPEN LINE FROM BUS 342442 [2W GLASGOW 69.000] TO BUS 342445 [2W GLASGOW T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.3709e-06 | -0.00034696
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 504 342442-342445(1) | OPEN LINE FROM BUS 342442 [2W GLASGOW 69.000] TO BUS 342445 [2W GLASGOW T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 1.1921e-07 | 1.1921e-07
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 505 342460-342463(1) | OPEN LINE FROM BUS 342460 [2W NICHVIL 69.000] TO BUS 342463 [2W NICHVIL T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93981 | 64.8472 | 0.00015944 | -0.00018615
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 505 342460-342463(1) | OPEN LINE FROM BUS 342460 [2W NICHVIL 69.000] TO BUS 342463 [2W NICHVIL T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 506 342469-342526(1) | OPEN LINE FROM BUS 342469 [2W SOMERSET 69.000] TO BUS 342526 [2ZOLLICOF T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8365 | 4.2915e-06 | -0.0003413
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 506 342469-342526(1) | OPEN LINE FROM BUS 342469 [2W SOMERSET 69.000] TO BUS 342526 [2ZOLLICOF T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 507 342472-342511(1) | OPEN LINE FROM BUS 342472 [2WALNUT GROV69.000] TO BUS 342511 [2WOODSTOCK 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8355 | -1.0014e-05 | -0.0003556
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 507 342472-342511(1) | OPEN LINE FROM BUS 342472 [2WALNUT GROV69.000] TO BUS 342511 [2WOODSTOCK 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 508 342478-342532(1) | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 2.4438e-06 | -0.00034314
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 508 342478-342532(1) | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 509 342478-342535(1) | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342535 [2ZULA T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 2.2054e-06 | -0.00034338
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 509 342478-342535(1) | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342535 [2ZULA T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 510 342478-342823(1) | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93969 | 64.8388 | 3.8207e-05 | -0.00030738
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 510 342478-342823(1) | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 511 342481-342484(1) | OPEN LINE FROM BUS 342481 [2WEBB CR R T69.000] TO BUS 342484 [2WEBB CR RDS69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 3.3975e-06 | -0.00034219
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 511 342481-342484(1) | OPEN LINE FROM BUS 342481 [2WEBB CR R T69.000] TO BUS 342484 [2WEBB CR RDS69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 512 342490-342493(1) | OPEN LINE FROM BUS 342490 [2WHITLEY CTY69.000] TO BUS 342493 [2WHITLY C KU69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8366 | 6.3777e-06 | -0.00033921
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 512 342490-342493(1) | OPEN LINE FROM BUS 342490 [2WHITLEY CTY69.000] TO BUS 342493 [2WHITLY C KU69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 513 342490-342499(1) | OPEN LINE FROM BUS 342490 [2WHITLEY CTY69.000] TO BUS 342499 [2WIBORG T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8359 | -3.6955e-06 | -0.00034928
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 513 342490-342499(1) | OPEN LINE FROM BUS 342490 [2WHITLEY CTY69.000] TO BUS 342499 [2WIBORG T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 514 342496-342499(1) | OPEN LINE FROM BUS 342496 [2WIBORG 69.000] TO BUS 342499 [2WIBORG T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8366 | 5.9605e-06 | -0.00033963
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 514 342496-342499(1) | OPEN LINE FROM BUS 342496 [2WIBORG 69.000] TO BUS 342499 [2WIBORG T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 515 342523-342526(1) | OPEN LINE FROM BUS 342523 [2ZOLLICOF 69.000] TO BUS 342526 [2ZOLLICOF T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8365 | 4.7088e-06 | -0.00034088
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 515 342523-342526(1) | OPEN LINE FROM BUS 342523 [2ZOLLICOF 69.000] TO BUS 342526 [2ZOLLICOF T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 516 342529-342535(1) | OPEN LINE FROM BUS 342529 [2ZULA 69.000] TO BUS 342535 [2ZULA T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 2.265e-06 | -0.00034332
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 516 342529-342535(1) | OPEN LINE FROM BUS 342529 [2ZULA 69.000] TO BUS 342535 [2ZULA T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 517 342538-342616(1) | OPEN LINE FROM BUS 342538 [4ARGENTUM 138.00] TO BUS 342616 [4LOVE HYDRO 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93957 | 64.8302 | -8.6427e-05 | -0.00043201
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 517 342538-342616(1) | OPEN LINE FROM BUS 342538 [4ARGENTUM 138.00] TO BUS 342616 [4LOVE HYDRO 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 518 342541-342544(1) | OPEN LINE FROM BUS 342541 [4AVON 138.00] TO BUS 342544 [4AVON-R 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 519 342541-342556(1) | OPEN LINE FROM BUS 342541 [4AVON 138.00] TO BUS 342556 [4BECKNERV T 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8349 | -1.7464e-05 | -0.00036305
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 519 342541-342556(1) | OPEN LINE FROM BUS 342541 [4AVON 138.00] TO BUS 342556 [4BECKNERV T 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 520 342541-342580(1) | OPEN LINE FROM BUS 342541 [4AVON 138.00] TO BUS 342580 [4FAYETTE 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93996 | 64.857 | 0.00030166 | -4.3929e-05
342580 | 4FAYETTE | 138 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 520 342541-342580(1) | OPEN LINE FROM BUS 342541 [4AVON 138.00] TO BUS 342580 [4FAYETTE 138.00] CKT 1 | 1.0015 | 138.2127 | 0.9329 | 128.7396 | -0.068646 | -0.0071044
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 520 342541-342580(1) | OPEN LINE FROM BUS 342541 [4AVON 138.00] TO BUS 342580 [4FAYETTE 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 521 342541-342631(1) | OPEN LINE FROM BUS 342541 [4AVON 138.00] TO BUS 342631 [4PARIS T 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 522 342541-342829(1) | OPEN LINE FROM BUS 342541 [4AVON 138.00] TO BUS 342829 [7AVON 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 1.1921e-07 | 1.1921e-07
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 523 342550-342559(1) | OPEN LINE FROM BUS 342550 [4BAVARIAN LF138.00] TO BUS 342559 [4BOONE CO 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93937 | 64.8163 | -0.00028825 | -0.00063384
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 523 342550-342559(1) | OPEN LINE FROM BUS 342550 [4BAVARIAN LF138.00] TO BUS 342559 [4BOONE CO 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 524 342550-342640(1) | OPEN LINE FROM BUS 342550 [4BAVARIAN LF138.00] TO BUS 342640 [4RENAKER 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93914 | 64.8005 | -0.00051707 | -0.00086266
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 524 342550-342640(1) | OPEN LINE FROM BUS 342550 [4BAVARIAN LF138.00] TO BUS 342640 [4RENAKER 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 525 342553-342556(1) | OPEN LINE FROM BUS 342553 [4BECKNERV 138.00] TO BUS 342556 [4BECKNERV T 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8368 | 9.954e-06 | -0.00033563
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 525 342553-342556(1) | OPEN LINE FROM BUS 342553 [4BECKNERV 138.00] TO BUS 342556 [4BECKNERV T 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 526 342556-342565(1) | OPEN LINE FROM BUS 342556 [4BECKNERV T 138.00] TO BUS 342565 [4BOONESBOR T138.00] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8355 | -1.0014e-05 | -0.0003556
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 526 342556-342565(1) | OPEN LINE FROM BUS 342556 [4BECKNERV T 138.00] TO BUS 342565 [4BOONESBOR T138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 527 342559-342646(1) | OPEN LINE FROM BUS 342559 [4BOONE CO 138.00] TO BUS 342646 [4RICHWOOD T 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 529 342565-342574(1) | OPEN LINE FROM BUS 342565 [4BOONESBOR T138.00] TO BUS 342574 [4DALE 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93922 | 64.8061 | -0.00043607 | -0.00078166
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 529 342565-342574(1) | OPEN LINE FROM BUS 342565 [4BOONESBOR T138.00] TO BUS 342574 [4DALE 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 530 342571-342589(1) | OPEN LINE FROM BUS 342571 [4CRANSTON 138.00] TO BUS 342589 [4GODDARD 138.00] CKT 1 | 0.93965 | 64.8362 | 0.9384 | 64.7497 | -0.0012533 | -0.0015989
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 530 342571-342589(1) | OPEN LINE FROM BUS 342571 [4CRANSTON 138.00] TO BUS 342589 [4GODDARD 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 531 342571-342649(1) | OPEN LINE FROM BUS 342571 [4CRANSTON 138.00] TO BUS 342649 [4ROWAN CO 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93893 | 64.7859 | -0.00072891 | -0.0010745
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 531 342571-342649(1) | OPEN LINE FROM BUS 342571 [4CRANSTON 138.00] TO BUS 342649 [4ROWAN CO 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 532 342574-342596(1) | OPEN LINE FROM BUS 342574 [4DALE 138.00] TO BUS 342596 [4HUNT 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93931 | 64.8125 | -0.00034261 | -0.0006882
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 532 342574-342596(1) | OPEN LINE FROM BUS 342574 [4DALE 138.00] TO BUS 342596 [4HUNT 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 533 342574-342676(1) | OPEN LINE FROM BUS 342574 [4DALE 138.00] TO BUS 342676 [4THREE FK T 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93977 | 64.8444 | 0.00011921 | -0.00022638
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 533 342574-342676(1) | OPEN LINE FROM BUS 342574 [4DALE 138.00] TO BUS 342676 [4THREE FK T 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 534 342577-342607(1) | OPEN LINE FROM BUS 342577 [4FAWKES EK 138.00] TO BUS 342607 [4JK SMITH 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93925 | 64.808 | -0.00040847 | -0.00075406
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 534 342577-342607(1) | OPEN LINE FROM BUS 342577 [4FAWKES EK 138.00] TO BUS 342607 [4JK SMITH 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 535 342577-342676(1) | OPEN LINE FROM BUS 342577 [4FAWKES EK 138.00] TO BUS 342676 [4THREE FK T 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93977 | 64.8441 | 0.00011575 | -0.00022984
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 535 342577-342676(1) | OPEN LINE FROM BUS 342577 [4FAWKES EK 138.00] TO BUS 342676 [4THREE FK T 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 536 342577-342691(1) | OPEN LINE FROM BUS 342577 [4FAWKES EK 138.00] TO BUS 342691 [4W BEREA 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93999 | 64.8593 | 0.00033534 | -1.0252e-05
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 536 342577-342691(1) | OPEN LINE FROM BUS 342577 [4FAWKES EK 138.00] TO BUS 342691 [4W BEREA 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 537 342583-342589(1) | OPEN LINE FROM BUS 342583 [4FLEMINGSBRG138.00] TO BUS 342589 [4GODDARD 138.00] CKT 1 | 0.93965 | 64.8362 | 0.9389 | 64.7839 | -0.00075728 | -0.0011029
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 537 342583-342589(1) | OPEN LINE FROM BUS 342583 [4FLEMINGSBRG138.00] TO BUS 342589 [4GODDARD 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 538 342583-342664(1) | OPEN LINE FROM BUS 342583 [4FLEMINGSBRG138.00] TO BUS 342664 [4SPURLOCK 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93958 | 64.831 | -7.4089e-05 | -0.00041968
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 539 342586-342587(1) | OPEN LINE FROM BUS 342586 [4GALLATIN CO138.00] TO BUS 342587 [1GALLATIN CO34.500] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 540 342586-342673(1) | OPEN LINE FROM BUS 342586 [4GALLATIN CO138.00] TO BUS 342673 [4STERLNG T 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 541 342589-342634(1) | OPEN LINE FROM BUS 342589 [4GODDARD 138.00] TO BUS 342634 [4PLUMVILLE 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93937 | 64.8162 | -0.00028878 | -0.00063437
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 541 342589-342634(1) | OPEN LINE FROM BUS 342589 [4GODDARD 138.00] TO BUS 342634 [4PLUMVILLE 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 542 342596-342607(1) | OPEN LINE FROM BUS 342596 [4HUNT 138.00] TO BUS 342607 [4JK SMITH 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 543 342598-342664(1) | OPEN LINE FROM BUS 342598 [4INLAND C T 138.00] TO BUS 342664 [4SPURLOCK 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 544 342601-342604(1) | OPEN LINE FROM BUS 342601 [4JACKSNVIL 138.00] TO BUS 342604 [4JACKSNVIL T138.00] CKT 1 | 0.93965 | 64.8362 | 0.9398 | 64.8463 | 0.00014704 | -0.00019854
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 544 342601-342604(1) | OPEN LINE FROM BUS 342601 [4JACKSNVIL 138.00] TO BUS 342604 [4JACKSNVIL T138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 545 342604-342631(1) | OPEN LINE FROM BUS 342604 [4JACKSNVIL T138.00] TO BUS 342631 [4PARIS T 138.00] CKT 1 | 0.93965 | 64.8362 | 0.9397 | 64.8395 | 4.8518e-05 | -0.00029707
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 545 342604-342631(1) | OPEN LINE FROM BUS 342604 [4JACKSNVIL T138.00] TO BUS 342631 [4PARIS T 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 546 342604-342640(1) | OPEN LINE FROM BUS 342604 [4JACKSNVIL T138.00] TO BUS 342640 [4RENAKER 138.00] CKT 1 | 0.93965 | 64.8362 | 0.9398 | 64.846 | 0.0001421 | -0.00020349
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 546 342604-342640(1) | OPEN LINE FROM BUS 342604 [4JACKSNVIL T138.00] TO BUS 342640 [4RENAKER 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 547 342607-342610(1) | OPEN LINE FROM BUS 342607 [4JK SMITH 138.00] TO BUS 342610 [4JK SMITH 21138.00] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8353 | -1.1742e-05 | -0.00035733
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 547 342607-342610(1) | OPEN LINE FROM BUS 342607 [4JK SMITH 138.00] TO BUS 342610 [4JK SMITH 21138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 548 342607-342613(1) | OPEN LINE FROM BUS 342607 [4JK SMITH 138.00] TO BUS 342613 [4JK SMITH 22138.00] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8354 | -1.1623e-05 | -0.00035721
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 548 342607-342613(1) | OPEN LINE FROM BUS 342607 [4JK SMITH 138.00] TO BUS 342613 [4JK SMITH 22138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 549 342607-342637(1) | OPEN LINE FROM BUS 342607 [4JK SMITH 138.00] TO BUS 342637 [4POWELL CO 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93904 | 64.7936 | -0.00061679 | -0.00096238
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 549 342607-342637(1) | OPEN LINE FROM BUS 342607 [4JK SMITH 138.00] TO BUS 342637 [4POWELL CO 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 550 342607-342688(1) | OPEN LINE FROM BUS 342607 [4JK SMITH 138.00] TO BUS 342688 [4UNION CTY T138.00] CKT 1 | 0.93965 | 64.8362 | 0.93916 | 64.8021 | -0.00049341 | -0.00083899
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 550 342607-342688(1) | OPEN LINE FROM BUS 342607 [4JK SMITH 138.00] TO BUS 342688 [4UNION CTY T138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 551 342610-342832(1) | OPEN LINE FROM BUS 342610 [4JK SMITH 21138.00] TO BUS 342832 [7JK SMITH 345.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8355 | -8.8215e-06 | -0.00035441
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 551 342610-342832(1) | OPEN LINE FROM BUS 342610 [4JK SMITH 21138.00] TO BUS 342832 [7JK SMITH 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 552 342613-342832(1) | OPEN LINE FROM BUS 342613 [4JK SMITH 22138.00] TO BUS 342832 [7JK SMITH 345.00] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8354 | -1.1206e-05 | -0.00035679
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 552 342613-342832(1) | OPEN LINE FROM BUS 342613 [4JK SMITH 22138.00] TO BUS 342832 [7JK SMITH 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 553 342622-342625(1) | OPEN LINE FROM BUS 342622 [4MAYSVIL I T138.00] TO BUS 342625 [4MAYSVIL IND138.00] CKT 1 | 0.93965 | 64.8362 | 0.93976 | 64.8438 | 0.00011009 | -0.0002355
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 554 342622-342634(1) | OPEN LINE FROM BUS 342622 [4MAYSVIL I T138.00] TO BUS 342634 [4PLUMVILLE 138.00] CKT 1 | 0.93965 | 64.8362 | 0.9395 | 64.8253 | -0.00015718 | -0.00050277
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 554 342622-342634(1) | OPEN LINE FROM BUS 342622 [4MAYSVIL I T138.00] TO BUS 342634 [4PLUMVILLE 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 555 342622-342664(1) | OPEN LINE FROM BUS 342622 [4MAYSVIL I T138.00] TO BUS 342664 [4SPURLOCK 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93916 | 64.8024 | -0.00048971 | -0.0008353
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 555 342622-342664(1) | OPEN LINE FROM BUS 342622 [4MAYSVIL I T138.00] TO BUS 342664 [4SPURLOCK 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 556 342637-342784(1) | OPEN LINE FROM BUS 342637 [4POWELL CO 138.00] TO BUS 342784 [5POWELL CO 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93973 | 64.8415 | 7.7128e-05 | -0.00026846
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 556 342637-342784(1) | OPEN LINE FROM BUS 342637 [4POWELL CO 138.00] TO BUS 342784 [5POWELL CO 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 557 342640-342664(1) | OPEN LINE FROM BUS 342640 [4RENAKER 138.00] TO BUS 342664 [4SPURLOCK 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 558 342643-342646(1) | OPEN LINE FROM BUS 342643 [4RICHWOOD 138.00] TO BUS 342646 [4RICHWOOD T 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 559 342646-342667(1) | OPEN LINE FROM BUS 342646 [4RICHWOOD T 138.00] TO BUS 342667 [4STANLEY PRK138.00] CKT 1 | 0.93965 | 64.8362 | 0.93945 | 64.8221 | -0.00020355 | -0.00054914
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 559 342646-342667(1) | OPEN LINE FROM BUS 342646 [4RICHWOOD T 138.00] TO BUS 342667 [4STANLEY PRK138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 560 342649-342658(1) | OPEN LINE FROM BUS 342649 [4ROWAN CO 138.00] TO BUS 342658 [4SKAGGS 138.00] CKT 1 | 0.93965 | 64.8362 | 0.94 | 64.8597 | 0.00034183 | -3.7551e-06
342658 | 4SKAGGS | 138 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 560 342649-342658(1) | OPEN LINE FROM BUS 342649 [4ROWAN CO 138.00] TO BUS 342658 [4SKAGGS 138.00] CKT 1 | 0.96629 | 133.3482 | 0.93933 | 129.6279 | -0.026959 | -0.00066769
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 560 342649-342658(1) | OPEN LINE FROM BUS 342649 [4ROWAN CO 138.00] TO BUS 342658 [4SKAGGS 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 561 342661-342664(1) | OPEN LINE FROM BUS 342661 [4SPUR-KENT-R138.00] TO BUS 342664 [4SPURLOCK 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 562 342664-342667(1) | OPEN LINE FROM BUS 342664 [4SPURLOCK 138.00] TO BUS 342667 [4STANLEY PRK138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 563 342664-342838(1) | OPEN LINE FROM BUS 342664 [4SPURLOCK 138.00] TO BUS 342838 [7SPURLOCK 345.00] CKT 1 | 0.93965 | 64.8362 | 0.93928 | 64.8105 | -0.0003714 | -0.00071698
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 563 342664-342838(1) | OPEN LINE FROM BUS 342664 [4SPURLOCK 138.00] TO BUS 342838 [7SPURLOCK 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 564 342664-342838(2) | OPEN LINE FROM BUS 342664 [4SPURLOCK 138.00] TO BUS 342838 [7SPURLOCK 345.00] CKT 2 | 0.93965 | 64.8362 | 0.93945 | 64.8219 | -0.00020605 | -0.00055164
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 564 342664-342838(2) | OPEN LINE FROM BUS 342664 [4SPURLOCK 138.00] TO BUS 342838 [7SPURLOCK 345.00] CKT 2 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 565 342664-342838(3) | OPEN LINE FROM BUS 342664 [4SPURLOCK 138.00] TO BUS 342838 [7SPURLOCK 345.00] CKT 3 | 0.93965 | 64.8362 | 0.93932 | 64.8133 | -0.00033128 | -0.00067687
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 565 342664-342838(3) | OPEN LINE FROM BUS 342664 [4SPURLOCK 138.00] TO BUS 342838 [7SPURLOCK 345.00] CKT 3 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 566 342670-342673(1) | OPEN LINE FROM BUS 342670 [4STERLING 138.00] TO BUS 342673 [4STERLNG T 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93993 | 64.8553 | 0.00027728 | -6.8307e-05
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 566 342670-342673(1) | OPEN LINE FROM BUS 342670 [4STERLING 138.00] TO BUS 342673 [4STERLNG T 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 567 342676-342679(1) | OPEN LINE FROM BUS 342676 [4THREE FK T 138.00] TO BUS 342679 [4THREE FORKS138.00] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8376 | 2.0266e-05 | -0.00032532
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 567 342676-342679(1) | OPEN LINE FROM BUS 342676 [4THREE FK T 138.00] TO BUS 342679 [4THREE FORKS138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 568 342685-342688(1) | OPEN LINE FROM BUS 342685 [4UNION CITY 138.00] TO BUS 342688 [4UNION CTY T138.00] CKT 1 | 0.93965 | 64.8362 | 0.93969 | 64.8384 | 3.2842e-05 | -0.00031275
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 568 342685-342688(1) | OPEN LINE FROM BUS 342685 [4UNION CITY 138.00] TO BUS 342688 [4UNION CTY T138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 569 342694-342814(1) | OPEN LINE FROM BUS 342694 [5BARREN CO 161.00] TO BUS 342814 [5SUMM SHADE 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 2.861e-06 | -0.00034273
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 569 342694-342814(1) | OPEN LINE FROM BUS 342694 [5BARREN CO 161.00] TO BUS 342814 [5SUMM SHADE 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 570 342697-342780(1) | OPEN LINE FROM BUS 342697 [5BEATTYV J 161.00] TO BUS 342780 [5MILL CRK T 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93973 | 64.8412 | 7.385e-05 | -0.00027174
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 570 342697-342780(1) | OPEN LINE FROM BUS 342697 [5BEATTYV J 161.00] TO BUS 342780 [5MILL CRK T 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 571 342700-342819(1) | OPEN LINE FROM BUS 342700 [5BULLITT CO 161.00] TO BUS 342819 [5TAYLORSV T 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93975 | 64.8425 | 9.2149e-05 | -0.00025344
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 571 342700-342819(1) | OPEN LINE FROM BUS 342700 [5BULLITT CO 161.00] TO BUS 342819 [5TAYLORSV T 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 572 342703-342769(1) | OPEN LINE FROM BUS 342703 [5CASEY CO 161.00] TO BUS 342769 [5MARION CO 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.837 | 1.2696e-05 | -0.00033289
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 572 342703-342769(1) | OPEN LINE FROM BUS 342703 [5CASEY CO 161.00] TO BUS 342769 [5MARION CO 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 573 342715-342718(1) | OPEN LINE FROM BUS 342715 [5COOPER1 161.00] TO BUS 342718 [5COOPER2 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8372 | 1.5855e-05 | -0.00032973
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 573 342715-342718(1) | OPEN LINE FROM BUS 342715 [5COOPER1 161.00] TO BUS 342718 [5COOPER2 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 574 342715-342790(1) | OPEN LINE FROM BUS 342715 [5COOPER1 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8372 | 1.4722e-05 | -0.00033087
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 574 342715-342790(1) | OPEN LINE FROM BUS 342715 [5COOPER1 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 1.1921e-07 | 1.1921e-07
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 575 342715-342799(1) | OPEN LINE FROM BUS 342715 [5COOPER1 161.00] TO BUS 342799 [5S OAKHILL 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93958 | 64.831 | -7.5281e-05 | -0.00042087
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 575 342715-342799(1) | OPEN LINE FROM BUS 342715 [5COOPER1 161.00] TO BUS 342799 [5S OAKHILL 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 576 342718-342727(1) | OPEN LINE FROM BUS 342718 [5COOPER2 161.00] TO BUS 342727 [5DENNY 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93971 | 64.8397 | 5.1379e-05 | -0.00029421
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 576 342718-342727(1) | OPEN LINE FROM BUS 342718 [5COOPER2 161.00] TO BUS 342727 [5DENNY 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 577 342718-342757(1) | OPEN LINE FROM BUS 342718 [5COOPER2 161.00] TO BUS 342757 [5LAUREL DAM 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93963 | 64.8343 | -2.7001e-05 | -0.00037259
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 577 342718-342757(1) | OPEN LINE FROM BUS 342718 [5COOPER2 161.00] TO BUS 342757 [5LAUREL DAM 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 578 342721-342724(1) | OPEN LINE FROM BUS 342721 [5DARWIN TH 161.00] TO BUS 342724 [5DARWIN TH T161.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8359 | -3.6955e-06 | -0.00034928
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 578 342721-342724(1) | OPEN LINE FROM BUS 342721 [5DARWIN TH 161.00] TO BUS 342724 [5DARWIN TH T161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 579 342724-342766(1) | OPEN LINE FROM BUS 342724 [5DARWIN TH T161.00] TO BUS 342766 [5LITTLE MT T161.00] CKT 1 | 0.93965 | 64.8362 | 0.93976 | 64.8436 | 0.00010836 | -0.00023723
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 579 342724-342766(1) | OPEN LINE FROM BUS 342724 [5DARWIN TH T161.00] TO BUS 342766 [5LITTLE MT T161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 580 342724-342808(1) | OPEN LINE FROM BUS 342724 [5DARWIN TH T161.00] TO BUS 342808 [5SHELBY CO 161.00] CKT 1 | 0.93965 | 64.8362 | 0.9397 | 64.8396 | 5.0068e-05 | -0.00029552
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 580 342724-342808(1) | OPEN LINE FROM BUS 342724 [5DARWIN TH T161.00] TO BUS 342808 [5SHELBY CO 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 581 342730-342820(1) | OPEN LINE FROM BUS 342730 [5FALL ROCK 161.00] TO BUS 342820 [5TYNER 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93962 | 64.8335 | -3.7909e-05 | -0.0003835
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 581 342730-342820(1) | OPEN LINE FROM BUS 342730 [5FALL ROCK 161.00] TO BUS 342820 [5TYNER 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 582 342733-342814(1) | OPEN LINE FROM BUS 342733 [5GREEN CO 161.00] TO BUS 342814 [5SUMM SHADE 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8358 | -5.0068e-06 | -0.00035059
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 582 342733-342814(1) | OPEN LINE FROM BUS 342733 [5GREEN CO 161.00] TO BUS 342814 [5SUMM SHADE 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 583 342733-342817(1) | OPEN LINE FROM BUS 342733 [5GREEN CO 161.00] TO BUS 342817 [5TAYLOR CO J161.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 3.5763e-07 | -0.00034523
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 583 342733-342817(1) | OPEN LINE FROM BUS 342733 [5GREEN CO 161.00] TO BUS 342817 [5TAYLOR CO J161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 584 342736-342739(1) | OPEN LINE FROM BUS 342736 [5GREEN HAL T161.00] TO BUS 342739 [5GREEN HALL 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8369 | 1.1384e-05 | -0.0003342
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 584 342736-342739(1) | OPEN LINE FROM BUS 342736 [5GREEN HAL T161.00] TO BUS 342739 [5GREEN HALL 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 585 342736-342820(1) | OPEN LINE FROM BUS 342736 [5GREEN HAL T161.00] TO BUS 342820 [5TYNER 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93993 | 64.8554 | 0.00027835 | -6.7234e-05
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 585 342736-342820(1) | OPEN LINE FROM BUS 342736 [5GREEN HAL T161.00] TO BUS 342820 [5TYNER 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 586 342742-342745(1) | OPEN LINE FROM BUS 342742 [5JABEZ 161.00] TO BUS 342745 [5JABEZ T 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 2.1458e-06 | -0.00034344
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 586 342742-342745(1) | OPEN LINE FROM BUS 342742 [5JABEZ 161.00] TO BUS 342745 [5JABEZ T 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 587 342745-342751(1) | OPEN LINE FROM BUS 342745 [5JABEZ T 161.00] TO BUS 342751 [5JAMESTOWN T161.00] CKT 1 | 0.93965 | 64.8362 | 0.93956 | 64.8295 | -9.5844e-05 | -0.00044143
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 587 342745-342751(1) | OPEN LINE FROM BUS 342745 [5JABEZ T 161.00] TO BUS 342751 [5JAMESTOWN T161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 588 342745-342799(1) | OPEN LINE FROM BUS 342745 [5JABEZ T 161.00] TO BUS 342799 [5S OAKHILL 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93956 | 64.8297 | -9.3937e-05 | -0.00043952
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 588 342745-342799(1) | OPEN LINE FROM BUS 342745 [5JABEZ T 161.00] TO BUS 342799 [5S OAKHILL 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 589 342748-342751(1) | OPEN LINE FROM BUS 342748 [5JAMESTOWN 161.00] TO BUS 342751 [5JAMESTOWN T161.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 1.967e-06 | -0.00034362
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 589 342748-342751(1) | OPEN LINE FROM BUS 342748 [5JAMESTOWN 161.00] TO BUS 342751 [5JAMESTOWN T161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 590 342751-342796(1) | OPEN LINE FROM BUS 342751 [5JAMESTOWN T161.00] TO BUS 342796 [5RUSSEL CO J161.00] CKT 1 | 0.93965 | 64.8362 | 0.93955 | 64.8288 | -0.00010669 | -0.00045228
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 590 342751-342796(1) | OPEN LINE FROM BUS 342751 [5JAMESTOWN T161.00] TO BUS 342796 [5RUSSEL CO J161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 591 342754-342757(1) | OPEN LINE FROM BUS 342754 [5LAUREL CO 161.00] TO BUS 342757 [5LAUREL DAM 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93962 | 64.8339 | -3.3021e-05 | -0.00037861
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 591 342754-342757(1) | OPEN LINE FROM BUS 342754 [5LAUREL CO 161.00] TO BUS 342757 [5LAUREL DAM 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 592 342754-342781(1) | OPEN LINE FROM BUS 342754 [5LAUREL CO 161.00] TO BUS 342781 [5PITTSBURG 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93961 | 64.8331 | -4.4167e-05 | -0.00038975
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 592 342754-342781(1) | OPEN LINE FROM BUS 342754 [5LAUREL CO 161.00] TO BUS 342781 [5PITTSBURG 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 593 342760-342790(1) | OPEN LINE FROM BUS 342760 [5LIBERTY J 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.93965 | 64.8362 | 0.93958 | 64.8314 | -6.9439e-05 | -0.00041503
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 593 342760-342790(1) | OPEN LINE FROM BUS 342760 [5LIBERTY J 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 594 342763-342766(1) | OPEN LINE FROM BUS 342763 [5LITTLE MT 161.00] TO BUS 342766 [5LITTLE MT T161.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8359 | -3.2187e-06 | -0.00034881
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 594 342763-342766(1) | OPEN LINE FROM BUS 342763 [5LITTLE MT 161.00] TO BUS 342766 [5LITTLE MT T161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 595 342766-342819(1) | OPEN LINE FROM BUS 342766 [5LITTLE MT T161.00] TO BUS 342819 [5TAYLORSV T 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93976 | 64.8435 | 0.00010598 | -0.00023961
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 595 342766-342819(1) | OPEN LINE FROM BUS 342766 [5LITTLE MT T161.00] TO BUS 342819 [5TAYLORSV T 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 596 342769-342770(1) | OPEN LINE FROM BUS 342769 [5MARION CO 161.00] TO BUS 342770 [4MARION CO 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8359 | -3.5167e-06 | -0.0003491
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 596 342769-342770(1) | OPEN LINE FROM BUS 342769 [5MARION CO 161.00] TO BUS 342770 [4MARION CO 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 597 342769-342775(1) | OPEN LINE FROM BUS 342769 [5MARION CO 161.00] TO BUS 342775 [5MARION IP T161.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -2.3842e-07 | -0.00034583
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 597 342769-342775(1) | OPEN LINE FROM BUS 342769 [5MARION CO 161.00] TO BUS 342775 [5MARION IP T161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 598 342772-342797(1) | OPEN LINE FROM BUS 342772 [5MARION IP 161.00] TO BUS 342797 [5S MARION IT161.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -1.7881e-06 | -0.00034738
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 598 342772-342797(1) | OPEN LINE FROM BUS 342772 [5MARION IP 161.00] TO BUS 342797 [5S MARION IT161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 599 342775-342797(1) | OPEN LINE FROM BUS 342775 [5MARION IP T161.00] TO BUS 342797 [5S MARION IT161.00] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8355 | -9.954e-06 | -0.00035554
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 599 342775-342797(1) | OPEN LINE FROM BUS 342775 [5MARION IP T161.00] TO BUS 342797 [5S MARION IT161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 600 342775-342805(1) | OPEN LINE FROM BUS 342775 [5MARION IP T161.00] TO BUS 342805 [5SALOMA T 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8359 | -4.1127e-06 | -0.0003497
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 600 342775-342805(1) | OPEN LINE FROM BUS 342775 [5MARION IP T161.00] TO BUS 342805 [5SALOMA T 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 601 342779-342780(1) | OPEN LINE FROM BUS 342779 [5MILLER CRK 161.00] TO BUS 342780 [5MILL CRK T 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8374 | 1.7583e-05 | -0.000328
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 601 342779-342780(1) | OPEN LINE FROM BUS 342779 [5MILLER CRK 161.00] TO BUS 342780 [5MILL CRK T 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 602 342780-342784(1) | OPEN LINE FROM BUS 342780 [5MILL CRK T 161.00] TO BUS 342784 [5POWELL CO 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93971 | 64.8403 | 5.9724e-05 | -0.00028586
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 602 342780-342784(1) | OPEN LINE FROM BUS 342780 [5MILL CRK T 161.00] TO BUS 342784 [5POWELL CO 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 603 342781-342820(1) | OPEN LINE FROM BUS 342781 [5PITTSBURG 161.00] TO BUS 342820 [5TYNER 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93972 | 64.8406 | 6.485e-05 | -0.00028074
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 603 342781-342820(1) | OPEN LINE FROM BUS 342781 [5PITTSBURG 161.00] TO BUS 342820 [5TYNER 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 604 342787-342790(1) | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.93965 | 64.8362 | 0.93963 | 64.8343 | -2.7597e-05 | -0.00037318
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 604 342787-342790(1) | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 605 342793-342796(1) | OPEN LINE FROM BUS 342793 [5RUSSEL CO 161.00] TO BUS 342796 [5RUSSEL CO J161.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 2.9206e-06 | -0.00034267
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 605 342793-342796(1) | OPEN LINE FROM BUS 342793 [5RUSSEL CO 161.00] TO BUS 342796 [5RUSSEL CO J161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 606 342797-342798(1) | OPEN LINE FROM BUS 342797 [5S MARION IT161.00] TO BUS 342798 [5S MARION IP161.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8356 | -7.8678e-06 | -0.00035346
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 606 342797-342798(1) | OPEN LINE FROM BUS 342797 [5S MARION IT161.00] TO BUS 342798 [5S MARION IP161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 607 342802-342805(1) | OPEN LINE FROM BUS 342802 [5SALOMA 161.00] TO BUS 342805 [5SALOMA T 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -2.7418e-06 | -0.00034833
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 607 342802-342805(1) | OPEN LINE FROM BUS 342802 [5SALOMA 161.00] TO BUS 342805 [5SALOMA T 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 608 342805-342817(1) | OPEN LINE FROM BUS 342805 [5SALOMA T 161.00] TO BUS 342817 [5TAYLOR CO J161.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -2.4438e-06 | -0.00034803
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 608 342805-342817(1) | OPEN LINE FROM BUS 342805 [5SALOMA T 161.00] TO BUS 342817 [5TAYLOR CO J161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 609 342818-342819(1) | OPEN LINE FROM BUS 342818 [5TAYLORSVILL161.00] TO BUS 342819 [5TAYLORSV T 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8359 | -3.6955e-06 | -0.00034928
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 609 342818-342819(1) | OPEN LINE FROM BUS 342818 [5TAYLORSVILL161.00] TO BUS 342819 [5TAYLORSV T 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 610 342829-342835(1) | OPEN LINE FROM BUS 342829 [7AVON 345.00] TO BUS 342835 [7N CLARK 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 611 342832-342835(1) | OPEN LINE FROM BUS 342832 [7JK SMITH 345.00] TO BUS 342835 [7N CLARK 345.00] CKT 1 | 0.93965 | 64.8362 | 0.93986 | 64.8504 | 0.00020689 | -0.0001387
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 611 342832-342835(1) | OPEN LINE FROM BUS 342832 [7JK SMITH 345.00] TO BUS 342835 [7N CLARK 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 612 342832-342841(1) | OPEN LINE FROM BUS 342832 [7JK SMITH 345.00] TO BUS 342841 [7W GARRARDEK345.00] CKT 1 | 0.93965 | 64.8362 | 0.93958 | 64.8311 | -7.3791e-05 | -0.00041938
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 612 342832-342841(1) | OPEN LINE FROM BUS 342832 [7JK SMITH 345.00] TO BUS 342841 [7W GARRARDEK345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 613 342835-342838(1) | OPEN LINE FROM BUS 342835 [7N CLARK 345.00] TO BUS 342838 [7SPURLOCK 345.00] CKT 1 | 0.93965 | 64.8362 | 0.93815 | 64.7323 | -0.0015051 | -0.0018507
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 613 342835-342838(1) | OPEN LINE FROM BUS 342835 [7N CLARK 345.00] TO BUS 342838 [7SPURLOCK 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 614 942410-942411(1) | OPEN LINE FROM BUS 942410 [AE2-254 TAP 69.000] TO BUS 942411 [AE2-254 C O169.000] CKT 1 | 0.93965 | 64.8362 | 0.93962 | 64.8338 | -3.4094e-05 | -0.00037968
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 614 942410-942411(1) | OPEN LINE FROM BUS 942410 [AE2-254 TAP 69.000] TO BUS 942411 [AE2-254 C O169.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 615 942411-942412(1) | OPEN LINE FROM BUS 942411 [AE2-254 C O169.000] TO BUS 942412 [AE2-254 E O169.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 2.3842e-07 | -0.00034535
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 615 942411-942412(1) | OPEN LINE FROM BUS 942411 [AE2-254 C O169.000] TO BUS 942412 [AE2-254 E O169.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 616 341020-243725(1) | OPEN LINE FROM BUS 341020 [2ARGENTUM 69.000] TO BUS 243725 [05GRAYSB 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 5.9605e-08 | -0.00034553
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 616 341020-243725(1) | OPEN LINE FROM BUS 341020 [2ARGENTUM 69.000] TO BUS 243725 [05GRAYSB 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 617 341071-324430(1) | OPEN LINE FROM BUS 341071 [2BEATTYV 69.000] TO BUS 324430 [2BEATTYVI KU69.000] CKT 1 | 0.93965 | 64.8362 | 0.93954 | 64.8284 | -0.00011241 | -0.000458
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 617 341071-324430(1) | OPEN LINE FROM BUS 341071 [2BEATTYV 69.000] TO BUS 324430 [2BEATTYVI KU69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 618 341089-325102(1) | OPEN LINE FROM BUS 341089 [2BEKAERT 69.000] TO BUS 325102 [2W SHELBY 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -2.7418e-06 | -0.00034833
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 618 341089-325102(1) | OPEN LINE FROM BUS 341089 [2BEKAERT 69.000] TO BUS 325102 [2W SHELBY 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 619 341161-324213(1) | OPEN LINE FROM BUS 341161 [2BONNIV EK 69.000] TO BUS 324213 [4BONNIEVILLE138.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8365 | 4.53e-06 | -0.00034106
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 619 341161-324213(1) | OPEN LINE FROM BUS 341161 [2BONNIV EK 69.000] TO BUS 324213 [4BONNIEVILLE138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 620 341188-324463(1) | OPEN LINE FROM BUS 341188 [2BRACKEN CO 69.000] TO BUS 324463 [2CARNTOWN 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 621 341188-324722(1) | OPEN LINE FROM BUS 341188 [2BRACKEN CO 69.000] TO BUS 324722 [2SHARON KU 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 622 341317-324474(1) | OPEN LINE FROM BUS 341317 [2CLAY VILLAG69.000] TO BUS 324474 [2CLAY VILG T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93974 | 64.8422 | 8.75e-05 | -0.00025809
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 622 341317-324474(1) | OPEN LINE FROM BUS 341317 [2CLAY VILLAG69.000] TO BUS 324474 [2CLAY VILG T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 623 341320-324830(1) | OPEN LINE FROM BUS 341320 [2COBURG 69.000] TO BUS 324830 [2CAMPBELV EK69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8357 | -7.0333e-06 | -0.00035262
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 623 341320-324830(1) | OPEN LINE FROM BUS 341320 [2COBURG 69.000] TO BUS 324830 [2CAMPBELV EK69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 624 341406-324530(1) | OPEN LINE FROM BUS 341406 [2DUNCAN LN T69.000] TO BUS 324530 [2FAWKES 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 625 341407-324425(1) | OPEN LINE FROM BUS 341407 [2E BARDSTOWN69.000] TO BUS 324425 [2BARDT IND T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93962 | 64.8341 | -3.022e-05 | -0.00037581
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 625 341407-324425(1) | OPEN LINE FROM BUS 341407 [2E BARDSTOWN69.000] TO BUS 324425 [2BARDT IND T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 626 341461-243721(Z1) | OPEN LINE FROM BUS 341461 [2FALCON EK 69.000] TO BUS 243721 [05FALCON 69.000] CKT Z1 | 0.93965 | 64.8362 | 0.93991 | 64.8541 | 0.00026017 | -8.5413e-05
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 626 341461-243721(Z1) | OPEN LINE FROM BUS 341461 [2FALCON EK 69.000] TO BUS 243721 [05FALCON 69.000] CKT Z1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 627 341515-324600(1) | OPEN LINE FROM BUS 341515 [2GARRARD CO 69.000] TO BUS 324600 [2LANCASTR KU69.000] CKT 1 | 0.93965 | 64.8362 | 0.93968 | 64.8379 | 2.563e-05 | -0.00031996
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 627 341515-324600(1) | OPEN LINE FROM BUS 341515 [2GARRARD CO 69.000] TO BUS 324600 [2LANCASTR KU69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 628 341539-324784(1) | OPEN LINE FROM BUS 341539 [2GOLDBUG 69.000] TO BUS 324784 [2WOFFORD 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 1.5497e-06 | -0.00034404
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 628 341539-324784(1) | OPEN LINE FROM BUS 341539 [2GOLDBUG 69.000] TO BUS 324784 [2WOFFORD 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 629 341554-243726(1) | OPEN LINE FROM BUS 341554 [2GRAYSON J 69.000] TO BUS 243726 [05GRAYSO 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93979 | 64.8456 | 0.00013626 | -0.00020933
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 629 341554-243726(1) | OPEN LINE FROM BUS 341554 [2GRAYSON J 69.000] TO BUS 243726 [05GRAYSO 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 630 341563-324554(1) | OPEN LINE FROM BUS 341563 [2GREEN CO 69.000] TO BUS 324554 [2GRENSBRG KU69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -1.6689e-06 | -0.00034726
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 630 341563-324554(1) | OPEN LINE FROM BUS 341563 [2GREEN CO 69.000] TO BUS 324554 [2GRENSBRG KU69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 631 341605-251579(1) | OPEN LINE FROM BUS 341605 [2HEBRON 69.000] TO BUS 251579 [08HEBRON 69.000] CKT 1 | 0.93965 | 64.8362 | 0.939 | 64.7908 | -0.00065762 | -0.0010032
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 631 341605-251579(1) | OPEN LINE FROM BUS 341605 [2HEBRON 69.000] TO BUS 251579 [08HEBRON 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 632 341608-243812(Z1) | OPEN LINE FROM BUS 341608 [2HELECHAW 69.000] TO BUS 243812 [05LEE C 69.000] CKT Z1 | 0.93965 | 64.8362 | 0.93961 | 64.8333 | -4.1425e-05 | -0.00038701
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 632 341608-243812(Z1) | OPEN LINE FROM BUS 341608 [2HELECHAW 69.000] TO BUS 243812 [05LEE C 69.000] CKT Z1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 633 341632-324575(1) | OPEN LINE FROM BUS 341632 [2HODGENVILLE69.000] TO BUS 324575 [2HODGENV KU 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -2.2054e-06 | -0.00034779
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 633 341632-324575(1) | OPEN LINE FROM BUS 341632 [2HODGENVILLE69.000] TO BUS 324575 [2HODGENV KU 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 634 341632-324660(1) | OPEN LINE FROM BUS 341632 [2HODGENVILLE69.000] TO BUS 324660 [2NEW HAVEN 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 1.7881e-06 | -0.0003438
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 634 341632-324660(1) | OPEN LINE FROM BUS 341632 [2HODGENVILLE69.000] TO BUS 324660 [2NEW HAVEN 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 635 341713-324519(1) | OPEN LINE FROM BUS 341713 [2KARGLE 69.000] TO BUS 324519 [2ETOWN KU 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 2.9802e-07 | -0.00034529
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 635 341713-324519(1) | OPEN LINE FROM BUS 341713 [2KARGLE 69.000] TO BUS 324519 [2ETOWN KU 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 636 341740-324576(1) | OPEN LINE FROM BUS 341740 [2LAUREL CO 69.000] TO BUS 324576 [2HOPEWELL 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8365 | 5.2452e-06 | -0.00034034
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 636 341740-324576(1) | OPEN LINE FROM BUS 341740 [2LAUREL CO 69.000] TO BUS 324576 [2HOPEWELL 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 637 341752-243737(Z1) | OPEN LINE FROM BUS 341752 [2LEON 69.000] TO BUS 243737 [05LEONKY 69.000] CKT Z1 | 0.93965 | 64.8362 | 0.93956 | 64.8294 | -9.8109e-05 | -0.0004437
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 637 341752-243737(Z1) | OPEN LINE FROM BUS 341752 [2LEON 69.000] TO BUS 243737 [05LEONKY 69.000] CKT Z1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 638 341755-324527(1) | OPEN LINE FROM BUS 341755 [2LIBER CH T 69.000] TO BUS 324527 [2FARLEY KU 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93971 | 64.8401 | 5.7757e-05 | -0.00028783
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 638 341755-324527(1) | OPEN LINE FROM BUS 341755 [2LIBER CH T 69.000] TO BUS 324527 [2FARLEY KU 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 639 341890-246973(Z1) | OPEN LINE FROM BUS 341890 [2MORGAN CO 69.000] TO BUS 246973 [05MORGCO 69.000] CKT Z1 | 0.93965 | 64.8362 | 0.93964 | 64.8353 | -1.2279e-05 | -0.00035787
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 639 341890-246973(Z1) | OPEN LINE FROM BUS 341890 [2MORGAN CO 69.000] TO BUS 246973 [05MORGCO 69.000] CKT Z1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 640 341923-324717(1) | OPEN LINE FROM BUS 341923 [2MURPHYSVIL 69.000] TO BUS 324717 [2SARDIS TAP 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93899 | 64.7902 | -0.00066561 | -0.0010112
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 640 341923-324717(1) | OPEN LINE FROM BUS 341923 [2MURPHYSVIL 69.000] TO BUS 324717 [2SARDIS TAP 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 641 341923-325019(1) | OPEN LINE FROM BUS 341923 [2MURPHYSVIL 69.000] TO BUS 325019 [2KENTON-6 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93948 | 64.8242 | -0.00017315 | -0.00051874
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 641 341923-325019(1) | OPEN LINE FROM BUS 341923 [2MURPHYSVIL 69.000] TO BUS 325019 [2KENTON-6 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 642 341929-324662(1) | OPEN LINE FROM BUS 341929 [2N LONDON 69.000] TO BUS 324662 [2N LONDON KU69.000] CKT 1 | 0.93965 | 64.8362 | 0.93962 | 64.834 | -3.1292e-05 | -0.00037688
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 642 341929-324662(1) | OPEN LINE FROM BUS 341929 [2N LONDON 69.000] TO BUS 324662 [2N LONDON KU69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 643 341935-324736(1) | OPEN LINE FROM BUS 341935 [2N SPRINGFLD69.000] TO BUS 324736 [2SPRINGFL KU69.000] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8373 | 1.7285e-05 | -0.0003283
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 643 341935-324736(1) | OPEN LINE FROM BUS 341935 [2N SPRINGFLD69.000] TO BUS 324736 [2SPRINGFL KU69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 644 341944-324288(1) | OPEN LINE FROM BUS 341944 [2NELSON CO 69.000] TO BUS 324288 [4NELSON CO 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8358 | -5.3644e-06 | -0.00035095
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 644 341944-324288(1) | OPEN LINE FROM BUS 341944 [2NELSON CO 69.000] TO BUS 324288 [4NELSON CO 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 645 342007-324455(1) | OPEN LINE FROM BUS 342007 [2OWEN CO 69.000] TO BUS 324455 [2BROMLEY 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93952 | 64.8268 | -0.00013518 | -0.00048077
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 645 342007-324455(1) | OPEN LINE FROM BUS 342007 [2OWEN CO 69.000] TO BUS 324455 [2BROMLEY 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 646 342008-324290(1) | OPEN LINE FROM BUS 342008 [4OWEN CO 138.00] TO BUS 324290 [4OWEN CO TAP138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 647 342055-243742(1) | OPEN LINE FROM BUS 342055 [2PELFREY 69.000] TO BUS 243742 [05CORYSS 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93957 | 64.8303 | -8.44e-05 | -0.00042999
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 647 342055-243742(1) | OPEN LINE FROM BUS 342055 [2PELFREY 69.000] TO BUS 243742 [05CORYSS 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 648 342058-324951(1) | OPEN LINE FROM BUS 342058 [2PENN 69.000] TO BUS 324951 [2SCOTT CO 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 649 342133-324492(1) | OPEN LINE FROM BUS 342133 [2RENAKER 69.000] TO BUS 324492 [2CYNTHIAN SW69.000] CKT 1 | 0.93965 | 64.8362 | 0.93845 | 64.7532 | -0.0012017 | -0.0015473
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 649 342133-324492(1) | OPEN LINE FROM BUS 342133 [2RENAKER 69.000] TO BUS 324492 [2CYNTHIAN SW69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 650 342157-324708(1) | OPEN LINE FROM BUS 342157 [2ROGERSVIL J69.000] TO BUS 324708 [2ROGERSVILLE69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -2.8014e-06 | -0.00034839
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 650 342157-324708(1) | OPEN LINE FROM BUS 342157 [2ROGERSVIL J69.000] TO BUS 324708 [2ROGERSVILLE69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 651 342184-324445(1) | OPEN LINE FROM BUS 342184 [2S ANDERSON 69.000] TO BUS 324445 [2BONDS MILL 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 0 | -0.00034559
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 651 342184-324445(1) | OPEN LINE FROM BUS 342184 [2S ANDERSON 69.000] TO BUS 324445 [2BONDS MILL 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 652 342184-324445(2) | OPEN LINE FROM BUS 342184 [2S ANDERSON 69.000] TO BUS 324445 [2BONDS MILL 69.000] CKT 2 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 0 | -0.00034559
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 652 342184-324445(2) | OPEN LINE FROM BUS 342184 [2S ANDERSON 69.000] TO BUS 324445 [2BONDS MILL 69.000] CKT 2 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 653 342218-247897(Z1) | OPEN LINE FROM BUS 342218 [2SALT LICK 138.00] TO BUS 247897 [05SNAG FK SS138.00] CKT Z1 | 0.93965 | 64.8362 | 0.93968 | 64.8377 | 2.1815e-05 | -0.00032377
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 653 342218-247897(Z1) | OPEN LINE FROM BUS 342218 [2SALT LICK 138.00] TO BUS 247897 [05SNAG FK SS138.00] CKT Z1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 654 342232-324787(1) | OPEN LINE FROM BUS 342232 [2SEWELLTON 69.000] TO BUS 324787 [2UNION UNDWR69.000] CKT 1 | 0.93965 | 64.8362 | 0.93963 | 64.8344 | -2.5034e-05 | -0.00037062
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 654 342232-324787(1) | OPEN LINE FROM BUS 342232 [2SEWELLTON 69.000] TO BUS 324787 [2UNION UNDWR69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 655 342248-324718(1) | OPEN LINE FROM BUS 342248 [2SHELBY TAP 69.000] TO BUS 324718 [2SHELBY CO T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 3.5763e-06 | -0.00034201
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 655 342248-324718(1) | OPEN LINE FROM BUS 342248 [2SHELBY TAP 69.000] TO BUS 324718 [2SHELBY CO T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 656 342287-324531(1) | OPEN LINE FROM BUS 342287 [2SOMERSET KU69.000] TO BUS 324531 [2FERGUSON SO69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -2.861e-06 | -0.00034845
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 656 342287-324531(1) | OPEN LINE FROM BUS 342287 [2SOMERSET KU69.000] TO BUS 324531 [2FERGUSON SO69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 657 342287-324737(1) | OPEN LINE FROM BUS 342287 [2SOMERSET KU69.000] TO BUS 324737 [2SOMERSET SO69.000] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8371 | 1.4246e-05 | -0.00033134
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 657 342287-324737(1) | OPEN LINE FROM BUS 342287 [2SOMERSET KU69.000] TO BUS 324737 [2SOMERSET SO69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 658 342307-324509(1) | OPEN LINE FROM BUS 342307 [2STEPHENSBRG69.000] TO BUS 324509 [2EASTVIEW 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -1.7881e-06 | -0.00034738
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 658 342307-324509(1) | OPEN LINE FROM BUS 342307 [2STEPHENSBRG69.000] TO BUS 324509 [2EASTVIEW 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 659 342340-324519(1) | OPEN LINE FROM BUS 342340 [2THARP T 69.000] TO BUS 324519 [2ETOWN KU 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8357 | -6.7949e-06 | -0.00035238
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 660 342343-246971(1) | OPEN LINE FROM BUS 342343 [2THELMA 69.000] TO BUS 246971 [05THELM2 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8374 | 1.8477e-05 | -0.00032711
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 660 342343-246971(1) | OPEN LINE FROM BUS 342343 [2THELMA 69.000] TO BUS 246971 [05THELM2 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 661 342454-251315(1) | OPEN LINE FROM BUS 342454 [2W M SMITH 69.000] TO BUS 251315 [08EKSMTH 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93976 | 64.8436 | 0.00010812 | -0.00023746
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 661 342454-251315(1) | OPEN LINE FROM BUS 342454 [2W M SMITH 69.000] TO BUS 251315 [08EKSMTH 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 662 342487-250148(1) | OPEN LINE FROM BUS 342487 [2WEBSTER RD 69.000] TO BUS 250148 [08EKPWEB 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 663 342538-243688(1) | OPEN LINE FROM BUS 342538 [4ARGENTUM 138.00] TO BUS 243688 [05S.PORT MTR138.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8367 | 8.2254e-06 | -0.00033736
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 663 342538-243688(1) | OPEN LINE FROM BUS 342538 [4ARGENTUM 138.00] TO BUS 243688 [05S.PORT MTR138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 664 342544-324275(1) | OPEN LINE FROM BUS 342544 [4AVON-R 138.00] TO BUS 324275 [4LOUDON AVE 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 665 342547-324210(1) | OPEN LINE FROM BUS 342547 [4BAKER LN 138.00] TO BUS 324210 [4BAKER LANE 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93995 | 64.8568 | 0.0002985 | -4.7088e-05
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 665 342547-324210(1) | OPEN LINE FROM BUS 342547 [4BAKER LN 138.00] TO BUS 324210 [4BAKER LANE 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 666 342559-250054(1) | OPEN LINE FROM BUS 342559 [4BOONE CO 138.00] TO BUS 250054 [08LONGBR 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 667 342565-325925(1) | OPEN LINE FROM BUS 342565 [4BOONESBOR T138.00] TO BUS 325925 [4BOONSBORO N138.00] CKT 1 | 0.93965 | 64.8362 | 0.93913 | 64.7997 | -0.0005278 | -0.00087339
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 667 342565-325925(1) | OPEN LINE FROM BUS 342565 [4BOONESBOR T138.00] TO BUS 325925 [4BOONSBORO N138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 668 342568-324047(1) | OPEN LINE FROM BUS 342568 [4CENT HARDIN138.00] TO BUS 324047 [4BLACKBRANCH138.00] CKT 1 | 0.93965 | 64.8362 | 0.93963 | 64.8343 | -2.6345e-05 | -0.00037193
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 668 342568-324047(1) | OPEN LINE FROM BUS 342568 [4CENT HARDIN138.00] TO BUS 324047 [4BLACKBRANCH138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 669 342568-324261(1) | OPEN LINE FROM BUS 342568 [4CENT HARDIN138.00] TO BUS 324261 [4HARDIN CO 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8356 | -8.1062e-06 | -0.00035369
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 669 342568-324261(1) | OPEN LINE FROM BUS 342568 [4CENT HARDIN138.00] TO BUS 324261 [4HARDIN CO 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 670 342577-324247(1) | OPEN LINE FROM BUS 342577 [4FAWKES EK 138.00] TO BUS 324247 [4FAWKES TAP 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 5.9605e-08 | -0.00034553
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 670 342577-324247(1) | OPEN LINE FROM BUS 342577 [4FAWKES EK 138.00] TO BUS 324247 [4FAWKES TAP 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 671 342577-324248(1) | OPEN LINE FROM BUS 342577 [4FAWKES EK 138.00] TO BUS 324248 [4FAWKES KU 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -4.1723e-07 | -0.000346
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 671 342577-324248(1) | OPEN LINE FROM BUS 342577 [4FAWKES EK 138.00] TO BUS 324248 [4FAWKES KU 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342586 | 4GALLATIN CO | 138 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 672 342586-324253(1) | OPEN LINE FROM BUS 342586 [4GALLATIN CO138.00] TO BUS 324253 [4GHENT 138.00] CKT 1 | 1.012 | 139.6531 | 0.93742 | 129.3634 | -0.074563 | -0.002584
342587 | 1GALLATIN CO | 34.5 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 672 342586-324253(1) | OPEN LINE FROM BUS 342586 [4GALLATIN CO138.00] TO BUS 324253 [4GHENT 138.00] CKT 1 | 0.98155 | 33.8636 | 0.89944 | 31.0307 | -0.082111 | -0.040559
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 672 342586-324253(1) | OPEN LINE FROM BUS 342586 [4GALLATIN CO138.00] TO BUS 324253 [4GHENT 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 673 342595-250152(1) | OPEN LINE FROM BUS 342595 [4HEBRON 138.00] TO BUS 250152 [08HEBRNG 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 674 342607-342918(1) | OPEN LINE FROM BUS 342607 [4JK SMITH 138.00] TO BUS 342918 [1JKCT 1G 13.800] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8367 | 7.689e-06 | -0.0003379
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 674 342607-342918(1) | OPEN LINE FROM BUS 342607 [4JK SMITH 138.00] TO BUS 342918 [1JKCT 1G 13.800] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 675 342607-342921(1) | OPEN LINE FROM BUS 342607 [4JK SMITH 138.00] TO BUS 342921 [1JKCT 2G 13.800] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8367 | 7.9274e-06 | -0.00033766
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 675 342607-342921(1) | OPEN LINE FROM BUS 342607 [4JK SMITH 138.00] TO BUS 342921 [1JKCT 2G 13.800] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 676 342607-342924(1) | OPEN LINE FROM BUS 342607 [4JK SMITH 138.00] TO BUS 342924 [1JKCT 3G 13.800] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8367 | 8.0466e-06 | -0.00033754
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 676 342607-342924(1) | OPEN LINE FROM BUS 342607 [4JK SMITH 138.00] TO BUS 342924 [1JKCT 3G 13.800] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 677 342607-342927(1) | OPEN LINE FROM BUS 342607 [4JK SMITH 138.00] TO BUS 342927 [1JKCT 4G 13.800] CKT 1 | 0.93965 | 64.8362 | 0.93949 | 64.8245 | -0.00016844 | -0.00051403
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 677 342607-342927(1) | OPEN LINE FROM BUS 342607 [4JK SMITH 138.00] TO BUS 342927 [1JKCT 4G 13.800] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 678 342607-342930(1) | OPEN LINE FROM BUS 342607 [4JK SMITH 138.00] TO BUS 342930 [1JKCT 5G 13.800] CKT 1 | 0.93965 | 64.8362 | 0.93949 | 64.8245 | -0.00016874 | -0.00051433
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 678 342607-342930(1) | OPEN LINE FROM BUS 342607 [4JK SMITH 138.00] TO BUS 342930 [1JKCT 5G 13.800] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 679 342607-342933(1) | OPEN LINE FROM BUS 342607 [4JK SMITH 138.00] TO BUS 342933 [1JKCT 6G 13.800] CKT 1 | 0.93965 | 64.8362 | 0.9395 | 64.8252 | -0.00015843 | -0.00050402
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 679 342607-342933(1) | OPEN LINE FROM BUS 342607 [4JK SMITH 138.00] TO BUS 342933 [1JKCT 6G 13.800] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 680 342607-342936(1) | OPEN LINE FROM BUS 342607 [4JK SMITH 138.00] TO BUS 342936 [1JKCT 7G 13.800] CKT 1 | 0.93965 | 64.8362 | 0.9395 | 64.8253 | -0.00015783 | -0.00050342
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 680 342607-342936(1) | OPEN LINE FROM BUS 342607 [4JK SMITH 138.00] TO BUS 342936 [1JKCT 7G 13.800] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 681 342616-342948(1) | OPEN LINE FROM BUS 342616 [4LOVE HYDRO 138.00] TO BUS 342948 [1LOVE HYDRO 4.1600] CKT 1 | 0.93965 | 64.8362 | 0.93957 | 64.8303 | -8.4341e-05 | -0.00042993
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 681 342616-342948(1) | OPEN LINE FROM BUS 342616 [4LOVE HYDRO 138.00] TO BUS 342948 [1LOVE HYDRO 4.1600] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 682 342631-324328(1) | OPEN LINE FROM BUS 342631 [4PARIS T 138.00] TO BUS 324328 [4PARIS 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93829 | 64.7422 | -0.0013621 | -0.0017077
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 682 342631-324328(1) | OPEN LINE FROM BUS 342631 [4PARIS T 138.00] TO BUS 324328 [4PARIS 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 683 342649-324302(1) | OPEN LINE FROM BUS 342649 [4ROWAN CO 138.00] TO BUS 324302 [4RODBURN 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93946 | 64.8227 | -0.00019538 | -0.00054097
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 683 342649-324302(1) | OPEN LINE FROM BUS 342649 [4ROWAN CO 138.00] TO BUS 324302 [4RODBURN 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 684 342661-324267(1) | OPEN LINE FROM BUS 342661 [4SPUR-KENT-R138.00] TO BUS 324267 [4KENTON 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 685 342664-342957(1) | OPEN LINE FROM BUS 342664 [4SPURLOCK 138.00] TO BUS 342957 [1SPURLK1G 22.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 686 342688-324276(1) | OPEN LINE FROM BUS 342688 [4UNION CTY T138.00] TO BUS 324276 [4LAKE REBA T138.00] CKT 1 | 0.93965 | 64.8362 | 0.9392 | 64.8048 | -0.00045455 | -0.00080013
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 686 342688-324276(1) | OPEN LINE FROM BUS 342688 [4UNION CTY T138.00] TO BUS 324276 [4LAKE REBA T138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 687 342697-324138(1) | OPEN LINE FROM BUS 342697 [5BEATTYV J 161.00] TO BUS 324138 [5DELVINTA 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93968 | 64.8382 | 3.0041e-05 | -0.00031555
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 687 342697-324138(1) | OPEN LINE FROM BUS 342697 [5BEATTYV J 161.00] TO BUS 324138 [5DELVINTA 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 688 342697-324430(1) | OPEN LINE FROM BUS 342697 [5BEATTYV J 161.00] TO BUS 324430 [2BEATTYVI KU69.000] CKT 1 | 0.93965 | 64.8362 | 0.93956 | 64.8299 | -9.1255e-05 | -0.00043684
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 688 342697-324430(1) | OPEN LINE FROM BUS 342697 [5BEATTYV J 161.00] TO BUS 324430 [2BEATTYVI KU69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 689 342700-326975(1) | OPEN LINE FROM BUS 342700 [5BULLITT CO 161.00] TO BUS 326975 [5CEDAR GRV 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8352 | -1.3292e-05 | -0.00035888
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 689 342700-326975(1) | OPEN LINE FROM BUS 342700 [5BULLITT CO 161.00] TO BUS 326975 [5CEDAR GRV 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 690 342700-326998(1) | OPEN LINE FROM BUS 342700 [5BULLITT CO 161.00] TO BUS 326998 [5BULLITT TAP161.00] CKT 1 | 0.93965 | 64.8362 | 0.93961 | 64.8333 | -4.1544e-05 | -0.00038713
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 690 342700-326998(1) | OPEN LINE FROM BUS 342700 [5BULLITT CO 161.00] TO BUS 326998 [5BULLITT TAP161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 691 342718-324141(1) | OPEN LINE FROM BUS 342718 [5COOPER2 161.00] TO BUS 324141 [5ELIHU 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8373 | 1.7226e-05 | -0.00032836
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 691 342718-324141(1) | OPEN LINE FROM BUS 342718 [5COOPER2 161.00] TO BUS 324141 [5ELIHU 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 692 342732-361603(1) | OPEN LINE FROM BUS 342732 [5FOX HOLLOW 161.00] TO BUS 361603 [5E GLASGOW T161.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 1.4305e-06 | -0.00034416
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 692 342732-361603(1) | OPEN LINE FROM BUS 342732 [5FOX HOLLOW 161.00] TO BUS 361603 [5E GLASGOW T161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 693 342736-324138(1) | OPEN LINE FROM BUS 342736 [5GREEN HAL T161.00] TO BUS 324138 [5DELVINTA 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93993 | 64.8552 | 0.00027621 | -6.938e-05
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 693 342736-324138(1) | OPEN LINE FROM BUS 342736 [5GREEN HAL T161.00] TO BUS 324138 [5DELVINTA 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 694 342757-342945(1) | OPEN LINE FROM BUS 342757 [5LAUREL DAM 161.00] TO BUS 342945 [1LAUREL 1G 13.800] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 1.1325e-06 | -0.00034446
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 694 342757-342945(1) | OPEN LINE FROM BUS 342757 [5LAUREL DAM 161.00] TO BUS 342945 [1LAUREL 1G 13.800] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 695 342770-324271(1) | OPEN LINE FROM BUS 342770 [4MARION CO 138.00] TO BUS 324271 [4LEBANON 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8359 | -3.5763e-06 | -0.00034916
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 695 342770-324271(1) | OPEN LINE FROM BUS 342770 [4MARION CO 138.00] TO BUS 324271 [4LEBANON 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 696 342778-360473(1) | OPEN LINE FROM BUS 342778 [5MCCREARY CO161.00] TO BUS 360473 [5JELLICO TN 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 9.5367e-07 | -0.00034463
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 696 342778-360473(1) | OPEN LINE FROM BUS 342778 [5MCCREARY CO161.00] TO BUS 360473 [5JELLICO TN 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 697 342778-360486(1) | OPEN LINE FROM BUS 342778 [5MCCREARY CO161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.0133e-06 | -0.0003466
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 697 342778-360486(1) | OPEN LINE FROM BUS 342778 [5MCCREARY CO161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 698 342778-361579(1) | OPEN LINE FROM BUS 342778 [5MCCREARY CO161.00] TO BUS 361579 [5WINFIELD TN161.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8356 | -7.987e-06 | -0.00035357
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 698 342778-361579(1) | OPEN LINE FROM BUS 342778 [5MCCREARY CO161.00] TO BUS 361579 [5WINFIELD TN161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 699 342781-324688(1) | OPEN LINE FROM BUS 342781 [5PITTSBURG 161.00] TO BUS 324688 [2PITTSBRG KU69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8356 | -8.1658e-06 | -0.00035375
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 699 342781-324688(1) | OPEN LINE FROM BUS 342781 [5PITTSBURG 161.00] TO BUS 324688 [2PITTSBRG KU69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 700 342796-360448(1) | OPEN LINE FROM BUS 342796 [5RUSSEL CO J161.00] TO BUS 360448 [5WOLF CRK HP161.00] CKT 1 | 0.93965 | 64.8362 | 0.93959 | 64.8316 | -6.6578e-05 | -0.00041217
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 700 342796-360448(1) | OPEN LINE FROM BUS 342796 [5RUSSEL CO J161.00] TO BUS 360448 [5WOLF CRK HP161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 701 342814-360334(1) | OPEN LINE FROM BUS 342814 [5SUMM SHADE 161.00] TO BUS 360334 [5SUMMER SHAD161.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 0 | -0.00034559
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 701 342814-360334(1) | OPEN LINE FROM BUS 342814 [5SUMM SHADE 161.00] TO BUS 360334 [5SUMMER SHAD161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 702 342814-361788(1) | OPEN LINE FROM BUS 342814 [5SUMM SHADE 161.00] TO BUS 361788 [5SUM SHAD TP161.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 0 | -0.00034559
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 702 342814-361788(1) | OPEN LINE FROM BUS 342814 [5SUMM SHADE 161.00] TO BUS 361788 [5SUM SHAD TP161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 703 342817-325921(1) | OPEN LINE FROM BUS 342817 [5TAYLOR CO J161.00] TO BUS 325921 [5TAYLOR CO 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8356 | -7.6294e-06 | -0.00035322
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 703 342817-325921(1) | OPEN LINE FROM BUS 342817 [5TAYLOR CO J161.00] TO BUS 325921 [5TAYLOR CO 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 704 342823-360486(1) | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.93965 | 64.8362 | 0.93969 | 64.8388 | 3.8087e-05 | -0.0003075
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 704 342823-360486(1) | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 705 342832-342939-342942(1) | OPEN LINE FROM BUS 342832 [7JK SMITH 345.00] TO BUS 342939 [1JKCT 9G 13.800] TO BUS 342942 [1JKCT 10G 13.800] CKT 1 | 0.93965 | 64.8362 | 0.93909 | 64.797 | -0.00056738 | -0.00091296
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 705 342832-342939-342942(1) | OPEN LINE FROM BUS 342832 [7JK SMITH 345.00] TO BUS 342939 [1JKCT 9G 13.800] TO BUS 342942 [1JKCT 10G 13.800] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 706 342838-249581(1) | OPEN LINE FROM BUS 342838 [7SPURLOCK 345.00] TO BUS 249581 [08MELDAL 345.00] CKT 1 | 0.93965 | 64.8362 | 0.93981 | 64.847 | 0.00015712 | -0.00018847
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 706 342838-249581(1) | OPEN LINE FROM BUS 342838 [7SPURLOCK 345.00] TO BUS 249581 [08MELDAL 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 707 342838-253077(1) | OPEN LINE FROM BUS 342838 [7SPURLOCK 345.00] TO BUS 253077 [09STUART 345.00] CKT 1 | 0.93965 | 64.8362 | 0.93984 | 64.8489 | 0.00018537 | -0.00016022
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 707 342838-253077(1) | OPEN LINE FROM BUS 342838 [7SPURLOCK 345.00] TO BUS 253077 [09STUART 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 708 342838-342960(1) | OPEN LINE FROM BUS 342838 [7SPURLOCK 345.00] TO BUS 342960 [1SPURLK2G 22.000] CKT 1 | 0.93965 | 64.8362 | 0.9386 | 64.7634 | -0.001054 | -0.0013996
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 708 342838-342960(1) | OPEN LINE FROM BUS 342838 [7SPURLOCK 345.00] TO BUS 342960 [1SPURLK2G 22.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 709 342838-342963(1) | OPEN LINE FROM BUS 342838 [7SPURLOCK 345.00] TO BUS 342963 [1SPURLK3G 18.000] CKT 1 | 0.93965 | 64.8362 | 0.93911 | 64.7984 | -0.00054783 | -0.00089341
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 709 342838-342963(1) | OPEN LINE FROM BUS 342838 [7SPURLOCK 345.00] TO BUS 342963 [1SPURLK3G 18.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 710 342838-342966(1) | OPEN LINE FROM BUS 342838 [7SPURLOCK 345.00] TO BUS 342966 [1SPURLK4G 18.000] CKT 1 | 0.93965 | 64.8362 | 0.9391 | 64.7979 | -0.00055474 | -0.00090033
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 710 342838-342966(1) | OPEN LINE FROM BUS 342838 [7SPURLOCK 345.00] TO BUS 342966 [1SPURLK4G 18.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 711 342841-325074(Z1) | OPEN LINE FROM BUS 342841 [7W GARRARDEK345.00] TO BUS 325074 [7W GARRARDKU345.00] CKT Z1 | 0.93965 | 64.8362 | 0.93991 | 64.854 | 0.00025922 | -8.6367e-05
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 711 342841-325074(Z1) | OPEN LINE FROM BUS 342841 [7W GARRARDEK345.00] TO BUS 325074 [7W GARRARDKU345.00] CKT Z1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 712 342844-384157(1) | OPEN LINE FROM BUS 342844 [8SOUTHGEN 500.00] TO BUS 384157 [8MILLER8 500.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 0 | -0.00034559
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 713 342847-243205(1) | OPEN LINE FROM BUS 342847 [9NORTHGEN 765.00] TO BUS 243205 [05COOK 765.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -2.6822e-06 | -0.00034827
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 713 342847-243205(1) | OPEN LINE FROM BUS 342847 [9NORTHGEN 765.00] TO BUS 243205 [05COOK 765.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BARREN CO - HORSECAVE 69 SS | BARREN CO - HORSECAVE 69 SS | 0.93965 | 64.8362 | 0.93965 | 64.8358 | -5.0068e-06 | -0.00035059
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BARREN CO - HORSECAVE 69 SS | BARREN CO - HORSECAVE 69 SS | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | CAVE CITY J-SEYMOUR T 69 SS | CAVE CITY J-SEYMOUR T 69 SS | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 1.1921e-07 | -0.00034547
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | CAVE CITY J-SEYMOUR T 69 SS | CAVE CITY J-SEYMOUR T 69 SS | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | CAVE CITY - CAVE CITY JCT 69 SS | CAVE CITY - CAVE CITY JCT 69 SS | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 2.3246e-06 | -0.00034326
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | CAVE CITY - CAVE CITY JCT 69 SS | CAVE CITY - CAVE CITY JCT 69 SS | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | FOX HOLLOW - PARKWAY1 69 SS | FOX HOLLOW - PARKWAY1 69 SS | 0.93965 | 64.8362 | 0.93965 | 64.8362 | -5.9605e-08 | -0.00034565
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | FOX HOLLOW - PARKWAY1 69 SS | FOX HOLLOW - PARKWAY1 69 SS | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | WAYNE CO - ZULA TAP 69 SS | WAYNE CO - ZULA TAP 69 SS | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 0 | -0.00034559
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | WAYNE CO - ZULA TAP 69 SS | WAYNE CO - ZULA TAP 69 SS | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | KU GARRARD T-MANCHESTER 69 SS | KU GARRARD T-MANCHESTER 69 SS | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 6.5565e-07 | -0.00034493
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | KU GARRARD T-MANCHESTER 69 SS | KU GARRARD T-MANCHESTER 69 SS | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | GREEN BRIAR T-MANCHESTER 69 SS | GREEN BRIAR T-MANCHESTER 69 SS | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 8.3447e-07 | -0.00034475
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | GREEN BRIAR T-MANCHESTER 69 SS | GREEN BRIAR T-MANCHESTER 69 SS | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | FALL ROCK-GREEN BRIAR T 69 SS | FALL ROCK-GREEN BRIAR T 69 SS | 0.93965 | 64.8362 | 0.9397 | 64.8396 | 4.9353e-05 | -0.00029624
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | FALL ROCK-GREEN BRIAR T 69 SS | FALL ROCK-GREEN BRIAR T 69 SS | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BIG CREEK - BIG CREEK TAP 69 SS | BIG CREEK - BIG CREEK TAP 69 SS | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.0133e-06 | -0.0003466
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BIG CREEK - BIG CREEK TAP 69 SS | BIG CREEK - BIG CREEK TAP 69 SS | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | FALL ROCK - BIG CREEK TAP 69 SS | FALL ROCK - BIG CREEK TAP 69 SS | 0.93965 | 64.8362 | 0.93965 | 64.8359 | -2.9802e-06 | -0.00034857
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | FALL ROCK - BIG CREEK TAP 69 SS | FALL ROCK - BIG CREEK TAP 69 SS | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BIG CREEK - ELK MT 69 SS | BIG CREEK - ELK MT 69 SS | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 1.4305e-06 | -0.00034416
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BIG CREEK - ELK MT 69 SS | BIG CREEK - ELK MT 69 SS | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | CLAY LICK JCT - S ANDERSON 69 SS | CLAY LICK JCT - S ANDERSON 69 SS | 0.93965 | 64.8362 | 0.93956 | 64.8299 | -9.0122e-05 | -0.00043571
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | CLAY LICK JCT - S ANDERSON 69 SS | CLAY LICK JCT - S ANDERSON 69 SS | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | CLAY LICK J-CLAY LICK SW 69 SS | CLAY LICK J-CLAY LICK SW 69 SS | 0.93965 | 64.8362 | 0.93966 | 64.8365 | 5.1856e-06 | -0.0003404
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | CLAY LICK J-CLAY LICK SW 69 SS | CLAY LICK J-CLAY LICK SW 69 SS | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | OWEN CO - OWEN CO JCT 2 69 SS | OWEN CO - OWEN CO JCT 2 69 SS | 0.93965 | 64.8362 | 0.93965 | 64.8357 | -6.4969e-06 | -0.00035208
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | OWEN CO - OWEN CO JCT 2 69 SS | OWEN CO - OWEN CO JCT 2 69 SS | 1.05 | 525 | 1.05 | 525 | 0 | 0
341200 | 2BROMLEYEK | 69 | EKPC' | RANGE | 0.94 | 1.05 | OWEN CO JCT 1 - BROMLEY EK 69 SS | OWEN CO JCT 1 - BROMLEY EK 69 SS | 0.99203 | 68.4498 | 0.93081 | 64.2256 | -0.061221 | -0.0091943
341920 | 2MUNK J | 69 | EKPC' | RANGE | 0.94 | 1.05 | OWEN CO JCT 1 - BROMLEY EK 69 SS | OWEN CO JCT 1 - BROMLEY EK 69 SS | 0.97761 | 67.4549 | 0.93551 | 64.5503 | -0.042094 | -0.0044877
341998 | 2OAKLEY NOEL | 69 | EKPC' | RANGE | 0.94 | 1.05 | OWEN CO JCT 1 - BROMLEY EK 69 SS | OWEN CO JCT 1 - BROMLEY EK 69 SS | 0.96812 | 66.8005 | 0.93806 | 64.7259 | -0.030067 | -0.0019436
342502 | 2WILLIAMSTWN | 69 | EKPC' | RANGE | 0.94 | 1.05 | OWEN CO JCT 1 - BROMLEY EK 69 SS | OWEN CO JCT 1 - BROMLEY EK 69 SS | 0.97778 | 67.467 | 0.93581 | 64.5712 | -0.041968 | -0.0041862
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | OWEN CO JCT 1 - BROMLEY EK 69 SS | OWEN CO JCT 1 - BROMLEY EK 69 SS | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BROMLEY EK - MUNK JCT 69 SS | BROMLEY EK - MUNK JCT 69 SS | 1.05 | 525 | 1.05 | 525 | 0 | 0
342502 | 2WILLIAMSTWN | 69 | EKPC' | RANGE | 0.94 | 1.05 | MUNK JCT - WILLIAMSTOWN 69 SS | MUNK JCT - WILLIAMSTOWN 69 SS | 0.97778 | 67.467 | 0.93402 | 64.4475 | -0.04376 | -0.0059783
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | MUNK JCT - WILLIAMSTOWN 69 SS | MUNK JCT - WILLIAMSTOWN 69 SS | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | RENAKER - THREE M 69 SS | RENAKER - THREE M 69 SS | 0.93965 | 64.8362 | 0.93888 | 64.7824 | -0.00077915 | -0.0011247
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | RENAKER - THREE M 69 SS | RENAKER - THREE M 69 SS | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | KU W FRANKFORT BRDGPT1 69 SS | KU W FRANKFORT BRDGPT1 69 SS | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -5.9605e-07 | -0.00034618
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | KU W FRANKFORT BRDGPT1 69 SS | KU W FRANKFORT BRDGPT1 69 SS | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BRIDGEPORT J-BRDGPT2 69 SS | BRIDGEPORT J-BRDGPT2 69 SS | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 1.1921e-07 | -0.00034547
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BRIDGEPORT J-BRDGPT2 69 SS | BRIDGEPORT J-BRDGPT2 69 SS | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | STANLEY PARKER - BANK LICK 69 SS | STANLEY PARKER - BANK LICK 69 SS | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BEATTYVILLE-BEATTYVLLE D SS | BEATTYVILLE-BEATTYVLLE D SS | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -6.5565e-07 | -0.00034624
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BEATTYVILLE-BEATTYVLLE D SS | BEATTYVILLE-BEATTYVLLE D SS | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BEATTYVILLE DIST - OAKDALE 69 SS | BEATTYVILLE DIST - OAKDALE 69 SS | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 0 | -0.00034559
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BEATTYVILLE DIST - OAKDALE 69 SS | BEATTYVILLE DIST - OAKDALE 69 SS | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SHELBY CO BUS SS | SHELBY CO BUS SS | 0.93965 | 64.8362 | 0.93972 | 64.8404 | 6.1452e-05 | -0.00028414
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SHELBY CO BUS SS | SHELBY CO BUS SS | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_OWEN-PENN69 | EKPC_P1-2_OWEN-PENN69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_PENN-RENAKER69 | EKPC_P1-2_PENN-RENAKER69 | 0.93965 | 64.8362 | 0.93908 | 64.7964 | -0.00057554 | -0.00092113
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_PENN-RENAKER69 | EKPC_P1-2_PENN-RENAKER69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_BOONE-HEBRON69 | EKPC_P1-2_BOONE-HEBRON69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_BOON-OWN-REN69 | EKPC_P1-2_BOON-OWN-REN69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_T FTJ-WEB RD69 | EKPC_P1-2_T FTJ-WEB RD69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_TFTJ- ST PRK69 | EKPC_P1-2_TFTJ- ST PRK69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_ST PRK-BRAK 69 | EKPC_P1-2_ST PRK-BRAK 69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_OWN-CARSON 69 | EKPC_P1-2_OWN-CARSON 69 | 0.93965 | 64.8362 | 0.93971 | 64.8397 | 5.12e-05 | -0.00029439
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_OWN-CARSON 69 | EKPC_P1-2_OWN-CARSON 69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_OWN-CLY VILL69 | EKPC_P1-2_OWN-CLY VILL69 | 0.93965 | 64.8362 | 0.93975 | 64.8427 | 9.4771e-05 | -0.00025082
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_OWN-CLY VILL69 | EKPC_P1-2_OWN-CLY VILL69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_BRAK- REN 69 | EKPC_P1-2_BRAK- REN 69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_BRAK- KU KEN69 | EKPC_P1-2_BRAK- KU KEN69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_PLUM-GODDARD69 | EKPC_P1-2_PLUM-GODDARD69 | 0.93965 | 64.8362 | 0.93981 | 64.8471 | 0.00015837 | -0.00018722
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_PLUM-GODDARD69 | EKPC_P1-2_PLUM-GODDARD69 | 1.05 | 525 | 1.05 | 525 | 1.1921e-07 | 1.1921e-07
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_MURPH - HQ 69 | EKPC_P1-2_MURPH - HQ 69 | 0.93965 | 64.8362 | 0.93953 | 64.8275 | -0.000126 | -0.00047159
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_MURPH - HQ 69 | EKPC_P1-2_MURPH - HQ 69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_MURPH-MILLBG69 | EKPC_P1-2_MURPH-MILLBG69 | 0.93965 | 64.8362 | 0.93903 | 64.7932 | -0.00062275 | -0.00096834
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_MURPH-MILLBG69 | EKPC_P1-2_MURPH-MILLBG69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_MURPH-KU KEN69 | EKPC_P1-2_MURPH-KU KEN69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_ARGEN - LEON69 | EKPC_P1-2_ARGEN - LEON69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_LEON-SKAGGS 69 | EKPC_P1-2_LEON-SKAGGS 69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_FIN-SHL-SHBV69 | EKPC_P1-2_FIN-SHL-SHBV69 | 0.93965 | 64.8362 | 0.93968 | 64.8379 | 2.5988e-05 | -0.0003196
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_FIN-SHL-SHBV69 | EKPC_P1-2_FIN-SHL-SHBV69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_SHL-BUD-BKRT69 | EKPC_P1-2_SHL-BUD-BKRT69 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -6.5565e-07 | -0.00034624
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_SHL-BUD-BKRT69 | EKPC_P1-2_SHL-BUD-BKRT69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_REN - HQ 69 | EKPC_P1-2_REN - HQ 69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_GODD - HOPE 69 | EKPC_P1-2_GODD - HOPE 69 | 0.93965 | 64.8362 | 0.93941 | 64.8196 | -0.00023955 | -0.00058514
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_GODD - HOPE 69 | EKPC_P1-2_GODD - HOPE 69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_GODD - ROW 69 | EKPC_P1-2_GODD - ROW 69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_BULL-W BARDJ69 | EKPC_P1-2_BULL-W BARDJ69 | 0.93965 | 64.8362 | 0.93965 | 64.8357 | -6.9737e-06 | -0.00035256
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_BULL-W BARDJ69 | EKPC_P1-2_BULL-W BARDJ69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_BULL - NELS 69 | EKPC_P1-2_BULL - NELS 69 | 0.93965 | 64.8362 | 0.93963 | 64.8345 | -2.4319e-05 | -0.00036991
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_BULL - NELS 69 | EKPC_P1-2_BULL - NELS 69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_N SPR -S AND69 | EKPC_P1-2_N SPR -S AND69 | 0.93965 | 64.8362 | 0.93969 | 64.8388 | 3.8445e-05 | -0.00030714
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_N SPR -S AND69 | EKPC_P1-2_N SPR -S AND69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_HNTFMJ-S AND69 | EKPC_P1-2_HNTFMJ-S AND69 | 0.93965 | 64.8362 | 0.93964 | 64.8355 | -9.5367e-06 | -0.00035512
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_HNTFMJ-S AND69 | EKPC_P1-2_HNTFMJ-S AND69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_BKR LN-FAY 69 | EKPC_P1-2_BKR LN-FAY 69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_HQ-HUNT 69 | EKPC_P1-2_HQ-HUNT 69 | 0.93965 | 64.8362 | 0.93909 | 64.7975 | -0.00055981 | -0.00090539
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_HQ-HUNT 69 | EKPC_P1-2_HQ-HUNT 69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_HUNT-POWELL 69 | EKPC_P1-2_HUNT-POWELL 69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_DALE-HTFRMJ69 | EKPC_P1-2_DALE-HTFRMJ69 | 0.93965 | 64.8362 | 0.93966 | 64.8368 | 9.8944e-06 | -0.00033569
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_DALE-HTFRMJ69 | EKPC_P1-2_DALE-HTFRMJ69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_DALE-GARRD 69 | EKPC_P1-2_DALE-GARRD 69 | 0.93965 | 64.8362 | 0.93971 | 64.8398 | 5.2214e-05 | -0.00029337
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_DALE-GARRD 69 | EKPC_P1-2_DALE-GARRD 69 | 1.05 | 525 | 1.05 | 525 | 1.1921e-07 | 1.1921e-07
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_HOPE - POW 69 | EKPC_P1-2_HOPE - POW 69 | 0.93965 | 64.8362 | 0.93964 | 64.8352 | -1.4067e-05 | -0.00035965
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_HOPE - POW 69 | EKPC_P1-2_HOPE - POW 69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_HOPE - MORG 69 | EKPC_P1-2_HOPE - MORG 69 | 0.93965 | 64.8362 | 0.93994 | 64.8562 | 0.00028998 | -5.5611e-05
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_HOPE - MORG 69 | EKPC_P1-2_HOPE - MORG 69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_MORG-SKAGGS69 | EKPC_P1-2_MORG-SKAGGS69 | 0.93965 | 64.8362 | 0.93983 | 64.8486 | 0.00017977 | -0.00016582
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_MORG-SKAGGS69 | EKPC_P1-2_MORG-SKAGGS69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_SKAGGS-FALC69 | EKPC_P1-2_SKAGGS-FALC69 | 0.93965 | 64.8362 | 0.93975 | 64.8424 | 9.0837e-05 | -0.00025475
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_SKAGGS-FALC69 | EKPC_P1-2_SKAGGS-FALC69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_SKAGGS-THELM69 | EKPC_P1-2_SKAGGS-THELM69 | 0.93965 | 64.8362 | 0.93983 | 64.8479 | 0.00017095 | -0.00017464
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_SKAGGS-THELM69 | EKPC_P1-2_SKAGGS-THELM69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_C HAR-KU ETN69 | EKPC_P1-2_C HAR-KU ETN69 | 0.93965 | 64.8362 | 0.93965 | 64.8355 | -9.1195e-06 | -0.00035471
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_C HAR-KU ETN69 | EKPC_P1-2_C HAR-KU ETN69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_STEPH-HODG 69 | EKPC_P1-2_STEPH-HODG 69 | 0.93965 | 64.8362 | 0.93965 | 64.8359 | -3.9339e-06 | -0.00034952
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_STEPH-HODG 69 | EKPC_P1-2_STEPH-HODG 69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_STEPH-BONN 69 | EKPC_P1-2_STEPH-BONN 69 | 0.93965 | 64.8362 | 0.93965 | 64.8358 | -4.53e-06 | -0.00035012
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_STEPH-BONN 69 | EKPC_P1-2_STEPH-BONN 69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_ETOWN-KU ETN69 | EKPC_P1-2_ETOWN-KU ETN69 | 0.93965 | 64.8362 | 0.93964 | 64.8354 | -1.1444e-05 | -0.00035703
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_ETOWN-KU ETN69 | EKPC_P1-2_ETOWN-KU ETN69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_ETWN-ROG-RAD69 | EKPC_P1-2_ETWN-ROG-RAD69 | 0.93965 | 64.8362 | 0.93963 | 64.8347 | -2.0564e-05 | -0.00036615
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_ETWN-ROG-RAD69 | EKPC_P1-2_ETWN-ROG-RAD69 | 1.05 | 525 | 1.05 | 525 | 1.1921e-07 | 1.1921e-07
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_ETOWN-NELSN 69 | EKPC_P1-2_ETOWN-NELSN 69 | 0.93965 | 64.8362 | 0.93965 | 64.8356 | -7.8082e-06 | -0.0003534
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_ETOWN-NELSN 69 | EKPC_P1-2_ETOWN-NELSN 69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_W BARDJ-EBRD69 | EKPC_P1-2_W BARDJ-EBRD69 | 0.93965 | 64.8362 | 0.93966 | 64.8366 | 6.9141e-06 | -0.00033867
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_W BARDJ-EBRD69 | EKPC_P1-2_W BARDJ-EBRD69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_HODG-GREEN 69 | EKPC_P1-2_HODG-GREEN 69 | 0.93965 | 64.8362 | 0.93965 | 64.8357 | -6.9737e-06 | -0.00035256
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_HODG-GREEN 69 | EKPC_P1-2_HODG-GREEN 69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_HODG-N SPR 69 | EKPC_P1-2_HODG-N SPR 69 | 0.93965 | 64.8362 | 0.93967 | 64.8373 | 1.6391e-05 | -0.0003292
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_HODG-N SPR 69 | EKPC_P1-2_HODG-N SPR 69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_E BARD-N SPR69 | EKPC_P1-2_E BARD-N SPR69 | 0.93965 | 64.8362 | 0.93967 | 64.8372 | 1.502e-05 | -0.00033057
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_E BARD-N SPR69 | EKPC_P1-2_E BARD-N SPR69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_E BRD-KU BRD69 | EKPC_P1-2_E BRD-KU BRD69 | 0.93965 | 64.8362 | 0.93964 | 64.8349 | -1.7762e-05 | -0.00036335
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_E BRD-KU BRD69 | EKPC_P1-2_E BRD-KU BRD69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_HNTFMJ-N SPR69 | EKPC_P1-2_HNTFMJ-N SPR69 | 0.93965 | 64.8362 | 0.93973 | 64.8414 | 7.5579e-05 | -0.00027001
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_HNTFMJ-N SPR69 | EKPC_P1-2_HNTFMJ-N SPR69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_W BER-THRLJ 69 | EKPC_P1-2_W BER-THRLJ 69 | 0.93965 | 64.8362 | 0.93976 | 64.8434 | 0.00010455 | -0.00024104
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_W BER-THRLJ 69 | EKPC_P1-2_W BER-THRLJ 69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_W BER-KU FAW69 | EKPC_P1-2_W BER-KU FAW69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_POW - ZACH 69 | EKPC_P1-2_POW - ZACH 69 | 0.93965 | 64.8362 | 0.93956 | 64.8299 | -9.1016e-05 | -0.0004366
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_POW - ZACH 69 | EKPC_P1-2_POW - ZACH 69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_ZACH-HELECH69 | EKPC_P1-2_ZACH-HELECH69 | 0.93965 | 64.8362 | 0.93947 | 64.8234 | -0.00018519 | -0.00053078
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_ZACH-HELECH69 | EKPC_P1-2_ZACH-HELECH69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_BETYV - OAK 69 | EKPC_P1-2_BETYV - OAK 69 | 0.93965 | 64.8362 | 0.93976 | 64.8432 | 0.00010186 | -0.00024372
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_BETYV - TYN 69 | EKPC_P1-2_BETYV - TYN 69 | 0.93965 | 64.8362 | 0.93972 | 64.8409 | 6.8188e-05 | -0.0002774
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_BETYV - TYN 69 | EKPC_P1-2_BETYV - TYN 69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_HELECH-MAG 69 | EKPC_P1-2_HELECH-MAG 69 | 0.93965 | 64.8362 | 0.93964 | 64.8354 | -1.1206e-05 | -0.00035679
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_HELECH-MAG 69 | EKPC_P1-2_HELECH-MAG 69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_FALC - MAG 69 | EKPC_P1-2_FALC - MAG 69 | 0.93965 | 64.8362 | 0.93938 | 64.817 | -0.00027758 | -0.00062317
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_FALC - MAG 69 | EKPC_P1-2_FALC - MAG 69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_MAG - THELM 69 | EKPC_P1-2_MAG - THELM 69 | 0.93965 | 64.8362 | 0.93999 | 64.8591 | 0.00033313 | -1.2457e-05
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_MAG - THELM 69 | EKPC_P1-2_MAG - THELM 69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_BONN - BARR 69 | EKPC_P1-2_BONN - BARR 69 | 0.93965 | 64.8362 | 0.93969 | 64.8383 | 3.165e-05 | -0.00031394
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_BONN - BARR 69 | EKPC_P1-2_BONN - BARR 69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_GREEN-SUM SH69 | EKPC_P1-2_GREEN-SUM SH69 | 0.93965 | 64.8362 | 0.93965 | 64.8359 | -3.7551e-06 | -0.00034934
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_GREEN-SUM SH69 | EKPC_P1-2_GREEN-SUM SH69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_CASEY-LIB J69 | EKPC_P1-2_CASEY-LIB J69 | 0.93965 | 64.8362 | 0.93966 | 64.8365 | 5.4836e-06 | -0.0003401
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_CASEY-LIB J69 | EKPC_P1-2_CASEY-LIB J69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_LIB J-GARR69 | EKPC_P1-2_LIB J-GARR69 | 0.93965 | 64.8362 | 0.93968 | 64.838 | 2.7239e-05 | -0.00031835
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_LIB J-GARR69 | EKPC_P1-2_LIB J-GARR69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_LIB J-WIND 69 | EKPC_P1-2_LIB J-WIND 69 | 0.93965 | 64.8362 | 0.93966 | 64.8365 | 4.4703e-06 | -0.00034112
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_PUL-WAL-SSET69 | EKPC_P1-2_PUL-WAL-SSET69 | 0.93965 | 64.8362 | 0.93977 | 64.8444 | 0.00011939 | -0.0002262
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_PUL-WAL-SSET69 | EKPC_P1-2_PUL-WAL-SSET69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_PUL - WOODSTOCK 69 | EKPC_P1-2_PUL - WOODSTOCK 69 | 0.93965 | 64.8362 | 0.93965 | 64.8359 | -4.1127e-06 | -0.0003497
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_PUL - WOODSTOCK 69 | EKPC_P1-2_PUL - WOODSTOCK 69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_THREELJ- WAL69 | EKPC_P1-2_THREELJ- WAL69 | 0.93965 | 64.8362 | 0.93967 | 64.8375 | 1.955e-05 | -0.00032604
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_THREELJ- WAL69 | EKPC_P1-2_THREELJ- WAL69 | 1.05 | 525 | 1.05 | 525 | 1.1921e-07 | 1.1921e-07
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_TYN - N LON 69 | EKPC_P1-2_TYN - N LON 69 | 0.93965 | 64.8362 | 0.93973 | 64.8416 | 7.9095e-05 | -0.00026649
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_TYN - N LON 69 | EKPC_P1-2_TYN - N LON 69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_FALL R-GARR69 | EKPC_P1-2_FALL R-GARR69 | 0.93965 | 64.8362 | 0.93969 | 64.8389 | 3.9995e-05 | -0.00030559
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_FALL R-GARR69 | EKPC_P1-2_FALL R-GARR69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_FALL R-GOOS 69 | EKPC_P1-2_FALL R-GOOS 69 | 0.93965 | 64.8362 | 0.93971 | 64.8402 | 5.8591e-05 | -0.000287
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_FALL R-GOOS 69 | EKPC_P1-2_FALL R-GOOS 69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_BARR- FOX H 69 | EKPC_P1-2_BARR- FOX H 69 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.2517e-06 | -0.00034684
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_BARR- FOX H 69 | EKPC_P1-2_BARR- FOX H 69 | 1.05 | 525 | 1.05 | 525 | 1.1921e-07 | 1.1921e-07
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_FOX H-SUMMSH69 | EKPC_P1-2_FOX H-SUMMSH69 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.3113e-06 | -0.0003469
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_FOX H-SUMMSH69 | EKPC_P1-2_FOX H-SUMMSH69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_SUMMSH-SEWJ 69 | EKPC_P1-2_SUMMSH-SEWJ 69 | 0.93965 | 64.8362 | 0.93967 | 64.8369 | 1.1384e-05 | -0.0003342
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_SUMMSH-SEWJ 69 | EKPC_P1-2_SUMMSH-SEWJ 69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_SUMMSH-WAYNE69 | EKPC_P1-2_SUMMSH-WAYNE69 | 0.93965 | 64.8362 | 0.93965 | 64.8358 | -5.3644e-06 | -0.00035095
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_SUMMSH-WAYNE69 | EKPC_P1-2_SUMMSH-WAYNE69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_WAYNE-ZULA 69 | EKPC_P1-2_WAYNE-ZULA 69 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 2.2054e-06 | -0.00034338
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_WAYNE-ZULA 69 | EKPC_P1-2_WAYNE-ZULA 69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_SEWJ - RUSS 69 | EKPC_P1-2_SEWJ - RUSS 69 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 2.9206e-06 | -0.00034267
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_SEWJ - RUSS 69 | EKPC_P1-2_SEWJ - RUSS 69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_SEWJ - WIND 69 | EKPC_P1-2_SEWJ - WIND 69 | 0.93965 | 64.8362 | 0.93967 | 64.8372 | 1.502e-05 | -0.00033057
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_SEWJ - WIND 69 | EKPC_P1-2_SEWJ - WIND 69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_RUSS-KU SSET69 | EKPC_P1-2_RUSS-KU SSET69 | 0.93965 | 64.8362 | 0.9397 | 64.8392 | 4.4525e-05 | -0.00030106
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_RUSS-KU SSET69 | EKPC_P1-2_RUSS-KU SSET69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_WIND - SSET 69 | EKPC_P1-2_WIND - SSET 69 | 0.93965 | 64.8362 | 0.93966 | 64.8365 | 5.722e-06 | -0.00033987
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_WIND - SSET 69 | EKPC_P1-2_WIND - SSET 69 | 1.05 | 525 | 1.05 | 525 | 1.1921e-07 | 1.1921e-07
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_SSET-KU ELI 69 | EKPC_P1-2_SSET-KU ELI 69 | 0.93965 | 64.8362 | 0.93967 | 64.8371 | 1.4126e-05 | -0.00033146
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_SSET-KU ELI 69 | EKPC_P1-2_SSET-KU ELI 69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_COOP-DENNY 69 | EKPC_P1-2_COOP-DENNY 69 | 0.93965 | 64.8362 | 0.93967 | 64.8372 | 1.5557e-05 | -0.00033003
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_COOP-DENNY 69 | EKPC_P1-2_COOP-DENNY 69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_LAUR-KU FAR69 | EKPC_P1-2_LAUR-KU FAR69 | 0.93965 | 64.8362 | 0.93974 | 64.8421 | 8.6844e-05 | -0.00025874
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_LAUR-KU FAR69 | EKPC_P1-2_LAUR-KU FAR69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_LAUR-KU SWTH69 | EKPC_P1-2_LAUR-KU SWTH69 | 0.93965 | 64.8362 | 0.93972 | 64.8406 | 6.4135e-05 | -0.00028145
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_LAUR-KU SWTH69 | EKPC_P1-2_LAUR-KU SWTH69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_WAYNE-DENNY69 | EKPC_P1-2_WAYNE-DENNY69 | 0.93965 | 64.8362 | 0.93967 | 64.8369 | 1.0848e-05 | -0.00033474
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_WAYNE-DENNY69 | EKPC_P1-2_WAYNE-DENNY69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_DENNY-MCCRRY69 | EKPC_P1-2_DENNY-MCCRRY69 | 0.93965 | 64.8362 | 0.93967 | 64.8371 | 1.3411e-05 | -0.00033218
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_DENNY-MCCRRY69 | EKPC_P1-2_DENNY-MCCRRY69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_MCCRY-KUWOFF69 | EKPC_P1-2_MCCRY-KUWOFF69 | 0.93965 | 64.8362 | 0.93966 | 64.8368 | 9.8348e-06 | -0.00033575
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_MCCRY-KUWOFF69 | EKPC_P1-2_MCCRY-KUWOFF69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_CLYV-SHL-FRK69 | EKPC_P1-2_CLYV-SHL-FRK69 | 0.93965 | 64.8362 | 0.93973 | 64.8413 | 7.4387e-05 | -0.0002712
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_CLYV-SHL-FRK69 | EKPC_P1-2_CLYV-SHL-FRK69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_BULL- PLENTG69 | EKPC_P1-2_BULL- PLENTG69 | 0.93965 | 64.8362 | 0.93964 | 64.8354 | -1.1384e-05 | -0.00035697
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_BULL- PLENTG69 | EKPC_P1-2_BULL- PLENTG69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_AEPMORG- MOR69 | EKPC_P1-2_AEPMORG- MOR69 | 0.93965 | 64.8362 | 0.9396 | 64.8324 | -5.3883e-05 | -0.00039947
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_AEPMORG- MOR69 | EKPC_P1-2_AEPMORG- MOR69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_AEPMORG-INDX69 | EKPC_P1-2_AEPMORG-INDX69 | 0.93965 | 64.8362 | 0.93963 | 64.8345 | -2.3782e-05 | -0.00036937
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_AEPMORG-INDX69 | EKPC_P1-2_AEPMORG-INDX69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_HODG-KU BARD69 | EKPC_P1-2_HODG-KU BARD69 | 0.93965 | 64.8362 | 0.93966 | 64.8367 | 7.6294e-06 | -0.00033796
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_HODG-KU BARD69 | EKPC_P1-2_HODG-KU BARD69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_HODG-KU ETWN69 | EKPC_P1-2_HODG-KU ETWN69 | 0.93965 | 64.8362 | 0.93966 | 64.8368 | 8.7023e-06 | -0.00033689
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_HODG-KU ETWN69 | EKPC_P1-2_HODG-KU ETWN69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_N SPR-KU LEB69 | EKPC_P1-2_N SPR-KU LEB69 | 0.93965 | 64.8362 | 0.93968 | 64.838 | 2.6703e-05 | -0.00031888
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_N SPR-KU LEB69 | EKPC_P1-2_N SPR-KU LEB69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_BAR-BON-FHOL69 | EKPC_P1-2_BAR-BON-FHOL69 | 0.93965 | 64.8362 | 0.93965 | 64.8358 | -5.722e-06 | -0.00035131
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_BAR-BON-FHOL69 | EKPC_P1-2_BAR-BON-FHOL69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_FHOL-PARK69 | EKPC_P1-2_FHOL-PARK69 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -1.6689e-06 | -0.00034726
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_FHOL-PARK69 | EKPC_P1-2_FHOL-PARK69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341320 | 2COBURG | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_GREEN-KUTAY69 | EKPC_P1-2_GREEN-KUTAY69 | 0.98131 | 67.7106 | 0.92672 | 63.9438 | -0.054591 | -0.013278
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_GREEN-KUTAY69 | EKPC_P1-2_GREEN-KUTAY69 | 0.93965 | 64.8362 | 0.93965 | 64.8357 | -6.3777e-06 | -0.00035197
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_GREEN-KUTAY69 | EKPC_P1-2_GREEN-KUTAY69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
324830 | 2CAMPBELV EK | 69 | LGEE' | RANGE | 0.94 | 1.06 | EKPC_P1-2_GREEN-KUTAY69 | EKPC_P1-2_GREEN-KUTAY69 | 0.99017 | 68.3215 | 0.91204 | 62.931 | -0.078122 | -0.027956
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_NLON-KU NLON69 | EKPC_P1-2_NLON-KU NLON69 | 0.93965 | 64.8362 | 0.93967 | 64.837 | 1.2696e-05 | -0.00033289
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_NLON-KU NLON69 | EKPC_P1-2_NLON-KU NLON69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_DK HEB-HEB 138 | EKPC_P1-2_DK HEB-HEB 138 | 0.93965 | 64.8362 | 0.93901 | 64.7916 | -0.00064582 | -0.0009914
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_DK HEB-HEB 138 | EKPC_P1-2_DK HEB-HEB 138 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_BOONE-BUFF138 | EKPC_P1-2_BOONE-BUFF138 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_BOONE-STANP138 | EKPC_P1-2_BOONE-STANP138 | 0.93965 | 64.8362 | 0.93983 | 64.8481 | 0.00017351 | -0.00017208
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_BOONE-STANP138 | EKPC_P1-2_BOONE-STANP138 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_BOONE-GALL138 | EKPC_P1-2_BOONE-GALL138 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_BOONE-REN 138 | EKPC_P1-2_BOONE-REN 138 | 0.93965 | 64.8362 | 0.93945 | 64.8221 | -0.00020325 | -0.00054884
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_BOONE-REN 138 | EKPC_P1-2_BOONE-REN 138 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_OWEN 138/69 | EKPC_P1-2_OWEN 138/69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_SPUR-KUKEN 138 | EKPC_P1-2_SPUR-KUKEN 138 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_SPUR-PLUM 138 | EKPC_P1-2_SPUR-PLUM 138 | 0.93965 | 64.8362 | 0.93957 | 64.8302 | -8.6725e-05 | -0.00043231
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_SPUR-PLUM 138 | EKPC_P1-2_SPUR-PLUM 138 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_SPUR-GODD 138 | EKPC_P1-2_SPUR-GODD 138 | 0.93965 | 64.8362 | 0.93892 | 64.7854 | -0.00073564 | -0.0010812
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_SPUR-GODD 138 | EKPC_P1-2_SPUR-GODD 138 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_GODD - ROW138 | EKPC_P1-2_GODD - ROW138 | 0.93965 | 64.8362 | 0.93903 | 64.7933 | -0.00062108 | -0.00096667
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_GODD - ROW138 | EKPC_P1-2_GODD - ROW138 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_AVN-PAR-REN138 | EKPC_P1-2_AVN-PAR-REN138 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_AVN-BBN-DLE138 | EKPC_P1-2_AVN-BBN-DLE138 | 0.93965 | 64.8362 | 0.93898 | 64.7894 | -0.00067747 | -0.0010231
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_AVN-BBN-DLE138 | EKPC_P1-2_AVN-BBN-DLE138 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_AVON-FAY 138 | EKPC_P1-2_AVON-FAY 138 | 0.93965 | 64.8362 | 0.93996 | 64.8571 | 0.00030345 | -4.214e-05
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_AVON-FAY 138 | EKPC_P1-2_AVON-FAY 138 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_AVON-LOUD 138 | EKPC_P1-2_AVON-LOUD 138 | 1.05 | 525 | 1.05 | 525 | 1.1921e-07 | 1.1921e-07
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_DALE-FAWK 138 | EKPC_P1-2_DALE-FAWK 138 | 0.93965 | 64.8362 | 0.93979 | 64.8452 | 0.00013119 | -0.0002144
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_DALE-FAWK 138 | EKPC_P1-2_DALE-FAWK 138 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_FAW-W BER 138 | EKPC_P1-2_FAW-W BER 138 | 0.93965 | 64.8362 | 0.93999 | 64.8593 | 0.00033581 | -9.7752e-06
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_FAW-W BER 138 | EKPC_P1-2_FAW-W BER 138 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_JKS 345/138 1 | EKPC_P1-2_JKS 345/138 1 | 0.93965 | 64.8362 | 0.93965 | 64.8355 | -9.0003e-06 | -0.00035459
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_JKS 345/138 1 | EKPC_P1-2_JKS 345/138 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_JKS 345/138 2 | EKPC_P1-2_JKS 345/138 2 | 0.93965 | 64.8362 | 0.93964 | 64.8354 | -1.1325e-05 | -0.00035691
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_JKS 345/138 2 | EKPC_P1-2_JKS 345/138 2 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_JKSMTH-REBA138 | EKPC_P1-2_JKSMTH-REBA138 | 0.93965 | 64.8362 | 0.93921 | 64.8053 | -0.00044656 | -0.00079215
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_JKSMTH-REBA138 | EKPC_P1-2_JKSMTH-REBA138 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_ROW-SKAG138 | EKPC_P1-2_ROW-SKAG138 | 0.93965 | 64.8362 | 0.94 | 64.8599 | 0.0003441 | -1.4901e-06
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_ROW-SKAG138 | EKPC_P1-2_ROW-SKAG138 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_CHARD-HRDBG138 | EKPC_P1-2_CHARD-HRDBG138 | 0.93965 | 64.8362 | 0.93961 | 64.8331 | -4.4405e-05 | -0.00038999
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_CHARD-HRDBG138 | EKPC_P1-2_CHARD-HRDBG138 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_COP-RUS-WLF161 | EKPC_P1-2_COP-RUS-WLF161 | 0.93965 | 64.8362 | 0.93955 | 64.8293 | -9.9659e-05 | -0.00044525
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_COP-RUS-WLF161 | EKPC_P1-2_COP-RUS-WLF161 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_COOP-DEN161 | EKPC_P1-2_COOP-DEN161 | 0.93965 | 64.8362 | 0.93971 | 64.8397 | 5.1558e-05 | -0.00029403
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_COOP-DEN161 | EKPC_P1-2_COOP-DEN161 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | EKPC_P1-2_COP-LIBJ-PU161 | 0.93965 | 64.8362 | 0.93959 | 64.8315 | -6.777e-05 | -0.00041336
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | EKPC_P1-2_COP-LIBJ-PU161 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_LIB-CAS-GAS-MAR161 | EKPC_P1-2_LIB-CAS-GAS-MAR161 | 0.93965 | 64.8362 | 0.93966 | 64.8366 | 7.093e-06 | -0.00033849
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_LIB-CAS-GAS-MAR161 | EKPC_P1-2_LIB-CAS-GAS-MAR161 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | EKPC_P1-2_MCCR-WAYNE161 | 0.93965 | 64.8362 | 0.93968 | 64.8383 | 3.0458e-05 | -0.00031513
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | EKPC_P1-2_MCCR-WAYNE161 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_LAUR-PIT-TY161 | EKPC_P1-2_LAUR-PIT-TY161 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 3.3975e-06 | -0.00034219
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_LAUR-PIT-TY161 | EKPC_P1-2_LAUR-PIT-TY161 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_TYN-DELV161 | EKPC_P1-2_TYN-DELV161 | 0.93965 | 64.8362 | 0.93994 | 64.8555 | 0.00028074 | -6.485e-05
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_TYN-DELV161 | EKPC_P1-2_TYN-DELV161 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_TYN-FALLR161 | EKPC_P1-2_TYN-FALLR161 | 0.93965 | 64.8362 | 0.93962 | 64.8336 | -3.6955e-05 | -0.00038254
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_TYN-FALLR161 | EKPC_P1-2_TYN-FALLR161 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_GRE-TAY-MAR161 | EKPC_P1-2_GRE-TAY-MAR161 | 0.93965 | 64.8362 | 0.93963 | 64.8345 | -2.4319e-05 | -0.00036991
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_GRE-TAY-MAR161 | EKPC_P1-2_GRE-TAY-MAR161 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_BARR-SUMSH161 | EKPC_P1-2_BARR-SUMSH161 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 2.9206e-06 | -0.00034267
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_BARR-SUMSH161 | EKPC_P1-2_BARR-SUMSH161 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_BULL-SUMSH161 | EKPC_P1-2_BULL-SUMSH161 | 0.93965 | 64.8362 | 0.93961 | 64.8332 | -4.22e-05 | -0.00038779
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_BULL-SUMSH161 | EKPC_P1-2_BULL-SUMSH161 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_BULL-BLUE L161 | EKPC_P1-2_BULL-BLUE L161 | 0.93965 | 64.8362 | 0.93963 | 64.8341 | -2.9266e-05 | -0.00037485
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_BULL-BLUE L161 | EKPC_P1-2_BULL-BLUE L161 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_BULL-SHEL161 | EKPC_P1-2_BULL-SHEL161 | 0.93965 | 64.8362 | 0.93969 | 64.8384 | 3.314e-05 | -0.00031245
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_BULL-SHEL161 | EKPC_P1-2_BULL-SHEL161 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_POW-BTV-DEL161 | EKPC_P1-2_POW-BTV-DEL161 | 0.93965 | 64.8362 | 0.93962 | 64.8337 | -3.5286e-05 | -0.00038087
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_POW-BTV-DEL161 | EKPC_P1-2_POW-BTV-DEL161 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | TVA SS-GLASGOW & LAFAYETTE 161 | TVA SS-GLASGOW & LAFAYETTE 161 | 0.93965 | 64.8362 | 0.93967 | 64.8373 | 1.7166e-05 | -0.00032842
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | TVA SS-GLASGOW & LAFAYETTE 161 | TVA SS-GLASGOW & LAFAYETTE 161 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | EK-TVA SSHD & SSHD 161 XFMR | EK-TVA SSHD & SSHD 161 XFMR | 0.93965 | 64.8362 | 0.93966 | 64.8366 | 6.9737e-06 | -0.00033861
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EK-TVA SSHD & SSHD 161 XFMR | EK-TVA SSHD & SSHD 161 XFMR | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | EKPC_P1-2_AVON-NCLA345 | EKPC_P1-2_AVON-NCLA345 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 714 324010-324114(1) | OPEN LINE FROM BUS 324010 [7TRIMBL REAC345.00] TO BUS 324114 [7TRIMBLE CO 345.00] CKT 1 | 0.93965 | 64.8362 | 0.93947 | 64.8235 | -0.00018269 | -0.00052828
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 714 324010-324114(1) | OPEN LINE FROM BUS 324010 [7TRIMBL REAC345.00] TO BUS 324114 [7TRIMBLE CO 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 715 324021-324103(Z1) | OPEN LINE FROM BUS 324021 [7BLUEGRASS12345.00] TO BUS 324103 [7BUCKNER 345.00] CKT Z1 | 0.93965 | 64.8362 | 0.93964 | 64.8353 | -1.1921e-05 | -0.00035751
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 715 324021-324103(Z1) | OPEN LINE FROM BUS 324021 [7BLUEGRASS12345.00] TO BUS 324103 [7BUCKNER 345.00] CKT Z1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 716 324022-324103(Z1) | OPEN LINE FROM BUS 324022 [7BLUEGRASS 3345.00] TO BUS 324103 [7BUCKNER 345.00] CKT Z1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -2.9802e-07 | -0.00034589
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 716 324022-324103(Z1) | OPEN LINE FROM BUS 324022 [7BLUEGRASS 3345.00] TO BUS 324103 [7BUCKNER 345.00] CKT Z1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 717 324029-324030(1) | OPEN LINE FROM BUS 324029 [7TRIMBLE CTA345.00] TO BUS 324030 [7TRIMBLE CTB345.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 0 | -0.00034559
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 717 324029-324030(1) | OPEN LINE FROM BUS 324029 [7TRIMBLE CTA345.00] TO BUS 324030 [7TRIMBLE CTB345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 718 324029-324114(1) | OPEN LINE FROM BUS 324029 [7TRIMBLE CTA345.00] TO BUS 324114 [7TRIMBLE CO 345.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 0 | -0.00034559
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 718 324029-324114(1) | OPEN LINE FROM BUS 324029 [7TRIMBLE CTA345.00] TO BUS 324114 [7TRIMBLE CO 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 719 324030-324114(1) | OPEN LINE FROM BUS 324030 [7TRIMBLE CTB345.00] TO BUS 324114 [7TRIMBLE CO 345.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 0 | -0.00034559
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 719 324030-324114(1) | OPEN LINE FROM BUS 324030 [7TRIMBLE CTB345.00] TO BUS 324114 [7TRIMBLE CO 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 720 324047-325055(1) | OPEN LINE FROM BUS 324047 [4BLACKBRANCH138.00] TO BUS 325055 [4RHUDES TP 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93962 | 64.834 | -3.1471e-05 | -0.00037706
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 720 324047-325055(1) | OPEN LINE FROM BUS 324047 [4BLACKBRANCH138.00] TO BUS 325055 [4RHUDES TP 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 721 324048-324437(1) | OPEN LINE FROM BUS 324048 [2PARKWY MINE69.000] TO BUS 324437 [2BEVIER KU 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 5.9605e-08 | -0.00034553
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 721 324048-324437(1) | OPEN LINE FROM BUS 324048 [2PARKWY MINE69.000] TO BUS 324437 [2BEVIER KU 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 722 324048-324584(1) | OPEN LINE FROM BUS 324048 [2PARKWY MINE69.000] TO BUS 324584 [2INDIAN HILL69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 1.1921e-07 | -0.00034547
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 722 324048-324584(1) | OPEN LINE FROM BUS 324048 [2PARKWY MINE69.000] TO BUS 324584 [2INDIAN HILL69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 723 324049-324572(1) | OPEN LINE FROM BUS 324049 [2OXFORD COAL69.000] TO BUS 324572 [2HILLSIDE 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 1.1921e-07 | -0.00034547
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 723 324049-324572(1) | OPEN LINE FROM BUS 324049 [2OXFORD COAL69.000] TO BUS 324572 [2HILLSIDE 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 724 324049-324745(1) | OPEN LINE FROM BUS 324049 [2OXFORD COAL69.000] TO BUS 324745 [2STRINGTOWN 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 1.1921e-07 | -0.00034547
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 724 324049-324745(1) | OPEN LINE FROM BUS 324049 [2OXFORD COAL69.000] TO BUS 324745 [2STRINGTOWN 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 725 324050-324362(1) | OPEN LINE FROM BUS 324050 [2JONESVILLE 69.000] TO BUS 324362 [2RIO 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 5.3644e-07 | -0.00034505
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 725 324050-324362(1) | OPEN LINE FROM BUS 324050 [2JONESVILLE 69.000] TO BUS 324362 [2RIO 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 726 324050-324447(1) | OPEN LINE FROM BUS 324050 [2JONESVILLE 69.000] TO BUS 324447 [2BONNIE KU 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.1325e-06 | -0.00034672
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 726 324050-324447(1) | OPEN LINE FROM BUS 324050 [2JONESVILLE 69.000] TO BUS 324447 [2BONNIE KU 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 727 324051-324173(1) | OPEN LINE FROM BUS 324051 [4MATANZAS 138.00] TO BUS 324173 [5MATANZAS 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -6.5565e-07 | -0.00034624
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 727 324051-324173(1) | OPEN LINE FROM BUS 324051 [4MATANZAS 138.00] TO BUS 324173 [5MATANZAS 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 728 324051-324173(2) | OPEN LINE FROM BUS 324051 [4MATANZAS 138.00] TO BUS 324173 [5MATANZAS 161.00] CKT 2 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -5.9605e-07 | -0.00034618
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 728 324051-324173(2) | OPEN LINE FROM BUS 324051 [4MATANZAS 138.00] TO BUS 324173 [5MATANZAS 161.00] CKT 2 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 729 324051-324255(1) | OPEN LINE FROM BUS 324051 [4MATANZAS 138.00] TO BUS 324255 [4GREEN RIVER138.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.7881e-07 | -0.00034577
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 729 324051-324255(1) | OPEN LINE FROM BUS 324051 [4MATANZAS 138.00] TO BUS 324255 [4GREEN RIVER138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 730 324051-324291(1) | OPEN LINE FROM BUS 324051 [4MATANZAS 138.00] TO BUS 324291 [4OHIO COUNTY138.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -1.7881e-06 | -0.00034738
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 730 324051-324291(1) | OPEN LINE FROM BUS 324051 [4MATANZAS 138.00] TO BUS 324291 [4OHIO COUNTY138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 731 324058-324059(1) | OPEN LINE FROM BUS 324058 [2BEAVER DAM 69.000] TO BUS 324059 [2BEAVER DM N69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 3.9935e-06 | -0.00034159
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 731 324058-324059(1) | OPEN LINE FROM BUS 324058 [2BEAVER DAM 69.000] TO BUS 324059 [2BEAVER DM N69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 732 324058-324667(1) | OPEN LINE FROM BUS 324058 [2BEAVER DAM 69.000] TO BUS 324667 [2OHIO COUNTY69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8367 | 7.7486e-06 | -0.00033784
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 732 324058-324667(1) | OPEN LINE FROM BUS 324058 [2BEAVER DAM 69.000] TO BUS 324667 [2OHIO COUNTY69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 733 324059-324080(1) | OPEN LINE FROM BUS 324059 [2BEAVER DM N69.000] TO BUS 324080 [2HARTFORD 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 2.2054e-06 | -0.00034338
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 733 324059-324080(1) | OPEN LINE FROM BUS 324059 [2BEAVER DM N69.000] TO BUS 324080 [2HARTFORD 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 734 324061-324079(1) | OPEN LINE FROM BUS 324061 [2BORG-WARNER69.000] TO BUS 324079 [2HANSON 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 4.2319e-06 | -0.00034136
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 734 324061-324079(1) | OPEN LINE FROM BUS 324061 [2BORG-WARNER69.000] TO BUS 324079 [2HANSON 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 735 324061-324873(1) | OPEN LINE FROM BUS 324061 [2BORG-WARNER69.000] TO BUS 324873 [2HANSON JCT 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8368 | 9.5367e-06 | -0.00033605
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 735 324061-324873(1) | OPEN LINE FROM BUS 324061 [2BORG-WARNER69.000] TO BUS 324873 [2HANSON JCT 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 736 324065-324843(1) | OPEN LINE FROM BUS 324065 [2DAWSON 764 69.000] TO BUS 324843 [2DAWSON IND 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 1.5497e-06 | -0.00034404
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 736 324065-324843(1) | OPEN LINE FROM BUS 324065 [2DAWSON 764 69.000] TO BUS 324843 [2DAWSON IND 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 737 324067-324512(1) | OPEN LINE FROM BUS 324067 [2EDDYV PRIS 69.000] TO BUS 324512 [2EDDYV PR TP69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 1.7881e-06 | -0.0003438
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 737 324067-324512(1) | OPEN LINE FROM BUS 324067 [2EDDYV PRIS 69.000] TO BUS 324512 [2EDDYV PR TP69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 738 324068-324349(1) | OPEN LINE FROM BUS 324068 [2E CAMPBELVL69.000] TO BUS 324349 [2CAMPBELVIL269.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -5.9605e-07 | -0.00034618
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 738 324068-324349(1) | OPEN LINE FROM BUS 324068 [2E CAMPBELVL69.000] TO BUS 324349 [2CAMPBELVIL269.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 739 324069-324687(1) | OPEN LINE FROM BUS 324069 [2PAYNES ML 69.000] TO BUS 324687 [2PISGAH 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 8.9407e-07 | -0.00034469
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 739 324069-324687(1) | OPEN LINE FROM BUS 324069 [2PAYNES ML 69.000] TO BUS 324687 [2PISGAH 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 740 324069-324763(1) | OPEN LINE FROM BUS 324069 [2PAYNES ML 69.000] TO BUS 324763 [2VERSAILLES 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8355 | -9.954e-06 | -0.00035554
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 740 324069-324763(1) | OPEN LINE FROM BUS 324069 [2PAYNES ML 69.000] TO BUS 324763 [2VERSAILLES 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 741 324075-324702(1) | OPEN LINE FROM BUS 324075 [2GRAHAM 69.000] TO BUS 324702 [2RIVER QUEEN69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 1.2517e-06 | -0.00034434
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 741 324075-324702(1) | OPEN LINE FROM BUS 324075 [2GRAHAM 69.000] TO BUS 324702 [2RIVER QUEEN69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 742 324077-326594(1) | OPEN LINE FROM BUS 324077 [2GREENVILE W69.000] TO BUS 326594 [2GREENVL 12 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 5.9605e-07 | -0.00034499
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 742 324077-326594(1) | OPEN LINE FROM BUS 324077 [2GREENVILE W69.000] TO BUS 326594 [2GREENVL 12 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 743 324081-326587(1) | OPEN LINE FROM BUS 324081 [2MADSNV GE 69.000] TO BUS 326587 [2MADSNV W TP69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 2.3842e-06 | -0.0003432
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 744 324082-324197(1) | OPEN LINE FROM BUS 324082 [2PARIS 4 69.000] TO BUS 324197 [2DETROIT HAR69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 745 324082-324476(1) | OPEN LINE FROM BUS 324082 [2PARIS 4 69.000] TO BUS 324476 [2CMC TAP 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 746 324082-325061(1) | OPEN LINE FROM BUS 324082 [2PARIS 4 69.000] TO BUS 325061 [2CMC 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 747 324083-326587(1) | OPEN LINE FROM BUS 324083 [2MADSNV W 69.000] TO BUS 326587 [2MADSNV W TP69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8368 | 9.2387e-06 | -0.00033635
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 747 324083-326587(1) | OPEN LINE FROM BUS 324083 [2MADSNV W 69.000] TO BUS 326587 [2MADSNV W TP69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 748 324085-324629(1) | OPEN LINE FROM BUS 324085 [2MARION 4 69.000] TO BUS 324629 [2MARION KU 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 1.6093e-06 | -0.00034398
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 748 324085-324629(1) | OPEN LINE FROM BUS 324085 [2MARION 4 69.000] TO BUS 324629 [2MARION KU 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 749 324086-324096(1) | OPEN LINE FROM BUS 324086 [2MORGANF IND69.000] TO BUS 324096 [2PEA WSH TAP69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 0 | -0.00034559
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 749 324086-324096(1) | OPEN LINE FROM BUS 324086 [2MORGANF IND69.000] TO BUS 324096 [2PEA WSH TAP69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 750 324086-324671(1) | OPEN LINE FROM BUS 324086 [2MORGANF IND69.000] TO BUS 324671 [2OVERLAD S T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 2.0862e-06 | -0.0003435
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 750 324086-324671(1) | OPEN LINE FROM BUS 324086 [2MORGANF IND69.000] TO BUS 324671 [2OVERLAD S T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 751 324087-324913(1) | OPEN LINE FROM BUS 324087 [2MT VERN SO 69.000] TO BUS 324913 [2MT VERNON 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93955 | 64.8291 | -0.00010175 | -0.00044733
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 751 324087-324913(1) | OPEN LINE FROM BUS 324087 [2MT VERN SO 69.000] TO BUS 324913 [2MT VERNON 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 752 324087-324927(1) | OPEN LINE FROM BUS 324087 [2MT VERN SO 69.000] TO BUS 324927 [2PINE HILL T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93957 | 64.8304 | -8.3923e-05 | -0.00042951
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 752 324087-324927(1) | OPEN LINE FROM BUS 324087 [2MT VERN SO 69.000] TO BUS 324927 [2PINE HILL T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 753 324090-324095(1) | OPEN LINE FROM BUS 324090 [2OVERLAND NO69.000] TO BUS 324095 [2UNIONTOWN 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 0 | -0.00034559
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 753 324090-324095(1) | OPEN LINE FROM BUS 324090 [2OVERLAND NO69.000] TO BUS 324095 [2UNIONTOWN 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 754 324091-324096(1) | OPEN LINE FROM BUS 324091 [2OVERLAND SO69.000] TO BUS 324096 [2PEA WSH TAP69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 5.9605e-08 | -0.00034553
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 754 324091-324096(1) | OPEN LINE FROM BUS 324091 [2OVERLAND SO69.000] TO BUS 324096 [2PEA WSH TAP69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 755 324092-324702(1) | OPEN LINE FROM BUS 324092 [2PEABODY RVR69.000] TO BUS 324702 [2RIVER QUEEN69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 5.9605e-08 | -0.00034553
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 755 324092-324702(1) | OPEN LINE FROM BUS 324092 [2PEABODY RVR69.000] TO BUS 324702 [2RIVER QUEEN69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 756 324093-324711(1) | OPEN LINE FROM BUS 324093 [2SPEN CHEMIC69.000] TO BUS 324711 [2SPEN CHEM T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 2.3842e-06 | -0.0003432
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 756 324093-324711(1) | OPEN LINE FROM BUS 324093 [2SPEN CHEMIC69.000] TO BUS 324711 [2SPEN CHEM T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 757 324094-324562(1) | OPEN LINE FROM BUS 324094 [2TURTLE CK T69.000] TO BUS 324562 [2HARLAN KU 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 2.3842e-07 | -0.00034535
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 757 324094-324562(1) | OPEN LINE FROM BUS 324094 [2TURTLE CK T69.000] TO BUS 324562 [2HARLAN KU 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 758 324094-324761(1) | OPEN LINE FROM BUS 324094 [2TURTLE CK T69.000] TO BUS 324761 [2VERDA 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 5.9605e-07 | -0.00034499
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 758 324094-324761(1) | OPEN LINE FROM BUS 324094 [2TURTLE CK T69.000] TO BUS 324761 [2VERDA 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 759 324094-325045(1) | OPEN LINE FROM BUS 324094 [2TURTLE CK T69.000] TO BUS 325045 [2TURTLE CRK 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8368 | 9.4771e-06 | -0.00033611
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 759 324094-325045(1) | OPEN LINE FROM BUS 324094 [2TURTLE CK T69.000] TO BUS 325045 [2TURTLE CRK 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 760 324095-326572(1) | OPEN LINE FROM BUS 324095 [2UNIONTOWN 69.000] TO BUS 326572 [2RIVRVW COAL69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 1.0133e-06 | -0.00034457
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 760 324095-326572(1) | OPEN LINE FROM BUS 324095 [2UNIONTOWN 69.000] TO BUS 326572 [2RIVRVW COAL69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 761 324096-324097(1) | OPEN LINE FROM BUS 324096 [2PEA WSH TAP69.000] TO BUS 324097 [2PEAB WASH 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 0 | -0.00034559
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 761 324096-324097(1) | OPEN LINE FROM BUS 324096 [2PEA WSH TAP69.000] TO BUS 324097 [2PEAB WASH 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 762 324098-324779(1) | OPEN LINE FROM BUS 324098 [2WEST VACO 69.000] TO BUS 324779 [2WICKLIFFE 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93968 | 64.8378 | 2.408e-05 | -0.00032151
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 762 324098-324779(1) | OPEN LINE FROM BUS 324098 [2WEST VACO 69.000] TO BUS 324779 [2WICKLIFFE 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 763 324100-324102(1) | OPEN LINE FROM BUS 324100 [7ALCALDE 345.00] TO BUS 324102 [7BROWN NORTH345.00] CKT 1 | 0.93965 | 64.8362 | 0.93933 | 64.8139 | -0.00032288 | -0.00066847
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 763 324100-324102(1) | OPEN LINE FROM BUS 324100 [7ALCALDE 345.00] TO BUS 324102 [7BROWN NORTH345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 764 324100-324112(1) | OPEN LINE FROM BUS 324100 [7ALCALDE 345.00] TO BUS 324112 [7PINEVILLE 345.00] CKT 1 | 0.93965 | 64.8362 | 0.93954 | 64.8282 | -0.00011563 | -0.00046122
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 764 324100-324112(1) | OPEN LINE FROM BUS 324100 [7ALCALDE 345.00] TO BUS 324112 [7PINEVILLE 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 765 324100-324130(1) | OPEN LINE FROM BUS 324100 [7ALCALDE 345.00] TO BUS 324130 [5ALCALDE 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93976 | 64.8437 | 0.00010991 | -0.00023568
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 765 324100-324130(1) | OPEN LINE FROM BUS 324100 [7ALCALDE 345.00] TO BUS 324130 [5ALCALDE 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 766 324101-324107(1) | OPEN LINE FROM BUS 324101 [7BLUE LICK 345.00] TO BUS 324107 [7MIDDLETOWN 345.00] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8355 | -9.5963e-06 | -0.00035518
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 766 324101-324107(1) | OPEN LINE FROM BUS 324101 [7BLUE LICK 345.00] TO BUS 324107 [7MIDDLETOWN 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 767 324101-324108(1) | OPEN LINE FROM BUS 324101 [7BLUE LICK 345.00] TO BUS 324108 [7MILL CREEK 345.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8358 | -5.1856e-06 | -0.00035077
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 767 324101-324108(1) | OPEN LINE FROM BUS 324101 [7BLUE LICK 345.00] TO BUS 324108 [7MILL CREEK 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
324915 | 2MT WAS EK J | 69 | LGEE' | RANGE | 0.94 | 1.06 | SINGLE OPN LIN 767 324101-324108(1) | OPEN LINE FROM BUS 324101 [7BLUE LICK 345.00] TO BUS 324108 [7MILL CREEK 345.00] CKT 1 | 0.94997 | 65.5482 | 0.93638 | 64.6103 | -0.013594 | -0.0036194
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 768 324101-324134(1) | OPEN LINE FROM BUS 324101 [7BLUE LICK 345.00] TO BUS 324134 [5BLUE LICK 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93969 | 64.8384 | 3.1829e-05 | -0.00031376
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 768 324101-324134(1) | OPEN LINE FROM BUS 324101 [7BLUE LICK 345.00] TO BUS 324134 [5BLUE LICK 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 769 324101-324212(1) | OPEN LINE FROM BUS 324101 [7BLUE LICK 345.00] TO BUS 324212 [4BLUE LICK 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.835 | -1.651e-05 | -0.0003621
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 769 324101-324212(1) | OPEN LINE FROM BUS 324101 [7BLUE LICK 345.00] TO BUS 324212 [4BLUE LICK 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
324915 | 2MT WAS EK J | 69 | LGEE' | RANGE | 0.94 | 1.06 | SINGLE OPN LIN 769 324101-324212(1) | OPEN LINE FROM BUS 324101 [7BLUE LICK 345.00] TO BUS 324212 [4BLUE LICK 138.00] CKT 1 | 0.94997 | 65.5482 | 0.91927 | 63.4298 | -0.030702 | -0.020727
325006 | 2W MT WSH EK | 69 | LGEE' | RANGE | 0.94 | 1.06 | SINGLE OPN LIN 769 324101-324212(1) | OPEN LINE FROM BUS 324101 [7BLUE LICK 345.00] TO BUS 324212 [4BLUE LICK 138.00] CKT 1 | 0.95952 | 66.2066 | 0.92914 | 64.1108 | -0.030375 | -0.010858
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 770 324102-324106(1) | OPEN LINE FROM BUS 324102 [7BROWN NORTH345.00] TO BUS 324106 [7HARDIN CO 345.00] CKT 1 | 0.93965 | 64.8362 | 0.93949 | 64.8251 | -0.00015968 | -0.00050527
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 770 324102-324106(1) | OPEN LINE FROM BUS 324102 [7BROWN NORTH345.00] TO BUS 324106 [7HARDIN CO 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 771 324102-324116(1) | OPEN LINE FROM BUS 324102 [7BROWN NORTH345.00] TO BUS 324116 [7W LEXINGTON345.00] CKT 1 | 0.93965 | 64.8362 | 0.93943 | 64.8206 | -0.00022513 | -0.00057071
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 771 324102-324116(1) | OPEN LINE FROM BUS 324102 [7BROWN NORTH345.00] TO BUS 324116 [7W LEXINGTON345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 772 324102-325074(1) | OPEN LINE FROM BUS 324102 [7BROWN NORTH345.00] TO BUS 325074 [7W GARRARDKU345.00] CKT 1 | 0.93965 | 64.8362 | 0.93987 | 64.8513 | 0.00021958 | -0.000126
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 772 324102-325074(1) | OPEN LINE FROM BUS 324102 [7BROWN NORTH345.00] TO BUS 325074 [7W GARRARDKU345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 773 324102-325956(1) | OPEN LINE FROM BUS 324102 [7BROWN NORTH345.00] TO BUS 325956 [4BROWN N 2 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8352 | -1.3113e-05 | -0.0003587
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 773 324102-325956(1) | OPEN LINE FROM BUS 324102 [7BROWN NORTH345.00] TO BUS 325956 [4BROWN N 2 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 774 324102-325957(2) | OPEN LINE FROM BUS 324102 [7BROWN NORTH345.00] TO BUS 325957 [4BROWN N 1 138.00] CKT 2 | 0.93965 | 64.8362 | 0.93964 | 64.8354 | -1.055e-05 | -0.00035614
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 774 324102-325957(2) | OPEN LINE FROM BUS 324102 [7BROWN NORTH345.00] TO BUS 325957 [4BROWN N 1 138.00] CKT 2 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 775 324103-324107(1) | OPEN LINE FROM BUS 324103 [7BUCKNER 345.00] TO BUS 324107 [7MIDDLETOWN 345.00] CKT 1 | 0.93965 | 64.8362 | 0.93959 | 64.832 | -6.0678e-05 | -0.00040627
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 775 324103-324107(1) | OPEN LINE FROM BUS 324103 [7BUCKNER 345.00] TO BUS 324107 [7MIDDLETOWN 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
324915 | 2MT WAS EK J | 69 | LGEE' | RANGE | 0.94 | 1.06 | SINGLE OPN LIN 775 324103-324107(1) | OPEN LINE FROM BUS 324103 [7BUCKNER 345.00] TO BUS 324107 [7MIDDLETOWN 345.00] CKT 1 | 0.94997 | 65.5482 | 0.93958 | 64.8307 | -0.010399 | -0.00042462
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 776 324103-324114(1) | OPEN LINE FROM BUS 324103 [7BUCKNER 345.00] TO BUS 324114 [7TRIMBLE CO 345.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -1.9073e-06 | -0.0003475
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 776 324103-324114(1) | OPEN LINE FROM BUS 324103 [7BUCKNER 345.00] TO BUS 324114 [7TRIMBLE CO 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 777 324104-324106(1) | OPEN LINE FROM BUS 324104 [7DAVIESS 345.00] TO BUS 324106 [7HARDIN CO 345.00] CKT 1 | 0.93965 | 64.8362 | 0.93976 | 64.8435 | 0.00010651 | -0.00023907
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 777 324104-324106(1) | OPEN LINE FROM BUS 324104 [7DAVIESS 345.00] TO BUS 324106 [7HARDIN CO 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 778 324105-324115(1) | OPEN LINE FROM BUS 324105 [7GHENT 345.00] TO BUS 324115 [7W FRANKFORT345.00] CKT 1 | 0.93965 | 64.8362 | 0.9388 | 64.7772 | -0.00085473 | -0.0012003
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 778 324105-324115(1) | OPEN LINE FROM BUS 324105 [7GHENT 345.00] TO BUS 324115 [7W FRANKFORT345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 779 324105-324116(1) | OPEN LINE FROM BUS 324105 [7GHENT 345.00] TO BUS 324116 [7W LEXINGTON345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 780 324105-324253(1) | OPEN LINE FROM BUS 324105 [7GHENT 345.00] TO BUS 324253 [4GHENT 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93951 | 64.8259 | -0.00014836 | -0.00049394
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 780 324105-324253(1) | OPEN LINE FROM BUS 324105 [7GHENT 345.00] TO BUS 324253 [4GHENT 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 781 324105-324253(2) | OPEN LINE FROM BUS 324105 [7GHENT 345.00] TO BUS 324253 [4GHENT 138.00] CKT 2 | 0.93965 | 64.8362 | 0.93947 | 64.8236 | -0.00018126 | -0.00052685
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 781 324105-324253(2) | OPEN LINE FROM BUS 324105 [7GHENT 345.00] TO BUS 324253 [4GHENT 138.00] CKT 2 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 782 324105-326536(1) | OPEN LINE FROM BUS 324105 [7GHENT 345.00] TO BUS 326536 [7GALLATIN 345.00] CKT 1 | 0.93965 | 64.8362 | 0.93854 | 64.759 | -0.0011187 | -0.0014643
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 782 324105-326536(1) | OPEN LINE FROM BUS 324105 [7GHENT 345.00] TO BUS 326536 [7GALLATIN 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 783 324106-324261(1) | OPEN LINE FROM BUS 324106 [7HARDIN CO 345.00] TO BUS 324261 [4HARDIN CO 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8355 | -9.3579e-06 | -0.00035495
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 783 324106-324261(1) | OPEN LINE FROM BUS 324106 [7HARDIN CO 345.00] TO BUS 324261 [4HARDIN CO 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 784 324106-324261(2) | OPEN LINE FROM BUS 324106 [7HARDIN CO 345.00] TO BUS 324261 [4HARDIN CO 138.00] CKT 2 | 0.93965 | 64.8362 | 0.93965 | 64.8356 | -7.7486e-06 | -0.00035334
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 784 324106-324261(2) | OPEN LINE FROM BUS 324106 [7HARDIN CO 345.00] TO BUS 324261 [4HARDIN CO 138.00] CKT 2 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 785 324106-325073(1) | OPEN LINE FROM BUS 324106 [7HARDIN CO 345.00] TO BUS 325073 [7REDMON RD 345.00] CKT 1 | 0.93965 | 64.8362 | 0.93952 | 64.8271 | -0.00013107 | -0.00047666
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 785 324106-325073(1) | OPEN LINE FROM BUS 324106 [7HARDIN CO 345.00] TO BUS 325073 [7REDMON RD 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 786 324107-324108(1) | OPEN LINE FROM BUS 324107 [7MIDDLETOWN 345.00] TO BUS 324108 [7MILL CREEK 345.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 3.5763e-07 | -0.00034523
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 786 324107-324108(1) | OPEN LINE FROM BUS 324107 [7MIDDLETOWN 345.00] TO BUS 324108 [7MILL CREEK 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 787 324107-324114(1) | OPEN LINE FROM BUS 324107 [7MIDDLETOWN 345.00] TO BUS 324114 [7TRIMBLE CO 345.00] CKT 1 | 0.93965 | 64.8362 | 0.93962 | 64.8335 | -3.8326e-05 | -0.00038391
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 787 324107-324114(1) | OPEN LINE FROM BUS 324107 [7MIDDLETOWN 345.00] TO BUS 324114 [7TRIMBLE CO 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 788 324107-324281(3) | OPEN LINE FROM BUS 324107 [7MIDDLETOWN 345.00] TO BUS 324281 [4MIDDLETOWN 138.00] CKT 3 | 0.93965 | 64.8362 | 0.93965 | 64.8356 | -8.7023e-06 | -0.00035429
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 788 324107-324281(3) | OPEN LINE FROM BUS 324107 [7MIDDLETOWN 345.00] TO BUS 324281 [4MIDDLETOWN 138.00] CKT 3 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 789 324107-324281(4) | OPEN LINE FROM BUS 324107 [7MIDDLETOWN 345.00] TO BUS 324281 [4MIDDLETOWN 138.00] CKT 4 | 0.93965 | 64.8362 | 0.93965 | 64.8356 | -7.987e-06 | -0.00035357
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 789 324107-324281(4) | OPEN LINE FROM BUS 324107 [7MIDDLETOWN 345.00] TO BUS 324281 [4MIDDLETOWN 138.00] CKT 4 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 790 324107-324281(5) | OPEN LINE FROM BUS 324107 [7MIDDLETOWN 345.00] TO BUS 324281 [4MIDDLETOWN 138.00] CKT 5 | 0.93965 | 64.8362 | 0.93965 | 64.8356 | -8.7023e-06 | -0.00035429
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 790 324107-324281(5) | OPEN LINE FROM BUS 324107 [7MIDDLETOWN 345.00] TO BUS 324281 [4MIDDLETOWN 138.00] CKT 5 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 791 324107-324281(7) | OPEN LINE FROM BUS 324107 [7MIDDLETOWN 345.00] TO BUS 324281 [4MIDDLETOWN 138.00] CKT 7 | 0.93965 | 64.8362 | 0.93965 | 64.8356 | -7.8678e-06 | -0.00035346
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 791 324107-324281(7) | OPEN LINE FROM BUS 324107 [7MIDDLETOWN 345.00] TO BUS 324281 [4MIDDLETOWN 138.00] CKT 7 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 792 324108-325073(1) | OPEN LINE FROM BUS 324108 [7MILL CREEK 345.00] TO BUS 325073 [7REDMON RD 345.00] CKT 1 | 0.93965 | 64.8362 | 0.93944 | 64.8215 | -0.00021249 | -0.00055808
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 792 324108-325073(1) | OPEN LINE FROM BUS 324108 [7MILL CREEK 345.00] TO BUS 325073 [7REDMON RD 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 793 324108-326001(1) | OPEN LINE FROM BUS 324108 [7MILL CREEK 345.00] TO BUS 326001 [7CANE RUN TP345.00] CKT 1 | 0.93965 | 64.8362 | 0.93962 | 64.8338 | -3.4094e-05 | -0.00037968
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 793 324108-326001(1) | OPEN LINE FROM BUS 324108 [7MILL CREEK 345.00] TO BUS 326001 [7CANE RUN TP345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 794 324109-324565(1) | OPEN LINE FROM BUS 324109 [7NAS 345.00] TO BUS 324565 [7NAS TAP 345.00] CKT 1 | 0.93965 | 64.8362 | 0.93944 | 64.8213 | -0.00021577 | -0.00056136
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 794 324109-324565(1) | OPEN LINE FROM BUS 324109 [7NAS 345.00] TO BUS 324565 [7NAS TAP 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 795 324110-324289(1) | OPEN LINE FROM BUS 324110 [7NORTHSIDE 345.00] TO BUS 324289 [4NORTHSIDE 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8366 | 6.8545e-06 | -0.00033873
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 795 324110-324289(1) | OPEN LINE FROM BUS 324110 [7NORTHSIDE 345.00] TO BUS 324289 [4NORTHSIDE 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 796 324110-326569(1) | OPEN LINE FROM BUS 324110 [7NORTHSIDE 345.00] TO BUS 326569 [7KENZIG ROAD345.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 2.9802e-06 | -0.00034261
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 796 324110-326569(1) | OPEN LINE FROM BUS 324110 [7NORTHSIDE 345.00] TO BUS 326569 [7KENZIG ROAD345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 797 324111-324294(1) | OPEN LINE FROM BUS 324111 [7PADDYS WEST345.00] TO BUS 324294 [4PADDYS WEST138.00] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8353 | -1.2517e-05 | -0.0003581
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 797 324111-324294(1) | OPEN LINE FROM BUS 324111 [7PADDYS WEST345.00] TO BUS 324294 [4PADDYS WEST138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 798 324111-326001(1) | OPEN LINE FROM BUS 324111 [7PADDYS WEST345.00] TO BUS 326001 [7CANE RUN TP345.00] CKT 1 | 0.93965 | 64.8362 | 0.93963 | 64.8342 | -2.8312e-05 | -0.0003739
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 798 324111-326001(1) | OPEN LINE FROM BUS 324111 [7PADDYS WEST345.00] TO BUS 326001 [7CANE RUN TP345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 799 324111-326569(1) | OPEN LINE FROM BUS 324111 [7PADDYS WEST345.00] TO BUS 326569 [7KENZIG ROAD345.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8356 | -8.5831e-06 | -0.00035417
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 799 324111-326569(1) | OPEN LINE FROM BUS 324111 [7PADDYS WEST345.00] TO BUS 326569 [7KENZIG ROAD345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 800 324112-324167(1) | OPEN LINE FROM BUS 324112 [7PINEVILLE 345.00] TO BUS 324167 [5PINEVILLE 2161.00] CKT 1 | 0.93965 | 64.8362 | 0.93941 | 64.819 | -0.00024915 | -0.00059474
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 800 324112-324167(1) | OPEN LINE FROM BUS 324112 [7PINEVILLE 345.00] TO BUS 324167 [5PINEVILLE 2161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 801 324112-325074(1) | OPEN LINE FROM BUS 324112 [7PINEVILLE 345.00] TO BUS 325074 [7W GARRARDKU345.00] CKT 1 | 0.93965 | 64.8362 | 0.93937 | 64.8162 | -0.0002889 | -0.00063449
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 801 324112-325074(1) | OPEN LINE FROM BUS 324112 [7PINEVILLE 345.00] TO BUS 325074 [7W GARRARDKU345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 802 324114-324314(5) | OPEN LINE FROM BUS 324114 [7TRIMBLE CO 345.00] TO BUS 324314 [4TRIMBLE CO 138.00] CKT 5 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -9.5367e-07 | -0.00034654
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 802 324114-324314(5) | OPEN LINE FROM BUS 324114 [7TRIMBLE CO 345.00] TO BUS 324314 [4TRIMBLE CO 138.00] CKT 5 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 803 324114-324314(6) | OPEN LINE FROM BUS 324114 [7TRIMBLE CO 345.00] TO BUS 324314 [4TRIMBLE CO 138.00] CKT 6 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -7.1526e-07 | -0.0003463
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 803 324114-324314(6) | OPEN LINE FROM BUS 324114 [7TRIMBLE CO 345.00] TO BUS 324314 [4TRIMBLE CO 138.00] CKT 6 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 804 324115-324319(1) | OPEN LINE FROM BUS 324115 [7W FRANKFORT345.00] TO BUS 324319 [4W FRANKFORT138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 805 324116-324320(1) | OPEN LINE FROM BUS 324116 [7W LEXINGTON345.00] TO BUS 324320 [4W LEXINGTON138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 806 324124-326564(1) | OPEN LINE FROM BUS 324124 [2CENTRTOWN S69.000] TO BUS 326564 [2LEW BREC 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 2.3842e-07 | -0.00034535
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 806 324124-326564(1) | OPEN LINE FROM BUS 324124 [2CENTRTOWN S69.000] TO BUS 326564 [2LEW BREC 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 807 324130-324141(1) | OPEN LINE FROM BUS 324130 [5ALCALDE 161.00] TO BUS 324141 [5ELIHU 161.00] CKT 1 | 0.93965 | 64.8362 | 0.9397 | 64.8391 | 4.2737e-05 | -0.00030285
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 807 324130-324141(1) | OPEN LINE FROM BUS 324130 [5ALCALDE 161.00] TO BUS 324141 [5ELIHU 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 808 324130-324143(1) | OPEN LINE FROM BUS 324130 [5ALCALDE 161.00] TO BUS 324143 [5FARLEY 161.00] CKT 1 | 0.93965 | 64.8362 | 0.9396 | 64.8322 | -5.7399e-05 | -0.00040299
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 808 324130-324143(1) | OPEN LINE FROM BUS 324130 [5ALCALDE 161.00] TO BUS 324143 [5FARLEY 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 809 324131-324139(1) | OPEN LINE FROM BUS 324131 [5ARNOLD 161.00] TO BUS 324139 [5DORCHESTER 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8354 | -1.0371e-05 | -0.00035596
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 809 324131-324139(1) | OPEN LINE FROM BUS 324131 [5ARNOLD 161.00] TO BUS 324139 [5DORCHESTER 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 810 324131-324146(1) | OPEN LINE FROM BUS 324131 [5ARNOLD 161.00] TO BUS 324146 [5HARLAN WYE 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93962 | 64.8338 | -3.4273e-05 | -0.00037986
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 810 324131-324146(1) | OPEN LINE FROM BUS 324131 [5ARNOLD 161.00] TO BUS 324146 [5HARLAN WYE 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 811 324131-324148(1) | OPEN LINE FROM BUS 324131 [5ARNOLD 161.00] TO BUS 324148 [5WOOTON TAP 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93958 | 64.8309 | -7.5877e-05 | -0.00042146
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 811 324131-324148(1) | OPEN LINE FROM BUS 324131 [5ARNOLD 161.00] TO BUS 324148 [5WOOTON TAP 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 812 324131-324416(1) | OPEN LINE FROM BUS 324131 [5ARNOLD 161.00] TO BUS 324416 [2ARNOLD 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.3113e-06 | -0.0003469
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 812 324131-324416(1) | OPEN LINE FROM BUS 324131 [5ARNOLD 161.00] TO BUS 324416 [2ARNOLD 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 813 324132-324133(1) | OPEN LINE FROM BUS 324132 [5ARTEMUS TAP161.00] TO BUS 324133 [5ARTEMUS 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93963 | 64.8347 | -2.11e-05 | -0.00036669
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 813 324132-324133(1) | OPEN LINE FROM BUS 324132 [5ARTEMUS TAP161.00] TO BUS 324133 [5ARTEMUS 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 814 324132-324143(1) | OPEN LINE FROM BUS 324132 [5ARTEMUS TAP161.00] TO BUS 324143 [5FARLEY 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93963 | 64.8343 | -2.7061e-05 | -0.00037265
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 814 324132-324143(1) | OPEN LINE FROM BUS 324132 [5ARTEMUS TAP161.00] TO BUS 324143 [5FARLEY 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 815 324132-324156(1) | OPEN LINE FROM BUS 324132 [5ARTEMUS TAP161.00] TO BUS 324156 [5PINEVILE SW161.00] CKT 1 | 0.93965 | 64.8362 | 0.9396 | 64.8327 | -5.0068e-05 | -0.00039566
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 815 324132-324156(1) | OPEN LINE FROM BUS 324132 [5ARTEMUS TAP161.00] TO BUS 324156 [5PINEVILE SW161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 816 324133-324417(1) | OPEN LINE FROM BUS 324133 [5ARTEMUS 161.00] TO BUS 324417 [2ARTEMUS 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93963 | 64.8348 | -2.0206e-05 | -0.00036579
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 816 324133-324417(1) | OPEN LINE FROM BUS 324133 [5ARTEMUS 161.00] TO BUS 324417 [2ARTEMUS 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 817 324134-326975(1) | OPEN LINE FROM BUS 324134 [5BLUE LICK 161.00] TO BUS 326975 [5CEDAR GRV 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93968 | 64.8383 | 3.0518e-05 | -0.00031507
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 817 324134-326975(1) | OPEN LINE FROM BUS 324134 [5BLUE LICK 161.00] TO BUS 326975 [5CEDAR GRV 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 818 324135-324136(1) | OPEN LINE FROM BUS 324135 [5CORYDON TAP161.00] TO BUS 324136 [5CORYDON 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 1.1325e-06 | -0.00034446
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 818 324135-324136(1) | OPEN LINE FROM BUS 324135 [5CORYDON TAP161.00] TO BUS 324136 [5CORYDON 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 819 324135-324144(1) | OPEN LINE FROM BUS 324135 [5CORYDON TAP161.00] TO BUS 324144 [5GREEN RIVER161.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -8.9407e-07 | -0.00034648
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 819 324135-324144(1) | OPEN LINE FROM BUS 324135 [5CORYDON TAP161.00] TO BUS 324144 [5GREEN RIVER161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 820 324135-324153(1) | OPEN LINE FROM BUS 324135 [5CORYDON TAP161.00] TO BUS 324153 [5MORGANFIELD161.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 4.1127e-06 | -0.00034148
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 820 324135-324153(1) | OPEN LINE FROM BUS 324135 [5CORYDON TAP161.00] TO BUS 324153 [5MORGANFIELD161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 821 324136-324484(1) | OPEN LINE FROM BUS 324136 [5CORYDON 161.00] TO BUS 324484 [2CORYDON 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 1.0729e-06 | -0.00034451
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 821 324136-324484(1) | OPEN LINE FROM BUS 324136 [5CORYDON 161.00] TO BUS 324484 [2CORYDON 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 822 324137-324151(1) | OPEN LINE FROM BUS 324137 [5CRITTENDEN 161.00] TO BUS 324151 [5LIVNGSTN CO161.00] CKT 1 | 0.93965 | 64.8362 | 0.93968 | 64.8382 | 2.9445e-05 | -0.00031614
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 822 324137-324151(1) | OPEN LINE FROM BUS 324137 [5CRITTENDEN 161.00] TO BUS 324151 [5LIVNGSTN CO161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 823 324137-324153(1) | OPEN LINE FROM BUS 324137 [5CRITTENDEN 161.00] TO BUS 324153 [5MORGANFIELD161.00] CKT 1 | 0.93965 | 64.8362 | 0.93968 | 64.8377 | 2.1756e-05 | -0.00032383
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 823 324137-324153(1) | OPEN LINE FROM BUS 324137 [5CRITTENDEN 161.00] TO BUS 324153 [5MORGANFIELD161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 824 324137-324486(1) | OPEN LINE FROM BUS 324137 [5CRITTENDEN 161.00] TO BUS 324486 [2CRITTENDEN 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 3.0398e-06 | -0.00034255
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 824 324137-324486(1) | OPEN LINE FROM BUS 324137 [5CRITTENDEN 161.00] TO BUS 324486 [2CRITTENDEN 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 825 324138-324148(1) | OPEN LINE FROM BUS 324138 [5DELVINTA 161.00] TO BUS 324148 [5WOOTON TAP 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93956 | 64.8295 | -9.6679e-05 | -0.00044227
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 825 324138-324148(1) | OPEN LINE FROM BUS 324138 [5DELVINTA 161.00] TO BUS 324148 [5WOOTON TAP 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 826 324138-324165(1) | OPEN LINE FROM BUS 324138 [5DELVINTA 161.00] TO BUS 324165 [5W IRVINE T 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8365 | 5.0068e-06 | -0.00034058
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 826 324138-324165(1) | OPEN LINE FROM BUS 324138 [5DELVINTA 161.00] TO BUS 324165 [5W IRVINE T 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 827 324139-324149(1) | OPEN LINE FROM BUS 324139 [5DORCHESTER 161.00] TO BUS 324149 [5IMBODEN 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8353 | -1.1861e-05 | -0.00035745
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 827 324139-324149(1) | OPEN LINE FROM BUS 324139 [5DORCHESTER 161.00] TO BUS 324149 [5IMBODEN 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 828 324139-324503(1) | OPEN LINE FROM BUS 324139 [5DORCHESTER 161.00] TO BUS 324503 [2DORCHESTER 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8359 | -3.5763e-06 | -0.00034916
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 828 324139-324503(1) | OPEN LINE FROM BUS 324139 [5DORCHESTER 161.00] TO BUS 324503 [2DORCHESTER 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 829 324139-324503(2) | OPEN LINE FROM BUS 324139 [5DORCHESTER 161.00] TO BUS 324503 [2DORCHESTER 69.000] CKT 2 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -2.563e-06 | -0.00034815
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 829 324139-324503(2) | OPEN LINE FROM BUS 324139 [5DORCHESTER 161.00] TO BUS 324503 [2DORCHESTER 69.000] CKT 2 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 830 324140-324160(1) | OPEN LINE FROM BUS 324140 [5EARLINGTN N161.00] TO BUS 324160 [5RIVER QN T 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -2.9802e-07 | -0.00034589
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 830 324140-324160(1) | OPEN LINE FROM BUS 324140 [5EARLINGTN N161.00] TO BUS 324160 [5RIVER QN T 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 831 324140-324164(1) | OPEN LINE FROM BUS 324140 [5EARLINGTN N161.00] TO BUS 324164 [5WALKER 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 2.9802e-07 | -0.00034529
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 831 324140-324164(1) | OPEN LINE FROM BUS 324140 [5EARLINGTN N161.00] TO BUS 324164 [5WALKER 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 832 324140-324506(1) | OPEN LINE FROM BUS 324140 [5EARLINGTN N161.00] TO BUS 324506 [2EARLINGTN N69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 5.3644e-07 | -0.00034505
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 832 324140-324506(1) | OPEN LINE FROM BUS 324140 [5EARLINGTN N161.00] TO BUS 324506 [2EARLINGTN N69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 833 324140-325079(1) | OPEN LINE FROM BUS 324140 [5EARLINGTN N161.00] TO BUS 325079 [5N PRINCETON161.00] CKT 1 | 0.93965 | 64.8362 | 0.93968 | 64.8379 | 2.5928e-05 | -0.00031966
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 833 324140-325079(1) | OPEN LINE FROM BUS 324140 [5EARLINGTN N161.00] TO BUS 325079 [5N PRINCETON161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 834 324141-324514(1) | OPEN LINE FROM BUS 324141 [5ELIHU 161.00] TO BUS 324514 [2ELIHU 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8356 | -8.2254e-06 | -0.00035381
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 834 324141-324514(1) | OPEN LINE FROM BUS 324141 [5ELIHU 161.00] TO BUS 324514 [2ELIHU 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 835 324141-324514(2) | OPEN LINE FROM BUS 324141 [5ELIHU 161.00] TO BUS 324514 [2ELIHU 69.000] CKT 2 | 0.93965 | 64.8362 | 0.93964 | 64.8355 | -9.4175e-06 | -0.00035501
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 835 324141-324514(2) | OPEN LINE FROM BUS 324141 [5ELIHU 161.00] TO BUS 324514 [2ELIHU 69.000] CKT 2 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 836 324143-324527(1) | OPEN LINE FROM BUS 324143 [5FARLEY 161.00] TO BUS 324527 [2FARLEY KU 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93974 | 64.842 | 8.4043e-05 | -0.00026155
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 836 324143-324527(1) | OPEN LINE FROM BUS 324143 [5FARLEY 161.00] TO BUS 324527 [2FARLEY KU 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 837 324144-324160(1) | OPEN LINE FROM BUS 324144 [5GREEN RIVER161.00] TO BUS 324160 [5RIVER QN T 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8358 | -5.126e-06 | -0.00035071
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 837 324144-324160(1) | OPEN LINE FROM BUS 324144 [5GREEN RIVER161.00] TO BUS 324160 [5RIVER QN T 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 838 324144-324255(1) | OPEN LINE FROM BUS 324144 [5GREEN RIVER161.00] TO BUS 324255 [4GREEN RIVER138.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 7.7486e-07 | -0.00034481
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 838 324144-324255(1) | OPEN LINE FROM BUS 324144 [5GREEN RIVER161.00] TO BUS 324255 [4GREEN RIVER138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 839 324144-324255(2) | OPEN LINE FROM BUS 324144 [5GREEN RIVER161.00] TO BUS 324255 [4GREEN RIVER138.00] CKT 2 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 8.9407e-07 | -0.00034469
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 839 324144-324255(2) | OPEN LINE FROM BUS 324144 [5GREEN RIVER161.00] TO BUS 324255 [4GREEN RIVER138.00] CKT 2 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 840 324144-324255(3) | OPEN LINE FROM BUS 324144 [5GREEN RIVER161.00] TO BUS 324255 [4GREEN RIVER138.00] CKT 3 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 7.1526e-07 | -0.00034487
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 840 324144-324255(3) | OPEN LINE FROM BUS 324144 [5GREEN RIVER161.00] TO BUS 324255 [4GREEN RIVER138.00] CKT 3 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 841 324145-324171(1) | OPEN LINE FROM BUS 324145 [5GRAHAMVILLE161.00] TO BUS 324171 [5GRAHMVILE 1161.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 4.0531e-06 | -0.00034153
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 841 324145-324171(1) | OPEN LINE FROM BUS 324145 [5GRAHAMVILLE161.00] TO BUS 324171 [5GRAHMVILE 1161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 842 324145-324172(1) | OPEN LINE FROM BUS 324145 [5GRAHAMVILLE161.00] TO BUS 324172 [5GRAHMVILE 2161.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 2.7418e-06 | -0.00034285
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 842 324145-324172(1) | OPEN LINE FROM BUS 324145 [5GRAHAMVILLE161.00] TO BUS 324172 [5GRAHMVILE 2161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 843 324145-324553(1) | OPEN LINE FROM BUS 324145 [5GRAHAMVILLE161.00] TO BUS 324553 [2GRAHAMVILLE69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 1.1921e-07 | -0.00034547
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 843 324145-324553(1) | OPEN LINE FROM BUS 324145 [5GRAHAMVILLE161.00] TO BUS 324553 [2GRAHAMVILLE69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 844 324145-325069(1) | OPEN LINE FROM BUS 324145 [5GRAHAMVILLE161.00] TO BUS 325069 [5SONG SP TP 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.2517e-06 | -0.00034684
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 844 324145-325069(1) | OPEN LINE FROM BUS 324145 [5GRAHAMVILLE161.00] TO BUS 325069 [5SONG SP TP 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 845 324145-325077(1) | OPEN LINE FROM BUS 324145 [5GRAHAMVILLE161.00] TO BUS 325077 [5COLEMAN TAP161.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8369 | 1.0371e-05 | -0.00033522
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 845 324145-325077(1) | OPEN LINE FROM BUS 324145 [5GRAHAMVILLE161.00] TO BUS 325077 [5COLEMAN TAP161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 846 324146-324147(1) | OPEN LINE FROM BUS 324146 [5HARLAN WYE 161.00] TO BUS 324147 [5HOWARDS BR 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8355 | -8.8215e-06 | -0.00035441
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 846 324146-324147(1) | OPEN LINE FROM BUS 324146 [5HARLAN WYE 161.00] TO BUS 324147 [5HOWARDS BR 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 847 324146-324155(1) | OPEN LINE FROM BUS 324146 [5HARLAN WYE 161.00] TO BUS 324155 [5PINEVILLE 1161.00] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8352 | -1.359e-05 | -0.00035918
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 847 324146-324155(1) | OPEN LINE FROM BUS 324146 [5HARLAN WYE 161.00] TO BUS 324155 [5PINEVILLE 1161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 848 324146-324157(1) | OPEN LINE FROM BUS 324146 [5HARLAN WYE 161.00] TO BUS 324157 [5POCKET N 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8355 | -9.1791e-06 | -0.00035477
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 848 324146-324157(1) | OPEN LINE FROM BUS 324146 [5HARLAN WYE 161.00] TO BUS 324157 [5POCKET N 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 849 324146-324564(1) | OPEN LINE FROM BUS 324146 [5HARLAN WYE 161.00] TO BUS 324564 [2HARLAN WYE 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8356 | -7.7486e-06 | -0.00035334
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 849 324146-324564(1) | OPEN LINE FROM BUS 324146 [5HARLAN WYE 161.00] TO BUS 324564 [2HARLAN WYE 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 850 324147-324155(1) | OPEN LINE FROM BUS 324147 [5HOWARDS BR 161.00] TO BUS 324155 [5PINEVILLE 1161.00] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8355 | -9.656e-06 | -0.00035524
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 850 324147-324155(1) | OPEN LINE FROM BUS 324147 [5HOWARDS BR 161.00] TO BUS 324155 [5PINEVILLE 1161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 851 324149-324157(1) | OPEN LINE FROM BUS 324149 [5IMBODEN 161.00] TO BUS 324157 [5POCKET N 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93962 | 64.8337 | -3.5644e-05 | -0.00038123
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 851 324149-324157(1) | OPEN LINE FROM BUS 324149 [5IMBODEN 161.00] TO BUS 324157 [5POCKET N 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 852 324149-324583(1) | OPEN LINE FROM BUS 324149 [5IMBODEN 161.00] TO BUS 324583 [2IMBODEN 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8357 | -6.1393e-06 | -0.00035173
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 852 324149-324583(1) | OPEN LINE FROM BUS 324149 [5IMBODEN 161.00] TO BUS 324583 [2IMBODEN 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 853 324150-324154(1) | OPEN LINE FROM BUS 324150 [5LEBANON JCT161.00] TO BUS 324154 [5PADDYS RUN 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93961 | 64.8332 | -4.2737e-05 | -0.00038832
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 853 324150-324154(1) | OPEN LINE FROM BUS 324150 [5LEBANON JCT161.00] TO BUS 324154 [5PADDYS RUN 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 854 324151-324161(1) | OPEN LINE FROM BUS 324151 [5LIVNGSTN CO161.00] TO BUS 324161 [5S PADUCAH 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 3.3975e-06 | -0.00034219
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 854 324151-324161(1) | OPEN LINE FROM BUS 324151 [5LIVNGSTN CO161.00] TO BUS 324161 [5S PADUCAH 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 855 324151-325028(1) | OPEN LINE FROM BUS 324151 [5LIVNGSTN CO161.00] TO BUS 325028 [5ASHWD SL TP161.00] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8375 | 2.0146e-05 | -0.00032544
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 855 324151-325028(1) | OPEN LINE FROM BUS 324151 [5LIVNGSTN CO161.00] TO BUS 325028 [5ASHWD SL TP161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 856 324152-324165(1) | OPEN LINE FROM BUS 324152 [5LAKE REBA T161.00] TO BUS 324165 [5W IRVINE T 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8359 | -3.9935e-06 | -0.00034958
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 856 324152-324165(1) | OPEN LINE FROM BUS 324152 [5LAKE REBA T161.00] TO BUS 324165 [5W IRVINE T 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 857 324152-324276(1) | OPEN LINE FROM BUS 324152 [5LAKE REBA T161.00] TO BUS 324276 [4LAKE REBA T138.00] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8371 | 1.3471e-05 | -0.00033212
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 857 324152-324276(1) | OPEN LINE FROM BUS 324152 [5LAKE REBA T161.00] TO BUS 324276 [4LAKE REBA T138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 858 324153-324645(1) | OPEN LINE FROM BUS 324153 [5MORGANFIELD161.00] TO BUS 324645 [2MORGANFIELD69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 1.9073e-06 | -0.00034368
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 858 324153-324645(1) | OPEN LINE FROM BUS 324153 [5MORGANFIELD161.00] TO BUS 324645 [2MORGANFIELD69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 859 324155-324156(1) | OPEN LINE FROM BUS 324155 [5PINEVILLE 1161.00] TO BUS 324156 [5PINEVILE SW161.00] CKT 1 | 0.93965 | 64.8362 | 0.93961 | 64.8328 | -4.8101e-05 | -0.00039369
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 859 324155-324156(1) | OPEN LINE FROM BUS 324155 [5PINEVILLE 1161.00] TO BUS 324156 [5PINEVILE SW161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 860 324155-324167(Z1) | OPEN LINE FROM BUS 324155 [5PINEVILLE 1161.00] TO BUS 324167 [5PINEVILLE 2161.00] CKT Z1 | 0.93965 | 64.8362 | 0.93956 | 64.8296 | -9.4414e-05 | -0.00044
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 860 324155-324167(Z1) | OPEN LINE FROM BUS 324155 [5PINEVILLE 1161.00] TO BUS 324167 [5PINEVILLE 2161.00] CKT Z1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 861 324155-324686(1) | OPEN LINE FROM BUS 324155 [5PINEVILLE 1161.00] TO BUS 324686 [2PINEVILLE 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8354 | -1.1444e-05 | -0.00035703
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 861 324155-324686(1) | OPEN LINE FROM BUS 324155 [5PINEVILLE 1161.00] TO BUS 324686 [2PINEVILLE 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 862 324157-324158(1) | OPEN LINE FROM BUS 324157 [5POCKET N 161.00] TO BUS 324158 [5POCKET 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93963 | 64.8344 | -2.4855e-05 | -0.00037044
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 862 324157-324158(1) | OPEN LINE FROM BUS 324157 [5POCKET N 161.00] TO BUS 324158 [5POCKET 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 863 324158-324689(1) | OPEN LINE FROM BUS 324158 [5POCKET 161.00] TO BUS 324689 [2POCKET 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93963 | 64.8345 | -2.4438e-05 | -0.00037003
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 863 324158-324689(1) | OPEN LINE FROM BUS 324158 [5POCKET 161.00] TO BUS 324689 [2POCKET 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 864 324159-324160(1) | OPEN LINE FROM BUS 324159 [5RIVER QUEEN161.00] TO BUS 324160 [5RIVER QN T 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 5.9605e-08 | -0.00034553
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 864 324159-324160(1) | OPEN LINE FROM BUS 324159 [5RIVER QUEEN161.00] TO BUS 324160 [5RIVER QN T 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 865 324159-324702(1) | OPEN LINE FROM BUS 324159 [5RIVER QUEEN161.00] TO BUS 324702 [2RIVER QUEEN69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 1.1921e-07 | -0.00034547
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 865 324159-324702(1) | OPEN LINE FROM BUS 324159 [5RIVER QUEEN161.00] TO BUS 324702 [2RIVER QUEEN69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 866 324161-324712(1) | OPEN LINE FROM BUS 324161 [5S PADUCAH 161.00] TO BUS 324712 [2SO PADUCAH 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 2.9802e-07 | -0.00034529
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 866 324161-324712(1) | OPEN LINE FROM BUS 324161 [5S PADUCAH 161.00] TO BUS 324712 [2SO PADUCAH 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 867 324161-325078(1) | OPEN LINE FROM BUS 324161 [5S PADUCAH 161.00] TO BUS 325078 [5PADUCAH PRI161.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8365 | 4.9472e-06 | -0.00034064
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 867 324161-325078(1) | OPEN LINE FROM BUS 324161 [5S PADUCAH 161.00] TO BUS 325078 [5PADUCAH PRI161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 868 324163-324165(1) | OPEN LINE FROM BUS 324163 [5WEST IRVINE161.00] TO BUS 324165 [5W IRVINE T 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93962 | 64.8341 | -2.9802e-05 | -0.00037539
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 868 324163-324165(1) | OPEN LINE FROM BUS 324163 [5WEST IRVINE161.00] TO BUS 324165 [5W IRVINE T 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 869 324163-324767(1) | OPEN LINE FROM BUS 324163 [5WEST IRVINE161.00] TO BUS 324767 [2WEST IRVINE69.000] CKT 1 | 0.93965 | 64.8362 | 0.93963 | 64.8344 | -2.4796e-05 | -0.00037038
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 869 324163-324767(1) | OPEN LINE FROM BUS 324163 [5WEST IRVINE161.00] TO BUS 324767 [2WEST IRVINE69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 870 324164-324769(1) | OPEN LINE FROM BUS 324164 [5WALKER 161.00] TO BUS 324769 [2WALKER KU 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 2.3842e-07 | -0.00034535
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 870 324164-324769(1) | OPEN LINE FROM BUS 324164 [5WALKER 161.00] TO BUS 324769 [2WALKER KU 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 871 324166-324779(1) | OPEN LINE FROM BUS 324166 [5WICKLIFFE 161.00] TO BUS 324779 [2WICKLIFFE 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.2517e-06 | -0.00034684
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 871 324166-324779(1) | OPEN LINE FROM BUS 324166 [5WICKLIFFE 161.00] TO BUS 324779 [2WICKLIFFE 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 872 324166-325069(1) | OPEN LINE FROM BUS 324166 [5WICKLIFFE 161.00] TO BUS 325069 [5SONG SP TP 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.3113e-06 | -0.0003469
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 872 324166-325069(1) | OPEN LINE FROM BUS 324166 [5WICKLIFFE 161.00] TO BUS 325069 [5SONG SP TP 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 873 324167-324686(2) | OPEN LINE FROM BUS 324167 [5PINEVILLE 2161.00] TO BUS 324686 [2PINEVILLE 69.000] CKT 2 | 0.93965 | 64.8362 | 0.93964 | 64.8351 | -1.508e-05 | -0.00036067
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 873 324167-324686(2) | OPEN LINE FROM BUS 324167 [5PINEVILLE 2161.00] TO BUS 324686 [2PINEVILLE 69.000] CKT 2 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 874 324191-324603(1) | OPEN LINE FROM BUS 324191 [2LEBANON E T69.000] TO BUS 324603 [2LEBANON CIT69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8355 | -9.1791e-06 | -0.00035477
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 874 324191-324603(1) | OPEN LINE FROM BUS 324191 [2LEBANON E T69.000] TO BUS 324603 [2LEBANON CIT69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 875 324191-324606(1) | OPEN LINE FROM BUS 324191 [2LEBANON E T69.000] TO BUS 324606 [2LEBANON 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8355 | -9.2387e-06 | -0.00035483
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 875 324191-324606(1) | OPEN LINE FROM BUS 324191 [2LEBANON E T69.000] TO BUS 324606 [2LEBANON 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 876 324192-324240(1) | OPEN LINE FROM BUS 324192 [4DAYTON-WALT138.00] TO BUS 324240 [4DAY-WALT TP138.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8359 | -3.0398e-06 | -0.00034863
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 876 324192-324240(1) | OPEN LINE FROM BUS 324192 [4DAYTON-WALT138.00] TO BUS 324240 [4DAY-WALT TP138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 877 324193-324251(1) | OPEN LINE FROM BUS 324193 [4FLEMINGB KU138.00] TO BUS 324251 [4FLEMNB KU T138.00] CKT 1 | 0.93965 | 64.8362 | 0.93981 | 64.8467 | 0.00015259 | -0.000193
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 877 324193-324251(1) | OPEN LINE FROM BUS 324193 [4FLEMINGB KU138.00] TO BUS 324251 [4FLEMNB KU T138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 878 324195-324722(1) | OPEN LINE FROM BUS 324195 [2AUGUSTA 69.000] TO BUS 324722 [2SHARON KU 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 879 324196-324224(1) | OPEN LINE FROM BUS 324196 [2BOONESB PRK69.000] TO BUS 324224 [2RED HOUSE 69.000] CKT 1 | 0.93965 | 64.8362 | 0.9397 | 64.8392 | 4.4227e-05 | -0.00030136
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 879 324196-324224(1) | OPEN LINE FROM BUS 324196 [2BOONESB PRK69.000] TO BUS 324224 [2RED HOUSE 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 880 324196-324449(1) | OPEN LINE FROM BUS 324196 [2BOONESB PRK69.000] TO BUS 324449 [2BOONSBORO N69.000] CKT 1 | 0.93965 | 64.8362 | 0.93975 | 64.8428 | 9.5785e-05 | -0.0002498
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 880 324196-324449(1) | OPEN LINE FROM BUS 324196 [2BOONESB PRK69.000] TO BUS 324449 [2BOONSBORO N69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 881 324198-324878(1) | OPEN LINE FROM BUS 324198 [2HUNT BOTTOM69.000] TO BUS 324878 [2HUNT BTM TP69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 9.5367e-07 | -0.00034463
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 881 324198-324878(1) | OPEN LINE FROM BUS 324198 [2HUNT BOTTOM69.000] TO BUS 324878 [2HUNT BTM TP69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 882 324199-324252(1) | OPEN LINE FROM BUS 324199 [2OWENTON 69.000] TO BUS 324252 [2SCHOLLS 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93968 | 64.838 | 2.6643e-05 | -0.00031894
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 882 324199-324252(1) | OPEN LINE FROM BUS 324199 [2OWENTON 69.000] TO BUS 324252 [2SCHOLLS 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 883 324200-324205(1) | OPEN LINE FROM BUS 324200 [4PLSUR RDG T138.00] TO BUS 324205 [4ASHBOTTOM 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 1.6689e-06 | -0.00034392
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 883 324200-324205(1) | OPEN LINE FROM BUS 324200 [4PLSUR RDG T138.00] TO BUS 324205 [4ASHBOTTOM 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 884 324200-324237(1) | OPEN LINE FROM BUS 324200 [4PLSUR RDG T138.00] TO BUS 324237 [4CANE RUN SW138.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 2.0266e-06 | -0.00034356
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 884 324200-324237(1) | OPEN LINE FROM BUS 324200 [4PLSUR RDG T138.00] TO BUS 324237 [4CANE RUN SW138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 885 324200-324299(1) | OPEN LINE FROM BUS 324200 [4PLSUR RDG T138.00] TO BUS 324299 [4PLEASUR RDG138.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 0 | -0.00034559
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 885 324200-324299(1) | OPEN LINE FROM BUS 324200 [4PLSUR RDG T138.00] TO BUS 324299 [4PLEASUR RDG138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 886 324201-324305(1) | OPEN LINE FROM BUS 324201 [4ADAMS 138.00] TO BUS 324305 [4SCOTT CO 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93963 | 64.8342 | -2.8491e-05 | -0.00037408
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 886 324201-324305(1) | OPEN LINE FROM BUS 324201 [4ADAMS 138.00] TO BUS 324305 [4SCOTT CO 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 887 324201-324313(1) | OPEN LINE FROM BUS 324201 [4ADAMS 138.00] TO BUS 324313 [4TOYOTA S 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93957 | 64.8303 | -8.4758e-05 | -0.00043035
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 887 324201-324313(1) | OPEN LINE FROM BUS 324201 [4ADAMS 138.00] TO BUS 324313 [4TOYOTA S 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 888 324201-324315(1) | OPEN LINE FROM BUS 324201 [4ADAMS 138.00] TO BUS 324315 [4TYRONE 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93931 | 64.8123 | -0.00034517 | -0.00069076
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 888 324201-324315(1) | OPEN LINE FROM BUS 324201 [4ADAMS 138.00] TO BUS 324315 [4TYRONE 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 889 324201-324335(1) | OPEN LINE FROM BUS 324201 [4ADAMS 138.00] TO BUS 324335 [4INNOVATION 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93943 | 64.8208 | -0.00022227 | -0.00056785
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 889 324201-324335(1) | OPEN LINE FROM BUS 324201 [4ADAMS 138.00] TO BUS 324335 [4INNOVATION 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 890 324201-324405(1) | OPEN LINE FROM BUS 324201 [4ADAMS 138.00] TO BUS 324405 [2ADAMS 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93968 | 64.8378 | 2.3901e-05 | -0.00032169
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 890 324201-324405(1) | OPEN LINE FROM BUS 324201 [4ADAMS 138.00] TO BUS 324405 [2ADAMS 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 891 324201-324405(2) | OPEN LINE FROM BUS 324201 [4ADAMS 138.00] TO BUS 324405 [2ADAMS 69.000] CKT 2 | 0.93965 | 64.8362 | 0.93968 | 64.8376 | 2.1219e-05 | -0.00032437
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 891 324201-324405(2) | OPEN LINE FROM BUS 324201 [4ADAMS 138.00] TO BUS 324405 [2ADAMS 69.000] CKT 2 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 892 324202-324241(1) | OPEN LINE FROM BUS 324202 [4ALGONQUIN 138.00] TO BUS 324241 [4DIXIE 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8366 | 6.3777e-06 | -0.00033921
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 892 324202-324241(1) | OPEN LINE FROM BUS 324202 [4ALGONQUIN 138.00] TO BUS 324241 [4DIXIE 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 893 324202-324408(1) | OPEN LINE FROM BUS 324202 [4ALGONQUIN 138.00] TO BUS 324408 [2ALGONQUIN 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8366 | 6.4969e-06 | -0.00033909
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 893 324202-324408(1) | OPEN LINE FROM BUS 324202 [4ALGONQUIN 138.00] TO BUS 324408 [2ALGONQUIN 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 894 324203-324258(1) | OPEN LINE FROM BUS 324203 [4AMERICAN AV138.00] TO BUS 324258 [4HAEFLING 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93973 | 64.8412 | 7.3493e-05 | -0.0002721
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 894 324203-324258(1) | OPEN LINE FROM BUS 324203 [4AMERICAN AV138.00] TO BUS 324258 [4HAEFLING 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 895 324203-324301(1) | OPEN LINE FROM BUS 324203 [4AMERICAN AV138.00] TO BUS 324301 [4REYNOLDS 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8358 | -5.0068e-06 | -0.00035059
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 895 324203-324301(1) | OPEN LINE FROM BUS 324203 [4AMERICAN AV138.00] TO BUS 324301 [4REYNOLDS 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 896 324203-324409(1) | OPEN LINE FROM BUS 324203 [4AMERICAN AV138.00] TO BUS 324409 [2AMERICAN AV69.000] CKT 1 | 0.93965 | 64.8362 | 0.93948 | 64.824 | -0.00017667 | -0.00052226
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 896 324203-324409(1) | OPEN LINE FROM BUS 324203 [4AMERICAN AV138.00] TO BUS 324409 [2AMERICAN AV69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 897 324204-324205(1) | OPEN LINE FROM BUS 324204 [4APPLIANC PK138.00] TO BUS 324205 [4ASHBOTTOM 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 3.2187e-06 | -0.00034237
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 897 324204-324205(1) | OPEN LINE FROM BUS 324204 [4APPLIANC PK138.00] TO BUS 324205 [4ASHBOTTOM 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 898 324204-324243(1) | OPEN LINE FROM BUS 324204 [4APPLIANC PK138.00] TO BUS 324243 [4ETHEL 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.1921e-06 | -0.00034678
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 898 324204-324243(1) | OPEN LINE FROM BUS 324204 [4APPLIANC PK138.00] TO BUS 324243 [4ETHEL 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 899 324204-324281(1) | OPEN LINE FROM BUS 324204 [4APPLIANC PK138.00] TO BUS 324281 [4MIDDLETOWN 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8356 | -7.3314e-06 | -0.00035292
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 899 324204-324281(1) | OPEN LINE FROM BUS 324204 [4APPLIANC PK138.00] TO BUS 324281 [4MIDDLETOWN 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 900 324205-324237(1) | OPEN LINE FROM BUS 324205 [4ASHBOTTOM 138.00] TO BUS 324237 [4CANE RUN SW138.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 1.6093e-06 | -0.00034398
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 900 324205-324237(1) | OPEN LINE FROM BUS 324205 [4ASHBOTTOM 138.00] TO BUS 324237 [4CANE RUN SW138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 901 324205-324257(1) | OPEN LINE FROM BUS 324205 [4ASHBOTTOM 138.00] TO BUS 324257 [4GRADE LANE 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 3.9339e-06 | -0.00034165
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 901 324205-324257(1) | OPEN LINE FROM BUS 324205 [4ASHBOTTOM 138.00] TO BUS 324257 [4GRADE LANE 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 902 324205-324279(1) | OPEN LINE FROM BUS 324205 [4ASHBOTTOM 138.00] TO BUS 324279 [4MANSLICK 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 9.5367e-07 | -0.00034463
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 902 324205-324279(1) | OPEN LINE FROM BUS 324205 [4ASHBOTTOM 138.00] TO BUS 324279 [4MANSLICK 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 903 324205-324419(1) | OPEN LINE FROM BUS 324205 [4ASHBOTTOM 138.00] TO BUS 324419 [2ASHBOT WEST69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -7.7486e-07 | -0.00034636
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 903 324205-324419(1) | OPEN LINE FROM BUS 324205 [4ASHBOTTOM 138.00] TO BUS 324419 [2ASHBOT WEST69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 904 324205-325023(2) | OPEN LINE FROM BUS 324205 [4ASHBOTTOM 138.00] TO BUS 325023 [2ASHBOT EAST69.000] CKT 2 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -8.3447e-07 | -0.00034642
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 904 324205-325023(2) | OPEN LINE FROM BUS 324205 [4ASHBOTTOM 138.00] TO BUS 325023 [2ASHBOT EAST69.000] CKT 2 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 905 324206-324284(1) | OPEN LINE FROM BUS 324206 [4ASHBY 138.00] TO BUS 324284 [4MILL CREEK 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 0 | -0.00034559
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 905 324206-324284(1) | OPEN LINE FROM BUS 324206 [4ASHBY 138.00] TO BUS 324284 [4MILL CREEK 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 906 324206-324299(1) | OPEN LINE FROM BUS 324206 [4ASHBY 138.00] TO BUS 324299 [4PLEASUR RDG138.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 2.9802e-07 | -0.00034529
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 906 324206-324299(1) | OPEN LINE FROM BUS 324206 [4ASHBY 138.00] TO BUS 324299 [4PLEASUR RDG138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 907 324207-324218(1) | OPEN LINE FROM BUS 324207 [4BARDSTOWN 138.00] TO BUS 324218 [4BROWN CT 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8352 | -1.4484e-05 | -0.00036007
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 907 324207-324218(1) | OPEN LINE FROM BUS 324207 [4BARDSTOWN 138.00] TO BUS 324218 [4BROWN CT 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 908 324207-324288(1) | OPEN LINE FROM BUS 324207 [4BARDSTOWN 138.00] TO BUS 324288 [4NELSON CO 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8358 | -5.722e-06 | -0.00035131
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 908 324207-324288(1) | OPEN LINE FROM BUS 324207 [4BARDSTOWN 138.00] TO BUS 324288 [4NELSON CO 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 909 324207-324426(1) | OPEN LINE FROM BUS 324207 [4BARDSTOWN 138.00] TO BUS 324426 [2BARDSTOWN 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -2.3246e-06 | -0.00034791
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 909 324207-324426(1) | OPEN LINE FROM BUS 324207 [4BARDSTOWN 138.00] TO BUS 324426 [2BARDSTOWN 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 910 324208-324265(1) | OPEN LINE FROM BUS 324208 [4BEARGRASS 138.00] TO BUS 324265 [4JEFFRSONV T138.00] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8371 | 1.3232e-05 | -0.00033236
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 910 324208-324265(1) | OPEN LINE FROM BUS 324208 [4BEARGRASS 138.00] TO BUS 324265 [4JEFFRSONV T138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 911 324208-324277(1) | OPEN LINE FROM BUS 324208 [4BEARGRASS 138.00] TO BUS 324277 [4LYNDON SO 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -6.5565e-07 | -0.00034624
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 911 324208-324277(1) | OPEN LINE FROM BUS 324208 [4BEARGRASS 138.00] TO BUS 324277 [4LYNDON SO 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 912 324208-324289(1) | OPEN LINE FROM BUS 324208 [4BEARGRASS 138.00] TO BUS 324289 [4NORTHSIDE 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 2.7418e-06 | -0.00034285
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 912 324208-324289(1) | OPEN LINE FROM BUS 324208 [4BEARGRASS 138.00] TO BUS 324289 [4NORTHSIDE 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 913 324208-324298(1) | OPEN LINE FROM BUS 324208 [4BEARGRASS 138.00] TO BUS 324298 [4PLAINVIEW T138.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 8.9407e-07 | -0.00034469
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 913 324208-324298(1) | OPEN LINE FROM BUS 324208 [4BEARGRASS 138.00] TO BUS 324298 [4PLAINVIEW T138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 914 324208-324321(1) | OPEN LINE FROM BUS 324208 [4BEARGRASS 138.00] TO BUS 324321 [4WATERSIDE 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.1921e-06 | -0.00034678
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 914 324208-324321(1) | OPEN LINE FROM BUS 324208 [4BEARGRASS 138.00] TO BUS 324321 [4WATERSIDE 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 915 324208-324321(2) | OPEN LINE FROM BUS 324208 [4BEARGRASS 138.00] TO BUS 324321 [4WATERSIDE 138.00] CKT 2 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.1921e-06 | -0.00034678
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 915 324208-324321(2) | OPEN LINE FROM BUS 324208 [4BEARGRASS 138.00] TO BUS 324321 [4WATERSIDE 138.00] CKT 2 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 916 324208-324429(1) | OPEN LINE FROM BUS 324208 [4BEARGRASS 138.00] TO BUS 324429 [2BEARGRASS 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8366 | 6.0201e-06 | -0.00033957
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 916 324208-324429(1) | OPEN LINE FROM BUS 324208 [4BEARGRASS 138.00] TO BUS 324429 [2BEARGRASS 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 917 324209-324263(1) | OPEN LINE FROM BUS 324209 [4BG PARKWAY 138.00] TO BUS 324263 [4HURSTBORNE 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8369 | 1.1504e-05 | -0.00033408
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 917 324209-324263(1) | OPEN LINE FROM BUS 324209 [4BG PARKWAY 138.00] TO BUS 324263 [4HURSTBORNE 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 918 324210-324262(1) | OPEN LINE FROM BUS 324210 [4BAKER LANE 138.00] TO BUS 324262 [4HIGBY MILL 138.00] CKT 1 | 0.93965 | 64.8362 | 0.9395 | 64.8258 | -0.00014973 | -0.00049531
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 918 324210-324262(1) | OPEN LINE FROM BUS 324210 [4BAKER LANE 138.00] TO BUS 324262 [4HIGBY MILL 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 919 324210-324334(1) | OPEN LINE FROM BUS 324210 [4BAKER LANE 138.00] TO BUS 324334 [4BROWN N 2-R138.00] CKT 1 | 0.93965 | 64.8362 | 0.93904 | 64.794 | -0.00061065 | -0.00095624
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 919 324210-324334(1) | OPEN LINE FROM BUS 324210 [4BAKER LANE 138.00] TO BUS 324334 [4BROWN N 2-R138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 920 324211-324221(1) | OPEN LINE FROM BUS 324211 [4BLACKWELL 138.00] TO BUS 324221 [4BUTLER 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 921 324211-324253(1) | OPEN LINE FROM BUS 324211 [4BLACKWELL 138.00] TO BUS 324253 [4GHENT 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 922 324212-324285(1) | OPEN LINE FROM BUS 324212 [4BLUE LICK 138.00] TO BUS 324285 [4MUD LANE 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8356 | -7.5698e-06 | -0.00035316
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 922 324212-324285(1) | OPEN LINE FROM BUS 324212 [4BLUE LICK 138.00] TO BUS 324285 [4MUD LANE 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 923 324213-324270(1) | OPEN LINE FROM BUS 324213 [4BONNIEVILLE138.00] TO BUS 324270 [4LEBANON WES138.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8359 | -3.3975e-06 | -0.00034899
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 923 324213-324270(1) | OPEN LINE FROM BUS 324213 [4BONNIEVILLE138.00] TO BUS 324270 [4LEBANON WES138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 924 324213-324447(1) | OPEN LINE FROM BUS 324213 [4BONNIEVILLE138.00] TO BUS 324447 [2BONNIE KU 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.3113e-06 | -0.0003469
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 924 324213-324447(1) | OPEN LINE FROM BUS 324213 [4BONNIEVILLE138.00] TO BUS 324447 [2BONNIE KU 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 925 324213-324800(1) | OPEN LINE FROM BUS 324213 [4BONNIEVILLE138.00] TO BUS 324800 [4MERE TVA 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8359 | -3.0398e-06 | -0.00034863
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 925 324213-324800(1) | OPEN LINE FROM BUS 324213 [4BONNIEVILLE138.00] TO BUS 324800 [4MERE TVA 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 926 324214-324243(1) | OPEN LINE FROM BUS 324214 [4BRECKNRIDGE138.00] TO BUS 324243 [4ETHEL 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 5.9605e-08 | -0.00034553
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 926 324214-324243(1) | OPEN LINE FROM BUS 324214 [4BRECKNRIDGE138.00] TO BUS 324243 [4ETHEL 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 927 324214-324263(1) | OPEN LINE FROM BUS 324214 [4BRECKNRIDGE138.00] TO BUS 324263 [4HURSTBORNE 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -6.5565e-07 | -0.00034624
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 927 324214-324263(1) | OPEN LINE FROM BUS 324214 [4BRECKNRIDGE138.00] TO BUS 324263 [4HURSTBORNE 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 928 324214-324451(1) | OPEN LINE FROM BUS 324214 [4BRECKNRIDGE138.00] TO BUS 324451 [2BRECKNRIDGE69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -6.5565e-07 | -0.00034624
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 928 324214-324451(1) | OPEN LINE FROM BUS 324214 [4BRECKNRIDGE138.00] TO BUS 324451 [2BRECKNRIDGE69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 929 324215-324237(1) | OPEN LINE FROM BUS 324215 [4BRIDGPOR HE138.00] TO BUS 324237 [4CANE RUN SW138.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 1.7881e-07 | -0.00034541
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 929 324215-324237(1) | OPEN LINE FROM BUS 324215 [4BRIDGPOR HE138.00] TO BUS 324237 [4CANE RUN SW138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 930 324215-324284(1) | OPEN LINE FROM BUS 324215 [4BRIDGPOR HE138.00] TO BUS 324284 [4MILL CREEK 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -2.3842e-07 | -0.00034583
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 930 324215-324284(1) | OPEN LINE FROM BUS 324215 [4BRIDGPOR HE138.00] TO BUS 324284 [4MILL CREEK 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 931 324217-324219(1) | OPEN LINE FROM BUS 324217 [4BROWN PLANT138.00] TO BUS 324219 [4BROWN T1 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8359 | -4.1127e-06 | -0.0003497
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 931 324217-324219(1) | OPEN LINE FROM BUS 324217 [4BROWN PLANT138.00] TO BUS 324219 [4BROWN T1 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 932 324217-324220(1) | OPEN LINE FROM BUS 324217 [4BROWN PLANT138.00] TO BUS 324220 [4BROWN T2 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -2.5034e-06 | -0.00034809
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 932 324217-324220(1) | OPEN LINE FROM BUS 324217 [4BROWN PLANT138.00] TO BUS 324220 [4BROWN T2 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 933 324217-324239(1) | OPEN LINE FROM BUS 324217 [4BROWN PLANT138.00] TO BUS 324239 [4DANVILE N T138.00] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8351 | -1.4722e-05 | -0.00036031
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 933 324217-324239(1) | OPEN LINE FROM BUS 324217 [4BROWN PLANT138.00] TO BUS 324239 [4DANVILE N T138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 934 324217-324248(1) | OPEN LINE FROM BUS 324217 [4BROWN PLANT138.00] TO BUS 324248 [4FAWKES KU 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93946 | 64.8226 | -0.00019628 | -0.00054187
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 934 324217-324248(1) | OPEN LINE FROM BUS 324217 [4BROWN PLANT138.00] TO BUS 324248 [4FAWKES KU 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 935 324218-324219(1) | OPEN LINE FROM BUS 324218 [4BROWN CT 138.00] TO BUS 324219 [4BROWN T1 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.2517e-06 | -0.00034684
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 935 324218-324219(1) | OPEN LINE FROM BUS 324218 [4BROWN CT 138.00] TO BUS 324219 [4BROWN T1 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 936 324218-324220(1) | OPEN LINE FROM BUS 324218 [4BROWN CT 138.00] TO BUS 324220 [4BROWN T2 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 2.563e-06 | -0.00034302
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 936 324218-324220(1) | OPEN LINE FROM BUS 324218 [4BROWN CT 138.00] TO BUS 324220 [4BROWN T2 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 937 324218-325957(1) | OPEN LINE FROM BUS 324218 [4BROWN CT 138.00] TO BUS 325957 [4BROWN N 1 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -7.7486e-07 | -0.00034636
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 937 324218-325957(1) | OPEN LINE FROM BUS 324218 [4BROWN CT 138.00] TO BUS 325957 [4BROWN N 1 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 938 324219-325957(1) | OPEN LINE FROM BUS 324219 [4BROWN T1 138.00] TO BUS 325957 [4BROWN N 1 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -6.5565e-07 | -0.00034624
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 938 324219-325957(1) | OPEN LINE FROM BUS 324219 [4BROWN T1 138.00] TO BUS 325957 [4BROWN N 1 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 939 324220-325956(1) | OPEN LINE FROM BUS 324220 [4BROWN T2 138.00] TO BUS 325956 [4BROWN N 2 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8365 | 4.8876e-06 | -0.0003407
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 939 324220-325956(1) | OPEN LINE FROM BUS 324220 [4BROWN T2 138.00] TO BUS 325956 [4BROWN N 2 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 940 324221-324225(1) | OPEN LINE FROM BUS 324221 [4BUTLER 138.00] TO BUS 324225 [4CARNTOWN TP138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 941 324222-324237(1) | OPEN LINE FROM BUS 324222 [4CAMPGROUND 138.00] TO BUS 324237 [4CANE RUN SW138.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8358 | -4.8876e-06 | -0.00035048
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 941 324222-324237(1) | OPEN LINE FROM BUS 324222 [4CAMPGROUND 138.00] TO BUS 324237 [4CANE RUN SW138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 942 324222-324295(1) | OPEN LINE FROM BUS 324222 [4CAMPGROUND 138.00] TO BUS 324295 [4PADDYS RUN 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8359 | -3.6359e-06 | -0.00034922
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 942 324222-324295(1) | OPEN LINE FROM BUS 324222 [4CAMPGROUND 138.00] TO BUS 324295 [4PADDYS RUN 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 943 324223-324294(1) | OPEN LINE FROM BUS 324223 [4CANAL 138.00] TO BUS 324294 [4PADDYS WEST138.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 3.9339e-06 | -0.00034165
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 943 324223-324294(1) | OPEN LINE FROM BUS 324223 [4CANAL 138.00] TO BUS 324294 [4PADDYS WEST138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 944 324223-324321(1) | OPEN LINE FROM BUS 324223 [4CANAL 138.00] TO BUS 324321 [4WATERSIDE 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8359 | -4.1127e-06 | -0.0003497
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 944 324223-324321(1) | OPEN LINE FROM BUS 324223 [4CANAL 138.00] TO BUS 324321 [4WATERSIDE 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 945 324223-324462(1) | OPEN LINE FROM BUS 324223 [4CANAL 138.00] TO BUS 324462 [2CANAL 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8366 | 6.7353e-06 | -0.00033885
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 945 324223-324462(1) | OPEN LINE FROM BUS 324223 [4CANAL 138.00] TO BUS 324462 [2CANAL 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 946 324225-324226(1) | OPEN LINE FROM BUS 324225 [4CARNTOWN TP138.00] TO BUS 324226 [4CARNTOWN 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 947 324225-324267(1) | OPEN LINE FROM BUS 324225 [4CARNTOWN TP138.00] TO BUS 324267 [4KENTON 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93863 | 64.7657 | -0.0010211 | -0.0013667
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 947 324225-324267(1) | OPEN LINE FROM BUS 324225 [4CARNTOWN TP138.00] TO BUS 324267 [4KENTON 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 948 324226-324463(1) | OPEN LINE FROM BUS 324226 [4CARNTOWN 138.00] TO BUS 324463 [2CARNTOWN 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 949 324227-324274(1) | OPEN LINE FROM BUS 324227 [4CARROLLTON 138.00] TO BUS 324274 [4LOCKPORT 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93958 | 64.8311 | -7.2598e-05 | -0.00041819
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 949 324227-324274(1) | OPEN LINE FROM BUS 324227 [4CARROLLTON 138.00] TO BUS 324274 [4LOCKPORT 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 950 324227-324466(1) | OPEN LINE FROM BUS 324227 [4CARROLLTON 138.00] TO BUS 324466 [2CARROLLTON 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93968 | 64.8376 | 2.11e-05 | -0.00032449
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 950 324227-324466(1) | OPEN LINE FROM BUS 324227 [4CARROLLTON 138.00] TO BUS 324466 [2CARROLLTON 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 951 324227-324466(2) | OPEN LINE FROM BUS 324227 [4CARROLLTON 138.00] TO BUS 324466 [2CARROLLTON 69.000] CKT 2 | 0.93965 | 64.8362 | 0.93967 | 64.837 | 1.2159e-05 | -0.00033343
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 951 324227-324466(2) | OPEN LINE FROM BUS 324227 [4CARROLLTON 138.00] TO BUS 324466 [2CARROLLTON 69.000] CKT 2 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 952 324227-326512(1) | OPEN LINE FROM BUS 324227 [4CARROLLTON 138.00] TO BUS 326512 [4AIRGAS 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93951 | 64.8259 | -0.00014865 | -0.00049424
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 952 324227-326512(1) | OPEN LINE FROM BUS 324227 [4CARROLLTON 138.00] TO BUS 326512 [4AIRGAS 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 953 324228-324281(1) | OPEN LINE FROM BUS 324228 [4CENTERFIELD138.00] TO BUS 324281 [4MIDDLETOWN 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -2.861e-06 | -0.00034845
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 953 324228-324281(1) | OPEN LINE FROM BUS 324228 [4CENTERFIELD138.00] TO BUS 324281 [4MIDDLETOWN 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 954 324228-324469(1) | OPEN LINE FROM BUS 324228 [4CENTERFIELD138.00] TO BUS 324469 [2CENTERFIELD69.000] CKT 1 | 0.93965 | 64.8362 | 0.9397 | 64.8393 | 4.5419e-05 | -0.00030017
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 954 324228-324469(1) | OPEN LINE FROM BUS 324228 [4CENTERFIELD138.00] TO BUS 324469 [2CENTERFIELD69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 955 324228-326520(1) | OPEN LINE FROM BUS 324228 [4CENTERFIELD138.00] TO BUS 326520 [4TRIMBLE TR9138.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8355 | -8.7619e-06 | -0.00035435
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 955 324228-326520(1) | OPEN LINE FROM BUS 324228 [4CENTERFIELD138.00] TO BUS 326520 [4TRIMBLE TR9138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 956 324229-324236(1) | OPEN LINE FROM BUS 324229 [4CLARK CO 138.00] TO BUS 324236 [4RICHMND NO 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93862 | 64.7647 | -0.001036 | -0.0013816
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 956 324229-324236(1) | OPEN LINE FROM BUS 324229 [4CLARK CO 138.00] TO BUS 324236 [4RICHMND NO 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 957 324229-324310(1) | OPEN LINE FROM BUS 324229 [4CLARK CO 138.00] TO BUS 324310 [4SPENCER RD 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93892 | 64.7857 | -0.00073087 | -0.0010765
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 957 324229-324310(1) | OPEN LINE FROM BUS 324229 [4CLARK CO 138.00] TO BUS 324310 [4SPENCER RD 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 958 324229-324472(1) | OPEN LINE FROM BUS 324229 [4CLARK CO 138.00] TO BUS 324472 [2CLARK CO 69.000] CKT 1 | 0.93965 | 64.8362 | 0.9396 | 64.8326 | -5.126e-05 | -0.00039685
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 958 324229-324472(1) | OPEN LINE FROM BUS 324229 [4CLARK CO 138.00] TO BUS 324472 [2CLARK CO 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 959 324230-324262(1) | OPEN LINE FROM BUS 324230 [4CLAYS MILL 138.00] TO BUS 324262 [4HIGBY MILL 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93934 | 64.8146 | -0.00031298 | -0.00065857
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 959 324230-324262(1) | OPEN LINE FROM BUS 324230 [4CLAYS MILL 138.00] TO BUS 324262 [4HIGBY MILL 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 960 324230-325957(1) | OPEN LINE FROM BUS 324230 [4CLAYS MILL 138.00] TO BUS 325957 [4BROWN N 1 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93925 | 64.808 | -0.00040734 | -0.00075293
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 960 324230-325957(1) | OPEN LINE FROM BUS 324230 [4CLAYS MILL 138.00] TO BUS 325957 [4BROWN N 1 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 961 324231-324256(1) | OPEN LINE FROM BUS 324231 [4CLOVERPORT 138.00] TO BUS 324256 [4GR RVR STL 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -2.7418e-06 | -0.00034833
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 961 324231-324256(1) | OPEN LINE FROM BUS 324231 [4CLOVERPORT 138.00] TO BUS 324256 [4GR RVR STL 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 962 324231-324260(1) | OPEN LINE FROM BUS 324231 [4CLOVERPORT 138.00] TO BUS 324260 [4HARDINSBURG138.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.1921e-07 | -0.00034571
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 962 324231-324260(1) | OPEN LINE FROM BUS 324231 [4CLOVERPORT 138.00] TO BUS 324260 [4HARDINSBURG138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 963 324231-325132(1) | OPEN LINE FROM BUS 324231 [4CLOVERPORT 138.00] TO BUS 325132 [4GREENSOL TP138.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8369 | 1.055e-05 | -0.00033504
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 963 324231-325132(1) | OPEN LINE FROM BUS 324231 [4CLOVERPORT 138.00] TO BUS 325132 [4GREENSOL TP138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 964 324232-326574(1) | OPEN LINE FROM BUS 324232 [4CANE RN 11A138.00] TO BUS 326574 [4CR11 TAP 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 7.1526e-07 | -0.00034487
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 964 324232-326574(1) | OPEN LINE FROM BUS 324232 [4CANE RN 11A138.00] TO BUS 326574 [4CR11 TAP 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 965 324236-324248(1) | OPEN LINE FROM BUS 324236 [4RICHMND NO 138.00] TO BUS 324248 [4FAWKES KU 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93854 | 64.759 | -0.0011176 | -0.0014632
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 965 324236-324248(1) | OPEN LINE FROM BUS 324236 [4RICHMND NO 138.00] TO BUS 324248 [4FAWKES KU 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 966 324237-324295(1) | OPEN LINE FROM BUS 324237 [4CANE RUN SW138.00] TO BUS 324295 [4PADDYS RUN 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8358 | -4.828e-06 | -0.00035042
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 966 324237-324295(1) | OPEN LINE FROM BUS 324237 [4CANE RUN SW138.00] TO BUS 324295 [4PADDYS RUN 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 967 324237-324488(1) | OPEN LINE FROM BUS 324237 [4CANE RUN SW138.00] TO BUS 324488 [2CANE RUN SW69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 7.1526e-07 | -0.00034487
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 967 324237-324488(1) | OPEN LINE FROM BUS 324237 [4CANE RUN SW138.00] TO BUS 324488 [2CANE RUN SW69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 968 324237-324488(2) | OPEN LINE FROM BUS 324237 [4CANE RUN SW138.00] TO BUS 324488 [2CANE RUN SW69.000] CKT 2 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 5.3644e-07 | -0.00034505
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 968 324237-324488(2) | OPEN LINE FROM BUS 324237 [4CANE RUN SW138.00] TO BUS 324488 [2CANE RUN SW69.000] CKT 2 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 969 324237-325096(22) | OPEN LINE FROM BUS 324237 [4CANE RUN SW138.00] TO BUS 325096 [4CANERN NGCC138.00] CKT 22 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -8.9407e-07 | -0.00034648
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 969 324237-325096(22) | OPEN LINE FROM BUS 324237 [4CANE RUN SW138.00] TO BUS 325096 [4CANERN NGCC138.00] CKT 22 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 970 324237-325096(24) | OPEN LINE FROM BUS 324237 [4CANE RUN SW138.00] TO BUS 325096 [4CANERN NGCC138.00] CKT 24 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -7.7486e-07 | -0.00034636
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 970 324237-325096(24) | OPEN LINE FROM BUS 324237 [4CANE RUN SW138.00] TO BUS 325096 [4CANERN NGCC138.00] CKT 24 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 971 324237-325096(25) | OPEN LINE FROM BUS 324237 [4CANE RUN SW138.00] TO BUS 325096 [4CANERN NGCC138.00] CKT 25 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -8.9407e-07 | -0.00034648
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 971 324237-325096(25) | OPEN LINE FROM BUS 324237 [4CANE RUN SW138.00] TO BUS 325096 [4CANERN NGCC138.00] CKT 25 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 972 324237-326565(23) | OPEN LINE FROM BUS 324237 [4CANE RUN SW138.00] TO BUS 326565 [4INTRNTL TAP138.00] CKT 23 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -7.7486e-07 | -0.00034636
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 972 324237-326565(23) | OPEN LINE FROM BUS 324237 [4CANE RUN SW138.00] TO BUS 326565 [4INTRNTL TAP138.00] CKT 23 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 973 324237-326574(21) | OPEN LINE FROM BUS 324237 [4CANE RUN SW138.00] TO BUS 326574 [4CR11 TAP 138.00] CKT 21 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -8.3447e-07 | -0.00034642
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 973 324237-326574(21) | OPEN LINE FROM BUS 324237 [4CANE RUN SW138.00] TO BUS 326574 [4CR11 TAP 138.00] CKT 21 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 974 324238-324239(1) | OPEN LINE FROM BUS 324238 [4DANVILLE N 138.00] TO BUS 324239 [4DANVILE N T138.00] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8351 | -1.5616e-05 | -0.0003612
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 974 324238-324239(1) | OPEN LINE FROM BUS 324238 [4DANVILLE N 138.00] TO BUS 324239 [4DANVILE N T138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 975 324238-324495(1) | OPEN LINE FROM BUS 324238 [4DANVILLE N 138.00] TO BUS 324495 [2DANVILLE N 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8351 | -1.4842e-05 | -0.00036043
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 975 324238-324495(1) | OPEN LINE FROM BUS 324238 [4DANVILLE N 138.00] TO BUS 324495 [2DANVILLE N 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 976 324239-325121(1) | OPEN LINE FROM BUS 324239 [4DANVILE N T138.00] TO BUS 325121 [4LOGAN TP 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.4901e-06 | -0.00034708
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 976 324239-325121(1) | OPEN LINE FROM BUS 324239 [4DANVILE N T138.00] TO BUS 325121 [4LOGAN TP 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 977 324240-324242(1) | OPEN LINE FROM BUS 324240 [4DAY-WALT TP138.00] TO BUS 324242 [4DOW CORN W 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93947 | 64.8237 | -0.00017989 | -0.00052547
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 977 324240-324242(1) | OPEN LINE FROM BUS 324240 [4DAY-WALT TP138.00] TO BUS 324242 [4DOW CORN W 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 978 324240-324287(1) | OPEN LINE FROM BUS 324240 [4DAY-WALT TP138.00] TO BUS 324287 [4NAS TAP 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93947 | 64.8231 | -0.00018865 | -0.00053424
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 978 324240-324287(1) | OPEN LINE FROM BUS 324240 [4DAY-WALT TP138.00] TO BUS 324287 [4NAS TAP 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 979 324241-324295(1) | OPEN LINE FROM BUS 324241 [4DIXIE 138.00] TO BUS 324295 [4PADDYS RUN 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8367 | 7.2718e-06 | -0.00033832
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 979 324241-324295(1) | OPEN LINE FROM BUS 324241 [4DIXIE 138.00] TO BUS 324295 [4PADDYS RUN 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 980 324242-326512(1) | OPEN LINE FROM BUS 324242 [4DOW CORN W 138.00] TO BUS 326512 [4AIRGAS 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93949 | 64.8251 | -0.00016016 | -0.00050575
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 980 324242-326512(1) | OPEN LINE FROM BUS 324242 [4DOW CORN W 138.00] TO BUS 326512 [4AIRGAS 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 981 324243-324518(1) | OPEN LINE FROM BUS 324243 [4ETHEL 138.00] TO BUS 324518 [2ETHEL 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.1921e-06 | -0.00034678
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 981 324243-324518(1) | OPEN LINE FROM BUS 324243 [4ETHEL 138.00] TO BUS 324518 [2ETHEL 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 982 324244-324261(1) | OPEN LINE FROM BUS 324244 [4ETOWN 138.00] TO BUS 324261 [4HARDIN CO 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8354 | -1.0312e-05 | -0.0003559
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 982 324244-324261(1) | OPEN LINE FROM BUS 324244 [4ETOWN 138.00] TO BUS 324261 [4HARDIN CO 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 983 324244-324288(1) | OPEN LINE FROM BUS 324244 [4ETOWN 138.00] TO BUS 324288 [4NELSON CO 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8349 | -1.8299e-05 | -0.00036389
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 983 324244-324288(1) | OPEN LINE FROM BUS 324244 [4ETOWN 138.00] TO BUS 324288 [4NELSON CO 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 984 324244-324519(1) | OPEN LINE FROM BUS 324244 [4ETOWN 138.00] TO BUS 324519 [2ETOWN KU 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -1.6689e-06 | -0.00034726
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 984 324244-324519(1) | OPEN LINE FROM BUS 324244 [4ETOWN 138.00] TO BUS 324519 [2ETOWN KU 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 985 324245-324246(1) | OPEN LINE FROM BUS 324245 [4FARMERS TAP138.00] TO BUS 324246 [4FARMERS 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93961 | 64.8333 | -4.1783e-05 | -0.00038737
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 985 324245-324246(1) | OPEN LINE FROM BUS 324245 [4FARMERS TAP138.00] TO BUS 324246 [4FARMERS 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 986 324245-324307(1) | OPEN LINE FROM BUS 324245 [4FARMERS TAP138.00] TO BUS 324307 [4SHARKEY TAP138.00] CKT 1 | 0.93965 | 64.8362 | 0.93951 | 64.8265 | -0.00014031 | -0.0004859
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 986 324245-324307(1) | OPEN LINE FROM BUS 324245 [4FARMERS TAP138.00] TO BUS 324307 [4SHARKEY TAP138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 987 324245-324310(1) | OPEN LINE FROM BUS 324245 [4FARMERS TAP138.00] TO BUS 324310 [4SPENCER RD 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93941 | 64.8193 | -0.00024354 | -0.00058913
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 987 324245-324310(1) | OPEN LINE FROM BUS 324245 [4FARMERS TAP138.00] TO BUS 324310 [4SPENCER RD 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 988 324246-324528(1) | OPEN LINE FROM BUS 324246 [4FARMERS 138.00] TO BUS 324528 [2FARMERS 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93962 | 64.834 | -3.1888e-05 | -0.00037748
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 988 324246-324528(1) | OPEN LINE FROM BUS 324246 [4FARMERS 138.00] TO BUS 324528 [2FARMERS 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 989 324247-324248(1) | OPEN LINE FROM BUS 324247 [4FAWKES TAP 138.00] TO BUS 324248 [4FAWKES KU 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -6.5565e-07 | -0.00034624
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 989 324247-324248(1) | OPEN LINE FROM BUS 324247 [4FAWKES TAP 138.00] TO BUS 324248 [4FAWKES KU 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 990 324247-324276(1) | OPEN LINE FROM BUS 324247 [4FAWKES TAP 138.00] TO BUS 324276 [4LAKE REBA T138.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 2.1458e-06 | -0.00034344
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 990 324247-324276(1) | OPEN LINE FROM BUS 324247 [4FAWKES TAP 138.00] TO BUS 324276 [4LAKE REBA T138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 991 324248-324530(1) | OPEN LINE FROM BUS 324248 [4FAWKES KU 138.00] TO BUS 324530 [2FAWKES 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93963 | 64.8345 | -2.4676e-05 | -0.00037026
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 991 324248-324530(1) | OPEN LINE FROM BUS 324248 [4FAWKES KU 138.00] TO BUS 324530 [2FAWKES 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 992 324248-324530(2) | OPEN LINE FROM BUS 324248 [4FAWKES KU 138.00] TO BUS 324530 [2FAWKES 69.000] CKT 2 | 0.93965 | 64.8362 | 0.93962 | 64.834 | -3.0637e-05 | -0.00037622
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 992 324248-324530(2) | OPEN LINE FROM BUS 324248 [4FAWKES KU 138.00] TO BUS 324530 [2FAWKES 69.000] CKT 2 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 993 324249-324257(1) | OPEN LINE FROM BUS 324249 [4FERN VALLEY138.00] TO BUS 324257 [4GRADE LANE 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 4.2319e-06 | -0.00034136
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 993 324249-324257(1) | OPEN LINE FROM BUS 324249 [4FERN VALLEY138.00] TO BUS 324257 [4GRADE LANE 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 994 324249-324292(1) | OPEN LINE FROM BUS 324249 [4FERN VALLEY138.00] TO BUS 324292 [4OKOLONA 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 1.1921e-07 | -0.00034547
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 994 324249-324292(1) | OPEN LINE FROM BUS 324249 [4FERN VALLEY138.00] TO BUS 324292 [4OKOLONA 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 995 324249-324322(1) | OPEN LINE FROM BUS 324249 [4FERN VALLEY138.00] TO BUS 324322 [4WATTERSON 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -1.6093e-06 | -0.0003472
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 995 324249-324322(1) | OPEN LINE FROM BUS 324249 [4FERN VALLEY138.00] TO BUS 324322 [4WATTERSON 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 996 324249-324532(1) | OPEN LINE FROM BUS 324249 [4FERN VALLEY138.00] TO BUS 324532 [2FERN VALLEY69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.1921e-07 | -0.00034571
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 996 324249-324532(1) | OPEN LINE FROM BUS 324249 [4FERN VALLEY138.00] TO BUS 324532 [2FERN VALLEY69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 997 324249-324532(2) | OPEN LINE FROM BUS 324249 [4FERN VALLEY138.00] TO BUS 324532 [2FERN VALLEY69.000] CKT 2 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.1921e-07 | -0.00034571
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 997 324249-324532(2) | OPEN LINE FROM BUS 324249 [4FERN VALLEY138.00] TO BUS 324532 [2FERN VALLEY69.000] CKT 2 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 998 324250-324306(1) | OPEN LINE FROM BUS 324250 [4E FRANKFORT138.00] TO BUS 324306 [4SHADRACK 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93961 | 64.8328 | -4.8459e-05 | -0.00039405
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 998 324250-324306(1) | OPEN LINE FROM BUS 324250 [4E FRANKFORT138.00] TO BUS 324306 [4SHADRACK 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 999 324250-324315(1) | OPEN LINE FROM BUS 324250 [4E FRANKFORT138.00] TO BUS 324315 [4TYRONE 138.00] CKT 1 | 0.93965 | 64.8362 | 0.9393 | 64.812 | -0.00035053 | -0.00069612
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 999 324250-324315(1) | OPEN LINE FROM BUS 324250 [4E FRANKFORT138.00] TO BUS 324315 [4TYRONE 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1000 324250-324535(1) | OPEN LINE FROM BUS 324250 [4E FRANKFORT138.00] TO BUS 324535 [2E FRANKFORT69.000] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8348 | -1.9372e-05 | -0.00036496
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1000 324250-324535(1) | OPEN LINE FROM BUS 324250 [4E FRANKFORT138.00] TO BUS 324535 [2E FRANKFORT69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1001 324250-324535(2) | OPEN LINE FROM BUS 324250 [4E FRANKFORT138.00] TO BUS 324535 [2E FRANKFORT69.000] CKT 2 | 0.93965 | 64.8362 | 0.93964 | 64.8349 | -1.806e-05 | -0.00036365
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1001 324250-324535(2) | OPEN LINE FROM BUS 324250 [4E FRANKFORT138.00] TO BUS 324535 [2E FRANKFORT69.000] CKT 2 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1002 324251-324254(1) | OPEN LINE FROM BUS 324251 [4FLEMNB KU T138.00] TO BUS 324254 [4GODDARD KU 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1003 324251-324323(1) | OPEN LINE FROM BUS 324251 [4FLEMNB KU T138.00] TO BUS 324323 [4WEDONIA 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1004 324252-324455(1) | OPEN LINE FROM BUS 324252 [2SCHOLLS 69.000] TO BUS 324455 [2BROMLEY 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93969 | 64.8386 | 3.5226e-05 | -0.00031036
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1004 324252-324455(1) | OPEN LINE FROM BUS 324252 [2SCHOLLS 69.000] TO BUS 324455 [2BROMLEY 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1005 324253-324287(1) | OPEN LINE FROM BUS 324253 [4GHENT 138.00] TO BUS 324287 [4NAS TAP 138.00] CKT 1 | 0.93965 | 64.8362 | 0.94 | 64.8597 | 0.00034106 | -4.53e-06
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1005 324253-324287(1) | OPEN LINE FROM BUS 324253 [4GHENT 138.00] TO BUS 324287 [4NAS TAP 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1006 324253-324290(1) | OPEN LINE FROM BUS 324253 [4GHENT 138.00] TO BUS 324290 [4OWEN CO TAP138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1007 324253-324831(1) | OPEN LINE FROM BUS 324253 [4GHENT 138.00] TO BUS 324831 [4WHITE SULPH138.00] CKT 1 | 0.93965 | 64.8362 | 0.93938 | 64.817 | -0.00027704 | -0.00062263
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1007 324253-324831(1) | OPEN LINE FROM BUS 324253 [4GHENT 138.00] TO BUS 324831 [4WHITE SULPH138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1008 324254-324302(1) | OPEN LINE FROM BUS 324254 [4GODDARD KU 138.00] TO BUS 324302 [4RODBURN 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1009 324255-324291(1) | OPEN LINE FROM BUS 324255 [4GREEN RIVER138.00] TO BUS 324291 [4OHIO COUNTY138.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 4.7684e-07 | -0.00034511
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1009 324255-324291(1) | OPEN LINE FROM BUS 324255 [4GREEN RIVER138.00] TO BUS 324291 [4OHIO COUNTY138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1010 324255-324550(1) | OPEN LINE FROM BUS 324255 [4GREEN RIVER138.00] TO BUS 324550 [2GREEN RIVER69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -5.3644e-07 | -0.00034612
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1010 324255-324550(1) | OPEN LINE FROM BUS 324255 [4GREEN RIVER138.00] TO BUS 324550 [2GREEN RIVER69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1011 324255-324550(2) | OPEN LINE FROM BUS 324255 [4GREEN RIVER138.00] TO BUS 324550 [2GREEN RIVER69.000] CKT 2 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -5.3644e-07 | -0.00034612
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1011 324255-324550(2) | OPEN LINE FROM BUS 324255 [4GREEN RIVER138.00] TO BUS 324550 [2GREEN RIVER69.000] CKT 2 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1012 324255-325015(1) | OPEN LINE FROM BUS 324255 [4GREEN RIVER138.00] TO BUS 325015 [4SMITH TAP 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 3.3975e-06 | -0.00034219
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1012 324255-325015(1) | OPEN LINE FROM BUS 324255 [4GREEN RIVER138.00] TO BUS 325015 [4SMITH TAP 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1013 324256-324551(1) | OPEN LINE FROM BUS 324256 [4GR RVR STL 138.00] TO BUS 324551 [2GR RVR STL 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.7881e-07 | -0.00034577
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1013 324256-324551(1) | OPEN LINE FROM BUS 324256 [4GR RVR STL 138.00] TO BUS 324551 [2GR RVR STL 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1014 324256-325015(1) | OPEN LINE FROM BUS 324256 [4GR RVR STL 138.00] TO BUS 325015 [4SMITH TAP 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 1.1921e-07 | -0.00034547
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1014 324256-325015(1) | OPEN LINE FROM BUS 324256 [4GR RVR STL 138.00] TO BUS 325015 [4SMITH TAP 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1015 324258-324264(1) | OPEN LINE FROM BUS 324258 [4HAEFLING 138.00] TO BUS 324264 [4IBM NORTHTP138.00] CKT 1 | 0.93965 | 64.8362 | 0.93951 | 64.8262 | -0.00014395 | -0.00048953
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1015 324258-324264(1) | OPEN LINE FROM BUS 324258 [4HAEFLING 138.00] TO BUS 324264 [4IBM NORTHTP138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1016 324258-324317(1) | OPEN LINE FROM BUS 324258 [4HAEFLING 138.00] TO BUS 324317 [4VILEY ROAD 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93936 | 64.8157 | -0.00029606 | -0.00064164
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1016 324258-324317(1) | OPEN LINE FROM BUS 324258 [4HAEFLING 138.00] TO BUS 324317 [4VILEY ROAD 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1017 324258-324335(1) | OPEN LINE FROM BUS 324258 [4HAEFLING 138.00] TO BUS 324335 [4INNOVATION 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93933 | 64.814 | -0.00032151 | -0.0006671
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1017 324258-324335(1) | OPEN LINE FROM BUS 324258 [4HAEFLING 138.00] TO BUS 324335 [4INNOVATION 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1018 324258-324558(1) | OPEN LINE FROM BUS 324258 [4HAEFLING 138.00] TO BUS 324558 [2HAEFLING 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93958 | 64.831 | -7.4267e-05 | -0.00041986
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1018 324258-324558(1) | OPEN LINE FROM BUS 324258 [4HAEFLING 138.00] TO BUS 324558 [2HAEFLING 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1019 324258-325100(1) | OPEN LINE FROM BUS 324258 [4HAEFLING 138.00] TO BUS 325100 [4W LEX R1 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93928 | 64.8104 | -0.00037372 | -0.00071931
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1020 324259-324278(1) | OPEN LINE FROM BUS 324259 [4HANCOCK 138.00] TO BUS 324278 [4MAGAZINE 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 3.0994e-06 | -0.00034249
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1020 324259-324278(1) | OPEN LINE FROM BUS 324259 [4HANCOCK 138.00] TO BUS 324278 [4MAGAZINE 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1021 324259-324561(1) | OPEN LINE FROM BUS 324259 [4HANCOCK 138.00] TO BUS 324561 [2HANCOCK 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 3.159e-06 | -0.00034243
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1021 324259-324561(1) | OPEN LINE FROM BUS 324259 [4HANCOCK 138.00] TO BUS 324561 [2HANCOCK 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1022 324260-325055(1) | OPEN LINE FROM BUS 324260 [4HARDINSBURG138.00] TO BUS 325055 [4RHUDES TP 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 1.3113e-06 | -0.00034428
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1022 324260-325055(1) | OPEN LINE FROM BUS 324260 [4HARDINSBURG138.00] TO BUS 325055 [4RHUDES TP 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1023 324261-324303(1) | OPEN LINE FROM BUS 324261 [4HARDIN CO 138.00] TO BUS 324303 [4ROGERSVILLE138.00] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8372 | 1.4663e-05 | -0.00033092
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1023 324261-324303(1) | OPEN LINE FROM BUS 324261 [4HARDIN CO 138.00] TO BUS 324303 [4ROGERSVILLE138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1024 324261-324563(1) | OPEN LINE FROM BUS 324261 [4HARDIN CO 138.00] TO BUS 324563 [2HARDIN CO 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -2.0862e-06 | -0.00034767
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1024 324261-324563(1) | OPEN LINE FROM BUS 324261 [4HARDIN CO 138.00] TO BUS 324563 [2HARDIN CO 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1025 324261-324563(2) | OPEN LINE FROM BUS 324261 [4HARDIN CO 138.00] TO BUS 324563 [2HARDIN CO 69.000] CKT 2 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -1.9073e-06 | -0.0003475
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1025 324261-324563(2) | OPEN LINE FROM BUS 324261 [4HARDIN CO 138.00] TO BUS 324563 [2HARDIN CO 69.000] CKT 2 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1026 324262-324269(1) | OPEN LINE FROM BUS 324262 [4HIGBY MILL 138.00] TO BUS 324269 [4LANSDOWNE 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93944 | 64.8215 | -0.00021249 | -0.00055808
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1026 324262-324269(1) | OPEN LINE FROM BUS 324262 [4HIGBY MILL 138.00] TO BUS 324269 [4LANSDOWNE 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1027 324262-324333(1) | OPEN LINE FROM BUS 324262 [4HIGBY MILL 138.00] TO BUS 324333 [4BROWN N 1-R138.00] CKT 1 | 0.93965 | 64.8362 | 0.93915 | 64.8015 | -0.00050205 | -0.00084764
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1027 324262-324333(1) | OPEN LINE FROM BUS 324262 [4HIGBY MILL 138.00] TO BUS 324333 [4BROWN N 1-R138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1028 324262-324568(1) | OPEN LINE FROM BUS 324262 [4HIGBY MILL 138.00] TO BUS 324568 [2HIGBY 618 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93958 | 64.831 | -7.4327e-05 | -0.00041991
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1028 324262-324568(1) | OPEN LINE FROM BUS 324262 [4HIGBY MILL 138.00] TO BUS 324568 [2HIGBY 618 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1029 324262-324569(1) | OPEN LINE FROM BUS 324262 [4HIGBY MILL 138.00] TO BUS 324569 [2HIGBY 608 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93957 | 64.8301 | -8.8215e-05 | -0.0004338
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1030 324262-324569(2) | OPEN LINE FROM BUS 324262 [4HIGBY MILL 138.00] TO BUS 324569 [2HIGBY 608 69.000] CKT 2 | 0.93965 | 64.8362 | 0.93958 | 64.8311 | -7.2598e-05 | -0.00041819
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1030 324262-324569(2) | OPEN LINE FROM BUS 324262 [4HIGBY MILL 138.00] TO BUS 324569 [2HIGBY 608 69.000] CKT 2 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1031 324262-325089(Z1) | OPEN LINE FROM BUS 324262 [4HIGBY MILL 138.00] TO BUS 325089 [4HIGBY MILL2138.00] CKT Z1 | 0.93965 | 64.8362 | 0.93973 | 64.841 | 7.0691e-05 | -0.0002749
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1031 324262-325089(Z1) | OPEN LINE FROM BUS 324262 [4HIGBY MILL 138.00] TO BUS 325089 [4HIGBY MILL2138.00] CKT Z1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1032 324263-324297(1) | OPEN LINE FROM BUS 324263 [4HURSTBORNE 138.00] TO BUS 324297 [4PLAINVIEW 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8356 | -7.8678e-06 | -0.00035346
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1032 324263-324297(1) | OPEN LINE FROM BUS 324263 [4HURSTBORNE 138.00] TO BUS 324297 [4PLAINVIEW 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1033 324264-324275(1) | OPEN LINE FROM BUS 324264 [4IBM NORTHTP138.00] TO BUS 324275 [4LOUDON AVE 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93952 | 64.8272 | -0.00013018 | -0.00047576
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1033 324264-324275(1) | OPEN LINE FROM BUS 324264 [4IBM NORTHTP138.00] TO BUS 324275 [4LOUDON AVE 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1034 324264-326548(1) | OPEN LINE FROM BUS 324264 [4IBM NORTHTP138.00] TO BUS 326548 [4IBM NORTH 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93968 | 64.8379 | 2.5451e-05 | -0.00032014
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1034 324264-326548(1) | OPEN LINE FROM BUS 324264 [4IBM NORTHTP138.00] TO BUS 326548 [4IBM NORTH 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1035 324265-324289(1) | OPEN LINE FROM BUS 324265 [4JEFFRSONV T138.00] TO BUS 324289 [4NORTHSIDE 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8359 | -3.5763e-06 | -0.00034916
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1035 324265-324289(1) | OPEN LINE FROM BUS 324265 [4JEFFRSONV T138.00] TO BUS 324289 [4NORTHSIDE 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1036 324267-324323(1) | OPEN LINE FROM BUS 324267 [4KENTON 138.00] TO BUS 324323 [4WEDONIA 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1037 324267-324589(1) | OPEN LINE FROM BUS 324267 [4KENTON 138.00] TO BUS 324589 [2KENTON 688 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1038 324267-324882(1) | OPEN LINE FROM BUS 324267 [4KENTON 138.00] TO BUS 324882 [2KENTON 698 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93982 | 64.8475 | 0.00016499 | -0.0001806
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1038 324267-324882(1) | OPEN LINE FROM BUS 324267 [4KENTON 138.00] TO BUS 324882 [2KENTON 698 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1039 324268-324284(1) | OPEN LINE FROM BUS 324268 [4KNOB CREEK 138.00] TO BUS 324284 [4MILL CREEK 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 3.9935e-06 | -0.00034159
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1039 324268-324284(1) | OPEN LINE FROM BUS 324268 [4KNOB CREEK 138.00] TO BUS 324284 [4MILL CREEK 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1040 324268-324300(1) | OPEN LINE FROM BUS 324268 [4KNOB CREEK 138.00] TO BUS 324300 [4POND CREEK 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8365 | 5.1856e-06 | -0.0003404
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1040 324268-324300(1) | OPEN LINE FROM BUS 324268 [4KNOB CREEK 138.00] TO BUS 324300 [4POND CREEK 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1041 324269-324601(1) | OPEN LINE FROM BUS 324269 [4LANSDOWNE 138.00] TO BUS 324601 [2LANSDOWNE 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93945 | 64.8221 | -0.00020337 | -0.00054896
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1041 324269-324601(1) | OPEN LINE FROM BUS 324269 [4LANSDOWNE 138.00] TO BUS 324601 [2LANSDOWNE 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1042 324270-324271(1) | OPEN LINE FROM BUS 324270 [4LEBANON WES138.00] TO BUS 324271 [4LEBANON 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -1.6689e-06 | -0.00034726
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1042 324270-324271(1) | OPEN LINE FROM BUS 324270 [4LEBANON WES138.00] TO BUS 324271 [4LEBANON 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 1.1921e-07 | 1.1921e-07
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1043 324271-324606(1) | OPEN LINE FROM BUS 324271 [4LEBANON 138.00] TO BUS 324606 [2LEBANON 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 1.0133e-06 | -0.00034457
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1043 324271-324606(1) | OPEN LINE FROM BUS 324271 [4LEBANON 138.00] TO BUS 324606 [2LEBANON 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1044 324271-324606(2) | OPEN LINE FROM BUS 324271 [4LEBANON 138.00] TO BUS 324606 [2LEBANON 69.000] CKT 2 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 2.9802e-07 | -0.00034529
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1044 324271-324606(2) | OPEN LINE FROM BUS 324271 [4LEBANON 138.00] TO BUS 324606 [2LEBANON 69.000] CKT 2 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1045 324271-325121(1) | OPEN LINE FROM BUS 324271 [4LEBANON 138.00] TO BUS 325121 [4LOGAN TP 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.3113e-06 | -0.0003469
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1045 324271-325121(1) | OPEN LINE FROM BUS 324271 [4LEBANON 138.00] TO BUS 325121 [4LOGAN TP 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1046 324272-324308(1) | OPEN LINE FROM BUS 324272 [4LEITCHFIELD138.00] TO BUS 324308 [4SHREWSBURY 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 8.9407e-07 | -0.00034469
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1046 324272-324308(1) | OPEN LINE FROM BUS 324272 [4LEITCHFIELD138.00] TO BUS 324308 [4SHREWSBURY 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1047 324272-324609(1) | OPEN LINE FROM BUS 324272 [4LEITCHFIELD138.00] TO BUS 324609 [2LEITCHFIELD69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 1.1325e-06 | -0.00034446
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1047 324272-324609(1) | OPEN LINE FROM BUS 324272 [4LEITCHFIELD138.00] TO BUS 324609 [2LEITCHFIELD69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1048 324273-326559(Z1) | OPEN LINE FROM BUS 324273 [4LAKE REBA 138.00] TO BUS 326559 [4BGAD TAP 138.00] CKT Z1 | 0.93965 | 64.8362 | 0.9395 | 64.8257 | -0.0001508 | -0.00049639
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1048 324273-326559(Z1) | OPEN LINE FROM BUS 324273 [4LAKE REBA 138.00] TO BUS 326559 [4BGAD TAP 138.00] CKT Z1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1049 324274-324306(1) | OPEN LINE FROM BUS 324274 [4LOCKPORT 138.00] TO BUS 324306 [4SHADRACK 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93959 | 64.832 | -6.0678e-05 | -0.00040627
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1049 324274-324306(1) | OPEN LINE FROM BUS 324274 [4LOCKPORT 138.00] TO BUS 324306 [4SHADRACK 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1050 324275-324618(1) | OPEN LINE FROM BUS 324275 [4LOUDON AVE 138.00] TO BUS 324618 [2LOUDON 628 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8348 | -1.9312e-05 | -0.0003649
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1050 324275-324618(1) | OPEN LINE FROM BUS 324275 [4LOUDON AVE 138.00] TO BUS 324618 [2LOUDON 628 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1051 324276-326559(1) | OPEN LINE FROM BUS 324276 [4LAKE REBA T138.00] TO BUS 326559 [4BGAD TAP 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93948 | 64.8243 | -0.00017202 | -0.00051761
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1051 324276-326559(1) | OPEN LINE FROM BUS 324276 [4LAKE REBA T138.00] TO BUS 326559 [4BGAD TAP 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1052 324277-324281(1) | OPEN LINE FROM BUS 324277 [4LYNDON SO 138.00] TO BUS 324281 [4MIDDLETOWN 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8355 | -9.5367e-06 | -0.00035512
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1052 324277-324281(1) | OPEN LINE FROM BUS 324277 [4LYNDON SO 138.00] TO BUS 324281 [4MIDDLETOWN 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1053 324277-324622(1) | OPEN LINE FROM BUS 324277 [4LYNDON SO 138.00] TO BUS 324622 [2LYNDON SO 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 0 | -0.00034559
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1053 324277-324622(1) | OPEN LINE FROM BUS 324277 [4LYNDON SO 138.00] TO BUS 324622 [2LYNDON SO 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1054 324278-324321(1) | OPEN LINE FROM BUS 324278 [4MAGAZINE 138.00] TO BUS 324321 [4WATERSIDE 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 1.0133e-06 | -0.00034457
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1054 324278-324321(1) | OPEN LINE FROM BUS 324278 [4MAGAZINE 138.00] TO BUS 324321 [4WATERSIDE 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1055 324279-324284(1) | OPEN LINE FROM BUS 324279 [4MANSLICK 138.00] TO BUS 324284 [4MILL CREEK 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 6.5565e-07 | -0.00034493
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1055 324279-324284(1) | OPEN LINE FROM BUS 324279 [4MANSLICK 138.00] TO BUS 324284 [4MILL CREEK 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1056 324281-324282(1) | OPEN LINE FROM BUS 324281 [4MIDDLETOWN 138.00] TO BUS 324282 [4MIDDLETWN-R138.00] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.835 | -1.6868e-05 | -0.00036246
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1056 324281-324282(1) | OPEN LINE FROM BUS 324281 [4MIDDLETOWN 138.00] TO BUS 324282 [4MIDDLETWN-R138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1057 324281-324364(1) | OPEN LINE FROM BUS 324281 [4MIDDLETOWN 138.00] TO BUS 324364 [4OLD HENRY 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8358 | -5.0664e-06 | -0.00035065
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1057 324281-324364(1) | OPEN LINE FROM BUS 324281 [4MIDDLETOWN 138.00] TO BUS 324364 [4OLD HENRY 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1058 324281-324637(1) | OPEN LINE FROM BUS 324281 [4MIDDLETOWN 138.00] TO BUS 324637 [2MIDDLETOWN 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | -5.9605e-08 | -0.00034565
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1058 324281-324637(1) | OPEN LINE FROM BUS 324281 [4MIDDLETOWN 138.00] TO BUS 324637 [2MIDDLETOWN 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1059 324281-324637(2) | OPEN LINE FROM BUS 324281 [4MIDDLETOWN 138.00] TO BUS 324637 [2MIDDLETOWN 69.000] CKT 2 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 0 | -0.00034559
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1059 324281-324637(2) | OPEN LINE FROM BUS 324281 [4MIDDLETOWN 138.00] TO BUS 324637 [2MIDDLETOWN 69.000] CKT 2 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1060 324281-324637(6) | OPEN LINE FROM BUS 324281 [4MIDDLETOWN 138.00] TO BUS 324637 [2MIDDLETOWN 69.000] CKT 6 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 2.3842e-07 | -0.00034535
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1060 324281-324637(6) | OPEN LINE FROM BUS 324281 [4MIDDLETOWN 138.00] TO BUS 324637 [2MIDDLETOWN 69.000] CKT 6 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1061 324281-325042(1) | OPEN LINE FROM BUS 324281 [4MIDDLETOWN 138.00] TO BUS 325042 [4JEFERSONTWN138.00] CKT 1 | 0.93965 | 64.8362 | 0.93963 | 64.8346 | -2.259e-05 | -0.00036818
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1061 324281-325042(1) | OPEN LINE FROM BUS 324281 [4MIDDLETOWN 138.00] TO BUS 325042 [4JEFERSONTWN138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1062 324282-324298(1) | OPEN LINE FROM BUS 324282 [4MIDDLETWN-R138.00] TO BUS 324298 [4PLAINVIEW T138.00] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.835 | -1.7047e-05 | -0.00036263
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1062 324282-324298(1) | OPEN LINE FROM BUS 324282 [4MIDDLETWN-R138.00] TO BUS 324298 [4PLAINVIEW T138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1063 324283-324320(1) | OPEN LINE FROM BUS 324283 [4MIDWAY 138.00] TO BUS 324320 [4W LEXINGTON138.00] CKT 1 | 0.93965 | 64.8362 | 0.93948 | 64.8239 | -0.0001775 | -0.00052309
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1063 324283-324320(1) | OPEN LINE FROM BUS 324283 [4MIDWAY 138.00] TO BUS 324320 [4W LEXINGTON138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1064 324283-324831(1) | OPEN LINE FROM BUS 324283 [4MIDWAY 138.00] TO BUS 324831 [4WHITE SULPH138.00] CKT 1 | 0.93965 | 64.8362 | 0.93945 | 64.8223 | -0.00020015 | -0.00054574
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1064 324283-324831(1) | OPEN LINE FROM BUS 324283 [4MIDWAY 138.00] TO BUS 324831 [4WHITE SULPH138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1065 324284-324640(7) | OPEN LINE FROM BUS 324284 [4MILL CREEK 138.00] TO BUS 324640 [2MILL CREEK 69.000] CKT 7 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -2.3842e-07 | -0.00034583
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1065 324284-324640(7) | OPEN LINE FROM BUS 324284 [4MILL CREEK 138.00] TO BUS 324640 [2MILL CREEK 69.000] CKT 7 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1066 324284-324640(8) | OPEN LINE FROM BUS 324284 [4MILL CREEK 138.00] TO BUS 324640 [2MILL CREEK 69.000] CKT 8 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -3.5763e-07 | -0.00034595
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1066 324284-324640(8) | OPEN LINE FROM BUS 324284 [4MILL CREEK 138.00] TO BUS 324640 [2MILL CREEK 69.000] CKT 8 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1067 324284-325088(1) | OPEN LINE FROM BUS 324284 [4MILL CREEK 138.00] TO BUS 325088 [4MIL CK YARD138.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8366 | 6.7353e-06 | -0.00033885
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1067 324284-325088(1) | OPEN LINE FROM BUS 324284 [4MILL CREEK 138.00] TO BUS 325088 [4MIL CK YARD138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 1.1921e-07 | 1.1921e-07
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1068 324285-324292(1) | OPEN LINE FROM BUS 324285 [4MUD LANE 138.00] TO BUS 324292 [4OKOLONA 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 1.1921e-07 | -0.00034547
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1068 324285-324292(1) | OPEN LINE FROM BUS 324285 [4MUD LANE 138.00] TO BUS 324292 [4OKOLONA 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1069 324285-324651(1) | OPEN LINE FROM BUS 324285 [4MUD LANE 138.00] TO BUS 324651 [2MUD LANE 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8357 | -6.1989e-06 | -0.00035179
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1069 324285-324651(1) | OPEN LINE FROM BUS 324285 [4MUD LANE 138.00] TO BUS 324651 [2MUD LANE 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1070 324286-324287(1) | OPEN LINE FROM BUS 324286 [4NAS 138.00] TO BUS 324287 [4NAS TAP 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93993 | 64.8553 | 0.00027704 | -6.8545e-05
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1070 324286-324287(1) | OPEN LINE FROM BUS 324286 [4NAS 138.00] TO BUS 324287 [4NAS TAP 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1071 324289-325013(1) | OPEN LINE FROM BUS 324289 [4NORTHSIDE 138.00] TO BUS 325013 [4CLIFTY TAP1138.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8367 | 8.4639e-06 | -0.00033712
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1071 324289-325013(1) | OPEN LINE FROM BUS 324289 [4NORTHSIDE 138.00] TO BUS 325013 [4CLIFTY TAP1138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1072 324290-324305(1) | OPEN LINE FROM BUS 324290 [4OWEN CO TAP138.00] TO BUS 324305 [4SCOTT CO 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93957 | 64.8306 | -8.1062e-05 | -0.00042665
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1072 324290-324305(1) | OPEN LINE FROM BUS 324290 [4OWEN CO TAP138.00] TO BUS 324305 [4SCOTT CO 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1073 324291-324667(1) | OPEN LINE FROM BUS 324291 [4OHIO COUNTY138.00] TO BUS 324667 [2OHIO COUNTY69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.4305e-06 | -0.00034702
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1073 324291-324667(1) | OPEN LINE FROM BUS 324291 [4OHIO COUNTY138.00] TO BUS 324667 [2OHIO COUNTY69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1074 324294-324295(1) | OPEN LINE FROM BUS 324294 [4PADDYS WEST138.00] TO BUS 324295 [4PADDYS RUN 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 1.6093e-06 | -0.00034398
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1074 324294-324295(1) | OPEN LINE FROM BUS 324294 [4PADDYS WEST138.00] TO BUS 324295 [4PADDYS RUN 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1075 324296-324320(1) | OPEN LINE FROM BUS 324296 [4PISGAH 138.00] TO BUS 324320 [4W LEXINGTON138.00] CKT 1 | 0.93965 | 64.8362 | 0.9397 | 64.8391 | 4.2439e-05 | -0.00030315
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1075 324296-324320(1) | OPEN LINE FROM BUS 324296 [4PISGAH 138.00] TO BUS 324320 [4W LEXINGTON138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1076 324296-324687(1) | OPEN LINE FROM BUS 324296 [4PISGAH 138.00] TO BUS 324687 [2PISGAH 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93933 | 64.8138 | -0.00032365 | -0.00066924
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1076 324296-324687(1) | OPEN LINE FROM BUS 324296 [4PISGAH 138.00] TO BUS 324687 [2PISGAH 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1077 324296-325857(1) | OPEN LINE FROM BUS 324296 [4PISGAH 138.00] TO BUS 325857 [4BROWN N TIE138.00] CKT 1 | 0.93965 | 64.8362 | 0.93952 | 64.8268 | -0.0001362 | -0.00048178
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1077 324296-325857(1) | OPEN LINE FROM BUS 324296 [4PISGAH 138.00] TO BUS 325857 [4BROWN N TIE138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1078 324297-324298(1) | OPEN LINE FROM BUS 324297 [4PLAINVIEW 138.00] TO BUS 324298 [4PLAINVIEW T138.00] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8354 | -1.1444e-05 | -0.00035703
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1078 324297-324298(1) | OPEN LINE FROM BUS 324297 [4PLAINVIEW 138.00] TO BUS 324298 [4PLAINVIEW T138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1079 324300-324311(1) | OPEN LINE FROM BUS 324300 [4POND CREEK 138.00] TO BUS 324311 [4TIP TOP 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8366 | 5.9605e-06 | -0.00033963
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1079 324300-324311(1) | OPEN LINE FROM BUS 324300 [4POND CREEK 138.00] TO BUS 324311 [4TIP TOP 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1080 324301-325089(1) | OPEN LINE FROM BUS 324301 [4REYNOLDS 138.00] TO BUS 325089 [4HIGBY MILL2138.00] CKT 1 | 0.93965 | 64.8362 | 0.93956 | 64.8296 | -9.5367e-05 | -0.00044096
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1080 324301-325089(1) | OPEN LINE FROM BUS 324301 [4REYNOLDS 138.00] TO BUS 325089 [4HIGBY MILL2138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1081 324302-324307(1) | OPEN LINE FROM BUS 324302 [4RODBURN 138.00] TO BUS 324307 [4SHARKEY TAP138.00] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8352 | -1.353e-05 | -0.00035912
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1081 324302-324307(1) | OPEN LINE FROM BUS 324302 [4RODBURN 138.00] TO BUS 324307 [4SHARKEY TAP138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1082 324303-324708(1) | OPEN LINE FROM BUS 324303 [4ROGERSVILLE138.00] TO BUS 324708 [2ROGERSVILLE69.000] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8372 | 1.5616e-05 | -0.00032997
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1082 324303-324708(1) | OPEN LINE FROM BUS 324303 [4ROGERSVILLE138.00] TO BUS 324708 [2ROGERSVILLE69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1083 324304-324762(1) | OPEN LINE FROM BUS 324304 [2VERSAILLE W69.000] TO BUS 324762 [2VERSAIL W T69.000] CKT 1 | 0.93965 | 64.8362 | 0.9397 | 64.8395 | 4.8637e-05 | -0.00029695
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1083 324304-324762(1) | OPEN LINE FROM BUS 324304 [2VERSAILLE W69.000] TO BUS 324762 [2VERSAIL W T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1084 324305-324951(1) | OPEN LINE FROM BUS 324305 [4SCOTT CO 138.00] TO BUS 324951 [2SCOTT CO 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93983 | 64.848 | 0.0001713 | -0.00017428
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1084 324305-324951(1) | OPEN LINE FROM BUS 324305 [4SCOTT CO 138.00] TO BUS 324951 [2SCOTT CO 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1085 324305-324991(1) | OPEN LINE FROM BUS 324305 [4SCOTT CO 138.00] TO BUS 324991 [4ROGERS GAP 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8359 | -3.2187e-06 | -0.00034881
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1085 324305-324991(1) | OPEN LINE FROM BUS 324305 [4SCOTT CO 138.00] TO BUS 324991 [4ROGERS GAP 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1086 324307-326556(1) | OPEN LINE FROM BUS 324307 [4SHARKEY TAP138.00] TO BUS 326556 [4N SHARKEY T138.00] CKT 1 | 0.93965 | 64.8362 | 0.93998 | 64.8588 | 0.00032854 | -1.7047e-05
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1086 324307-326556(1) | OPEN LINE FROM BUS 324307 [4SHARKEY TAP138.00] TO BUS 326556 [4N SHARKEY T138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1087 324310-324733(1) | OPEN LINE FROM BUS 324310 [4SPENCER RD 138.00] TO BUS 324733 [2SPENCER RD 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93958 | 64.8312 | -7.1943e-05 | -0.00041753
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1087 324310-324733(1) | OPEN LINE FROM BUS 324310 [4SPENCER RD 138.00] TO BUS 324733 [2SPENCER RD 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1088 324310-325009(1) | OPEN LINE FROM BUS 324310 [4SPENCER RD 138.00] TO BUS 325009 [2SPENCER A 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1089 324311-324976(3) | OPEN LINE FROM BUS 324311 [4TIP TOP 138.00] TO BUS 324976 [2TIP TOP 1 69.000] CKT 3 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 1.4305e-06 | -0.00034416
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1089 324311-324976(3) | OPEN LINE FROM BUS 324311 [4TIP TOP 138.00] TO BUS 324976 [2TIP TOP 1 69.000] CKT 3 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1090 324311-325132(1) | OPEN LINE FROM BUS 324311 [4TIP TOP 138.00] TO BUS 325132 [4GREENSOL TP138.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8368 | 9.8348e-06 | -0.00033575
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1090 324311-325132(1) | OPEN LINE FROM BUS 324311 [4TIP TOP 138.00] TO BUS 325132 [4GREENSOL TP138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1091 324312-324313(1) | OPEN LINE FROM BUS 324312 [4TOYOTA N 138.00] TO BUS 324313 [4TOYOTA S 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8353 | -1.204e-05 | -0.00035763
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1091 324312-324313(1) | OPEN LINE FROM BUS 324312 [4TOYOTA N 138.00] TO BUS 324313 [4TOYOTA S 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1092 324312-324991(1) | OPEN LINE FROM BUS 324312 [4TOYOTA N 138.00] TO BUS 324991 [4ROGERS GAP 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.3113e-06 | -0.0003469
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1092 324312-324991(1) | OPEN LINE FROM BUS 324312 [4TOYOTA N 138.00] TO BUS 324991 [4ROGERS GAP 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1093 324314-326520(Z1) | OPEN LINE FROM BUS 324314 [4TRIMBLE CO 138.00] TO BUS 326520 [4TRIMBLE TR9138.00] CKT Z1 | 0.93965 | 64.8362 | 0.93965 | 64.8356 | -7.5102e-06 | -0.0003531
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1093 324314-326520(Z1) | OPEN LINE FROM BUS 324314 [4TRIMBLE CO 138.00] TO BUS 326520 [4TRIMBLE TR9138.00] CKT Z1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1094 324315-324755(1) | OPEN LINE FROM BUS 324315 [4TYRONE 138.00] TO BUS 324755 [2TYRONE 69.000] CKT 1 | 0.93965 | 64.8362 | 0.9395 | 64.8255 | -0.00015444 | -0.00050002
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1094 324315-324755(1) | OPEN LINE FROM BUS 324315 [4TYRONE 138.00] TO BUS 324755 [2TYRONE 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1095 324315-325957(1) | OPEN LINE FROM BUS 324315 [4TYRONE 138.00] TO BUS 325957 [4BROWN N 1 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93958 | 64.8309 | -7.5459e-05 | -0.00042105
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1095 324315-325957(1) | OPEN LINE FROM BUS 324315 [4TYRONE 138.00] TO BUS 325957 [4BROWN N 1 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1096 324316-324759(1) | OPEN LINE FROM BUS 324316 [4VIRGINIA CI138.00] TO BUS 324759 [2VIRGINIA CI69.000] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8369 | 1.1265e-05 | -0.00033432
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1096 324316-324759(1) | OPEN LINE FROM BUS 324316 [4VIRGINIA CI138.00] TO BUS 324759 [2VIRGINIA CI69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1097 324317-325101(1) | OPEN LINE FROM BUS 324317 [4VILEY ROAD 138.00] TO BUS 325101 [4W LEX R2 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93926 | 64.8089 | -0.00039518 | -0.00074077
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1097 324317-325101(1) | OPEN LINE FROM BUS 324317 [4VILEY ROAD 138.00] TO BUS 325101 [4W LEX R2 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1098 324318-324764(1) | OPEN LINE FROM BUS 324318 [4WEST CLIFF 138.00] TO BUS 324764 [2WEST CLIFF 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -2.5034e-06 | -0.00034809
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1098 324318-324764(1) | OPEN LINE FROM BUS 324318 [4WEST CLIFF 138.00] TO BUS 324764 [2WEST CLIFF 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1099 324318-324764(2) | OPEN LINE FROM BUS 324318 [4WEST CLIFF 138.00] TO BUS 324764 [2WEST CLIFF 69.000] CKT 2 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -5.9605e-07 | -0.00034618
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1099 324318-324764(2) | OPEN LINE FROM BUS 324318 [4WEST CLIFF 138.00] TO BUS 324764 [2WEST CLIFF 69.000] CKT 2 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1100 324319-324765(1) | OPEN LINE FROM BUS 324319 [4W FRANKFORT138.00] TO BUS 324765 [2W FRANKFORT69.000] CKT 1 | 0.93965 | 64.8362 | 0.93963 | 64.8348 | -1.961e-05 | -0.0003652
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1100 324319-324765(1) | OPEN LINE FROM BUS 324319 [4W FRANKFORT138.00] TO BUS 324765 [2W FRANKFORT69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1101 324320-325089(1) | OPEN LINE FROM BUS 324320 [4W LEXINGTON138.00] TO BUS 325089 [4HIGBY MILL2138.00] CKT 1 | 0.93965 | 64.8362 | 0.93951 | 64.8261 | -0.00014591 | -0.0004915
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1101 324320-325089(1) | OPEN LINE FROM BUS 324320 [4W LEXINGTON138.00] TO BUS 325089 [4HIGBY MILL2138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1102 324320-325100(1) | OPEN LINE FROM BUS 324320 [4W LEXINGTON138.00] TO BUS 325100 [4W LEX R1 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93929 | 64.8112 | -0.00036132 | -0.00070691
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1102 324320-325100(1) | OPEN LINE FROM BUS 324320 [4W LEXINGTON138.00] TO BUS 325100 [4W LEX R1 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1103 324320-325101(1) | OPEN LINE FROM BUS 324320 [4W LEXINGTON138.00] TO BUS 325101 [4W LEX R2 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93927 | 64.8095 | -0.00038642 | -0.000732
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1103 324320-325101(1) | OPEN LINE FROM BUS 324320 [4W LEXINGTON138.00] TO BUS 325101 [4W LEX R2 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1104 324322-324771(1) | OPEN LINE FROM BUS 324322 [4WATTERSON 138.00] TO BUS 324771 [2WATTERSON 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -1.7285e-06 | -0.00034732
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1104 324322-324771(1) | OPEN LINE FROM BUS 324322 [4WATTERSON 138.00] TO BUS 324771 [2WATTERSON 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1105 324322-324771(2) | OPEN LINE FROM BUS 324322 [4WATTERSON 138.00] TO BUS 324771 [2WATTERSON 69.000] CKT 2 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -4.1723e-07 | -0.000346
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1105 324322-324771(2) | OPEN LINE FROM BUS 324322 [4WATTERSON 138.00] TO BUS 324771 [2WATTERSON 69.000] CKT 2 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1106 324322-325042(1) | OPEN LINE FROM BUS 324322 [4WATTERSON 138.00] TO BUS 325042 [4JEFERSONTWN138.00] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8349 | -1.7524e-05 | -0.00036311
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1106 324322-325042(1) | OPEN LINE FROM BUS 324322 [4WATTERSON 138.00] TO BUS 325042 [4JEFERSONTWN138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1107 324328-324680(1) | OPEN LINE FROM BUS 324328 [4PARIS 138.00] TO BUS 324680 [2PARIS KU 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93833 | 64.7445 | -0.0013288 | -0.0016744
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1107 324328-324680(1) | OPEN LINE FROM BUS 324328 [4PARIS 138.00] TO BUS 324680 [2PARIS KU 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1108 324329-324364(1) | OPEN LINE FROM BUS 324329 [4COLLINS 138.00] TO BUS 324364 [4OLD HENRY 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8365 | 5.722e-06 | -0.00033987
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1108 324329-324364(1) | OPEN LINE FROM BUS 324329 [4COLLINS 138.00] TO BUS 324364 [4OLD HENRY 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1109 324329-324481(1) | OPEN LINE FROM BUS 324329 [4COLLINS 138.00] TO BUS 324481 [2COLLINS 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8366 | 6.9141e-06 | -0.00033867
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1109 324329-324481(1) | OPEN LINE FROM BUS 324329 [4COLLINS 138.00] TO BUS 324481 [2COLLINS 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 1.1921e-07 | 1.1921e-07
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1110 324330-324783(1) | OPEN LINE FROM BUS 324330 [2WINCHES IND69.000] TO BUS 324783 [2WINCHSTR KU69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1111 324330-325063(1) | OPEN LINE FROM BUS 324330 [2WINCHES IND69.000] TO BUS 325063 [2CORPORAT DR69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1112 324331-324418(1) | OPEN LINE FROM BUS 324331 [2ASHLAND AVE69.000] TO BUS 324418 [2ASHLND AV T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93974 | 64.842 | 8.4102e-05 | -0.00026149
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1112 324331-324418(1) | OPEN LINE FROM BUS 324331 [2ASHLAND AVE69.000] TO BUS 324418 [2ASHLND AV T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1113 324332-325059(1) | OPEN LINE FROM BUS 324332 [2LAKE SHORE 69.000] TO BUS 325059 [2BRYANT RD T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93994 | 64.8556 | 0.00028205 | -6.3539e-05
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1113 324332-325059(1) | OPEN LINE FROM BUS 324332 [2LAKE SHORE 69.000] TO BUS 325059 [2BRYANT RD T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1114 324333-325957(1) | OPEN LINE FROM BUS 324333 [4BROWN N 1-R138.00] TO BUS 325957 [4BROWN N 1 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93917 | 64.803 | -0.00048107 | -0.00082666
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1114 324333-325957(1) | OPEN LINE FROM BUS 324333 [4BROWN N 1-R138.00] TO BUS 325957 [4BROWN N 1 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1115 324334-325956(1) | OPEN LINE FROM BUS 324334 [4BROWN N 2-R138.00] TO BUS 325956 [4BROWN N 2 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93906 | 64.7952 | -0.00059408 | -0.00093967
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1115 324334-325956(1) | OPEN LINE FROM BUS 324334 [4BROWN N 2-R138.00] TO BUS 325956 [4BROWN N 2 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1116 324337-324650(1) | OPEN LINE FROM BUS 324337 [2MOUNT TABOR69.000] TO BUS 324650 [2MT TBR T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 3.2187e-06 | -0.00034237
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1116 324337-324650(1) | OPEN LINE FROM BUS 324337 [2MOUNT TABOR69.000] TO BUS 324650 [2MT TBR T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1117 324338-324339(1) | OPEN LINE FROM BUS 324338 [2SCOTT ST 4 69.000] TO BUS 324339 [2SCOTT ST 1269.000] CKT 1 | 0.93965 | 64.8362 | 0.93975 | 64.8425 | 9.1612e-05 | -0.00025398
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1117 324338-324339(1) | OPEN LINE FROM BUS 324338 [2SCOTT ST 4 69.000] TO BUS 324339 [2SCOTT ST 1269.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1118 324338-324952(1) | OPEN LINE FROM BUS 324338 [2SCOTT ST 4 69.000] TO BUS 324952 [2SCOTT ST TP69.000] CKT 1 | 0.93965 | 64.8362 | 0.93978 | 64.8445 | 0.00012153 | -0.00022405
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1118 324338-324952(1) | OPEN LINE FROM BUS 324338 [2SCOTT ST 4 69.000] TO BUS 324952 [2SCOTT ST TP69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1119 324340-324734(1) | OPEN LINE FROM BUS 324340 [2SPINDLETOP 69.000] TO BUS 324734 [2SPINDLETP T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8368 | 8.7023e-06 | -0.00033689
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1119 324340-324734(1) | OPEN LINE FROM BUS 324340 [2SPINDLETOP 69.000] TO BUS 324734 [2SPINDLETP T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1120 324341-324781(1) | OPEN LINE FROM BUS 324341 [2WILMORE 69.000] TO BUS 324781 [2WILMORE T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8365 | 4.6492e-06 | -0.00034094
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1120 324341-324781(1) | OPEN LINE FROM BUS 324341 [2WILMORE 69.000] TO BUS 324781 [2WILMORE T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1121 324344-324421(1) | OPEN LINE FROM BUS 324344 [2ATOKA 69.000] TO BUS 324421 [2ATOKA TAP 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 2.0266e-06 | -0.00034356
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1121 324344-324421(1) | OPEN LINE FROM BUS 324344 [2ATOKA 69.000] TO BUS 324421 [2ATOKA TAP 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1122 324345-324425(1) | OPEN LINE FROM BUS 324345 [2BARDTWN IND69.000] TO BUS 324425 [2BARDT IND T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8374 | 1.7464e-05 | -0.00032812
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1122 324345-324425(1) | OPEN LINE FROM BUS 324345 [2BARDTWN IND69.000] TO BUS 324425 [2BARDT IND T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1123 324346-324612(1) | OPEN LINE FROM BUS 324346 [2RICHMND E 69.000] TO BUS 324612 [2LAKE REBA 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93974 | 64.8421 | 8.6606e-05 | -0.00025898
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1123 324346-324612(1) | OPEN LINE FROM BUS 324346 [2RICHMND E 69.000] TO BUS 324612 [2LAKE REBA 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1124 324347-325058(1) | OPEN LINE FROM BUS 324347 [2BEATTY 649 69.000] TO BUS 325058 [2BEATTY 614 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8372 | 1.5676e-05 | -0.00032991
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1124 324347-325058(1) | OPEN LINE FROM BUS 324347 [2BEATTY 649 69.000] TO BUS 325058 [2BEATTY 614 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1125 324348-324808(1) | OPEN LINE FROM BUS 324348 [2BRODHEAD CI69.000] TO BUS 324808 [2BRODHEAD KU69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8365 | 5.2452e-06 | -0.00034034
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1126 324349-324479(1) | OPEN LINE FROM BUS 324349 [2CAMPBELVIL269.000] TO BUS 324479 [2CAMPBELVL T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 4.2319e-06 | -0.00034136
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1126 324349-324479(1) | OPEN LINE FROM BUS 324349 [2CAMPBELVIL269.000] TO BUS 324479 [2CAMPBELVL T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1127 324350-324485(1) | OPEN LINE FROM BUS 324350 [2CRAB ORCHAR69.000] TO BUS 324485 [2CRAB ORCH T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 3.2783e-06 | -0.00034231
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1127 324350-324485(1) | OPEN LINE FROM BUS 324350 [2CRAB ORCHAR69.000] TO BUS 324485 [2CRAB ORCH T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1128 324351-324354(1) | OPEN LINE FROM BUS 324351 [2ETOWN 3 69.000] TO BUS 324354 [2GATES RUBBR69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8367 | 7.391e-06 | -0.0003382
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1128 324351-324354(1) | OPEN LINE FROM BUS 324351 [2ETOWN 3 69.000] TO BUS 324354 [2GATES RUBBR69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1129 324351-324519(1) | OPEN LINE FROM BUS 324351 [2ETOWN 3 69.000] TO BUS 324519 [2ETOWN KU 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8369 | 1.0133e-05 | -0.00033545
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1129 324351-324519(1) | OPEN LINE FROM BUS 324351 [2ETOWN 3 69.000] TO BUS 324519 [2ETOWN KU 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1130 324352-324563(1) | OPEN LINE FROM BUS 324352 [2ETOWN IND 69.000] TO BUS 324563 [2HARDIN CO 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8365 | 5.3644e-06 | -0.00034022
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1130 324352-324563(1) | OPEN LINE FROM BUS 324352 [2ETOWN IND 69.000] TO BUS 324563 [2HARDIN CO 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1131 324353-324863(1) | OPEN LINE FROM BUS 324353 [2FLORDA TILE69.000] TO BUS 324863 [2FLA TILE T169.000] CKT 1 | 0.93965 | 64.8362 | 0.93972 | 64.8406 | 6.4135e-05 | -0.00028145
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1131 324353-324863(1) | OPEN LINE FROM BUS 324353 [2FLORDA TILE69.000] TO BUS 324863 [2FLA TILE T169.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1132 324354-326561(1) | OPEN LINE FROM BUS 324354 [2GATES RUBBR69.000] TO BUS 326561 [2ETOWN WEST 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8367 | 7.2718e-06 | -0.00033832
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1132 324354-326561(1) | OPEN LINE FROM BUS 324354 [2GATES RUBBR69.000] TO BUS 326561 [2ETOWN WEST 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1133 324355-325054(1) | OPEN LINE FROM BUS 324355 [2HARRDSBRG 469.000] TO BUS 325054 [2HARRDSBRG N69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8368 | 9.954e-06 | -0.00033563
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1133 324355-325054(1) | OPEN LINE FROM BUS 324355 [2HARRDSBRG 469.000] TO BUS 325054 [2HARRDSBRG N69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1134 324355-326578(1) | OPEN LINE FROM BUS 324355 [2HARRDSBRG 469.000] TO BUS 326578 [2HARRDSBRG 169.000] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8369 | 1.1444e-05 | -0.00033414
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1135 324356-325054(1) | OPEN LINE FROM BUS 324356 [2HARRDSBRG1269.000] TO BUS 325054 [2HARRDSBRG N69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 4.0531e-06 | -0.00034153
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1135 324356-325054(1) | OPEN LINE FROM BUS 324356 [2HARRDSBRG1269.000] TO BUS 325054 [2HARRDSBRG N69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1136 324357-324600(1) | OPEN LINE FROM BUS 324357 [2LANCASTER 169.000] TO BUS 324600 [2LANCASTR KU69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8367 | 7.9274e-06 | -0.00033766
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1136 324357-324600(1) | OPEN LINE FROM BUS 324357 [2LANCASTER 169.000] TO BUS 324600 [2LANCASTR KU69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1137 324358-324914(1) | OPEN LINE FROM BUS 324358 [2M-V CLARKSN69.000] TO BUS 324914 [2M-V CLARK T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 1.1921e-06 | -0.0003444
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1137 324358-324914(1) | OPEN LINE FROM BUS 324358 [2M-V CLARKSN69.000] TO BUS 324914 [2M-V CLARK T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 1.1921e-07 | 1.1921e-07
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1138 324359-324913(1) | OPEN LINE FROM BUS 324359 [2MT VERN 58969.000] TO BUS 324913 [2MT VERNON 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.837 | 1.2577e-05 | -0.00033301
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1138 324359-324913(1) | OPEN LINE FROM BUS 324359 [2MT VERN 58969.000] TO BUS 324913 [2MT VERNON 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1139 324360-324927(1) | OPEN LINE FROM BUS 324360 [2PINE HILL 69.000] TO BUS 324927 [2PINE HILL T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 4.1127e-06 | -0.00034148
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1139 324360-324927(1) | OPEN LINE FROM BUS 324360 [2PINE HILL 69.000] TO BUS 324927 [2PINE HILL T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1140 324361-324935(1) | OPEN LINE FROM BUS 324361 [2RADCLIFF KU69.000] TO BUS 324935 [2RADCLF KU T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 2.6226e-06 | -0.00034297
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1140 324361-324935(1) | OPEN LINE FROM BUS 324361 [2RADCLIFF KU69.000] TO BUS 324935 [2RADCLF KU T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1141 324363-324957(1) | OPEN LINE FROM BUS 324363 [2SHELB CI KU69.000] TO BUS 324957 [2SHELBY CI T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 3.9935e-06 | -0.00034159
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1141 324363-324957(1) | OPEN LINE FROM BUS 324363 [2SHELB CI KU69.000] TO BUS 324957 [2SHELBY CI T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1142 324363-326518(1) | OPEN LINE FROM BUS 324363 [2SHELB CI KU69.000] TO BUS 326518 [2SHELB CI EK69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 5.9605e-07 | -0.00034499
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1142 324363-326518(1) | OPEN LINE FROM BUS 324363 [2SHELB CI KU69.000] TO BUS 326518 [2SHELB CI EK69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1143 324372-324514(1) | OPEN LINE FROM BUS 324372 [2BURNSIDE 69.000] TO BUS 324514 [2ELIHU 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8368 | 9.7752e-06 | -0.00033581
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1143 324372-324514(1) | OPEN LINE FROM BUS 324372 [2BURNSIDE 69.000] TO BUS 324514 [2ELIHU 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1144 324373-324814(1) | OPEN LINE FROM BUS 324373 [2CATRON CRK 69.000] TO BUS 324814 [2CATRON CK T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 1.9073e-06 | -0.00034368
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1144 324373-324814(1) | OPEN LINE FROM BUS 324373 [2CATRON CRK 69.000] TO BUS 324814 [2CATRON CK T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1145 324374-324376(1) | OPEN LINE FROM BUS 324374 [2CROCKETT KU69.000] TO BUS 324376 [2DEER BRANCH69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8367 | 7.5698e-06 | -0.00033802
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1145 324374-324376(1) | OPEN LINE FROM BUS 324374 [2CROCKETT KU69.000] TO BUS 324376 [2DEER BRANCH69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1146 324374-325083(1) | OPEN LINE FROM BUS 324374 [2CROCKETT KU69.000] TO BUS 325083 [2ALEX CK TAP69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 2.9802e-06 | -0.00034261
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1146 324374-325083(1) | OPEN LINE FROM BUS 324374 [2CROCKETT KU69.000] TO BUS 325083 [2ALEX CK TAP69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1147 324375-324442(1) | OPEN LINE FROM BUS 324375 [2DAYHOIT 69.000] TO BUS 324442 [2BLEDSOE TAP69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8367 | 7.2122e-06 | -0.00033838
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1147 324375-324442(1) | OPEN LINE FROM BUS 324375 [2DAYHOIT 69.000] TO BUS 324442 [2BLEDSOE TAP69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 1.1921e-07 | 1.1921e-07
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1148 324376-324813(1) | OPEN LINE FROM BUS 324376 [2DEER BRANCH69.000] TO BUS 324813 [2CARY 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8367 | 8.5831e-06 | -0.000337
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1148 324376-324813(1) | OPEN LINE FROM BUS 324376 [2DEER BRANCH69.000] TO BUS 324813 [2CARY 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1149 324377-325083(1) | OPEN LINE FROM BUS 324377 [2GARDNER 69.000] TO BUS 325083 [2ALEX CK TAP69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 3.5763e-07 | -0.00034523
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1149 324377-325083(1) | OPEN LINE FROM BUS 324377 [2GARDNER 69.000] TO BUS 325083 [2ALEX CK TAP69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1150 324378-324636(1) | OPEN LINE FROM BUS 324378 [2MIDDLBO780 69.000] TO BUS 324636 [2MIDDLESBORO69.000] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8354 | -1.0788e-05 | -0.00035638
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1150 324378-324636(1) | OPEN LINE FROM BUS 324378 [2MIDDLBO780 69.000] TO BUS 324636 [2MIDDLESBORO69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1151 324380-324393(1) | OPEN LINE FROM BUS 324380 [2DANIEL BRAN69.000] TO BUS 324393 [2ROSE HILL 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8367 | 7.8678e-06 | -0.00033772
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1151 324380-324393(1) | OPEN LINE FROM BUS 324380 [2DANIEL BRAN69.000] TO BUS 324393 [2ROSE HILL 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1152 324380-324945(1) | OPEN LINE FROM BUS 324380 [2DANIEL BRAN69.000] TO BUS 324945 [2ROSE HILL T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8368 | 8.9407e-06 | -0.00033665
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1152 324380-324945(1) | OPEN LINE FROM BUS 324380 [2DANIEL BRAN69.000] TO BUS 324945 [2ROSE HILL T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1153 324381-325001(1) | OPEN LINE FROM BUS 324381 [2WILLAMSBURG69.000] TO BUS 325001 [2WILLMBRG SW69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8367 | 8.3447e-06 | -0.00033724
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1153 324381-325001(1) | OPEN LINE FROM BUS 324381 [2WILLAMSBURG69.000] TO BUS 325001 [2WILLMBRG SW69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1154 324382-325001(1) | OPEN LINE FROM BUS 324382 [2WILLMBRG SO69.000] TO BUS 325001 [2WILLMBRG SW69.000] CKT 1 | 0.93965 | 64.8362 | 0.93969 | 64.8389 | 4.0352e-05 | -0.00030524
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1154 324382-325001(1) | OPEN LINE FROM BUS 324382 [2WILLMBRG SO69.000] TO BUS 325001 [2WILLMBRG SW69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1155 324384-324549(1) | OPEN LINE FROM BUS 324384 [2APPALACHIA 69.000] TO BUS 324549 [2GORGE 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8366 | 6.9141e-06 | -0.00033867
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1155 324384-324549(1) | OPEN LINE FROM BUS 324384 [2APPALACHIA 69.000] TO BUS 324549 [2GORGE 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 1.1921e-07 | 1.1921e-07
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1156 324385-324549(1) | OPEN LINE FROM BUS 324385 [2BIG STONE G69.000] TO BUS 324549 [2GORGE 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93968 | 64.8381 | 2.8253e-05 | -0.00031734
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1156 324385-324549(1) | OPEN LINE FROM BUS 324385 [2BIG STONE G69.000] TO BUS 324549 [2GORGE 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1157 324386-324388(1) | OPEN LINE FROM BUS 324386 [2DIXIANA 69.000] TO BUS 324388 [2CRITICAL FK69.000] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8371 | 1.4186e-05 | -0.0003314
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1157 324386-324388(1) | OPEN LINE FROM BUS 324386 [2DIXIANA 69.000] TO BUS 324388 [2CRITICAL FK69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1158 324387-324392(1) | OPEN LINE FROM BUS 324387 [2ADDINGTON 69.000] TO BUS 324392 [2ROCKY FORK 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8372 | 1.5259e-05 | -0.00033033
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1158 324387-324392(1) | OPEN LINE FROM BUS 324387 [2ADDINGTON 69.000] TO BUS 324392 [2ROCKY FORK 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1159 324387-325064(1) | OPEN LINE FROM BUS 324387 [2ADDINGTON 69.000] TO BUS 325064 [2LAUREL GROV69.000] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8373 | 1.7226e-05 | -0.00032836
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1159 324387-325064(1) | OPEN LINE FROM BUS 324387 [2ADDINGTON 69.000] TO BUS 325064 [2LAUREL GROV69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1160 324388-325031(1) | OPEN LINE FROM BUS 324388 [2CRITICAL FK69.000] TO BUS 325031 [2LIPPS 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8371 | 1.4007e-05 | -0.00033158
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1160 324388-325031(1) | OPEN LINE FROM BUS 324388 [2CRITICAL FK69.000] TO BUS 325031 [2LIPPS 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1161 324389-324851(1) | OPEN LINE FROM BUS 324389 [2DWINA 69.000] TO BUS 324851 [2DWINA TAP 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 1.6093e-06 | -0.00034398
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1161 324389-324851(1) | OPEN LINE FROM BUS 324389 [2DWINA 69.000] TO BUS 324851 [2DWINA TAP 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1162 324390-324391(1) | OPEN LINE FROM BUS 324390 [2PENNINGTON 69.000] TO BUS 324391 [2POOR VALLEY69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 1.7881e-06 | -0.0003438
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1162 324390-324391(1) | OPEN LINE FROM BUS 324390 [2PENNINGTON 69.000] TO BUS 324391 [2POOR VALLEY69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1163 324391-324689(1) | OPEN LINE FROM BUS 324391 [2POOR VALLEY69.000] TO BUS 324689 [2POCKET 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8369 | 1.1265e-05 | -0.00033432
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1163 324391-324689(1) | OPEN LINE FROM BUS 324391 [2POOR VALLEY69.000] TO BUS 324689 [2POCKET 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1164 324392-325031(1) | OPEN LINE FROM BUS 324392 [2ROCKY FORK 69.000] TO BUS 325031 [2LIPPS 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8372 | 1.4901e-05 | -0.00033069
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1164 324392-325031(1) | OPEN LINE FROM BUS 324392 [2ROCKY FORK 69.000] TO BUS 325031 [2LIPPS 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1165 324394-324977(1) | OPEN LINE FROM BUS 324394 [2TOMS CREEK 69.000] TO BUS 324977 [2TOMS CRK TP69.000] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8373 | 1.6391e-05 | -0.0003292
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1165 324394-324977(1) | OPEN LINE FROM BUS 324394 [2TOMS CREEK 69.000] TO BUS 324977 [2TOMS CRK TP69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1166 324395-325005(1) | OPEN LINE FROM BUS 324395 [2WISE 69.000] TO BUS 325005 [2WISE TAP 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8374 | 1.8656e-05 | -0.00032693
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1167 324400-324510(1) | OPEN LINE FROM BUS 324400 [2WHAS TAP 69.000] TO BUS 324510 [2EASTWOOD 69.000] CKT 1 | 0.93965 | 64.8362 | 0.9397 | 64.8396 | 4.9651e-05 | -0.00029594
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1167 324400-324510(1) | OPEN LINE FROM BUS 324400 [2WHAS TAP 69.000] TO BUS 324510 [2EASTWOOD 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1168 324400-324775(1) | OPEN LINE FROM BUS 324400 [2WHAS TAP 69.000] TO BUS 324775 [2WHAS 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -8.3447e-07 | -0.00034642
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1168 324400-324775(1) | OPEN LINE FROM BUS 324400 [2WHAS TAP 69.000] TO BUS 324775 [2WHAS 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1169 324400-325022(1) | OPEN LINE FROM BUS 324400 [2WHAS TAP 69.000] TO BUS 325022 [2EASTWOOD W 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8365 | 5.424e-06 | -0.00034016
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1169 324400-325022(1) | OPEN LINE FROM BUS 324400 [2WHAS TAP 69.000] TO BUS 325022 [2EASTWOOD W 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1170 324401-324541(1) | OPEN LINE FROM BUS 324401 [2FREYS HIL J69.000] TO BUS 324541 [2FORD 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8359 | -4.1723e-06 | -0.00034976
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1170 324401-324541(1) | OPEN LINE FROM BUS 324401 [2FREYS HIL J69.000] TO BUS 324541 [2FORD 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1171 324401-324545(1) | OPEN LINE FROM BUS 324401 [2FREYS HIL J69.000] TO BUS 324545 [2FREYS HILL 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 1.3113e-06 | -0.00034428
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1171 324401-324545(1) | OPEN LINE FROM BUS 324401 [2FREYS HIL J69.000] TO BUS 324545 [2FREYS HILL 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1172 324401-324785(1) | OPEN LINE FROM BUS 324401 [2FREYS HIL J69.000] TO BUS 324785 [2WORTHINGTON69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8357 | -6.0797e-06 | -0.00035167
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1172 324401-324785(1) | OPEN LINE FROM BUS 324401 [2FREYS HIL J69.000] TO BUS 324785 [2WORTHINGTON69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1173 324402-324859(1) | OPEN LINE FROM BUS 324402 [2FAIRMOUNT T69.000] TO BUS 324859 [2FAIRMOUNT 169.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8365 | 5.3048e-06 | -0.00034028
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1173 324402-324859(1) | OPEN LINE FROM BUS 324402 [2FAIRMOUNT T69.000] TO BUS 324859 [2FAIRMOUNT 169.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1174 324403-324469(1) | OPEN LINE FROM BUS 324403 [2CRESTWOOD T69.000] TO BUS 324469 [2CENTERFIELD69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.2517e-06 | -0.00034684
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1174 324403-324469(1) | OPEN LINE FROM BUS 324403 [2CRESTWOOD T69.000] TO BUS 324469 [2CENTERFIELD69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1175 324403-324487(1) | OPEN LINE FROM BUS 324403 [2CRESTWOOD T69.000] TO BUS 324487 [2CRESTWOOD 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 1.3113e-06 | -0.00034428
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1175 324403-324487(1) | OPEN LINE FROM BUS 324403 [2CRESTWOOD T69.000] TO BUS 324487 [2CRESTWOOD 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1176 324403-324616(1) | OPEN LINE FROM BUS 324403 [2CRESTWOOD T69.000] TO BUS 324616 [2LONG RUN 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -1.6689e-06 | -0.00034726
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1176 324403-324616(1) | OPEN LINE FROM BUS 324403 [2CRESTWOOD T69.000] TO BUS 324616 [2LONG RUN 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1177 324404-324622(1) | OPEN LINE FROM BUS 324404 [2LYNDON TAP 69.000] TO BUS 324622 [2LYNDON SO 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.4305e-06 | -0.00034702
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1177 324404-324622(1) | OPEN LINE FROM BUS 324404 [2LYNDON TAP 69.000] TO BUS 324622 [2LYNDON SO 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1178 324404-324623(1) | OPEN LINE FROM BUS 324404 [2LYNDON TAP 69.000] TO BUS 324623 [2LYNDON 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 6.5565e-07 | -0.00034493
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1178 324404-324623(1) | OPEN LINE FROM BUS 324404 [2LYNDON TAP 69.000] TO BUS 324623 [2LYNDON 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1179 324404-324750(1) | OPEN LINE FROM BUS 324404 [2LYNDON TAP 69.000] TO BUS 324750 [2TAYLOR LG 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -2.0862e-06 | -0.00034767
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1179 324404-324750(1) | OPEN LINE FROM BUS 324404 [2LYNDON TAP 69.000] TO BUS 324750 [2TAYLOR LG 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1180 324405-324547(1) | OPEN LINE FROM BUS 324405 [2ADAMS 69.000] TO BUS 324547 [2GEORGETOWN 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93938 | 64.8172 | -0.00027502 | -0.0006206
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1180 324405-324547(1) | OPEN LINE FROM BUS 324405 [2ADAMS 69.000] TO BUS 324547 [2GEORGETOWN 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1181 324405-326989(1) | OPEN LINE FROM BUS 324405 [2ADAMS 69.000] TO BUS 326989 [2LONG LICK 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93951 | 64.8263 | -0.0001421 | -0.00048769
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1181 324405-326989(1) | OPEN LINE FROM BUS 324405 [2ADAMS 69.000] TO BUS 326989 [2LONG LICK 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1182 324406-324637(1) | OPEN LINE FROM BUS 324406 [2AIKEN 69.000] TO BUS 324637 [2MIDDLETOWN 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93969 | 64.8387 | 3.7134e-05 | -0.00030845
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1182 324406-324637(1) | OPEN LINE FROM BUS 324406 [2AIKEN 69.000] TO BUS 324637 [2MIDDLETOWN 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1183 324406-324673(1) | OPEN LINE FROM BUS 324406 [2AIKEN 69.000] TO BUS 324673 [2OXMOOR 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.0729e-06 | -0.00034666
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1183 324406-324673(1) | OPEN LINE FROM BUS 324406 [2AIKEN 69.000] TO BUS 324673 [2OXMOOR 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1184 324406-325022(1) | OPEN LINE FROM BUS 324406 [2AIKEN 69.000] TO BUS 325022 [2EASTWOOD W 69.000] CKT 1 | 0.93965 | 64.8362 | 0.9397 | 64.8395 | 4.7922e-05 | -0.00029767
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1184 324406-325022(1) | OPEN LINE FROM BUS 324406 [2AIKEN 69.000] TO BUS 325022 [2EASTWOOD W 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1185 324407-324755(1) | OPEN LINE FROM BUS 324407 [2ALEXANDER 69.000] TO BUS 324755 [2TYRONE 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8348 | -1.9312e-05 | -0.0003649
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1185 324407-324755(1) | OPEN LINE FROM BUS 324407 [2ALEXANDER 69.000] TO BUS 324755 [2TYRONE 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1186 324407-324955(1) | OPEN LINE FROM BUS 324407 [2ALEXANDER 69.000] TO BUS 324955 [2SHANNON RUN69.000] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.837 | 1.1921e-05 | -0.00033367
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1186 324407-324955(1) | OPEN LINE FROM BUS 324407 [2ALEXANDER 69.000] TO BUS 324955 [2SHANNON RUN69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1187 324408-324552(1) | OPEN LINE FROM BUS 324408 [2ALGONQUIN 69.000] TO BUS 324552 [2GRADY 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 1.1921e-07 | -0.00034547
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1187 324408-324552(1) | OPEN LINE FROM BUS 324408 [2ALGONQUIN 69.000] TO BUS 324552 [2GRADY 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1188 324408-324625(1) | OPEN LINE FROM BUS 324408 [2ALGONQUIN 69.000] TO BUS 324625 [2MAGAZINE 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 2.2054e-06 | -0.00034338
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1188 324408-324625(1) | OPEN LINE FROM BUS 324408 [2ALGONQUIN 69.000] TO BUS 324625 [2MAGAZINE 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1189 324408-324649(1) | OPEN LINE FROM BUS 324408 [2ALGONQUIN 69.000] TO BUS 324649 [2MORRIS FORM69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 3.5763e-07 | -0.00034523
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1189 324408-324649(1) | OPEN LINE FROM BUS 324408 [2ALGONQUIN 69.000] TO BUS 324649 [2MORRIS FORM69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1190 324408-324719(1) | OPEN LINE FROM BUS 324408 [2ALGONQUIN 69.000] TO BUS 324719 [2SEMINOLE 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.4305e-06 | -0.00034702
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1190 324408-324719(1) | OPEN LINE FROM BUS 324408 [2ALGONQUIN 69.000] TO BUS 324719 [2SEMINOLE 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1191 324408-324739(1) | OPEN LINE FROM BUS 324408 [2ALGONQUIN 69.000] TO BUS 324739 [2STEWART 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 3.5763e-07 | -0.00034523
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1191 324408-324739(1) | OPEN LINE FROM BUS 324408 [2ALGONQUIN 69.000] TO BUS 324739 [2STEWART 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1192 324409-324632(1) | OPEN LINE FROM BUS 324409 [2AMERICAN AV69.000] TO BUS 324632 [2UK MED CENT69.000] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8349 | -1.7464e-05 | -0.00036305
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1192 324409-324632(1) | OPEN LINE FROM BUS 324409 [2AMERICAN AV69.000] TO BUS 324632 [2UK MED CENT69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1193 324409-324683(1) | OPEN LINE FROM BUS 324409 [2AMERICAN AV69.000] TO BUS 324683 [2PICADOME 69.000] CKT 1 | 0.93965 | 64.8362 | 0.9397 | 64.8391 | 4.214e-05 | -0.00030345
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1193 324409-324683(1) | OPEN LINE FROM BUS 324409 [2AMERICAN AV69.000] TO BUS 324683 [2PICADOME 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1194 324409-324772(1) | OPEN LINE FROM BUS 324409 [2AMERICAN AV69.000] TO BUS 324772 [2UK WEST 2 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8367 | 8.1658e-06 | -0.00033742
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1194 324409-324772(1) | OPEN LINE FROM BUS 324409 [2AMERICAN AV69.000] TO BUS 324772 [2UK WEST 2 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1195 324411-324440(1) | OPEN LINE FROM BUS 324411 [2ANDOVER TAP69.000] TO BUS 324440 [2BLACK MOUNT69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -1.6093e-06 | -0.0003472
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1195 324411-324440(1) | OPEN LINE FROM BUS 324411 [2ANDOVER TAP69.000] TO BUS 324440 [2BLACK MOUNT69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1196 324411-324583(1) | OPEN LINE FROM BUS 324411 [2ANDOVER TAP69.000] TO BUS 324583 [2IMBODEN 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8358 | -4.6492e-06 | -0.00035024
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1196 324411-324583(1) | OPEN LINE FROM BUS 324411 [2ANDOVER TAP69.000] TO BUS 324583 [2IMBODEN 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1197 324411-324670(1) | OPEN LINE FROM BUS 324411 [2ANDOVER TAP69.000] TO BUS 324670 [2OSAKA EAST 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8372 | 1.5795e-05 | -0.00032979
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1197 324411-324670(1) | OPEN LINE FROM BUS 324411 [2ANDOVER TAP69.000] TO BUS 324670 [2OSAKA EAST 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1198 324412-324670(1) | OPEN LINE FROM BUS 324412 [2ANDOVER 69.000] TO BUS 324670 [2OSAKA EAST 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8372 | 1.502e-05 | -0.00033057
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1198 324412-324670(1) | OPEN LINE FROM BUS 324412 [2ANDOVER 69.000] TO BUS 324670 [2OSAKA EAST 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1199 324413-324414(1) | OPEN LINE FROM BUS 324413 [2AO SMITH TP69.000] TO BUS 324414 [2AO SMITH 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93994 | 64.8556 | 0.00028181 | -6.3777e-05
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1199 324413-324414(1) | OPEN LINE FROM BUS 324413 [2AO SMITH TP69.000] TO BUS 324414 [2AO SMITH 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1200 324413-324461(1) | OPEN LINE FROM BUS 324413 [2AO SMITH TP69.000] TO BUS 324461 [2CAMARGO 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93953 | 64.8273 | -0.00012785 | -0.00047344
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1200 324413-324461(1) | OPEN LINE FROM BUS 324413 [2AO SMITH TP69.000] TO BUS 324461 [2CAMARGO 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1201 324413-324733(1) | OPEN LINE FROM BUS 324413 [2AO SMITH TP69.000] TO BUS 324733 [2SPENCER RD 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93956 | 64.8299 | -9.0539e-05 | -0.00043613
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1201 324413-324733(1) | OPEN LINE FROM BUS 324413 [2AO SMITH TP69.000] TO BUS 324733 [2SPENCER RD 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1202 324414-326531(1) | OPEN LINE FROM BUS 324414 [2AO SMITH 69.000] TO BUS 326531 [2HINKSTON 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93972 | 64.8407 | 6.5863e-05 | -0.00027972
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1202 324414-326531(1) | OPEN LINE FROM BUS 324414 [2AO SMITH 69.000] TO BUS 326531 [2HINKSTON 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1203 324415-324593(1) | OPEN LINE FROM BUS 324415 [2APPOLO FUEL69.000] TO BUS 324593 [2KU PARK 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8357 | -6.6161e-06 | -0.0003522
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1203 324415-324593(1) | OPEN LINE FROM BUS 324415 [2APPOLO FUEL69.000] TO BUS 324593 [2KU PARK 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1204 324415-324636(1) | OPEN LINE FROM BUS 324415 [2APPOLO FUEL69.000] TO BUS 324636 [2MIDDLESBORO69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8357 | -6.8545e-06 | -0.00035244
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1204 324415-324636(1) | OPEN LINE FROM BUS 324415 [2APPOLO FUEL69.000] TO BUS 324636 [2MIDDLESBORO69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1205 324416-324433(1) | OPEN LINE FROM BUS 324416 [2ARNOLD 69.000] TO BUS 324433 [2BENHAM 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8372 | 1.4722e-05 | -0.00033087
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1205 324416-324433(1) | OPEN LINE FROM BUS 324416 [2ARNOLD 69.000] TO BUS 324433 [2BENHAM 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1206 324416-324490(1) | OPEN LINE FROM BUS 324416 [2ARNOLD 69.000] TO BUS 324490 [2CUMBERLAND 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8365 | 4.7684e-06 | -0.00034082
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1206 324416-324490(1) | OPEN LINE FROM BUS 324416 [2ARNOLD 69.000] TO BUS 324490 [2CUMBERLAND 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1207 324417-324423(1) | OPEN LINE FROM BUS 324417 [2ARTEMUS 69.000] TO BUS 324423 [2BARBOURVILE69.000] CKT 1 | 0.93965 | 64.8362 | 0.93963 | 64.8347 | -2.0862e-05 | -0.00036645
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1207 324417-324423(1) | OPEN LINE FROM BUS 324417 [2ARTEMUS 69.000] TO BUS 324423 [2BARBOURVILE69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1208 324418-324632(1) | OPEN LINE FROM BUS 324418 [2ASHLND AV T69.000] TO BUS 324632 [2UK MED CENT69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8368 | 8.9407e-06 | -0.00033665
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1208 324418-324632(1) | OPEN LINE FROM BUS 324418 [2ASHLND AV T69.000] TO BUS 324632 [2UK MED CENT69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1209 324418-324934(1) | OPEN LINE FROM BUS 324418 [2ASHLND AV T69.000] TO BUS 324934 [2RACE STREET69.000] CKT 1 | 0.93965 | 64.8362 | 0.93968 | 64.8381 | 2.8789e-05 | -0.0003168
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1209 324418-324934(1) | OPEN LINE FROM BUS 324418 [2ASHLND AV T69.000] TO BUS 324934 [2RACE STREET69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1210 324419-325024(1) | OPEN LINE FROM BUS 324419 [2ASHBOT WEST69.000] TO BUS 325024 [2ASHBOT SPRK69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -4.7684e-07 | -0.00034606
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1210 324419-325024(1) | OPEN LINE FROM BUS 324419 [2ASHBOT WEST69.000] TO BUS 325024 [2ASHBOT SPRK69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1211 324421-324450(1) | OPEN LINE FROM BUS 324421 [2ATOKA TAP 69.000] TO BUS 324450 [2BOYLE CO 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93963 | 64.8342 | -2.8014e-05 | -0.0003736
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1211 324421-324450(1) | OPEN LINE FROM BUS 324421 [2ATOKA TAP 69.000] TO BUS 324450 [2BOYLE CO 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1212 324421-324495(1) | OPEN LINE FROM BUS 324421 [2ATOKA TAP 69.000] TO BUS 324495 [2DANVILLE N 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93962 | 64.8341 | -2.9743e-05 | -0.00037533
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1212 324421-324495(1) | OPEN LINE FROM BUS 324421 [2ATOKA TAP 69.000] TO BUS 324495 [2DANVILLE N 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1213 324422-324508(1) | OPEN LINE FROM BUS 324422 [2AVON T2 69.000] TO BUS 324508 [2EASTLAND 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93919 | 64.8041 | -0.00046474 | -0.00081033
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1213 324422-324508(1) | OPEN LINE FROM BUS 324422 [2AVON T2 69.000] TO BUS 324508 [2EASTLAND 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1214 324422-324680(1) | OPEN LINE FROM BUS 324422 [2AVON T2 69.000] TO BUS 324680 [2PARIS KU 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93937 | 64.8162 | -0.0002892 | -0.00063479
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1214 324422-324680(1) | OPEN LINE FROM BUS 324422 [2AVON T2 69.000] TO BUS 324680 [2PARIS KU 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1215 324422-325081(1) | OPEN LINE FROM BUS 324422 [2AVON T2 69.000] TO BUS 325081 [2BRIAR HILL 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93978 | 64.8447 | 0.00012457 | -0.00022101
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1215 324422-325081(1) | OPEN LINE FROM BUS 324422 [2AVON T2 69.000] TO BUS 325081 [2BRIAR HILL 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1216 324423-324438(1) | OPEN LINE FROM BUS 324423 [2BARBOURVILE69.000] TO BUS 324438 [2BIMBLE 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -8.3447e-07 | -0.00034642
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1216 324423-324438(1) | OPEN LINE FROM BUS 324423 [2BARBOURVILE69.000] TO BUS 324438 [2BIMBLE 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1217 324424-324801(1) | OPEN LINE FROM BUS 324424 [2BARDTWN CTY69.000] TO BUS 324801 [2BARTON 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 2.1458e-06 | -0.00034344
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1217 324424-324801(1) | OPEN LINE FROM BUS 324424 [2BARDTWN CTY69.000] TO BUS 324801 [2BARTON 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1218 324424-326537(1) | OPEN LINE FROM BUS 324424 [2BARDTWN CTY69.000] TO BUS 326537 [2WOODLAWN KU69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -2.6822e-06 | -0.00034827
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1218 324424-326537(1) | OPEN LINE FROM BUS 324424 [2BARDTWN CTY69.000] TO BUS 326537 [2WOODLAWN KU69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341047 | 2BALLTOWN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1219 324425-324426(1) | OPEN LINE FROM BUS 324425 [2BARDT IND T69.000] TO BUS 324426 [2BARDSTOWN 69.000] CKT 1 | 0.98081 | 67.6761 | 0.93916 | 64.8018 | -0.041657 | -0.00084394
341053 | 2BARD SHOP | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1219 324425-324426(1) | OPEN LINE FROM BUS 324425 [2BARDT IND T69.000] TO BUS 324426 [2BARDSTOWN 69.000] CKT 1 | 0.99156 | 68.4178 | 0.93328 | 64.3964 | -0.05828 | -0.0067187
341056 | 2BARD SHOP T | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1219 324425-324426(1) | OPEN LINE FROM BUS 324425 [2BARDT IND T69.000] TO BUS 324426 [2BARDSTOWN 69.000] CKT 1 | 0.99196 | 68.4455 | 0.93371 | 64.4258 | -0.058255 | -0.0062922
341140 | 2BLUE G PW | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1219 324425-324426(1) | OPEN LINE FROM BUS 324425 [2BARDT IND T69.000] TO BUS 324426 [2BARDSTOWN 69.000] CKT 1 | 0.99058 | 68.3498 | 0.9334 | 64.4046 | -0.057177 | -0.0066003
341143 | 2BLUE G PW T | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1219 324425-324426(1) | OPEN LINE FROM BUS 324425 [2BARDT IND T69.000] TO BUS 324426 [2BARDSTOWN 69.000] CKT 1 | 0.99064 | 68.3545 | 0.93347 | 64.4096 | -0.057172 | -0.0065276
341407 | 2E BARDSTOWN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1219 324425-324426(1) | OPEN LINE FROM BUS 324425 [2BARDT IND T69.000] TO BUS 324426 [2BARDSTOWN 69.000] CKT 1 | 0.99368 | 68.5638 | 0.93169 | 64.2866 | -0.061989 | -0.0083107
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1219 324425-324426(1) | OPEN LINE FROM BUS 324425 [2BARDT IND T69.000] TO BUS 324426 [2BARDSTOWN 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93961 | 64.8328 | -4.828e-05 | -0.00039387
342016 | 2OWENS IL | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1219 324425-324426(1) | OPEN LINE FROM BUS 324425 [2BARDT IND T69.000] TO BUS 324426 [2BARDSTOWN 69.000] CKT 1 | 0.99116 | 68.3898 | 0.93009 | 64.1763 | -0.061066 | -0.0099092
342019 | 2OWENS IL J | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1219 324425-324426(1) | OPEN LINE FROM BUS 324425 [2BARDT IND T69.000] TO BUS 324426 [2BARDSTOWN 69.000] CKT 1 | 0.99245 | 68.4793 | 0.93147 | 64.2717 | -0.06098 | -0.0085267
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1219 324425-324426(1) | OPEN LINE FROM BUS 324425 [2BARDT IND T69.000] TO BUS 324426 [2BARDSTOWN 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
324345 | 2BARDTWN IND | 69 | LGEE' | RANGE | 0.94 | 1.06 | SINGLE OPN LIN 1219 324425-324426(1) | OPEN LINE FROM BUS 324425 [2BARDT IND T69.000] TO BUS 324426 [2BARDSTOWN 69.000] CKT 1 | 0.98911 | 68.2489 | 0.9226 | 63.6596 | -0.066512 | -0.017397
324425 | 2BARDT IND T | 69 | LGEE' | RANGE | 0.94 | 1.06 | SINGLE OPN LIN 1219 324425-324426(1) | OPEN LINE FROM BUS 324425 [2BARDT IND T69.000] TO BUS 324426 [2BARDSTOWN 69.000] CKT 1 | 0.99636 | 68.7491 | 0.93038 | 64.196 | -0.065987 | -0.0096236
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1220 324426-324525(1) | OPEN LINE FROM BUS 324426 [2BARDSTOWN 69.000] TO BUS 324525 [2FAIRFIELD 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8354 | -1.1563e-05 | -0.00035715
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1220 324426-324525(1) | OPEN LINE FROM BUS 324426 [2BARDSTOWN 69.000] TO BUS 324525 [2FAIRFIELD 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1221 324426-326537(Z1) | OPEN LINE FROM BUS 324426 [2BARDSTOWN 69.000] TO BUS 326537 [2WOODLAWN KU69.000] CKT Z1 | 0.93965 | 64.8362 | 0.93965 | 64.8359 | -3.8743e-06 | -0.00034946
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1221 324426-326537(Z1) | OPEN LINE FROM BUS 324426 [2BARDSTOWN 69.000] TO BUS 326537 [2WOODLAWN KU69.000] CKT Z1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1222 324427-324779(1) | OPEN LINE FROM BUS 324427 [2BARDWELL 69.000] TO BUS 324779 [2WICKLIFFE 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 2.3842e-07 | -0.00034535
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1222 324427-324779(1) | OPEN LINE FROM BUS 324427 [2BARDWELL 69.000] TO BUS 324779 [2WICKLIFFE 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1223 324427-324823(1) | OPEN LINE FROM BUS 324427 [2BARDWELL 69.000] TO BUS 324823 [2CLINTON 58169.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 1.1921e-07 | -0.00034547
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1223 324427-324823(1) | OPEN LINE FROM BUS 324427 [2BARDWELL 69.000] TO BUS 324823 [2CLINTON 58169.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1224 324428-324778(1) | OPEN LINE FROM BUS 324428 [2BARLOW 69.000] TO BUS 324778 [2WICKLIFE CI69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 5.9605e-08 | -0.00034553
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1224 324428-324778(1) | OPEN LINE FROM BUS 324428 [2BARLOW 69.000] TO BUS 324778 [2WICKLIFE CI69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1225 324428-324864(1) | OPEN LINE FROM BUS 324428 [2BARLOW 69.000] TO BUS 324864 [2FORRESTDALE69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 5.9605e-08 | -0.00034553
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1225 324428-324864(1) | OPEN LINE FROM BUS 324428 [2BARLOW 69.000] TO BUS 324864 [2FORRESTDALE69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1226 324429-324453(1) | OPEN LINE FROM BUS 324429 [2BEARGRASS 69.000] TO BUS 324453 [2BEARGRS PMP69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.1921e-07 | -0.00034571
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1226 324429-324453(1) | OPEN LINE FROM BUS 324429 [2BEARGRASS 69.000] TO BUS 324453 [2BEARGRS PMP69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1227 324429-324475(1) | OPEN LINE FROM BUS 324429 [2BEARGRASS 69.000] TO BUS 324475 [2CLIFTON 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.1921e-07 | -0.00034571
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1227 324429-324475(1) | OPEN LINE FROM BUS 324429 [2BEARGRASS 69.000] TO BUS 324475 [2CLIFTON 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1228 324429-324624(1) | OPEN LINE FROM BUS 324429 [2BEARGRASS 69.000] TO BUS 324624 [2MADISON LGE69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 2.0862e-06 | -0.0003435
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1228 324429-324624(1) | OPEN LINE FROM BUS 324429 [2BEARGRASS 69.000] TO BUS 324624 [2MADISON LGE69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1229 324429-324710(1) | OPEN LINE FROM BUS 324429 [2BEARGRASS 69.000] TO BUS 324710 [2RVR CITY SH69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 7.1526e-07 | -0.00034487
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1229 324429-324710(1) | OPEN LINE FROM BUS 324429 [2BEARGRASS 69.000] TO BUS 324710 [2RVR CITY SH69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1230 324430-325058(1) | OPEN LINE FROM BUS 324430 [2BEATTYVI KU69.000] TO BUS 325058 [2BEATTY 614 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8367 | 7.987e-06 | -0.0003376
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1230 324430-325058(1) | OPEN LINE FROM BUS 324430 [2BEATTYVI KU69.000] TO BUS 325058 [2BEATTY 614 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1231 324432-324558(1) | OPEN LINE FROM BUS 324432 [2BELT LINE 69.000] TO BUS 324558 [2HAEFLING 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93949 | 64.8249 | -0.00016266 | -0.00050825
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1231 324432-324558(1) | OPEN LINE FROM BUS 324432 [2BELT LINE 69.000] TO BUS 324558 [2HAEFLING 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1232 324432-324879(1) | OPEN LINE FROM BUS 324432 [2BELT LINE 69.000] TO BUS 324879 [2IBM 998 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93952 | 64.8271 | -0.00013131 | -0.0004769
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1232 324432-324879(1) | OPEN LINE FROM BUS 324432 [2BELT LINE 69.000] TO BUS 324879 [2IBM 998 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1233 324433-324621(1) | OPEN LINE FROM BUS 324433 [2BENHAM 69.000] TO BUS 324621 [2LYNCH 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8371 | 1.4186e-05 | -0.0003314
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1233 324433-324621(1) | OPEN LINE FROM BUS 324433 [2BENHAM 69.000] TO BUS 324621 [2LYNCH 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1234 324434-324435(1) | OPEN LINE FROM BUS 324434 [2BEREA TAP 69.000] TO BUS 324435 [2BEREA NORTH69.000] CKT 1 | 0.93965 | 64.8362 | 0.93978 | 64.8448 | 0.00012559 | -0.00022
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1234 324434-324435(1) | OPEN LINE FROM BUS 324434 [2BEREA TAP 69.000] TO BUS 324435 [2BEREA NORTH69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1235 324434-324668(1) | OPEN LINE FROM BUS 324434 [2BEREA TAP 69.000] TO BUS 324668 [2OKONITE 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93963 | 64.8342 | -2.8551e-05 | -0.00037414
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1235 324434-324668(1) | OPEN LINE FROM BUS 324434 [2BEREA TAP 69.000] TO BUS 324668 [2OKONITE 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1236 324435-324805(1) | OPEN LINE FROM BUS 324435 [2BEREA NORTH69.000] TO BUS 324805 [2BEREA 2 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93968 | 64.838 | 2.6822e-05 | -0.00031877
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1236 324435-324805(1) | OPEN LINE FROM BUS 324435 [2BEREA NORTH69.000] TO BUS 324805 [2BEREA 2 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1237 324436-324676(1) | OPEN LINE FROM BUS 324436 [2BEREA EK TP69.000] TO BUS 324676 [2PAINT LICK 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93956 | 64.8297 | -9.4056e-05 | -0.00043964
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1237 324436-324676(1) | OPEN LINE FROM BUS 324436 [2BEREA EK TP69.000] TO BUS 324676 [2PAINT LICK 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1238 324436-324805(1) | OPEN LINE FROM BUS 324436 [2BEREA EK TP69.000] TO BUS 324805 [2BEREA 2 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93956 | 64.8296 | -9.4295e-05 | -0.00043988
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1238 324436-324805(1) | OPEN LINE FROM BUS 324436 [2BEREA EK TP69.000] TO BUS 324805 [2BEREA 2 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1239 324437-324745(1) | OPEN LINE FROM BUS 324437 [2BEVIER KU 69.000] TO BUS 324745 [2STRINGTOWN 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 1.1921e-07 | -0.00034547
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1239 324437-324745(1) | OPEN LINE FROM BUS 324437 [2BEVIER KU 69.000] TO BUS 324745 [2STRINGTOWN 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1240 324438-324515(1) | OPEN LINE FROM BUS 324438 [2BIMBLE 69.000] TO BUS 324515 [2EMANUEL TAP69.000] CKT 1 | 0.93965 | 64.8362 | 0.93957 | 64.8306 | -8.0884e-05 | -0.00042647
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1240 324438-324515(1) | OPEN LINE FROM BUS 324438 [2BIMBLE 69.000] TO BUS 324515 [2EMANUEL TAP69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1241 324438-324573(1) | OPEN LINE FROM BUS 324438 [2BIMBLE 69.000] TO BUS 324573 [2HINKLE 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93963 | 64.8343 | -2.6166e-05 | -0.00037175
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1241 324438-324573(1) | OPEN LINE FROM BUS 324438 [2BIMBLE 69.000] TO BUS 324573 [2HINKLE 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1242 324439-324518(1) | OPEN LINE FROM BUS 324439 [2BISHOP 69.000] TO BUS 324518 [2ETHEL 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 1.7881e-07 | -0.00034541
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1242 324439-324518(1) | OPEN LINE FROM BUS 324439 [2BISHOP 69.000] TO BUS 324518 [2ETHEL 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1243 324439-324532(1) | OPEN LINE FROM BUS 324439 [2BISHOP 69.000] TO BUS 324532 [2FERN VALLEY69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.7881e-07 | -0.00034577
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1243 324439-324532(1) | OPEN LINE FROM BUS 324439 [2BISHOP 69.000] TO BUS 324532 [2FERN VALLEY69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1244 324440-324621(1) | OPEN LINE FROM BUS 324440 [2BLACK MOUNT69.000] TO BUS 324621 [2LYNCH 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -1.9073e-06 | -0.0003475
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1244 324440-324621(1) | OPEN LINE FROM BUS 324440 [2BLACK MOUNT69.000] TO BUS 324621 [2LYNCH 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1245 324441-324503(1) | OPEN LINE FROM BUS 324441 [2BLACKWOOD 69.000] TO BUS 324503 [2DORCHESTER 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -4.1723e-07 | -0.000346
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1245 324441-324503(1) | OPEN LINE FROM BUS 324441 [2BLACKWOOD 69.000] TO BUS 324503 [2DORCHESTER 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1246 324441-324802(1) | OPEN LINE FROM BUS 324441 [2BLACKWOOD 69.000] TO BUS 324802 [2BEAR BRANCH69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -2.9802e-07 | -0.00034589
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1246 324441-324802(1) | OPEN LINE FROM BUS 324441 [2BLACKWOOD 69.000] TO BUS 324802 [2BEAR BRANCH69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1247 324442-324497(1) | OPEN LINE FROM BUS 324442 [2BLEDSOE TAP69.000] TO BUS 324497 [2DAYHOIT TAP69.000] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8371 | 1.3471e-05 | -0.00033212
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1247 324442-324497(1) | OPEN LINE FROM BUS 324442 [2BLEDSOE TAP69.000] TO BUS 324497 [2DAYHOIT TAP69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1248 324442-325008(1) | OPEN LINE FROM BUS 324442 [2BLEDSOE TAP69.000] TO BUS 325008 [2BLEDSOE 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8366 | 6.3777e-06 | -0.00033921
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1248 324442-325008(1) | OPEN LINE FROM BUS 324442 [2BLEDSOE TAP69.000] TO BUS 325008 [2BLEDSOE 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1249 324443-324789(1) | OPEN LINE FROM BUS 324443 [2BLUE LICK 69.000] TO BUS 324789 [2BLUE LCK TP69.000] CKT 1 | 0.93965 | 64.8362 | 0.93962 | 64.834 | -3.0994e-05 | -0.00037658
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1249 324443-324789(1) | OPEN LINE FROM BUS 324443 [2BLUE LICK 69.000] TO BUS 324789 [2BLUE LCK TP69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1250 324444-324651(1) | OPEN LINE FROM BUS 324444 [2BLUELICK EK69.000] TO BUS 324651 [2MUD LANE 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 2.3842e-07 | -0.00034535
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1250 324444-324651(1) | OPEN LINE FROM BUS 324444 [2BLUELICK EK69.000] TO BUS 324651 [2MUD LANE 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1251 324444-324788(1) | OPEN LINE FROM BUS 324444 [2BLUELICK EK69.000] TO BUS 324788 [2BROOKS EK T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 2.3842e-07 | -0.00034535
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1251 324444-324788(1) | OPEN LINE FROM BUS 324444 [2BLUELICK EK69.000] TO BUS 324788 [2BROOKS EK T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1252 324445-324620(1) | OPEN LINE FROM BUS 324445 [2BONDS MILL 69.000] TO BUS 324620 [2LAWRENCEBRG69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8357 | -6.6757e-06 | -0.00035226
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1252 324445-324620(1) | OPEN LINE FROM BUS 324445 [2BONDS MILL 69.000] TO BUS 324620 [2LAWRENCEBRG69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1253 324445-324732(1) | OPEN LINE FROM BUS 324445 [2BONDS MILL 69.000] TO BUS 324732 [2SOUTHVILLE 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93968 | 64.838 | 2.7001e-05 | -0.00031859
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1253 324445-324732(1) | OPEN LINE FROM BUS 324445 [2BONDS MILL 69.000] TO BUS 324732 [2SOUTHVILLE 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1254 324445-324863(1) | OPEN LINE FROM BUS 324445 [2BONDS MILL 69.000] TO BUS 324863 [2FLA TILE T169.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -2.265e-06 | -0.00034785
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1254 324445-324863(1) | OPEN LINE FROM BUS 324445 [2BONDS MILL 69.000] TO BUS 324863 [2FLA TILE T169.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1255 324445-325087(1) | OPEN LINE FROM BUS 324445 [2BONDS MILL 69.000] TO BUS 325087 [2CLAY LICK T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93955 | 64.8291 | -0.00010157 | -0.00044715
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1255 324445-325087(1) | OPEN LINE FROM BUS 324445 [2BONDS MILL 69.000] TO BUS 325087 [2CLAY LICK T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1256 324446-324824(1) | OPEN LINE FROM BUS 324446 [2BOND 69.000] TO BUS 324824 [2CLINCH VALL69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8359 | -2.9802e-06 | -0.00034857
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1256 324446-324824(1) | OPEN LINE FROM BUS 324446 [2BOND 69.000] TO BUS 324824 [2CLINCH VALL69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1257 324446-324977(1) | OPEN LINE FROM BUS 324446 [2BOND 69.000] TO BUS 324977 [2TOMS CRK TP69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 1.1325e-06 | -0.00034446
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1257 324446-324977(1) | OPEN LINE FROM BUS 324446 [2BOND 69.000] TO BUS 324977 [2TOMS CRK TP69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1258 324447-324731(1) | OPEN LINE FROM BUS 324447 [2BONNIE KU 69.000] TO BUS 324731 [2SONORA TAP 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -2.6822e-06 | -0.00034827
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1258 324447-324731(1) | OPEN LINE FROM BUS 324447 [2BONNIE KU 69.000] TO BUS 324731 [2SONORA TAP 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1259 324448-324782(1) | OPEN LINE FROM BUS 324448 [2BOONE AVE 69.000] TO BUS 324782 [2WINCHEST SO69.000] CKT 1 | 0.93965 | 64.8362 | 0.93903 | 64.7927 | -0.00062907 | -0.00097466
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1259 324448-324782(1) | OPEN LINE FROM BUS 324448 [2BOONE AVE 69.000] TO BUS 324782 [2WINCHEST SO69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1260 324448-325004(1) | OPEN LINE FROM BUS 324448 [2BOONE AVE 69.000] TO BUS 325004 [2WINCHES WTR69.000] CKT 1 | 0.93965 | 64.8362 | 0.93933 | 64.8135 | -0.00032794 | -0.00067353
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1260 324448-325004(1) | OPEN LINE FROM BUS 324448 [2BOONE AVE 69.000] TO BUS 325004 [2WINCHES WTR69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1261 324449-325004(1) | OPEN LINE FROM BUS 324449 [2BOONSBORO N69.000] TO BUS 325004 [2WINCHES WTR69.000] CKT 1 | 0.93965 | 64.8362 | 0.93924 | 64.8075 | -0.00041491 | -0.0007605
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1261 324449-325004(1) | OPEN LINE FROM BUS 324449 [2BOONSBORO N69.000] TO BUS 325004 [2WINCHES WTR69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1262 324449-325925(1) | OPEN LINE FROM BUS 324449 [2BOONSBORO N69.000] TO BUS 325925 [4BOONSBORO N138.00] CKT 1 | 0.93965 | 64.8362 | 0.93913 | 64.7999 | -0.00052595 | -0.00087154
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1262 324449-325925(1) | OPEN LINE FROM BUS 324449 [2BOONSBORO N69.000] TO BUS 325925 [4BOONSBORO N138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1263 324450-324494(1) | OPEN LINE FROM BUS 324450 [2BOYLE CO 69.000] TO BUS 324494 [2DANVILLE 1 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 2.4438e-06 | -0.00034314
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1263 324450-324494(1) | OPEN LINE FROM BUS 324450 [2BOYLE CO 69.000] TO BUS 324494 [2DANVILLE 1 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1264 324451-324574(1) | OPEN LINE FROM BUS 324451 [2BRECKNRIDGE69.000] TO BUS 324574 [2HILLCREST 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.0133e-06 | -0.0003466
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1264 324451-324574(1) | OPEN LINE FROM BUS 324451 [2BRECKNRIDGE69.000] TO BUS 324574 [2HILLCREST 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1265 324451-324673(1) | OPEN LINE FROM BUS 324451 [2BRECKNRIDGE69.000] TO BUS 324673 [2OXMOOR 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.1325e-06 | -0.00034672
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1265 324451-324673(1) | OPEN LINE FROM BUS 324451 [2BRECKNRIDGE69.000] TO BUS 324673 [2OXMOOR 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1266 324453-324475(1) | OPEN LINE FROM BUS 324453 [2BEARGRS PMP69.000] TO BUS 324475 [2CLIFTON 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.1921e-07 | -0.00034571
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1266 324453-324475(1) | OPEN LINE FROM BUS 324453 [2BEARGRS PMP69.000] TO BUS 324475 [2CLIFTON 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1267 324455-324966(1) | OPEN LINE FROM BUS 324455 [2BROMLEY 69.000] TO BUS 324966 [2SPARTA KU 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93937 | 64.8166 | -0.00028354 | -0.00062913
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1267 324455-324966(1) | OPEN LINE FROM BUS 324455 [2BROMLEY 69.000] TO BUS 324966 [2SPARTA KU 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1268 324456-324465(1) | OPEN LINE FROM BUS 324456 [2BRUSH CREEK69.000] TO BUS 324465 [2CARPENTER T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8357 | -7.1526e-06 | -0.00035274
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1268 324456-324465(1) | OPEN LINE FROM BUS 324456 [2BRUSH CREEK69.000] TO BUS 324465 [2CARPENTER T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1269 324456-324593(1) | OPEN LINE FROM BUS 324456 [2BRUSH CREEK69.000] TO BUS 324593 [2KU PARK 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8357 | -7.1526e-06 | -0.00035274
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1269 324456-324593(1) | OPEN LINE FROM BUS 324456 [2BRUSH CREEK69.000] TO BUS 324593 [2KU PARK 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1270 324457-324610(1) | OPEN LINE FROM BUS 324457 [2BUCHANAN 69.000] TO BUS 324610 [2LEX PLANT 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93974 | 64.8421 | 8.601e-05 | -0.00025958
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1270 324457-324610(1) | OPEN LINE FROM BUS 324457 [2BUCHANAN 69.000] TO BUS 324610 [2LEX PLANT 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1271 324457-324986(1) | OPEN LINE FROM BUS 324457 [2BUCHANAN 69.000] TO BUS 324986 [2W HIGH T2 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93973 | 64.8412 | 7.3671e-05 | -0.00027192
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1271 324457-324986(1) | OPEN LINE FROM BUS 324457 [2BUCHANAN 69.000] TO BUS 324986 [2W HIGH T2 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1272 324458-324501(1) | OPEN LINE FROM BUS 324458 [2BUENA VISTA69.000] TO BUS 324501 [2DIX DAM 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93961 | 64.833 | -4.6253e-05 | -0.00039184
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1272 324458-324501(1) | OPEN LINE FROM BUS 324458 [2BUENA VISTA69.000] TO BUS 324501 [2DIX DAM 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1273 324458-324546(1) | OPEN LINE FROM BUS 324458 [2BUENA VISTA69.000] TO BUS 324546 [2GARRARD CT 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93962 | 64.8338 | -3.4571e-05 | -0.00038016
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1273 324458-324546(1) | OPEN LINE FROM BUS 324458 [2BUENA VISTA69.000] TO BUS 324546 [2GARRARD CT 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1274 324459-324626(1) | OPEN LINE FROM BUS 324459 [2BUSH TAP 69.000] TO BUS 324626 [2MANCHEST SO69.000] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8374 | 1.8001e-05 | -0.00032759
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1274 324459-324626(1) | OPEN LINE FROM BUS 324459 [2BUSH TAP 69.000] TO BUS 324626 [2MANCHEST SO69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1275 324459-326533(1) | OPEN LINE FROM BUS 324459 [2BUSH TAP 69.000] TO BUS 326533 [2BUSH EKPC 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93968 | 64.8381 | 2.8729e-05 | -0.00031686
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1275 324459-326533(1) | OPEN LINE FROM BUS 324459 [2BUSH TAP 69.000] TO BUS 326533 [2BUSH EKPC 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1276 324460-324686(1) | OPEN LINE FROM BUS 324460 [2CALLOWAY 69.000] TO BUS 324686 [2PINEVILLE 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.1325e-06 | -0.00034672
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1276 324460-324686(1) | OPEN LINE FROM BUS 324460 [2CALLOWAY 69.000] TO BUS 324686 [2PINEVILLE 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1277 324460-324706(1) | OPEN LINE FROM BUS 324460 [2CALLOWAY 69.000] TO BUS 324706 [2ROCKY BRNCH69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -7.1526e-07 | -0.0003463
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1277 324460-324706(1) | OPEN LINE FROM BUS 324460 [2CALLOWAY 69.000] TO BUS 324706 [2ROCKY BRNCH69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1278 324461-324912(1) | OPEN LINE FROM BUS 324461 [2CAMARGO 69.000] TO BUS 324912 [2MT STERL KU69.000] CKT 1 | 0.93965 | 64.8362 | 0.93968 | 64.8376 | 2.1398e-05 | -0.00032419
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1278 324461-324912(1) | OPEN LINE FROM BUS 324461 [2CAMARGO 69.000] TO BUS 324912 [2MT STERL KU69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1279 324462-324499(1) | OPEN LINE FROM BUS 324462 [2CANAL 69.000] TO BUS 324499 [2DEL PARK 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.0133e-06 | -0.0003466
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1279 324462-324499(1) | OPEN LINE FROM BUS 324462 [2CANAL 69.000] TO BUS 324499 [2DEL PARK 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1280 324462-324624(1) | OPEN LINE FROM BUS 324462 [2CANAL 69.000] TO BUS 324624 [2MADISON LGE69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8356 | -7.6294e-06 | -0.00035322
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1280 324462-324624(1) | OPEN LINE FROM BUS 324462 [2CANAL 69.000] TO BUS 324624 [2MADISON LGE69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1281 324462-324625(1) | OPEN LINE FROM BUS 324462 [2CANAL 69.000] TO BUS 324625 [2MAGAZINE 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 2.2054e-06 | -0.00034338
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1281 324462-324625(1) | OPEN LINE FROM BUS 324462 [2CANAL 69.000] TO BUS 324625 [2MAGAZINE 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1282 324462-324665(1) | OPEN LINE FROM BUS 324462 [2CANAL 69.000] TO BUS 324665 [2OHIO FALL 169.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8358 | -4.4107e-06 | -0.00035
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1282 324462-324665(1) | OPEN LINE FROM BUS 324462 [2CANAL 69.000] TO BUS 324665 [2OHIO FALL 169.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1283 324462-324666(1) | OPEN LINE FROM BUS 324462 [2CANAL 69.000] TO BUS 324666 [2OHIO FALL 269.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8359 | -4.2915e-06 | -0.00034988
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1283 324462-324666(1) | OPEN LINE FROM BUS 324462 [2CANAL 69.000] TO BUS 324666 [2OHIO FALL 269.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1284 324464-324615(1) | OPEN LINE FROM BUS 324464 [2CARON 69.000] TO BUS 324615 [2LONDON 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93968 | 64.8378 | 2.3127e-05 | -0.00032246
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1284 324464-324615(1) | OPEN LINE FROM BUS 324464 [2CARON 69.000] TO BUS 324615 [2LONDON 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
324464 | 2CARON | 69 | LGEE' | RANGE | 0.94 | 1.06 | SINGLE OPN LIN 1284 324464-324615(1) | OPEN LINE FROM BUS 324464 [2CARON 69.000] TO BUS 324615 [2LONDON 69.000] CKT 1 | 0.969 | 66.8609 | 0.93999 | 64.8593 | -0.029009 | -1.0014e-05
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1285 324464-324860(1) | OPEN LINE FROM BUS 324464 [2CARON 69.000] TO BUS 324860 [2FARISTON 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8367 | 7.2718e-06 | -0.00033832
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1285 324464-324860(1) | OPEN LINE FROM BUS 324464 [2CARON 69.000] TO BUS 324860 [2FARISTON 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1286 324465-324784(1) | OPEN LINE FROM BUS 324465 [2CARPENTER T69.000] TO BUS 324784 [2WOFFORD 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.0133e-06 | -0.0003466
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1286 324465-324784(1) | OPEN LINE FROM BUS 324465 [2CARPENTER T69.000] TO BUS 324784 [2WOFFORD 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1287 324465-326535(1) | OPEN LINE FROM BUS 324465 [2CARPENTER T69.000] TO BUS 326535 [2CARPENTER 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93968 | 64.8381 | 2.7597e-05 | -0.00031799
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1287 324465-326535(1) | OPEN LINE FROM BUS 324465 [2CARPENTER T69.000] TO BUS 326535 [2CARPENTER 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1288 324466-324602(1) | OPEN LINE FROM BUS 324466 [2CARROLLTON 69.000] TO BUS 324602 [2LAWRENCE TP69.000] CKT 1 | 0.93965 | 64.8362 | 0.93963 | 64.8345 | -2.4259e-05 | -0.00036985
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1288 324466-324602(1) | OPEN LINE FROM BUS 324466 [2CARROLLTON 69.000] TO BUS 324602 [2LAWRENCE TP69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1289 324466-324634(1) | OPEN LINE FROM BUS 324466 [2CARROLLTON 69.000] TO BUS 324634 [2METAL+THERM69.000] CKT 1 | 0.93965 | 64.8362 | 0.93979 | 64.8457 | 0.00013846 | -0.00020713
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1289 324466-324634(1) | OPEN LINE FROM BUS 324466 [2CARROLLTON 69.000] TO BUS 324634 [2METAL+THERM69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1290 324467-324528(1) | OPEN LINE FROM BUS 324467 [2CAVE RUN TP69.000] TO BUS 324528 [2FARMERS 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93963 | 64.8346 | -2.265e-05 | -0.00036824
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1290 324467-324528(1) | OPEN LINE FROM BUS 324467 [2CAVE RUN TP69.000] TO BUS 324528 [2FARMERS 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1291 324467-324714(1) | OPEN LINE FROM BUS 324467 [2CAVE RUN TP69.000] TO BUS 324714 [2SALT LICK 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93962 | 64.8339 | -3.2425e-05 | -0.00037801
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1291 324467-324714(1) | OPEN LINE FROM BUS 324467 [2CAVE RUN TP69.000] TO BUS 324714 [2SALT LICK 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1292 324467-326538(1) | OPEN LINE FROM BUS 324467 [2CAVE RUN TP69.000] TO BUS 326538 [2CAVE RUN 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93969 | 64.8387 | 3.7611e-05 | -0.00030798
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1292 324467-326538(1) | OPEN LINE FROM BUS 324467 [2CAVE RUN TP69.000] TO BUS 326538 [2CAVE RUN 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1293 324468-324572(1) | OPEN LINE FROM BUS 324468 [2CENTRL CI S69.000] TO BUS 324572 [2HILLSIDE 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 0 | -0.00034559
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1293 324468-324572(1) | OPEN LINE FROM BUS 324468 [2CENTRL CI S69.000] TO BUS 324572 [2HILLSIDE 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1294 324468-324817(1) | OPEN LINE FROM BUS 324468 [2CENTRL CI S69.000] TO BUS 324817 [2CENTRAL CIT69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 0 | -0.00034559
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1294 324468-324817(1) | OPEN LINE FROM BUS 324468 [2CENTRL CI S69.000] TO BUS 324817 [2CENTRAL CIT69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1295 324469-324681(1) | OPEN LINE FROM BUS 324469 [2CENTERFIELD69.000] TO BUS 324681 [2PENAL FARM 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8357 | -6.4969e-06 | -0.00035208
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1295 324469-324681(1) | OPEN LINE FROM BUS 324469 [2CENTERFIELD69.000] TO BUS 324681 [2PENAL FARM 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1296 324469-324682(1) | OPEN LINE FROM BUS 324469 [2CENTERFIELD69.000] TO BUS 324682 [2PENAL TAP 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93973 | 64.8415 | 7.7307e-05 | -0.00026828
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1296 324469-324682(1) | OPEN LINE FROM BUS 324469 [2CENTERFIELD69.000] TO BUS 324682 [2PENAL TAP 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1297 324470-324486(1) | OPEN LINE FROM BUS 324470 [2CERRO-SALEM69.000] TO BUS 324486 [2CRITTENDEN 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 5.9605e-07 | -0.00034499
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1297 324470-324486(1) | OPEN LINE FROM BUS 324470 [2CERRO-SALEM69.000] TO BUS 324486 [2CRITTENDEN 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1298 324470-324948(1) | OPEN LINE FROM BUS 324470 [2CERRO-SALEM69.000] TO BUS 324948 [2SALEM KU 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 5.3644e-07 | -0.00034505
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1298 324470-324948(1) | OPEN LINE FROM BUS 324470 [2CERRO-SALEM69.000] TO BUS 324948 [2SALEM KU 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1299 324471-324777(1) | OPEN LINE FROM BUS 324471 [2CHRISTIAN 69.000] TO BUS 324777 [2WHEATCROFT 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 1.1921e-07 | -0.00034547
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1299 324471-324777(1) | OPEN LINE FROM BUS 324471 [2CHRISTIAN 69.000] TO BUS 324777 [2WHEATCROFT 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1300 324471-324822(1) | OPEN LINE FROM BUS 324471 [2CHRISTIAN 69.000] TO BUS 324822 [2CLAY KU 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 5.9605e-08 | -0.00034553
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1300 324471-324822(1) | OPEN LINE FROM BUS 324471 [2CHRISTIAN 69.000] TO BUS 324822 [2CLAY KU 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1301 324472-324540(1) | OPEN LINE FROM BUS 324472 [2CLARK CO 69.000] TO BUS 324540 [2FOGG PIKE T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93956 | 64.8295 | -9.7096e-05 | -0.00044268
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1301 324472-324540(1) | OPEN LINE FROM BUS 324472 [2CLARK CO 69.000] TO BUS 324540 [2FOGG PIKE T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1302 324472-324749(1) | OPEN LINE FROM BUS 324472 [2CLARK CO 69.000] TO BUS 324749 [2SYLVANIA 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93969 | 64.8384 | 3.1888e-05 | -0.0003137
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1302 324472-324749(1) | OPEN LINE FROM BUS 324472 [2CLARK CO 69.000] TO BUS 324749 [2SYLVANIA 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1303 324473-324561(1) | OPEN LINE FROM BUS 324473 [2CLAY LGE 69.000] TO BUS 324561 [2HANCOCK 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 3.2783e-06 | -0.00034231
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1303 324473-324561(1) | OPEN LINE FROM BUS 324473 [2CLAY LGE 69.000] TO BUS 324561 [2HANCOCK 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1304 324473-324570(1) | OPEN LINE FROM BUS 324473 [2CLAY LGE 69.000] TO BUS 324570 [2HIGHLAND 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -1.967e-06 | -0.00034755
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1304 324473-324570(1) | OPEN LINE FROM BUS 324473 [2CLAY LGE 69.000] TO BUS 324570 [2HIGHLAND 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1305 324473-324624(1) | OPEN LINE FROM BUS 324473 [2CLAY LGE 69.000] TO BUS 324624 [2MADISON LGE69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -1.7285e-06 | -0.00034732
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1305 324473-324624(1) | OPEN LINE FROM BUS 324473 [2CLAY LGE 69.000] TO BUS 324624 [2MADISON LGE69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1306 324474-324725(1) | OPEN LINE FROM BUS 324474 [2CLAY VILG T69.000] TO BUS 324725 [2SHELBYVIL E69.000] CKT 1 | 0.93965 | 64.8362 | 0.93976 | 64.8437 | 0.00010926 | -0.00023633
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1306 324474-324725(1) | OPEN LINE FROM BUS 324474 [2CLAY VILG T69.000] TO BUS 324725 [2SHELBYVIL E69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1307 324474-324765(1) | OPEN LINE FROM BUS 324474 [2CLAY VILG T69.000] TO BUS 324765 [2W FRANKFORT69.000] CKT 1 | 0.93965 | 64.8362 | 0.93961 | 64.8334 | -4.0352e-05 | -0.00038594
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1307 324474-324765(1) | OPEN LINE FROM BUS 324474 [2CLAY VILG T69.000] TO BUS 324765 [2W FRANKFORT69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1308 324475-324574(1) | OPEN LINE FROM BUS 324475 [2CLIFTON 69.000] TO BUS 324574 [2HILLCREST 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 0 | -0.00034559
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1308 324475-324574(1) | OPEN LINE FROM BUS 324475 [2CLIFTON 69.000] TO BUS 324574 [2HILLCREST 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1309 324476-324581(1) | OPEN LINE FROM BUS 324476 [2CMC TAP 69.000] TO BUS 324581 [2HUGHES LANE69.000] CKT 1 | 0.93965 | 64.8362 | 0.93914 | 64.8005 | -0.00051737 | -0.00086296
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1309 324476-324581(1) | OPEN LINE FROM BUS 324476 [2CMC TAP 69.000] TO BUS 324581 [2HUGHES LANE69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1310 324476-324680(1) | OPEN LINE FROM BUS 324476 [2CMC TAP 69.000] TO BUS 324680 [2PARIS KU 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1311 324477-324502(1) | OPEN LINE FROM BUS 324477 [2CAMP BRECKN69.000] TO BUS 324502 [2DIXON KU 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 1.1921e-07 | -0.00034547
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1311 324477-324502(1) | OPEN LINE FROM BUS 324477 [2CAMP BRECKN69.000] TO BUS 324502 [2DIXON KU 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1312 324477-324645(1) | OPEN LINE FROM BUS 324477 [2CAMP BRECKN69.000] TO BUS 324645 [2MORGANFIELD69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 1.7881e-07 | -0.00034541
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1312 324477-324645(1) | OPEN LINE FROM BUS 324477 [2CAMP BRECKN69.000] TO BUS 324645 [2MORGANFIELD69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1313 324478-324516(1) | OPEN LINE FROM BUS 324478 [2CAMPBELBURG69.000] TO BUS 324516 [2EMINENCE KU69.000] CKT 1 | 0.93965 | 64.8362 | 0.93963 | 64.8343 | -2.7478e-05 | -0.00037307
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1313 324478-324516(1) | OPEN LINE FROM BUS 324478 [2CAMPBELBURG69.000] TO BUS 324516 [2EMINENCE KU69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1314 324478-324828(1) | OPEN LINE FROM BUS 324478 [2CAMPBELBURG69.000] TO BUS 324828 [2CAMPBBRG KU69.000] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8349 | -1.8537e-05 | -0.00036412
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1314 324478-324828(1) | OPEN LINE FROM BUS 324478 [2CAMPBELBURG69.000] TO BUS 324828 [2CAMPBBRG KU69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1315 324479-324751(1) | OPEN LINE FROM BUS 324479 [2CAMPBELVL T69.000] TO BUS 324751 [2TAYLOR CO 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.3709e-06 | -0.00034696
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1315 324479-324751(1) | OPEN LINE FROM BUS 324479 [2CAMPBELVL T69.000] TO BUS 324751 [2TAYLOR CO 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1316 324479-324889(1) | OPEN LINE FROM BUS 324479 [2CAMPBELVL T69.000] TO BUS 324889 [2LEBANON SO 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -5.3644e-07 | -0.00034612
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1316 324479-324889(1) | OPEN LINE FROM BUS 324479 [2CAMPBELVL T69.000] TO BUS 324889 [2LEBANON SO 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1317 324480-324515(1) | OPEN LINE FROM BUS 324480 [2CMPGND EK T69.000] TO BUS 324515 [2EMANUEL TAP69.000] CKT 1 | 0.93965 | 64.8362 | 0.9396 | 64.8326 | -5.2035e-05 | -0.00039762
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1317 324480-324515(1) | OPEN LINE FROM BUS 324480 [2CMPGND EK T69.000] TO BUS 324515 [2EMANUEL TAP69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1318 324480-324615(1) | OPEN LINE FROM BUS 324480 [2CMPGND EK T69.000] TO BUS 324615 [2LONDON 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8351 | -1.4782e-05 | -0.00036037
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1318 324480-324615(1) | OPEN LINE FROM BUS 324480 [2CMPGND EK T69.000] TO BUS 324615 [2LONDON 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1319 324480-326521(1) | OPEN LINE FROM BUS 324480 [2CMPGND EK T69.000] TO BUS 326521 [2CAMPGRND EK69.000] CKT 1 | 0.93965 | 64.8362 | 0.9397 | 64.8394 | 4.7147e-05 | -0.00029844
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1319 324480-326521(1) | OPEN LINE FROM BUS 324480 [2CMPGND EK T69.000] TO BUS 326521 [2CAMPGRND EK69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1320 324481-324487(1) | OPEN LINE FROM BUS 324481 [2COLLINS 69.000] TO BUS 324487 [2CRESTWOOD 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -4.7684e-07 | -0.00034606
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1320 324481-324487(1) | OPEN LINE FROM BUS 324481 [2COLLINS 69.000] TO BUS 324487 [2CRESTWOOD 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1321 324481-324541(1) | OPEN LINE FROM BUS 324481 [2COLLINS 69.000] TO BUS 324541 [2FORD 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -2.2054e-06 | -0.00034779
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1321 324481-324541(1) | OPEN LINE FROM BUS 324481 [2COLLINS 69.000] TO BUS 324541 [2FORD 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1322 324482-324748(1) | OPEN LINE FROM BUS 324482 [2CORBIN EAST69.000] TO BUS 324748 [2SWEET HOLLO69.000] CKT 1 | 0.93965 | 64.8362 | 0.93962 | 64.8339 | -3.2365e-05 | -0.00037795
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1322 324482-324748(1) | OPEN LINE FROM BUS 324482 [2CORBIN EAST69.000] TO BUS 324748 [2SWEET HOLLO69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1323 324482-324832(1) | OPEN LINE FROM BUS 324482 [2CORBIN EAST69.000] TO BUS 324832 [2CORBIN 1 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93959 | 64.8318 | -6.3121e-05 | -0.00040871
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1323 324482-324832(1) | OPEN LINE FROM BUS 324482 [2CORBIN EAST69.000] TO BUS 324832 [2CORBIN 1 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1324 324484-324571(1) | OPEN LINE FROM BUS 324484 [2CORYDON 69.000] TO BUS 324571 [2HIGHLAND MI69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -2.9802e-07 | -0.00034589
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1324 324484-324571(1) | OPEN LINE FROM BUS 324484 [2CORYDON 69.000] TO BUS 324571 [2HIGHLAND MI69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1325 324484-324711(1) | OPEN LINE FROM BUS 324484 [2CORYDON 69.000] TO BUS 324711 [2SPEN CHEM T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 2.3246e-06 | -0.00034326
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1325 324484-324711(1) | OPEN LINE FROM BUS 324484 [2CORYDON 69.000] TO BUS 324711 [2SPEN CHEM T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
324093 | 2SPEN CHEMIC | 69 | LGEE' | RANGE | 0.94 | 1.06 | SINGLE OPN LIN 1325 324484-324711(1) | OPEN LINE FROM BUS 324484 [2CORYDON 69.000] TO BUS 324711 [2SPEN CHEM T69.000] CKT 1 | 0.99977 | 68.9839 | 0.92636 | 63.9188 | -0.073407 | -0.013641
324711 | 2SPEN CHEM T | 69 | LGEE' | RANGE | 0.94 | 1.06 | SINGLE OPN LIN 1325 324484-324711(1) | OPEN LINE FROM BUS 324484 [2CORYDON 69.000] TO BUS 324711 [2SPEN CHEM T69.000] CKT 1 | 1.001 | 69.0686 | 0.92768 | 64.0103 | -0.073309 | -0.012315
324786 | 2ZION | 69 | LGEE' | RANGE | 0.94 | 1.06 | SINGLE OPN LIN 1325 324484-324711(1) | OPEN LINE FROM BUS 324484 [2CORYDON 69.000] TO BUS 324711 [2SPEN CHEM T69.000] CKT 1 | 0.99254 | 68.4852 | 0.9365 | 64.6188 | -0.056034 | -0.003495
324790 | 2AIRLINE RD | 69 | LGEE' | RANGE | 0.94 | 1.06 | SINGLE OPN LIN 1325 324484-324711(1) | OPEN LINE FROM BUS 324484 [2CORYDON 69.000] TO BUS 324711 [2SPEN CHEM T69.000] CKT 1 | 0.99598 | 68.7229 | 0.93086 | 64.2296 | -0.06512 | -0.0091367
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1326 324485-324600(1) | OPEN LINE FROM BUS 324485 [2CRAB ORCH T69.000] TO BUS 324600 [2LANCASTR KU69.000] CKT 1 | 0.93965 | 64.8362 | 0.9396 | 64.8321 | -5.8055e-05 | -0.00040364
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1326 324485-324600(1) | OPEN LINE FROM BUS 324485 [2CRAB ORCH T69.000] TO BUS 324600 [2LANCASTR KU69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1327 324485-324808(1) | OPEN LINE FROM BUS 324485 [2CRAB ORCH T69.000] TO BUS 324808 [2BRODHEAD KU69.000] CKT 1 | 0.93965 | 64.8362 | 0.93961 | 64.8328 | -4.9233e-05 | -0.00039482
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1327 324485-324808(1) | OPEN LINE FROM BUS 324485 [2CRAB ORCH T69.000] TO BUS 324808 [2BRODHEAD KU69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1328 324486-324628(1) | OPEN LINE FROM BUS 324486 [2CRITTENDEN 69.000] TO BUS 324628 [2MARION SO 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 1.6093e-06 | -0.00034398
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1328 324486-324628(1) | OPEN LINE FROM BUS 324486 [2CRITTENDEN 69.000] TO BUS 324628 [2MARION SO 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 1.1921e-07 | 1.1921e-07
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1329 324488-324529(1) | OPEN LINE FROM BUS 324488 [2CANE RUN SW69.000] TO BUS 324529 [2FARNSLEY 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 2.3842e-07 | -0.00034535
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1329 324488-324529(1) | OPEN LINE FROM BUS 324488 [2CANE RUN SW69.000] TO BUS 324529 [2FARNSLEY 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1330 324488-324724(1) | OPEN LINE FROM BUS 324488 [2CANE RUN SW69.000] TO BUS 324724 [2SHIVELY 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 4.7684e-07 | -0.00034511
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1330 324488-324724(1) | OPEN LINE FROM BUS 324488 [2CANE RUN SW69.000] TO BUS 324724 [2SHIVELY 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1331 324488-324739(1) | OPEN LINE FROM BUS 324488 [2CANE RUN SW69.000] TO BUS 324739 [2STEWART 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 1.1325e-06 | -0.00034446
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1331 324488-324739(1) | OPEN LINE FROM BUS 324488 [2CANE RUN SW69.000] TO BUS 324739 [2STEWART 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1332 324489-324654(1) | OPEN LINE FROM BUS 324489 [2CUMB FALL T69.000] TO BUS 324654 [2MT VIC EK J69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8358 | -5.4836e-06 | -0.00035107
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1332 324489-324654(1) | OPEN LINE FROM BUS 324489 [2CUMB FALL T69.000] TO BUS 324654 [2MT VIC EK J69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1333 324489-324784(1) | OPEN LINE FROM BUS 324489 [2CUMB FALL T69.000] TO BUS 324784 [2WOFFORD 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 1.6689e-06 | -0.00034392
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1333 324489-324784(1) | OPEN LINE FROM BUS 324489 [2CUMB FALL T69.000] TO BUS 324784 [2WOFFORD 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1334 324489-325034(1) | OPEN LINE FROM BUS 324489 [2CUMB FALL T69.000] TO BUS 325034 [2CUMBER FALL69.000] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8374 | 1.8358e-05 | -0.00032723
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1334 324489-325034(1) | OPEN LINE FROM BUS 324489 [2CUMB FALL T69.000] TO BUS 325034 [2CUMBER FALL69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1335 324490-324827(1) | OPEN LINE FROM BUS 324490 [2CUMBERLAND 69.000] TO BUS 324827 [2CLOVERLICK 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8365 | 4.7088e-06 | -0.00034088
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1335 324490-324827(1) | OPEN LINE FROM BUS 324490 [2CUMBERLAND 69.000] TO BUS 324827 [2CLOVERLICK 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1336 324491-324837(1) | OPEN LINE FROM BUS 324491 [2CYNTHIAN SO69.000] TO BUS 324837 [2CYNTHIAN KU69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1337 324491-325085(1) | OPEN LINE FROM BUS 324491 [2CYNTHIAN SO69.000] TO BUS 325085 [2CYNTHI EK T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1338 324492-324595(1) | OPEN LINE FROM BUS 324492 [2CYNTHIAN SW69.000] TO BUS 324595 [2KAWNEER 69.000] CKT 1 | 0.93965 | 64.8362 | 0.9385 | 64.7564 | -0.0011559 | -0.0015015
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1338 324492-324595(1) | OPEN LINE FROM BUS 324492 [2CYNTHIAN SW69.000] TO BUS 324595 [2KAWNEER 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1339 324493-324518(1) | OPEN LINE FROM BUS 324493 [2DAHLIA 69.000] TO BUS 324518 [2ETHEL 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -3.5763e-07 | -0.00034595
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1339 324493-324518(1) | OPEN LINE FROM BUS 324493 [2DAHLIA 69.000] TO BUS 324518 [2ETHEL 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1340 324493-324570(1) | OPEN LINE FROM BUS 324493 [2DAHLIA 69.000] TO BUS 324570 [2HIGHLAND 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 1.1921e-07 | -0.00034547
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1340 324493-324570(1) | OPEN LINE FROM BUS 324493 [2DAHLIA 69.000] TO BUS 324570 [2HIGHLAND 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1341 324494-324840(1) | OPEN LINE FROM BUS 324494 [2DANVILLE 1 69.000] TO BUS 324840 [2DANVILLE E 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 2.9802e-07 | -0.00034529
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1341 324494-324840(1) | OPEN LINE FROM BUS 324494 [2DANVILLE 1 69.000] TO BUS 324840 [2DANVILLE E 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1342 324495-326579(1) | OPEN LINE FROM BUS 324495 [2DANVILLE N 69.000] TO BUS 326579 [2HARRDSBRG 269.000] CKT 1 | 0.93965 | 64.8362 | 0.93963 | 64.8348 | -1.9431e-05 | -0.00036502
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1342 324495-326579(1) | OPEN LINE FROM BUS 324495 [2DANVILLE N 69.000] TO BUS 326579 [2HARRDSBRG 269.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1343 324496-324767(1) | OPEN LINE FROM BUS 324496 [2DARK HOLLOW69.000] TO BUS 324767 [2WEST IRVINE69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8357 | -6.0201e-06 | -0.00035161
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1343 324496-324767(1) | OPEN LINE FROM BUS 324496 [2DARK HOLLOW69.000] TO BUS 324767 [2WEST IRVINE69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1344 324496-324880(1) | OPEN LINE FROM BUS 324496 [2DARK HOLLOW69.000] TO BUS 324880 [2IRVINE 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -2.8014e-06 | -0.00034839
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1344 324496-324880(1) | OPEN LINE FROM BUS 324496 [2DARK HOLLOW69.000] TO BUS 324880 [2IRVINE 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1345 324497-324564(1) | OPEN LINE FROM BUS 324497 [2DAYHOIT TAP69.000] TO BUS 324564 [2HARLAN WYE 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.0133e-06 | -0.0003466
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1345 324497-324564(1) | OPEN LINE FROM BUS 324497 [2DAYHOIT TAP69.000] TO BUS 324564 [2HARLAN WYE 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1346 324497-324588(1) | OPEN LINE FROM BUS 324497 [2DAYHOIT TAP69.000] TO BUS 324588 [2KENTENIA 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.7881e-07 | -0.00034577
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1346 324497-324588(1) | OPEN LINE FROM BUS 324497 [2DAYHOIT TAP69.000] TO BUS 324588 [2KENTENIA 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1347 324498-324621(1) | OPEN LINE FROM BUS 324498 [2DAYS BRANCH69.000] TO BUS 324621 [2LYNCH 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -2.1458e-06 | -0.00034773
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1347 324498-324621(1) | OPEN LINE FROM BUS 324498 [2DAYS BRANCH69.000] TO BUS 324621 [2LYNCH 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1348 324498-324876(1) | OPEN LINE FROM BUS 324498 [2DAYS BRANCH69.000] TO BUS 324876 [2HOLMES MILL69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8359 | -4.3511e-06 | -0.00034994
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1348 324498-324876(1) | OPEN LINE FROM BUS 324498 [2DAYS BRANCH69.000] TO BUS 324876 [2HOLMES MILL69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1349 324499-324552(1) | OPEN LINE FROM BUS 324499 [2DEL PARK 69.000] TO BUS 324552 [2GRADY 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 3.0994e-06 | -0.00034249
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1349 324499-324552(1) | OPEN LINE FROM BUS 324499 [2DEL PARK 69.000] TO BUS 324552 [2GRADY 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1350 324500-324924(1) | OPEN LINE FROM BUS 324500 [2DELAPLAIN T69.000] TO BUS 324924 [2OXFORD 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93955 | 64.8286 | -0.00010884 | -0.00045443
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1350 324500-324924(1) | OPEN LINE FROM BUS 324500 [2DELAPLAIN T69.000] TO BUS 324924 [2OXFORD 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1351 324501-324764(1) | OPEN LINE FROM BUS 324501 [2DIX DAM 69.000] TO BUS 324764 [2WEST CLIFF 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8352 | -1.4067e-05 | -0.00035965
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1351 324501-324764(1) | OPEN LINE FROM BUS 324501 [2DIX DAM 69.000] TO BUS 324764 [2WEST CLIFF 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1352 324502-324658(1) | OPEN LINE FROM BUS 324502 [2DIXON KU 69.000] TO BUS 324658 [2NEBO 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 0 | -0.00034559
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1352 324502-324658(1) | OPEN LINE FROM BUS 324502 [2DIXON KU 69.000] TO BUS 324658 [2NEBO 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1353 324503-325064(1) | OPEN LINE FROM BUS 324503 [2DORCHESTER 69.000] TO BUS 325064 [2LAUREL GROV69.000] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8374 | 1.7762e-05 | -0.00032783
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1353 324503-325064(1) | OPEN LINE FROM BUS 324503 [2DORCHESTER 69.000] TO BUS 325064 [2LAUREL GROV69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1354 324504-324662(1) | OPEN LINE FROM BUS 324504 [2E BERNST KU69.000] TO BUS 324662 [2N LONDON KU69.000] CKT 1 | 0.93965 | 64.8362 | 0.93961 | 64.833 | -4.5478e-05 | -0.00039107
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1354 324504-324662(1) | OPEN LINE FROM BUS 324504 [2E BERNST KU69.000] TO BUS 324662 [2N LONDON KU69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1355 324504-324927(1) | OPEN LINE FROM BUS 324504 [2E BERNST KU69.000] TO BUS 324927 [2PINE HILL T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93957 | 64.8306 | -8.0585e-05 | -0.00042617
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1355 324504-324927(1) | OPEN LINE FROM BUS 324504 [2E BERNST KU69.000] TO BUS 324927 [2PINE HILL T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1356 324505-324506(1) | OPEN LINE FROM BUS 324505 [2E DIAMOND 69.000] TO BUS 324506 [2EARLINGTN N69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 1.3709e-06 | -0.00034422
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1356 324505-324506(1) | OPEN LINE FROM BUS 324505 [2E DIAMOND 69.000] TO BUS 324506 [2EARLINGTN N69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1357 324505-324947(1) | OPEN LINE FROM BUS 324505 [2E DIAMOND 69.000] TO BUS 324947 [2RUMSEY 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 8.9407e-07 | -0.00034469
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1357 324505-324947(1) | OPEN LINE FROM BUS 324505 [2E DIAMOND 69.000] TO BUS 324947 [2RUMSEY 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1358 324506-324769(1) | OPEN LINE FROM BUS 324506 [2EARLINGTN N69.000] TO BUS 324769 [2WALKER KU 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 9.5367e-07 | -0.00034463
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1358 324506-324769(1) | OPEN LINE FROM BUS 324506 [2EARLINGTN N69.000] TO BUS 324769 [2WALKER KU 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1359 324506-324954(1) | OPEN LINE FROM BUS 324506 [2EARLINGTN N69.000] TO BUS 324954 [2SENTRY TAP 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.1921e-07 | -0.00034571
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1359 324506-324954(1) | OPEN LINE FROM BUS 324506 [2EARLINGTN N69.000] TO BUS 324954 [2SENTRY TAP 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1360 324507-324769(1) | OPEN LINE FROM BUS 324507 [2EARLINGTON 69.000] TO BUS 324769 [2WALKER KU 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 1.0133e-06 | -0.00034457
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1360 324507-324769(1) | OPEN LINE FROM BUS 324507 [2EARLINGTON 69.000] TO BUS 324769 [2WALKER KU 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1361 324507-324850(1) | OPEN LINE FROM BUS 324507 [2EARLINGTON 69.000] TO BUS 324850 [2DOZIER H 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 3.5763e-07 | -0.00034523
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1361 324507-324850(1) | OPEN LINE FROM BUS 324507 [2EARLINGTON 69.000] TO BUS 324850 [2DOZIER H 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1362 324508-324617(1) | OPEN LINE FROM BUS 324508 [2EASTLAND 69.000] TO BUS 324617 [2LOUDON 618 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93913 | 64.8 | -0.0005241 | -0.00086969
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1362 324508-324617(1) | OPEN LINE FROM BUS 324508 [2EASTLAND 69.000] TO BUS 324617 [2LOUDON 618 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1363 324509-324914(1) | OPEN LINE FROM BUS 324509 [2EASTVIEW 69.000] TO BUS 324914 [2M-V CLARK T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -1.6689e-06 | -0.00034726
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1363 324509-324914(1) | OPEN LINE FROM BUS 324509 [2EASTVIEW 69.000] TO BUS 324914 [2M-V CLARK T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1364 324510-324729(1) | OPEN LINE FROM BUS 324510 [2EASTWOOD 69.000] TO BUS 324729 [2SIMPSONVILL69.000] CKT 1 | 0.93965 | 64.8362 | 0.9397 | 64.8395 | 4.9174e-05 | -0.00029641
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1364 324510-324729(1) | OPEN LINE FROM BUS 324510 [2EASTWOOD 69.000] TO BUS 324729 [2SIMPSONVILL69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1365 324511-324584(1) | OPEN LINE FROM BUS 324511 [2ECHOLS 69.000] TO BUS 324584 [2INDIAN HILL69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 6.5565e-07 | -0.00034493
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1365 324511-324584(1) | OPEN LINE FROM BUS 324511 [2ECHOLS 69.000] TO BUS 324584 [2INDIAN HILL69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1366 324511-324959(1) | OPEN LINE FROM BUS 324511 [2ECHOLS 69.000] TO BUS 324959 [2SIMMONS 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 6.5565e-07 | -0.00034493
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1366 324511-324959(1) | OPEN LINE FROM BUS 324511 [2ECHOLS 69.000] TO BUS 324959 [2SIMMONS 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1367 324512-324693(1) | OPEN LINE FROM BUS 324512 [2EDDYV PR TP69.000] TO BUS 324693 [2PRINCETON 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8365 | 4.4703e-06 | -0.00034112
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1367 324512-324693(1) | OPEN LINE FROM BUS 324512 [2EDDYV PR TP69.000] TO BUS 324693 [2PRINCETON 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1368 324513-324693(1) | OPEN LINE FROM BUS 324513 [2EDDYVILLE 69.000] TO BUS 324693 [2PRINCETON 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | -5.9605e-08 | -0.00034565
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1368 324513-324693(1) | OPEN LINE FROM BUS 324513 [2EDDYVILLE 69.000] TO BUS 324693 [2PRINCETON 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1369 324513-324885(1) | OPEN LINE FROM BUS 324513 [2EDDYVILLE 69.000] TO BUS 324885 [2KUTTAWA 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 2.3842e-07 | -0.00034535
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1369 324513-324885(1) | OPEN LINE FROM BUS 324513 [2EDDYVILLE 69.000] TO BUS 324885 [2KUTTAWA 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1370 324514-324531(1) | OPEN LINE FROM BUS 324514 [2ELIHU 69.000] TO BUS 324531 [2FERGUSON SO69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8359 | -3.9935e-06 | -0.00034958
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1370 324514-324531(1) | OPEN LINE FROM BUS 324514 [2ELIHU 69.000] TO BUS 324531 [2FERGUSON SO69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1371 324514-324654(1) | OPEN LINE FROM BUS 324514 [2ELIHU 69.000] TO BUS 324654 [2MT VIC EK J69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8357 | -6.4969e-06 | -0.00035208
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1371 324514-324654(1) | OPEN LINE FROM BUS 324514 [2ELIHU 69.000] TO BUS 324654 [2MT VIC EK J69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1372 324514-324962(1) | OPEN LINE FROM BUS 324514 [2ELIHU 69.000] TO BUS 324962 [2SOMERSET 1 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93969 | 64.8386 | 3.5346e-05 | -0.00031024
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1372 324514-324962(1) | OPEN LINE FROM BUS 324514 [2ELIHU 69.000] TO BUS 324962 [2SOMERSET 1 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1373 324515-326530(1) | OPEN LINE FROM BUS 324515 [2EMANUEL TAP69.000] TO BUS 326530 [2EMANUEL 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.4305e-06 | -0.00034702
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1373 324515-326530(1) | OPEN LINE FROM BUS 324515 [2EMANUEL TAP69.000] TO BUS 326530 [2EMANUEL 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1374 324516-324585(1) | OPEN LINE FROM BUS 324516 [2EMINENCE KU69.000] TO BUS 324585 [2JERICHO 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8371 | 1.3232e-05 | -0.00033236
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1374 324516-324585(1) | OPEN LINE FROM BUS 324516 [2EMINENCE KU69.000] TO BUS 324585 [2JERICHO 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1375 324516-324727(1) | OPEN LINE FROM BUS 324516 [2EMINENCE KU69.000] TO BUS 324727 [2SHELBYVILLE69.000] CKT 1 | 0.93965 | 64.8362 | 0.93972 | 64.8406 | 6.4075e-05 | -0.00028151
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1375 324516-324727(1) | OPEN LINE FROM BUS 324516 [2EMINENCE KU69.000] TO BUS 324727 [2SHELBYVILLE69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1376 324517-325005(1) | OPEN LINE FROM BUS 324517 [2ESSERVILLE 69.000] TO BUS 325005 [2WISE TAP 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 0 | -0.00034559
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1376 324517-325005(1) | OPEN LINE FROM BUS 324517 [2ESSERVILLE 69.000] TO BUS 325005 [2WISE TAP 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1377 324518-324657(1) | OPEN LINE FROM BUS 324518 [2ETHEL 69.000] TO BUS 324657 [2NACHAND 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 5.9605e-08 | -0.00034553
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1377 324518-324657(1) | OPEN LINE FROM BUS 324518 [2ETHEL 69.000] TO BUS 324657 [2NACHAND 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1378 324519-324520(1) | OPEN LINE FROM BUS 324519 [2ETOWN KU 69.000] TO BUS 324520 [2ETOWN 2 TAP69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.7881e-07 | -0.00034577
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1378 324519-324520(1) | OPEN LINE FROM BUS 324519 [2ETOWN KU 69.000] TO BUS 324520 [2ETOWN 2 TAP69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1379 324519-324521(1) | OPEN LINE FROM BUS 324519 [2ETOWN KU 69.000] TO BUS 324521 [2ETOWN 4 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -2.3842e-06 | -0.00034797
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1379 324519-324521(1) | OPEN LINE FROM BUS 324519 [2ETOWN KU 69.000] TO BUS 324521 [2ETOWN 4 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1380 324519-324563(1) | OPEN LINE FROM BUS 324519 [2ETOWN KU 69.000] TO BUS 324563 [2HARDIN CO 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -3.5763e-07 | -0.00034595
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1380 324519-324563(1) | OPEN LINE FROM BUS 324519 [2ETOWN KU 69.000] TO BUS 324563 [2HARDIN CO 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1381 324519-324563(2) | OPEN LINE FROM BUS 324519 [2ETOWN KU 69.000] TO BUS 324563 [2HARDIN CO 69.000] CKT 2 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -3.5763e-07 | -0.00034595
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1381 324519-324563(2) | OPEN LINE FROM BUS 324519 [2ETOWN KU 69.000] TO BUS 324563 [2HARDIN CO 69.000] CKT 2 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1382 324520-326555(1) | OPEN LINE FROM BUS 324520 [2ETOWN 2 TAP69.000] TO BUS 326555 [2RINEYVIL RD69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.7881e-07 | -0.00034577
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1382 324520-326555(1) | OPEN LINE FROM BUS 324520 [2ETOWN 2 TAP69.000] TO BUS 326555 [2RINEYVIL RD69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1383 324521-324575(1) | OPEN LINE FROM BUS 324521 [2ETOWN 4 69.000] TO BUS 324575 [2HODGENV KU 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8357 | -6.1989e-06 | -0.00035179
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1383 324521-324575(1) | OPEN LINE FROM BUS 324521 [2ETOWN 4 69.000] TO BUS 324575 [2HODGENV KU 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1384 324522-324523(1) | OPEN LINE FROM BUS 324522 [2EVARTS TAP 69.000] TO BUS 324523 [2EVARTS 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8357 | -5.9009e-06 | -0.00035149
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1384 324522-324523(1) | OPEN LINE FROM BUS 324522 [2EVARTS TAP 69.000] TO BUS 324523 [2EVARTS 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1385 324522-324692(1) | OPEN LINE FROM BUS 324522 [2EVARTS TAP 69.000] TO BUS 324692 [2POWELL MTN 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -1.7285e-06 | -0.00034732
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1385 324522-324692(1) | OPEN LINE FROM BUS 324522 [2EVARTS TAP 69.000] TO BUS 324692 [2POWELL MTN 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1386 324522-324761(1) | OPEN LINE FROM BUS 324522 [2EVARTS TAP 69.000] TO BUS 324761 [2VERDA 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 3.5763e-07 | -0.00034523
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1386 324522-324761(1) | OPEN LINE FROM BUS 324522 [2EVARTS TAP 69.000] TO BUS 324761 [2VERDA 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1387 324523-324798(1) | OPEN LINE FROM BUS 324523 [2EVARTS 69.000] TO BUS 324798 [2BAILEY CRK 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8359 | -3.8147e-06 | -0.0003494
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1387 324523-324798(1) | OPEN LINE FROM BUS 324523 [2EVARTS 69.000] TO BUS 324798 [2BAILEY CRK 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1388 324524-325009(1) | OPEN LINE FROM BUS 324524 [2EWINGTON 69.000] TO BUS 325009 [2SPENCER A 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1389 324525-324974(1) | OPEN LINE FROM BUS 324525 [2FAIRFIELD 69.000] TO BUS 324974 [2TAYLRV EK T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8352 | -1.3947e-05 | -0.00035954
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1389 324525-324974(1) | OPEN LINE FROM BUS 324525 [2FAIRFIELD 69.000] TO BUS 324974 [2TAYLRV EK T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1390 324526-324730(1) | OPEN LINE FROM BUS 324526 [2FAIRMOUNT 269.000] TO BUS 324730 [2SMYRNA 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8367 | 7.391e-06 | -0.0003382
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1390 324526-324730(1) | OPEN LINE FROM BUS 324526 [2FAIRMOUNT 269.000] TO BUS 324730 [2SMYRNA 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1391 324527-324704(1) | OPEN LINE FROM BUS 324527 [2FARLEY KU 69.000] TO BUS 324704 [2ROCKHOLD 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8359 | -4.2319e-06 | -0.00034982
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1391 324527-324704(1) | OPEN LINE FROM BUS 324527 [2FARLEY KU 69.000] TO BUS 324704 [2ROCKHOLD 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1392 324527-324758(1) | OPEN LINE FROM BUS 324527 [2FARLEY KU 69.000] TO BUS 324758 [2US STEEL 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93969 | 64.8388 | 3.7909e-05 | -0.00030768
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1392 324527-324758(1) | OPEN LINE FROM BUS 324527 [2FARLEY KU 69.000] TO BUS 324758 [2US STEEL 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1393 324528-324647(1) | OPEN LINE FROM BUS 324528 [2FARMERS 69.000] TO BUS 324647 [2MOREHEAD W 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93962 | 64.8341 | -2.9504e-05 | -0.00037509
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1393 324528-324647(1) | OPEN LINE FROM BUS 324528 [2FARMERS 69.000] TO BUS 324647 [2MOREHEAD W 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1394 324529-324675(1) | OPEN LINE FROM BUS 324529 [2FARNSLEY 69.000] TO BUS 324675 [2PADDYS RUN 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -3.5763e-07 | -0.00034595
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1394 324529-324675(1) | OPEN LINE FROM BUS 324529 [2FARNSLEY 69.000] TO BUS 324675 [2PADDYS RUN 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1395 324529-324724(1) | OPEN LINE FROM BUS 324529 [2FARNSLEY 69.000] TO BUS 324724 [2SHIVELY 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 0 | -0.00034559
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1395 324529-324724(1) | OPEN LINE FROM BUS 324529 [2FARNSLEY 69.000] TO BUS 324724 [2SHIVELY 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1396 324530-324701(1) | OPEN LINE FROM BUS 324530 [2FAWKES 69.000] TO BUS 324701 [2RICHMND 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8359 | -3.8743e-06 | -0.00034946
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1396 324530-324701(1) | OPEN LINE FROM BUS 324530 [2FAWKES 69.000] TO BUS 324701 [2RICHMND 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1397 324533-324535(1) | OPEN LINE FROM BUS 324533 [2FRANKFORT 169.000] TO BUS 324535 [2E FRANKFORT69.000] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8374 | 1.7345e-05 | -0.00032824
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1397 324533-324535(1) | OPEN LINE FROM BUS 324533 [2FRANKFORT 169.000] TO BUS 324535 [2E FRANKFORT69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 1.1921e-07 | 1.1921e-07
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1398 324534-324535(1) | OPEN LINE FROM BUS 324534 [2FRANKFORT 269.000] TO BUS 324535 [2E FRANKFORT69.000] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8352 | -1.353e-05 | -0.00035912
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1398 324534-324535(1) | OPEN LINE FROM BUS 324534 [2FRANKFORT 269.000] TO BUS 324535 [2E FRANKFORT69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1399 324534-324762(1) | OPEN LINE FROM BUS 324534 [2FRANKFORT 269.000] TO BUS 324762 [2VERSAIL W T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.835 | -1.6153e-05 | -0.00036174
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1399 324534-324762(1) | OPEN LINE FROM BUS 324534 [2FRANKFORT 269.000] TO BUS 324762 [2VERSAIL W T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1400 324535-326528(1) | OPEN LINE FROM BUS 324535 [2E FRANKFORT69.000] TO BUS 326528 [2BRIDGEPORT 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93956 | 64.8299 | -9.1255e-05 | -0.00043684
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1400 324535-326528(1) | OPEN LINE FROM BUS 324535 [2E FRANKFORT69.000] TO BUS 326528 [2BRIDGEPORT 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1401 324536-324653(1) | OPEN LINE FROM BUS 324536 [2FINCHVILLE 69.000] TO BUS 324653 [2M-V SIMPSON69.000] CKT 1 | 0.93965 | 64.8362 | 0.93971 | 64.84 | 5.5194e-05 | -0.00029039
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1401 324536-324653(1) | OPEN LINE FROM BUS 324536 [2FINCHVILLE 69.000] TO BUS 324653 [2M-V SIMPSON69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1402 324536-324718(1) | OPEN LINE FROM BUS 324536 [2FINCHVILLE 69.000] TO BUS 324718 [2SHELBY CO T69.000] CKT 1 | 0.93965 | 64.8362 | 0.9397 | 64.8395 | 4.9055e-05 | -0.00029653
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1402 324536-324718(1) | OPEN LINE FROM BUS 324536 [2FINCHVILLE 69.000] TO BUS 324718 [2SHELBY CO T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1403 324536-324752(1) | OPEN LINE FROM BUS 324536 [2FINCHVILLE 69.000] TO BUS 324752 [2TAYLORSV KU69.000] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8349 | -1.7643e-05 | -0.00036323
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1403 324536-324752(1) | OPEN LINE FROM BUS 324536 [2FINCHVILLE 69.000] TO BUS 324752 [2TAYLORSV KU69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1404 324537-324620(1) | OPEN LINE FROM BUS 324537 [2FLA TILE T269.000] TO BUS 324620 [2LAWRENCEBRG69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 4.1127e-06 | -0.00034148
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1404 324537-324620(1) | OPEN LINE FROM BUS 324537 [2FLA TILE T269.000] TO BUS 324620 [2LAWRENCEBRG69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1405 324537-324755(1) | OPEN LINE FROM BUS 324537 [2FLA TILE T269.000] TO BUS 324755 [2TYRONE 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 4.2319e-06 | -0.00034136
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1405 324537-324755(1) | OPEN LINE FROM BUS 324537 [2FLA TILE T269.000] TO BUS 324755 [2TYRONE 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1406 324538-324561(1) | OPEN LINE FROM BUS 324538 [2FLOYD 69.000] TO BUS 324561 [2HANCOCK 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -2.9802e-07 | -0.00034589
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1406 324538-324561(1) | OPEN LINE FROM BUS 324538 [2FLOYD 69.000] TO BUS 324561 [2HANCOCK 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1407 324538-324614(1) | OPEN LINE FROM BUS 324538 [2FLOYD 69.000] TO BUS 324614 [2LOCUST TAP 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 7.1526e-07 | -0.00034487
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1407 324538-324614(1) | OPEN LINE FROM BUS 324538 [2FLOYD 69.000] TO BUS 324614 [2LOCUST TAP 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1408 324539-324601(1) | OPEN LINE FROM BUS 324539 [2FMC 69.000] TO BUS 324601 [2LANSDOWNE 69.000] CKT 1 | 0.93965 | 64.8362 | 0.9397 | 64.8391 | 4.2617e-05 | -0.00030297
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1408 324539-324601(1) | OPEN LINE FROM BUS 324539 [2FMC 69.000] TO BUS 324601 [2LANSDOWNE 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1409 324539-324613(1) | OPEN LINE FROM BUS 324539 [2FMC 69.000] TO BUS 324613 [2LK SHORE TP69.000] CKT 1 | 0.93965 | 64.8362 | 0.93863 | 64.7653 | -0.0010267 | -0.0013723
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1409 324539-324613(1) | OPEN LINE FROM BUS 324539 [2FMC 69.000] TO BUS 324613 [2LK SHORE TP69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1410 324540-324912(1) | OPEN LINE FROM BUS 324540 [2FOGG PIKE T69.000] TO BUS 324912 [2MT STERL KU69.000] CKT 1 | 0.93965 | 64.8362 | 0.93956 | 64.8298 | -9.2506e-05 | -0.00043809
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1410 324540-324912(1) | OPEN LINE FROM BUS 324540 [2FOGG PIKE T69.000] TO BUS 324912 [2MT STERL KU69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1411 324541-324637(1) | OPEN LINE FROM BUS 324541 [2FORD 69.000] TO BUS 324637 [2MIDDLETOWN 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -1.7285e-06 | -0.00034732
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1411 324541-324637(1) | OPEN LINE FROM BUS 324541 [2FORD 69.000] TO BUS 324637 [2MIDDLETOWN 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1412 324542-324588(1) | OPEN LINE FROM BUS 324542 [2FORESTER CR69.000] TO BUS 324588 [2KENTENIA 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.7881e-07 | -0.00034577
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1412 324542-324588(1) | OPEN LINE FROM BUS 324542 [2FORESTER CR69.000] TO BUS 324588 [2KENTENIA 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1413 324542-324706(1) | OPEN LINE FROM BUS 324542 [2FORESTER CR69.000] TO BUS 324706 [2ROCKY BRNCH69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.7881e-07 | -0.00034577
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1413 324542-324706(1) | OPEN LINE FROM BUS 324542 [2FORESTER CR69.000] TO BUS 324706 [2ROCKY BRNCH69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1414 324543-324686(1) | OPEN LINE FROM BUS 324543 [2FOUR MILE 69.000] TO BUS 324686 [2PINEVILLE 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.0133e-06 | -0.0003466
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1414 324543-324686(1) | OPEN LINE FROM BUS 324543 [2FOUR MILE 69.000] TO BUS 324686 [2PINEVILLE 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1415 324543-324813(1) | OPEN LINE FROM BUS 324543 [2FOUR MILE 69.000] TO BUS 324813 [2CARY 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -9.5367e-07 | -0.00034654
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1415 324543-324813(1) | OPEN LINE FROM BUS 324543 [2FOUR MILE 69.000] TO BUS 324813 [2CARY 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1416 324544-324693(1) | OPEN LINE FROM BUS 324544 [2FREDONIA QU69.000] TO BUS 324693 [2PRINCETON 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 5.3644e-07 | -0.00034505
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1416 324544-324693(1) | OPEN LINE FROM BUS 324544 [2FREDONIA QU69.000] TO BUS 324693 [2PRINCETON 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1417 324544-324865(1) | OPEN LINE FROM BUS 324544 [2FREDONIA QU69.000] TO BUS 324865 [2FREDONIA 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 6.5565e-07 | -0.00034493
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1417 324544-324865(1) | OPEN LINE FROM BUS 324544 [2FREDONIA QU69.000] TO BUS 324865 [2FREDONIA 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1418 324545-324623(1) | OPEN LINE FROM BUS 324545 [2FREYS HILL 69.000] TO BUS 324623 [2LYNDON 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -6.5565e-07 | -0.00034624
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1418 324545-324623(1) | OPEN LINE FROM BUS 324545 [2FREYS HILL 69.000] TO BUS 324623 [2LYNDON 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1419 324546-324600(1) | OPEN LINE FROM BUS 324546 [2GARRARD CT 69.000] TO BUS 324600 [2LANCASTR KU69.000] CKT 1 | 0.93965 | 64.8362 | 0.93962 | 64.8338 | -3.3736e-05 | -0.00037932
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1419 324546-324600(1) | OPEN LINE FROM BUS 324546 [2GARRARD CT 69.000] TO BUS 324600 [2LANCASTR KU69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1420 324547-324890(1) | OPEN LINE FROM BUS 324547 [2GEORGETOWN 69.000] TO BUS 324890 [2LEMONS MILL69.000] CKT 1 | 0.93965 | 64.8362 | 0.93944 | 64.8216 | -0.00021058 | -0.00055617
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1420 324547-324890(1) | OPEN LINE FROM BUS 324547 [2GEORGETOWN 69.000] TO BUS 324890 [2LEMONS MILL69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1421 324549-324583(1) | OPEN LINE FROM BUS 324549 [2GORGE 69.000] TO BUS 324583 [2IMBODEN 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8355 | -1.0192e-05 | -0.00035578
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1421 324549-324583(1) | OPEN LINE FROM BUS 324549 [2GORGE 69.000] TO BUS 324583 [2IMBODEN 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1422 324549-324894(1) | OPEN LINE FROM BUS 324549 [2GORGE 69.000] TO BUS 324894 [2E STONE G T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -2.9206e-06 | -0.00034851
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1422 324549-324894(1) | OPEN LINE FROM BUS 324549 [2GORGE 69.000] TO BUS 324894 [2E STONE G T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1423 324550-324652(1) | OPEN LINE FROM BUS 324550 [2GREEN RIVER69.000] TO BUS 324652 [2MUHLENBRG P69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 1.1921e-07 | -0.00034547
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1423 324550-324652(1) | OPEN LINE FROM BUS 324550 [2GREEN RIVER69.000] TO BUS 324652 [2MUHLENBRG P69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1424 324550-324709(1) | OPEN LINE FROM BUS 324550 [2GREEN RIVER69.000] TO BUS 324709 [2RVR QUEEN T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 0 | -0.00034559
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1424 324550-324709(1) | OPEN LINE FROM BUS 324550 [2GREEN RIVER69.000] TO BUS 324709 [2RVR QUEEN T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1425 324550-324723(1) | OPEN LINE FROM BUS 324550 [2GREEN RIVER69.000] TO BUS 324723 [2SHAVER CHAP69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -8.3447e-07 | -0.00034642
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1425 324550-324723(1) | OPEN LINE FROM BUS 324550 [2GREEN RIVER69.000] TO BUS 324723 [2SHAVER CHAP69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1426 324550-325082(1) | OPEN LINE FROM BUS 324550 [2GREEN RIVER69.000] TO BUS 325082 [2ARMSTR BREC69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.4305e-06 | -0.00034702
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1426 324550-325082(1) | OPEN LINE FROM BUS 324550 [2GREEN RIVER69.000] TO BUS 325082 [2ARMSTR BREC69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1427 324550-326513(1) | OPEN LINE FROM BUS 324550 [2GREEN RIVER69.000] TO BUS 326513 [2EQAL M BREC69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 1.7881e-07 | -0.00034541
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1427 324550-326513(1) | OPEN LINE FROM BUS 324550 [2GREEN RIVER69.000] TO BUS 326513 [2EQAL M BREC69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1428 324551-324786(1) | OPEN LINE FROM BUS 324551 [2GR RVR STL 69.000] TO BUS 324786 [2ZION 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 5.9605e-07 | -0.00034499
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1428 324551-324786(1) | OPEN LINE FROM BUS 324551 [2GR RVR STL 69.000] TO BUS 324786 [2ZION 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1429 324551-324947(1) | OPEN LINE FROM BUS 324551 [2GR RVR STL 69.000] TO BUS 324947 [2RUMSEY 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 4.7684e-07 | -0.00034511
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1429 324551-324947(1) | OPEN LINE FROM BUS 324551 [2GR RVR STL 69.000] TO BUS 324947 [2RUMSEY 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1430 324552-324675(1) | OPEN LINE FROM BUS 324552 [2GRADY 69.000] TO BUS 324675 [2PADDYS RUN 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 2.9206e-06 | -0.00034267
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1430 324552-324675(1) | OPEN LINE FROM BUS 324552 [2GRADY 69.000] TO BUS 324675 [2PADDYS RUN 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1431 324553-324864(1) | OPEN LINE FROM BUS 324553 [2GRAHAMVILLE69.000] TO BUS 324864 [2FORRESTDALE69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 1.1921e-07 | -0.00034547
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1431 324553-324864(1) | OPEN LINE FROM BUS 324553 [2GRAHAMVILLE69.000] TO BUS 324864 [2FORRESTDALE69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1432 324554-324830(1) | OPEN LINE FROM BUS 324554 [2GRENSBRG KU69.000] TO BUS 324830 [2CAMPBELV EK69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.1921e-06 | -0.00034678
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1432 324554-324830(1) | OPEN LINE FROM BUS 324554 [2GRENSBRG KU69.000] TO BUS 324830 [2CAMPBELV EK69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1433 324555-324716(1) | OPEN LINE FROM BUS 324555 [2VA CTY REAC69.000] TO BUS 324716 [2SANDY RIDGE69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8358 | -4.6492e-06 | -0.00035024
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1433 324555-324716(1) | OPEN LINE FROM BUS 324555 [2VA CTY REAC69.000] TO BUS 324716 [2SANDY RIDGE69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1434 324555-324759(1) | OPEN LINE FROM BUS 324555 [2VA CTY REAC69.000] TO BUS 324759 [2VIRGINIA CI69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8359 | -4.2915e-06 | -0.00034988
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1434 324555-324759(1) | OPEN LINE FROM BUS 324555 [2VA CTY REAC69.000] TO BUS 324759 [2VIRGINIA CI69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1435 324556-324702(1) | OPEN LINE FROM BUS 324556 [2GREENV W TP69.000] TO BUS 324702 [2RIVER QUEEN69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 5.3644e-07 | -0.00034505
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1435 324556-324702(1) | OPEN LINE FROM BUS 324556 [2GREENV W TP69.000] TO BUS 324702 [2RIVER QUEEN69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1436 324556-324870(1) | OPEN LINE FROM BUS 324556 [2GREENV W TP69.000] TO BUS 324870 [2GREENVILLE 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 1.7881e-07 | -0.00034541
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1436 324556-324870(1) | OPEN LINE FROM BUS 324556 [2GREENV W TP69.000] TO BUS 324870 [2GREENVILLE 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1437 324556-326593(1) | OPEN LINE FROM BUS 324556 [2GREENV W TP69.000] TO BUS 326593 [2GREENVIL N 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8367 | 7.5698e-06 | -0.00033802
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1437 324556-326593(1) | OPEN LINE FROM BUS 324556 [2GREENV W TP69.000] TO BUS 326593 [2GREENVIL N 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1438 324557-324829(1) | OPEN LINE FROM BUS 324557 [2GR RVR PLAZ69.000] TO BUS 324829 [2CAMPBELVIL169.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.3709e-06 | -0.00034696
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1438 324557-324829(1) | OPEN LINE FROM BUS 324557 [2GR RVR PLAZ69.000] TO BUS 324829 [2CAMPBELVIL169.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1439 324557-324830(1) | OPEN LINE FROM BUS 324557 [2GR RVR PLAZ69.000] TO BUS 324830 [2CAMPBELV EK69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8359 | -3.0398e-06 | -0.00034863
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1439 324557-324830(1) | OPEN LINE FROM BUS 324557 [2GR RVR PLAZ69.000] TO BUS 324830 [2CAMPBELV EK69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1440 324558-324734(1) | OPEN LINE FROM BUS 324558 [2HAEFLING 69.000] TO BUS 324734 [2SPINDLETP T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93958 | 64.8309 | -7.6473e-05 | -0.00042206
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1440 324558-324734(1) | OPEN LINE FROM BUS 324558 [2HAEFLING 69.000] TO BUS 324734 [2SPINDLETP T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1441 324558-324766(1) | OPEN LINE FROM BUS 324558 [2HAEFLING 69.000] TO BUS 324766 [2W HIGH T1 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93972 | 64.841 | 6.9559e-05 | -0.00027603
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1441 324558-324766(1) | OPEN LINE FROM BUS 324558 [2HAEFLING 69.000] TO BUS 324766 [2W HIGH T1 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1442 324559-324797(1) | OPEN LINE FROM BUS 324559 [2HALEY 69.000] TO BUS 324797 [2AVON T1 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 1.0729e-06 | -0.00034451
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1442 324559-324797(1) | OPEN LINE FROM BUS 324559 [2HALEY 69.000] TO BUS 324797 [2AVON T1 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1443 324559-326586(1) | OPEN LINE FROM BUS 324559 [2HALEY 69.000] TO BUS 326586 [2HUME RD TAP69.000] CKT 1 | 0.93965 | 64.8362 | 0.93962 | 64.8336 | -3.6836e-05 | -0.00038242
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1443 324559-326586(1) | OPEN LINE FROM BUS 324559 [2HALEY 69.000] TO BUS 326586 [2HUME RD TAP69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1444 324560-324689(1) | OPEN LINE FROM BUS 324560 [2HAMBLIN TAP69.000] TO BUS 324689 [2POCKET 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8358 | -5.6028e-06 | -0.00035119
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1444 324560-324689(1) | OPEN LINE FROM BUS 324560 [2HAMBLIN TAP69.000] TO BUS 324689 [2POCKET 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1445 324560-324815(1) | OPEN LINE FROM BUS 324560 [2HAMBLIN TAP69.000] TO BUS 324815 [2CAWOOD 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -1.5497e-06 | -0.00034714
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1445 324560-324815(1) | OPEN LINE FROM BUS 324560 [2HAMBLIN TAP69.000] TO BUS 324815 [2CAWOOD 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1446 324560-325041(1) | OPEN LINE FROM BUS 324560 [2HAMBLIN TAP69.000] TO BUS 325041 [2STONE TVA 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8374 | 1.7941e-05 | -0.00032765
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1446 324560-325041(1) | OPEN LINE FROM BUS 324560 [2HAMBLIN TAP69.000] TO BUS 325041 [2STONE TVA 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1447 324562-324564(1) | OPEN LINE FROM BUS 324562 [2HARLAN KU 69.000] TO BUS 324564 [2HARLAN WYE 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -3.5763e-07 | -0.00034595
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1447 324562-324564(1) | OPEN LINE FROM BUS 324562 [2HARLAN KU 69.000] TO BUS 324564 [2HARLAN WYE 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1448 324563-324731(1) | OPEN LINE FROM BUS 324563 [2HARDIN CO 69.000] TO BUS 324731 [2SONORA TAP 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8359 | -3.5763e-06 | -0.00034916
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1448 324563-324731(1) | OPEN LINE FROM BUS 324563 [2HARDIN CO 69.000] TO BUS 324731 [2SONORA TAP 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1449 324565-324566(1) | OPEN LINE FROM BUS 324565 [7NAS TAP 345.00] TO BUS 324566 [7NAS 222 345.00] CKT 1 | 0.93965 | 64.8362 | 0.93926 | 64.8092 | -0.00039071 | -0.0007363
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1449 324565-324566(1) | OPEN LINE FROM BUS 324565 [7NAS TAP 345.00] TO BUS 324566 [7NAS 222 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1450 324567-324780(1) | OPEN LINE FROM BUS 324567 [2HIGBY MIL 269.000] TO BUS 324780 [2WIL DOWN T169.000] CKT 1 | 0.93965 | 64.8362 | 0.93963 | 64.8344 | -2.5213e-05 | -0.0003708
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1450 324567-324780(1) | OPEN LINE FROM BUS 324567 [2HIGBY MIL 269.000] TO BUS 324780 [2WIL DOWN T169.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1451 324568-324569(1) | OPEN LINE FROM BUS 324568 [2HIGBY 618 69.000] TO BUS 324569 [2HIGBY 608 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8358 | -4.5896e-06 | -0.00035018
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1451 324568-324569(1) | OPEN LINE FROM BUS 324568 [2HIGBY 618 69.000] TO BUS 324569 [2HIGBY 608 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1452 324568-324713(1) | OPEN LINE FROM BUS 324568 [2HIGBY 618 69.000] TO BUS 324713 [2SO ELKHORN 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93976 | 64.8435 | 0.00010592 | -0.00023967
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1452 324568-324713(1) | OPEN LINE FROM BUS 324568 [2HIGBY 618 69.000] TO BUS 324713 [2SO ELKHORN 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1453 324568-324742(1) | OPEN LINE FROM BUS 324568 [2HIGBY 618 69.000] TO BUS 324742 [2STONEWALL T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93961 | 64.8331 | -4.4942e-05 | -0.00039053
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1453 324568-324742(1) | OPEN LINE FROM BUS 324568 [2HIGBY 618 69.000] TO BUS 324742 [2STONEWALL T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1454 324569-324632(1) | OPEN LINE FROM BUS 324569 [2HIGBY 608 69.000] TO BUS 324632 [2UK MED CENT69.000] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8348 | -1.9133e-05 | -0.00036472
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1454 324569-324632(1) | OPEN LINE FROM BUS 324569 [2HIGBY 608 69.000] TO BUS 324632 [2UK MED CENT69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1455 324571-324671(1) | OPEN LINE FROM BUS 324571 [2HIGHLAND MI69.000] TO BUS 324671 [2OVERLAD S T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -2.9802e-07 | -0.00034589
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1455 324571-324671(1) | OPEN LINE FROM BUS 324571 [2HIGHLAND MI69.000] TO BUS 324671 [2OVERLAD S T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1456 324572-324691(1) | OPEN LINE FROM BUS 324572 [2HILLSIDE 69.000] TO BUS 324691 [2POWDERLY 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 5.9605e-08 | -0.00034553
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1456 324572-324691(1) | OPEN LINE FROM BUS 324572 [2HILLSIDE 69.000] TO BUS 324691 [2POWDERLY 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1457 324573-324741(1) | OPEN LINE FROM BUS 324573 [2HINKLE 69.000] TO BUS 324741 [2STINKIN CRK69.000] CKT 1 | 0.93965 | 64.8362 | 0.93962 | 64.8337 | -3.5524e-05 | -0.00038111
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1457 324573-324741(1) | OPEN LINE FROM BUS 324573 [2HINKLE 69.000] TO BUS 324741 [2STINKIN CRK69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1458 324576-324748(1) | OPEN LINE FROM BUS 324576 [2HOPEWELL 69.000] TO BUS 324748 [2SWEET HOLLO69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 2.0266e-06 | -0.00034356
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1458 324576-324748(1) | OPEN LINE FROM BUS 324576 [2HOPEWELL 69.000] TO BUS 324748 [2SWEET HOLLO69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1459 324577-324693(1) | OPEN LINE FROM BUS 324577 [2HARDESTY A 69.000] TO BUS 324693 [2PRINCETON 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 1.3709e-06 | -0.00034422
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1459 324577-324693(1) | OPEN LINE FROM BUS 324577 [2HARDESTY A 69.000] TO BUS 324693 [2PRINCETON 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1460 324577-324769(1) | OPEN LINE FROM BUS 324577 [2HARDESTY A 69.000] TO BUS 324769 [2WALKER KU 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 1.3113e-06 | -0.00034428
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1460 324577-324769(1) | OPEN LINE FROM BUS 324577 [2HARDESTY A 69.000] TO BUS 324769 [2WALKER KU 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1461 324578-324690(1) | OPEN LINE FROM BUS 324578 [2HARDESTY B 69.000] TO BUS 324690 [2DAWSON TAP 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 1.0133e-06 | -0.00034457
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1461 324578-324690(1) | OPEN LINE FROM BUS 324578 [2HARDESTY B 69.000] TO BUS 324690 [2DAWSON TAP 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1462 324578-324769(1) | OPEN LINE FROM BUS 324578 [2HARDESTY B 69.000] TO BUS 324769 [2WALKER KU 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 7.1526e-07 | -0.00034487
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1462 324578-324769(1) | OPEN LINE FROM BUS 324578 [2HARDESTY B 69.000] TO BUS 324769 [2WALKER KU 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1463 324579-324580(1) | OPEN LINE FROM BUS 324579 [2HARMNY LAND69.000] TO BUS 324580 [2HARRODS CRK69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8359 | -3.3975e-06 | -0.00034899
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1463 324579-324580(1) | OPEN LINE FROM BUS 324579 [2HARMNY LAND69.000] TO BUS 324580 [2HARRODS CRK69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1464 324579-324960(1) | OPEN LINE FROM BUS 324579 [2HARMNY LAND69.000] TO BUS 324960 [2SKYLIGHT 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8358 | -5.6624e-06 | -0.00035125
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1464 324579-324960(1) | OPEN LINE FROM BUS 324579 [2HARMNY LAND69.000] TO BUS 324960 [2SKYLIGHT 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1465 324580-324750(1) | OPEN LINE FROM BUS 324580 [2HARRODS CRK69.000] TO BUS 324750 [2TAYLOR LG 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -6.5565e-07 | -0.00034624
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1465 324580-324750(1) | OPEN LINE FROM BUS 324580 [2HARRODS CRK69.000] TO BUS 324750 [2TAYLOR LG 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1466 324580-324785(1) | OPEN LINE FROM BUS 324580 [2HARRODS CRK69.000] TO BUS 324785 [2WORTHINGTON69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 6.5565e-07 | -0.00034493
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1466 324580-324785(1) | OPEN LINE FROM BUS 324580 [2HARRODS CRK69.000] TO BUS 324785 [2WORTHINGTON69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1467 324581-324586(1) | OPEN LINE FROM BUS 324581 [2HUGHES LANE69.000] TO BUS 324586 [2JOYLAND 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1468 324582-324610(1) | OPEN LINE FROM BUS 324582 [2IBM 69.000] TO BUS 324610 [2LEX PLANT 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93958 | 64.8311 | -7.3195e-05 | -0.00041878
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1468 324582-324610(1) | OPEN LINE FROM BUS 324582 [2IBM 69.000] TO BUS 324610 [2LEX PLANT 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1469 324582-324879(1) | OPEN LINE FROM BUS 324582 [2IBM 69.000] TO BUS 324879 [2IBM 998 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93953 | 64.8279 | -0.00011969 | -0.00046527
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1469 324582-324879(1) | OPEN LINE FROM BUS 324582 [2IBM 69.000] TO BUS 324879 [2IBM 998 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1470 324583-324591(1) | OPEN LINE FROM BUS 324583 [2IMBODEN 69.000] TO BUS 324591 [2KEOKEE TAP 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -1.9073e-06 | -0.0003475
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1470 324583-324591(1) | OPEN LINE FROM BUS 324583 [2IMBODEN 69.000] TO BUS 324591 [2KEOKEE TAP 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1471 324584-324659(1) | OPEN LINE FROM BUS 324584 [2INDIAN HILL69.000] TO BUS 324659 [2NELSON 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 1.7881e-07 | -0.00034541
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1471 324584-324659(1) | OPEN LINE FROM BUS 324584 [2INDIAN HILL69.000] TO BUS 324659 [2NELSON 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1472 324585-324598(1) | OPEN LINE FROM BUS 324585 [2JERICHO 69.000] TO BUS 324598 [2LA GRANGE E69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 2.9802e-06 | -0.00034261
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1472 324585-324598(1) | OPEN LINE FROM BUS 324585 [2JERICHO 69.000] TO BUS 324598 [2LA GRANGE E69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1473 324586-324610(1) | OPEN LINE FROM BUS 324586 [2JOYLAND 69.000] TO BUS 324610 [2LEX PLANT 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93928 | 64.8103 | -0.00037515 | -0.00072074
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1473 324586-324610(1) | OPEN LINE FROM BUS 324586 [2JOYLAND 69.000] TO BUS 324610 [2LEX PLANT 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1474 324587-324702(1) | OPEN LINE FROM BUS 324587 [2KEN AMERICA69.000] TO BUS 324702 [2RIVER QUEEN69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | -5.9605e-08 | -0.00034565
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1474 324587-324702(1) | OPEN LINE FROM BUS 324587 [2KEN AMERICA69.000] TO BUS 324702 [2RIVER QUEEN69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1475 324587-324709(1) | OPEN LINE FROM BUS 324587 [2KEN AMERICA69.000] TO BUS 324709 [2RVR QUEEN T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 0 | -0.00034559
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1475 324587-324709(1) | OPEN LINE FROM BUS 324587 [2KEN AMERICA69.000] TO BUS 324709 [2RVR QUEEN T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1476 324589-324722(1) | OPEN LINE FROM BUS 324589 [2KENTON 688 69.000] TO BUS 324722 [2SHARON KU 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1477 324589-324899(1) | OPEN LINE FROM BUS 324589 [2KENTON 688 69.000] TO BUS 324899 [2MAYSVILLE E69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1478 324589-325019(1) | OPEN LINE FROM BUS 324589 [2KENTON 688 69.000] TO BUS 325019 [2KENTON-6 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93981 | 64.8468 | 0.00015384 | -0.00019175
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1478 324589-325019(1) | OPEN LINE FROM BUS 324589 [2KENTON 688 69.000] TO BUS 325019 [2KENTON-6 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1479 324590-324719(1) | OPEN LINE FROM BUS 324590 [2KENWOOD 69.000] TO BUS 324719 [2SEMINOLE 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 1.1921e-07 | -0.00034547
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1479 324590-324719(1) | OPEN LINE FROM BUS 324590 [2KENWOOD 69.000] TO BUS 324719 [2SEMINOLE 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1480 324590-325023(1) | OPEN LINE FROM BUS 324590 [2KENWOOD 69.000] TO BUS 325023 [2ASHBOT EAST69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 5.9605e-07 | -0.00034499
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1480 324590-325023(1) | OPEN LINE FROM BUS 324590 [2KENWOOD 69.000] TO BUS 325023 [2ASHBOT EAST69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1481 324591-324592(1) | OPEN LINE FROM BUS 324591 [2KEOKEE TAP 69.000] TO BUS 324592 [2KEOKEE TVA 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -1.967e-06 | -0.00034755
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1481 324591-324592(1) | OPEN LINE FROM BUS 324591 [2KEOKEE TAP 69.000] TO BUS 324592 [2KEOKEE TVA 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1482 324592-324689(1) | OPEN LINE FROM BUS 324592 [2KEOKEE TVA 69.000] TO BUS 324689 [2POCKET 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -2.4438e-06 | -0.00034803
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1482 324592-324689(1) | OPEN LINE FROM BUS 324592 [2KEOKEE TVA 69.000] TO BUS 324689 [2POCKET 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1483 324593-324686(1) | OPEN LINE FROM BUS 324593 [2KU PARK 69.000] TO BUS 324686 [2PINEVILLE 69.000] CKT 1 | 0.93965 | 64.8362 | 0.9396 | 64.8321 | -5.9128e-05 | -0.00040472
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1483 324593-324686(1) | OPEN LINE FROM BUS 324593 [2KU PARK 69.000] TO BUS 324686 [2PINEVILLE 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1484 324593-324741(1) | OPEN LINE FROM BUS 324593 [2KU PARK 69.000] TO BUS 324741 [2STINKIN CRK69.000] CKT 1 | 0.93965 | 64.8362 | 0.93961 | 64.8332 | -4.214e-05 | -0.00038773
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1484 324593-324741(1) | OPEN LINE FROM BUS 324593 [2KU PARK 69.000] TO BUS 324741 [2STINKIN CRK69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1485 324595-324837(1) | OPEN LINE FROM BUS 324595 [2KAWNEER 69.000] TO BUS 324837 [2CYNTHIAN KU69.000] CKT 1 | 0.93965 | 64.8362 | 0.93811 | 64.7294 | -0.0015472 | -0.0018928
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1485 324595-324837(1) | OPEN LINE FROM BUS 324595 [2KAWNEER 69.000] TO BUS 324837 [2CYNTHIAN KU69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1486 324597-324764(1) | OPEN LINE FROM BUS 324597 [2KY ST HOSP 69.000] TO BUS 324764 [2WEST CLIFF 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8358 | -4.4703e-06 | -0.00035006
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1486 324597-324764(1) | OPEN LINE FROM BUS 324597 [2KY ST HOSP 69.000] TO BUS 324764 [2WEST CLIFF 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1487 324597-324840(1) | OPEN LINE FROM BUS 324597 [2KY ST HOSP 69.000] TO BUS 324840 [2DANVILLE E 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8359 | -3.6359e-06 | -0.00034922
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1487 324597-324840(1) | OPEN LINE FROM BUS 324597 [2KY ST HOSP 69.000] TO BUS 324840 [2DANVILLE E 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1488 324598-324682(1) | OPEN LINE FROM BUS 324598 [2LA GRANGE E69.000] TO BUS 324682 [2PENAL TAP 69.000] CKT 1 | 0.93965 | 64.8362 | 0.9397 | 64.8395 | 4.8876e-05 | -0.00029671
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1488 324598-324682(1) | OPEN LINE FROM BUS 324598 [2LA GRANGE E69.000] TO BUS 324682 [2PENAL TAP 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1489 324599-324600(1) | OPEN LINE FROM BUS 324599 [2LANCASTER 269.000] TO BUS 324600 [2LANCASTR KU69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8359 | -3.6359e-06 | -0.00034922
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1489 324599-324600(1) | OPEN LINE FROM BUS 324599 [2LANCASTER 269.000] TO BUS 324600 [2LANCASTR KU69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1490 324599-324971(1) | OPEN LINE FROM BUS 324599 [2LANCASTER 269.000] TO BUS 324971 [2STANFORD NO69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8357 | -6.1989e-06 | -0.00035179
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1490 324599-324971(1) | OPEN LINE FROM BUS 324599 [2LANCASTER 269.000] TO BUS 324971 [2STANFORD NO69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1491 324601-324650(1) | OPEN LINE FROM BUS 324601 [2LANSDOWNE 69.000] TO BUS 324650 [2MT TBR T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8356 | -7.8082e-06 | -0.0003534
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1491 324601-324650(1) | OPEN LINE FROM BUS 324601 [2LANSDOWNE 69.000] TO BUS 324650 [2MT TBR T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1492 324601-324780(1) | OPEN LINE FROM BUS 324601 [2LANSDOWNE 69.000] TO BUS 324780 [2WIL DOWN T169.000] CKT 1 | 0.93965 | 64.8362 | 0.93972 | 64.8405 | 6.2287e-05 | -0.0002833
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1492 324601-324780(1) | OPEN LINE FROM BUS 324601 [2LANSDOWNE 69.000] TO BUS 324780 [2WIL DOWN T169.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1493 324602-324828(1) | OPEN LINE FROM BUS 324602 [2LAWRENCE TP69.000] TO BUS 324828 [2CAMPBBRG KU69.000] CKT 1 | 0.93965 | 64.8362 | 0.93963 | 64.8346 | -2.2709e-05 | -0.0003683
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1493 324602-324828(1) | OPEN LINE FROM BUS 324602 [2LAWRENCE TP69.000] TO BUS 324828 [2CAMPBBRG KU69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1494 324602-324888(1) | OPEN LINE FROM BUS 324602 [2LAWRENCE TP69.000] TO BUS 324888 [2LAWRENCE 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 5.9605e-07 | -0.00034499
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1494 324602-324888(1) | OPEN LINE FROM BUS 324602 [2LAWRENCE TP69.000] TO BUS 324888 [2LAWRENCE 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1495 324603-324605(1) | OPEN LINE FROM BUS 324603 [2LEBANON CIT69.000] TO BUS 324605 [2LEBANON EK 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.7881e-07 | -0.00034577
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1495 324603-324605(1) | OPEN LINE FROM BUS 324603 [2LEBANON CIT69.000] TO BUS 324605 [2LEBANON EK 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
324605 | 2LEBANON EK | 69 | LGEE' | RANGE | 0.94 | 1.06 | SINGLE OPN LIN 1495 324603-324605(1) | OPEN LINE FROM BUS 324603 [2LEBANON CIT69.000] TO BUS 324605 [2LEBANON EK 69.000] CKT 1 | 1.004 | 69.2734 | 0.92194 | 63.6141 | -0.082019 | -0.018057
324889 | 2LEBANON SO | 69 | LGEE' | RANGE | 0.94 | 1.06 | SINGLE OPN LIN 1495 324603-324605(1) | OPEN LINE FROM BUS 324603 [2LEBANON CIT69.000] TO BUS 324605 [2LEBANON EK 69.000] CKT 1 | 1.0021 | 69.1446 | 0.924 | 63.7559 | -0.078098 | -0.016002
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1496 324604-324606(1) | OPEN LINE FROM BUS 324604 [2LEBANON IND69.000] TO BUS 324606 [2LEBANON 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.837 | 1.2815e-05 | -0.00033277
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1496 324604-324606(1) | OPEN LINE FROM BUS 324604 [2LEBANON IND69.000] TO BUS 324606 [2LEBANON 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1497 324604-325020(1) | OPEN LINE FROM BUS 324604 [2LEBANON IND69.000] TO BUS 325020 [2LEBANON E 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8369 | 1.1206e-05 | -0.00033438
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1497 324604-325020(1) | OPEN LINE FROM BUS 324604 [2LEBANON IND69.000] TO BUS 325020 [2LEBANON E 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1498 324605-324889(1) | OPEN LINE FROM BUS 324605 [2LEBANON EK 69.000] TO BUS 324889 [2LEBANON SO 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -5.3644e-07 | -0.00034612
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1498 324605-324889(1) | OPEN LINE FROM BUS 324605 [2LEBANON EK 69.000] TO BUS 324889 [2LEBANON SO 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1499 324606-324736(1) | OPEN LINE FROM BUS 324606 [2LEBANON 69.000] TO BUS 324736 [2SPRINGFL KU69.000] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8353 | -1.2934e-05 | -0.00035852
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1499 324606-324736(1) | OPEN LINE FROM BUS 324606 [2LEBANON 69.000] TO BUS 324736 [2SPRINGFL KU69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1500 324607-324608(1) | OPEN LINE FROM BUS 324607 [2LEITCHF CIT69.000] TO BUS 324608 [2LEITCHF E 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 3.0398e-06 | -0.00034255
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1500 324607-324608(1) | OPEN LINE FROM BUS 324607 [2LEITCHF CIT69.000] TO BUS 324608 [2LEITCHF E 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1501 324607-324609(1) | OPEN LINE FROM BUS 324607 [2LEITCHF CIT69.000] TO BUS 324609 [2LEITCHFIELD69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 2.2054e-06 | -0.00034338
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1501 324607-324609(1) | OPEN LINE FROM BUS 324607 [2LEITCHF CIT69.000] TO BUS 324609 [2LEITCHFIELD69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1502 324608-324992(1) | OPEN LINE FROM BUS 324608 [2LEITCHF E 69.000] TO BUS 324992 [2WARREN TIE 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8354 | -1.0371e-05 | -0.00035596
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1502 324608-324992(1) | OPEN LINE FROM BUS 324608 [2LEITCHF E 69.000] TO BUS 324992 [2WARREN TIE 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1503 324609-324643(1) | OPEN LINE FROM BUS 324609 [2LEITCHFIELD69.000] TO BUS 324643 [2MILL WOOD 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 3.9935e-06 | -0.00034159
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1503 324609-324643(1) | OPEN LINE FROM BUS 324609 [2LEITCHFIELD69.000] TO BUS 324643 [2MILL WOOD 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1504 324609-325040(1) | OPEN LINE FROM BUS 324609 [2LEITCHFIELD69.000] TO BUS 325040 [2LEITCHF TVA69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 5.9605e-08 | -0.00034553
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1504 324609-325040(1) | OPEN LINE FROM BUS 324609 [2LEITCHFIELD69.000] TO BUS 325040 [2LEITCHF TVA69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1505 324609-325040(2) | OPEN LINE FROM BUS 324609 [2LEITCHFIELD69.000] TO BUS 325040 [2LEITCHF TVA69.000] CKT 2 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 5.9605e-08 | -0.00034553
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1505 324609-325040(2) | OPEN LINE FROM BUS 324609 [2LEITCHFIELD69.000] TO BUS 325040 [2LEITCHF TVA69.000] CKT 2 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1506 324610-324617(1) | OPEN LINE FROM BUS 324610 [2LEX PLANT 69.000] TO BUS 324617 [2LOUDON 618 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93962 | 64.8335 | -3.8147e-05 | -0.00038373
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1506 324610-324617(1) | OPEN LINE FROM BUS 324610 [2LEX PLANT 69.000] TO BUS 324617 [2LOUDON 618 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1507 324610-324674(1) | OPEN LINE FROM BUS 324610 [2LEX PLANT 69.000] TO BUS 324674 [2PROC & GAMB69.000] CKT 1 | 0.93965 | 64.8362 | 0.93972 | 64.8409 | 6.938e-05 | -0.00027621
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1507 324610-324674(1) | OPEN LINE FROM BUS 324610 [2LEX PLANT 69.000] TO BUS 324674 [2PROC & GAMB69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1508 324611-324618(1) | OPEN LINE FROM BUS 324611 [2LIBERTY RD 69.000] TO BUS 324618 [2LOUDON 628 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93972 | 64.8406 | 6.3956e-05 | -0.00028163
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1508 324611-324618(1) | OPEN LINE FROM BUS 324611 [2LIBERTY RD 69.000] TO BUS 324618 [2LOUDON 628 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1509 324611-324891(1) | OPEN LINE FROM BUS 324611 [2LIBERTY RD 69.000] TO BUS 324891 [2LEX WATER 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8369 | 1.0312e-05 | -0.00033528
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1509 324611-324891(1) | OPEN LINE FROM BUS 324611 [2LIBERTY RD 69.000] TO BUS 324891 [2LEX WATER 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1510 324612-324701(1) | OPEN LINE FROM BUS 324612 [2LAKE REBA 69.000] TO BUS 324701 [2RICHMND 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8354 | -1.0908e-05 | -0.0003565
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1510 324612-324701(1) | OPEN LINE FROM BUS 324612 [2LAKE REBA 69.000] TO BUS 324701 [2RICHMND 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1511 324612-324768(1) | OPEN LINE FROM BUS 324612 [2LAKE REBA 69.000] TO BUS 324768 [2WACO 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 1.7285e-06 | -0.00034386
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1511 324612-324768(1) | OPEN LINE FROM BUS 324612 [2LAKE REBA 69.000] TO BUS 324768 [2WACO 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1512 324613-324618(1) | OPEN LINE FROM BUS 324613 [2LK SHORE TP69.000] TO BUS 324618 [2LOUDON 628 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93956 | 64.8298 | -9.2685e-05 | -0.00043827
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1512 324613-324618(1) | OPEN LINE FROM BUS 324613 [2LK SHORE TP69.000] TO BUS 324618 [2LOUDON 628 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1513 324613-325059(1) | OPEN LINE FROM BUS 324613 [2LK SHORE TP69.000] TO BUS 325059 [2BRYANT RD T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1514 324614-324719(1) | OPEN LINE FROM BUS 324614 [2LOCUST TAP 69.000] TO BUS 324719 [2SEMINOLE 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 1.2517e-06 | -0.00034434
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1514 324614-324719(1) | OPEN LINE FROM BUS 324614 [2LOCUST TAP 69.000] TO BUS 324719 [2SEMINOLE 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1515 324614-326545(1) | OPEN LINE FROM BUS 324614 [2LOCUST TAP 69.000] TO BUS 326545 [2LOCUST LGE 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8365 | 4.828e-06 | -0.00034076
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1515 324614-326545(1) | OPEN LINE FROM BUS 324614 [2LOCUST TAP 69.000] TO BUS 326545 [2LOCUST LGE 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1516 324615-324688(1) | OPEN LINE FROM BUS 324615 [2LONDON 69.000] TO BUS 324688 [2PITTSBRG KU69.000] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8375 | 1.9789e-05 | -0.0003258
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1516 324615-324688(1) | OPEN LINE FROM BUS 324615 [2LONDON 69.000] TO BUS 324688 [2PITTSBRG KU69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1517 324616-324775(1) | OPEN LINE FROM BUS 324616 [2LONG RUN 69.000] TO BUS 324775 [2WHAS 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -1.7285e-06 | -0.00034732
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1517 324616-324775(1) | OPEN LINE FROM BUS 324616 [2LONG RUN 69.000] TO BUS 324775 [2WHAS 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1518 324617-324618(1) | OPEN LINE FROM BUS 324617 [2LOUDON 618 69.000] TO BUS 324618 [2LOUDON 628 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93962 | 64.8339 | -3.2902e-05 | -0.00037849
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1518 324617-324618(1) | OPEN LINE FROM BUS 324617 [2LOUDON 618 69.000] TO BUS 324618 [2LOUDON 628 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1519 324618-326586(1) | OPEN LINE FROM BUS 324618 [2LOUDON 628 69.000] TO BUS 326586 [2HUME RD TAP69.000] CKT 1 | 0.93965 | 64.8362 | 0.93948 | 64.8243 | -0.00017124 | -0.00051683
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1519 324618-326586(1) | OPEN LINE FROM BUS 324618 [2LOUDON 628 69.000] TO BUS 326586 [2HUME RD TAP69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1520 324619-324998(1) | OPEN LINE FROM BUS 324619 [2LOWER MIL C69.000] TO BUS 324998 [2WEST CO 2 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.0133e-06 | -0.0003466
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1520 324619-324998(1) | OPEN LINE FROM BUS 324619 [2LOWER MIL C69.000] TO BUS 324998 [2WEST CO 2 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1521 324621-326523(1) | OPEN LINE FROM BUS 324621 [2LYNCH 69.000] TO BUS 326523 [2ARKLAND JCT69.000] CKT 1 | 0.93965 | 64.8362 | 0.93971 | 64.8398 | 5.2154e-05 | -0.00029343
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1521 324621-326523(1) | OPEN LINE FROM BUS 324621 [2LYNCH 69.000] TO BUS 326523 [2ARKLAND JCT69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1522 324622-324637(1) | OPEN LINE FROM BUS 324622 [2LYNDON SO 69.000] TO BUS 324637 [2MIDDLETOWN 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.1921e-06 | -0.00034678
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1522 324622-324637(1) | OPEN LINE FROM BUS 324622 [2LYNDON SO 69.000] TO BUS 324637 [2MIDDLETOWN 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1523 324622-324673(1) | OPEN LINE FROM BUS 324622 [2LYNDON SO 69.000] TO BUS 324673 [2OXMOOR 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -4.7684e-07 | -0.00034606
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1523 324622-324673(1) | OPEN LINE FROM BUS 324622 [2LYNDON SO 69.000] TO BUS 324673 [2OXMOOR 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1524 324623-324637(1) | OPEN LINE FROM BUS 324623 [2LYNDON 69.000] TO BUS 324637 [2MIDDLETOWN 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.4305e-06 | -0.00034702
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1524 324623-324637(1) | OPEN LINE FROM BUS 324623 [2LYNDON 69.000] TO BUS 324637 [2MIDDLETOWN 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1525 324626-324627(1) | OPEN LINE FROM BUS 324626 [2MANCHEST SO69.000] TO BUS 324627 [2MANCHEST KU69.000] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8353 | -1.1921e-05 | -0.00035751
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1525 324626-324627(1) | OPEN LINE FROM BUS 324626 [2MANCHEST SO69.000] TO BUS 324627 [2MANCHEST KU69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1526 324628-324629(1) | OPEN LINE FROM BUS 324628 [2MARION SO 69.000] TO BUS 324629 [2MARION KU 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 1.1921e-06 | -0.0003444
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1526 324628-324629(1) | OPEN LINE FROM BUS 324628 [2MARION SO 69.000] TO BUS 324629 [2MARION KU 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1527 324629-324904(1) | OPEN LINE FROM BUS 324629 [2MARION KU 69.000] TO BUS 324904 [2MEXICO KU 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 8.3447e-07 | -0.00034475
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1527 324629-324904(1) | OPEN LINE FROM BUS 324629 [2MARION KU 69.000] TO BUS 324904 [2MEXICO KU 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1528 324630-324862(1) | OPEN LINE FROM BUS 324630 [2MADSNV LP E69.000] TO BUS 324862 [2FIES CITY 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.7881e-07 | -0.00034577
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1528 324630-324862(1) | OPEN LINE FROM BUS 324630 [2MADSNV LP E69.000] TO BUS 324862 [2FIES CITY 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1529 324631-324658(1) | OPEN LINE FROM BUS 324631 [2MADSNV LP W69.000] TO BUS 324658 [2NEBO 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 5.9605e-08 | -0.00034553
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1529 324631-324658(1) | OPEN LINE FROM BUS 324631 [2MADSNV LP W69.000] TO BUS 324658 [2NEBO 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1530 324633-324636(1) | OPEN LINE FROM BUS 324633 [2MELDRUM 69.000] TO BUS 324636 [2MIDDLESBORO69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -2.2054e-06 | -0.00034779
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1530 324633-324636(1) | OPEN LINE FROM BUS 324633 [2MELDRUM 69.000] TO BUS 324636 [2MIDDLESBORO69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1531 324633-324684(1) | OPEN LINE FROM BUS 324633 [2MELDRUM 69.000] TO BUS 324684 [2PINEVIL 72269.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8359 | -3.9935e-06 | -0.00034958
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1531 324633-324684(1) | OPEN LINE FROM BUS 324633 [2MELDRUM 69.000] TO BUS 324684 [2PINEVIL 72269.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1532 324634-324849(1) | OPEN LINE FROM BUS 324634 [2METAL+THERM69.000] TO BUS 324849 [2DOW CORNING69.000] CKT 1 | 0.93965 | 64.8362 | 0.93988 | 64.8514 | 0.00022143 | -0.00012416
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1532 324634-324849(1) | OPEN LINE FROM BUS 324634 [2METAL+THERM69.000] TO BUS 324849 [2DOW CORNING69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1533 324636-324874(1) | OPEN LINE FROM BUS 324636 [2MIDDLESBORO69.000] TO BUS 324874 [2HARROGATE 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8367 | 7.4506e-06 | -0.00033814
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1533 324636-324874(1) | OPEN LINE FROM BUS 324636 [2MIDDLESBORO69.000] TO BUS 324874 [2HARROGATE 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1534 324637-324653(1) | OPEN LINE FROM BUS 324637 [2MIDDLETOWN 69.000] TO BUS 324653 [2M-V SIMPSON69.000] CKT 1 | 0.93965 | 64.8362 | 0.93971 | 64.8398 | 5.3287e-05 | -0.0002923
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1534 324637-324653(1) | OPEN LINE FROM BUS 324637 [2MIDDLETOWN 69.000] TO BUS 324653 [2M-V SIMPSON69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1535 324638-324706(1) | OPEN LINE FROM BUS 324638 [2MILL CRK KU69.000] TO BUS 324706 [2ROCKY BRNCH69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -8.9407e-07 | -0.00034648
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1535 324638-324706(1) | OPEN LINE FROM BUS 324638 [2MILL CRK KU69.000] TO BUS 324706 [2ROCKY BRNCH69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1536 324638-324813(1) | OPEN LINE FROM BUS 324638 [2MILL CRK KU69.000] TO BUS 324813 [2CARY 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -7.7486e-07 | -0.00034636
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1536 324638-324813(1) | OPEN LINE FROM BUS 324638 [2MILL CRK KU69.000] TO BUS 324813 [2CARY 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1537 324639-324642(1) | OPEN LINE FROM BUS 324639 [2MILLRSB624 69.000] TO BUS 324642 [2MILLERSBURG69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1538 324639-324812(1) | OPEN LINE FROM BUS 324639 [2MILLRSB624 69.000] TO BUS 324812 [2CARLISLE 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1539 324639-325035(1) | OPEN LINE FROM BUS 324639 [2MILLRSB624 69.000] TO BUS 325035 [2BLUE SOL TP69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1540 324641-324751(1) | OPEN LINE FROM BUS 324641 [2MILE LAN TP69.000] TO BUS 324751 [2TAYLOR CO 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8356 | -7.391e-06 | -0.00035298
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1540 324641-324751(1) | OPEN LINE FROM BUS 324641 [2MILE LAN TP69.000] TO BUS 324751 [2TAYLOR CO 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1541 324641-324829(1) | OPEN LINE FROM BUS 324641 [2MILE LAN TP69.000] TO BUS 324829 [2CAMPBELVIL169.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8359 | -4.3511e-06 | -0.00034994
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1541 324641-324829(1) | OPEN LINE FROM BUS 324641 [2MILE LAN TP69.000] TO BUS 324829 [2CAMPBELVIL169.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1542 324641-326970(1) | OPEN LINE FROM BUS 324641 [2MILE LAN TP69.000] TO BUS 326970 [2MILE LAN EK69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.1921e-06 | -0.00034678
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1542 324641-326970(1) | OPEN LINE FROM BUS 324641 [2MILE LAN TP69.000] TO BUS 326970 [2MILE LAN EK69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1543 324642-324677(1) | OPEN LINE FROM BUS 324642 [2MILLERSBURG69.000] TO BUS 324677 [2PARIS 12 69.000] CKT 1 | 0.93965 | 64.8362 | 0.9399 | 64.8533 | 0.00024813 | -9.7454e-05
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1543 324642-324677(1) | OPEN LINE FROM BUS 324642 [2MILLERSBURG69.000] TO BUS 324677 [2PARIS 12 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1544 324642-324679(1) | OPEN LINE FROM BUS 324642 [2MILLERSBURG69.000] TO BUS 324679 [2PARIS 3 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93983 | 64.8485 | 0.0001784 | -0.00016719
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1544 324642-324679(1) | OPEN LINE FROM BUS 324642 [2MILLERSBURG69.000] TO BUS 324679 [2PARIS 3 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1545 324642-324717(1) | OPEN LINE FROM BUS 324642 [2MILLERSBURG69.000] TO BUS 324717 [2SARDIS TAP 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93895 | 64.7874 | -0.00070614 | -0.0010517
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1545 324642-324717(1) | OPEN LINE FROM BUS 324642 [2MILLERSBURG69.000] TO BUS 324717 [2SARDIS TAP 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1546 324643-324811(1) | OPEN LINE FROM BUS 324643 [2MILL WOOD 69.000] TO BUS 324811 [2CANEYVL JCT69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 3.8743e-06 | -0.00034171
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1546 324643-324811(1) | OPEN LINE FROM BUS 324643 [2MILL WOOD 69.000] TO BUS 324811 [2CANEYVL JCT69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1547 324644-324645(1) | OPEN LINE FROM BUS 324644 [2MORGANFLD 469.000] TO BUS 324645 [2MORGANFIELD69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 1.7881e-07 | -0.00034541
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1547 324644-324645(1) | OPEN LINE FROM BUS 324644 [2MORGANFLD 469.000] TO BUS 324645 [2MORGANFIELD69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1548 324644-324776(1) | OPEN LINE FROM BUS 324644 [2MORGANFLD 469.000] TO BUS 324776 [2WHEATCROF T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 1.1921e-07 | -0.00034547
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1548 324644-324776(1) | OPEN LINE FROM BUS 324644 [2MORGANFLD 469.000] TO BUS 324776 [2WHEATCROF T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1549 324645-324671(1) | OPEN LINE FROM BUS 324645 [2MORGANFIELD69.000] TO BUS 324671 [2OVERLAD S T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.1921e-07 | -0.00034571
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1549 324645-324671(1) | OPEN LINE FROM BUS 324645 [2MORGANFIELD69.000] TO BUS 324671 [2OVERLAD S T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1550 324645-326546(1) | OPEN LINE FROM BUS 324645 [2MORGANFIELD69.000] TO BUS 326546 [2SUNOCO TAP 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 1.1921e-07 | -0.00034547
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1550 324645-326546(1) | OPEN LINE FROM BUS 324645 [2MORGANFIELD69.000] TO BUS 326546 [2SUNOCO TAP 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1551 324645-326572(1) | OPEN LINE FROM BUS 324645 [2MORGANFIELD69.000] TO BUS 326572 [2RIVRVW COAL69.000] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8374 | 1.806e-05 | -0.00032753
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1551 324645-326572(1) | OPEN LINE FROM BUS 324645 [2MORGANFIELD69.000] TO BUS 326572 [2RIVRVW COAL69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1552 324646-324707(1) | OPEN LINE FROM BUS 324646 [2MOREHEAD E 69.000] TO BUS 324707 [2RODBURN 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8353 | -1.2398e-05 | -0.00035799
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1552 324646-324707(1) | OPEN LINE FROM BUS 324646 [2MOREHEAD E 69.000] TO BUS 324707 [2RODBURN 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1553 324646-324910(1) | OPEN LINE FROM BUS 324646 [2MOREHEAD E 69.000] TO BUS 324910 [2MOREHEAD 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 8.3447e-07 | -0.00034475
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1553 324646-324910(1) | OPEN LINE FROM BUS 324646 [2MOREHEAD E 69.000] TO BUS 324910 [2MOREHEAD 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1554 324647-324910(1) | OPEN LINE FROM BUS 324647 [2MOREHEAD W 69.000] TO BUS 324910 [2MOREHEAD 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8358 | -5.7817e-06 | -0.00035137
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1554 324647-324910(1) | OPEN LINE FROM BUS 324647 [2MOREHEAD W 69.000] TO BUS 324910 [2MOREHEAD 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1555 324648-324664(1) | OPEN LINE FROM BUS 324648 [2MORTONS GAP69.000] TO BUS 324664 [2OAK HILL KU69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8365 | 4.2915e-06 | -0.0003413
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1555 324648-324664(1) | OPEN LINE FROM BUS 324648 [2MORTONS GAP69.000] TO BUS 324664 [2OAK HILL KU69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1556 324648-324769(1) | OPEN LINE FROM BUS 324648 [2MORTONS GAP69.000] TO BUS 324769 [2WALKER KU 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8366 | 6.3777e-06 | -0.00033921
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1556 324648-324769(1) | OPEN LINE FROM BUS 324648 [2MORTONS GAP69.000] TO BUS 324769 [2WALKER KU 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1557 324649-324675(1) | OPEN LINE FROM BUS 324649 [2MORRIS FORM69.000] TO BUS 324675 [2PADDYS RUN 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 4.1723e-07 | -0.00034517
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1557 324649-324675(1) | OPEN LINE FROM BUS 324649 [2MORRIS FORM69.000] TO BUS 324675 [2PADDYS RUN 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1558 324650-324891(1) | OPEN LINE FROM BUS 324650 [2MT TBR T 69.000] TO BUS 324891 [2LEX WATER 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8356 | -7.4506e-06 | -0.00035304
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1558 324650-324891(1) | OPEN LINE FROM BUS 324650 [2MT TBR T 69.000] TO BUS 324891 [2LEX WATER 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1559 324652-324817(1) | OPEN LINE FROM BUS 324652 [2MUHLENBRG P69.000] TO BUS 324817 [2CENTRAL CIT69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 5.9605e-08 | -0.00034553
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1559 324652-324817(1) | OPEN LINE FROM BUS 324652 [2MUHLENBRG P69.000] TO BUS 324817 [2CENTRAL CIT69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1560 324655-324748(1) | OPEN LINE FROM BUS 324655 [2N CORBIN T 69.000] TO BUS 324748 [2SWEET HOLLO69.000] CKT 1 | 0.93965 | 64.8362 | 0.93961 | 64.833 | -4.5061e-05 | -0.00039065
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1560 324655-324748(1) | OPEN LINE FROM BUS 324655 [2N CORBIN T 69.000] TO BUS 324748 [2SWEET HOLLO69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1561 324655-324791(1) | OPEN LINE FROM BUS 324655 [2N CORBIN T 69.000] TO BUS 324791 [2AISIN 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93963 | 64.8341 | -2.9266e-05 | -0.00037485
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1561 324655-324791(1) | OPEN LINE FROM BUS 324655 [2N CORBIN T 69.000] TO BUS 324791 [2AISIN 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1562 324655-326542(1) | OPEN LINE FROM BUS 324655 [2N CORBIN T 69.000] TO BUS 326542 [2N CORBIN 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93968 | 64.8377 | 2.2769e-05 | -0.00032282
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1562 324655-326542(1) | OPEN LINE FROM BUS 324655 [2N CORBIN T 69.000] TO BUS 326542 [2N CORBIN 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1563 324656-324968(1) | OPEN LINE FROM BUS 324656 [2N MADISON T69.000] TO BUS 324968 [2SPEAR STA B69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8368 | 1.0073e-05 | -0.00033551
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1563 324656-324968(1) | OPEN LINE FROM BUS 324656 [2N MADISON T69.000] TO BUS 324968 [2SPEAR STA B69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1564 324657-324771(1) | OPEN LINE FROM BUS 324657 [2NACHAND 69.000] TO BUS 324771 [2WATTERSON 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -1.967e-06 | -0.00034755
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1564 324657-324771(1) | OPEN LINE FROM BUS 324657 [2NACHAND 69.000] TO BUS 324771 [2WATTERSON 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1565 324658-324774(1) | OPEN LINE FROM BUS 324658 [2NEBO 69.000] TO BUS 324774 [2WEBCOAL 4 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 0 | -0.00034559
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1565 324658-324774(1) | OPEN LINE FROM BUS 324658 [2NEBO 69.000] TO BUS 324774 [2WEBCOAL 4 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1566 324658-324776(1) | OPEN LINE FROM BUS 324658 [2NEBO 69.000] TO BUS 324776 [2WHEATCROF T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 0 | -0.00034559
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1566 324658-324776(1) | OPEN LINE FROM BUS 324658 [2NEBO 69.000] TO BUS 324776 [2WHEATCROF T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1567 324658-324931(1) | OPEN LINE FROM BUS 324658 [2NEBO 69.000] TO BUS 324931 [2PROVIDNCE E69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 0 | -0.00034559
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1567 324658-324931(1) | OPEN LINE FROM BUS 324658 [2NEBO 69.000] TO BUS 324931 [2PROVIDNCE E69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1568 324659-326513(1) | OPEN LINE FROM BUS 324659 [2NELSON 69.000] TO BUS 326513 [2EQAL M BREC69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 1.7881e-07 | -0.00034541
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1568 324659-326513(1) | OPEN LINE FROM BUS 324659 [2NELSON 69.000] TO BUS 326513 [2EQAL M BREC69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1569 324660-324801(1) | OPEN LINE FROM BUS 324660 [2NEW HAVEN 69.000] TO BUS 324801 [2BARTON 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 1.9073e-06 | -0.00034368
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1569 324660-324801(1) | OPEN LINE FROM BUS 324660 [2NEW HAVEN 69.000] TO BUS 324801 [2BARTON 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1570 324661-324989(1) | OPEN LINE FROM BUS 324661 [2NICHLSV 7 69.000] TO BUS 324989 [2W NICHSV T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.9399 | 64.8529 | 0.00024223 | -0.00010335
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1570 324661-324989(1) | OPEN LINE FROM BUS 324661 [2NICHLSV 7 69.000] TO BUS 324989 [2W NICHSV T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1571 324662-324688(1) | OPEN LINE FROM BUS 324662 [2N LONDON KU69.000] TO BUS 324688 [2PITTSBRG KU69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8358 | -5.6624e-06 | -0.00035125
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1571 324662-324688(1) | OPEN LINE FROM BUS 324662 [2N LONDON KU69.000] TO BUS 324688 [2PITTSBRG KU69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1572 324663-324826(1) | OPEN LINE FROM BUS 324663 [2NORTON EAST69.000] TO BUS 324826 [2CLINCH V SW69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 6.5565e-07 | -0.00034493
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1572 324663-324826(1) | OPEN LINE FROM BUS 324663 [2NORTON EAST69.000] TO BUS 324826 [2CLINCH V SW69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1573 324667-324703(1) | OPEN LINE FROM BUS 324667 [2OHIO COUNTY69.000] TO BUS 324703 [2RIVERVIEW 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 6.5565e-07 | -0.00034493
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1573 324667-324703(1) | OPEN LINE FROM BUS 324667 [2OHIO COUNTY69.000] TO BUS 324703 [2RIVERVIEW 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1574 324667-324770(1) | OPEN LINE FROM BUS 324667 [2OHIO COUNTY69.000] TO BUS 324770 [2WARREN 4 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 2.861e-06 | -0.00034273
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1574 324667-324770(1) | OPEN LINE FROM BUS 324667 [2OHIO COUNTY69.000] TO BUS 324770 [2WARREN 4 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1575 324668-324936(1) | OPEN LINE FROM BUS 324668 [2OKONITE 69.000] TO BUS 324936 [2RICHMND IND69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -2.3842e-06 | -0.00034797
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1575 324668-324936(1) | OPEN LINE FROM BUS 324668 [2OKONITE 69.000] TO BUS 324936 [2RICHMND IND69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1576 324672-324916(1) | OPEN LINE FROM BUS 324672 [2OXFORD EK T69.000] TO BUS 324916 [2NEWTOWN TAP69.000] CKT 1 | 0.93965 | 64.8362 | 0.9397 | 64.8392 | 4.3988e-05 | -0.0003016
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1576 324672-324916(1) | OPEN LINE FROM BUS 324672 [2OXFORD EK T69.000] TO BUS 324916 [2NEWTOWN TAP69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1577 324674-324934(1) | OPEN LINE FROM BUS 324674 [2PROC & GAMB69.000] TO BUS 324934 [2RACE STREET69.000] CKT 1 | 0.93965 | 64.8362 | 0.9397 | 64.8392 | 4.4286e-05 | -0.0003013
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1577 324674-324934(1) | OPEN LINE FROM BUS 324674 [2PROC & GAMB69.000] TO BUS 324934 [2RACE STREET69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1578 324677-324680(1) | OPEN LINE FROM BUS 324677 [2PARIS 12 69.000] TO BUS 324680 [2PARIS KU 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93929 | 64.8108 | -0.00036734 | -0.00071293
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1578 324677-324680(1) | OPEN LINE FROM BUS 324677 [2PARIS 12 69.000] TO BUS 324680 [2PARIS KU 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1579 324678-324679(1) | OPEN LINE FROM BUS 324678 [2PARIS CITY 69.000] TO BUS 324679 [2PARIS 3 69.000] CKT 1 | 0.93965 | 64.8362 | 0.9395 | 64.8254 | -0.00015521 | -0.0005008
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1579 324678-324679(1) | OPEN LINE FROM BUS 324678 [2PARIS CITY 69.000] TO BUS 324679 [2PARIS 3 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1580 324678-324680(1) | OPEN LINE FROM BUS 324678 [2PARIS CITY 69.000] TO BUS 324680 [2PARIS KU 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93917 | 64.8025 | -0.00048733 | -0.00083292
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1580 324678-324680(1) | OPEN LINE FROM BUS 324678 [2PARIS CITY 69.000] TO BUS 324680 [2PARIS KU 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1581 324681-324960(1) | OPEN LINE FROM BUS 324681 [2PENAL FARM 69.000] TO BUS 324960 [2SKYLIGHT 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8357 | -6.4969e-06 | -0.00035208
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1581 324681-324960(1) | OPEN LINE FROM BUS 324681 [2PENAL FARM 69.000] TO BUS 324960 [2SKYLIGHT 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1582 324682-324887(1) | OPEN LINE FROM BUS 324682 [2PENAL TAP 69.000] TO BUS 324887 [2LA GRANG PE69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 6.5565e-07 | -0.00034493
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1582 324682-324887(1) | OPEN LINE FROM BUS 324682 [2PENAL TAP 69.000] TO BUS 324887 [2LA GRANG PE69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1583 324683-324866(1) | OPEN LINE FROM BUS 324683 [2PICADOME 69.000] TO BUS 324866 [2GE LAMP 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8371 | 1.3888e-05 | -0.0003317
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1583 324683-324866(1) | OPEN LINE FROM BUS 324683 [2PICADOME 69.000] TO BUS 324866 [2GE LAMP 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1584 324684-324686(1) | OPEN LINE FROM BUS 324684 [2PINEVIL 72269.000] TO BUS 324686 [2PINEVILLE 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8355 | -9.8944e-06 | -0.00035548
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1584 324684-324686(1) | OPEN LINE FROM BUS 324684 [2PINEVIL 72269.000] TO BUS 324686 [2PINEVILLE 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1585 324687-324694(1) | OPEN LINE FROM BUS 324687 [2PISGAH 69.000] TO BUS 324694 [2PARKR MIL T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93941 | 64.8195 | -0.00024194 | -0.00058752
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1585 324687-324694(1) | OPEN LINE FROM BUS 324687 [2PISGAH 69.000] TO BUS 324694 [2PARKR MIL T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1586 324689-324738(1) | OPEN LINE FROM BUS 324689 [2POCKET 69.000] TO BUS 324738 [2SAINT CHARL69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -1.7881e-06 | -0.00034738
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1586 324689-324738(1) | OPEN LINE FROM BUS 324689 [2POCKET 69.000] TO BUS 324738 [2SAINT CHARL69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1587 324689-324744(1) | OPEN LINE FROM BUS 324689 [2POCKET 69.000] TO BUS 324744 [2STRAGHT CRK69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8357 | -6.4969e-06 | -0.00035208
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1587 324689-324744(1) | OPEN LINE FROM BUS 324689 [2POCKET 69.000] TO BUS 324744 [2STRAGHT CRK69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1588 324690-324747(1) | OPEN LINE FROM BUS 324690 [2DAWSON TAP 69.000] TO BUS 324747 [2SUNSET MINE69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 1.7881e-06 | -0.0003438
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1588 324690-324747(1) | OPEN LINE FROM BUS 324690 [2DAWSON TAP 69.000] TO BUS 324747 [2SUNSET MINE69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1589 324690-324843(1) | OPEN LINE FROM BUS 324690 [2DAWSON TAP 69.000] TO BUS 324843 [2DAWSON IND 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 2.5034e-06 | -0.00034308
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1589 324690-324843(1) | OPEN LINE FROM BUS 324690 [2DAWSON TAP 69.000] TO BUS 324843 [2DAWSON IND 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1590 324691-324870(1) | OPEN LINE FROM BUS 324691 [2POWDERLY 69.000] TO BUS 324870 [2GREENVILLE 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 1.1921e-07 | -0.00034547
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1590 324691-324870(1) | OPEN LINE FROM BUS 324691 [2POWDERLY 69.000] TO BUS 324870 [2GREENVILLE 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1591 324692-324738(1) | OPEN LINE FROM BUS 324692 [2POWELL MTN 69.000] TO BUS 324738 [2SAINT CHARL69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.4305e-06 | -0.00034702
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1591 324692-324738(1) | OPEN LINE FROM BUS 324692 [2POWELL MTN 69.000] TO BUS 324738 [2SAINT CHARL69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1592 324693-324747(1) | OPEN LINE FROM BUS 324693 [2PRINCETON 69.000] TO BUS 324747 [2SUNSET MINE69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 1.8477e-06 | -0.00034374
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1592 324693-324747(1) | OPEN LINE FROM BUS 324693 [2PRINCETON 69.000] TO BUS 324747 [2SUNSET MINE69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1593 324694-324884(1) | OPEN LINE FROM BUS 324694 [2PARKR MIL T69.000] TO BUS 324884 [2KUNKEL 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8354 | -1.0848e-05 | -0.00035644
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1593 324694-324884(1) | OPEN LINE FROM BUS 324694 [2PARKR MIL T69.000] TO BUS 324884 [2KUNKEL 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1594 324694-324930(1) | OPEN LINE FROM BUS 324694 [2PARKR MIL T69.000] TO BUS 324930 [2PARKER MILL69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8357 | -7.093e-06 | -0.00035268
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1594 324694-324930(1) | OPEN LINE FROM BUS 324694 [2PARKR MIL T69.000] TO BUS 324930 [2PARKER MILL69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1595 324695-324749(1) | OPEN LINE FROM BUS 324695 [2PARKER SEAL69.000] TO BUS 324749 [2SYLVANIA 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 3.159e-06 | -0.00034243
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1595 324695-324749(1) | OPEN LINE FROM BUS 324695 [2PARKER SEAL69.000] TO BUS 324749 [2SYLVANIA 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1596 324695-324783(1) | OPEN LINE FROM BUS 324695 [2PARKER SEAL69.000] TO BUS 324783 [2WINCHSTR KU69.000] CKT 1 | 0.93965 | 64.8362 | 0.93963 | 64.8343 | -2.7478e-05 | -0.00037307
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1596 324695-324783(1) | OPEN LINE FROM BUS 324695 [2PARKER SEAL69.000] TO BUS 324783 [2WINCHSTR KU69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1597 324696-324706(1) | OPEN LINE FROM BUS 324696 [2PUCKETT CRK69.000] TO BUS 324706 [2ROCKY BRNCH69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 3.5763e-07 | -0.00034523
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1597 324696-324706(1) | OPEN LINE FROM BUS 324696 [2PUCKETT CRK69.000] TO BUS 324706 [2ROCKY BRNCH69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1598 324696-324792(1) | OPEN LINE FROM BUS 324696 [2PUCKETT CRK69.000] TO BUS 324792 [2ALVA 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 1.7881e-07 | -0.00034541
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1598 324696-324792(1) | OPEN LINE FROM BUS 324696 [2PUCKETT CRK69.000] TO BUS 324792 [2ALVA 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1599 324698-324708(1) | OPEN LINE FROM BUS 324698 [2RADCLIFF SO69.000] TO BUS 324708 [2ROGERSVILLE69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 0 | -0.00034559
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1599 324698-324708(1) | OPEN LINE FROM BUS 324698 [2RADCLIFF SO69.000] TO BUS 324708 [2ROGERSVILLE69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1600 324698-326555(1) | OPEN LINE FROM BUS 324698 [2RADCLIFF SO69.000] TO BUS 326555 [2RINEYVIL RD69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | -5.9605e-08 | -0.00034565
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1600 324698-326555(1) | OPEN LINE FROM BUS 324698 [2RADCLIFF SO69.000] TO BUS 326555 [2RINEYVIL RD69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1601 324699-324768(1) | OPEN LINE FROM BUS 324699 [2RICE STA TP69.000] TO BUS 324768 [2WACO 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 1.6689e-06 | -0.00034392
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1601 324699-324768(1) | OPEN LINE FROM BUS 324699 [2RICE STA TP69.000] TO BUS 324768 [2WACO 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1602 324699-326552(1) | OPEN LINE FROM BUS 324699 [2RICE STA TP69.000] TO BUS 326552 [2SE COAL TP 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8359 | -4.0531e-06 | -0.00034964
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1602 324699-326552(1) | OPEN LINE FROM BUS 324699 [2RICE STA TP69.000] TO BUS 326552 [2SE COAL TP 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1603 324700-324938(1) | OPEN LINE FROM BUS 324700 [2RICHMND SO 69.000] TO BUS 324938 [2RICHMND 3 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93963 | 64.8344 | -2.6107e-05 | -0.00037169
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1603 324700-324938(1) | OPEN LINE FROM BUS 324700 [2RICHMND SO 69.000] TO BUS 324938 [2RICHMND 3 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1604 324703-324959(1) | OPEN LINE FROM BUS 324703 [2RIVERVIEW 69.000] TO BUS 324959 [2SIMMONS 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 6.5565e-07 | -0.00034493
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1604 324703-324959(1) | OPEN LINE FROM BUS 324703 [2RIVERVIEW 69.000] TO BUS 324959 [2SIMMONS 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1605 324704-324784(1) | OPEN LINE FROM BUS 324704 [2ROCKHOLD 69.000] TO BUS 324784 [2WOFFORD 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8354 | -1.1444e-05 | -0.00035703
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1605 324704-324784(1) | OPEN LINE FROM BUS 324704 [2ROCKHOLD 69.000] TO BUS 324784 [2WOFFORD 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1606 324705-324783(1) | OPEN LINE FROM BUS 324705 [2ROCKWELL 69.000] TO BUS 324783 [2WINCHSTR KU69.000] CKT 1 | 0.93965 | 64.8362 | 0.93972 | 64.8405 | 6.2346e-05 | -0.00028324
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1606 324705-324783(1) | OPEN LINE FROM BUS 324705 [2ROCKWELL 69.000] TO BUS 324783 [2WINCHSTR KU69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1607 324705-324855(1) | OPEN LINE FROM BUS 324705 [2ROCKWELL 69.000] TO BUS 324855 [2EKPC OFF TP69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -1.6093e-06 | -0.0003472
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1607 324705-324855(1) | OPEN LINE FROM BUS 324705 [2ROCKWELL 69.000] TO BUS 324855 [2EKPC OFF TP69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1608 324708-324944(1) | OPEN LINE FROM BUS 324708 [2ROGERSVILLE69.000] TO BUS 324944 [2ROGERSV 60569.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8367 | 8.2254e-06 | -0.00033736
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1608 324708-324944(1) | OPEN LINE FROM BUS 324708 [2ROGERSVILLE69.000] TO BUS 324944 [2ROGERSV 60569.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1609 324709-324981(1) | OPEN LINE FROM BUS 324709 [2RVR QUEEN T69.000] TO BUS 324981 [2TEXAS GAS T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.7881e-07 | -0.00034577
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1609 324709-324981(1) | OPEN LINE FROM BUS 324709 [2RVR QUEEN T69.000] TO BUS 324981 [2TEXAS GAS T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1610 324710-324750(1) | OPEN LINE FROM BUS 324710 [2RVR CITY SH69.000] TO BUS 324750 [2TAYLOR LG 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 7.1526e-07 | -0.00034487
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1610 324710-324750(1) | OPEN LINE FROM BUS 324710 [2RVR CITY SH69.000] TO BUS 324750 [2TAYLOR LG 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1611 324711-324790(1) | OPEN LINE FROM BUS 324711 [2SPEN CHEM T69.000] TO BUS 324790 [2AIRLINE RD 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 1.6093e-06 | -0.00034398
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1611 324711-324790(1) | OPEN LINE FROM BUS 324711 [2SPEN CHEM T69.000] TO BUS 324790 [2AIRLINE RD 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1612 324712-324825(1) | OPEN LINE FROM BUS 324712 [2SO PADUCAH 69.000] TO BUS 324825 [2CLINTON KU 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 0 | -0.00034559
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1612 324712-324825(1) | OPEN LINE FROM BUS 324712 [2SO PADUCAH 69.000] TO BUS 324825 [2CLINTON KU 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1613 324713-324955(1) | OPEN LINE FROM BUS 324713 [2SO ELKHORN 69.000] TO BUS 324955 [2SHANNON RUN69.000] CKT 1 | 0.93965 | 64.8362 | 0.9397 | 64.8393 | 4.5419e-05 | -0.00030017
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1613 324713-324955(1) | OPEN LINE FROM BUS 324713 [2SO ELKHORN 69.000] TO BUS 324955 [2SHANNON RUN69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1614 324714-324733(1) | OPEN LINE FROM BUS 324714 [2SALT LICK 69.000] TO BUS 324733 [2SPENCER RD 69.000] CKT 1 | 0.93965 | 64.8362 | 0.9396 | 64.8321 | -5.8174e-05 | -0.00040376
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1614 324714-324733(1) | OPEN LINE FROM BUS 324714 [2SALT LICK 69.000] TO BUS 324733 [2SPENCER RD 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1615 324715-324721(1) | OPEN LINE FROM BUS 324715 [2SALVISA 69.000] TO BUS 324721 [2SHAKERTOWN 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93955 | 64.8287 | -0.00010794 | -0.00045353
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1615 324715-324721(1) | OPEN LINE FROM BUS 324715 [2SALVISA 69.000] TO BUS 324721 [2SHAKERTOWN 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1616 324715-325087(1) | OPEN LINE FROM BUS 324715 [2SALVISA 69.000] TO BUS 325087 [2CLAY LICK T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93955 | 64.8292 | -0.00010085 | -0.00044644
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1616 324715-325087(1) | OPEN LINE FROM BUS 324715 [2SALVISA 69.000] TO BUS 325087 [2CLAY LICK T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1617 324716-324977(1) | OPEN LINE FROM BUS 324716 [2SANDY RIDGE69.000] TO BUS 324977 [2TOMS CRK TP69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8359 | -3.5763e-06 | -0.00034916
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1617 324716-324977(1) | OPEN LINE FROM BUS 324716 [2SANDY RIDGE69.000] TO BUS 324977 [2TOMS CRK TP69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1618 324717-326549(1) | OPEN LINE FROM BUS 324717 [2SARDIS TAP 69.000] TO BUS 326549 [2SARDIS 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93976 | 64.8436 | 0.00010753 | -0.00023806
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1618 324717-326549(1) | OPEN LINE FROM BUS 324717 [2SARDIS TAP 69.000] TO BUS 326549 [2SARDIS 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1619 324718-324726(1) | OPEN LINE FROM BUS 324718 [2SHELBY CO T69.000] TO BUS 324726 [2SHELBYVIL S69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8365 | 5.6028e-06 | -0.00033998
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1619 324718-324726(1) | OPEN LINE FROM BUS 324718 [2SHELBY CO T69.000] TO BUS 324726 [2SHELBYVIL S69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1620 324719-324724(1) | OPEN LINE FROM BUS 324719 [2SEMINOLE 69.000] TO BUS 324724 [2SHIVELY 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 9.5367e-07 | -0.00034463
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1620 324719-324724(1) | OPEN LINE FROM BUS 324719 [2SEMINOLE 69.000] TO BUS 324724 [2SHIVELY 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1621 324721-324764(1) | OPEN LINE FROM BUS 324721 [2SHAKERTOWN 69.000] TO BUS 324764 [2WEST CLIFF 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93954 | 64.8281 | -0.00011736 | -0.00046295
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1621 324721-324764(1) | OPEN LINE FROM BUS 324721 [2SHAKERTOWN 69.000] TO BUS 324764 [2WEST CLIFF 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1622 324723-325086(1) | OPEN LINE FROM BUS 324723 [2SHAVER CHAP69.000] TO BUS 325086 [2KEN AMERI 269.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -2.3842e-07 | -0.00034583
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1622 324723-325086(1) | OPEN LINE FROM BUS 324723 [2SHAVER CHAP69.000] TO BUS 325086 [2KEN AMERI 269.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1623 324725-324727(1) | OPEN LINE FROM BUS 324725 [2SHELBYVIL E69.000] TO BUS 324727 [2SHELBYVILLE69.000] CKT 1 | 0.93965 | 64.8362 | 0.93976 | 64.8432 | 0.00010246 | -0.00024313
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1623 324725-324727(1) | OPEN LINE FROM BUS 324725 [2SHELBYVIL E69.000] TO BUS 324727 [2SHELBYVILLE69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1624 324726-324727(1) | OPEN LINE FROM BUS 324726 [2SHELBYVIL S69.000] TO BUS 324727 [2SHELBYVILLE69.000] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8373 | 1.6153e-05 | -0.00032943
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1624 324726-324727(1) | OPEN LINE FROM BUS 324726 [2SHELBYVIL S69.000] TO BUS 324727 [2SHELBYVILLE69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1625 324727-325102(1) | OPEN LINE FROM BUS 324727 [2SHELBYVILLE69.000] TO BUS 325102 [2W SHELBY 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93968 | 64.8377 | 2.2531e-05 | -0.00032306
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1625 324727-325102(1) | OPEN LINE FROM BUS 324727 [2SHELBYVILLE69.000] TO BUS 325102 [2W SHELBY 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1626 324728-324781(1) | OPEN LINE FROM BUS 324728 [2SHUN PIKE 69.000] TO BUS 324781 [2WILMORE T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 3.6955e-06 | -0.00034189
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1626 324728-324781(1) | OPEN LINE FROM BUS 324728 [2SHUN PIKE 69.000] TO BUS 324781 [2WILMORE T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1627 324729-325102(1) | OPEN LINE FROM BUS 324729 [2SIMPSONVILL69.000] TO BUS 325102 [2W SHELBY 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93972 | 64.8404 | 6.181e-05 | -0.00028378
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1627 324729-325102(1) | OPEN LINE FROM BUS 324729 [2SIMPSONVILL69.000] TO BUS 325102 [2W SHELBY 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1628 324731-326547(1) | OPEN LINE FROM BUS 324731 [2SONORA TAP 69.000] TO BUS 326547 [2SONORA 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 1.3113e-06 | -0.00034428
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1628 324731-326547(1) | OPEN LINE FROM BUS 324731 [2SONORA TAP 69.000] TO BUS 326547 [2SONORA 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1629 324734-324848(1) | OPEN LINE FROM BUS 324734 [2SPINDLETP T69.000] TO BUS 324848 [2DONERAIL 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93958 | 64.8309 | -7.5459e-05 | -0.00042105
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1629 324734-324848(1) | OPEN LINE FROM BUS 324734 [2SPINDLETP T69.000] TO BUS 324848 [2DONERAIL 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1630 324735-324794(1) | OPEN LINE FROM BUS 324735 [2SOUTH POINT69.000] TO BUS 324794 [2ASHLND PIPE69.000] CKT 1 | 0.93965 | 64.8362 | 0.93961 | 64.8328 | -4.828e-05 | -0.00039387
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1630 324735-324794(1) | OPEN LINE FROM BUS 324735 [2SOUTH POINT69.000] TO BUS 324794 [2ASHLND PIPE69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
324794 | 2ASHLND PIPE | 69 | LGEE' | RANGE | 0.94 | 1.06 | SINGLE OPN LIN 1630 324735-324794(1) | OPEN LINE FROM BUS 324735 [2SOUTH POINT69.000] TO BUS 324794 [2ASHLND PIPE69.000] CKT 1 | 1.0045 | 69.309 | 0.91556 | 63.1738 | -0.088916 | -0.024438
324842 | 2DAVIS TAP | 69 | LGEE' | RANGE | 0.94 | 1.06 | SINGLE OPN LIN 1630 324735-324794(1) | OPEN LINE FROM BUS 324735 [2SOUTH POINT69.000] TO BUS 324794 [2ASHLND PIPE69.000] CKT 1 | 1.0037 | 69.2557 | 0.923 | 63.687 | -0.080705 | -0.016999
324967 | 2SPEAR STA A | 69 | LGEE' | RANGE | 0.94 | 1.06 | SINGLE OPN LIN 1630 324735-324794(1) | OPEN LINE FROM BUS 324735 [2SOUTH POINT69.000] TO BUS 324794 [2ASHLND PIPE69.000] CKT 1 | 1.0026 | 69.1798 | 0.93423 | 64.4619 | -0.068375 | -0.0057696
324987 | 2W HICKMAN | 69 | LGEE' | RANGE | 0.94 | 1.06 | SINGLE OPN LIN 1630 324735-324794(1) | OPEN LINE FROM BUS 324735 [2SOUTH POINT69.000] TO BUS 324794 [2ASHLND PIPE69.000] CKT 1 | 1.0044 | 69.3064 | 0.91558 | 63.1752 | -0.088858 | -0.024417
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1631 324737-324969(1) | OPEN LINE FROM BUS 324737 [2SOMERSET SO69.000] TO BUS 324969 [2SMRST 615KU69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 3.9339e-06 | -0.00034165
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1631 324737-324969(1) | OPEN LINE FROM BUS 324737 [2SOMERSET SO69.000] TO BUS 324969 [2SMRST 615KU69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1632 324740-324788(1) | OPEN LINE FROM BUS 324740 [2SOUTH PARK 69.000] TO BUS 324788 [2BROOKS EK T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.3113e-06 | -0.0003469
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1632 324740-324788(1) | OPEN LINE FROM BUS 324740 [2SOUTH PARK 69.000] TO BUS 324788 [2BROOKS EK T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1633 324740-325024(1) | OPEN LINE FROM BUS 324740 [2SOUTH PARK 69.000] TO BUS 325024 [2ASHBOT SPRK69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -2.8014e-06 | -0.00034839
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1633 324740-325024(1) | OPEN LINE FROM BUS 324740 [2SOUTH PARK 69.000] TO BUS 325024 [2ASHBOT SPRK69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
325043 | 2SHEPHERDSV | 69 | LGEE' | RANGE | 0.94 | 1.06 | SINGLE OPN LIN 1633 324740-325024(1) | OPEN LINE FROM BUS 324740 [2SOUTH PARK 69.000] TO BUS 325024 [2ASHBOT SPRK69.000] CKT 1 | 0.9733 | 67.1579 | 0.93738 | 64.679 | -0.035925 | -0.0026225
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1634 324742-324866(1) | OPEN LINE FROM BUS 324742 [2STONEWALL T69.000] TO BUS 324866 [2GE LAMP 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8359 | -4.2915e-06 | -0.00034988
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1634 324742-324866(1) | OPEN LINE FROM BUS 324742 [2STONEWALL T69.000] TO BUS 324866 [2GE LAMP 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1635 324742-324972(1) | OPEN LINE FROM BUS 324742 [2STONEWALL T69.000] TO BUS 324972 [2STONEWALL 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93963 | 64.8347 | -2.0921e-05 | -0.00036651
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1635 324742-324972(1) | OPEN LINE FROM BUS 324742 [2STONEWALL T69.000] TO BUS 324972 [2STONEWALL 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1636 324743-324759(1) | OPEN LINE FROM BUS 324743 [2SAINT PAUL 69.000] TO BUS 324759 [2VIRGINIA CI69.000] CKT 1 | 0.93965 | 64.8362 | 0.93962 | 64.8338 | -3.3915e-05 | -0.0003795
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1636 324743-324759(1) | OPEN LINE FROM BUS 324743 [2SAINT PAUL 69.000] TO BUS 324759 [2VIRGINIA CI69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1637 324743-324851(1) | OPEN LINE FROM BUS 324743 [2SAINT PAUL 69.000] TO BUS 324851 [2DWINA TAP 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 5.3644e-07 | -0.00034505
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1637 324743-324851(1) | OPEN LINE FROM BUS 324743 [2SAINT PAUL 69.000] TO BUS 324851 [2DWINA TAP 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1638 324744-324876(1) | OPEN LINE FROM BUS 324744 [2STRAGHT CRK69.000] TO BUS 324876 [2HOLMES MILL69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8358 | -5.0068e-06 | -0.00035059
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1638 324744-324876(1) | OPEN LINE FROM BUS 324744 [2STRAGHT CRK69.000] TO BUS 324876 [2HOLMES MILL69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1639 324746-326546(1) | OPEN LINE FROM BUS 324746 [2SUNOCO 69.000] TO BUS 326546 [2SUNOCO TAP 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 5.3644e-07 | -0.00034505
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1639 324746-326546(1) | OPEN LINE FROM BUS 324746 [2SUNOCO 69.000] TO BUS 326546 [2SUNOCO TAP 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1640 324751-325921(1) | OPEN LINE FROM BUS 324751 [2TAYLOR CO 69.000] TO BUS 325921 [5TAYLOR CO 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8356 | -7.5102e-06 | -0.0003531
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1640 324751-325921(1) | OPEN LINE FROM BUS 324751 [2TAYLOR CO 69.000] TO BUS 325921 [5TAYLOR CO 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1641 324752-324974(1) | OPEN LINE FROM BUS 324752 [2TAYLORSV KU69.000] TO BUS 324974 [2TAYLRV EK T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8352 | -1.3888e-05 | -0.00035948
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1641 324752-324974(1) | OPEN LINE FROM BUS 324752 [2TAYLORSV KU69.000] TO BUS 324974 [2TAYLRV EK T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1642 324754-324928(1) | OPEN LINE FROM BUS 324754 [2TUNNEL H KU69.000] TO BUS 324928 [2POOLE 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 2.0862e-06 | -0.0003435
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1642 324754-324928(1) | OPEN LINE FROM BUS 324754 [2TUNNEL H KU69.000] TO BUS 324928 [2POOLE 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1643 324755-324762(1) | OPEN LINE FROM BUS 324755 [2TYRONE 69.000] TO BUS 324762 [2VERSAIL W T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93969 | 64.8386 | 3.5346e-05 | -0.00031024
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1643 324755-324762(1) | OPEN LINE FROM BUS 324755 [2TYRONE 69.000] TO BUS 324762 [2VERSAIL W T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1644 324755-324920(1) | OPEN LINE FROM BUS 324755 [2TYRONE 69.000] TO BUS 324920 [2NINEVAH TAP69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8368 | 9.1791e-06 | -0.00033641
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1644 324755-324920(1) | OPEN LINE FROM BUS 324755 [2TYRONE 69.000] TO BUS 324920 [2NINEVAH TAP69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1645 324755-324985(1) | OPEN LINE FROM BUS 324755 [2TYRONE 69.000] TO BUS 324985 [2VSAIL BYPAS69.000] CKT 1 | 0.93965 | 64.8362 | 0.93937 | 64.8166 | -0.00028408 | -0.00062966
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1645 324755-324985(1) | OPEN LINE FROM BUS 324755 [2TYRONE 69.000] TO BUS 324985 [2VSAIL BYPAS69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1646 324756-324772(1) | OPEN LINE FROM BUS 324756 [2UK WEST 1 69.000] TO BUS 324772 [2UK WEST 2 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93968 | 64.8377 | 2.2531e-05 | -0.00032306
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1646 324756-324772(1) | OPEN LINE FROM BUS 324756 [2UK WEST 1 69.000] TO BUS 324772 [2UK WEST 2 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1647 324756-324952(1) | OPEN LINE FROM BUS 324756 [2UK WEST 1 69.000] TO BUS 324952 [2SCOTT ST TP69.000] CKT 1 | 0.93965 | 64.8362 | 0.93969 | 64.8384 | 3.2961e-05 | -0.00031263
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1647 324756-324952(1) | OPEN LINE FROM BUS 324756 [2UK WEST 1 69.000] TO BUS 324952 [2SCOTT ST TP69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1648 324757-324941(1) | OPEN LINE FROM BUS 324757 [2UPR MIL CRK69.000] TO BUS 324941 [2RIVERPORT 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -9.5367e-07 | -0.00034654
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1648 324757-324941(1) | OPEN LINE FROM BUS 324757 [2UPR MIL CRK69.000] TO BUS 324941 [2RIVERPORT 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
324941 | 2RIVERPORT | 69 | LGEE' | RANGE | 0.94 | 1.06 | SINGLE OPN LIN 1648 324757-324941(1) | OPEN LINE FROM BUS 324757 [2UPR MIL CRK69.000] TO BUS 324941 [2RIVERPORT 69.000] CKT 1 | 0.992 | 68.4483 | 0.93737 | 64.6784 | -0.054637 | -0.002632
324975 | 2TERRY | 69 | LGEE' | RANGE | 0.94 | 1.06 | SINGLE OPN LIN 1648 324757-324941(1) | OPEN LINE FROM BUS 324757 [2UPR MIL CRK69.000] TO BUS 324941 [2RIVERPORT 69.000] CKT 1 | 0.98781 | 68.1591 | 0.93737 | 64.6783 | -0.050446 | -0.0026329
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1649 324758-324833(1) | OPEN LINE FROM BUS 324758 [2US STEEL 69.000] TO BUS 324833 [2CORBIN 2 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93973 | 64.8415 | 7.7009e-05 | -0.00026858
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1649 324758-324833(1) | OPEN LINE FROM BUS 324758 [2US STEEL 69.000] TO BUS 324833 [2CORBIN 2 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1650 324760-324838(1) | OPEN LINE FROM BUS 324760 [2VAKSDAHL AV69.000] TO BUS 324838 [2DANV IND TP69.000] CKT 1 | 0.93965 | 64.8362 | 0.93963 | 64.8342 | -2.8849e-05 | -0.00037444
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1650 324760-324838(1) | OPEN LINE FROM BUS 324760 [2VAKSDAHL AV69.000] TO BUS 324838 [2DANV IND TP69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1651 324763-324985(1) | OPEN LINE FROM BUS 324763 [2VERSAILLES 69.000] TO BUS 324985 [2VSAIL BYPAS69.000] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8351 | -1.4722e-05 | -0.00036031
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1651 324763-324985(1) | OPEN LINE FROM BUS 324763 [2VERSAILLES 69.000] TO BUS 324985 [2VSAIL BYPAS69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1652 324764-326578(1) | OPEN LINE FROM BUS 324764 [2WEST CLIFF 69.000] TO BUS 326578 [2HARRDSBRG 169.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8357 | -6.8545e-06 | -0.00035244
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1652 324764-326578(1) | OPEN LINE FROM BUS 324764 [2WEST CLIFF 69.000] TO BUS 326578 [2HARRDSBRG 169.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1653 324765-326528(1) | OPEN LINE FROM BUS 324765 [2W FRANKFORT69.000] TO BUS 326528 [2BRIDGEPORT 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93955 | 64.8289 | -0.0001055 | -0.00045109
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1653 324765-326528(1) | OPEN LINE FROM BUS 324765 [2W FRANKFORT69.000] TO BUS 326528 [2BRIDGEPORT 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1654 324765-326973(1) | OPEN LINE FROM BUS 324765 [2W FRANKFORT69.000] TO BUS 326973 [2BRIDGPRT 1 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8356 | -7.5102e-06 | -0.0003531
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1654 324765-326973(1) | OPEN LINE FROM BUS 324765 [2W FRANKFORT69.000] TO BUS 326973 [2BRIDGPRT 1 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1655 324766-324952(1) | OPEN LINE FROM BUS 324766 [2W HIGH T1 69.000] TO BUS 324952 [2SCOTT ST TP69.000] CKT 1 | 0.93965 | 64.8362 | 0.93971 | 64.8398 | 5.2691e-05 | -0.0002929
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1655 324766-324952(1) | OPEN LINE FROM BUS 324766 [2W HIGH T1 69.000] TO BUS 324952 [2SCOTT ST TP69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1656 324767-326552(Z1) | OPEN LINE FROM BUS 324767 [2WEST IRVINE69.000] TO BUS 326552 [2SE COAL TP 69.000] CKT Z1 | 0.93965 | 64.8362 | 0.93965 | 64.8359 | -3.5167e-06 | -0.0003491
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1656 324767-326552(Z1) | OPEN LINE FROM BUS 324767 [2WEST IRVINE69.000] TO BUS 326552 [2SE COAL TP 69.000] CKT Z1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1657 324770-324946(1) | OPEN LINE FROM BUS 324770 [2WARREN 4 69.000] TO BUS 324946 [2ROSINE JCT 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 2.7418e-06 | -0.00034285
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1657 324770-324946(1) | OPEN LINE FROM BUS 324770 [2WARREN 4 69.000] TO BUS 324946 [2ROSINE JCT 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1658 324774-324993(1) | OPEN LINE FROM BUS 324774 [2WEBCOAL 4 69.000] TO BUS 324993 [2WARRIOR CL 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 0 | -0.00034559
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1658 324774-324993(1) | OPEN LINE FROM BUS 324774 [2WEBCOAL 4 69.000] TO BUS 324993 [2WARRIOR CL 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1659 324776-324777(1) | OPEN LINE FROM BUS 324776 [2WHEATCROF T69.000] TO BUS 324777 [2WHEATCROFT 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 5.9605e-08 | -0.00034553
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1659 324776-324777(1) | OPEN LINE FROM BUS 324776 [2WHEATCROF T69.000] TO BUS 324777 [2WHEATCROFT 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1660 324777-324973(1) | OPEN LINE FROM BUS 324777 [2WHEATCROFT 69.000] TO BUS 324973 [2STURGIS 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 5.9605e-08 | -0.00034553
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1660 324777-324973(1) | OPEN LINE FROM BUS 324777 [2WHEATCROFT 69.000] TO BUS 324973 [2STURGIS 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1661 324778-324779(1) | OPEN LINE FROM BUS 324778 [2WICKLIFE CI69.000] TO BUS 324779 [2WICKLIFFE 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 5.9605e-08 | -0.00034553
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1661 324778-324779(1) | OPEN LINE FROM BUS 324778 [2WICKLIFE CI69.000] TO BUS 324779 [2WICKLIFFE 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1662 324782-324783(1) | OPEN LINE FROM BUS 324782 [2WINCHEST SO69.000] TO BUS 324783 [2WINCHSTR KU69.000] CKT 1 | 0.93965 | 64.8362 | 0.93905 | 64.7945 | -0.0006038 | -0.00094938
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1662 324782-324783(1) | OPEN LINE FROM BUS 324782 [2WINCHEST SO69.000] TO BUS 324783 [2WINCHSTR KU69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1663 324784-325001(1) | OPEN LINE FROM BUS 324784 [2WOFFORD 69.000] TO BUS 325001 [2WILLMBRG SW69.000] CKT 1 | 0.93965 | 64.8362 | 0.9397 | 64.8395 | 4.8459e-05 | -0.00029713
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1663 324784-325001(1) | OPEN LINE FROM BUS 324784 [2WOFFORD 69.000] TO BUS 325001 [2WILLMBRG SW69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1664 324786-324790(1) | OPEN LINE FROM BUS 324786 [2ZION 69.000] TO BUS 324790 [2AIRLINE RD 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 1.1325e-06 | -0.00034446
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1664 324786-324790(1) | OPEN LINE FROM BUS 324786 [2ZION 69.000] TO BUS 324790 [2AIRLINE RD 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1665 324787-324990(1) | OPEN LINE FROM BUS 324787 [2UNION UNDWR69.000] TO BUS 324990 [2WAITSBORO 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8356 | -8.0466e-06 | -0.00035363
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1665 324787-324990(1) | OPEN LINE FROM BUS 324787 [2UNION UNDWR69.000] TO BUS 324990 [2WAITSBORO 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1666 324788-324809(1) | OPEN LINE FROM BUS 324788 [2BROOKS EK T69.000] TO BUS 324809 [2BROOKS EKPC69.000] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8354 | -1.055e-05 | -0.00035614
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1666 324788-324809(1) | OPEN LINE FROM BUS 324788 [2BROOKS EK T69.000] TO BUS 324809 [2BROOKS EKPC69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1667 324789-324806(1) | OPEN LINE FROM BUS 324789 [2BLUE LCK TP69.000] TO BUS 324806 [2BEULAH EKPC69.000] CKT 1 | 0.93965 | 64.8362 | 0.93962 | 64.834 | -3.1769e-05 | -0.00037736
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1667 324789-324806(1) | OPEN LINE FROM BUS 324789 [2BLUE LCK TP69.000] TO BUS 324806 [2BEULAH EKPC69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1668 324789-325021(1) | OPEN LINE FROM BUS 324789 [2BLUE LCK TP69.000] TO BUS 325021 [2CONESTOGA 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 2.7418e-06 | -0.00034285
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1668 324789-325021(1) | OPEN LINE FROM BUS 324789 [2BLUE LCK TP69.000] TO BUS 325021 [2CONESTOGA 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1669 324791-324860(1) | OPEN LINE FROM BUS 324791 [2AISIN 69.000] TO BUS 324860 [2FARISTON 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.4305e-06 | -0.00034702
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1669 324791-324860(1) | OPEN LINE FROM BUS 324791 [2AISIN 69.000] TO BUS 324860 [2FARISTON 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1670 324792-324819(1) | OPEN LINE FROM BUS 324792 [2ALVA 69.000] TO BUS 324819 [2CHUNKLIC BR69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 3.5763e-07 | -0.00034523
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1670 324792-324819(1) | OPEN LINE FROM BUS 324792 [2ALVA 69.000] TO BUS 324819 [2CHUNKLIC BR69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1671 324794-324987(1) | OPEN LINE FROM BUS 324794 [2ASHLND PIPE69.000] TO BUS 324987 [2W HICKMAN 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8357 | -6.3777e-06 | -0.00035197
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1671 324794-324987(1) | OPEN LINE FROM BUS 324794 [2ASHLND PIPE69.000] TO BUS 324987 [2W HICKMAN 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1672 324795-324922(1) | OPEN LINE FROM BUS 324795 [2ASHBYBRG PU69.000] TO BUS 324922 [2ONTON 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.1921e-07 | -0.00034571
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1672 324795-324922(1) | OPEN LINE FROM BUS 324795 [2ASHBYBRG PU69.000] TO BUS 324922 [2ONTON 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1673 324797-324855(1) | OPEN LINE FROM BUS 324797 [2AVON T1 69.000] TO BUS 324855 [2EKPC OFF TP69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -1.9073e-06 | -0.0003475
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1673 324797-324855(1) | OPEN LINE FROM BUS 324797 [2AVON T1 69.000] TO BUS 324855 [2EKPC OFF TP69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1674 324798-324875(1) | OPEN LINE FROM BUS 324798 [2BAILEY CRK 69.000] TO BUS 324875 [2HIGHSPLINT 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8359 | -3.2783e-06 | -0.00034887
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1674 324798-324875(1) | OPEN LINE FROM BUS 324798 [2BAILEY CRK 69.000] TO BUS 324875 [2HIGHSPLINT 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1675 324799-324931(1) | OPEN LINE FROM BUS 324799 [2BARNHILL 69.000] TO BUS 324931 [2PROVIDNCE E69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 0 | -0.00034559
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1675 324799-324931(1) | OPEN LINE FROM BUS 324799 [2BARNHILL 69.000] TO BUS 324931 [2PROVIDNCE E69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1676 324799-324932(1) | OPEN LINE FROM BUS 324799 [2BARNHILL 69.000] TO BUS 324932 [2PROVIDENCE 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 0 | -0.00034559
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1676 324799-324932(1) | OPEN LINE FROM BUS 324799 [2BARNHILL 69.000] TO BUS 324932 [2PROVIDENCE 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1677 324802-324871(1) | OPEN LINE FROM BUS 324802 [2BEAR BRANCH69.000] TO BUS 324871 [2HAMER 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -7.7486e-07 | -0.00034636
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1677 324802-324871(1) | OPEN LINE FROM BUS 324802 [2BEAR BRANCH69.000] TO BUS 324871 [2HAMER 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1678 324803-324907(1) | OPEN LINE FROM BUS 324803 [2BEAR TRACK 69.000] TO BUS 324907 [2MILLER CRK 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8365 | 5.1856e-06 | -0.0003404
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1678 324803-324907(1) | OPEN LINE FROM BUS 324803 [2BEAR TRACK 69.000] TO BUS 324907 [2MILLER CRK 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1679 324803-325058(1) | OPEN LINE FROM BUS 324803 [2BEAR TRACK 69.000] TO BUS 325058 [2BEATTY 614 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8366 | 5.8413e-06 | -0.00033975
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1679 324803-325058(1) | OPEN LINE FROM BUS 324803 [2BEAR TRACK 69.000] TO BUS 325058 [2BEATTY 614 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1680 324804-324908(1) | OPEN LINE FROM BUS 324804 [2BEDFORD TAP69.000] TO BUS 324908 [2MILTON 69.000] CKT 1 | 0.93965 | 64.8362 | 0.9396 | 64.8327 | -4.9651e-05 | -0.00039524
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1680 324804-324908(1) | OPEN LINE FROM BUS 324804 [2BEDFORD TAP69.000] TO BUS 324908 [2MILTON 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1681 324804-325033(1) | OPEN LINE FROM BUS 324804 [2BEDFORD TAP69.000] TO BUS 325033 [2BEDFORD KU 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 1.6093e-06 | -0.00034398
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1681 324804-325033(1) | OPEN LINE FROM BUS 324804 [2BEDFORD TAP69.000] TO BUS 325033 [2BEDFORD KU 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1682 324806-324925(1) | OPEN LINE FROM BUS 324806 [2BEULAH EKPC69.000] TO BUS 324925 [2PLEAS GRV T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93963 | 64.8345 | -2.3663e-05 | -0.00036925
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1682 324806-324925(1) | OPEN LINE FROM BUS 324806 [2BEULAH EKPC69.000] TO BUS 324925 [2PLEAS GRV T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1683 324808-324913(1) | OPEN LINE FROM BUS 324808 [2BRODHEAD KU69.000] TO BUS 324913 [2MT VERNON 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93962 | 64.8335 | -3.8922e-05 | -0.00038451
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1683 324808-324913(1) | OPEN LINE FROM BUS 324808 [2BRODHEAD KU69.000] TO BUS 324913 [2MT VERNON 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1684 324809-324958(1) | OPEN LINE FROM BUS 324809 [2BROOKS EKPC69.000] TO BUS 324958 [2SHEPHRDSV T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 1.7285e-06 | -0.00034386
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1684 324809-324958(1) | OPEN LINE FROM BUS 324809 [2BROOKS EKPC69.000] TO BUS 324958 [2SHEPHRDSV T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1685 324810-324947(1) | OPEN LINE FROM BUS 324810 [2CALHOUN 69.000] TO BUS 324947 [2RUMSEY 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 8.3447e-07 | -0.00034475
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1685 324810-324947(1) | OPEN LINE FROM BUS 324810 [2CALHOUN 69.000] TO BUS 324947 [2RUMSEY 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1686 324811-324946(1) | OPEN LINE FROM BUS 324811 [2CANEYVL JCT69.000] TO BUS 324946 [2ROSINE JCT 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 3.4571e-06 | -0.00034213
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1686 324811-324946(1) | OPEN LINE FROM BUS 324811 [2CANEYVL JCT69.000] TO BUS 324946 [2ROSINE JCT 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1687 324814-324956(1) | OPEN LINE FROM BUS 324814 [2CATRON CK T69.000] TO BUS 324956 [2SHAWNEE GAS69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 1.6093e-06 | -0.00034398
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1687 324814-324956(1) | OPEN LINE FROM BUS 324814 [2CATRON CK T69.000] TO BUS 324956 [2SHAWNEE GAS69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1688 324815-325007(1) | OPEN LINE FROM BUS 324815 [2CAWOOD 69.000] TO BUS 325007 [2YANCY TAP 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -8.3447e-07 | -0.00034642
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1688 324815-325007(1) | OPEN LINE FROM BUS 324815 [2CAWOOD 69.000] TO BUS 325007 [2YANCY TAP 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1689 324816-324970(1) | OPEN LINE FROM BUS 324816 [2CEMETARY RD69.000] TO BUS 324970 [2STANFORD KU69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 1.1325e-06 | -0.00034446
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1689 324816-324970(1) | OPEN LINE FROM BUS 324816 [2CEMETARY RD69.000] TO BUS 324970 [2STANFORD KU69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1690 324818-324827(1) | OPEN LINE FROM BUS 324818 [2CHAD TAP 69.000] TO BUS 324827 [2CLOVERLICK 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8365 | 4.4703e-06 | -0.00034112
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1690 324818-324827(1) | OPEN LINE FROM BUS 324818 [2CHAD TAP 69.000] TO BUS 324827 [2CLOVERLICK 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1691 324818-324978(1) | OPEN LINE FROM BUS 324818 [2CHAD TAP 69.000] TO BUS 324978 [2TOTZ 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.0729e-06 | -0.00034666
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1691 324818-324978(1) | OPEN LINE FROM BUS 324818 [2CHAD TAP 69.000] TO BUS 324978 [2TOTZ 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1692 324819-324945(1) | OPEN LINE FROM BUS 324819 [2CHUNKLIC BR69.000] TO BUS 324945 [2ROSE HILL T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 3.5763e-07 | -0.00034523
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1692 324819-324945(1) | OPEN LINE FROM BUS 324819 [2CHUNKLIC BR69.000] TO BUS 324945 [2ROSE HILL T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1693 324820-324850(1) | OPEN LINE FROM BUS 324820 [2ISLAND MINE69.000] TO BUS 324850 [2DOZIER H 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 0 | -0.00034559
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1693 324820-324850(1) | OPEN LINE FROM BUS 324820 [2ISLAND MINE69.000] TO BUS 324850 [2DOZIER H 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1694 324820-324981(1) | OPEN LINE FROM BUS 324820 [2ISLAND MINE69.000] TO BUS 324981 [2TEXAS GAS T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 0 | -0.00034559
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1694 324820-324981(1) | OPEN LINE FROM BUS 324820 [2ISLAND MINE69.000] TO BUS 324981 [2TEXAS GAS T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1695 324821-324914(1) | OPEN LINE FROM BUS 324821 [2CLARKSON 69.000] TO BUS 324914 [2M-V CLARK T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -1.7881e-06 | -0.00034738
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1695 324821-324914(1) | OPEN LINE FROM BUS 324821 [2CLARKSON 69.000] TO BUS 324914 [2M-V CLARK T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1696 324821-324992(1) | OPEN LINE FROM BUS 324821 [2CLARKSON 69.000] TO BUS 324992 [2WARREN TIE 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8354 | -1.0431e-05 | -0.00035602
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1696 324821-324992(1) | OPEN LINE FROM BUS 324821 [2CLARKSON 69.000] TO BUS 324992 [2WARREN TIE 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1697 324822-324996(1) | OPEN LINE FROM BUS 324822 [2CLAY KU 69.000] TO BUS 324996 [2DOTIKI TAP 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 5.9605e-08 | -0.00034553
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1697 324822-324996(1) | OPEN LINE FROM BUS 324822 [2CLAY KU 69.000] TO BUS 324996 [2DOTIKI TAP 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1698 324823-324825(1) | OPEN LINE FROM BUS 324823 [2CLINTON 58169.000] TO BUS 324825 [2CLINTON KU 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 0 | -0.00034559
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1698 324823-324825(1) | OPEN LINE FROM BUS 324823 [2CLINTON 58169.000] TO BUS 324825 [2CLINTON KU 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1699 324824-325005(1) | OPEN LINE FROM BUS 324824 [2CLINCH VALL69.000] TO BUS 325005 [2WISE TAP 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -7.1526e-07 | -0.0003463
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1699 324824-325005(1) | OPEN LINE FROM BUS 324824 [2CLINCH VALL69.000] TO BUS 325005 [2WISE TAP 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1700 324826-324999(1) | OPEN LINE FROM BUS 324826 [2CLINCH V SW69.000] TO BUS 324999 [2WHTE OAK KU69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 9.5367e-07 | -0.00034463
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1700 324826-324999(1) | OPEN LINE FROM BUS 324826 [2CLINCH V SW69.000] TO BUS 324999 [2WHTE OAK KU69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1701 324832-324833(1) | OPEN LINE FROM BUS 324832 [2CORBIN 1 69.000] TO BUS 324833 [2CORBIN 2 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93977 | 64.8441 | 0.00011569 | -0.0002299
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1701 324832-324833(1) | OPEN LINE FROM BUS 324832 [2CORBIN 1 69.000] TO BUS 324833 [2CORBIN 2 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1702 324836-324853(1) | OPEN LINE FROM BUS 324836 [2BENS BRANCH69.000] TO BUS 324853 [2E STONE GAP69.000] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8373 | 1.6928e-05 | -0.00032866
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1702 324836-324853(1) | OPEN LINE FROM BUS 324836 [2BENS BRANCH69.000] TO BUS 324853 [2E STONE GAP69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1703 324836-324894(1) | OPEN LINE FROM BUS 324836 [2BENS BRANCH69.000] TO BUS 324894 [2E STONE G T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8373 | 1.6987e-05 | -0.0003286
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1703 324836-324894(1) | OPEN LINE FROM BUS 324836 [2BENS BRANCH69.000] TO BUS 324894 [2E STONE G T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1704 324838-324957(1) | OPEN LINE FROM BUS 324838 [2DANV IND TP69.000] TO BUS 324957 [2SHELBY CI T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93963 | 64.8342 | -2.8968e-05 | -0.00037456
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1704 324838-324957(1) | OPEN LINE FROM BUS 324838 [2DANV IND TP69.000] TO BUS 324957 [2SHELBY CI T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1705 324839-324909(1) | OPEN LINE FROM BUS 324839 [2DANVILE IND69.000] TO BUS 324909 [2MINR FARM T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8372 | 1.502e-05 | -0.00033057
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1705 324839-324909(1) | OPEN LINE FROM BUS 324839 [2DANVILE IND69.000] TO BUS 324909 [2MINR FARM T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1706 324841-324909(1) | OPEN LINE FROM BUS 324841 [2DANVILLE W 69.000] TO BUS 324909 [2MINR FARM T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 3.9339e-06 | -0.00034165
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1706 324841-324909(1) | OPEN LINE FROM BUS 324841 [2DANVILLE W 69.000] TO BUS 324909 [2MINR FARM T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1707 324842-324967(1) | OPEN LINE FROM BUS 324842 [2DAVIS TAP 69.000] TO BUS 324967 [2SPEAR STA A69.000] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8372 | 1.4603e-05 | -0.00033098
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1707 324842-324967(1) | OPEN LINE FROM BUS 324842 [2DAVIS TAP 69.000] TO BUS 324967 [2SPEAR STA A69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1708 324842-324987(1) | OPEN LINE FROM BUS 324842 [2DAVIS TAP 69.000] TO BUS 324987 [2W HICKMAN 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8372 | 1.4842e-05 | -0.00033075
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1708 324842-324987(1) | OPEN LINE FROM BUS 324842 [2DAVIS TAP 69.000] TO BUS 324987 [2W HICKMAN 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1709 324844-324943(1) | OPEN LINE FROM BUS 324844 [2DELAPLAIN 69.000] TO BUS 324943 [2ROGERS GAP 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93987 | 64.8508 | 0.00021219 | -0.0001334
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1709 324844-324943(1) | OPEN LINE FROM BUS 324844 [2DELAPLAIN 69.000] TO BUS 324943 [2ROGERS GAP 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1710 324845-324962(1) | OPEN LINE FROM BUS 324845 [2DENHAM ST 69.000] TO BUS 324962 [2SOMERSET 1 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93968 | 64.8381 | 2.8908e-05 | -0.00031668
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1710 324845-324962(1) | OPEN LINE FROM BUS 324845 [2DENHAM ST 69.000] TO BUS 324962 [2SOMERSET 1 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1711 324845-324963(1) | OPEN LINE FROM BUS 324845 [2DENHAM ST 69.000] TO BUS 324963 [2SOMERSET 2 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8367 | 8.2254e-06 | -0.00033736
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1711 324845-324963(1) | OPEN LINE FROM BUS 324845 [2DENHAM ST 69.000] TO BUS 324963 [2SOMERSET 2 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1712 324846-324932(1) | OPEN LINE FROM BUS 324846 [2DIAMOND 69.000] TO BUS 324932 [2PROVIDENCE 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 5.9605e-08 | -0.00034553
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1712 324846-324932(1) | OPEN LINE FROM BUS 324846 [2DIAMOND 69.000] TO BUS 324932 [2PROVIDENCE 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1713 324846-324996(1) | OPEN LINE FROM BUS 324846 [2DIAMOND 69.000] TO BUS 324996 [2DOTIKI TAP 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 5.9605e-08 | -0.00034553
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1713 324846-324996(1) | OPEN LINE FROM BUS 324846 [2DIAMOND 69.000] TO BUS 324996 [2DOTIKI TAP 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1714 324847-324973(1) | OPEN LINE FROM BUS 324847 [2DODGE HILL 69.000] TO BUS 324973 [2STURGIS 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 1.1921e-07 | -0.00034547
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1714 324847-324973(1) | OPEN LINE FROM BUS 324847 [2DODGE HILL 69.000] TO BUS 324973 [2STURGIS 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1715 324847-326546(1) | OPEN LINE FROM BUS 324847 [2DODGE HILL 69.000] TO BUS 326546 [2SUNOCO TAP 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 1.1921e-07 | -0.00034547
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1715 324847-326546(1) | OPEN LINE FROM BUS 324847 [2DODGE HILL 69.000] TO BUS 326546 [2SUNOCO TAP 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1716 324848-324877(1) | OPEN LINE FROM BUS 324848 [2DONERAIL 69.000] TO BUS 324877 [2HOOVER KU 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93958 | 64.8309 | -7.5936e-05 | -0.00042152
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1716 324848-324877(1) | OPEN LINE FROM BUS 324848 [2DONERAIL 69.000] TO BUS 324877 [2HOOVER KU 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1717 324849-324867(1) | OPEN LINE FROM BUS 324849 [2DOW CORNING69.000] TO BUS 324867 [2GHENT 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93995 | 64.8564 | 0.00029272 | -5.2869e-05
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1717 324849-324867(1) | OPEN LINE FROM BUS 324849 [2DOW CORNING69.000] TO BUS 324867 [2GHENT 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1718 324851-324999(1) | OPEN LINE FROM BUS 324851 [2DWINA TAP 69.000] TO BUS 324999 [2WHTE OAK KU69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 2.3842e-07 | -0.00034535
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1718 324851-324999(1) | OPEN LINE FROM BUS 324851 [2DWINA TAP 69.000] TO BUS 324999 [2WHTE OAK KU69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1719 324852-324885(1) | OPEN LINE FROM BUS 324852 [2DYCUSBURG 69.000] TO BUS 324885 [2KUTTAWA 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 2.9802e-07 | -0.00034529
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1719 324852-324885(1) | OPEN LINE FROM BUS 324852 [2DYCUSBURG 69.000] TO BUS 324885 [2KUTTAWA 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1720 324852-324949(1) | OPEN LINE FROM BUS 324852 [2DYCUSBURG 69.000] TO BUS 324949 [2SALEM 673 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 3.5763e-07 | -0.00034523
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1720 324852-324949(1) | OPEN LINE FROM BUS 324852 [2DYCUSBURG 69.000] TO BUS 324949 [2SALEM 673 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1721 324855-326541(1) | OPEN LINE FROM BUS 324855 [2EKPC OFF TP69.000] TO BUS 326541 [2EKPC OFFICE69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8369 | 1.0252e-05 | -0.00033534
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1721 324855-326541(1) | OPEN LINE FROM BUS 324855 [2EKPC OFF TP69.000] TO BUS 326541 [2EKPC OFFICE69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1722 324856-324880(1) | OPEN LINE FROM BUS 324856 [2ESTIL ST CO69.000] TO BUS 324880 [2IRVINE 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8366 | 5.9009e-06 | -0.00033969
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1722 324856-324880(1) | OPEN LINE FROM BUS 324856 [2ESTIL ST CO69.000] TO BUS 324880 [2IRVINE 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1723 324856-324907(1) | OPEN LINE FROM BUS 324856 [2ESTIL ST CO69.000] TO BUS 324907 [2MILLER CRK 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8366 | 6.0797e-06 | -0.00033951
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1723 324856-324907(1) | OPEN LINE FROM BUS 324856 [2ESTIL ST CO69.000] TO BUS 324907 [2MILLER CRK 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1724 324857-324858(1) | OPEN LINE FROM BUS 324857 [2ETOWN 2 69.000] TO BUS 324858 [2ETOWN 5 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8372 | 1.5199e-05 | -0.00033039
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1724 324857-324858(1) | OPEN LINE FROM BUS 324857 [2ETOWN 2 69.000] TO BUS 324858 [2ETOWN 5 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1725 324862-325086(1) | OPEN LINE FROM BUS 324862 [2FIES CITY 69.000] TO BUS 325086 [2KEN AMERI 269.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -2.3842e-07 | -0.00034583
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1725 324862-325086(1) | OPEN LINE FROM BUS 324862 [2FIES CITY 69.000] TO BUS 325086 [2KEN AMERI 269.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1726 324863-324920(1) | OPEN LINE FROM BUS 324863 [2FLA TILE T169.000] TO BUS 324920 [2NINEVAH TAP69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8366 | 7.1526e-06 | -0.00033844
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1726 324863-324920(1) | OPEN LINE FROM BUS 324863 [2FLA TILE T169.000] TO BUS 324920 [2NINEVAH TAP69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1727 324865-324904(1) | OPEN LINE FROM BUS 324865 [2FREDONIA 69.000] TO BUS 324904 [2MEXICO KU 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 7.1526e-07 | -0.00034487
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1727 324865-324904(1) | OPEN LINE FROM BUS 324865 [2FREDONIA 69.000] TO BUS 324904 [2MEXICO KU 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1728 324867-324911(1) | OPEN LINE FROM BUS 324867 [2GHENT 69.000] TO BUS 324911 [2MARKLAND DM69.000] CKT 1 | 0.93965 | 64.8362 | 0.93995 | 64.8568 | 0.00029987 | -4.5717e-05
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1728 324867-324911(1) | OPEN LINE FROM BUS 324867 [2GHENT 69.000] TO BUS 324911 [2MARKLAND DM69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1729 324871-324894(1) | OPEN LINE FROM BUS 324871 [2HAMER 69.000] TO BUS 324894 [2E STONE G T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -9.5367e-07 | -0.00034654
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1729 324871-324894(1) | OPEN LINE FROM BUS 324871 [2HAMER 69.000] TO BUS 324894 [2E STONE G T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1730 324873-324896(1) | OPEN LINE FROM BUS 324873 [2HANSON JCT 69.000] TO BUS 324896 [2MADSNV E 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8368 | 9.5367e-06 | -0.00033605
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1730 324873-324896(1) | OPEN LINE FROM BUS 324873 [2HANSON JCT 69.000] TO BUS 324896 [2MADSNV E 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1731 324875-324942(1) | OPEN LINE FROM BUS 324875 [2HIGHSPLINT 69.000] TO BUS 324942 [2ROBBINS 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -2.2054e-06 | -0.00034779
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1731 324875-324942(1) | OPEN LINE FROM BUS 324875 [2HIGHSPLINT 69.000] TO BUS 324942 [2ROBBINS 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1732 324877-324890(1) | OPEN LINE FROM BUS 324877 [2HOOVER KU 69.000] TO BUS 324890 [2LEMONS MILL69.000] CKT 1 | 0.93965 | 64.8362 | 0.93958 | 64.8307 | -7.8619e-05 | -0.00042421
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1732 324877-324890(1) | OPEN LINE FROM BUS 324877 [2HOOVER KU 69.000] TO BUS 324890 [2LEMONS MILL69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1733 324878-324908(1) | OPEN LINE FROM BUS 324878 [2HUNT BTM TP69.000] TO BUS 324908 [2MILTON 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93961 | 64.8329 | -4.7565e-05 | -0.00039315
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1733 324878-324908(1) | OPEN LINE FROM BUS 324878 [2HUNT BTM TP69.000] TO BUS 324908 [2MILTON 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1734 324881-324942(1) | OPEN LINE FROM BUS 324881 [2JACKS CREEK69.000] TO BUS 324942 [2ROBBINS 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.4305e-06 | -0.00034702
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1734 324881-324942(1) | OPEN LINE FROM BUS 324881 [2JACKS CREEK69.000] TO BUS 324942 [2ROBBINS 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1735 324881-324978(1) | OPEN LINE FROM BUS 324881 [2JACKS CREEK69.000] TO BUS 324978 [2TOTZ 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.3113e-06 | -0.0003469
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1735 324881-324978(1) | OPEN LINE FROM BUS 324881 [2JACKS CREEK69.000] TO BUS 324978 [2TOTZ 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1736 324884-324979(1) | OPEN LINE FROM BUS 324884 [2KUNKEL 69.000] TO BUS 324979 [2TRAFTON AVE69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 1.3709e-06 | -0.00034422
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1736 324884-324979(1) | OPEN LINE FROM BUS 324884 [2KUNKEL 69.000] TO BUS 324979 [2TRAFTON AVE69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1737 324886-324967(1) | OPEN LINE FROM BUS 324886 [2KY RIVER 69.000] TO BUS 324967 [2SPEAR STA A69.000] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8372 | 1.4901e-05 | -0.00033069
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1737 324886-324967(1) | OPEN LINE FROM BUS 324886 [2KY RIVER 69.000] TO BUS 324967 [2SPEAR STA A69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1738 324886-324968(1) | OPEN LINE FROM BUS 324886 [2KY RIVER 69.000] TO BUS 324968 [2SPEAR STA B69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8368 | 1.0073e-05 | -0.00033551
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1738 324886-324968(1) | OPEN LINE FROM BUS 324886 [2KY RIVER 69.000] TO BUS 324968 [2SPEAR STA B69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1739 324892-324945(1) | OPEN LINE FROM BUS 324892 [2LIGGETT 69.000] TO BUS 324945 [2ROSE HILL T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -4.7684e-07 | -0.00034606
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1739 324892-324945(1) | OPEN LINE FROM BUS 324892 [2LIGGETT 69.000] TO BUS 324945 [2ROSE HILL T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1740 324892-325007(1) | OPEN LINE FROM BUS 324892 [2LIGGETT 69.000] TO BUS 325007 [2YANCY TAP 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -6.5565e-07 | -0.00034624
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1740 324892-325007(1) | OPEN LINE FROM BUS 324892 [2LIGGETT 69.000] TO BUS 325007 [2YANCY TAP 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1741 324893-324897(1) | OPEN LINE FROM BUS 324893 [2MADSNV GE T69.000] TO BUS 324897 [2MADSNV N 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.837 | 1.21e-05 | -0.00033349
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1741 324893-324897(1) | OPEN LINE FROM BUS 324893 [2MADSNV GE T69.000] TO BUS 324897 [2MADSNV N 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1742 324893-326587(1) | OPEN LINE FROM BUS 324893 [2MADSNV GE T69.000] TO BUS 326587 [2MADSNV W TP69.000] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.837 | 1.2219e-05 | -0.00033337
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1742 324893-326587(1) | OPEN LINE FROM BUS 324893 [2MADSNV GE T69.000] TO BUS 326587 [2MADSNV W TP69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1743 324895-324897(1) | OPEN LINE FROM BUS 324895 [2MADSNV HO 69.000] TO BUS 324897 [2MADSNV N 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 4.1723e-06 | -0.00034142
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1743 324895-324897(1) | OPEN LINE FROM BUS 324895 [2MADSNV HO 69.000] TO BUS 324897 [2MADSNV N 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1744 324896-324902(1) | OPEN LINE FROM BUS 324896 [2MADSNV E 69.000] TO BUS 324902 [2MCCOY AVE 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8371 | 1.3947e-05 | -0.00033164
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1744 324896-324902(1) | OPEN LINE FROM BUS 324896 [2MADSNV E 69.000] TO BUS 324902 [2MCCOY AVE 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1745 324898-324954(1) | OPEN LINE FROM BUS 324898 [2MANITOU 69.000] TO BUS 324954 [2SENTRY TAP 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | -5.9605e-08 | -0.00034565
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1745 324898-324954(1) | OPEN LINE FROM BUS 324898 [2MANITOU 69.000] TO BUS 324954 [2SENTRY TAP 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1746 324898-324993(1) | OPEN LINE FROM BUS 324898 [2MANITOU 69.000] TO BUS 324993 [2WARRIOR CL 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.1921e-07 | -0.00034571
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1746 324898-324993(1) | OPEN LINE FROM BUS 324898 [2MANITOU 69.000] TO BUS 324993 [2WARRIOR CL 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1747 324899-324900(1) | OPEN LINE FROM BUS 324899 [2MAYSVILLE E69.000] TO BUS 324900 [2MAYSVILLE M69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1748 324903-324964(1) | OPEN LINE FROM BUS 324903 [2MCKEE ROAD 69.000] TO BUS 324964 [2SOMERSET 3 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93969 | 64.8386 | 3.4988e-05 | -0.0003106
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1748 324903-324964(1) | OPEN LINE FROM BUS 324903 [2MCKEE ROAD 69.000] TO BUS 324964 [2SOMERSET 3 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1749 324903-324965(1) | OPEN LINE FROM BUS 324903 [2MCKEE ROAD 69.000] TO BUS 324965 [2SOMERSET NO69.000] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8369 | 1.0848e-05 | -0.00033474
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1749 324903-324965(1) | OPEN LINE FROM BUS 324903 [2MCKEE ROAD 69.000] TO BUS 324965 [2SOMERSET NO69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1750 324909-325032(1) | OPEN LINE FROM BUS 324909 [2MINR FARM T69.000] TO BUS 325032 [2MINOR FARM 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 4.2319e-06 | -0.00034136
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1750 324909-325032(1) | OPEN LINE FROM BUS 324909 [2MINR FARM T69.000] TO BUS 325032 [2MINOR FARM 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1751 324911-324994(1) | OPEN LINE FROM BUS 324911 [2MARKLAND DM69.000] TO BUS 324994 [2WARSAW KU 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93996 | 64.8569 | 0.00030118 | -4.4405e-05
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1751 324911-324994(1) | OPEN LINE FROM BUS 324911 [2MARKLAND DM69.000] TO BUS 324994 [2WARSAW KU 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1752 324915-325006(1) | OPEN LINE FROM BUS 324915 [2MT WAS EK J69.000] TO BUS 325006 [2W MT WSH EK69.000] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8351 | -1.4603e-05 | -0.00036019
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1752 324915-325006(1) | OPEN LINE FROM BUS 324915 [2MT WAS EK J69.000] TO BUS 325006 [2W MT WSH EK69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1753 324916-324924(1) | OPEN LINE FROM BUS 324916 [2NEWTOWN TAP69.000] TO BUS 324924 [2OXFORD 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93942 | 64.82 | -0.00023425 | -0.00057983
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1753 324916-324924(1) | OPEN LINE FROM BUS 324916 [2NEWTOWN TAP69.000] TO BUS 324924 [2OXFORD 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1754 324916-325027(1) | OPEN LINE FROM BUS 324916 [2NEWTOWN TAP69.000] TO BUS 325027 [2NEWTOWN 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93938 | 64.8175 | -0.00027061 | -0.00061619
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1754 324916-325027(1) | OPEN LINE FROM BUS 324916 [2NEWTOWN TAP69.000] TO BUS 325027 [2NEWTOWN 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1755 324917-324918(1) | OPEN LINE FROM BUS 324917 [2NICHLSV 3 69.000] TO BUS 324918 [2NICHLSV 4&569.000] CKT 1 | 0.93965 | 64.8362 | 0.9397 | 64.8396 | 4.9949e-05 | -0.00029564
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1755 324917-324918(1) | OPEN LINE FROM BUS 324917 [2NICHLSV 3 69.000] TO BUS 324918 [2NICHLSV 4&569.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1756 324917-324980(1) | OPEN LINE FROM BUS 324917 [2NICHLSV 3 69.000] TO BUS 324980 [2RJ CORMAN 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 5.9605e-08 | -0.00034553
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1756 324917-324980(1) | OPEN LINE FROM BUS 324917 [2NICHLSV 3 69.000] TO BUS 324980 [2RJ CORMAN 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1757 324918-324919(1) | OPEN LINE FROM BUS 324918 [2NICHLSV 4&569.000] TO BUS 324919 [2NICHLSV 6&869.000] CKT 1 | 0.93965 | 64.8362 | 0.93983 | 64.8481 | 0.00017327 | -0.00017232
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1757 324918-324919(1) | OPEN LINE FROM BUS 324918 [2NICHLSV 4&569.000] TO BUS 324919 [2NICHLSV 6&869.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1758 324919-324989(1) | OPEN LINE FROM BUS 324919 [2NICHLSV 6&869.000] TO BUS 324989 [2W NICHSV T 69.000] CKT 1 | 0.93965 | 64.8362 | 0.9399 | 64.8529 | 0.00024217 | -0.00010341
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1758 324919-324989(1) | OPEN LINE FROM BUS 324919 [2NICHLSV 6&869.000] TO BUS 324989 [2W NICHSV T 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1759 324920-326529(1) | OPEN LINE FROM BUS 324920 [2NINEVAH TAP69.000] TO BUS 326529 [2NINEVAH 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93968 | 64.838 | 2.6166e-05 | -0.00031942
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1759 324920-326529(1) | OPEN LINE FROM BUS 324920 [2NINEVAH TAP69.000] TO BUS 326529 [2NINEVAH 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1760 324922-326563(1) | OPEN LINE FROM BUS 324922 [2ONTON 69.000] TO BUS 326563 [2ADVENT MINE69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 5.9605e-07 | -0.00034499
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1760 324922-326563(1) | OPEN LINE FROM BUS 324922 [2ONTON 69.000] TO BUS 326563 [2ADVENT MINE69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1761 324925-325006(1) | OPEN LINE FROM BUS 324925 [2PLEAS GRV T69.000] TO BUS 325006 [2W MT WSH EK69.000] CKT 1 | 0.93965 | 64.8362 | 0.93963 | 64.8345 | -2.3663e-05 | -0.00036925
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1761 324925-325006(1) | OPEN LINE FROM BUS 324925 [2PLEAS GRV T69.000] TO BUS 325006 [2W MT WSH EK69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1762 324928-324953(1) | OPEN LINE FROM BUS 324928 [2POOLE 69.000] TO BUS 324953 [2SEBREE 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 1.7881e-06 | -0.0003438
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1762 324928-324953(1) | OPEN LINE FROM BUS 324928 [2POOLE 69.000] TO BUS 324953 [2SEBREE 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1763 324930-324972(1) | OPEN LINE FROM BUS 324930 [2PARKER MILL69.000] TO BUS 324972 [2STONEWALL 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8366 | 6.1989e-06 | -0.00033939
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1763 324930-324972(1) | OPEN LINE FROM BUS 324930 [2PARKER MILL69.000] TO BUS 324972 [2STONEWALL 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1764 324934-324984(1) | OPEN LINE FROM BUS 324934 [2RACE STREET69.000] TO BUS 324984 [2VINE STREET69.000] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8349 | -1.7703e-05 | -0.00036329
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1764 324934-324984(1) | OPEN LINE FROM BUS 324934 [2RACE STREET69.000] TO BUS 324984 [2VINE STREET69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1765 324935-324944(1) | OPEN LINE FROM BUS 324935 [2RADCLF KU T69.000] TO BUS 324944 [2ROGERSV 60569.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8365 | 4.8876e-06 | -0.0003407
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1765 324935-324944(1) | OPEN LINE FROM BUS 324935 [2RADCLF KU T69.000] TO BUS 324944 [2ROGERSV 60569.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1766 324935-324982(1) | OPEN LINE FROM BUS 324935 [2RADCLF KU T69.000] TO BUS 324982 [2VINE GRV KU69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 1.1325e-06 | -0.00034446
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1766 324935-324982(1) | OPEN LINE FROM BUS 324935 [2RADCLF KU T69.000] TO BUS 324982 [2VINE GRV KU69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1767 324936-324940(1) | OPEN LINE FROM BUS 324936 [2RICHMND IND69.000] TO BUS 324940 [2RICHMND J 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -7.1526e-07 | -0.0003463
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1767 324936-324940(1) | OPEN LINE FROM BUS 324936 [2RICHMND IND69.000] TO BUS 324940 [2RICHMND J 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1768 324937-324939(1) | OPEN LINE FROM BUS 324937 [2RICHMND 2 69.000] TO BUS 324939 [2RICHMND 4 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93972 | 64.8405 | 6.3002e-05 | -0.00028259
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1768 324937-324939(1) | OPEN LINE FROM BUS 324937 [2RICHMND 2 69.000] TO BUS 324939 [2RICHMND 4 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1769 324938-324940(1) | OPEN LINE FROM BUS 324938 [2RICHMND 3 69.000] TO BUS 324940 [2RICHMND J 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -2.3842e-07 | -0.00034583
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1769 324938-324940(1) | OPEN LINE FROM BUS 324938 [2RICHMND 3 69.000] TO BUS 324940 [2RICHMND J 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1770 324941-324975(1) | OPEN LINE FROM BUS 324941 [2RIVERPORT 69.000] TO BUS 324975 [2TERRY 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -9.5367e-07 | -0.00034654
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1770 324941-324975(1) | OPEN LINE FROM BUS 324941 [2RIVERPORT 69.000] TO BUS 324975 [2TERRY 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
324975 | 2TERRY | 69 | LGEE' | RANGE | 0.94 | 1.06 | SINGLE OPN LIN 1770 324941-324975(1) | OPEN LINE FROM BUS 324941 [2RIVERPORT 69.000] TO BUS 324975 [2TERRY 69.000] CKT 1 | 0.98781 | 68.1591 | 0.93729 | 64.6733 | -0.050519 | -0.0027059
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1771 324948-324949(1) | OPEN LINE FROM BUS 324948 [2SALEM KU 69.000] TO BUS 324949 [2SALEM 673 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 4.7684e-07 | -0.00034511
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1771 324948-324949(1) | OPEN LINE FROM BUS 324948 [2SALEM KU 69.000] TO BUS 324949 [2SALEM 673 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1772 324950-325084(1) | OPEN LINE FROM BUS 324950 [2SCIENC HILL69.000] TO BUS 325084 [2FLOYD EKP T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8366 | 5.8413e-06 | -0.00033975
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1772 324950-325084(1) | OPEN LINE FROM BUS 324950 [2SCIENC HILL69.000] TO BUS 325084 [2FLOYD EKP T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1773 324951-326989(1) | OPEN LINE FROM BUS 324951 [2SCOTT CO 69.000] TO BUS 326989 [2LONG LICK 69.000] CKT 1 | 0.93965 | 64.8362 | 0.9395 | 64.8256 | -0.00015301 | -0.00049859
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1773 324951-326989(1) | OPEN LINE FROM BUS 324951 [2SCOTT CO 69.000] TO BUS 326989 [2LONG LICK 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1774 324953-326563(1) | OPEN LINE FROM BUS 324953 [2SEBREE 69.000] TO BUS 326563 [2ADVENT MINE69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 5.9605e-07 | -0.00034499
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1774 324953-326563(1) | OPEN LINE FROM BUS 324953 [2SEBREE 69.000] TO BUS 326563 [2ADVENT MINE69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1775 324954-325762(1) | OPEN LINE FROM BUS 324954 [2SENTRY TAP 69.000] TO BUS 325762 [2WARRIOR TAP69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 2.7418e-06 | -0.00034285
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1775 324954-325762(1) | OPEN LINE FROM BUS 324954 [2SENTRY TAP 69.000] TO BUS 325762 [2WARRIOR TAP69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1776 324957-324970(1) | OPEN LINE FROM BUS 324957 [2SHELBY CI T69.000] TO BUS 324970 [2STANFORD KU69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8359 | -3.2783e-06 | -0.00034887
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1776 324957-324970(1) | OPEN LINE FROM BUS 324957 [2SHELBY CI T69.000] TO BUS 324970 [2STANFORD KU69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1777 324958-325043(1) | OPEN LINE FROM BUS 324958 [2SHEPHRDSV T69.000] TO BUS 325043 [2SHEPHERDSV 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 1.7285e-06 | -0.00034386
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1777 324958-325043(1) | OPEN LINE FROM BUS 324958 [2SHEPHRDSV T69.000] TO BUS 325043 [2SHEPHERDSV 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1778 324959-326564(1) | OPEN LINE FROM BUS 324959 [2SIMMONS 69.000] TO BUS 326564 [2LEW BREC 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 1.7881e-07 | -0.00034541
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1778 324959-326564(1) | OPEN LINE FROM BUS 324959 [2SIMMONS 69.000] TO BUS 326564 [2LEW BREC 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1779 324961-324963(1) | OPEN LINE FROM BUS 324961 [2SOMERSET GE69.000] TO BUS 324963 [2SOMERSET 2 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 1.7881e-07 | -0.00034541
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1779 324961-324963(1) | OPEN LINE FROM BUS 324961 [2SOMERSET GE69.000] TO BUS 324963 [2SOMERSET 2 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1780 324966-324994(1) | OPEN LINE FROM BUS 324966 [2SPARTA KU 69.000] TO BUS 324994 [2WARSAW KU 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93936 | 64.8156 | -0.00029814 | -0.00064373
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1780 324966-324994(1) | OPEN LINE FROM BUS 324966 [2SPARTA KU 69.000] TO BUS 324994 [2WARSAW KU 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1781 324969-324990(1) | OPEN LINE FROM BUS 324969 [2SMRST 615KU69.000] TO BUS 324990 [2WAITSBORO 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 3.9339e-06 | -0.00034165
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1781 324969-324990(1) | OPEN LINE FROM BUS 324969 [2SMRST 615KU69.000] TO BUS 324990 [2WAITSBORO 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1782 324970-324971(1) | OPEN LINE FROM BUS 324970 [2STANFORD KU69.000] TO BUS 324971 [2STANFORD NO69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8367 | 7.4506e-06 | -0.00033814
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1782 324970-324971(1) | OPEN LINE FROM BUS 324970 [2STANFORD KU69.000] TO BUS 324971 [2STANFORD NO69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1783 324975-324997(1) | OPEN LINE FROM BUS 324975 [2TERRY 69.000] TO BUS 324997 [2WEST CO 1 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -8.9407e-07 | -0.00034648
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1783 324975-324997(1) | OPEN LINE FROM BUS 324975 [2TERRY 69.000] TO BUS 324997 [2WEST CO 1 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1784 324979-324986(1) | OPEN LINE FROM BUS 324979 [2TRAFTON AVE69.000] TO BUS 324986 [2W HIGH T2 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93973 | 64.8412 | 7.3552e-05 | -0.00027204
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1784 324979-324986(1) | OPEN LINE FROM BUS 324979 [2TRAFTON AVE69.000] TO BUS 324986 [2W HIGH T2 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1785 324981-325062(1) | OPEN LINE FROM BUS 324981 [2TEXAS GAS T69.000] TO BUS 325062 [2TEXAS GAS 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 9.5367e-07 | -0.00034463
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1785 324981-325062(1) | OPEN LINE FROM BUS 324981 [2TEXAS GAS T69.000] TO BUS 325062 [2TEXAS GAS 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1786 324984-324988(1) | OPEN LINE FROM BUS 324984 [2VINE STREET69.000] TO BUS 324988 [2WEST HIGH 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93963 | 64.8342 | -2.7955e-05 | -0.00037354
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1786 324984-324988(1) | OPEN LINE FROM BUS 324984 [2VINE STREET69.000] TO BUS 324988 [2WEST HIGH 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1787 324994-325025(1) | OPEN LINE FROM BUS 324994 [2WARSAW KU 69.000] TO BUS 325025 [2WARSAW EAST69.000] CKT 1 | 0.93965 | 64.8362 | 0.93928 | 64.8102 | -0.00037557 | -0.00072116
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1787 324994-325025(1) | OPEN LINE FROM BUS 324994 [2WARSAW KU 69.000] TO BUS 325025 [2WARSAW EAST69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1788 324995-325084(1) | OPEN LINE FROM BUS 324995 [2WAYNESBURG 69.000] TO BUS 325084 [2FLOYD EKP T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8366 | 6.2585e-06 | -0.00033933
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1788 324995-325084(1) | OPEN LINE FROM BUS 324995 [2WAYNESBURG 69.000] TO BUS 325084 [2FLOYD EKP T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1789 324996-325010(1) | OPEN LINE FROM BUS 324996 [2DOTIKI TAP 69.000] TO BUS 325010 [2WEBCOAL 2 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.1921e-07 | -0.00034571
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1789 324996-325010(1) | OPEN LINE FROM BUS 324996 [2DOTIKI TAP 69.000] TO BUS 325010 [2WEBCOAL 2 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1790 324997-324998(1) | OPEN LINE FROM BUS 324997 [2WEST CO 1 69.000] TO BUS 324998 [2WEST CO 2 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -9.5367e-07 | -0.00034654
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1790 324997-324998(1) | OPEN LINE FROM BUS 324997 [2WEST CO 1 69.000] TO BUS 324998 [2WEST CO 2 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1791 325002-325003(Z1) | OPEN LINE FROM BUS 325002 [2WILS DOWN 169.000] TO BUS 325003 [2WILS DOWN 269.000] CKT Z1 | 0.93965 | 64.8362 | 0.93967 | 64.8371 | 1.2994e-05 | -0.00033259
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1791 325002-325003(Z1) | OPEN LINE FROM BUS 325002 [2WILS DOWN 169.000] TO BUS 325003 [2WILS DOWN 269.000] CKT Z1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1792 325008-325026(1) | OPEN LINE FROM BUS 325008 [2BLEDSOE 69.000] TO BUS 325026 [2PINE MOUNTN69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 2.4438e-06 | -0.00034314
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1792 325008-325026(1) | OPEN LINE FROM BUS 325008 [2BLEDSOE 69.000] TO BUS 325026 [2PINE MOUNTN69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1793 325010-325011(1) | OPEN LINE FROM BUS 325010 [2WEBCOAL 2 69.000] TO BUS 325011 [2DOTIKI 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 0 | -0.00034559
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1793 325010-325011(1) | OPEN LINE FROM BUS 325010 [2WEBCOAL 2 69.000] TO BUS 325011 [2DOTIKI 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1794 325017-325018(1) | OPEN LINE FROM BUS 325017 [2CMWA 69.000] TO BUS 325018 [2CLA 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1795 325018-325061(1) | OPEN LINE FROM BUS 325018 [2CLA 69.000] TO BUS 325061 [2CMC 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1796 325023-325024(1) | OPEN LINE FROM BUS 325023 [2ASHBOT EAST69.000] TO BUS 325024 [2ASHBOT SPRK69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | -5.9605e-08 | -0.00034565
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1796 325023-325024(1) | OPEN LINE FROM BUS 325023 [2ASHBOT EAST69.000] TO BUS 325024 [2ASHBOT SPRK69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1797 325028-325047(1) | OPEN LINE FROM BUS 325028 [5ASHWD SL TP161.00] TO BUS 325047 [5ASHWOOD 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93962 | 64.8338 | -3.3736e-05 | -0.00037932
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1797 325028-325047(1) | OPEN LINE FROM BUS 325028 [5ASHWD SL TP161.00] TO BUS 325047 [5ASHWOOD 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1798 325028-326589(1) | OPEN LINE FROM BUS 325028 [5ASHWD SL TP161.00] TO BUS 326589 [5N PRN LIV R161.00] CKT 1 | 0.93965 | 64.8362 | 0.93969 | 64.8384 | 3.2306e-05 | -0.00031328
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1798 325028-326589(1) | OPEN LINE FROM BUS 325028 [5ASHWD SL TP161.00] TO BUS 326589 [5N PRN LIV R161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1799 325035-325050(1) | OPEN LINE FROM BUS 325035 [2BLUE SOL TP69.000] TO BUS 325050 [2BLUE SOLAR 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8359 | -2.9802e-06 | -0.00034857
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1799 325035-325050(1) | OPEN LINE FROM BUS 325035 [2BLUE SOL TP69.000] TO BUS 325050 [2BLUE SOLAR 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1800 325035-325085(1) | OPEN LINE FROM BUS 325035 [2BLUE SOL TP69.000] TO BUS 325085 [2CYNTHI EK T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1801 325041-325068(1) | OPEN LINE FROM BUS 325041 [2STONE TVA 69.000] TO BUS 325068 [2HAMBLIN 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8374 | 1.7881e-05 | -0.00032771
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1801 325041-325068(1) | OPEN LINE FROM BUS 325041 [2STONE TVA 69.000] TO BUS 325068 [2HAMBLIN 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1802 325044-326565(1) | OPEN LINE FROM BUS 325044 [4INTRNTL 138.00] TO BUS 326565 [4INTRNTL TAP138.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8367 | 7.4506e-06 | -0.00033814
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1802 325044-326565(1) | OPEN LINE FROM BUS 325044 [4INTRNTL 138.00] TO BUS 326565 [4INTRNTL TAP138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1803 325045-325092(1) | OPEN LINE FROM BUS 325045 [2TURTLE CRK 69.000] TO BUS 325092 [2COAL GOOD 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8368 | 9.0003e-06 | -0.00033659
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1803 325045-325092(1) | OPEN LINE FROM BUS 325045 [2TURTLE CRK 69.000] TO BUS 325092 [2COAL GOOD 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1804 325055-325116(1) | OPEN LINE FROM BUS 325055 [4RHUDES TP 138.00] TO BUS 325116 [4RHUDES CR 138.00] CKT 1 | 0.93965 | 64.8362 | 0.9396 | 64.8321 | -5.883e-05 | -0.00040442
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1804 325055-325116(1) | OPEN LINE FROM BUS 325055 [4RHUDES TP 138.00] TO BUS 325116 [4RHUDES CR 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1805 325057-325088(1) | OPEN LINE FROM BUS 325057 [4KOSMOS CEME138.00] TO BUS 325088 [4MIL CK YARD138.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8366 | 6.7353e-06 | -0.00033885
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1805 325057-325088(1) | OPEN LINE FROM BUS 325057 [4KOSMOS CEME138.00] TO BUS 325088 [4MIL CK YARD138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1806 325059-325060(1) | OPEN LINE FROM BUS 325059 [2BRYANT RD T69.000] TO BUS 325060 [2BRYANT ROAD69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1807 325075-325077(Z1) | OPEN LINE FROM BUS 325075 [5KMPA COLEMN161.00] TO BUS 325077 [5COLEMAN TAP161.00] CKT Z1 | 0.93965 | 64.8362 | 0.9397 | 64.8394 | 4.6432e-05 | -0.00029916
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1807 325075-325077(Z1) | OPEN LINE FROM BUS 325075 [5KMPA COLEMN161.00] TO BUS 325077 [5COLEMAN TAP161.00] CKT Z1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1808 325077-325078(1) | OPEN LINE FROM BUS 325077 [5COLEMAN TAP161.00] TO BUS 325078 [5PADUCAH PRI161.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8366 | 7.1526e-06 | -0.00033844
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1808 325077-325078(1) | OPEN LINE FROM BUS 325077 [5COLEMAN TAP161.00] TO BUS 325078 [5PADUCAH PRI161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1809 325078-326562(1) | OPEN LINE FROM BUS 325078 [5PADUCAH PRI161.00] TO BUS 326562 [2PAD PRI 62469.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 5.9605e-08 | -0.00034553
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1809 325078-326562(1) | OPEN LINE FROM BUS 325078 [5PADUCAH PRI161.00] TO BUS 326562 [2PAD PRI 62469.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
326562 | 2PAD PRI 624 | 69 | LGEE' | RANGE | 0.94 | 1.06 | SINGLE OPN LIN 1809 325078-326562(1) | OPEN LINE FROM BUS 325078 [5PADUCAH PRI161.00] TO BUS 326562 [2PAD PRI 62469.000] CKT 1 | 1.0483 | 72.3348 | 1.0664 | 73.5834 | 0.018096 | 0.0064268
326596 | 2PAD PRI 614 | 69 | LGEE' | RANGE | 0.94 | 1.06 | SINGLE OPN LIN 1809 325078-326562(1) | OPEN LINE FROM BUS 325078 [5PADUCAH PRI161.00] TO BUS 326562 [2PAD PRI 62469.000] CKT 1 | 1.0484 | 72.337 | 1.0664 | 73.5842 | 0.018076 | 0.006438
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1810 325078-326596(1) | OPEN LINE FROM BUS 325078 [5PADUCAH PRI161.00] TO BUS 326596 [2PAD PRI 61469.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 5.9605e-08 | -0.00034553
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1810 325078-326596(1) | OPEN LINE FROM BUS 325078 [5PADUCAH PRI161.00] TO BUS 326596 [2PAD PRI 61469.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
326562 | 2PAD PRI 624 | 69 | LGEE' | RANGE | 0.94 | 1.06 | SINGLE OPN LIN 1810 325078-326596(1) | OPEN LINE FROM BUS 325078 [5PADUCAH PRI161.00] TO BUS 326596 [2PAD PRI 61469.000] CKT 1 | 1.0483 | 72.3348 | 1.0664 | 73.5842 | 0.018107 | 0.0064378
326596 | 2PAD PRI 614 | 69 | LGEE' | RANGE | 0.94 | 1.06 | SINGLE OPN LIN 1810 325078-326596(1) | OPEN LINE FROM BUS 325078 [5PADUCAH PRI161.00] TO BUS 326596 [2PAD PRI 61469.000] CKT 1 | 1.0484 | 72.337 | 1.0665 | 73.5879 | 0.018129 | 0.0064915
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1811 325079-326589(1) | OPEN LINE FROM BUS 325079 [5N PRINCETON161.00] TO BUS 326589 [5N PRN LIV R161.00] CKT 1 | 0.93965 | 64.8362 | 0.93969 | 64.8384 | 3.2306e-05 | -0.00031328
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1811 325079-326589(1) | OPEN LINE FROM BUS 325079 [5N PRINCETON161.00] TO BUS 326589 [5N PRN LIV R161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1812 325079-326591(1) | OPEN LINE FROM BUS 325079 [5N PRINCETON161.00] TO BUS 326591 [5W PRINCETON161.00] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8372 | 1.4901e-05 | -0.00033069
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1813 325083-326544(1) | OPEN LINE FROM BUS 325083 [2ALEX CK TAP69.000] TO BUS 326544 [2ALEX CREEK 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 2.3246e-06 | -0.00034326
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1813 325083-326544(1) | OPEN LINE FROM BUS 325083 [2ALEX CK TAP69.000] TO BUS 326544 [2ALEX CREEK 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1814 325096-326002(1) | OPEN LINE FROM BUS 325096 [4CANERN NGCC138.00] TO BUS 326002 [7CANERN NGCC345.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -4.1723e-07 | -0.000346
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1814 325096-326002(1) | OPEN LINE FROM BUS 325096 [4CANERN NGCC138.00] TO BUS 326002 [7CANERN NGCC345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1815 325096-326565(23) | OPEN LINE FROM BUS 325096 [4CANERN NGCC138.00] TO BUS 326565 [4INTRNTL TAP138.00] CKT 23 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.0729e-06 | -0.00034666
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1815 325096-326565(23) | OPEN LINE FROM BUS 325096 [4CANERN NGCC138.00] TO BUS 326565 [4INTRNTL TAP138.00] CKT 23 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1816 325096-326566(71) | OPEN LINE FROM BUS 325096 [4CANERN NGCC138.00] TO BUS 326566 [4CANE RUN 71138.00] CKT 71 | 0.93965 | 64.8362 | 0.93957 | 64.8307 | -7.9513e-05 | -0.0004251
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1816 325096-326566(71) | OPEN LINE FROM BUS 325096 [4CANERN NGCC138.00] TO BUS 326566 [4CANE RUN 71138.00] CKT 71 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1817 325096-326567(72) | OPEN LINE FROM BUS 325096 [4CANERN NGCC138.00] TO BUS 326567 [4CANE RUN 72138.00] CKT 72 | 0.93965 | 64.8362 | 0.93957 | 64.8306 | -7.987e-05 | -0.00042546
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1817 325096-326567(72) | OPEN LINE FROM BUS 325096 [4CANERN NGCC138.00] TO BUS 326567 [4CANE RUN 72138.00] CKT 72 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1818 325096-326568(7S) | OPEN LINE FROM BUS 325096 [4CANERN NGCC138.00] TO BUS 326568 [4CANE RUN 7S138.00] CKT 7S | 0.93965 | 64.8362 | 0.93957 | 64.8301 | -8.7082e-05 | -0.00043267
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1818 325096-326568(7S) | OPEN LINE FROM BUS 325096 [4CANERN NGCC138.00] TO BUS 326568 [4CANE RUN 7S138.00] CKT 7S | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1819 325096-326574(21) | OPEN LINE FROM BUS 325096 [4CANERN NGCC138.00] TO BUS 326574 [4CR11 TAP 138.00] CKT 21 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -7.7486e-07 | -0.00034636
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1819 325096-326574(21) | OPEN LINE FROM BUS 325096 [4CANERN NGCC138.00] TO BUS 326574 [4CR11 TAP 138.00] CKT 21 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1820 325761-325762(1) | OPEN LINE FROM BUS 325761 [2WARRIOR PRP69.000] TO BUS 325762 [2WARRIOR TAP69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 2.6226e-06 | -0.00034297
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1821 325762-325767(1) | OPEN LINE FROM BUS 325762 [2WARRIOR TAP69.000] TO BUS 325767 [2SENTRY 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | -5.9605e-08 | -0.00034565
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1821 325762-325767(1) | OPEN LINE FROM BUS 325762 [2WARRIOR TAP69.000] TO BUS 325767 [2SENTRY 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1822 325857-325956(Z1) | OPEN LINE FROM BUS 325857 [4BROWN N TIE138.00] TO BUS 325956 [4BROWN N 2 138.00] CKT Z1 | 0.93965 | 64.8362 | 0.93962 | 64.834 | -3.0816e-05 | -0.0003764
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1822 325857-325956(Z1) | OPEN LINE FROM BUS 325857 [4BROWN N TIE138.00] TO BUS 325956 [4BROWN N 2 138.00] CKT Z1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1823 325857-325957(Z1) | OPEN LINE FROM BUS 325857 [4BROWN N TIE138.00] TO BUS 325957 [4BROWN N 1 138.00] CKT Z1 | 0.93965 | 64.8362 | 0.93963 | 64.8347 | -2.1398e-05 | -0.00036699
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1823 325857-325957(Z1) | OPEN LINE FROM BUS 325857 [4BROWN N TIE138.00] TO BUS 325957 [4BROWN N 1 138.00] CKT Z1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1824 326001-326002(1) | OPEN LINE FROM BUS 326001 [7CANE RUN TP345.00] TO BUS 326002 [7CANERN NGCC345.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -8.3447e-07 | -0.00034642
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1824 326001-326002(1) | OPEN LINE FROM BUS 326001 [7CANE RUN TP345.00] TO BUS 326002 [7CANERN NGCC345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1825 326517-326523(1) | OPEN LINE FROM BUS 326517 [2OVEN FORK 69.000] TO BUS 326523 [2ARKLAND JCT69.000] CKT 1 | 0.93965 | 64.8362 | 0.93971 | 64.8397 | 5.1081e-05 | -0.00029451
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1825 326517-326523(1) | OPEN LINE FROM BUS 326517 [2OVEN FORK 69.000] TO BUS 326523 [2ARKLAND JCT69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1826 326523-326534(1) | OPEN LINE FROM BUS 326523 [2ARKLAND JCT69.000] TO BUS 326534 [2ARKLAND 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 1.1325e-06 | -0.00034446
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1826 326523-326534(1) | OPEN LINE FROM BUS 326523 [2ARKLAND JCT69.000] TO BUS 326534 [2ARKLAND 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1827 326524-326527(1) | OPEN LINE FROM BUS 326524 [2VAN METER 69.000] TO BUS 326527 [2TREEHAVEN T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93969 | 64.8385 | 3.4332e-05 | -0.00031126
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1827 326524-326527(1) | OPEN LINE FROM BUS 326524 [2VAN METER 69.000] TO BUS 326527 [2TREEHAVEN T69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 1.1921e-07 | 1.1921e-07
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1828 326525-326527(1) | OPEN LINE FROM BUS 326525 [2TREEHAVEN 69.000] TO BUS 326527 [2TREEHAVEN T69.000] CKT 1 | 0.93965 | 64.8362 | 0.93968 | 64.838 | 2.6345e-05 | -0.00031924
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1829 326526-326556(1) | OPEN LINE FROM BUS 326526 [4N SHARKEY 138.00] TO BUS 326556 [4N SHARKEY T138.00] CKT 1 | 0.93965 | 64.8362 | 0.93969 | 64.8387 | 3.7193e-05 | -0.00030839
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1829 326526-326556(1) | OPEN LINE FROM BUS 326526 [4N SHARKEY 138.00] TO BUS 326556 [4N SHARKEY T138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1830 326527-326541(1) | OPEN LINE FROM BUS 326527 [2TREEHAVEN T69.000] TO BUS 326541 [2EKPC OFFICE69.000] CKT 1 | 0.93965 | 64.8362 | 0.93971 | 64.8403 | 6.038e-05 | -0.00028521
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1830 326527-326541(1) | OPEN LINE FROM BUS 326527 [2TREEHAVEN T69.000] TO BUS 326541 [2EKPC OFFICE69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1831 326528-326974(1) | OPEN LINE FROM BUS 326528 [2BRIDGEPORT 69.000] TO BUS 326974 [2BRIDGPRT 2 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8358 | -5.1856e-06 | -0.00035077
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1831 326528-326974(1) | OPEN LINE FROM BUS 326528 [2BRIDGEPORT 69.000] TO BUS 326974 [2BRIDGPRT 2 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1832 326530-326539(1) | OPEN LINE FROM BUS 326530 [2EMANUEL 69.000] TO BUS 326539 [2GIRDLER 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93962 | 64.8339 | -3.314e-05 | -0.00037873
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1832 326530-326539(1) | OPEN LINE FROM BUS 326530 [2EMANUEL 69.000] TO BUS 326539 [2GIRDLER 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1833 326532-326556(1) | OPEN LINE FROM BUS 326532 [4SHARKEY 138.00] TO BUS 326556 [4N SHARKEY T138.00] CKT 1 | 0.93965 | 64.8362 | 0.93995 | 64.8563 | 0.00029242 | -5.3167e-05
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1833 326532-326556(1) | OPEN LINE FROM BUS 326532 [4SHARKEY 138.00] TO BUS 326556 [4N SHARKEY T138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1834 326552-326553(1) | OPEN LINE FROM BUS 326552 [2SE COAL TP 69.000] TO BUS 326553 [2SE COAL 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 5.3644e-07 | -0.00034505
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1834 326552-326553(1) | OPEN LINE FROM BUS 326552 [2SE COAL TP 69.000] TO BUS 326553 [2SE COAL 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1835 326559-326560(1) | OPEN LINE FROM BUS 326559 [4BGAD TAP 138.00] TO BUS 326560 [4BG ARMY DEP138.00] CKT 1 | 0.93965 | 64.8362 | 0.93969 | 64.8389 | 3.9697e-05 | -0.00030589
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1835 326559-326560(1) | OPEN LINE FROM BUS 326559 [4BGAD TAP 138.00] TO BUS 326560 [4BG ARMY DEP138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1836 326562-326596(Z1) | OPEN LINE FROM BUS 326562 [2PAD PRI 62469.000] TO BUS 326596 [2PAD PRI 61469.000] CKT Z1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 5.9605e-08 | -0.00034553
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1836 326562-326596(Z1) | OPEN LINE FROM BUS 326562 [2PAD PRI 62469.000] TO BUS 326596 [2PAD PRI 61469.000] CKT Z1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
326596 | 2PAD PRI 614 | 69 | LGEE' | RANGE | 0.94 | 1.06 | SINGLE OPN LIN 1836 326562-326596(Z1) | OPEN LINE FROM BUS 326562 [2PAD PRI 62469.000] TO BUS 326596 [2PAD PRI 61469.000] CKT Z1 | 1.0484 | 72.337 | 1.0824 | 74.6862 | 0.034046 | 0.022408
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1837 326571-326586(1) | OPEN LINE FROM BUS 326571 [2HUME RD 69.000] TO BUS 326586 [2HUME RD TAP69.000] CKT 1 | 0.93965 | 64.8362 | 0.93984 | 64.8488 | 0.00018376 | -0.00016183
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1837 326571-326586(1) | OPEN LINE FROM BUS 326571 [2HUME RD 69.000] TO BUS 326586 [2HUME RD TAP69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1838 326578-326579(1) | OPEN LINE FROM BUS 326578 [2HARRDSBRG 169.000] TO BUS 326579 [2HARRDSBRG 269.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 1.3113e-06 | -0.00034428
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1838 326578-326579(1) | OPEN LINE FROM BUS 326578 [2HARRDSBRG 169.000] TO BUS 326579 [2HARRDSBRG 269.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1839 326578-326584(1) | OPEN LINE FROM BUS 326578 [2HARRDSBRG 169.000] TO BUS 326584 [2CORNG7462_369.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 2.265e-06 | -0.00034332
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1839 326578-326584(1) | OPEN LINE FROM BUS 326578 [2HARRDSBRG 169.000] TO BUS 326584 [2CORNG7462_369.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1840 326579-326580(1) | OPEN LINE FROM BUS 326579 [2HARRDSBRG 269.000] TO BUS 326580 [2CORNIG 825369.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 2.7418e-06 | -0.00034285
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1840 326579-326580(1) | OPEN LINE FROM BUS 326579 [2HARRDSBRG 269.000] TO BUS 326580 [2CORNIG 825369.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1841 326582-326583(1) | OPEN LINE FROM BUS 326582 [2CORNG8251_269.000] TO BUS 326583 [2CORNIG 746169.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 1.7285e-06 | -0.00034386
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1841 326582-326583(1) | OPEN LINE FROM BUS 326582 [2CORNG8251_269.000] TO BUS 326583 [2CORNIG 746169.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1842 326583-326584(1) | OPEN LINE FROM BUS 326583 [2CORNIG 746169.000] TO BUS 326584 [2CORNG7462_369.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 1.7285e-06 | -0.00034386
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1842 326583-326584(1) | OPEN LINE FROM BUS 326583 [2CORNIG 746169.000] TO BUS 326584 [2CORNG7462_369.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1843 326591-326592(1) | OPEN LINE FROM BUS 326591 [5W PRINCETON161.00] TO BUS 326592 [5E PRINCETON161.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8365 | 5.3644e-06 | -0.00034022
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1843 326591-326592(1) | OPEN LINE FROM BUS 326591 [5W PRINCETON161.00] TO BUS 326592 [5E PRINCETON161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1844 326593-326594(1) | OPEN LINE FROM BUS 326593 [2GREENVIL N 69.000] TO BUS 326594 [2GREENVL 12 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 2.9206e-06 | -0.00034267
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1844 326593-326594(1) | OPEN LINE FROM BUS 326593 [2GREENVIL N 69.000] TO BUS 326594 [2GREENVL 12 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1845 324010-248000(1) | OPEN LINE FROM BUS 324010 [7TRIMBL REAC345.00] TO BUS 248000 [06CLIFTY 345.00] CKT 1 | 0.93965 | 64.8362 | 0.93947 | 64.8235 | -0.00018269 | -0.00052828
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1845 324010-248000(1) | OPEN LINE FROM BUS 324010 [7TRIMBL REAC345.00] TO BUS 248000 [06CLIFTY 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1846 324021-324044(1) | OPEN LINE FROM BUS 324021 [7BLUEGRASS12345.00] TO BUS 324044 [1BLUEGRASS 118.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -2.9802e-07 | -0.00034589
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1846 324021-324044(1) | OPEN LINE FROM BUS 324021 [7BLUEGRASS12345.00] TO BUS 324044 [1BLUEGRASS 118.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1847 324021-324045(1) | OPEN LINE FROM BUS 324021 [7BLUEGRASS12345.00] TO BUS 324045 [1BLUEGRASS 218.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.0729e-06 | -0.00034666
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1847 324021-324045(1) | OPEN LINE FROM BUS 324021 [7BLUEGRASS12345.00] TO BUS 324045 [1BLUEGRASS 218.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 1.1921e-07 | 1.1921e-07
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1848 324022-324046(1) | OPEN LINE FROM BUS 324022 [7BLUEGRASS 3345.00] TO BUS 324046 [1BLUEGRASS 318.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -2.9802e-07 | -0.00034589
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1848 324022-324046(1) | OPEN LINE FROM BUS 324022 [7BLUEGRASS 3345.00] TO BUS 324046 [1BLUEGRASS 318.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1850 324104-324113(1) | OPEN LINE FROM BUS 324104 [7DAVIESS 345.00] TO BUS 324113 [7SMITH 345.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8359 | -3.4571e-06 | -0.00034904
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1850 324104-324113(1) | OPEN LINE FROM BUS 324104 [7DAVIESS 345.00] TO BUS 324113 [7SMITH 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1851 324104-340561(1) | OPEN LINE FROM BUS 324104 [7DAVIESS 345.00] TO BUS 340561 [7WILSON 345.00] CKT 1 | 0.93965 | 64.8362 | 0.9397 | 64.8396 | 4.9531e-05 | -0.00029606
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1851 324104-340561(1) | OPEN LINE FROM BUS 324104 [7DAVIESS 345.00] TO BUS 340561 [7WILSON 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1852 324104-340563(1) | OPEN LINE FROM BUS 324104 [7DAVIESS 345.00] TO BUS 340563 [7COLEMAN 345.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8368 | 1.0014e-05 | -0.00033557
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1852 324104-340563(1) | OPEN LINE FROM BUS 324104 [7DAVIESS 345.00] TO BUS 340563 [7COLEMAN 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1853 324105-249501(1) | OPEN LINE FROM BUS 324105 [7GHENT 345.00] TO BUS 249501 [08BATESV 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1854 324105-249532(1) | OPEN LINE FROM BUS 324105 [7GHENT 345.00] TO BUS 249532 [08TRIMBL 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1855 324108-324284-326550(5) | OPEN LINE FROM BUS 324108 [7MILL CREEK 345.00] TO BUS 324284 [4MILL CREEK 138.00] TO BUS 326550 [1MC TR5 TERT13.800] CKT 5 | 0.93965 | 64.8362 | 0.93965 | 64.8359 | -4.1723e-06 | -0.00034976
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1855 324108-324284-326550(5) | OPEN LINE FROM BUS 324108 [7MILL CREEK 345.00] TO BUS 324284 [4MILL CREEK 138.00] TO BUS 326550 [1MC TR5 TERT13.800] CKT 5 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1856 324108-324284-326551(6) | OPEN LINE FROM BUS 324108 [7MILL CREEK 345.00] TO BUS 324284 [4MILL CREEK 138.00] TO BUS 326551 [1MC TR6 TERT13.800] CKT 6 | 0.93965 | 64.8362 | 0.93965 | 64.8359 | -3.6955e-06 | -0.00034928
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1856 324108-324284-326551(6) | OPEN LINE FROM BUS 324108 [7MILL CREEK 345.00] TO BUS 324284 [4MILL CREEK 138.00] TO BUS 326551 [1MC TR6 TERT13.800] CKT 6 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1857 324112-324072(1) | OPEN LINE FROM BUS 324112 [7PINEVILLE 345.00] TO BUS 324072 [8PINEVILLE 500.00] CKT 1 | 0.93965 | 64.8362 | 0.93968 | 64.838 | 2.6584e-05 | -0.000319
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1857 324112-324072(1) | OPEN LINE FROM BUS 324112 [7PINEVILLE 345.00] TO BUS 324072 [8PINEVILLE 500.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1858 324114-249520(1) | OPEN LINE FROM BUS 324114 [7TRIMBLE CO 345.00] TO BUS 249520 [08SPEED 345.00] CKT 1 | 0.93965 | 64.8362 | 0.93956 | 64.8294 | -9.8288e-05 | -0.00044388
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1858 324114-249520(1) | OPEN LINE FROM BUS 324114 [7TRIMBLE CO 345.00] TO BUS 249520 [08SPEED 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1859 324114-249532(1) | OPEN LINE FROM BUS 324114 [7TRIMBLE CO 345.00] TO BUS 249532 [08TRIMBL 345.00] CKT 1 | 0.93965 | 64.8362 | 0.9399 | 64.8531 | 0.00024509 | -0.00010049
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1859 324114-249532(1) | OPEN LINE FROM BUS 324114 [7TRIMBLE CO 345.00] TO BUS 249532 [08TRIMBL 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1863 324144-340553(1) | OPEN LINE FROM BUS 324144 [5GREEN RIVER161.00] TO BUS 340553 [5WLSNBR 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8352 | -1.4424e-05 | -0.00036001
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1863 324144-340553(1) | OPEN LINE FROM BUS 324144 [5GREEN RIVER161.00] TO BUS 340553 [5WLSNBR 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1864 324148-243668(1) | OPEN LINE FROM BUS 324148 [5WOOTON TAP 161.00] TO BUS 243668 [05WOOTON 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8359 | -3.3379e-06 | -0.00034893
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1864 324148-243668(1) | OPEN LINE FROM BUS 324148 [5WOOTON TAP 161.00] TO BUS 243668 [05WOOTON 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1865 324150-360334(1) | OPEN LINE FROM BUS 324150 [5LEBANON JCT161.00] TO BUS 360334 [5SUMMER SHAD161.00] CKT 1 | 0.93965 | 64.8362 | 0.93962 | 64.8338 | -3.4034e-05 | -0.00037962
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1865 324150-360334(1) | OPEN LINE FROM BUS 324150 [5LEBANON JCT161.00] TO BUS 360334 [5SUMMER SHAD161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1866 324151-360125(1) | OPEN LINE FROM BUS 324151 [5LIVNGSTN CO161.00] TO BUS 360125 [5CALVERT KY 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 4.1723e-06 | -0.00034142
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1866 324151-360125(1) | OPEN LINE FROM BUS 324151 [5LIVNGSTN CO161.00] TO BUS 360125 [5CALVERT KY 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1867 324151-360127(1) | OPEN LINE FROM BUS 324151 [5LIVNGSTN CO161.00] TO BUS 360127 [5KENTUCKY HP161.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 2.9802e-06 | -0.00034261
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1867 324151-360127(1) | OPEN LINE FROM BUS 324151 [5LIVNGSTN CO161.00] TO BUS 360127 [5KENTUCKY HP161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1868 324156-360452(1) | OPEN LINE FROM BUS 324156 [5PINEVILE SW161.00] TO BUS 360452 [5PINEVILL KY161.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -2.7418e-06 | -0.00034833
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1868 324156-360452(1) | OPEN LINE FROM BUS 324156 [5PINEVILE SW161.00] TO BUS 360452 [5PINEVILL KY161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1869 324157-324073(1) | OPEN LINE FROM BUS 324157 [5POCKET N 161.00] TO BUS 324073 [8POCKET N 500.00] CKT 1 | 0.93965 | 64.8362 | 0.93955 | 64.8287 | -0.00010777 | -0.00045335
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1869 324157-324073(1) | OPEN LINE FROM BUS 324157 [5POCKET N 161.00] TO BUS 324073 [8POCKET N 500.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1870 324171-351003(1) | OPEN LINE FROM BUS 324171 [5GRAHMVILE 1161.00] TO BUS 351003 [5JOPPA TS 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 3.9935e-06 | -0.00034159
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1870 324171-351003(1) | OPEN LINE FROM BUS 324171 [5GRAHMVILE 1161.00] TO BUS 351003 [5JOPPA TS 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1871 324172-351002(1) | OPEN LINE FROM BUS 324172 [5GRAHMVILE 2161.00] TO BUS 351002 [5JOPPA S 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 2.7418e-06 | -0.00034285
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1871 324172-351002(1) | OPEN LINE FROM BUS 324172 [5GRAHMVILE 2161.00] TO BUS 351002 [5JOPPA S 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1872 324173-340553(1) | OPEN LINE FROM BUS 324173 [5MATANZAS 161.00] TO BUS 340553 [5WLSNBR 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8367 | 8.2254e-06 | -0.00033736
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1872 324173-340553(1) | OPEN LINE FROM BUS 324173 [5MATANZAS 161.00] TO BUS 340553 [5WLSNBR 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1873 324173-340624(1) | OPEN LINE FROM BUS 324173 [5MATANZAS 161.00] TO BUS 340624 [5BRTAP 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.837 | 1.1861e-05 | -0.00033373
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1873 324173-340624(1) | OPEN LINE FROM BUS 324173 [5MATANZAS 161.00] TO BUS 340624 [5BRTAP 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1875 324211-251561(1) | OPEN LINE FROM BUS 324211 [4BLACKWELL 138.00] TO BUS 251561 [08BLACKW 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8349 | -1.8895e-05 | -0.00036448
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1875 324211-251561(1) | OPEN LINE FROM BUS 324211 [4BLACKWELL 138.00] TO BUS 251561 [08BLACKW 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1877 324217-325012(1) | OPEN LINE FROM BUS 324217 [4BROWN PLANT138.00] TO BUS 325012 [1BROWN SOLAR13.200] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8359 | -4.0531e-06 | -0.00034964
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1877 324217-325012(1) | OPEN LINE FROM BUS 324217 [4BROWN PLANT138.00] TO BUS 325012 [1BROWN SOLAR13.200] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1878 324227-248009(1) | OPEN LINE FROM BUS 324227 [4CARROLLTON 138.00] TO BUS 248009 [06CLIFTY 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93983 | 64.8482 | 0.00017446 | -0.00017112
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1878 324227-248009(1) | OPEN LINE FROM BUS 324227 [4CARROLLTON 138.00] TO BUS 248009 [06CLIFTY 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1879 324231-253623(1) | OPEN LINE FROM BUS 324231 [4CLOVERPORT 138.00] TO BUS 253623 [10CANTAP 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8365 | 4.4107e-06 | -0.00034118
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1879 324231-253623(1) | OPEN LINE FROM BUS 324231 [4CLOVERPORT 138.00] TO BUS 253623 [10CANTAP 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1880 324231-340615(1) | OPEN LINE FROM BUS 324231 [4CLOVERPORT 138.00] TO BUS 340615 [4N.HARD 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | -5.9605e-08 | -0.00034565
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1880 324231-340615(1) | OPEN LINE FROM BUS 324231 [4CLOVERPORT 138.00] TO BUS 340615 [4N.HARD 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1881 324232-324399(1) | OPEN LINE FROM BUS 324232 [4CANE RN 11A138.00] TO BUS 324399 [1CANERN11 14.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 7.7486e-07 | -0.00034481
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1884 324253-249723(1) | OPEN LINE FROM BUS 324253 [4GHENT 138.00] TO BUS 249723 [08FAIRVW 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93932 | 64.8129 | -0.00033641 | -0.000682
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1884 324253-249723(1) | OPEN LINE FROM BUS 324253 [4GHENT 138.00] TO BUS 249723 [08FAIRVW 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1886 324256-324309(1) | OPEN LINE FROM BUS 324256 [4GR RVR STL 138.00] TO BUS 324309 [4SMITH 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | -5.9605e-08 | -0.00034565
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1886 324256-324309(1) | OPEN LINE FROM BUS 324256 [4GR RVR STL 138.00] TO BUS 324309 [4SMITH 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1887 324260-340615(1) | OPEN LINE FROM BUS 324260 [4HARDINSBURG138.00] TO BUS 340615 [4N.HARD 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 2.3842e-07 | -0.00034535
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1887 324260-340615(1) | OPEN LINE FROM BUS 324260 [4HARDINSBURG138.00] TO BUS 340615 [4N.HARD 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1889 324265-249763(1) | OPEN LINE FROM BUS 324265 [4JEFFRSONV T138.00] TO BUS 249763 [08JEFF 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8357 | -6.2585e-06 | -0.00035185
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1889 324265-249763(1) | OPEN LINE FROM BUS 324265 [4JEFFRSONV T138.00] TO BUS 249763 [08JEFF 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1890 324267-247508(1) | OPEN LINE FROM BUS 324267 [4KENTON 138.00] TO BUS 247508 [05SARDINIA 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93883 | 64.7796 | -0.00082016 | -0.0011657
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1890 324267-247508(1) | OPEN LINE FROM BUS 324267 [4KENTON 138.00] TO BUS 247508 [05SARDINIA 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1892 324268-324170(1) | OPEN LINE FROM BUS 324268 [4KNOB CREEK 138.00] TO BUS 324170 [1KNOB CRK 34.500] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8359 | -3.9339e-06 | -0.00034952
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1892 324268-324170(1) | OPEN LINE FROM BUS 324268 [4KNOB CREEK 138.00] TO BUS 324170 [1KNOB CRK 34.500] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1899 324289-249789(1) | OPEN LINE FROM BUS 324289 [4NORTHSIDE 138.00] TO BUS 249789 [08LOUCMJ 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8365 | 5.424e-06 | -0.00034016
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1899 324289-249789(1) | OPEN LINE FROM BUS 324289 [4NORTHSIDE 138.00] TO BUS 249789 [08LOUCMJ 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1901 324294-249730(1) | OPEN LINE FROM BUS 324294 [4PADDYS WEST138.00] TO BUS 249730 [08GALAGH 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.835 | -1.663e-05 | -0.00036222
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1901 324294-249730(1) | OPEN LINE FROM BUS 324294 [4PADDYS WEST138.00] TO BUS 249730 [08GALAGH 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1902 324295-324431(4A) | OPEN LINE FROM BUS 324295 [4PADDYS RUN 138.00] TO BUS 324431 [1PADDYR1 14.000] CKT 4A | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.7881e-07 | -0.00034577
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1902 324295-324431(4A) | OPEN LINE FROM BUS 324295 [4PADDYS RUN 138.00] TO BUS 324431 [1PADDYR1 14.000] CKT 4A | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1903 324295-324596(5) | OPEN LINE FROM BUS 324295 [4PADDYS RUN 138.00] TO BUS 324596 [1PADDYR2A 14.000] CKT 5 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | -5.9605e-08 | -0.00034565
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1903 324295-324596(5) | OPEN LINE FROM BUS 324295 [4PADDYS RUN 138.00] TO BUS 324596 [1PADDYR2A 14.000] CKT 5 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1904 324295-324675-324635(3) | OPEN LINE FROM BUS 324295 [4PADDYS RUN 138.00] TO BUS 324675 [2PADDYS RUN 69.000] TO BUS 324635 [1PADDYR2B 14.000] CKT 3 | 0.93965 | 64.8362 | 0.93966 | 64.8365 | 5.4836e-06 | -0.0003401
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1904 324295-324675-324635(3) | OPEN LINE FROM BUS 324295 [4PADDYS RUN 138.00] TO BUS 324675 [2PADDYS RUN 69.000] TO BUS 324635 [1PADDYR2B 14.000] CKT 3 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1906 324311-324366(1) | OPEN LINE FROM BUS 324311 [4TIP TOP 138.00] TO BUS 324366 [1TIPTOP 1 34.500] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 1.4901e-06 | -0.0003441
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1906 324311-324366(1) | OPEN LINE FROM BUS 324311 [4TIP TOP 138.00] TO BUS 324366 [1TIPTOP 1 34.500] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1907 324311-324753-326511(2) | OPEN LINE FROM BUS 324311 [4TIP TOP 138.00] TO BUS 324753 [2TIP TOP 2 69.000] TO BUS 326511 [1TIPTOP 34.500] CKT 2 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 3.2187e-06 | -0.00034237
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1907 324311-324753-326511(2) | OPEN LINE FROM BUS 324311 [4TIP TOP 138.00] TO BUS 324753 [2TIP TOP 2 69.000] TO BUS 326511 [1TIPTOP 34.500] CKT 2 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1908 324316-242605(1) | OPEN LINE FROM BUS 324316 [4VIRGINIA CI138.00] TO BUS 242605 [05CLNCHR 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8368 | 9.5963e-06 | -0.00033599
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1908 324316-242605(1) | OPEN LINE FROM BUS 324316 [4VIRGINIA CI138.00] TO BUS 242605 [05CLNCHR 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1910 324405-326500(1) | OPEN LINE FROM BUS 324405 [2ADAMS 69.000] TO BUS 326500 [1ADAMS 34.500] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -8.9407e-07 | -0.00034648
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1910 324405-326500(1) | OPEN LINE FROM BUS 324405 [2ADAMS 69.000] TO BUS 326500 [1ADAMS 34.500] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1911 324412-326501(1) | OPEN LINE FROM BUS 324412 [2ANDOVER 69.000] TO BUS 326501 [1ANDOVE 34.500] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8372 | 1.508e-05 | -0.00033051
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1911 324412-326501(1) | OPEN LINE FROM BUS 324412 [2ANDOVER 69.000] TO BUS 326501 [1ANDOVE 34.500] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1915 324437-324063(1) | OPEN LINE FROM BUS 324437 [2BEVIER KU 69.000] TO BUS 324063 [1BEVIER 34.500] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 2.3246e-06 | -0.00034326
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1918 324446-324397(1) | OPEN LINE FROM BUS 324446 [2BOND 69.000] TO BUS 324397 [1BOND 23.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8368 | 1.0014e-05 | -0.00033557
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1918 324446-324397(1) | OPEN LINE FROM BUS 324446 [2BOND 69.000] TO BUS 324397 [1BOND 23.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1923 324503-324398(1) | OPEN LINE FROM BUS 324503 [2DORCHESTER 69.000] TO BUS 324398 [1DORCHEST 23.000] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.837 | 1.204e-05 | -0.00033355
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1923 324503-324398(1) | OPEN LINE FROM BUS 324503 [2DORCHESTER 69.000] TO BUS 324398 [1DORCHEST 23.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1924 324503-326504(1) | OPEN LINE FROM BUS 324503 [2DORCHESTER 69.000] TO BUS 326504 [1DORCHE 34.500] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 1.0729e-06 | -0.00034451
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1924 324503-326504(1) | OPEN LINE FROM BUS 324503 [2DORCHESTER 69.000] TO BUS 326504 [1DORCHE 34.500] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1925 324507-324123(1) | OPEN LINE FROM BUS 324507 [2EARLINGTON 69.000] TO BUS 324123 [1EARLINGT 34.500] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 1.4305e-06 | -0.00034416
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1925 324507-324123(1) | OPEN LINE FROM BUS 324507 [2EARLINGTON 69.000] TO BUS 324123 [1EARLINGT 34.500] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1927 324512-362916(1) | OPEN LINE FROM BUS 324512 [2EDDYV PR TP69.000] TO BUS 362916 [2KY DAM 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8365 | 5.0664e-06 | -0.00034052
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1927 324512-362916(1) | OPEN LINE FROM BUS 324512 [2EDDYV PR TP69.000] TO BUS 362916 [2KY DAM 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1933 324533-326505(1) | OPEN LINE FROM BUS 324533 [2FRANKFORT 169.000] TO BUS 326505 [1FFRT 34.500] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8374 | 1.7405e-05 | -0.00032818
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1933 324533-326505(1) | OPEN LINE FROM BUS 324533 [2FRANKFORT 169.000] TO BUS 326505 [1FFRT 34.500] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1934 324550-324128(1) | OPEN LINE FROM BUS 324550 [2GREEN RIVER69.000] TO BUS 324128 [1GREEN RIVER34.500] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 2.265e-06 | -0.00034332
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1934 324550-324128(1) | OPEN LINE FROM BUS 324550 [2GREEN RIVER69.000] TO BUS 324128 [1GREEN RIVER34.500] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1935 324551-324669(1) | OPEN LINE FROM BUS 324551 [2GR RVR STL 69.000] TO BUS 324669 [2OMU 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 5.9605e-07 | -0.00034499
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1935 324551-324669(1) | OPEN LINE FROM BUS 324551 [2GR RVR STL 69.000] TO BUS 324669 [2OMU 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1937 324574-324043(1) | OPEN LINE FROM BUS 324574 [2HILLCREST 69.000] TO BUS 324043 [1ZORN 13.800] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 0 | -0.00034559
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1937 324574-324043(1) | OPEN LINE FROM BUS 324574 [2HILLCREST 69.000] TO BUS 324043 [1ZORN 13.800] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1940 324578-324142(1) | OPEN LINE FROM BUS 324578 [2HARDESTY B 69.000] TO BUS 324142 [1HARDSTY 34.500] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 1.1921e-06 | -0.0003444
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1940 324578-324142(1) | OPEN LINE FROM BUS 324578 [2HARDESTY B 69.000] TO BUS 324142 [1HARDSTY 34.500] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1941 324583-324168(1) | OPEN LINE FROM BUS 324583 [2IMBODEN 69.000] TO BUS 324168 [1IMBODEN 34.500] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 1.1325e-06 | -0.00034446
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1941 324583-324168(1) | OPEN LINE FROM BUS 324583 [2IMBODEN 69.000] TO BUS 324168 [1IMBODEN 34.500] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1945 324664-326507(1) | OPEN LINE FROM BUS 324664 [2OAK HILL KU69.000] TO BUS 326507 [1OAK HI 34.500] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8365 | 4.2915e-06 | -0.0003413
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1945 324664-326507(1) | OPEN LINE FROM BUS 324664 [2OAK HILL KU69.000] TO BUS 326507 [1OAK HI 34.500] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1948 324689-324184(1) | OPEN LINE FROM BUS 324689 [2POCKET 69.000] TO BUS 324184 [1POCKET 34.500] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 6.5565e-07 | -0.00034493
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1948 324689-324184(1) | OPEN LINE FROM BUS 324689 [2POCKET 69.000] TO BUS 324184 [1POCKET 34.500] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1949 324693-326509(1) | OPEN LINE FROM BUS 324693 [2PRINCETON 69.000] TO BUS 326509 [1PRINCE 34.500] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 1.8477e-06 | -0.00034374
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1949 324693-326509(1) | OPEN LINE FROM BUS 324693 [2PRINCETON 69.000] TO BUS 326509 [1PRINCE 34.500] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1950 324707-243740(Z1) | OPEN LINE FROM BUS 324707 [2RODBURN 69.000] TO BUS 243740 [05MOREHE 69.000] CKT Z1 | 0.93965 | 64.8362 | 0.93983 | 64.8485 | 0.00017834 | -0.00016725
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1950 324707-243740(Z1) | OPEN LINE FROM BUS 324707 [2RODBURN 69.000] TO BUS 243740 [05MOREHE 69.000] CKT Z1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1952 324712-362116(1) | OPEN LINE FROM BUS 324712 [2SO PADUCAH 69.000] TO BUS 362116 [2KY HYDRO 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 4.1723e-07 | -0.00034517
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1952 324712-362116(1) | OPEN LINE FROM BUS 324712 [2SO PADUCAH 69.000] TO BUS 362116 [2KY HYDRO 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1959 324764-324368(1) | OPEN LINE FROM BUS 324764 [2WEST CLIFF 69.000] TO BUS 324368 [1W CLIFF 34.500] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -9.5367e-07 | -0.00034654
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1959 324764-324368(1) | OPEN LINE FROM BUS 324764 [2WEST CLIFF 69.000] TO BUS 324368 [1W CLIFF 34.500] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1962 324803-324057(1) | OPEN LINE FROM BUS 324803 [2BEAR TRACK 69.000] TO BUS 324057 [1BEAR TRA 34.500] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 8.9407e-07 | -0.00034469
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1962 324803-324057(1) | OPEN LINE FROM BUS 324803 [2BEAR TRACK 69.000] TO BUS 324057 [1BEAR TRA 34.500] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1964 324947-324190(1) | OPEN LINE FROM BUS 324947 [2RUMSEY 69.000] TO BUS 324190 [1RUMSEY 34.500] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 0 | -0.00034559
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1964 324947-324190(1) | OPEN LINE FROM BUS 324947 [2RUMSEY 69.000] TO BUS 324190 [1RUMSEY 34.500] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1965 324948-324883(1) | OPEN LINE FROM BUS 324948 [2SALEM KU 69.000] TO BUS 324883 [1SALEM 34.500] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 1.0133e-06 | -0.00034457
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1965 324948-324883(1) | OPEN LINE FROM BUS 324948 [2SALEM KU 69.000] TO BUS 324883 [1SALEM 34.500] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1967 325013-248009(1) | OPEN LINE FROM BUS 325013 [4CLIFTY TAP1138.00] TO BUS 248009 [06CLIFTY 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8368 | 8.8811e-06 | -0.00033671
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1967 325013-248009(1) | OPEN LINE FROM BUS 325013 [4CLIFTY TAP1138.00] TO BUS 248009 [06CLIFTY 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1968 325014-248009(1) | OPEN LINE FROM BUS 325014 [4CLIFTY TAP2138.00] TO BUS 248009 [06CLIFTY 138.00] CKT 1 | 0.93965 | 64.8362 | 0.9395 | 64.8254 | -0.00015652 | -0.00050211
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1968 325014-248009(1) | OPEN LINE FROM BUS 325014 [4CLIFTY TAP2138.00] TO BUS 248009 [06CLIFTY 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1969 325014-250057(1) | OPEN LINE FROM BUS 325014 [4CLIFTY TAP2138.00] TO BUS 250057 [08M.FORT 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93946 | 64.8229 | -0.00019228 | -0.00053787
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1969 325014-250057(1) | OPEN LINE FROM BUS 325014 [4CLIFTY TAP2138.00] TO BUS 250057 [08M.FORT 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1970 325015-324309(1) | OPEN LINE FROM BUS 325015 [4SMITH TAP 138.00] TO BUS 324309 [4SMITH 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 0 | -0.00034559
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1970 325015-324309(1) | OPEN LINE FROM BUS 325015 [4SMITH TAP 138.00] TO BUS 324309 [4SMITH 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1972 325047-325046(1) | OPEN LINE FROM BUS 325047 [5ASHWOOD 161.00] TO BUS 325046 [1ASHWOOD COL34.500] CKT 1 | 0.93965 | 64.8362 | 0.93962 | 64.8338 | -3.3736e-05 | -0.00037932
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1972 325047-325046(1) | OPEN LINE FROM BUS 325047 [5ASHWOOD 161.00] TO BUS 325046 [1ASHWOOD COL34.500] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1973 325073-340651(1) | OPEN LINE FROM BUS 325073 [7REDMON RD 345.00] TO BUS 340651 [OTTERCRK345 345.00] CKT 1 | 0.93965 | 64.8362 | 0.93963 | 64.8346 | -2.1815e-05 | -0.0003674
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1973 325073-340651(1) | OPEN LINE FROM BUS 325073 [7REDMON RD 345.00] TO BUS 340651 [OTTERCRK345 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1976 325116-325117(1) | OPEN LINE FROM BUS 325116 [4RHUDES CR 138.00] TO BUS 325117 [1RHUDES COL 34.500] CKT 1 | 0.93965 | 64.8362 | 0.9396 | 64.8321 | -5.8651e-05 | -0.00040424
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1976 325116-325117(1) | OPEN LINE FROM BUS 325116 [4RHUDES CR 138.00] TO BUS 325117 [1RHUDES COL 34.500] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1979 326569-248830(1) | OPEN LINE FROM BUS 326569 [7KENZIG ROAD345.00] TO BUS 248830 [07RAMSY5 345.00] CKT 1 | 0.93965 | 64.8362 | 0.93983 | 64.8484 | 0.0001781 | -0.00016749
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1979 326569-248830(1) | OPEN LINE FROM BUS 326569 [7KENZIG ROAD345.00] TO BUS 248830 [07RAMSY5 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1980 326569-249520(1) | OPEN LINE FROM BUS 326569 [7KENZIG ROAD345.00] TO BUS 249520 [08SPEED 345.00] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8352 | -1.4484e-05 | -0.00036007
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1980 326569-249520(1) | OPEN LINE FROM BUS 326569 [7KENZIG ROAD345.00] TO BUS 249520 [08SPEED 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1981 326596-324697(1) | OPEN LINE FROM BUS 326596 [2PAD PRI 61469.000] TO BUS 324697 [1KMPA PAD2 13.800] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.835 | -1.6749e-05 | -0.00036234
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1981 326596-324697(1) | OPEN LINE FROM BUS 326596 [2PAD PRI 61469.000] TO BUS 324697 [1KMPA PAD2 13.800] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1982 326596-324933(1) | OPEN LINE FROM BUS 326596 [2PAD PRI 61469.000] TO BUS 324933 [1KMPA PAD1 13.800] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.835 | -1.6689e-05 | -0.00036228
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1982 326596-324933(1) | OPEN LINE FROM BUS 326596 [2PAD PRI 61469.000] TO BUS 324933 [1KMPA PAD1 13.800] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1985 326998-361788(1) | OPEN LINE FROM BUS 326998 [5BULLITT TAP161.00] TO BUS 361788 [5SUM SHAD TP161.00] CKT 1 | 0.93965 | 64.8362 | 0.93961 | 64.8332 | -4.214e-05 | -0.00038773
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 1985 326998-361788(1) | OPEN LINE FROM BUS 326998 [5BULLITT TAP161.00] TO BUS 361788 [5SUM SHAD TP161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | MERE SWS | MERE SWS | 0.93965 | 64.8362 | 0.93965 | 64.8356 | -7.391e-06 | -0.00035298
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | MERE SWS | MERE SWS | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-69-51 | B-69-51 | 0.93965 | 64.8362 | 0.93964 | 64.8348 | -1.9372e-05 | -0.00036496
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-69-51 | B-69-51 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-69-446 | B-69-446 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 8.9407e-07 | -0.00034469
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-69-446 | B-69-446 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-69-65 | B-69-65 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.1921e-07 | -0.00034571
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-69-65 | B-69-65 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-69-63 | B-69-63 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 7.7486e-07 | -0.00034481
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-69-63 | B-69-63 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-69-66 | B-69-66 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 0 | -0.00034559
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-69-66 | B-69-66 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-69-53 | B-69-53 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 2.3842e-07 | -0.00034535
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-69-53 | B-69-53 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-69-36 | B-69-36 | 0.93965 | 64.8362 | 0.93829 | 64.7418 | -0.0013673 | -0.0017129
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-69-36 | B-69-36 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-69-49 | B-69-49 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 6.5565e-07 | -0.00034493
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-69-49 | B-69-49 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-69-37 | B-69-37 | 0.93965 | 64.8362 | 0.93954 | 64.8284 | -0.00011289 | -0.00045848
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-69-37 | B-69-37 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-69-11 | B-69-11 | 0.93965 | 64.8362 | 0.93955 | 64.8288 | -0.00010633 | -0.00045192
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-69-11 | B-69-11 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-69-50 | B-69-50 | 0.93965 | 64.8362 | 0.93959 | 64.8318 | -6.3658e-05 | -0.00040925
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-69-50 | B-69-50 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-69-316A | B-69-316A | 0.93965 | 64.8362 | 0.93965 | 64.8356 | -7.8678e-06 | -0.00035346
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-69-316A | B-69-316A | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-69-9 | B-69-9 | 0.93965 | 64.8362 | 0.93965 | 64.8359 | -3.4571e-06 | -0.00034904
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-69-9 | B-69-9 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SW-1000 | SW-1000 | 0.93965 | 64.8362 | 0.93953 | 64.8277 | -0.00012237 | -0.00046796
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SW-1000 | SW-1000 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-69-47 | B-69-47 | 0.93965 | 64.8362 | 0.93967 | 64.8371 | 1.3173e-05 | -0.00033242
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-69-47 | B-69-47 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-69-48 | B-69-48 | 0.93965 | 64.8362 | 0.93966 | 64.8367 | 7.391e-06 | -0.0003382
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-69-48 | B-69-48 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-69-52 | B-69-52 | 0.93965 | 64.8362 | 0.93964 | 64.8355 | -1.0192e-05 | -0.00035578
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-69-52 | B-69-52 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-69-56 | B-69-56 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 1.1921e-07 | -0.00034547
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-69-56 | B-69-56 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-69-57 | B-69-57 | 0.93965 | 64.8362 | 0.93965 | 64.8359 | -4.0531e-06 | -0.00034964
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-69-57 | B-69-57 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-69-58 | B-69-58 | 0.93965 | 64.8362 | 0.93967 | 64.8369 | 1.0908e-05 | -0.00033468
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-69-58 | B-69-58 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-69-60 | B-69-60 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -1.7285e-06 | -0.00034732
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-69-60 | B-69-60 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-69-61 | B-69-61 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -2.8014e-06 | -0.00034839
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-69-61 | B-69-61 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-69-62 | B-69-62 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | -5.9605e-08 | -0.00034565
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-69-62 | B-69-62 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-69-318 | B-69-318 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.1921e-06 | -0.00034678
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-69-318 | B-69-318 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-69-319 | B-69-319 | 0.93965 | 64.8362 | 0.93964 | 64.8352 | -1.359e-05 | -0.00035918
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-69-319 | B-69-319 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-69-67 | B-69-67 | 0.93965 | 64.8362 | 0.93985 | 64.8494 | 0.00019217 | -0.00015342
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-69-67 | B-69-67 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-69-693 | B-69-693 | 0.93965 | 64.8362 | 0.9398 | 64.8465 | 0.00014931 | -0.00019628
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-69-693 | B-69-693 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-69-69 | B-69-69 | 0.93965 | 64.8362 | 0.93956 | 64.8299 | -9.0897e-05 | -0.00043648
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-69-69 | B-69-69 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-69-72 | B-69-72 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -1.9073e-06 | -0.0003475
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-69-72 | B-69-72 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-69-74 | B-69-74 | 0.93965 | 64.8362 | 0.93961 | 64.8329 | -4.7326e-05 | -0.00039291
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-69-74 | B-69-74 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-69-76 | B-69-76 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | -5.9605e-08 | -0.00034565
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-69-76 | B-69-76 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-69-77 | B-69-77 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.7881e-07 | -0.00034577
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-69-77 | B-69-77 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-69-73 | B-69-73 | 0.93965 | 64.8362 | 0.93961 | 64.8331 | -4.4644e-05 | -0.00039023
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-69-73 | B-69-73 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-69-10 | B-69-10 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.4305e-06 | -0.00034702
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-69-10 | B-69-10 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-345-449 | B-345-449 | 0.93965 | 64.8362 | 0.93905 | 64.7944 | -0.00060487 | -0.00095046
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-345-449 | B-345-449 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-138-123 | B-138-123 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-69-322 | B-69-322 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 4.1723e-07 | -0.00034517
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-69-322 | B-69-322 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-69-324 | B-69-324 | 0.93965 | 64.8362 | 0.93971 | 64.8397 | 5.1975e-05 | -0.00029361
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-69-324 | B-69-324 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-69-79 | B-69-79 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -2.9206e-06 | -0.00034851
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-69-79 | B-69-79 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-69-80 | B-69-80 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.1325e-06 | -0.00034672
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-69-80 | B-69-80 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-69-325 | B-69-325 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -2.0266e-06 | -0.00034761
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-69-325 | B-69-325 | 1.05 | 525 | 1.05 | 525 | 1.1921e-07 | 1.1921e-07
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-69-327 | B-69-327 | 0.93965 | 64.8362 | 0.93954 | 64.8283 | -0.0001142 | -0.00045979
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-69-327 | B-69-327 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-138-115 | B-138-115 | 0.93965 | 64.8362 | 0.93964 | 64.835 | -1.6332e-05 | -0.00036192
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-138-115 | B-138-115 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-69-448 | B-69-448 | 0.93965 | 64.8362 | 0.93962 | 64.8338 | -3.3975e-05 | -0.00037956
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-69-448 | B-69-448 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-161-131 | B-161-131 | 0.93965 | 64.8362 | 0.93961 | 64.8332 | -4.2737e-05 | -0.00038832
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-161-131 | B-161-131 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-69-334 | B-69-334 | 0.93965 | 64.8362 | 0.93992 | 64.8542 | 0.00026166 | -8.3923e-05
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-69-334 | B-69-334 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-69-335 | B-69-335 | 0.93965 | 64.8362 | 0.93953 | 64.8275 | -0.00012499 | -0.00047058
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-69-335 | B-69-335 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-138-447 | B-138-447 | 0.93965 | 64.8362 | 0.93995 | 64.8569 | 0.00030053 | -4.5061e-05
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-138-447 | B-138-447 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-69-330 | B-69-330 | 0.93965 | 64.8362 | 0.93995 | 64.8568 | 0.00029945 | -4.6134e-05
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-69-330 | B-69-330 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-69-332 | B-69-332 | 0.93965 | 64.8362 | 0.93965 | 64.8358 | -5.0068e-06 | -0.00035059
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-69-332 | B-69-332 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-69-337 | B-69-337 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.0133e-06 | -0.0003466
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-69-337 | B-69-337 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-69-338 | B-69-338 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -9.5367e-07 | -0.00034654
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-69-338 | B-69-338 | 1.05 | 525 | 1.05 | 525 | 0 | 0
324757 | 2UPR MIL CRK | 69 | LGEE' | RANGE | 0.94 | 1.06 | B-69-338 | B-69-338 | 1.0049 | 69.3354 | 0.93762 | 64.6956 | -0.067244 | -0.0023826
324941 | 2RIVERPORT | 69 | LGEE' | RANGE | 0.94 | 1.06 | B-69-338 | B-69-338 | 0.992 | 68.4483 | 0.9376 | 64.6942 | -0.054408 | -0.0024033
324975 | 2TERRY | 69 | LGEE' | RANGE | 0.94 | 1.06 | B-69-338 | B-69-338 | 0.98781 | 68.1591 | 0.93758 | 64.693 | -0.050232 | -0.0024197
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-69-450 | B-69-450 | 0.93965 | 64.8362 | 0.93978 | 64.845 | 0.00012815 | -0.00021744
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-69-450 | B-69-450 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-500-97 | B-500-97 | 0.93965 | 64.8362 | 0.93949 | 64.8249 | -0.00016266 | -0.00050825
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-500-97 | B-500-97 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-69-339 | B-69-339 | 0.93965 | 64.8362 | 0.93956 | 64.8298 | -9.1374e-05 | -0.00043696
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-69-339 | B-69-339 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-69-340 | B-69-340 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -5.9605e-07 | -0.00034618
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-69-340 | B-69-340 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-2000 | BB-2000 | 0.93965 | 64.8362 | 0.93865 | 64.7666 | -0.0010085 | -0.0013541
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-2000 | BB-2000 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1366 | BB-1366 | 0.93965 | 64.8362 | 0.93943 | 64.8204 | -0.00022763 | -0.00057322
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1366 | BB-1366 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1452 | BB-1452 | 0.93965 | 64.8362 | 0.93996 | 64.8571 | 0.00030375 | -4.1842e-05
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1452 | BB-1452 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1386 | BB-1386 | 0.93965 | 64.8362 | 0.93963 | 64.8344 | -2.4736e-05 | -0.00037032
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1386 | BB-1386 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1456 | BB-1456 | 0.93965 | 64.8362 | 0.9397 | 64.8395 | 4.7863e-05 | -0.00029773
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1456 | BB-1456 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1280 | BB-1280 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1479 | BB-1479 | 0.93965 | 64.8362 | 0.93957 | 64.83 | -8.8751e-05 | -0.00043434
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1479 | BB-1479 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1317 | BB-1317 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1225 | BB-1225 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -2.2054e-06 | -0.00034779
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1225 | BB-1225 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1373 | BB-1373 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1073 | BB-1073 | 0.93965 | 64.8362 | 0.9396 | 64.8321 | -5.8889e-05 | -0.00040448
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1493 | BB-1493 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1494 | BB-1494 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1495 | BB-1495 | 0.93965 | 64.8362 | 0.93903 | 64.7932 | -0.00062275 | -0.00096834
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1495 | BB-1495 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1395 | BB-1395 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1318 | BB-1318 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1352 | BB-1352 | 0.93965 | 64.8362 | 0.93926 | 64.8087 | -0.00039834 | -0.00074393
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1352 | BB-1352 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1405 | BB-1405 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1301 | BB-1301 | 0.93965 | 64.8362 | 0.93982 | 64.8474 | 0.0001629 | -0.00018269
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1301 | BB-1301 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1387 | BB-1387 | 0.93965 | 64.8362 | 0.93968 | 64.8382 | 2.9981e-05 | -0.00031561
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1387 | BB-1387 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1443 | BB-1443 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1335 | BB-1335 | 0.93965 | 64.8362 | 0.93983 | 64.8481 | 0.00017309 | -0.0001725
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1335 | BB-1335 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1298 | BB-1298 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1369 | BB-1369 | 0.93965 | 64.8362 | 0.93971 | 64.8402 | 5.8472e-05 | -0.00028712
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1369 | BB-1369 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1297 | BB-1297 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1288 | BB-1288 | 0.93965 | 64.8362 | 0.93986 | 64.8506 | 0.00020999 | -0.0001356
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1288 | BB-1288 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1468 | BB-1468 | 0.93965 | 64.8362 | 0.93979 | 64.8458 | 0.00014007 | -0.00020552
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1468 | BB-1468 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1315 | BB-1315 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1482 | BB-1482 | 0.93965 | 64.8362 | 0.93998 | 64.8584 | 0.00032246 | -2.3127e-05
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1482 | BB-1482 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1368 | BB-1368 | 0.93965 | 64.8362 | 0.93947 | 64.8232 | -0.00018781 | -0.0005334
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1368 | BB-1368 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1312 | BB-1312 | 0.93965 | 64.8362 | 0.9398 | 64.8464 | 0.00014853 | -0.00019705
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1312 | BB-1312 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1313 | BB-1313 | 0.93965 | 64.8362 | 0.93985 | 64.8497 | 0.00019652 | -0.00014907
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1313 | BB-1313 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1319 | BB-1319 | 0.93965 | 64.8362 | 0.93944 | 64.8213 | -0.00021577 | -0.00056136
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1319 | BB-1319 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1323 | BB-1323 | 0.93965 | 64.8362 | 0.93966 | 64.8365 | 4.9472e-06 | -0.00034064
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1323 | BB-1323 | 1.05 | 525 | 1.05 | 525 | 1.1921e-07 | 1.1921e-07
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1325 | BB-1325 | 0.93965 | 64.8362 | 0.93966 | 64.8368 | 9.0599e-06 | -0.00033653
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1325 | BB-1325 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1407 | BB-1407 | 0.93965 | 64.8362 | 0.93966 | 64.8368 | 1.0014e-05 | -0.00033557
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1407 | BB-1407 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1356 | BB-1356 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 4.0531e-06 | -0.00034153
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1356 | BB-1356 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1316 | BB-1316 | 0.93965 | 64.8362 | 0.93963 | 64.8343 | -2.6524e-05 | -0.00037211
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1316 | BB-1316 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1370 | BB-1370 | 0.93965 | 64.8362 | 0.93962 | 64.834 | -3.0577e-05 | -0.00037616
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1370 | BB-1370 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1349 | BB-1349 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -1.9073e-06 | -0.0003475
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1349 | BB-1349 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1320 | BB-1320 | 0.93965 | 64.8362 | 0.93966 | 64.8367 | 7.6294e-06 | -0.00033796
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1320 | BB-1320 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1434 | BB-1434 | 0.93965 | 64.8362 | 0.93966 | 64.8368 | 8.7023e-06 | -0.00033689
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1434 | BB-1434 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1285 | BB-1285 | 0.93965 | 64.8362 | 0.93966 | 64.8367 | 7.6294e-06 | -0.00033796
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1285 | BB-1285 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1401 | BB-1401 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 2.9206e-06 | -0.00034267
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1401 | BB-1401 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | MORG-WHT-NEB | MORG-WHT-NEB | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 1.5497e-06 | -0.00034404
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | MORG-WHT-NEB | MORG-WHT-NEB | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1302 | BB-1302 | 0.93965 | 64.8362 | 0.93972 | 64.8404 | 6.0916e-05 | -0.00028467
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1302 | BB-1302 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1400 | BB-1400 | 0.93965 | 64.8362 | 0.93967 | 64.8372 | 1.5736e-05 | -0.00032985
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1400 | BB-1400 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1344 | BB-1344 | 0.93965 | 64.8362 | 0.93967 | 64.8374 | 1.7762e-05 | -0.00032783
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1344 | BB-1344 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1473 | BB-1473 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.3709e-06 | -0.00034696
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1473 | BB-1473 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1420 | BB-1420 | 0.93965 | 64.8362 | 0.93967 | 64.837 | 1.1623e-05 | -0.00033396
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1420 | BB-1420 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1306 | BB-1306 | 0.93965 | 64.8362 | 0.93967 | 64.8373 | 1.7226e-05 | -0.00032836
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1306 | BB-1306 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1307 | BB-1307 | 0.93965 | 64.8362 | 0.93971 | 64.84 | 5.5611e-05 | -0.00028998
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1307 | BB-1307 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1415 | BB-1415 | 0.93965 | 64.8362 | 0.93968 | 64.838 | 2.6107e-05 | -0.00031948
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1415 | BB-1415 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1342 | BB-1342 | 0.93965 | 64.8362 | 0.93968 | 64.8377 | 2.2352e-05 | -0.00032324
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1342 | BB-1342 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1287 | BB-1287 | 0.93965 | 64.8362 | 0.93967 | 64.8375 | 2.0206e-05 | -0.00032538
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1287 | BB-1287 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1491 | BB-1491 | 0.93965 | 64.8362 | 0.93968 | 64.8379 | 2.5034e-05 | -0.00032055
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1491 | BB-1491 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1303 | BB-1303 | 0.93965 | 64.8362 | 0.93965 | 64.8356 | -7.3314e-06 | -0.00035292
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1303 | BB-1303 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1374 | BB-1374 | 0.93965 | 64.8362 | 0.93967 | 64.8369 | 1.0848e-05 | -0.00033474
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1374 | BB-1374 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1367 | BB-1367 | 0.93965 | 64.8362 | 0.93968 | 64.8378 | 2.3127e-05 | -0.00032246
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1367 | BB-1367 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1339 | BB-1339 | 0.93965 | 64.8362 | 0.93965 | 64.8355 | -9.1195e-06 | -0.00035471
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1339 | BB-1339 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1308 | BB-1308 | 0.93965 | 64.8362 | 0.93971 | 64.8397 | 5.1439e-05 | -0.00029415
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1308 | BB-1308 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1338 | BB-1338 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 1.0133e-06 | -0.00034457
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1338 | BB-1338 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1404 | BB-1404 | 0.93965 | 64.8362 | 0.93976 | 64.8433 | 0.00010306 | -0.00024253
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1404 | BB-1404 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1442 | BB-1442 | 0.93965 | 64.8362 | 0.93966 | 64.8365 | 5.1856e-06 | -0.0003404
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1442 | BB-1442 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1513 | BB-1513 | 0.93965 | 64.8362 | 0.93974 | 64.8421 | 8.6844e-05 | -0.00025874
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1513 | BB-1513 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1408 | BB-1408 | 0.93965 | 64.8362 | 0.93967 | 64.8373 | 1.6212e-05 | -0.00032938
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1408 | BB-1408 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1286 | BB-1286 | 0.93965 | 64.8362 | 0.93983 | 64.8481 | 0.00017363 | -0.00017196
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1286 | BB-1286 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1365 | BB-1365 | 0.93965 | 64.8362 | 0.93961 | 64.8328 | -4.9055e-05 | -0.00039464
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1486 | BB-1486 | 0.93965 | 64.8362 | 0.93973 | 64.8411 | 7.1585e-05 | -0.000274
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1486 | BB-1486 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1322 | BB-1322 | 0.93965 | 64.8362 | 0.93964 | 64.8355 | -1.0073e-05 | -0.00035566
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1322 | BB-1322 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1379 | BB-1379 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -2.3842e-07 | -0.00034583
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1379 | BB-1379 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1391 | BB-1391 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 2.3246e-06 | -0.00034326
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1391 | BB-1391 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1403 | BB-1403 | 0.93965 | 64.8362 | 0.93967 | 64.8373 | 1.7166e-05 | -0.00032842
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1403 | BB-1403 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1390 | BB-1390 | 0.93965 | 64.8362 | 0.93966 | 64.8367 | 7.8678e-06 | -0.00033772
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1390 | BB-1390 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1425 | BB-1425 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 3.5167e-06 | -0.00034207
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1425 | BB-1425 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1436 | BB-1436 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 3.0994e-06 | -0.00034249
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1436 | BB-1436 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1321 | BB-1321 | 0.93965 | 64.8362 | 0.93964 | 64.8349 | -1.7762e-05 | -0.00036335
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1321 | BB-1321 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1343 | BB-1343 | 0.93965 | 64.8362 | 0.93972 | 64.8405 | 6.3539e-05 | -0.00028205
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1343 | BB-1343 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1300 | BB-1300 | 0.93965 | 64.8362 | 0.93967 | 64.837 | 1.2457e-05 | -0.00033313
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1300 | BB-1300 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1294 | BB-1294 | 0.93965 | 64.8362 | 0.93969 | 64.8385 | 3.3379e-05 | -0.00031221
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1294 | BB-1294 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1327 | BB-1327 | 0.93965 | 64.8362 | 0.9396 | 64.8324 | -5.4896e-05 | -0.00040048
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1327 | BB-1327 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1336 | BB-1336 | 0.93965 | 64.8362 | 0.93973 | 64.8414 | 7.5519e-05 | -0.00027007
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1336 | BB-1336 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1446 | BB-1446 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1514 | BB-1514 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1345 | BB-1345 | 0.93965 | 64.8362 | 0.93955 | 64.8293 | -9.9838e-05 | -0.00044543
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1345 | BB-1345 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1361 | BB-1361 | 0.93965 | 64.8362 | 0.93955 | 64.8292 | -0.00010091 | -0.0004465
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1361 | BB-1361 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-3000 | BB-3000 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 2.1458e-06 | -0.00034344
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-3000 | BB-3000 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1337 | BB-1337 | 0.93965 | 64.8362 | 0.93966 | 64.8366 | 5.8413e-06 | -0.00033975
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1337 | BB-1337 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1432 | BB-1432 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 4.1723e-07 | -0.00034517
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1461 | BB-1461 | 0.93965 | 64.8362 | 0.93967 | 64.837 | 1.204e-05 | -0.00033355
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1461 | BB-1461 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1353 | BB-1353 | 0.93965 | 64.8362 | 0.93968 | 64.8378 | 2.3544e-05 | -0.00032204
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1353 | BB-1353 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1457 | BB-1457 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 3.2187e-06 | -0.00034237
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1457 | BB-1457 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-69-41 | B-69-41 | 0.93965 | 64.8362 | 0.93966 | 64.8368 | 9.7156e-06 | -0.00033587
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-69-41 | B-69-41 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1299 | BB-1299 | 0.93965 | 64.8362 | 0.93966 | 64.8367 | 7.8082e-06 | -0.00033778
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1299 | BB-1299 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1428 | BB-1428 | 0.93965 | 64.8362 | 0.93968 | 64.8378 | 2.408e-05 | -0.00032151
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1428 | BB-1428 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1428A | BB-1428A | 0.93965 | 64.8362 | 0.93968 | 64.8378 | 2.408e-05 | -0.00032151
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1428A | BB-1428A | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-69-40 | B-69-40 | 0.93965 | 64.8362 | 0.93967 | 64.837 | 1.1921e-05 | -0.00033367
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-69-40 | B-69-40 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1464 | BB-1464 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 1.3709e-06 | -0.00034422
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1464 | BB-1464 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1410 | BB-1410 | 0.93965 | 64.8362 | 0.93966 | 64.8365 | 4.6492e-06 | -0.00034094
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1410 | BB-1410 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1326 | BB-1326 | 0.93965 | 64.8362 | 0.93966 | 64.8366 | 5.9009e-06 | -0.00033969
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1326 | BB-1326 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1406 | BB-1406 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 1.9073e-06 | -0.00034368
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1406 | BB-1406 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-69-42 | B-69-42 | 0.93965 | 64.8362 | 0.93968 | 64.8379 | 2.5988e-05 | -0.0003196
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-69-42 | B-69-42 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1399 | BB-1399 | 0.93965 | 64.8362 | 0.93975 | 64.8426 | 9.352e-05 | -0.00025207
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1399 | BB-1399 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1346 | BB-1346 | 0.93965 | 64.8362 | 0.93975 | 64.843 | 9.9123e-05 | -0.00024647
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1346 | BB-1346 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-69-78 | B-69-78 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -1.8477e-06 | -0.00034744
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-69-78 | B-69-78 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1332 | BB-1332 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 4.1723e-07 | -0.00034517
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1332 | BB-1332 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1402 | BB-1402 | 0.93965 | 64.8362 | 0.93965 | 64.8357 | -6.4969e-06 | -0.00035208
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1402 | BB-1402 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1398 | BB-1398 | 0.93965 | 64.8362 | 0.93966 | 64.8368 | 8.8811e-06 | -0.00033671
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1398 | BB-1398 | 1.05 | 525 | 1.05 | 525 | 1.1921e-07 | 1.1921e-07
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1453 | BB-1453 | 0.93965 | 64.8362 | 0.93966 | 64.8365 | 5.722e-06 | -0.00033987
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1453 | BB-1453 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1274 | BB-1274 | 0.93965 | 64.8362 | 0.93964 | 64.835 | -1.663e-05 | -0.00036222
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1274 | BB-1274 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1277 | BB-1277 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 1.2517e-06 | -0.00034434
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1277 | BB-1277 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1289 | BB-1289 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 7.7486e-07 | -0.00034481
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1289 | BB-1289 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1328 | BB-1328 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.1921e-07 | -0.00034571
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1328 | BB-1328 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1272 | BB-1272 | 0.93965 | 64.8362 | 0.93971 | 64.8402 | 5.8413e-05 | -0.00028718
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1272 | BB-1272 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-69-45 | B-69-45 | 0.93965 | 64.8362 | 0.93959 | 64.8316 | -6.5625e-05 | -0.00041121
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-69-45 | B-69-45 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1512 | BB-1512 | 0.93965 | 64.8362 | 0.93964 | 64.8354 | -1.1444e-05 | -0.00035703
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1512 | BB-1512 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1470 | BB-1470 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -1.6689e-06 | -0.00034726
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1470 | BB-1470 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1430 | BB-1430 | 0.93965 | 64.8362 | 0.93967 | 64.8371 | 1.2994e-05 | -0.00033259
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1430 | BB-1430 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1450 | BB-1450 | 0.93965 | 64.8362 | 0.93971 | 64.8399 | 5.4836e-05 | -0.00029075
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1450 | BB-1450 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1424 | BB-1424 | 0.93965 | 64.8362 | 0.9397 | 64.8392 | 4.4525e-05 | -0.00030106
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1424 | BB-1424 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1393 | BB-1393 | 0.93965 | 64.8362 | 0.93966 | 64.8368 | 9.1791e-06 | -0.00033641
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1393 | BB-1393 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1392 | BB-1392 | 0.93965 | 64.8362 | 0.93965 | 64.8358 | -5.1856e-06 | -0.00035077
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1392 | BB-1392 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1375 | BB-1375 | 0.93965 | 64.8362 | 0.93966 | 64.8366 | 6.2585e-06 | -0.00033933
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1375 | BB-1375 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-69-136 | B-69-136 | 0.93965 | 64.8362 | 0.93971 | 64.8397 | 5.1379e-05 | -0.00029421
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-69-136 | B-69-136 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-69-137 | B-69-137 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 3.3975e-06 | -0.00034219
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-69-137 | B-69-137 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-69-140 | B-69-140 | 0.93965 | 64.8362 | 0.93965 | 64.8357 | -6.9141e-06 | -0.0003525
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-69-140 | B-69-140 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-69-141 | B-69-141 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -3.5763e-07 | -0.00034595
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-69-141 | B-69-141 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1364 | BB-1364 | 0.93965 | 64.8362 | 0.93956 | 64.8298 | -9.2208e-05 | -0.0004378
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1364 | BB-1364 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1355 | BB-1355 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -2.1458e-06 | -0.00034773
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1355 | BB-1355 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1354 | BB-1354 | 0.93965 | 64.8362 | 0.93967 | 64.8375 | 2.0146e-05 | -0.00032544
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1354 | BB-1354 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1270 | BB-1270 | 0.93965 | 64.8362 | 0.93965 | 64.8358 | -4.4107e-06 | -0.00035
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1270 | BB-1270 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1271 | BB-1271 | 0.93965 | 64.8362 | 0.93965 | 64.8359 | -4.2915e-06 | -0.00034988
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1271 | BB-1271 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1275 | BB-1275 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 3.0994e-06 | -0.00034249
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1275 | BB-1275 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | PRIN-KYD-PAD | PRIN-KYD-PAD | 0.93965 | 64.8362 | 0.93966 | 64.8367 | 7.9274e-06 | -0.00033766
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | PRIN-KYD-PAD | PRIN-KYD-PAD | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-69-46 | B-69-46 | 0.93965 | 64.8362 | 0.93959 | 64.8317 | -6.3896e-05 | -0.00040948
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-69-46 | B-69-46 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | P1-1000 | P1-1000 | 0.93965 | 64.8362 | 0.93989 | 64.8525 | 0.00023758 | -0.000108
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | P1-1000 | P1-1000 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | P1-1001 | P1-1001 | 0.93965 | 64.8362 | 0.93966 | 64.8366 | 6.3777e-06 | -0.00033921
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | P1-1001 | P1-1001 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-69-25 | B-69-25 | 0.93965 | 64.8362 | 0.93967 | 64.8373 | 1.5974e-05 | -0.00032961
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-69-25 | B-69-25 | 1.05 | 525 | 1.05 | 525 | 0 | 0
324903 | 2MCKEE ROAD | 69 | LGEE' | RANGE | 0.94 | 1.06 | B-69-25 | B-69-25 | 0.98332 | 67.8489 | 0.93755 | 64.6907 | -0.045771 | -0.0024538
324950 | 2SCIENC HILL | 69 | LGEE' | RANGE | 0.94 | 1.06 | B-69-25 | B-69-25 | 0.97943 | 67.5807 | 0.93344 | 64.4074 | -0.04599 | -0.0065587
324965 | 2SOMERSET NO | 69 | LGEE' | RANGE | 0.94 | 1.06 | B-69-25 | B-69-25 | 0.98322 | 67.8425 | 0.93745 | 64.6839 | -0.045777 | -0.0025523
324995 | 2WAYNESBURG | 69 | LGEE' | RANGE | 0.94 | 1.06 | B-69-25 | B-69-25 | 0.97445 | 67.2368 | 0.92818 | 64.0447 | -0.046262 | -0.011816
325084 | 2FLOYD EKP T | 69 | LGEE' | RANGE | 0.94 | 1.06 | B-69-25 | B-69-25 | 0.97663 | 67.3872 | 0.93048 | 64.2029 | -0.046149 | -0.0095228
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1164 | BB-1164 | 0.93965 | 64.8362 | 0.93957 | 64.8306 | -8.1182e-05 | -0.00042677
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1164 | BB-1164 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1097 | BB-1097 | 0.93965 | 64.8362 | 0.9395 | 64.8253 | -0.00015712 | -0.00050271
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1097 | BB-1097 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-138-114 | B-138-114 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-138-119 | B-138-119 | 0.93965 | 64.8362 | 0.93973 | 64.8414 | 7.6294e-05 | -0.00026929
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-138-119 | B-138-119 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-138-113 | B-138-113 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-138-118 | B-138-118 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1179 | BB-1179 | 0.93965 | 64.8362 | 0.93985 | 64.8496 | 0.00019437 | -0.00015122
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1179 | BB-1179 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1192 | BB-1192 | 0.93965 | 64.8362 | 0.93947 | 64.8237 | -0.00018013 | -0.00052571
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1192 | BB-1192 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1201 | BB-1201 | 0.93965 | 64.8362 | 0.93954 | 64.8284 | -0.00011206 | -0.00045764
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1201 | BB-1201 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1203 | BB-1203 | 0.93965 | 64.8362 | 0.93943 | 64.8204 | -0.000229 | -0.00057459
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1203 | BB-1203 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1240 | BB-1240 | 0.93965 | 64.8362 | 0.93954 | 64.8283 | -0.0001142 | -0.00045979
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1240 | BB-1240 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-138-122 | B-138-122 | 0.93965 | 64.8362 | 0.93925 | 64.8079 | -0.00040907 | -0.00075465
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-138-122 | B-138-122 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1143 | BB-1143 | 0.93965 | 64.8362 | 0.93935 | 64.8153 | -0.00030231 | -0.0006479
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1143 | BB-1143 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1049 | BB-1049 | 0.93965 | 64.8362 | 0.93971 | 64.84 | 5.5492e-05 | -0.0002901
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1049 | BB-1049 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-138-111 | B-138-111 | 0.93965 | 64.8362 | 0.93964 | 64.8349 | -1.8418e-05 | -0.00036401
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-161-125 | B-161-125 | 0.93965 | 64.8362 | 0.9396 | 64.8321 | -5.9307e-05 | -0.00040489
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-161-125 | B-161-125 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-138-21 | B-138-21 | 0.93965 | 64.8362 | 0.93963 | 64.8348 | -2.0266e-05 | -0.00036585
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-138-21 | B-138-21 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1133 | BB-1133 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 5.9605e-07 | -0.00034499
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1133 | BB-1133 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-161-126 | B-161-126 | 0.93965 | 64.8362 | 0.93962 | 64.8335 | -3.8207e-05 | -0.00038379
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-161-126 | B-161-126 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1063 | BB-1063 | 0.93965 | 64.8362 | 0.93964 | 64.8352 | -1.4126e-05 | -0.00035971
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1063 | BB-1063 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-161-24 | B-161-24 | 0.93965 | 64.8362 | 0.93951 | 64.8263 | -0.00014257 | -0.00048816
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-161-24 | B-161-24 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-161-23 | B-161-23 | 0.93965 | 64.8362 | 0.93963 | 64.8344 | -2.557e-05 | -0.00037116
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-161-23 | B-161-23 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-161-124 | B-161-124 | 0.93965 | 64.8362 | 0.93961 | 64.8332 | -4.3392e-05 | -0.00038898
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-161-124 | B-161-124 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1509 | BB-1509 | 0.93965 | 64.8362 | 0.93994 | 64.8555 | 0.00028074 | -6.485e-05
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1509 | BB-1509 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-138-112 | B-138-112 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 1.7881e-06 | -0.0003438
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-138-112 | B-138-112 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1239 | BB-1239 | 0.93965 | 64.8362 | 0.93921 | 64.8053 | -0.00044656 | -0.00079215
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1239 | BB-1239 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1216 | BB-1216 | 0.93965 | 64.8362 | 0.93963 | 64.8345 | -2.4438e-05 | -0.00037003
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1216 | BB-1216 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1019 | BB-1019 | 0.93965 | 64.8362 | 0.9388 | 64.7772 | -0.00085384 | -0.0011994
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1019 | BB-1019 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-138-97 | B-138-97 | 0.93965 | 64.8362 | 0.93898 | 64.7894 | -0.00067747 | -0.0010231
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-138-97 | B-138-97 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-161-108 | B-161-108 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -1.6093e-06 | -0.0003472
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-161-108 | B-161-108 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1057 | BB-1057 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 2.3842e-07 | -0.00034535
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1057 | BB-1057 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-161-106 | B-161-106 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 1.7285e-06 | -0.00034386
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-161-106 | B-161-106 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-161-128 | B-161-128 | 0.93965 | 64.8362 | 0.93963 | 64.8345 | -2.4319e-05 | -0.00036991
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-161-128 | B-161-128 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-69-18 | B-69-18 | 0.93965 | 64.8362 | 0.93959 | 64.832 | -5.9605e-05 | -0.00040519
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-69-18 | B-69-18 | 1.05 | 525 | 1.05 | 525 | 0 | 0
324604 | 2LEBANON IND | 69 | LGEE' | RANGE | 0.94 | 1.06 | B-69-18 | B-69-18 | 1.0065 | 69.451 | 0.9391 | 64.7978 | -0.067437 | -0.00090122
325020 | 2LEBANON E | 69 | LGEE' | RANGE | 0.94 | 1.06 | B-69-18 | B-69-18 | 1.0055 | 69.3804 | 0.938 | 64.7222 | -0.067511 | -0.0019975
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-69-19 | B-69-19 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -6.5565e-07 | -0.00034624
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-69-19 | B-69-19 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-138-28 | B-138-28 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 1.5497e-06 | -0.00034404
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-138-28 | B-138-28 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1228 | BB-1228 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 1.3113e-06 | -0.00034428
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1228 | BB-1228 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1229 | BB-1229 | 0.93965 | 64.8362 | 0.93966 | 64.8366 | 6.7353e-06 | -0.00033885
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1229 | BB-1229 | 1.05 | 525 | 1.05 | 525 | 1.1921e-07 | 1.1921e-07
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1066 | BB-1066 | 0.93965 | 64.8362 | 0.93962 | 64.834 | -3.1888e-05 | -0.00037748
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1066 | BB-1066 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1026 | BB-1026 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 4.0531e-06 | -0.00034153
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1026 | BB-1026 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-345-475 | B-345-475 | 0.93965 | 64.8362 | 0.93962 | 64.8337 | -3.6001e-05 | -0.00038159
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-345-475 | B-345-475 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1139 | BB-1139 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 5.9605e-08 | -0.00034553
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1139 | BB-1139 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-138-130 | B-138-130 | 0.93965 | 64.8362 | 0.9397 | 64.839 | 4.1902e-05 | -0.00030369
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-138-130 | B-138-130 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-138-12 | B-138-12 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-69-13 | B-69-13 | 0.93965 | 64.8362 | 0.93842 | 64.7508 | -0.0012364 | -0.001582
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-69-13 | B-69-13 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-69-15 | B-69-15 | 0.93965 | 64.8362 | 0.93954 | 64.8285 | -0.00011063 | -0.00045621
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-69-15 | B-69-15 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-69-20 | B-69-20 | 0.93965 | 64.8362 | 0.93963 | 64.8347 | -2.116e-05 | -0.00036675
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-69-20 | B-69-20 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-69-26 | B-69-26 | 0.93965 | 64.8362 | 0.93972 | 64.8407 | 6.5625e-05 | -0.00027996
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-69-26 | B-69-26 | 1.05 | 525 | 1.05 | 525 | 1.1921e-07 | 1.1921e-07
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-69-29 | B-69-29 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 1.9073e-06 | -0.00034368
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-69-29 | B-69-29 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-69-30 | B-69-30 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.1325e-06 | -0.00034672
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-69-30 | B-69-30 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-69-31 | B-69-31 | 0.93965 | 64.8362 | 0.93966 | 64.8365 | 4.828e-06 | -0.00034076
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-69-31 | B-69-31 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1205 | BB-1205 | 0.93965 | 64.8362 | 0.93966 | 64.8365 | 5.3644e-06 | -0.00034022
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1205 | BB-1205 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1187 | BB-1187 | 0.93965 | 64.8362 | 0.93966 | 64.8365 | 5.6028e-06 | -0.00033998
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1187 | BB-1187 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1136 | BB-1136 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.0729e-06 | -0.00034666
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1112 | BB-1112 | 0.93965 | 64.8362 | 0.93966 | 64.8367 | 7.3314e-06 | -0.00033826
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1112 | BB-1112 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1098 | BB-1098 | 0.93965 | 64.8362 | 0.93967 | 64.8371 | 1.4424e-05 | -0.00033116
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1098 | BB-1098 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1075 | BB-1075 | 0.93965 | 64.8362 | 0.93963 | 64.8345 | -2.4498e-05 | -0.00037009
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1075 | BB-1075 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1062 | BB-1062 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.2517e-06 | -0.00034684
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1062 | BB-1062 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1060 | BB-1060 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 3.9935e-06 | -0.00034159
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1060 | BB-1060 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1061 | BB-1061 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 2.7418e-06 | -0.00034285
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1061 | BB-1061 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-69-135 | B-69-135 | 0.93965 | 64.8362 | 0.93958 | 64.8307 | -7.9334e-05 | -0.00042492
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-69-135 | B-69-135 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-69-132 | B-69-132 | 0.93965 | 64.8362 | 0.93963 | 64.8347 | -2.0504e-05 | -0.00036609
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-69-132 | B-69-132 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-138-120 | B-138-120 | 0.93965 | 64.8362 | 0.93965 | 64.8358 | -4.8876e-06 | -0.00035048
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-138-120 | B-138-120 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-138-121 | B-138-121 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 1.967e-06 | -0.00034362
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-138-121 | B-138-121 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-138-109 | B-138-109 | 0.93965 | 64.8362 | 0.93964 | 64.835 | -1.651e-05 | -0.0003621
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-138-109 | B-138-109 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1226 | BB-1226 | 0.93965 | 64.8362 | 0.93964 | 64.8352 | -1.4126e-05 | -0.00035971
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1226 | BB-1226 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1001 | BB-1001 | 0.93965 | 64.8362 | 0.93963 | 64.8344 | -2.5809e-05 | -0.0003714
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1001 | BB-1001 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-345-100 | B-345-100 | 0.93965 | 64.8362 | 0.9395 | 64.8257 | -0.00015122 | -0.0004968
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-345-100 | B-345-100 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-161-107 | B-161-107 | 0.93965 | 64.8362 | 0.93968 | 64.8382 | 2.9385e-05 | -0.0003162
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-161-107 | B-161-107 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-138-110 | B-138-110 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -8.3447e-07 | -0.00034642
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-138-110 | B-138-110 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-138-117 | B-138-117 | 0.93965 | 64.8362 | 0.93953 | 64.8273 | -0.00012767 | -0.00047326
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-138-117 | B-138-117 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-161-84 | B-161-84 | 0.93965 | 64.8362 | 0.93967 | 64.8369 | 1.1027e-05 | -0.00033456
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-161-84 | B-161-84 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-138-116 | B-138-116 | 0.93965 | 64.8362 | 0.93978 | 64.8446 | 0.00012219 | -0.0002234
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-138-116 | B-138-116 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-345-101 | B-345-101 | 0.93965 | 64.8362 | 0.93964 | 64.8351 | -1.4961e-05 | -0.00036055
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-345-101 | B-345-101 | 1.05 | 525 | 1.05 | 525 | 0 | 0
324915 | 2MT WAS EK J | 69 | LGEE' | RANGE | 0.94 | 1.06 | B-345-101 | B-345-101 | 0.94997 | 65.5482 | 0.91909 | 63.417 | -0.030887 | -0.020912
325006 | 2W MT WSH EK | 69 | LGEE' | RANGE | 0.94 | 1.06 | B-345-101 | B-345-101 | 0.95952 | 66.2066 | 0.92896 | 64.0979 | -0.030561 | -0.011044
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-345-102 | B-345-102 | 0.93965 | 64.8362 | 0.93968 | 64.8382 | 2.9504e-05 | -0.00031608
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-345-102 | B-345-102 | 1.05 | 525 | 1.05 | 525 | 0 | 0
324915 | 2MT WAS EK J | 69 | LGEE' | RANGE | 0.94 | 1.06 | B-345-102 | B-345-102 | 0.94997 | 65.5482 | 0.93982 | 64.8474 | -0.010157 | -0.00018287
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-69-133 | B-69-133 | 0.93965 | 64.8362 | 0.9394 | 64.8183 | -0.00025868 | -0.00060427
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-69-133 | B-69-133 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1074 | BB-1074 | 0.93965 | 64.8362 | 0.93953 | 64.8274 | -0.00012642 | -0.00047201
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1074 | BB-1074 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1132 | BB-1132 | 0.93965 | 64.8362 | 0.93915 | 64.8015 | -0.00050205 | -0.00084764
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1132 | BB-1132 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1218 | BB-1218 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 1.1921e-07 | -0.00034547
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1218 | BB-1218 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-2021 | BB-2021 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | BB-1245B | BB-1245B | 0.93965 | 64.8362 | 0.93966 | 64.8365 | 5.0664e-06 | -0.00034052
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | BB-1245B | BB-1245B | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-69-35 | B-69-35 | 0.93965 | 64.8362 | 0.93964 | 64.8349 | -1.7524e-05 | -0.00036311
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-69-35 | B-69-35 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-69-32 | B-69-32 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 3.9935e-06 | -0.00034159
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-69-32 | B-69-32 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | B-69-33 | B-69-33 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.0729e-06 | -0.00034666
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | B-69-33 | B-69-33 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | P1-1002 | P1-1002 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | P1-2-1004 | P1-2-1004 | 0.93965 | 64.8362 | 0.93966 | 64.8366 | 6.1989e-06 | -0.00033939
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | P1-2-1004 | P1-2-1004 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | P1-2-1005 | P1-2-1005 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -4.7684e-07 | -0.00034606
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | P1-2-1005 | P1-2-1005 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1986 242691-243088(1) | OPEN LINE FROM BUS 242691 [05KENOVA 138.00] TO BUS 243088 [05S.POINT1 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93962 | 64.8337 | -3.5703e-05 | -0.00038129
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1986 242691-243088(1) | OPEN LINE FROM BUS 242691 [05KENOVA 138.00] TO BUS 243088 [05S.POINT1 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1987 242927-242938(1) | OPEN LINE FROM BUS 242927 [05MARQUI 765.00] TO BUS 242938 [05MARQUI 345.00] CKT 1 | 0.93965 | 64.8362 | 0.93923 | 64.8067 | -0.00042737 | -0.00077295
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1987 242927-242938(1) | OPEN LINE FROM BUS 242927 [05MARQUI 765.00] TO BUS 242938 [05MARQUI 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1988 242938-243034(2) | OPEN LINE FROM BUS 242938 [05MARQUI 345.00] TO BUS 243034 [05MARQUI 138.00] CKT 2 | 0.93965 | 64.8362 | 0.93959 | 64.832 | -5.9783e-05 | -0.00040537
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1988 242938-243034(2) | OPEN LINE FROM BUS 242938 [05MARQUI 345.00] TO BUS 243034 [05MARQUI 138.00] CKT 2 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1989 242938-243034(3) | OPEN LINE FROM BUS 242938 [05MARQUI 345.00] TO BUS 243034 [05MARQUI 138.00] CKT 3 | 0.93965 | 64.8362 | 0.93959 | 64.832 | -5.9485e-05 | -0.00040507
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1989 242938-243034(3) | OPEN LINE FROM BUS 242938 [05MARQUI 345.00] TO BUS 243034 [05MARQUI 138.00] CKT 3 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1990 242938-246888(1) | OPEN LINE FROM BUS 242938 [05MARQUI 345.00] TO BUS 246888 [05BIERSR 345.00] CKT 1 | 0.93965 | 64.8362 | 0.93954 | 64.8284 | -0.00011194 | -0.00045753
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1990 242938-246888(1) | OPEN LINE FROM BUS 242938 [05MARQUI 345.00] TO BUS 246888 [05BIERSR 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1991 242982-243047(1) | OPEN LINE FROM BUS 242982 [05CENPOR 138.00] TO BUS 243047 [05N PORT 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8357 | -7.093e-06 | -0.00035268
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1991 242982-243047(1) | OPEN LINE FROM BUS 242982 [05CENPOR 138.00] TO BUS 243047 [05N PORT 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1992 242988-242992(1) | OPEN LINE FROM BUS 242988 [05DOGWOO 138.00] TO BUS 242992 [05E WHEE 138.00] CKT 1 | 0.93965 | 64.8362 | 0.9397 | 64.8395 | 4.8518e-05 | -0.00029707
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1992 242988-242992(1) | OPEN LINE FROM BUS 242988 [05DOGWOO 138.00] TO BUS 242992 [05E WHEE 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1993 242988-243042(1) | OPEN LINE FROM BUS 242988 [05DOGWOO 138.00] TO BUS 243042 [05MILLBR PK1138.00] CKT 1 | 0.93965 | 64.8362 | 0.93972 | 64.8404 | 6.1333e-05 | -0.00028425
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1993 242988-243042(1) | OPEN LINE FROM BUS 242988 [05DOGWOO 138.00] TO BUS 243042 [05MILLBR PK1138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1994 243013-243069(1) | OPEN LINE FROM BUS 243013 [05GAVIN1 138.00] TO BUS 243069 [05FIREBR 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8359 | -3.159e-06 | -0.00034875
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1994 243013-243069(1) | OPEN LINE FROM BUS 243013 [05GAVIN1 138.00] TO BUS 243069 [05FIREBR 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1995 243019-243102(1) | OPEN LINE FROM BUS 243019 [05HILLSB 138.00] TO BUS 243102 [05SINK SP8SS138.00] CKT 1 | 0.93965 | 64.8362 | 0.93963 | 64.8345 | -2.3663e-05 | -0.00036925
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1995 243019-243102(1) | OPEN LINE FROM BUS 243019 [05HILLSB 138.00] TO BUS 243102 [05SINK SP8SS138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1996 243042-243047(1) | OPEN LINE FROM BUS 243042 [05MILLBR PK1138.00] TO BUS 243047 [05N PORT 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8355 | -9.3579e-06 | -0.00035495
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1996 243042-243047(1) | OPEN LINE FROM BUS 243042 [05MILLBR PK1138.00] TO BUS 243047 [05N PORT 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1997 243042-243069(1) | OPEN LINE FROM BUS 243042 [05MILLBR PK1138.00] TO BUS 243069 [05FIREBR 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93968 | 64.8378 | 2.3246e-05 | -0.00032234
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1997 243042-243069(1) | OPEN LINE FROM BUS 243042 [05MILLBR PK1138.00] TO BUS 243069 [05FIREBR 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1998 243042-243173(5) | OPEN LINE FROM BUS 243042 [05MILLBR PK1138.00] TO BUS 243173 [05MILLBRK 69.000] CKT 5 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 2.861e-06 | -0.00034273
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1998 243042-243173(5) | OPEN LINE FROM BUS 243042 [05MILLBR PK1138.00] TO BUS 243173 [05MILLBRK 69.000] CKT 5 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1999 243047-243087(1) | OPEN LINE FROM BUS 243047 [05N PORT 138.00] TO BUS 243087 [05S LUCA 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93958 | 64.8311 | -7.2598e-05 | -0.00041819
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 1999 243047-243087(1) | OPEN LINE FROM BUS 243047 [05N PORT 138.00] TO BUS 243087 [05S LUCA 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2000 243047-243819(1) | OPEN LINE FROM BUS 243047 [05N PORT 138.00] TO BUS 243819 [05N PORTSM 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -1.8477e-06 | -0.00034744
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2000 243047-243819(1) | OPEN LINE FROM BUS 243047 [05N PORT 138.00] TO BUS 243819 [05N PORTSM 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2001 243069-246782(1) | OPEN LINE FROM BUS 243069 [05FIREBR 138.00] TO BUS 246782 [05FIREBRCK 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -2.8014e-06 | -0.00034839
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2001 243069-246782(1) | OPEN LINE FROM BUS 243069 [05FIREBR 138.00] TO BUS 246782 [05FIREBRCK 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2002 243088-243184(2) | OPEN LINE FROM BUS 243088 [05S.POINT1 138.00] TO BUS 243184 [05S POINT 34.500] CKT 2 | 0.93965 | 64.8362 | 0.93965 | 64.8357 | -6.6757e-06 | -0.00035226
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2002 243088-243184(2) | OPEN LINE FROM BUS 243088 [05S.POINT1 138.00] TO BUS 243184 [05S POINT 34.500] CKT 2 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2003 243167-243171(1) | OPEN LINE FROM BUS 243167 [05FRANKLIN 69.000] TO BUS 243171 [05HAYPRTRDSS69.000] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8351 | -1.4722e-05 | -0.00036031
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2003 243167-243171(1) | OPEN LINE FROM BUS 243167 [05FRANKLIN 69.000] TO BUS 243171 [05HAYPRTRDSS69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2004 243167-243178(1) | OPEN LINE FROM BUS 243167 [05FRANKLIN 69.000] TO BUS 243178 [05GINAT C SS69.000] CKT 1 | 0.93965 | 64.8362 | 0.93962 | 64.8335 | -3.8326e-05 | -0.00038391
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2004 243167-243178(1) | OPEN LINE FROM BUS 243167 [05FRANKLIN 69.000] TO BUS 243178 [05GINAT C SS69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2005 243167-243725(1) | OPEN LINE FROM BUS 243167 [05FRANKLIN 69.000] TO BUS 243725 [05GRAYSB 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93963 | 64.8346 | -2.1994e-05 | -0.00036758
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2005 243167-243725(1) | OPEN LINE FROM BUS 243167 [05FRANKLIN 69.000] TO BUS 243725 [05GRAYSB 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2006 243171-243183(1) | OPEN LINE FROM BUS 243171 [05HAYPRTRDSS69.000] TO BUS 243183 [05WHEELRBR 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8351 | -1.4722e-05 | -0.00036031
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2006 243171-243183(1) | OPEN LINE FROM BUS 243171 [05HAYPRTRDSS69.000] TO BUS 243183 [05WHEELRBR 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2007 243173-243181(1) | OPEN LINE FROM BUS 243173 [05MILLBRK 69.000] TO BUS 243181 [05SCIOTOVI 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -2.0266e-06 | -0.00034761
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2007 243173-243181(1) | OPEN LINE FROM BUS 243173 [05MILLBRK 69.000] TO BUS 243181 [05SCIOTOVI 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2008 243173-243597(1) | OPEN LINE FROM BUS 243173 [05MILLBRK 69.000] TO BUS 243597 [05ASHLEY 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -2.9206e-06 | -0.00034851
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2008 243173-243597(1) | OPEN LINE FROM BUS 243173 [05MILLBRK 69.000] TO BUS 243597 [05ASHLEY 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2009 243173-246916(1) | OPEN LINE FROM BUS 243173 [05MILLBRK 69.000] TO BUS 246916 [05CORNRSTN 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -2.9802e-07 | -0.00034589
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2009 243173-246916(1) | OPEN LINE FROM BUS 243173 [05MILLBRK 69.000] TO BUS 246916 [05CORNRSTN 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2010 243173-246917(1) | OPEN LINE FROM BUS 243173 [05MILLBRK 69.000] TO BUS 246917 [05RUHLMAN 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -4.7684e-07 | -0.00034606
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2010 243173-246917(1) | OPEN LINE FROM BUS 243173 [05MILLBRK 69.000] TO BUS 246917 [05RUHLMAN 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2011 243176-243178(1) | OPEN LINE FROM BUS 243176 [05N HAVERH 69.000] TO BUS 243178 [05GINAT C SS69.000] CKT 1 | 0.93965 | 64.8362 | 0.9396 | 64.8327 | -5.0545e-05 | -0.00039613
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2011 243176-243178(1) | OPEN LINE FROM BUS 243176 [05N HAVERH 69.000] TO BUS 243178 [05GINAT C SS69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2012 243178-247476(1) | OPEN LINE FROM BUS 243178 [05GINAT C SS69.000] TO BUS 247476 [05PLYMOUTHHT69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 2.9802e-06 | -0.00034261
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2012 243178-247476(1) | OPEN LINE FROM BUS 243178 [05GINAT C SS69.000] TO BUS 247476 [05PLYMOUTHHT69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2013 243181-243183(1) | OPEN LINE FROM BUS 243181 [05SCIOTOVI 69.000] TO BUS 243183 [05WHEELRBR 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8355 | -9.0599e-06 | -0.00035465
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2013 243181-243183(1) | OPEN LINE FROM BUS 243181 [05SCIOTOVI 69.000] TO BUS 243183 [05WHEELRBR 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2014 243618-247072(1) | OPEN LINE FROM BUS 243618 [05STUART 69.000] TO BUS 247072 [05RAVNSS 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93956 | 64.8298 | -9.191e-05 | -0.0004375
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2014 243618-247072(1) | OPEN LINE FROM BUS 243618 [05STUART 69.000] TO BUS 247072 [05RAVNSS 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2015 243656-243808(1) | OPEN LINE FROM BUS 243656 [05BEAVC1EQ 999.00] TO BUS 243808 [05BEAVERCR 46.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8357 | -6.3777e-06 | -0.00035197
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2015 243656-243808(1) | OPEN LINE FROM BUS 243656 [05BEAVC1EQ 999.00] TO BUS 243808 [05BEAVERCR 46.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2016 243657-243808(1) | OPEN LINE FROM BUS 243657 [05BEAVC2EQ 999.00] TO BUS 243808 [05BEAVERCR 46.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8358 | -5.6028e-06 | -0.00035119
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2016 243657-243808(1) | OPEN LINE FROM BUS 243657 [05BEAVC2EQ 999.00] TO BUS 243808 [05BEAVERCR 46.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2017 243663-243702(1) | OPEN LINE FROM BUS 243663 [05THELMAEQ 999.00] TO BUS 243702 [05THELMA 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93949 | 64.8248 | -0.00016385 | -0.00050944
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2017 243663-243702(1) | OPEN LINE FROM BUS 243663 [05THELMAEQ 999.00] TO BUS 243702 [05THELMA 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2018 243663-243750(1) | OPEN LINE FROM BUS 243663 [05THELMAEQ 999.00] TO BUS 243750 [05THELM1 69.000] CKT 1 | 0.93965 | 64.8362 | 0.9394 | 64.8188 | -0.00025094 | -0.00059652
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2018 243663-243750(1) | OPEN LINE FROM BUS 243663 [05THELMAEQ 999.00] TO BUS 243750 [05THELM1 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2020 243678-243679(1) | OPEN LINE FROM BUS 243678 [05BSANDX 138.00] TO BUS 243679 [05BUSSYV 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93918 | 64.8037 | -0.00047076 | -0.00081635
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2020 243678-243679(1) | OPEN LINE FROM BUS 243678 [05BSANDX 138.00] TO BUS 243679 [05BUSSYV 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2021 243679-243702(1) | OPEN LINE FROM BUS 243679 [05BUSSYV 138.00] TO BUS 243702 [05THELMA 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93919 | 64.8044 | -0.00046057 | -0.00080615
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2021 243679-243702(1) | OPEN LINE FROM BUS 243679 [05BUSSYV 138.00] TO BUS 243702 [05THELMA 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2022 243684-243702(1) | OPEN LINE FROM BUS 243684 [05DEWEY 138.00] TO BUS 243702 [05THELMA 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93982 | 64.8476 | 0.00016648 | -0.00017911
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2022 243684-243702(1) | OPEN LINE FROM BUS 243684 [05DEWEY 138.00] TO BUS 243702 [05THELMA 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2023 243684-243804(1) | OPEN LINE FROM BUS 243684 [05DEWEY 138.00] TO BUS 243804 [05DEWEY 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8357 | -6.5565e-06 | -0.00035214
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2023 243684-243804(1) | OPEN LINE FROM BUS 243684 [05DEWEY 138.00] TO BUS 243804 [05DEWEY 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2024 243684-244008(1) | OPEN LINE FROM BUS 243684 [05DEWEY 138.00] TO BUS 244008 [05STANVILLE1138.00] CKT 1 | 0.93965 | 64.8362 | 0.93974 | 64.842 | 8.4519e-05 | -0.00026107
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2024 243684-244008(1) | OPEN LINE FROM BUS 243684 [05DEWEY 138.00] TO BUS 244008 [05STANVILLE1138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2025 243688-244686(Z1) | OPEN LINE FROM BUS 243688 [05S.PORT MTR138.00] TO BUS 244686 [05VANCEBURG 138.00] CKT Z1 | 0.93965 | 64.8362 | 0.93967 | 64.8369 | 1.1265e-05 | -0.00033432
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2025 243688-244686(Z1) | OPEN LINE FROM BUS 243688 [05S.PORT MTR138.00] TO BUS 244686 [05VANCEBURG 138.00] CKT Z1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2026 243702-246971(1) | OPEN LINE FROM BUS 243702 [05THELMA 138.00] TO BUS 246971 [05THELM2 69.000] CKT 1 | 0.93965 | 64.8362 | 0.9396 | 64.8327 | -5.0724e-05 | -0.00039631
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2026 243702-246971(1) | OPEN LINE FROM BUS 243702 [05THELMA 138.00] TO BUS 246971 [05THELM2 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2027 243712-243716(1) | OPEN LINE FROM BUS 243712 [05CANNONSB 69.000] TO BUS 243716 [05COALTON 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8358 | -5.1856e-06 | -0.00035077
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2027 243712-243716(1) | OPEN LINE FROM BUS 243712 [05CANNONSB 69.000] TO BUS 243716 [05COALTON 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2028 243714-243727(1) | OPEN LINE FROM BUS 243714 [05CHAVIES 69.000] TO BUS 243727 [05HADDIX 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93959 | 64.8314 | -6.8903e-05 | -0.00041449
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2028 243714-243727(1) | OPEN LINE FROM BUS 243714 [05CHAVIES 69.000] TO BUS 243727 [05HADDIX 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2029 243716-243732(1) | OPEN LINE FROM BUS 243716 [05COALTON 69.000] TO BUS 243732 [05HITCHI 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93906 | 64.7951 | -0.00059456 | -0.00094014
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2029 243716-243732(1) | OPEN LINE FROM BUS 243716 [05COALTON 69.000] TO BUS 243732 [05HITCHI 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2030 243716-243743(1) | OPEN LINE FROM BUS 243716 [05COALTON 69.000] TO BUS 243743 [05PRINCESS 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93958 | 64.831 | -7.4148e-05 | -0.00041974
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2030 243716-243743(1) | OPEN LINE FROM BUS 243716 [05COALTON 69.000] TO BUS 243743 [05PRINCESS 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2031 243724-243737(1) | OPEN LINE FROM BUS 243724 [05GRAHN 69.000] TO BUS 243737 [05LEONKY 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93975 | 64.8426 | 9.2924e-05 | -0.00025266
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2031 243724-243737(1) | OPEN LINE FROM BUS 243724 [05GRAHN 69.000] TO BUS 243737 [05LEONKY 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2032 243724-243742(1) | OPEN LINE FROM BUS 243724 [05GRAHN 69.000] TO BUS 243742 [05CORYSS 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93979 | 64.8457 | 0.00013822 | -0.00020736
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2032 243724-243742(1) | OPEN LINE FROM BUS 243724 [05GRAHN 69.000] TO BUS 243742 [05CORYSS 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2033 243727-243734(1) | OPEN LINE FROM BUS 243727 [05HADDIX 69.000] TO BUS 243734 [05JACKSON 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93963 | 64.8343 | -2.7299e-05 | -0.00037289
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2033 243727-243734(1) | OPEN LINE FROM BUS 243727 [05HADDIX 69.000] TO BUS 243734 [05JACKSON 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2034 243728-243740(1) | OPEN LINE FROM BUS 243728 [05HAYWAR 69.000] TO BUS 243740 [05MOREHE 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93997 | 64.8576 | 0.00031066 | -3.4928e-05
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2034 243728-243740(1) | OPEN LINE FROM BUS 243728 [05HAYWAR 69.000] TO BUS 243740 [05MOREHE 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2035 243728-243741(1) | OPEN LINE FROM BUS 243728 [05HAYWAR 69.000] TO BUS 243741 [05OLIVEHIL 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93985 | 64.8498 | 0.00019741 | -0.00014818
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2035 243728-243741(1) | OPEN LINE FROM BUS 243728 [05HAYWAR 69.000] TO BUS 243741 [05OLIVEHIL 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2036 243732-243737(1) | OPEN LINE FROM BUS 243732 [05HITCHI 69.000] TO BUS 243737 [05LEONKY 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93929 | 64.8108 | -0.00036734 | -0.00071293
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2036 243732-243737(1) | OPEN LINE FROM BUS 243732 [05HITCHI 69.000] TO BUS 243737 [05LEONKY 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2037 243733-243812(1) | OPEN LINE FROM BUS 243733 [05INDEX 69.000] TO BUS 243812 [05LEE C 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93956 | 64.8299 | -9.0837e-05 | -0.00043643
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2037 243733-243812(1) | OPEN LINE FROM BUS 243733 [05INDEX 69.000] TO BUS 243812 [05LEE C 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2039 243734-243812(1) | OPEN LINE FROM BUS 243734 [05JACKSON 69.000] TO BUS 243812 [05LEE C 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93968 | 64.8381 | 2.7716e-05 | -0.00031787
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2039 243734-243812(1) | OPEN LINE FROM BUS 243734 [05JACKSON 69.000] TO BUS 243812 [05LEE C 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2041 243741-243742(1) | OPEN LINE FROM BUS 243741 [05OLIVEHIL 69.000] TO BUS 243742 [05CORYSS 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 3.8743e-06 | -0.00034171
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2041 243741-243742(1) | OPEN LINE FROM BUS 243741 [05OLIVEHIL 69.000] TO BUS 243742 [05CORYSS 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2042 243750-244632(1) | OPEN LINE FROM BUS 243750 [05THELM1 69.000] TO BUS 244632 [05W.PNTSVL 69.000] CKT 1 | 0.93965 | 64.8362 | 0.9394 | 64.8187 | -0.00025314 | -0.00059873
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2042 243750-244632(1) | OPEN LINE FROM BUS 243750 [05THELM1 69.000] TO BUS 244632 [05W.PNTSVL 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2043 243758-243759(1) | OPEN LINE FROM BUS 243758 [05MIDDLECR 46.000] TO BUS 243759 [05PRESTNSB 46.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8365 | 4.4703e-06 | -0.00034112
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2043 243758-243759(1) | OPEN LINE FROM BUS 243758 [05MIDDLECR 46.000] TO BUS 243759 [05PRESTNSB 46.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2044 243808-244592(1) | OPEN LINE FROM BUS 243808 [05BEAVERCR 46.000] TO BUS 244592 [05BURTON 46.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 2.4438e-06 | -0.00034314
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2044 243808-244592(1) | OPEN LINE FROM BUS 243808 [05BEAVERCR 46.000] TO BUS 244592 [05BURTON 46.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2045 243808-244616(1) | OPEN LINE FROM BUS 243808 [05BEAVERCR 46.000] TO BUS 244616 [05MCKINNEY 46.000] CKT 1 | 0.93965 | 64.8362 | 0.9396 | 64.8325 | -5.3108e-05 | -0.0003987
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2045 243808-244616(1) | OPEN LINE FROM BUS 243808 [05BEAVERCR 46.000] TO BUS 244616 [05MCKINNEY 46.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2046 244632-246970(1) | OPEN LINE FROM BUS 244632 [05W.PNTSVL 69.000] TO BUS 246970 [05MAYOTRL 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93946 | 64.8231 | -0.00018954 | -0.00053513
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2046 244632-246970(1) | OPEN LINE FROM BUS 244632 [05W.PNTSVL 69.000] TO BUS 246970 [05MAYOTRL 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2047 246970-246971(1) | OPEN LINE FROM BUS 246970 [05MAYOTRL 69.000] TO BUS 246971 [05THELM2 69.000] CKT 1 | 0.93965 | 64.8362 | 0.9395 | 64.8258 | -0.0001502 | -0.00049579
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2047 246970-246971(1) | OPEN LINE FROM BUS 246970 [05MAYOTRL 69.000] TO BUS 246971 [05THELM2 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2048 242691-242835(1) | OPEN LINE FROM BUS 242691 [05KENOVA 138.00] TO BUS 242835 [05TRISTA 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.1325e-06 | -0.00034672
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2048 242691-242835(1) | OPEN LINE FROM BUS 242691 [05KENOVA 138.00] TO BUS 242835 [05TRISTA 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2049 242691-244720(1) | OPEN LINE FROM BUS 242691 [05KENOVA 138.00] TO BUS 244720 [05KENOVA H 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8352 | -1.4544e-05 | -0.00036013
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2049 242691-244720(1) | OPEN LINE FROM BUS 242691 [05KENOVA 138.00] TO BUS 244720 [05KENOVA H 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2050 242918-244965(EQ) | OPEN LINE FROM BUS 242918 [05SPOIN4EQ 999.00] TO BUS 244965 [05S POINT 69.000] CKT EQ | 0.93965 | 64.8362 | 0.93965 | 64.8357 | -7.1526e-06 | -0.00035274
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2050 242918-244965(EQ) | OPEN LINE FROM BUS 242918 [05SPOIN4EQ 999.00] TO BUS 244965 [05S POINT 69.000] CKT EQ | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2051 242918-245615(4) | OPEN LINE FROM BUS 242918 [05SPOIN4EQ 999.00] TO BUS 245615 [05S.POINT2 138.00] CKT 4 | 0.93965 | 64.8362 | 0.93965 | 64.8357 | -7.2122e-06 | -0.0003528
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2051 242918-245615(4) | OPEN LINE FROM BUS 242918 [05SPOIN4EQ 999.00] TO BUS 245615 [05S.POINT2 138.00] CKT 4 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2052 242927-242924(1) | OPEN LINE FROM BUS 242927 [05MARQUI 765.00] TO BUS 242924 [05HANG R 765.00] CKT 1 | 0.93965 | 64.8362 | 0.93923 | 64.8066 | -0.00042892 | -0.0007745
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2052 242927-242924(1) | OPEN LINE FROM BUS 242927 [05MARQUI 765.00] TO BUS 242924 [05HANG R 765.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2053 242938-248005(1) | OPEN LINE FROM BUS 242938 [05MARQUI 345.00] TO BUS 248005 [06KYGER 345.00] CKT 1 | 0.93965 | 64.8362 | 0.93962 | 64.8341 | -2.9504e-05 | -0.00037509
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2053 242938-248005(1) | OPEN LINE FROM BUS 242938 [05MARQUI 345.00] TO BUS 248005 [06KYGER 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2054 242938-248005(2) | OPEN LINE FROM BUS 242938 [05MARQUI 345.00] TO BUS 248005 [06KYGER 345.00] CKT 2 | 0.93965 | 64.8362 | 0.93959 | 64.8316 | -6.5386e-05 | -0.00041097
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2054 242938-248005(2) | OPEN LINE FROM BUS 242938 [05MARQUI 345.00] TO BUS 248005 [06KYGER 345.00] CKT 2 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2055 242938-248013(1) | OPEN LINE FROM BUS 242938 [05MARQUI 345.00] TO BUS 248013 [06PIERCE 345.00] CKT 1 | 0.93965 | 64.8362 | 0.93897 | 64.7891 | -0.00068182 | -0.0010274
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2055 242938-248013(1) | OPEN LINE FROM BUS 242938 [05MARQUI 345.00] TO BUS 248013 [06PIERCE 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2056 242938-253077(1) | OPEN LINE FROM BUS 242938 [05MARQUI 345.00] TO BUS 253077 [09STUART 345.00] CKT 1 | 0.93965 | 64.8362 | 0.93955 | 64.829 | -0.00010318 | -0.00044876
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2056 242938-253077(1) | OPEN LINE FROM BUS 242938 [05MARQUI 345.00] TO BUS 253077 [09STUART 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2057 242982-243815(2) | OPEN LINE FROM BUS 242982 [05CENPOR 138.00] TO BUS 243815 [05CENPORTS 69.000] CKT 2 | 0.93965 | 64.8362 | 0.93965 | 64.8358 | -5.2452e-06 | -0.00035083
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2057 242982-243815(2) | OPEN LINE FROM BUS 242982 [05CENPOR 138.00] TO BUS 243815 [05CENPORTS 69.000] CKT 2 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2058 242992-243124(1) | OPEN LINE FROM BUS 242992 [05E WHEE 138.00] TO BUS 243124 [05TEXEAS 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93969 | 64.8385 | 3.3915e-05 | -0.00031167
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2058 242992-243124(1) | OPEN LINE FROM BUS 242992 [05E WHEE 138.00] TO BUS 243124 [05TEXEAS 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2059 242992-243968(1) | OPEN LINE FROM BUS 242992 [05E WHEE 138.00] TO BUS 243968 [05IRONWOODSS138.00] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8369 | 1.1325e-05 | -0.00033426
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2059 242992-243968(1) | OPEN LINE FROM BUS 242992 [05E WHEE 138.00] TO BUS 243968 [05IRONWOODSS138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2060 243013-242698(1) | OPEN LINE FROM BUS 243013 [05GAVIN1 138.00] TO BUS 242698 [05LAKIN 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93962 | 64.8339 | -3.3081e-05 | -0.00037867
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2060 243013-242698(1) | OPEN LINE FROM BUS 243013 [05GAVIN1 138.00] TO BUS 242698 [05LAKIN 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2061 243013-242807(1) | OPEN LINE FROM BUS 243013 [05GAVIN1 138.00] TO BUS 242807 [05SPORN 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93963 | 64.8342 | -2.8968e-05 | -0.00037456
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2061 243013-242807(1) | OPEN LINE FROM BUS 243013 [05GAVIN1 138.00] TO BUS 242807 [05SPORN 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2062 243013-243611(1) | OPEN LINE FROM BUS 243013 [05GAVIN1 138.00] TO BUS 243611 [05CARTWRT SS138.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8359 | -3.7551e-06 | -0.00034934
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2062 243013-243611(1) | OPEN LINE FROM BUS 243013 [05GAVIN1 138.00] TO BUS 243611 [05CARTWRT SS138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2063 243013-243766(ZC) | OPEN LINE FROM BUS 243013 [05GAVIN1 138.00] TO BUS 243766 [05LIGHTSTONL138.00] CKT ZC | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 0 | -0.00034559
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2063 243013-243766(ZC) | OPEN LINE FROM BUS 243013 [05GAVIN1 138.00] TO BUS 243766 [05LIGHTSTONL138.00] CKT ZC | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2064 243013-243766(ZD) | OPEN LINE FROM BUS 243013 [05GAVIN1 138.00] TO BUS 243766 [05LIGHTSTONL138.00] CKT ZD | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 0 | -0.00034559
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2064 243013-243766(ZD) | OPEN LINE FROM BUS 243013 [05GAVIN1 138.00] TO BUS 243766 [05LIGHTSTONL138.00] CKT ZD | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2065 243013-244949(1) | OPEN LINE FROM BUS 243013 [05GAVIN1 138.00] TO BUS 244949 [05GAVIN 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | -5.9605e-08 | -0.00034565
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2065 243013-244949(1) | OPEN LINE FROM BUS 243013 [05GAVIN1 138.00] TO BUS 244949 [05GAVIN 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2066 243013-244949(2) | OPEN LINE FROM BUS 243013 [05GAVIN1 138.00] TO BUS 244949 [05GAVIN 69.000] CKT 2 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | -5.9605e-08 | -0.00034565
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2066 243013-244949(2) | OPEN LINE FROM BUS 243013 [05GAVIN1 138.00] TO BUS 244949 [05GAVIN 69.000] CKT 2 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2067 243013-246324(Z1) | OPEN LINE FROM BUS 243013 [05GAVIN1 138.00] TO BUS 246324 [05GAVIN_CAP 138.00] CKT Z1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 0 | -0.00034559
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2067 243013-246324(Z1) | OPEN LINE FROM BUS 243013 [05GAVIN1 138.00] TO BUS 246324 [05GAVIN_CAP 138.00] CKT Z1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2068 243019-242787(1) | OPEN LINE FROM BUS 243019 [05HILLSB 138.00] TO BUS 242787 [05MIDDLEB SS138.00] CKT 1 | 0.93965 | 64.8362 | 0.93944 | 64.8212 | -0.00021636 | -0.00056195
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2068 243019-242787(1) | OPEN LINE FROM BUS 243019 [05HILLSB 138.00] TO BUS 242787 [05MIDDLEB SS138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2069 243019-246911(1) | OPEN LINE FROM BUS 243019 [05HILLSB 138.00] TO BUS 246911 [05HIGHLA 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93961 | 64.8332 | -4.2379e-05 | -0.00038797
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2069 243019-246911(1) | OPEN LINE FROM BUS 243019 [05HILLSB 138.00] TO BUS 246911 [05HIGHLA 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2070 243019-246946(1) | OPEN LINE FROM BUS 243019 [05HILLSB 138.00] TO BUS 246946 [05WLDCAT 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93899 | 64.7905 | -0.00066209 | -0.0010077
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2070 243019-246946(1) | OPEN LINE FROM BUS 243019 [05HILLSB 138.00] TO BUS 246946 [05WLDCAT 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2071 243019-249995(1) | OPEN LINE FROM BUS 243019 [05HILLSB 138.00] TO BUS 249995 [08CLINCO 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93987 | 64.8511 | 0.0002172 | -0.00012839
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2071 243019-249995(1) | OPEN LINE FROM BUS 243019 [05HILLSB 138.00] TO BUS 249995 [08CLINCO 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2072 243034-243501(1) | OPEN LINE FROM BUS 243034 [05MARQUI 138.00] TO BUS 243501 [05E.BEAV 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8354 | -1.1563e-05 | -0.00035715
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2072 243034-243501(1) | OPEN LINE FROM BUS 243034 [05MARQUI 138.00] TO BUS 243501 [05E.BEAV 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2073 243034-243544(2) | OPEN LINE FROM BUS 243034 [05MARQUI 138.00] TO BUS 243544 [05MILPRD 138.00] CKT 2 | 0.93965 | 64.8362 | 0.93958 | 64.8313 | -7.0751e-05 | -0.00041634
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2073 243034-243544(2) | OPEN LINE FROM BUS 243034 [05MARQUI 138.00] TO BUS 243544 [05MILPRD 138.00] CKT 2 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2074 243034-245632(1) | OPEN LINE FROM BUS 243034 [05MARQUI 138.00] TO BUS 245632 [05ARBOLES 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93948 | 64.8244 | -0.00017011 | -0.0005157
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2074 243034-245632(1) | OPEN LINE FROM BUS 243034 [05MARQUI 138.00] TO BUS 245632 [05ARBOLES 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2075 243042-245948(Z1) | OPEN LINE FROM BUS 243042 [05MILLBR PK1138.00] TO BUS 245948 [05MILLBR PK2138.00] CKT Z1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 0 | -0.00034559
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2075 243042-245948(Z1) | OPEN LINE FROM BUS 243042 [05MILLBR PK1138.00] TO BUS 245948 [05MILLBR PK2138.00] CKT Z1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2076 243042-245949(Z1) | OPEN LINE FROM BUS 243042 [05MILLBR PK1138.00] TO BUS 245949 [05MLBRPK_ARG138.00] CKT Z1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 0 | -0.00034559
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2076 243042-245949(Z1) | OPEN LINE FROM BUS 243042 [05MILLBR PK1138.00] TO BUS 245949 [05MLBRPK_ARG138.00] CKT Z1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2077 243064-242929(2) | OPEN LINE FROM BUS 243064 [05NPROCT 138.00] TO BUS 242929 [05NPROCT 765.00] CKT 2 | 0.93965 | 64.8362 | 0.93944 | 64.8213 | -0.00021583 | -0.00056142
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2077 243064-242929(2) | OPEN LINE FROM BUS 243064 [05NPROCT 138.00] TO BUS 242929 [05NPROCT 765.00] CKT 2 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2078 243064-242999(1) | OPEN LINE FROM BUS 243064 [05NPROCT 138.00] TO BUS 242999 [05EPROCT 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8359 | -2.9802e-06 | -0.00034857
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2078 243064-242999(1) | OPEN LINE FROM BUS 243064 [05NPROCT 138.00] TO BUS 242999 [05EPROCT 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2079 243064-243193(1) | OPEN LINE FROM BUS 243064 [05NPROCT 138.00] TO BUS 243193 [05VIKING SS 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8358 | -5.3048e-06 | -0.00035089
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2079 243064-243193(1) | OPEN LINE FROM BUS 243064 [05NPROCT 138.00] TO BUS 243193 [05VIKING SS 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2080 243064-243675(1) | OPEN LINE FROM BUS 243064 [05NPROCT 138.00] TO BUS 243675 [05BELLF1 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93962 | 64.834 | -3.0756e-05 | -0.00037634
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2080 243064-243675(1) | OPEN LINE FROM BUS 243064 [05NPROCT 138.00] TO BUS 243675 [05BELLF1 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2081 243064-245615(1) | OPEN LINE FROM BUS 243064 [05NPROCT 138.00] TO BUS 245615 [05S.POINT2 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8351 | -1.5497e-05 | -0.00036108
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2081 243064-245615(1) | OPEN LINE FROM BUS 243064 [05NPROCT 138.00] TO BUS 245615 [05S.POINT2 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2082 243064-245664(1) | OPEN LINE FROM BUS 243064 [05NPROCT 138.00] TO BUS 245664 [05E.HUNTING1138.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.0133e-06 | -0.0003466
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2082 243064-245664(1) | OPEN LINE FROM BUS 243064 [05NPROCT 138.00] TO BUS 245664 [05E.HUNTING1138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2083 243064-290186(2) | OPEN LINE FROM BUS 243064 [05NPROCT 138.00] TO BUS 290186 [05N.CHESPK 138.00] CKT 2 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -9.5367e-07 | -0.00034654
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2083 243064-290186(2) | OPEN LINE FROM BUS 243064 [05NPROCT 138.00] TO BUS 290186 [05N.CHESPK 138.00] CKT 2 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2084 243087-243140(1) | OPEN LINE FROM BUS 243087 [05S LUCA 138.00] TO BUS 243140 [05WAKEFL 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93957 | 64.8305 | -8.2493e-05 | -0.00042808
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2084 243087-243140(1) | OPEN LINE FROM BUS 243087 [05S LUCA 138.00] TO BUS 243140 [05WAKEFL 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2085 243088-245615(Z1) | OPEN LINE FROM BUS 243088 [05S.POINT1 138.00] TO BUS 245615 [05S.POINT2 138.00] CKT Z1 | 0.93965 | 64.8362 | 0.9396 | 64.8322 | -5.7518e-05 | -0.00040311
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2085 243088-245615(Z1) | OPEN LINE FROM BUS 243088 [05S.POINT1 138.00] TO BUS 245615 [05S.POINT2 138.00] CKT Z1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2086 243088-245948(1) | OPEN LINE FROM BUS 243088 [05S.POINT1 138.00] TO BUS 245948 [05MILLBR PK2138.00] CKT 1 | 0.93965 | 64.8362 | 0.93962 | 64.8336 | -3.7193e-05 | -0.00038278
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2086 243088-245948(1) | OPEN LINE FROM BUS 243088 [05S.POINT1 138.00] TO BUS 245948 [05MILLBR PK2138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 1.1921e-07 | 1.1921e-07
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2087 243102-244942(Z1) | OPEN LINE FROM BUS 243102 [05SINK SP8SS138.00] TO BUS 244942 [05SINK SP8 138.00] CKT Z1 | 0.93965 | 64.8362 | 0.93967 | 64.8374 | 1.8656e-05 | -0.00032693
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2087 243102-244942(Z1) | OPEN LINE FROM BUS 243102 [05SINK SP8SS138.00] TO BUS 244942 [05SINK SP8 138.00] CKT Z1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2088 243102-245948(1) | OPEN LINE FROM BUS 243102 [05SINK SP8SS138.00] TO BUS 245948 [05MILLBR PK2138.00] CKT 1 | 0.93965 | 64.8362 | 0.93963 | 64.8342 | -2.8849e-05 | -0.00037444
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2088 243102-245948(1) | OPEN LINE FROM BUS 243102 [05SINK SP8SS138.00] TO BUS 245948 [05MILLBR PK2138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2089 243171-290138(1) | OPEN LINE FROM BUS 243171 [05HAYPRTRDSS69.000] TO BUS 290138 [05KOT COAL 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 1.3113e-06 | -0.00034428
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2089 243171-290138(1) | OPEN LINE FROM BUS 243171 [05HAYPRTRDSS69.000] TO BUS 290138 [05KOT COAL 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2090 243173-246850(1) | OPEN LINE FROM BUS 243173 [05MILLBRK 69.000] TO BUS 246850 [05TYGART 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -4.7684e-07 | -0.00034606
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2090 243173-246850(1) | OPEN LINE FROM BUS 243173 [05MILLBRK 69.000] TO BUS 246850 [05TYGART 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2091 243176-243164(1) | OPEN LINE FROM BUS 243176 [05N HAVERH 69.000] TO BUS 243164 [05DCHEMTAP 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 4.1127e-06 | -0.00034148
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2091 243176-243164(1) | OPEN LINE FROM BUS 243176 [05N HAVERH 69.000] TO BUS 243164 [05DCHEMTAP 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2092 243176-243827(1) | OPEN LINE FROM BUS 243176 [05N HAVERH 69.000] TO BUS 243827 [05SUNCOKE 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8356 | -8.4043e-06 | -0.00035399
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2092 243176-243827(1) | OPEN LINE FROM BUS 243176 [05N HAVERH 69.000] TO BUS 243827 [05SUNCOKE 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2093 243176-247033(1) | OPEN LINE FROM BUS 243176 [05N HAVERH 69.000] TO BUS 247033 [05HAVERHSS 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 1.6689e-06 | -0.00034392
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2093 243176-247033(1) | OPEN LINE FROM BUS 243176 [05N HAVERH 69.000] TO BUS 247033 [05HAVERHSS 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2094 243184-244719(1) | OPEN LINE FROM BUS 243184 [05S POINT 34.500] TO BUS 244719 [05VIRGINIA 34.500] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 3.5763e-07 | -0.00034523
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2094 243184-244719(1) | OPEN LINE FROM BUS 243184 [05S POINT 34.500] TO BUS 244719 [05VIRGINIA 34.500] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2095 243184-244968(1) | OPEN LINE FROM BUS 243184 [05S POINT 34.500] TO BUS 244968 [05SPTETHNO 34.500] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 0 | -0.00034559
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2095 243184-244968(1) | OPEN LINE FROM BUS 243184 [05S POINT 34.500] TO BUS 244968 [05SPTETHNO 34.500] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2096 243184-244968(2) | OPEN LINE FROM BUS 243184 [05S POINT 34.500] TO BUS 244968 [05SPTETHNO 34.500] CKT 2 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 0 | -0.00034559
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2096 243184-244968(2) | OPEN LINE FROM BUS 243184 [05S POINT 34.500] TO BUS 244968 [05SPTETHNO 34.500] CKT 2 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2097 243453-243454(1) | OPEN LINE FROM BUS 243453 [05BEATTY 345.00] TO BUS 243454 [05BIXBY 345.00] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8348 | -1.8954e-05 | -0.00036454
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2097 243453-243454(1) | OPEN LINE FROM BUS 243453 [05BEATTY 345.00] TO BUS 243454 [05BIXBY 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2098 243453-243469(3) | OPEN LINE FROM BUS 243453 [05BEATTY 345.00] TO BUS 243469 [05BEATTY 138.00] CKT 3 | 0.93965 | 64.8362 | 0.93965 | 64.8356 | -7.391e-06 | -0.00035298
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2098 243453-243469(3) | OPEN LINE FROM BUS 243453 [05BEATTY 345.00] TO BUS 243469 [05BEATTY 138.00] CKT 3 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2099 243453-243469(4) | OPEN LINE FROM BUS 243453 [05BEATTY 345.00] TO BUS 243469 [05BEATTY 138.00] CKT 4 | 0.93965 | 64.8362 | 0.93965 | 64.8356 | -7.3314e-06 | -0.00035292
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2099 243453-243469(4) | OPEN LINE FROM BUS 243453 [05BEATTY 345.00] TO BUS 243469 [05BEATTY 138.00] CKT 4 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2100 243453-244022(1) | OPEN LINE FROM BUS 243453 [05BEATTY 345.00] TO BUS 244022 [05COLE 345.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 4.2319e-06 | -0.00034136
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2100 243453-244022(1) | OPEN LINE FROM BUS 243453 [05BEATTY 345.00] TO BUS 244022 [05COLE 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2101 243453-245769(1) | OPEN LINE FROM BUS 243453 [05BEATTY 345.00] TO BUS 245769 [05ADKINS 345.00] CKT 1 | 0.93965 | 64.8362 | 0.93926 | 64.809 | -0.00039351 | -0.0007391
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2101 243453-245769(1) | OPEN LINE FROM BUS 243453 [05BEATTY 345.00] TO BUS 245769 [05ADKINS 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2102 243453-253248(1) | OPEN LINE FROM BUS 243453 [05BEATTY 345.00] TO BUS 253248 [09MDISON 345.00] CKT 1 | 0.93965 | 64.8362 | 0.93972 | 64.8409 | 6.9261e-05 | -0.00027633
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2102 243453-253248(1) | OPEN LINE FROM BUS 243453 [05BEATTY 345.00] TO BUS 253248 [09MDISON 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2103 243597-246741(1) | OPEN LINE FROM BUS 243597 [05ASHLEY 69.000] TO BUS 246741 [05PEDRO 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 2.3842e-07 | -0.00034535
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2103 243597-246741(1) | OPEN LINE FROM BUS 243597 [05ASHLEY 69.000] TO BUS 246741 [05PEDRO 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2104 243618-253076(1) | OPEN LINE FROM BUS 243618 [05STUART 69.000] TO BUS 253076 [09STUART 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93956 | 64.8298 | -9.1672e-05 | -0.00043726
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2104 243618-253076(1) | OPEN LINE FROM BUS 243618 [05STUART 69.000] TO BUS 253076 [09STUART 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2105 243656-243671(1) | OPEN LINE FROM BUS 243656 [05BEAVC1EQ 999.00] TO BUS 243671 [05BEAVER CR1138.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8357 | -6.0201e-06 | -0.00035161
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2105 243656-243671(1) | OPEN LINE FROM BUS 243656 [05BEAVC1EQ 999.00] TO BUS 243671 [05BEAVER CR1138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2106 243657-243708(1) | OPEN LINE FROM BUS 243657 [05BEAVC2EQ 999.00] TO BUS 243708 [05BEAVERCR 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8368 | 8.6427e-06 | -0.00033695
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2106 243657-243708(1) | OPEN LINE FROM BUS 243657 [05BEAVC2EQ 999.00] TO BUS 243708 [05BEAVERCR 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2107 243657-244688(1) | OPEN LINE FROM BUS 243657 [05BEAVC2EQ 999.00] TO BUS 244688 [05BEAVER CR2138.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 3.6359e-06 | -0.00034195
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2107 243657-244688(1) | OPEN LINE FROM BUS 243657 [05BEAVC2EQ 999.00] TO BUS 244688 [05BEAVER CR2138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2108 243678-243669(SR) | OPEN LINE FROM BUS 243678 [05BSANDX 138.00] TO BUS 243669 [05B SAND 138.00] CKT SR | 0.93965 | 64.8362 | 0.93919 | 64.8044 | -0.00046092 | -0.00080651
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2108 243678-243669(SR) | OPEN LINE FROM BUS 243678 [05BSANDX 138.00] TO BUS 243669 [05B SAND 138.00] CKT SR | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2109 243688-245949(1) | OPEN LINE FROM BUS 243688 [05S.PORT MTR138.00] TO BUS 245949 [05MLBRPK_ARG138.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8365 | 4.8876e-06 | -0.0003407
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2109 243688-245949(1) | OPEN LINE FROM BUS 243688 [05S.PORT MTR138.00] TO BUS 245949 [05MLBRPK_ARG138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2111 243712-244727(1) | OPEN LINE FROM BUS 243712 [05CANNONSB 69.000] TO BUS 244727 [05S.NEAL 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93954 | 64.828 | -0.00011843 | -0.00046402
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2111 243712-244727(1) | OPEN LINE FROM BUS 243712 [05CANNONSB 69.000] TO BUS 244727 [05S.NEAL 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2119 243743-244670(1) | OPEN LINE FROM BUS 243743 [05PRINCESS 69.000] TO BUS 244670 [05HOODSCRK 69.000] CKT 1 | 0.93965 | 64.8362 | 0.9395 | 64.8252 | -0.00015932 | -0.00050491
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2119 243743-244670(1) | OPEN LINE FROM BUS 243743 [05PRINCESS 69.000] TO BUS 244670 [05HOODSCRK 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2120 243759-243753(1) | OPEN LINE FROM BUS 243759 [05PRESTNSB 46.000] TO BUS 243753 [05ALLEN 46.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -7.1526e-07 | -0.0003463
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2120 243759-243753(1) | OPEN LINE FROM BUS 243759 [05PRESTNSB 46.000] TO BUS 243753 [05ALLEN 46.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2121 243759-243754(1) | OPEN LINE FROM BUS 243759 [05PRESTNSB 46.000] TO BUS 243754 [05EPRESTNS 46.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 4.2319e-06 | -0.00034136
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2121 243759-243754(1) | OPEN LINE FROM BUS 243759 [05PRESTNSB 46.000] TO BUS 243754 [05EPRESTNS 46.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2122 243759-247415(1) | OPEN LINE FROM BUS 243759 [05PRESTNSB 46.000] TO BUS 247415 [05JENWILEYSS46.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8359 | -3.0994e-06 | -0.00034869
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2122 243759-247415(1) | OPEN LINE FROM BUS 243759 [05PRESTNSB 46.000] TO BUS 247415 [05JENWILEYSS46.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2123 243804-244575(1) | OPEN LINE FROM BUS 243804 [05DEWEY 69.000] TO BUS 244575 [05PEVLER 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8357 | -6.4373e-06 | -0.00035203
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2123 243804-244575(1) | OPEN LINE FROM BUS 243804 [05DEWEY 69.000] TO BUS 244575 [05PEVLER 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2126 243819-243822(1) | OPEN LINE FROM BUS 243819 [05N PORTSM 69.000] TO BUS 243822 [05ROSEMNT SS69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8356 | -7.5102e-06 | -0.0003531
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2126 243819-243822(1) | OPEN LINE FROM BUS 243819 [05N PORTSM 69.000] TO BUS 243822 [05ROSEMNT SS69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2127 243819-243826(1) | OPEN LINE FROM BUS 243819 [05N PORTSM 69.000] TO BUS 243826 [05ORTELCRN 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8358 | -5.8413e-06 | -0.00035143
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2127 243819-243826(1) | OPEN LINE FROM BUS 243819 [05N PORTSM 69.000] TO BUS 243826 [05ORTELCRN 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2128 244008-242915(Z1) | OPEN LINE FROM BUS 244008 [05STANVILLE1138.00] TO BUS 242915 [05STANVILLE2138.00] CKT Z1 | 0.93965 | 64.8362 | 0.93974 | 64.8421 | 8.6188e-05 | -0.0002594
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2128 244008-242915(Z1) | OPEN LINE FROM BUS 244008 [05STANVILLE1138.00] TO BUS 242915 [05STANVILLE2138.00] CKT Z1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2129 244592-244599(1) | OPEN LINE FROM BUS 244592 [05BURTON 46.000] TO BUS 244599 [05ELWOOD 46.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 1.2517e-06 | -0.00034434
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2129 244592-244599(1) | OPEN LINE FROM BUS 244592 [05BURTON 46.000] TO BUS 244599 [05ELWOOD 46.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2130 244616-244626(1) | OPEN LINE FROM BUS 244616 [05MCKINNEY 46.000] TO BUS 244626 [05SALSBURY 46.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 8.3447e-07 | -0.00034475
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2130 244616-244626(1) | OPEN LINE FROM BUS 244616 [05MCKINNEY 46.000] TO BUS 244626 [05SALSBURY 46.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2131 246782-247061(1) | OPEN LINE FROM BUS 246782 [05FIREBRCK 69.000] TO BUS 247061 [05JEFFERSNSS69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 3.9339e-06 | -0.00034165
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2131 246782-247061(1) | OPEN LINE FROM BUS 246782 [05FIREBRCK 69.000] TO BUS 247061 [05JEFFERSNSS69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2132 246782-247062(1) | OPEN LINE FROM BUS 246782 [05FIREBRCK 69.000] TO BUS 247062 [05BLOOM SS 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8355 | -9.656e-06 | -0.00035524
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2132 246782-247062(1) | OPEN LINE FROM BUS 246782 [05FIREBRCK 69.000] TO BUS 247062 [05BLOOM SS 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2133 246888-243454(1) | OPEN LINE FROM BUS 246888 [05BIERSR 345.00] TO BUS 243454 [05BIXBY 345.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 3.8743e-06 | -0.00034171
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2133 246888-243454(1) | OPEN LINE FROM BUS 246888 [05BIERSR 345.00] TO BUS 243454 [05BIXBY 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2134 246888-246889(1) | OPEN LINE FROM BUS 246888 [05BIERSR 345.00] TO BUS 246889 [05BIERSR 138.00] CKT 1 | 0.93965 | 64.8362 | 0.9395 | 64.8258 | -0.00015044 | -0.00049603
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2134 246888-246889(1) | OPEN LINE FROM BUS 246888 [05BIERSR 345.00] TO BUS 246889 [05BIERSR 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2135 246916-243815(1) | OPEN LINE FROM BUS 246916 [05CORNRSTN 69.000] TO BUS 243815 [05CENPORTS 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -2.9802e-07 | -0.00034589
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2135 246916-243815(1) | OPEN LINE FROM BUS 246916 [05CORNRSTN 69.000] TO BUS 243815 [05CENPORTS 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2136 246917-243815(1) | OPEN LINE FROM BUS 246917 [05RUHLMAN 69.000] TO BUS 243815 [05CENPORTS 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 0 | -0.00034559
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2136 246917-243815(1) | OPEN LINE FROM BUS 246917 [05RUHLMAN 69.000] TO BUS 243815 [05CENPORTS 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2139 247072-246790(1) | OPEN LINE FROM BUS 247072 [05RAVNSS 69.000] TO BUS 246790 [05BROWNHLS 69.000] CKT 1 | 0.93965 | 64.8362 | 0.9396 | 64.8324 | -5.3823e-05 | -0.00039941
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2139 247072-246790(1) | OPEN LINE FROM BUS 247072 [05RAVNSS 69.000] TO BUS 246790 [05BROWNHLS 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2140 247072-247073(1) | OPEN LINE FROM BUS 247072 [05RAVNSS 69.000] TO BUS 247073 [05RAVEN 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 3.3379e-06 | -0.00034225
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2140 247072-247073(1) | OPEN LINE FROM BUS 247072 [05RAVNSS 69.000] TO BUS 247073 [05RAVEN 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2141 249564-249991(1) | OPEN LINE FROM BUS 249564 [08BUFTN1 345.00] TO BUS 249991 [08BUFTN1 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2142 249564-249991(46) | OPEN LINE FROM BUS 249564 [08BUFTN1 345.00] TO BUS 249991 [08BUFTN1 138.00] CKT 46 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2143 249566-249570(1) | OPEN LINE FROM BUS 249566 [08FOSTER 345.00] TO BUS 249570 [08P.UNON 345.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8358 | -5.6028e-06 | -0.00035119
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2143 249566-249570(1) | OPEN LINE FROM BUS 249566 [08FOSTER 345.00] TO BUS 249570 [08P.UNON 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2144 249566-249578(1) | OPEN LINE FROM BUS 249566 [08FOSTER 345.00] TO BUS 249578 [08HILCRT 345.00] CKT 1 | 0.93965 | 64.8362 | 0.93912 | 64.7996 | -0.00053036 | -0.00087595
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2144 249566-249578(1) | OPEN LINE FROM BUS 249566 [08FOSTER 345.00] TO BUS 249578 [08HILCRT 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2145 249566-249582(1) | OPEN LINE FROM BUS 249566 [08FOSTER 345.00] TO BUS 249582 [08GARVER 345.00] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8351 | -1.5795e-05 | -0.00036138
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2145 249566-249582(1) | OPEN LINE FROM BUS 249566 [08FOSTER 345.00] TO BUS 249582 [08GARVER 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2146 249567-249575(1) | OPEN LINE FROM BUS 249567 [08M.FORT 345.00] TO BUS 249575 [08TERMNL 345.00] CKT 1 | 0.93965 | 64.8362 | 0.93873 | 64.7723 | -0.00092471 | -0.0012703
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2146 249567-249575(1) | OPEN LINE FROM BUS 249567 [08M.FORT 345.00] TO BUS 249575 [08TERMNL 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2147 249567-250057(10) | OPEN LINE FROM BUS 249567 [08M.FORT 345.00] TO BUS 250057 [08M.FORT 138.00] CKT 10 | 0.93965 | 64.8362 | 0.93908 | 64.7964 | -0.0005756 | -0.00092119
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2147 249567-250057(10) | OPEN LINE FROM BUS 249567 [08M.FORT 345.00] TO BUS 250057 [08M.FORT 138.00] CKT 10 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2148 249567-250057(9) | OPEN LINE FROM BUS 249567 [08M.FORT 345.00] TO BUS 250057 [08M.FORT 138.00] CKT 9 | 0.93965 | 64.8362 | 0.93908 | 64.7964 | -0.00057656 | -0.00092214
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2148 249567-250057(9) | OPEN LINE FROM BUS 249567 [08M.FORT 345.00] TO BUS 250057 [08M.FORT 138.00] CKT 9 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2149 249570-249575(1) | OPEN LINE FROM BUS 249570 [08P.UNON 345.00] TO BUS 249575 [08TERMNL 345.00] CKT 1 | 0.93965 | 64.8362 | 0.93968 | 64.8382 | 3.0279e-05 | -0.00031531
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2149 249570-249575(1) | OPEN LINE FROM BUS 249570 [08P.UNON 345.00] TO BUS 249575 [08TERMNL 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2150 249570-249577(1) | OPEN LINE FROM BUS 249570 [08P.UNON 345.00] TO BUS 249577 [08ZIMER 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2151 249570-250082(1) | OPEN LINE FROM BUS 249570 [08P.UNON 345.00] TO BUS 250082 [08P.UN1 138.00] CKT 1 | 0.93965 | 64.8362 | 0.9391 | 64.7979 | -0.00055468 | -0.00090027
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2151 249570-250082(1) | OPEN LINE FROM BUS 249570 [08P.UNON 345.00] TO BUS 250082 [08P.UN1 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2152 249570-250083(1) | OPEN LINE FROM BUS 249570 [08P.UNON 345.00] TO BUS 250083 [08P.UN2 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93935 | 64.815 | -0.00030696 | -0.00065255
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2152 249570-250083(1) | OPEN LINE FROM BUS 249570 [08P.UNON 345.00] TO BUS 250083 [08P.UN2 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2153 249571-249573(1) | OPEN LINE FROM BUS 249571 [08REDBK1 345.00] TO BUS 249573 [08SGROVE 345.00] CKT 1 | 0.93965 | 64.8362 | 0.93889 | 64.7834 | -0.00076449 | -0.0011101
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2153 249571-249573(1) | OPEN LINE FROM BUS 249571 [08REDBK1 345.00] TO BUS 249573 [08SGROVE 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 1.1921e-07 | 1.1921e-07
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2154 249571-249575(1) | OPEN LINE FROM BUS 249571 [08REDBK1 345.00] TO BUS 249575 [08TERMNL 345.00] CKT 1 | 0.93965 | 64.8362 | 0.93953 | 64.8274 | -0.00012743 | -0.00047302
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2154 249571-249575(1) | OPEN LINE FROM BUS 249571 [08REDBK1 345.00] TO BUS 249575 [08TERMNL 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2155 249573-249577(1) | OPEN LINE FROM BUS 249573 [08SGROVE 345.00] TO BUS 249577 [08ZIMER 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2156 249573-250097(1) | OPEN LINE FROM BUS 249573 [08SGROVE 345.00] TO BUS 250097 [08SGROVE 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2157 249577-249580(Z1) | OPEN LINE FROM BUS 249577 [08ZIMER 345.00] TO BUS 249580 [08ZIMERG 345.00] CKT Z1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2158 249577-249581(1) | OPEN LINE FROM BUS 249577 [08ZIMER 345.00] TO BUS 249581 [08MELDAL 345.00] CKT 1 | 0.93965 | 64.8362 | 0.93978 | 64.8448 | 0.00012523 | -0.00022036
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2158 249577-249581(1) | OPEN LINE FROM BUS 249577 [08ZIMER 345.00] TO BUS 249581 [08MELDAL 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2159 249578-250136(1) | OPEN LINE FROM BUS 249578 [08HILCRT 345.00] TO BUS 250136 [08HILCRT 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93963 | 64.8345 | -2.3901e-05 | -0.00036949
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2159 249578-250136(1) | OPEN LINE FROM BUS 249578 [08HILCRT 345.00] TO BUS 250136 [08HILCRT 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2160 249580-251968(1H) | OPEN LINE FROM BUS 249580 [08ZIMERG 345.00] TO BUS 251968 [08ZIMRHP 26.000] CKT 1H | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2161 249580-251969(1L) | OPEN LINE FROM BUS 249580 [08ZIMERG 345.00] TO BUS 251969 [08ZIMRLP 22.000] CKT 1L | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2162 249581-250145(1) | OPEN LINE FROM BUS 249581 [08MELDAL 345.00] TO BUS 250145 [08MELDAL 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8368 | 8.8811e-06 | -0.00033671
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2162 249581-250145(1) | OPEN LINE FROM BUS 249581 [08MELDAL 345.00] TO BUS 250145 [08MELDAL 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2163 249990-250021(1) | OPEN LINE FROM BUS 249990 [08BROWN 138.00] TO BUS 250021 [08ESTWD2 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93958 | 64.8313 | -7.0393e-05 | -0.00041598
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2163 249990-250021(1) | OPEN LINE FROM BUS 249990 [08BROWN 138.00] TO BUS 250021 [08ESTWD2 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2164 249991-250028(1) | OPEN LINE FROM BUS 249991 [08BUFTN1 138.00] TO BUS 250028 [08FLRNC2 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2165 249991-250077(1) | OPEN LINE FROM BUS 249991 [08BUFTN1 138.00] TO BUS 250077 [08MTZION 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2166 249991-250148(1) | OPEN LINE FROM BUS 249991 [08BUFTN1 138.00] TO BUS 250148 [08EKPWEB 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93916 | 64.8019 | -0.00049609 | -0.00084168
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2166 249991-250148(1) | OPEN LINE FROM BUS 249991 [08BUFTN1 138.00] TO BUS 250148 [08EKPWEB 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2167 249991-251279(2) | OPEN LINE FROM BUS 249991 [08BUFTN1 138.00] TO BUS 251279 [08BUFTN2 69.000] CKT 2 | 0.93965 | 64.8362 | 0.93927 | 64.8093 | -0.00038886 | -0.00073445
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2167 249991-251279(2) | OPEN LINE FROM BUS 249991 [08BUFTN1 138.00] TO BUS 251279 [08BUFTN2 69.000] CKT 2 | 1.05 | 525 | 1.05 | 525 | 1.1921e-07 | 1.1921e-07
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2168 249999-250007(1) | OPEN LINE FROM BUS 249999 [08CNSTNC 138.00] TO BUS 250007 [08CRSNT1 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93947 | 64.8237 | -0.00017995 | -0.00052553
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2168 249999-250007(1) | OPEN LINE FROM BUS 249999 [08CNSTNC 138.00] TO BUS 250007 [08CRSNT1 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2169 249999-250044(1) | OPEN LINE FROM BUS 249999 [08CNSTNC 138.00] TO BUS 250044 [08HEBRN2 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93939 | 64.8183 | -0.00025946 | -0.00060505
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2169 249999-250044(1) | OPEN LINE FROM BUS 249999 [08CNSTNC 138.00] TO BUS 250044 [08HEBRN2 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2170 250016-250057(1) | OPEN LINE FROM BUS 250016 [08EBNZR 138.00] TO BUS 250057 [08M.FORT 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93936 | 64.8155 | -0.00029898 | -0.00064456
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2170 250016-250057(1) | OPEN LINE FROM BUS 250016 [08EBNZR 138.00] TO BUS 250057 [08M.FORT 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2171 250044-250152(Z1) | OPEN LINE FROM BUS 250044 [08HEBRN2 138.00] TO BUS 250152 [08HEBRNG 138.00] CKT Z1 | 0.93965 | 64.8362 | 0.93937 | 64.8164 | -0.00028658 | -0.00063217
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2171 250044-250152(Z1) | OPEN LINE FROM BUS 250044 [08HEBRN2 138.00] TO BUS 250152 [08HEBRNG 138.00] CKT Z1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2172 250045-250151(Z1) | OPEN LINE FROM BUS 250045 [08HEBRN1 138.00] TO BUS 250151 [08HEBTAP 138.00] CKT Z1 | 0.93965 | 64.8362 | 0.93973 | 64.841 | 7.0632e-05 | -0.00027496
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2172 250045-250151(Z1) | OPEN LINE FROM BUS 250045 [08HEBRN1 138.00] TO BUS 250151 [08HEBTAP 138.00] CKT Z1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2173 250054-250077(1) | OPEN LINE FROM BUS 250054 [08LONGBR 138.00] TO BUS 250077 [08MTZION 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93882 | 64.7783 | -0.00083876 | -0.0011843
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2173 250054-250077(1) | OPEN LINE FROM BUS 250054 [08LONGBR 138.00] TO BUS 250077 [08MTZION 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2174 250057-250058(1) | OPEN LINE FROM BUS 250057 [08M.FORT 138.00] TO BUS 250058 [08M.FTGT 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93914 | 64.8005 | -0.00051624 | -0.00086182
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2174 250057-250058(1) | OPEN LINE FROM BUS 250057 [08M.FORT 138.00] TO BUS 250058 [08M.FTGT 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2175 250057-250060(1) | OPEN LINE FROM BUS 250057 [08M.FORT 138.00] TO BUS 250060 [08MDWAY1 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93953 | 64.8279 | -0.00012016 | -0.00046575
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2175 250057-250060(1) | OPEN LINE FROM BUS 250057 [08M.FORT 138.00] TO BUS 250060 [08MDWAY1 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2176 250057-250070(1) | OPEN LINE FROM BUS 250057 [08M.FORT 138.00] TO BUS 250070 [08MRGAN1 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93958 | 64.831 | -7.54e-05 | -0.00042099
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2176 250057-250070(1) | OPEN LINE FROM BUS 250057 [08M.FORT 138.00] TO BUS 250070 [08MRGAN1 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2177 250057-250131(1) | OPEN LINE FROM BUS 250057 [08M.FORT 138.00] TO BUS 250131 [08WILEY2 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93953 | 64.8277 | -0.00012302 | -0.00046861
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2177 250057-250131(1) | OPEN LINE FROM BUS 250057 [08M.FORT 138.00] TO BUS 250131 [08WILEY2 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2178 250057-250151(1) | OPEN LINE FROM BUS 250057 [08M.FORT 138.00] TO BUS 250151 [08HEBTAP 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2179 250058-251378(1) | OPEN LINE FROM BUS 250058 [08M.FTGT 138.00] TO BUS 251378 [08M.FTGT 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93915 | 64.801 | -0.00050926 | -0.00085485
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2179 250058-251378(1) | OPEN LINE FROM BUS 250058 [08M.FTGT 138.00] TO BUS 251378 [08M.FTGT 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2180 250136-250141(1) | OPEN LINE FROM BUS 250136 [08HILCRT 138.00] TO BUS 250141 [08SCEAST 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93958 | 64.831 | -7.54e-05 | -0.00042099
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2180 250136-250141(1) | OPEN LINE FROM BUS 250136 [08HILCRT 138.00] TO BUS 250141 [08SCEAST 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2181 250145-250154(1) | OPEN LINE FROM BUS 250145 [08MELDAL 138.00] TO BUS 250154 [08MELDLS 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8368 | 8.8215e-06 | -0.00033677
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2181 250145-250154(1) | OPEN LINE FROM BUS 250145 [08MELDAL 138.00] TO BUS 250154 [08MELDLS 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2182 250151-250152(Z1) | OPEN LINE FROM BUS 250151 [08HEBTAP 138.00] TO BUS 250152 [08HEBRNG 138.00] CKT Z1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2183 250154-251970(T1) | OPEN LINE FROM BUS 250154 [08MELDLS 138.00] TO BUS 251970 [08MELDL1 13.800] CKT T1 | 0.93965 | 64.8362 | 0.93966 | 64.8367 | 7.391e-06 | -0.0003382
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2183 250154-251970(T1) | OPEN LINE FROM BUS 250154 [08MELDLS 138.00] TO BUS 251970 [08MELDL1 13.800] CKT T1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2184 250154-251971(T2) | OPEN LINE FROM BUS 250154 [08MELDLS 138.00] TO BUS 251971 [08MELDL2 13.800] CKT T2 | 0.93965 | 64.8362 | 0.93966 | 64.8367 | 7.391e-06 | -0.0003382
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2184 250154-251971(T2) | OPEN LINE FROM BUS 250154 [08MELDLS 138.00] TO BUS 251971 [08MELDL2 13.800] CKT T2 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2185 250154-251972(T3) | OPEN LINE FROM BUS 250154 [08MELDLS 138.00] TO BUS 251972 [08MELDL3 13.800] CKT T3 | 0.93965 | 64.8362 | 0.93966 | 64.8367 | 7.391e-06 | -0.0003382
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2185 250154-251972(T3) | OPEN LINE FROM BUS 250154 [08MELDLS 138.00] TO BUS 251972 [08MELDL3 13.800] CKT T3 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2186 251276-251469(1) | OPEN LINE FROM BUS 251276 [08BROWER 69.000] TO BUS 251469 [08T28652 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93969 | 64.8389 | 3.9101e-05 | -0.00030649
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2186 251276-251469(1) | OPEN LINE FROM BUS 251276 [08BROWER 69.000] TO BUS 251469 [08T28652 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2187 251291-251301(1) | OPEN LINE FROM BUS 251291 [08CNSTNC 69.000] TO BUS 251301 [08CWW-BN 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93962 | 64.8335 | -3.8445e-05 | -0.00038403
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2187 251291-251301(1) | OPEN LINE FROM BUS 251291 [08CNSTNC 69.000] TO BUS 251301 [08CWW-BN 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2188 251291-251315(1) | OPEN LINE FROM BUS 251291 [08CNSTNC 69.000] TO BUS 251315 [08EKSMTH 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93953 | 64.8277 | -0.00012285 | -0.00046843
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2188 251291-251315(1) | OPEN LINE FROM BUS 251291 [08CNSTNC 69.000] TO BUS 251315 [08EKSMTH 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2189 251301-251310(1) | OPEN LINE FROM BUS 251301 [08CWW-BN 69.000] TO BUS 251310 [08DRYCRK 69.000] CKT 1 | 0.93965 | 64.8362 | 0.9396 | 64.8326 | -5.2094e-05 | -0.00039768
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2189 251301-251310(1) | OPEN LINE FROM BUS 251301 [08CWW-BN 69.000] TO BUS 251310 [08DRYCRK 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2190 251314-251315(1) | OPEN LINE FROM BUS 251314 [08EKDOWN 69.000] TO BUS 251315 [08EKSMTH 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93953 | 64.8273 | -0.00012875 | -0.00047433
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2190 251314-251315(1) | OPEN LINE FROM BUS 251314 [08EKDOWN 69.000] TO BUS 251315 [08EKSMTH 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2191 251314-251467(1) | OPEN LINE FROM BUS 251314 [08EKDOWN 69.000] TO BUS 251467 [08T15268 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93953 | 64.8276 | -0.00012398 | -0.00046957
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2191 251314-251467(1) | OPEN LINE FROM BUS 251314 [08EKDOWN 69.000] TO BUS 251467 [08T15268 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2192 251367-251368(Z1) | OPEN LINE FROM BUS 251367 [08LEVIA 69.000] TO BUS 251368 [08LEVIB 69.000] CKT Z1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2193 251367-251467(1) | OPEN LINE FROM BUS 251367 [08LEVIA 69.000] TO BUS 251467 [08T15268 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2194 251378-251406(1) | OPEN LINE FROM BUS 251378 [08M.FTGT 69.000] TO BUS 251406 [08MONSTW 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93977 | 64.8438 | 0.00011075 | -0.00023484
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2194 251378-251406(1) | OPEN LINE FROM BUS 251378 [08M.FTGT 69.000] TO BUS 251406 [08MONSTW 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2195 251378-251469(1) | OPEN LINE FROM BUS 251378 [08M.FTGT 69.000] TO BUS 251469 [08T28652 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93961 | 64.8331 | -4.4584e-05 | -0.00039017
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2195 251378-251469(1) | OPEN LINE FROM BUS 251378 [08M.FTGT 69.000] TO BUS 251469 [08T28652 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2196 251378-251579(1) | OPEN LINE FROM BUS 251378 [08M.FTGT 69.000] TO BUS 251579 [08HEBRON 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2197 251467-251579(1) | OPEN LINE FROM BUS 251467 [08T15268 69.000] TO BUS 251579 [08HEBRON 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93944 | 64.8216 | -0.00021088 | -0.00055647
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2197 251467-251579(1) | OPEN LINE FROM BUS 251467 [08T15268 69.000] TO BUS 251579 [08HEBRON 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2198 251468-251469(1) | OPEN LINE FROM BUS 251468 [08T28651 69.000] TO BUS 251469 [08T28652 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93959 | 64.8318 | -6.3241e-05 | -0.00040883
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2198 251468-251469(1) | OPEN LINE FROM BUS 251468 [08T28651 69.000] TO BUS 251469 [08T28652 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2199 249564-248002(1) | OPEN LINE FROM BUS 249564 [08BUFTN1 345.00] TO BUS 248002 [06DEARB2 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2200 249564-248013(1) | OPEN LINE FROM BUS 249564 [08BUFTN1 345.00] TO BUS 248013 [06PIERCE 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2201 249566-248013(1) | OPEN LINE FROM BUS 249566 [08FOSTER 345.00] TO BUS 248013 [06PIERCE 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2202 249566-250029(1) | OPEN LINE FROM BUS 249566 [08FOSTER 345.00] TO BUS 250029 [08FOSTER 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93932 | 64.8134 | -0.00033045 | -0.00067604
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2202 249566-250029(1) | OPEN LINE FROM BUS 249566 [08FOSTER 345.00] TO BUS 250029 [08FOSTER 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2203 249566-253006(1) | OPEN LINE FROM BUS 249566 [08FOSTER 345.00] TO BUS 253006 [09BATH 345.00] CKT 1 | 0.93965 | 64.8362 | 0.93976 | 64.8431 | 0.00010091 | -0.00024468
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2203 249566-253006(1) | OPEN LINE FROM BUS 249566 [08FOSTER 345.00] TO BUS 253006 [09BATH 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2204 249566-253079(1) | OPEN LINE FROM BUS 249566 [08FOSTER 345.00] TO BUS 253079 [09SUGRCK 345.00] CKT 1 | 0.93965 | 64.8362 | 0.93976 | 64.8435 | 0.00010663 | -0.00023896
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2204 249566-253079(1) | OPEN LINE FROM BUS 249566 [08FOSTER 345.00] TO BUS 253079 [09SUGRCK 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2205 249567-243233(1) | OPEN LINE FROM BUS 249567 [08M.FORT 345.00] TO BUS 243233 [05TANNER 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2206 249567-249576(1) | OPEN LINE FROM BUS 249567 [08M.FORT 345.00] TO BUS 249576 [08WODSDL 345.00] CKT 1 | 0.93965 | 64.8362 | 0.93932 | 64.8133 | -0.00033158 | -0.00067717
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2206 249567-249576(1) | OPEN LINE FROM BUS 249567 [08M.FORT 345.00] TO BUS 249576 [08WODSDL 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2207 249567-251950(7) | OPEN LINE FROM BUS 249567 [08M.FORT 345.00] TO BUS 251950 [08M.FRT7 22.000] CKT 7 | 0.93965 | 64.8362 | 0.93858 | 64.7623 | -0.0010703 | -0.0014158
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2207 249567-251950(7) | OPEN LINE FROM BUS 249567 [08M.FORT 345.00] TO BUS 251950 [08M.FRT7 22.000] CKT 7 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2208 249567-251951(8) | OPEN LINE FROM BUS 249567 [08M.FORT 345.00] TO BUS 251951 [08M.FRT8 22.000] CKT 8 | 0.93965 | 64.8362 | 0.93858 | 64.7623 | -0.0010709 | -0.0014165
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2208 249567-251951(8) | OPEN LINE FROM BUS 249567 [08M.FORT 345.00] TO BUS 251951 [08M.FRT8 22.000] CKT 8 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2209 249567-253090(1) | OPEN LINE FROM BUS 249567 [08M.FORT 345.00] TO BUS 253090 [09WMILTN 345.00] CKT 1 | 0.93965 | 64.8362 | 0.93925 | 64.8082 | -0.00040579 | -0.00075138
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2209 249567-253090(1) | OPEN LINE FROM BUS 249567 [08M.FORT 345.00] TO BUS 253090 [09WMILTN 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2210 249571-250092(1) | OPEN LINE FROM BUS 249571 [08REDBK1 345.00] TO BUS 250092 [08REDBK1 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93894 | 64.7867 | -0.00071663 | -0.0010622
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2210 249571-250092(1) | OPEN LINE FROM BUS 249571 [08REDBK1 345.00] TO BUS 250092 [08REDBK1 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2211 249571-250093(1) | OPEN LINE FROM BUS 249571 [08REDBK1 345.00] TO BUS 250093 [08REDBK2 138.00] CKT 1 | 0.93965 | 64.8362 | 0.9389 | 64.7844 | -0.00074977 | -0.0010954
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2211 249571-250093(1) | OPEN LINE FROM BUS 249571 [08REDBK1 345.00] TO BUS 250093 [08REDBK2 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2212 249575-249565(1) | OPEN LINE FROM BUS 249575 [08TERMNL 345.00] TO BUS 249565 [08EBEND 345.00] CKT 1 | 0.93965 | 64.8362 | 0.93887 | 64.7822 | -0.00078267 | -0.0011283
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2212 249575-249565(1) | OPEN LINE FROM BUS 249575 [08TERMNL 345.00] TO BUS 249565 [08EBEND 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2213 249575-250117(1) | OPEN LINE FROM BUS 249575 [08TERMNL 345.00] TO BUS 250117 [08TRMNL1 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93869 | 64.7695 | -0.00096595 | -0.0013115
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2213 249575-250117(1) | OPEN LINE FROM BUS 249575 [08TERMNL 345.00] TO BUS 250117 [08TRMNL1 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2214 249575-250118(1) | OPEN LINE FROM BUS 249575 [08TERMNL 345.00] TO BUS 250118 [08TRMNL2 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93864 | 64.7662 | -0.0010133 | -0.0013589
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2214 249575-250118(1) | OPEN LINE FROM BUS 249575 [08TERMNL 345.00] TO BUS 250118 [08TRMNL2 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2215 249578-253077(1) | OPEN LINE FROM BUS 249578 [08HILCRT 345.00] TO BUS 253077 [09STUART 345.00] CKT 1 | 0.93965 | 64.8362 | 0.93906 | 64.795 | -0.00059628 | -0.00094187
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2215 249578-253077(1) | OPEN LINE FROM BUS 249578 [08HILCRT 345.00] TO BUS 253077 [09STUART 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2217 249582-249574(1) | OPEN LINE FROM BUS 249582 [08GARVER 345.00] TO BUS 249574 [08TDHNTR 345.00] CKT 1 | 0.93965 | 64.8362 | 0.93968 | 64.8381 | 2.7478e-05 | -0.00031811
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2217 249582-249574(1) | OPEN LINE FROM BUS 249582 [08GARVER 345.00] TO BUS 249574 [08TDHNTR 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2218 249582-249583(1) | OPEN LINE FROM BUS 249582 [08GARVER 345.00] TO BUS 249583 [08NTEGEN 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2219 249582-250162(1) | OPEN LINE FROM BUS 249582 [08GARVER 345.00] TO BUS 250162 [08GARVER 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93954 | 64.8282 | -0.00011557 | -0.00046116
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2219 249582-250162(1) | OPEN LINE FROM BUS 249582 [08GARVER 345.00] TO BUS 250162 [08GARVER 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2220 249990-253076(1) | OPEN LINE FROM BUS 249990 [08BROWN 138.00] TO BUS 253076 [09STUART 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93956 | 64.8297 | -9.3818e-05 | -0.00043941
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2220 249990-253076(1) | OPEN LINE FROM BUS 249990 [08BROWN 138.00] TO BUS 253076 [09STUART 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2221 249990-251277-251792(1) | OPEN LINE FROM BUS 249990 [08BROWN 138.00] TO BUS 251277 [08BROWN 69.000] TO BUS 251792 [08BROWN 34.500] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8373 | 1.6987e-05 | -0.0003286
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2221 249990-251277-251792(1) | OPEN LINE FROM BUS 249990 [08BROWN 138.00] TO BUS 251277 [08BROWN 69.000] TO BUS 251792 [08BROWN 34.500] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2222 249991-251278(1) | OPEN LINE FROM BUS 249991 [08BUFTN1 138.00] TO BUS 251278 [08BUFTN1 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8356 | -7.6294e-06 | -0.00035322
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2222 249991-251278(1) | OPEN LINE FROM BUS 249991 [08BUFTN1 138.00] TO BUS 251278 [08BUFTN1 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2223 249991-251278-252039(1) | OPEN LINE FROM BUS 249991 [08BUFTN1 138.00] TO BUS 251278 [08BUFTN1 69.000] TO BUS 252039 [08BUFTN1 12.470] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8367 | 8.0466e-06 | -0.00033754
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2223 249991-251278-252039(1) | OPEN LINE FROM BUS 249991 [08BUFTN1 138.00] TO BUS 251278 [08BUFTN1 69.000] TO BUS 252039 [08BUFTN1 12.470] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2224 250007-250014(1) | OPEN LINE FROM BUS 250007 [08CRSNT1 138.00] TO BUS 250014 [08DNLSN1 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93971 | 64.8402 | 5.9009e-05 | -0.00028658
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2224 250007-250014(1) | OPEN LINE FROM BUS 250007 [08CRSNT1 138.00] TO BUS 250014 [08DNLSN1 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2225 250007-250124(1) | OPEN LINE FROM BUS 250007 [08CRSNT1 138.00] TO BUS 250124 [08WENDEA 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2226 250016-250061(1) | OPEN LINE FROM BUS 250016 [08EBNZR 138.00] TO BUS 250061 [08MDWAY2 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8369 | 1.0669e-05 | -0.00033492
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2226 250016-250061(1) | OPEN LINE FROM BUS 250016 [08EBNZR 138.00] TO BUS 250061 [08MDWAY2 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2227 250016-251311(1) | OPEN LINE FROM BUS 250016 [08EBNZR 138.00] TO BUS 251311 [08EBNZR1 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93972 | 64.8404 | 6.1452e-05 | -0.00028414
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2227 250016-251311(1) | OPEN LINE FROM BUS 250016 [08EBNZR 138.00] TO BUS 251311 [08EBNZR1 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2228 250016-251312(1) | OPEN LINE FROM BUS 250016 [08EBNZR 138.00] TO BUS 251312 [08EBNZR2 69.000] CKT 1 | 0.93965 | 64.8362 | 0.9396 | 64.8323 | -5.5313e-05 | -0.0004009
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2228 250016-251312(1) | OPEN LINE FROM BUS 250016 [08EBNZR 138.00] TO BUS 251312 [08EBNZR2 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2229 250016-251793(1) | OPEN LINE FROM BUS 250016 [08EBNZR 138.00] TO BUS 251793 [08EBNZR6 34.500] CKT 1 | 0.93965 | 64.8362 | 0.93978 | 64.8448 | 0.00012475 | -0.00022084
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2229 250016-251793(1) | OPEN LINE FROM BUS 250016 [08EBNZR 138.00] TO BUS 251793 [08EBNZR6 34.500] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2230 250021-250020(Z1) | OPEN LINE FROM BUS 250021 [08ESTWD2 138.00] TO BUS 250020 [08ESTWD1 138.00] CKT Z1 | 0.93965 | 64.8362 | 0.93962 | 64.834 | -3.1233e-05 | -0.00037682
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2230 250021-250020(Z1) | OPEN LINE FROM BUS 250021 [08ESTWD2 138.00] TO BUS 250020 [08ESTWD1 138.00] CKT Z1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2231 250028-250027(Z1) | OPEN LINE FROM BUS 250028 [08FLRNC2 138.00] TO BUS 250027 [08FLRNC1 138.00] CKT Z1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2233 250057-249736(1) | OPEN LINE FROM BUS 250057 [08M.FORT 138.00] TO BUS 249736 [08GRDALE 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93928 | 64.8101 | -0.00037783 | -0.00072342
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2233 250057-249736(1) | OPEN LINE FROM BUS 250057 [08M.FORT 138.00] TO BUS 249736 [08GRDALE 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2235 250058-251960-251961(18) | OPEN LINE FROM BUS 250058 [08M.FTGT 138.00] TO BUS 251960 [08MFTGT1 13.800] TO BUS 251961 [08MFTGT2 13.800] CKT 18 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 8.9407e-07 | -0.00034469
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2235 250058-251960-251961(18) | OPEN LINE FROM BUS 250058 [08M.FTGT 138.00] TO BUS 251960 [08MFTGT1 13.800] TO BUS 251961 [08MFTGT2 13.800] CKT 18 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2236 250060-250048(1) | OPEN LINE FROM BUS 250060 [08MDWAY1 138.00] TO BUS 250048 [08KLEMN1 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93957 | 64.8301 | -8.7678e-05 | -0.00043327
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2236 250060-250048(1) | OPEN LINE FROM BUS 250060 [08MDWAY1 138.00] TO BUS 250048 [08KLEMN1 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2237 250070-250032(1) | OPEN LINE FROM BUS 250070 [08MRGAN1 138.00] TO BUS 250032 [08FRFLD1 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93963 | 64.8345 | -2.4617e-05 | -0.0003702
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2237 250070-250032(1) | OPEN LINE FROM BUS 250070 [08MRGAN1 138.00] TO BUS 250032 [08FRFLD1 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2238 250082-249985(1) | OPEN LINE FROM BUS 250082 [08P.UN1 138.00] TO BUS 249985 [08BECKET 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93954 | 64.8285 | -0.00011039 | -0.00045598
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2238 250082-249985(1) | OPEN LINE FROM BUS 250082 [08P.UN1 138.00] TO BUS 249985 [08BECKET 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2239 250082-250050(1) | OPEN LINE FROM BUS 250082 [08P.UN1 138.00] TO BUS 250050 [08KMPER1 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93952 | 64.8272 | -0.00013 | -0.00047559
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2239 250082-250050(1) | OPEN LINE FROM BUS 250082 [08P.UN1 138.00] TO BUS 250050 [08KMPER1 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2240 250082-250067(1) | OPEN LINE FROM BUS 250082 [08P.UN1 138.00] TO BUS 250067 [08MLHSR2 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93962 | 64.8336 | -3.7611e-05 | -0.0003832
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2240 250082-250067(1) | OPEN LINE FROM BUS 250082 [08P.UN1 138.00] TO BUS 250067 [08MLHSR2 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2241 250082-250096(1) | OPEN LINE FROM BUS 250082 [08P.UN1 138.00] TO BUS 250096 [08SEWARD 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93959 | 64.832 | -6.0022e-05 | -0.00040561
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2241 250082-250096(1) | OPEN LINE FROM BUS 250082 [08P.UN1 138.00] TO BUS 250096 [08SEWARD 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2242 250082-250157(1) | OPEN LINE FROM BUS 250082 [08P.UN1 138.00] TO BUS 250157 [08CORNTP 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93962 | 64.8341 | -2.9445e-05 | -0.00037503
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2242 250082-250157(1) | OPEN LINE FROM BUS 250082 [08P.UN1 138.00] TO BUS 250157 [08CORNTP 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2243 250082-251428-251798(1) | OPEN LINE FROM BUS 250082 [08P.UN1 138.00] TO BUS 251428 [08P.UNN1 69.000] TO BUS 251798 [08PORTU6 34.500] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.835 | -1.6689e-05 | -0.00036228
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2243 250082-251428-251798(1) | OPEN LINE FROM BUS 250082 [08P.UN1 138.00] TO BUS 251428 [08P.UNN1 69.000] TO BUS 251798 [08PORTU6 34.500] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2244 250083-250013(1) | OPEN LINE FROM BUS 250083 [08P.UN2 138.00] TO BUS 250013 [08DIMICK 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93963 | 64.8346 | -2.3186e-05 | -0.00036877
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2244 250083-250013(1) | OPEN LINE FROM BUS 250083 [08P.UN2 138.00] TO BUS 250013 [08DIMICK 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2245 250083-250065(1) | OPEN LINE FROM BUS 250083 [08P.UN2 138.00] TO BUS 250065 [08MILIKN 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93959 | 64.832 | -5.9545e-05 | -0.00040513
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2245 250083-250065(1) | OPEN LINE FROM BUS 250083 [08P.UN2 138.00] TO BUS 250065 [08MILIKN 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2246 250083-250160(1) | OPEN LINE FROM BUS 250083 [08P.UN2 138.00] TO BUS 250160 [08PROVID 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93957 | 64.8305 | -8.148e-05 | -0.00042707
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2246 250083-250160(1) | OPEN LINE FROM BUS 250083 [08P.UN2 138.00] TO BUS 250160 [08PROVID 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2247 250083-251429(1) | OPEN LINE FROM BUS 250083 [08P.UN2 138.00] TO BUS 251429 [08P.UNN2 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93961 | 64.8328 | -4.9055e-05 | -0.00039464
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2247 250083-251429(1) | OPEN LINE FROM BUS 250083 [08P.UN2 138.00] TO BUS 251429 [08P.UNN2 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2248 250083-251798(1) | OPEN LINE FROM BUS 250083 [08P.UN2 138.00] TO BUS 251798 [08PORTU6 34.500] CKT 1 | 0.93965 | 64.8362 | 0.93974 | 64.8419 | 8.3387e-05 | -0.0002622
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2248 250083-251798(1) | OPEN LINE FROM BUS 250083 [08P.UN2 138.00] TO BUS 251798 [08PORTU6 34.500] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2249 250083-252045(5) | OPEN LINE FROM BUS 250083 [08P.UN2 138.00] TO BUS 252045 [08PORTU2 12.470] CKT 5 | 0.93965 | 64.8362 | 0.93973 | 64.8413 | 7.4029e-05 | -0.00027156
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2249 250083-252045(5) | OPEN LINE FROM BUS 250083 [08P.UN2 138.00] TO BUS 252045 [08PORTU2 12.470] CKT 5 | 1.05 | 525 | 1.05 | 525 | 1.1921e-07 | 1.1921e-07
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2250 250083-251428-252045(1) | OPEN LINE FROM BUS 250083 [08P.UN2 138.00] TO BUS 251428 [08P.UNN1 69.000] TO BUS 252045 [08PORTU2 12.470] CKT 1 | 0.93965 | 64.8362 | 0.9396 | 64.8322 | -5.6982e-05 | -0.00040257
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2250 250083-251428-252045(1) | OPEN LINE FROM BUS 250083 [08P.UN2 138.00] TO BUS 251428 [08P.UNN1 69.000] TO BUS 252045 [08PORTU2 12.470] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2251 250097-249988(1) | OPEN LINE FROM BUS 250097 [08SGROVE 138.00] TO BUS 249988 [08BKJ135 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93975 | 64.8427 | 9.4175e-05 | -0.00025141
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2251 250097-249988(1) | OPEN LINE FROM BUS 250097 [08SGROVE 138.00] TO BUS 249988 [08BKJ135 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2252 250097-250042(1) | OPEN LINE FROM BUS 250097 [08SGROVE 138.00] TO BUS 250042 [08HANDS1 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93955 | 64.829 | -0.00010425 | -0.00044984
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2252 250097-250042(1) | OPEN LINE FROM BUS 250097 [08SGROVE 138.00] TO BUS 250042 [08HANDS1 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2253 250097-250052(1) | OPEN LINE FROM BUS 250097 [08SGROVE 138.00] TO BUS 250052 [08KYUNIV 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93939 | 64.8178 | -0.0002653 | -0.00061089
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2253 250097-250052(1) | OPEN LINE FROM BUS 250097 [08SGROVE 138.00] TO BUS 250052 [08KYUNIV 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2254 250097-250053(1) | OPEN LINE FROM BUS 250097 [08SGROVE 138.00] TO BUS 250053 [08LAFARG 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93945 | 64.8218 | -0.00020838 | -0.00055397
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2254 250097-250053(1) | OPEN LINE FROM BUS 250097 [08SGROVE 138.00] TO BUS 250053 [08LAFARG 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2255 250131-250032(1) | OPEN LINE FROM BUS 250131 [08WILEY2 138.00] TO BUS 250032 [08FRFLD1 138.00] CKT 1 | 0.93965 | 64.8362 | 0.9397 | 64.8394 | 4.7624e-05 | -0.00029796
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2255 250131-250032(1) | OPEN LINE FROM BUS 250131 [08WILEY2 138.00] TO BUS 250032 [08FRFLD1 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2256 250131-250068(1) | OPEN LINE FROM BUS 250131 [08WILEY2 138.00] TO BUS 250068 [08MPLKL1 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93962 | 64.8341 | -2.9624e-05 | -0.00037521
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2256 250131-250068(1) | OPEN LINE FROM BUS 250131 [08WILEY2 138.00] TO BUS 250068 [08MPLKL1 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2257 250131-250155(1) | OPEN LINE FROM BUS 250131 [08WILEY2 138.00] TO BUS 250155 [08WILCAP 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93935 | 64.8151 | -0.00030524 | -0.00065082
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2257 250131-250155(1) | OPEN LINE FROM BUS 250131 [08WILEY2 138.00] TO BUS 250155 [08WILCAP 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2258 250131-251826(1) | OPEN LINE FROM BUS 250131 [08WILEY2 138.00] TO BUS 251826 [WILLEY 1 34.500] CKT 1 | 0.93965 | 64.8362 | 0.93981 | 64.8467 | 0.00015318 | -0.0001924
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2258 250131-251826(1) | OPEN LINE FROM BUS 250131 [08WILEY2 138.00] TO BUS 251826 [WILLEY 1 34.500] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2259 250136-250166(Z1) | OPEN LINE FROM BUS 250136 [08HILCRT 138.00] TO BUS 250166 [08HLCRTC 138.00] CKT Z1 | 0.93965 | 64.8362 | 0.93961 | 64.8333 | -4.1485e-05 | -0.00038707
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2259 250136-250166(Z1) | OPEN LINE FROM BUS 250136 [08HILCRT 138.00] TO BUS 250166 [08HLCRTC 138.00] CKT Z1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2260 250141-250020(1) | OPEN LINE FROM BUS 250141 [08SCEAST 138.00] TO BUS 250020 [08ESTWD1 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93959 | 64.8318 | -6.3777e-05 | -0.00040936
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2260 250141-250020(1) | OPEN LINE FROM BUS 250141 [08SCEAST 138.00] TO BUS 250020 [08ESTWD1 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2261 250148-250043(1) | OPEN LINE FROM BUS 250148 [08EKPWEB 138.00] TO BUS 250043 [08HANDS2 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93979 | 64.8455 | 0.00013608 | -0.00020951
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2261 250148-250043(1) | OPEN LINE FROM BUS 250148 [08EKPWEB 138.00] TO BUS 250043 [08HANDS2 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2264 251279-251527(1) | OPEN LINE FROM BUS 251279 [08BUFTN2 69.000] TO BUS 251527 [08TP6763 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93991 | 64.8536 | 0.00025326 | -9.2328e-05
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2264 251279-251527(1) | OPEN LINE FROM BUS 251279 [08BUFTN2 69.000] TO BUS 251527 [08TP6763 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2265 251279-251543(1) | OPEN LINE FROM BUS 251279 [08BUFTN2 69.000] TO BUS 251543 [08VILLA 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8375 | 1.8895e-05 | -0.00032669
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2265 251279-251543(1) | OPEN LINE FROM BUS 251279 [08BUFTN2 69.000] TO BUS 251543 [08VILLA 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2266 251310-251284(1) | OPEN LINE FROM BUS 251310 [08DRYCRK 69.000] TO BUS 251284 [08ATLAS 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93954 | 64.8282 | -0.00011575 | -0.00046134
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2266 251310-251284(1) | OPEN LINE FROM BUS 251310 [08DRYCRK 69.000] TO BUS 251284 [08ATLAS 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2268 251368-251373(1) | OPEN LINE FROM BUS 251368 [08LEVIB 69.000] TO BUS 251373 [08LMBRG1 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 1.1921e-07 | 1.1921e-07
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2269 251405-251449(1) | OPEN LINE FROM BUS 251405 [08MONSTE 69.000] TO BUS 251449 [08SAYLPK 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93969 | 64.8384 | 3.2485e-05 | -0.0003131
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2269 251405-251449(1) | OPEN LINE FROM BUS 251405 [08MONSTE 69.000] TO BUS 251449 [08SAYLPK 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2270 251468-251414(1) | OPEN LINE FROM BUS 251468 [08T28651 69.000] TO BUS 251414 [08NEUMAN 69.000] CKT 1 | 0.93965 | 64.8362 | 0.9396 | 64.8321 | -5.8889e-05 | -0.00040448
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2270 251468-251414(1) | OPEN LINE FROM BUS 251468 [08T28651 69.000] TO BUS 251414 [08NEUMAN 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2272 360112-360450(1) | OPEN LINE FROM BUS 360112 [5RUGBY TN 161.00] TO BUS 360450 [5HUNTSVL TN 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -7.7486e-07 | -0.00034636
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2272 360112-360450(1) | OPEN LINE FROM BUS 360112 [5RUGBY TN 161.00] TO BUS 360450 [5HUNTSVL TN 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2273 360145-360473(1) | OPEN LINE FROM BUS 360145 [5ROYAL BLUE 161.00] TO BUS 360473 [5JELLICO TN 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.7881e-07 | -0.00034577
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2273 360145-360473(1) | OPEN LINE FROM BUS 360145 [5ROYAL BLUE 161.00] TO BUS 360473 [5JELLICO TN 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2274 360145-361771(1) | OPEN LINE FROM BUS 360145 [5ROYAL BLUE 161.00] TO BUS 361771 [5ROYL BLU SS161.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 7.1526e-07 | -0.00034487
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2274 360145-361771(1) | OPEN LINE FROM BUS 360145 [5ROYAL BLUE 161.00] TO BUS 361771 [5ROYL BLU SS161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2275 360333-361113(1) | OPEN LINE FROM BUS 360333 [5GLASGOW KY 161.00] TO BUS 361113 [5GLASGOW TP 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8359 | -3.2187e-06 | -0.00034881
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2275 360333-361113(1) | OPEN LINE FROM BUS 360333 [5GLASGOW KY 161.00] TO BUS 361113 [5GLASGOW TP 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2276 360334-360354(1) | OPEN LINE FROM BUS 360334 [5SUMMER SHAD161.00] TO BUS 360354 [5LAFAYETT TN161.00] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.837 | 1.1683e-05 | -0.00033391
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2276 360334-360354(1) | OPEN LINE FROM BUS 360334 [5SUMMER SHAD161.00] TO BUS 360354 [5LAFAYETT TN161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2277 360334-360448(1) | OPEN LINE FROM BUS 360334 [5SUMMER SHAD161.00] TO BUS 360448 [5WOLF CRK HP161.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -8.3447e-07 | -0.00034642
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2277 360334-360448(1) | OPEN LINE FROM BUS 360334 [5SUMMER SHAD161.00] TO BUS 360448 [5WOLF CRK HP161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2278 360334-361064(1) | OPEN LINE FROM BUS 360334 [5SUMMER SHAD161.00] TO BUS 361064 [5TOMPKNSV TP161.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8357 | -6.8545e-06 | -0.00035244
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2278 360334-361064(1) | OPEN LINE FROM BUS 360334 [5SUMMER SHAD161.00] TO BUS 361064 [5TOMPKNSV TP161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2279 360334-361788(1) | OPEN LINE FROM BUS 360334 [5SUMMER SHAD161.00] TO BUS 361788 [5SUM SHAD TP161.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 0 | -0.00034559
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2279 360334-361788(1) | OPEN LINE FROM BUS 360334 [5SUMMER SHAD161.00] TO BUS 361788 [5SUM SHAD TP161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2280 360338-361139(1) | OPEN LINE FROM BUS 360338 [5SCOTTSVL KY161.00] TO BUS 361139 [5S SCOTTSVLE161.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 1.4305e-06 | -0.00034416
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2280 360338-361139(1) | OPEN LINE FROM BUS 360338 [5SCOTTSVL KY161.00] TO BUS 361139 [5S SCOTTSVLE161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2281 360342-362499(1) | OPEN LINE FROM BUS 360342 [5LIVINGST TN161.00] TO BUS 362499 [2LIVINGST TN69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 0 | -0.00034559
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2281 360342-362499(1) | OPEN LINE FROM BUS 360342 [5LIVINGST TN161.00] TO BUS 362499 [2LIVINGST TN69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2282 360354-361139(1) | OPEN LINE FROM BUS 360354 [5LAFAYETT TN161.00] TO BUS 361139 [5S SCOTTSVLE161.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 2.5034e-06 | -0.00034308
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2282 360354-361139(1) | OPEN LINE FROM BUS 360354 [5LAFAYETT TN161.00] TO BUS 361139 [5S SCOTTSVLE161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2283 360354-361265(1) | OPEN LINE FROM BUS 360354 [5LAFAYETT TN161.00] TO BUS 361265 [5HARTSVLE TP161.00] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.837 | 1.2815e-05 | -0.00033277
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2283 360354-361265(1) | OPEN LINE FROM BUS 360354 [5LAFAYETT TN161.00] TO BUS 361265 [5HARTSVLE TP161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2284 360354-361558(1) | OPEN LINE FROM BUS 360354 [5LAFAYETT TN161.00] TO BUS 361558 [5E SUMNER TP161.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 1.7881e-07 | -0.00034541
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2284 360354-361558(1) | OPEN LINE FROM BUS 360354 [5LAFAYETT TN161.00] TO BUS 361558 [5E SUMNER TP161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2285 360445-360450(1) | OPEN LINE FROM BUS 360445 [5BRAYTOWN TN161.00] TO BUS 360450 [5HUNTSVL TN 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8366 | 6.1393e-06 | -0.00033945
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2285 360445-360450(1) | OPEN LINE FROM BUS 360445 [5BRAYTOWN TN161.00] TO BUS 360450 [5HUNTSVL TN 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2286 360448-360486(1) | OPEN LINE FROM BUS 360448 [5WOLF CRK HP161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8353 | -1.2279e-05 | -0.00035787
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2286 360448-360486(1) | OPEN LINE FROM BUS 360448 [5WOLF CRK HP161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2287 360448-361618(1) | OPEN LINE FROM BUS 360448 [5WOLF CRK HP161.00] TO BUS 361618 [5KELSEY RD 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 2.3842e-07 | -0.00034535
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2287 360448-361618(1) | OPEN LINE FROM BUS 360448 [5WOLF CRK HP161.00] TO BUS 361618 [5KELSEY RD 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2288 360448-361666(1) | OPEN LINE FROM BUS 360448 [5WOLF CRK HP161.00] TO BUS 361666 [5BURKSVLTP 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 7.7486e-07 | -0.00034481
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2288 360448-361666(1) | OPEN LINE FROM BUS 360448 [5WOLF CRK HP161.00] TO BUS 361666 [5BURKSVLTP 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2289 360448-364620(1) | OPEN LINE FROM BUS 360448 [5WOLF CRK HP161.00] TO BUS 364620 [1WOLFCR H1-213.800] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8359 | -4.0531e-06 | -0.00034964
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2289 360448-364620(1) | OPEN LINE FROM BUS 360448 [5WOLF CRK HP161.00] TO BUS 364620 [1WOLFCR H1-213.800] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2290 360448-364621(2) | OPEN LINE FROM BUS 360448 [5WOLF CRK HP161.00] TO BUS 364621 [1WOLFCR H3-413.800] CKT 2 | 0.93965 | 64.8362 | 0.93965 | 64.8359 | -4.0531e-06 | -0.00034964
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2290 360448-364621(2) | OPEN LINE FROM BUS 360448 [5WOLF CRK HP161.00] TO BUS 364621 [1WOLFCR H3-413.800] CKT 2 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2291 360448-364622(3) | OPEN LINE FROM BUS 360448 [5WOLF CRK HP161.00] TO BUS 364622 [1WOLFCR H5-613.800] CKT 3 | 0.93965 | 64.8362 | 0.93965 | 64.8359 | -4.0531e-06 | -0.00034964
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2291 360448-364622(3) | OPEN LINE FROM BUS 360448 [5WOLF CRK HP161.00] TO BUS 364622 [1WOLFCR H5-613.800] CKT 3 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2292 360450-361580(1) | OPEN LINE FROM BUS 360450 [5HUNTSVL TN 161.00] TO BUS 361580 [5ONEIDA TN 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8352 | -1.3411e-05 | -0.000359
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2292 360450-361580(1) | OPEN LINE FROM BUS 360450 [5HUNTSVL TN 161.00] TO BUS 361580 [5ONEIDA TN 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2293 360450-361618(1) | OPEN LINE FROM BUS 360450 [5HUNTSVL TN 161.00] TO BUS 361618 [5KELSEY RD 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 1.5497e-06 | -0.00034404
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2293 360450-361618(1) | OPEN LINE FROM BUS 360450 [5HUNTSVL TN 161.00] TO BUS 361618 [5KELSEY RD 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2294 360454-361771(1) | OPEN LINE FROM BUS 360454 [5CARYVILL TN161.00] TO BUS 361771 [5ROYL BLU SS161.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8365 | 5.0068e-06 | -0.00034058
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2294 360454-361771(1) | OPEN LINE FROM BUS 360454 [5CARYVILL TN161.00] TO BUS 361771 [5ROYL BLU SS161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2295 360509-361246(1) | OPEN LINE FROM BUS 360509 [5W TOMPKINSV161.00] TO BUS 361246 [5W TOMPKINST161.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.1325e-06 | -0.00034672
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2295 360509-361246(1) | OPEN LINE FROM BUS 360509 [5W TOMPKINSV161.00] TO BUS 361246 [5W TOMPKINST161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2296 361064-361246(1) | OPEN LINE FROM BUS 361064 [5TOMPKNSV TP161.00] TO BUS 361246 [5W TOMPKINST161.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8358 | -4.9472e-06 | -0.00035053
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2296 361064-361246(1) | OPEN LINE FROM BUS 361064 [5TOMPKNSV TP161.00] TO BUS 361246 [5W TOMPKINST161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2297 361064-361666(1) | OPEN LINE FROM BUS 361064 [5TOMPKNSV TP161.00] TO BUS 361666 [5BURKSVLTP 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -1.7285e-06 | -0.00034732
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2297 361064-361666(1) | OPEN LINE FROM BUS 361064 [5TOMPKNSV TP161.00] TO BUS 361666 [5BURKSVLTP 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2298 361113-361735(1) | OPEN LINE FROM BUS 361113 [5GLASGOW TP 161.00] TO BUS 361735 [5TRANSPARK 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 1.9073e-06 | -0.00034368
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2298 361113-361735(1) | OPEN LINE FROM BUS 361113 [5GLASGOW TP 161.00] TO BUS 361735 [5TRANSPARK 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2299 361114-361735(1) | OPEN LINE FROM BUS 361114 [5BRISTOW TAP161.00] TO BUS 361735 [5TRANSPARK 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 4.1723e-07 | -0.00034517
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2299 361114-361735(1) | OPEN LINE FROM BUS 361114 [5BRISTOW TAP161.00] TO BUS 361735 [5TRANSPARK 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2300 361117-361246(1) | OPEN LINE FROM BUS 361117 [5TOMPKNSV PS161.00] TO BUS 361246 [5W TOMPKINST161.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8359 | -3.6955e-06 | -0.00034928
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2300 361117-361246(1) | OPEN LINE FROM BUS 361117 [5TOMPKNSV PS161.00] TO BUS 361246 [5W TOMPKINST161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2301 361265-361266(1) | OPEN LINE FROM BUS 361265 [5HARTSVLE TP161.00] TO BUS 361266 [5HARTSVLE TN161.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -4.1723e-07 | -0.000346
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2301 361265-361266(1) | OPEN LINE FROM BUS 361265 [5HARTSVLE TP161.00] TO BUS 361266 [5HARTSVLE TN161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2302 361267-361558(1) | OPEN LINE FROM BUS 361267 [5WESTMORELD 161.00] TO BUS 361558 [5E SUMNER TP161.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 5.3644e-07 | -0.00034505
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2302 361267-361558(1) | OPEN LINE FROM BUS 361267 [5WESTMORELD 161.00] TO BUS 361558 [5E SUMNER TP161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2303 361558-361559(1) | OPEN LINE FROM BUS 361558 [5E SUMNER TP161.00] TO BUS 361559 [5E SUMNER TN161.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.3113e-06 | -0.0003469
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2303 361558-361559(1) | OPEN LINE FROM BUS 361558 [5E SUMNER TP161.00] TO BUS 361559 [5E SUMNER TN161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2304 361579-361580(1) | OPEN LINE FROM BUS 361579 [5WINFIELD TN161.00] TO BUS 361580 [5ONEIDA TN 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8355 | -8.8811e-06 | -0.00035447
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2304 361579-361580(1) | OPEN LINE FROM BUS 361579 [5WINFIELD TN161.00] TO BUS 361580 [5ONEIDA TN 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2305 361603-361604(1) | OPEN LINE FROM BUS 361603 [5E GLASGOW T161.00] TO BUS 361604 [5E GLASGOW 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8359 | -3.2783e-06 | -0.00034887
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2305 361603-361604(1) | OPEN LINE FROM BUS 361603 [5E GLASGOW T161.00] TO BUS 361604 [5E GLASGOW 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2306 361618-361619(1) | OPEN LINE FROM BUS 361618 [5KELSEY RD 161.00] TO BUS 361619 [5BYRDSTOWN 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.7881e-07 | -0.00034577
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2306 361618-361619(1) | OPEN LINE FROM BUS 361618 [5KELSEY RD 161.00] TO BUS 361619 [5BYRDSTOWN 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2307 361666-361667(1) | OPEN LINE FROM BUS 361666 [5BURKSVLTP 161.00] TO BUS 361667 [5BURKESVL KY161.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.3709e-06 | -0.00034696
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2307 361666-361667(1) | OPEN LINE FROM BUS 361666 [5BURKSVLTP 161.00] TO BUS 361667 [5BURKESVL KY161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2308 362058-362059(1) | OPEN LINE FROM BUS 362058 [2MOSS TN TAP69.000] TO BUS 362059 [2TOMPKINSVL 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -3.5763e-07 | -0.00034595
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2308 362058-362059(1) | OPEN LINE FROM BUS 362058 [2MOSS TN TAP69.000] TO BUS 362059 [2TOMPKINSVL 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2309 362058-362061(1) | OPEN LINE FROM BUS 362058 [2MOSS TN TAP69.000] TO BUS 362061 [2DALE HOLLOW69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -7.7486e-07 | -0.00034636
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2309 362058-362061(1) | OPEN LINE FROM BUS 362058 [2MOSS TN TAP69.000] TO BUS 362061 [2DALE HOLLOW69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2310 362058-363060(1) | OPEN LINE FROM BUS 362058 [2MOSS TN TAP69.000] TO BUS 363060 [2MOSS TN 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.3709e-06 | -0.00034696
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2310 362058-363060(1) | OPEN LINE FROM BUS 362058 [2MOSS TN TAP69.000] TO BUS 363060 [2MOSS TN 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2311 362059-362060(1) | OPEN LINE FROM BUS 362059 [2TOMPKINSVL 69.000] TO BUS 362060 [2SUMMER SHAD69.000] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 6.5565e-07 | -0.00034493
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2311 362059-362060(1) | OPEN LINE FROM BUS 362059 [2TOMPKINSVL 69.000] TO BUS 362060 [2SUMMER SHAD69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2312 362060-362061(1) | OPEN LINE FROM BUS 362060 [2SUMMER SHAD69.000] TO BUS 362061 [2DALE HOLLOW69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.7881e-07 | -0.00034577
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2312 362060-362061(1) | OPEN LINE FROM BUS 362060 [2SUMMER SHAD69.000] TO BUS 362061 [2DALE HOLLOW69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2313 362061-364614(1) | OPEN LINE FROM BUS 362061 [2DALE HOLLOW69.000] TO BUS 364614 [1DALE HOL H113.800] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 2.7418e-06 | -0.00034285
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2313 362061-364614(1) | OPEN LINE FROM BUS 362061 [2DALE HOLLOW69.000] TO BUS 364614 [1DALE HOL H113.800] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2314 362061-364615(2) | OPEN LINE FROM BUS 362061 [2DALE HOLLOW69.000] TO BUS 364615 [1DALE HOL H213.800] CKT 2 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 2.7418e-06 | -0.00034285
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2314 362061-364615(2) | OPEN LINE FROM BUS 362061 [2DALE HOLLOW69.000] TO BUS 364615 [1DALE HOL H213.800] CKT 2 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2315 362061-364616(3) | OPEN LINE FROM BUS 362061 [2DALE HOLLOW69.000] TO BUS 364616 [1DALE HOL H313.800] CKT 3 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 2.7418e-06 | -0.00034285
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2315 362061-364616(3) | OPEN LINE FROM BUS 362061 [2DALE HOLLOW69.000] TO BUS 364616 [1DALE HOL H313.800] CKT 3 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2316 360112-361287(1) | OPEN LINE FROM BUS 360112 [5RUGBY TN 161.00] TO BUS 361287 [5JAMESTWN TN161.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -1.9073e-06 | -0.0003475
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2316 360112-361287(1) | OPEN LINE FROM BUS 360112 [5RUGBY TN 161.00] TO BUS 361287 [5JAMESTWN TN161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2319 360334-360607(1) | OPEN LINE FROM BUS 360334 [5SUMMER SHAD161.00] TO BUS 360607 [5S GLASGOW 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 3.6955e-06 | -0.00034189
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2319 360334-360607(1) | OPEN LINE FROM BUS 360334 [5SUMMER SHAD161.00] TO BUS 360607 [5S GLASGOW 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2320 360334-362060-362483(2) | OPEN LINE FROM BUS 360334 [5SUMMER SHAD161.00] TO BUS 362060 [2SUMMER SHAD69.000] TO BUS 362483 [1SUMMER SHAD13.200] CKT 2 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 1.3113e-06 | -0.00034428
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2320 360334-362060-362483(2) | OPEN LINE FROM BUS 360334 [5SUMMER SHAD161.00] TO BUS 362060 [2SUMMER SHAD69.000] TO BUS 362483 [1SUMMER SHAD13.200] CKT 2 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2321 360338-361553(1) | OPEN LINE FROM BUS 360338 [5SCOTTSVL KY161.00] TO BUS 361553 [5N SCOTTSVLE161.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -2.3246e-06 | -0.00034791
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2321 360338-361553(1) | OPEN LINE FROM BUS 360338 [5SCOTTSVL KY161.00] TO BUS 361553 [5N SCOTTSVLE161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2322 360338-361621(1) | OPEN LINE FROM BUS 360338 [5SCOTTSVL KY161.00] TO BUS 361621 [5ALVATON TP 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.2517e-06 | -0.00034684
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2322 360338-361621(1) | OPEN LINE FROM BUS 360338 [5SCOTTSVL KY161.00] TO BUS 361621 [5ALVATON TP 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2323 360342-361617(1) | OPEN LINE FROM BUS 360342 [5LIVINGST TN161.00] TO BUS 361617 [5MONROE TAP 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8358 | -5.6624e-06 | -0.00035125
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2323 360342-361617(1) | OPEN LINE FROM BUS 360342 [5LIVINGST TN161.00] TO BUS 361617 [5MONROE TAP 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2324 360342-361731(1) | OPEN LINE FROM BUS 360342 [5LIVINGST TN161.00] TO BUS 361731 [5RICKMAN TAP161.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8358 | -5.722e-06 | -0.00035131
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2324 360342-361731(1) | OPEN LINE FROM BUS 360342 [5LIVINGST TN161.00] TO BUS 361731 [5RICKMAN TAP161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2325 360352-360349(2) | OPEN LINE FROM BUS 360352 [5GALLATIN F1161.00] TO BUS 360349 [5LEBANON TN 161.00] CKT 2 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.1921e-06 | -0.00034678
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2325 360352-360349(2) | OPEN LINE FROM BUS 360352 [5GALLATIN F1161.00] TO BUS 360349 [5LEBANON TN 161.00] CKT 2 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2326 360352-360382(1) | OPEN LINE FROM BUS 360352 [5GALLATIN F1161.00] TO BUS 360382 [5HOEGANAES 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8359 | -2.9802e-06 | -0.00034857
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2326 360352-360382(1) | OPEN LINE FROM BUS 360352 [5GALLATIN F1161.00] TO BUS 360382 [5HOEGANAES 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2327 360352-360773(1) | OPEN LINE FROM BUS 360352 [5GALLATIN F1161.00] TO BUS 360773 [5WILSON #2 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 3.9339e-06 | -0.00034165
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2327 360352-360773(1) | OPEN LINE FROM BUS 360352 [5GALLATIN F1161.00] TO BUS 360773 [5WILSON #2 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2328 360352-361128(1) | OPEN LINE FROM BUS 360352 [5GALLATIN F1161.00] TO BUS 361128 [5LEBANON IPT161.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8361 | -1.4305e-06 | -0.00034702
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2328 360352-361128(1) | OPEN LINE FROM BUS 360352 [5GALLATIN F1161.00] TO BUS 361128 [5LEBANON IPT161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2329 360352-361714(1) | OPEN LINE FROM BUS 360352 [5GALLATIN F1161.00] TO BUS 361714 [5GAL SCRB TP161.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8365 | 5.4836e-06 | -0.0003401
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2329 360352-361714(1) | OPEN LINE FROM BUS 360352 [5GALLATIN F1161.00] TO BUS 361714 [5GAL SCRB TP161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2330 360352-361827(1) | OPEN LINE FROM BUS 360352 [5GALLATIN F1161.00] TO BUS 361827 [5W TROUSDALE161.00] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8371 | 1.4365e-05 | -0.00033122
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2330 360352-361827(1) | OPEN LINE FROM BUS 360352 [5GALLATIN F1161.00] TO BUS 361827 [5W TROUSDALE161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2331 360352-364121(1) | OPEN LINE FROM BUS 360352 [5GALLATIN F1161.00] TO BUS 364121 [1GALLATIN F124.000] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8373 | 1.6332e-05 | -0.00032926
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2331 360352-364121(1) | OPEN LINE FROM BUS 360352 [5GALLATIN F1161.00] TO BUS 364121 [1GALLATIN F124.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2332 360352-364122(2) | OPEN LINE FROM BUS 360352 [5GALLATIN F1161.00] TO BUS 364122 [1GALLATIN F224.000] CKT 2 | 0.93965 | 64.8362 | 0.93967 | 64.8373 | 1.6332e-05 | -0.00032926
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2332 360352-364122(2) | OPEN LINE FROM BUS 360352 [5GALLATIN F1161.00] TO BUS 364122 [1GALLATIN F224.000] CKT 2 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2333 360352-364221-364222(T1) | OPEN LINE FROM BUS 360352 [5GALLATIN F1161.00] TO BUS 364221 [1GALLATIN T113.800] TO BUS 364222 [1GALLATIN T213.800] CKT T1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 0 | -0.00034559
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2333 360352-364221-364222(T1) | OPEN LINE FROM BUS 360352 [5GALLATIN F1161.00] TO BUS 364221 [1GALLATIN T113.800] TO BUS 364222 [1GALLATIN T213.800] CKT T1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2334 360352-364223-364224(T2) | OPEN LINE FROM BUS 360352 [5GALLATIN F1161.00] TO BUS 364223 [1GALLATIN T313.800] TO BUS 364224 [1GALLATIN T413.800] CKT T2 | 0.93965 | 64.8362 | 0.93966 | 64.8365 | 5.3048e-06 | -0.00034028
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2334 360352-364223-364224(T2) | OPEN LINE FROM BUS 360352 [5GALLATIN F1161.00] TO BUS 364223 [1GALLATIN T313.800] TO BUS 364224 [1GALLATIN T413.800] CKT T2 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2335 360445-361542(1) | OPEN LINE FROM BUS 360445 [5BRAYTOWN TN161.00] TO BUS 361542 [5WINDROCK 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8365 | 5.6624e-06 | -0.00033993
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2335 360445-361542(1) | OPEN LINE FROM BUS 360445 [5BRAYTOWN TN161.00] TO BUS 361542 [5WINDROCK 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2337 360454-361330(1) | OPEN LINE FROM BUS 360454 [5CARYVILL TN161.00] TO BUS 361330 [5JACKSBRO TP161.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8363 | 2.6226e-06 | -0.00034297
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2337 360454-361330(1) | OPEN LINE FROM BUS 360454 [5CARYVILL TN161.00] TO BUS 361330 [5JACKSBRO TP161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2341 361113-360607(1) | OPEN LINE FROM BUS 361113 [5GLASGOW TP 161.00] TO BUS 360607 [5S GLASGOW 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 8.3447e-07 | -0.00034475
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2341 361113-360607(1) | OPEN LINE FROM BUS 361113 [5GLASGOW TP 161.00] TO BUS 360607 [5S GLASGOW 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2342 361114-360332(1) | OPEN LINE FROM BUS 361114 [5BRISTOW TAP161.00] TO BUS 360332 [5E BOWLGREEN161.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8368 | 8.7619e-06 | -0.00033683
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2342 361114-360332(1) | OPEN LINE FROM BUS 361114 [5BRISTOW TAP161.00] TO BUS 360332 [5E BOWLGREEN161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2343 361114-360335(1) | OPEN LINE FROM BUS 361114 [5BRISTOW TAP161.00] TO BUS 360335 [5BRISTOW KY 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8359 | -3.2783e-06 | -0.00034887
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2343 361114-360335(1) | OPEN LINE FROM BUS 361114 [5BRISTOW TAP161.00] TO BUS 360335 [5BRISTOW KY 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2344 361265-361827(1) | OPEN LINE FROM BUS 361265 [5HARTSVLE TP161.00] TO BUS 361827 [5W TROUSDALE161.00] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8371 | 1.3292e-05 | -0.0003323
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2344 361265-361827(1) | OPEN LINE FROM BUS 361265 [5HARTSVLE TP161.00] TO BUS 361827 [5W TROUSDALE161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2345 361267-360530(1) | OPEN LINE FROM BUS 361267 [5WESTMORELD 161.00] TO BUS 360530 [5ANGELTOWN 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8362 | 6.5565e-07 | -0.00034493
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2345 361267-360530(1) | OPEN LINE FROM BUS 361267 [5WESTMORELD 161.00] TO BUS 360530 [5ANGELTOWN 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2348 361603-360607(1) | OPEN LINE FROM BUS 361603 [5E GLASGOW T161.00] TO BUS 360607 [5S GLASGOW 161.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8365 | 4.8876e-06 | -0.0003407
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2348 361603-360607(1) | OPEN LINE FROM BUS 361603 [5E GLASGOW T161.00] TO BUS 360607 [5S GLASGOW 161.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 1.1921e-07 | 1.1921e-07
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2352 253006-253027(1) | OPEN LINE FROM BUS 253006 [09BATH 345.00] TO BUS 253027 [09GREENE 345.00] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8349 | -1.7583e-05 | -0.00036317
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2352 253006-253027(1) | OPEN LINE FROM BUS 253006 [09BATH 345.00] TO BUS 253027 [09GREENE 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2353 253013-253014(1) | OPEN LINE FROM BUS 253013 [09CLINTO 69.000] TO BUS 253014 [09CLINTO 345.00] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8348 | -1.9193e-05 | -0.00036478
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2353 253013-253014(1) | OPEN LINE FROM BUS 253013 [09CLINTO 69.000] TO BUS 253014 [09CLINTO 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2354 253013-253014(2) | OPEN LINE FROM BUS 253013 [09CLINTO 69.000] TO BUS 253014 [09CLINTO 345.00] CKT 2 | 0.93965 | 64.8362 | 0.93964 | 64.8348 | -1.9252e-05 | -0.00036484
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2354 253013-253014(2) | OPEN LINE FROM BUS 253013 [09CLINTO 69.000] TO BUS 253014 [09CLINTO 345.00] CKT 2 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2355 253013-253094(1) | OPEN LINE FROM BUS 253013 [09CLINTO 69.000] TO BUS 253094 [09WILMNG 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | -5.9605e-08 | -0.00034565
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2355 253013-253094(1) | OPEN LINE FROM BUS 253013 [09CLINTO 69.000] TO BUS 253094 [09WILMNG 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2356 253013-253094(2) | OPEN LINE FROM BUS 253013 [09CLINTO 69.000] TO BUS 253094 [09WILMNG 69.000] CKT 2 | 0.93965 | 64.8362 | 0.93965 | 64.836 | -1.8477e-06 | -0.00034744
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2356 253013-253094(2) | OPEN LINE FROM BUS 253013 [09CLINTO 69.000] TO BUS 253094 [09WILMNG 69.000] CKT 2 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2357 253014-253027(1) | OPEN LINE FROM BUS 253014 [09CLINTO 345.00] TO BUS 253027 [09GREENE 345.00] CKT 1 | 0.93965 | 64.8362 | 0.93901 | 64.7917 | -0.00064403 | -0.00098962
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2357 253014-253027(1) | OPEN LINE FROM BUS 253014 [09CLINTO 345.00] TO BUS 253027 [09GREENE 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2358 253026-253027(1) | OPEN LINE FROM BUS 253026 [09GREENE 138.00] TO BUS 253027 [09GREENE 345.00] CKT 1 | 0.93965 | 64.8362 | 0.93962 | 64.8335 | -3.8683e-05 | -0.00038427
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2358 253026-253027(1) | OPEN LINE FROM BUS 253026 [09GREENE 138.00] TO BUS 253027 [09GREENE 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2359 253026-253027(2) | OPEN LINE FROM BUS 253026 [09GREENE 138.00] TO BUS 253027 [09GREENE 345.00] CKT 2 | 0.93965 | 64.8362 | 0.93961 | 64.8334 | -4.0531e-05 | -0.00038612
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2359 253026-253027(2) | OPEN LINE FROM BUS 253026 [09GREENE 138.00] TO BUS 253027 [09GREENE 345.00] CKT 2 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2360 253027-253079(1) | OPEN LINE FROM BUS 253027 [09GREENE 345.00] TO BUS 253079 [09SUGRCK 345.00] CKT 1 | 0.93965 | 64.8362 | 0.93972 | 64.8404 | 6.175e-05 | -0.00028384
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2360 253027-253079(1) | OPEN LINE FROM BUS 253027 [09GREENE 345.00] TO BUS 253079 [09SUGRCK 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2361 253076-253077(1) | OPEN LINE FROM BUS 253076 [09STUART 138.00] TO BUS 253077 [09STUART 345.00] CKT 1 | 0.93965 | 64.8362 | 0.93947 | 64.8231 | -0.00018853 | -0.00053412
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2361 253076-253077(1) | OPEN LINE FROM BUS 253076 [09STUART 138.00] TO BUS 253077 [09STUART 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2362 253077-253100(1) | OPEN LINE FROM BUS 253077 [09STUART 345.00] TO BUS 253100 [09ATLNTA 345.00] CKT 1 | 0.93965 | 64.8362 | 0.93914 | 64.8009 | -0.00051051 | -0.0008561
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2362 253077-253100(1) | OPEN LINE FROM BUS 253077 [09STUART 345.00] TO BUS 253100 [09ATLNTA 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2363 253099-253100(1) | OPEN LINE FROM BUS 253099 [09ATLNTA 69.000] TO BUS 253100 [09ATLNTA 345.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8364 | 3.0994e-06 | -0.00034249
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2363 253099-253100(1) | OPEN LINE FROM BUS 253099 [09ATLNTA 69.000] TO BUS 253100 [09ATLNTA 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2364 253099-253181(1) | OPEN LINE FROM BUS 253099 [09ATLNTA 69.000] TO BUS 253181 [09NHOLLN 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93954 | 64.8282 | -0.00011569 | -0.00046128
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2364 253099-253181(1) | OPEN LINE FROM BUS 253099 [09ATLNTA 69.000] TO BUS 253181 [09NHOLLN 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2366 253006-253005(1) | OPEN LINE FROM BUS 253006 [09BATH 345.00] TO BUS 253005 [09BATH 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8352 | -1.353e-05 | -0.00035912
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2366 253006-253005(1) | OPEN LINE FROM BUS 253006 [09BATH 345.00] TO BUS 253005 [09BATH 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2367 253006-253005(2) | OPEN LINE FROM BUS 253006 [09BATH 345.00] TO BUS 253005 [09BATH 138.00] CKT 2 | 0.93965 | 64.8362 | 0.93964 | 64.8352 | -1.353e-05 | -0.00035912
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2367 253006-253005(2) | OPEN LINE FROM BUS 253006 [09BATH 345.00] TO BUS 253005 [09BATH 138.00] CKT 2 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2368 253006-253047(1) | OPEN LINE FROM BUS 253006 [09BATH 345.00] TO BUS 253047 [09MIAMI 345.00] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8375 | 1.955e-05 | -0.00032604
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2368 253006-253047(1) | OPEN LINE FROM BUS 253006 [09BATH 345.00] TO BUS 253047 [09MIAMI 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2369 253014-253310(1) | OPEN LINE FROM BUS 253014 [09CLINTO 345.00] TO BUS 253310 [AC1-085 POI 345.00] CKT 1 | 0.93965 | 64.8362 | 0.93868 | 64.7688 | -0.00097603 | -0.0013216
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2369 253014-253310(1) | OPEN LINE FROM BUS 253014 [09CLINTO 345.00] TO BUS 253310 [AC1-085 POI 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2370 253026-238623(1) | OPEN LINE FROM BUS 253026 [09GREENE 138.00] TO BUS 238623 [02CLARK 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93971 | 64.8399 | 5.4657e-05 | -0.00029093
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2370 253026-238623(1) | OPEN LINE FROM BUS 253026 [09GREENE 138.00] TO BUS 238623 [02CLARK 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2371 253026-253002(1) | OPEN LINE FROM BUS 253026 [09GREENE 138.00] TO BUS 253002 [09AIRWAY 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.835 | -1.7285e-05 | -0.00036287
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2371 253026-253002(1) | OPEN LINE FROM BUS 253026 [09GREENE 138.00] TO BUS 253002 [09AIRWAY 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2372 253026-253040(1) | OPEN LINE FROM BUS 253026 [09GREENE 138.00] TO BUS 253040 [09KNOLLW 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93962 | 64.834 | -3.1352e-05 | -0.00037694
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2372 253026-253040(1) | OPEN LINE FROM BUS 253026 [09GREENE 138.00] TO BUS 253040 [09KNOLLW 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2373 253026-253062(1) | OPEN LINE FROM BUS 253026 [09GREENE 138.00] TO BUS 253062 [09OVERL1 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93963 | 64.8348 | -1.9491e-05 | -0.00036508
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2373 253026-253062(1) | OPEN LINE FROM BUS 253026 [09GREENE 138.00] TO BUS 253062 [09OVERL1 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2374 253026-253083(1) | OPEN LINE FROM BUS 253026 [09GREENE 138.00] TO BUS 253083 [09TREBEI 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | 1.1921e-07 | -0.00034547
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2374 253026-253083(1) | OPEN LINE FROM BUS 253026 [09GREENE 138.00] TO BUS 253083 [09TREBEI 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2375 253026-253107(1) | OPEN LINE FROM BUS 253026 [09GREENE 138.00] TO BUS 253107 [09ALPHA 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93966 | 64.8365 | 5.4836e-06 | -0.0003401
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2375 253026-253107(1) | OPEN LINE FROM BUS 253026 [09GREENE 138.00] TO BUS 253107 [09ALPHA 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2376 253027-253248(1) | OPEN LINE FROM BUS 253027 [09GREENE 345.00] TO BUS 253248 [09MDISON 345.00] CKT 1 | 0.93965 | 64.8362 | 0.93972 | 64.8409 | 6.9261e-05 | -0.00027633
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2376 253027-253248(1) | OPEN LINE FROM BUS 253027 [09GREENE 345.00] TO BUS 253248 [09MDISON 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2381 253077-253310(1) | OPEN LINE FROM BUS 253077 [09STUART 345.00] TO BUS 253310 [AC1-085 POI 345.00] CKT 1 | 0.93965 | 64.8362 | 0.93901 | 64.7915 | -0.00064754 | -0.00099313
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2381 253077-253310(1) | OPEN LINE FROM BUS 253077 [09STUART 345.00] TO BUS 253310 [AC1-085 POI 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2382 253077-253352(1) | OPEN LINE FROM BUS 253077 [09STUART 345.00] TO BUS 253352 [AB1-169 MAIN345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2385 253079-253078(1) | OPEN LINE FROM BUS 253079 [09SUGRCK 345.00] TO BUS 253078 [09SUGRCK 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93963 | 64.8343 | -2.7478e-05 | -0.00037307
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2385 253079-253078(1) | OPEN LINE FROM BUS 253079 [09SUGRCK 345.00] TO BUS 253078 [09SUGRCK 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2386 253079-253078(2) | OPEN LINE FROM BUS 253079 [09SUGRCK 345.00] TO BUS 253078 [09SUGRCK 138.00] CKT 2 | 0.93965 | 64.8362 | 0.93963 | 64.8342 | -2.9027e-05 | -0.00037462
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2386 253079-253078(2) | OPEN LINE FROM BUS 253079 [09SUGRCK 345.00] TO BUS 253078 [09SUGRCK 138.00] CKT 2 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2387 253094-253043(1) | OPEN LINE FROM BUS 253094 [09WILMNG 69.000] TO BUS 253043 [09MRTNSV 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93958 | 64.8307 | -7.8976e-05 | -0.00042456
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2387 253094-253043(1) | OPEN LINE FROM BUS 253094 [09WILMNG 69.000] TO BUS 253043 [09MRTNSV 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2388 253094-253115(1) | OPEN LINE FROM BUS 253094 [09WILMNG 69.000] TO BUS 253115 [09AIRPRK 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93964 | 64.8351 | -1.4901e-05 | -0.00036049
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2388 253094-253115(1) | OPEN LINE FROM BUS 253094 [09WILMNG 69.000] TO BUS 253115 [09AIRPRK 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2389 253094-253131(1) | OPEN LINE FROM BUS 253094 [09WILMNG 69.000] TO BUS 253131 [09COL ST 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8359 | -3.6359e-06 | -0.00034922
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2389 253094-253131(1) | OPEN LINE FROM BUS 253094 [09WILMNG 69.000] TO BUS 253131 [09COL ST 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2390 253094-253237(1) | OPEN LINE FROM BUS 253094 [09WILMNG 69.000] TO BUS 253237 [09WEBBRD 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93963 | 64.8348 | -1.9431e-05 | -0.00036502
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2390 253094-253237(1) | OPEN LINE FROM BUS 253094 [09WILMNG 69.000] TO BUS 253237 [09WEBBRD 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2391 253099-253322(1) | OPEN LINE FROM BUS 253099 [09ATLNTA 69.000] TO BUS 253322 [AC1-069 MAIN69.000] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8372 | 1.5378e-05 | -0.00033021
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2391 253099-253322(1) | OPEN LINE FROM BUS 253099 [09ATLNTA 69.000] TO BUS 253322 [AC1-069 MAIN69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2392 253099-253330(1) | OPEN LINE FROM BUS 253099 [09ATLNTA 69.000] TO BUS 253330 [AC1-068 MAIN69.000] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.8372 | 1.5378e-05 | -0.00033021
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2392 253099-253330(1) | OPEN LINE FROM BUS 253099 [09ATLNTA 69.000] TO BUS 253330 [AC1-068 MAIN69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2393 253099-253335(1) | OPEN LINE FROM BUS 253099 [09ATLNTA 69.000] TO BUS 253335 [AC1-165 MAIN69.000] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.837 | 1.2338e-05 | -0.00033325
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2393 253099-253335(1) | OPEN LINE FROM BUS 253099 [09ATLNTA 69.000] TO BUS 253335 [AC1-165 MAIN69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2394 253099-253340(1) | OPEN LINE FROM BUS 253099 [09ATLNTA 69.000] TO BUS 253340 [AC1-166 MAIN69.000] CKT 1 | 0.93965 | 64.8362 | 0.93967 | 64.837 | 1.2338e-05 | -0.00033325
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2394 253099-253340(1) | OPEN LINE FROM BUS 253099 [09ATLNTA 69.000] TO BUS 253340 [AC1-166 MAIN69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2395 253100-245769(1) | OPEN LINE FROM BUS 253100 [09ATLNTA 345.00] TO BUS 245769 [05ADKINS 345.00] CKT 1 | 0.93965 | 64.8362 | 0.93919 | 64.804 | -0.00046551 | -0.0008111
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2395 253100-245769(1) | OPEN LINE FROM BUS 253100 [09ATLNTA 345.00] TO BUS 245769 [05ADKINS 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2396 253181-253201(1) | OPEN LINE FROM BUS 253181 [09NHOLLN 69.000] TO BUS 253201 [09ROBINS 69.000] CKT 1 | 0.93965 | 64.8362 | 0.93955 | 64.8288 | -0.00010681 | -0.0004524
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2396 253181-253201(1) | OPEN LINE FROM BUS 253181 [09NHOLLN 69.000] TO BUS 253201 [09ROBINS 69.000] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2397 248005-248013(1) | OPEN LINE FROM BUS 248005 [06KYGER 345.00] TO BUS 248013 [06PIERCE 345.00] CKT 1 | 0.93965 | 64.8362 | 0.93898 | 64.7898 | -0.00067109 | -0.0010167
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN LIN 2397 248005-248013(1) | OPEN LINE FROM BUS 248005 [06KYGER 345.00] TO BUS 248013 [06PIERCE 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2398 248005-242528(1) | OPEN LINE FROM BUS 248005 [06KYGER 345.00] TO BUS 242528 [05SPORN 345.00] CKT 1 | 0.93965 | 64.8362 | 0.93957 | 64.8302 | -8.5652e-05 | -0.00043124
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2398 248005-242528(1) | OPEN LINE FROM BUS 248005 [06KYGER 345.00] TO BUS 242528 [05SPORN 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2401 248005-248027-248026(1) | OPEN LINE FROM BUS 248005 [06KYGER 345.00] TO BUS 248027 [06KYGER 1LP 15.500] TO BUS 248026 [06KYGER 1HP 15.500] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | -5.9605e-08 | -0.00034565
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2401 248005-248027-248026(1) | OPEN LINE FROM BUS 248005 [06KYGER 345.00] TO BUS 248027 [06KYGER 1LP 15.500] TO BUS 248026 [06KYGER 1HP 15.500] CKT 1 | 1.05 | 525 | 1.05 | 525 | 1.1921e-07 | 1.1921e-07
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2402 248005-248029-248028(1) | OPEN LINE FROM BUS 248005 [06KYGER 345.00] TO BUS 248029 [06KYGER 2LP 15.500] TO BUS 248028 [06KYGER 2HP 15.500] CKT 1 | 0.93965 | 64.8362 | 0.9396 | 64.8324 | -5.4359e-05 | -0.00039995
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2402 248005-248029-248028(1) | OPEN LINE FROM BUS 248005 [06KYGER 345.00] TO BUS 248029 [06KYGER 2LP 15.500] TO BUS 248028 [06KYGER 2HP 15.500] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2403 248005-248031-248030(1) | OPEN LINE FROM BUS 248005 [06KYGER 345.00] TO BUS 248031 [06KYGER 3LP 15.500] TO BUS 248030 [06KYGER 3HP 15.500] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | -5.9605e-08 | -0.00034565
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2403 248005-248031-248030(1) | OPEN LINE FROM BUS 248005 [06KYGER 345.00] TO BUS 248031 [06KYGER 3LP 15.500] TO BUS 248030 [06KYGER 3HP 15.500] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2404 248005-248033-248032(1) | OPEN LINE FROM BUS 248005 [06KYGER 345.00] TO BUS 248033 [06KYGER 4LP 15.500] TO BUS 248032 [06KYGER 4HP 15.500] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | -5.9605e-08 | -0.00034565
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2404 248005-248033-248032(1) | OPEN LINE FROM BUS 248005 [06KYGER 345.00] TO BUS 248033 [06KYGER 4LP 15.500] TO BUS 248032 [06KYGER 4HP 15.500] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2405 248005-248035-248034(1) | OPEN LINE FROM BUS 248005 [06KYGER 345.00] TO BUS 248035 [06KYGER 5LP 15.500] TO BUS 248034 [06KYGER 5HP 15.500] CKT 1 | 0.93965 | 64.8362 | 0.93965 | 64.8362 | -5.9605e-08 | -0.00034565
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2405 248005-248035-248034(1) | OPEN LINE FROM BUS 248005 [06KYGER 345.00] TO BUS 248035 [06KYGER 5LP 15.500] TO BUS 248034 [06KYGER 5HP 15.500] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2406 248009-248008(SR) | OPEN LINE FROM BUS 248009 [06CLIFTY 138.00] TO BUS 248008 [06CLIFTX 138.00] CKT SR | 0.93965 | 64.8362 | 0.93978 | 64.8445 | 0.00012082 | -0.00022477
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2411 248013-248000(1) | OPEN LINE FROM BUS 248013 [06PIERCE 345.00] TO BUS 248000 [06CLIFTY 345.00] CKT 1 | 0.93965 | 64.8362 | 0.93893 | 64.786 | -0.00072724 | -0.0010728
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2411 248013-248000(1) | OPEN LINE FROM BUS 248013 [06PIERCE 345.00] TO BUS 248000 [06CLIFTY 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2412 248013-248000(2) | OPEN LINE FROM BUS 248013 [06PIERCE 345.00] TO BUS 248000 [06CLIFTY 345.00] CKT 2 | 0.93965 | 64.8362 | 0.93893 | 64.786 | -0.00072724 | -0.0010728
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2412 248013-248000(2) | OPEN LINE FROM BUS 248013 [06PIERCE 345.00] TO BUS 248000 [06CLIFTY 345.00] CKT 2 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2413 248013-248001(1) | OPEN LINE FROM BUS 248013 [06PIERCE 345.00] TO BUS 248001 [06DEARB1 345.00] CKT 1 | 0.93965 | 64.8362 | 0.93928 | 64.81 | -0.00037903 | -0.00072461
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2413 248013-248001(1) | OPEN LINE FROM BUS 248013 [06PIERCE 345.00] TO BUS 248001 [06DEARB1 345.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2416 248013-250086(17) | OPEN LINE FROM BUS 248013 [06PIERCE 345.00] TO BUS 250086 [08PIERCE 138.00] CKT 17 | 0.93965 | 64.8362 | 0.93929 | 64.8111 | -0.00036365 | -0.00070924
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2416 248013-250086(17) | OPEN LINE FROM BUS 248013 [06PIERCE 345.00] TO BUS 250086 [08PIERCE 138.00] CKT 17 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2417 248013-250143(18) | OPEN LINE FROM BUS 248013 [06PIERCE 345.00] TO BUS 250143 [08PRCE18 138.00] CKT 18 | 0.93965 | 64.8362 | 0.93927 | 64.8097 | -0.00038397 | -0.00072956
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2417 248013-250143(18) | OPEN LINE FROM BUS 248013 [06PIERCE 345.00] TO BUS 250143 [08PRCE18 138.00] CKT 18 | 1.05 | 525 | 1.05 | 525 | 0 | 0
341584 | 2GRIFFIN | 69 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2418 249736-249754(1) | OPEN LINE FROM BUS 249736 [08GRDALE 138.00] TO BUS 249754 [08HEHIDN 138.00] CKT 1 | 0.93965 | 64.8362 | 0.93893 | 64.786 | -0.0007267 | -0.0010723
342844 | 8SOUTHGEN | 500 | EKPC' | RANGE | 0.94 | 1.05 | SINGLE OPN TIE 2418 249736-249754(1) | OPEN LINE FROM BUS 249736 [08GRDALE 138.00] TO BUS 249754 [08HEHIDN 138.00] CKT 1 | 1.05 | 525 | 1.05 | 525 | 0 | 0

## Contingency Events
CONTINGENCY | EVENTS | CONVERGED | CONVERGENCE STATE | ISLANDS | MVAWORST | MVATOTAL | LOADS SHED | MWs SHED
BASE CASE | BASE CASE | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.4852
SINGLE OPN LIN 1 339206-342769(1) | OPEN LINE FROM BUS 339206 [AE1-143 C 161.00] TO BUS 342769 [5MARION CO 161.00] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.18892 | 10.5594
SINGLE OPN LIN 2 339206-939132(1) | OPEN LINE FROM BUS 339206 [AE1-143 C 161.00] TO BUS 939132 [AE1-143 E 161.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.41172 | 24.1895
SINGLE OPN LIN 3 341002-341443(1) | OPEN LINE FROM BUS 341002 [2AIRPORT RD 69.000] TO BUS 341443 [2ELLIO CO PT69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.6616
SINGLE OPN LIN 4 341002-341752(1) | OPEN LINE FROM BUS 341002 [2AIRPORT RD 69.000] TO BUS 341752 [2LEON 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.3985
SINGLE OPN LIN 5 341005-342181(1) | OPEN LINE FROM BUS 341005 [2ALBANY 69.000] TO BUS 342181 [2S ALBANY 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.39169 | 34.9761 | 1 | 7.995
SINGLE OPN LIN 6 341005-342283(1) | OPEN LINE FROM BUS 341005 [2ALBANY 69.000] TO BUS 342283 [2SNOW T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.28636 | 4.8163
SINGLE OPN LIN 7 341005-342397(1) | OPEN LINE FROM BUS 341005 [2ALBANY 69.000] TO BUS 342397 [2UPCHURCH T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.543
SINGLE OPN LIN 8 341008-342106(1) | OPEN LINE FROM BUS 341008 [2ALCAN 69.000] TO BUS 342106 [2PPG J 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.3485
SINGLE OPN LIN 9 341008-342430(1) | OPEN LINE FROM BUS 341008 [2ALCAN 69.000] TO BUS 342430 [2W BEREA 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.8969
SINGLE OPN LIN 10 341014-341017(1) | OPEN LINE FROM BUS 341014 [2ANNVILLE 69.000] TO BUS 341017 [2ANNVILLE T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.16551 | 20.9344 | 1 | 4.3545
SINGLE OPN LIN 11 341017-341428(1) | OPEN LINE FROM BUS 341017 [2ANNVILLE T 69.000] TO BUS 341428 [2EBERLE T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6083
SINGLE OPN LIN 12 341017-342391(1) | OPEN LINE FROM BUS 341017 [2ANNVILLE T 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.3415
SINGLE OPN LIN 13 341020-341782(1) | OPEN LINE FROM BUS 341020 [2ARGENTUM 69.000] TO BUS 341782 [2LOW GAP T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.36764 | 13.2113
SINGLE OPN LIN 14 341020-342538(1) | OPEN LINE FROM BUS 341020 [2ARGENTUM 69.000] TO BUS 342538 [4ARGENTUM 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.955
SINGLE OPN LIN 15 341029-341032(1) | OPEN LINE FROM BUS 341029 [2ASAHI M W 69.000] TO BUS 341032 [2ASAHI M W T69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.74851 | 52.2652 | 1 | 11.9039
SINGLE OPN LIN 16 341032-341379(1) | OPEN LINE FROM BUS 341032 [2ASAHI M W T69.000] TO BUS 341379 [2DAHL ROAD 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.4123
SINGLE OPN LIN 17 341032-342472(1) | OPEN LINE FROM BUS 341032 [2ASAHI M W T69.000] TO BUS 342472 [2WALNUT GROV69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.4283
SINGLE OPN LIN 18 341035-341038(1) | OPEN LINE FROM BUS 341035 [2BACON CRK 69.000] TO BUS 341038 [2BACON CRK T69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.16275 | 20.7476 | 1 | 4.3674
SINGLE OPN LIN 19 341038-341755(1) | OPEN LINE FROM BUS 341038 [2BACON CRK T69.000] TO BUS 341755 [2LIBER CH T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.9369
SINGLE OPN LIN 20 341038-342187(1) | OPEN LINE FROM BUS 341038 [2BACON CRK T69.000] TO BUS 342187 [2S CORBIN 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 3.479
SINGLE OPN LIN 21 341041-341635(1) | OPEN LINE FROM BUS 341041 [2BAKER LN 69.000] TO BUS 341635 [2HOLLOWAY 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.63107 | 46.3181 | 1 | 10.8215
SINGLE OPN LIN 22 341041-341638(1) | OPEN LINE FROM BUS 341041 [2BAKER LN 69.000] TO BUS 341638 [2HOLLOWAY J 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.347 | 17.7579
SINGLE OPN LIN 23 341041-342547(1) | OPEN LINE FROM BUS 341041 [2BAKER LN 69.000] TO BUS 342547 [4BAKER LN 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.41357 | 19.5713
SINGLE OPN LIN 24 341044-341671(1) | OPEN LINE FROM BUS 341044 [2BALLARD 69.000] TO BUS 341671 [2HUNT FARM J69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.0083
SINGLE OPN LIN 25 341044-342361(1) | OPEN LINE FROM BUS 341044 [2BALLARD 69.000] TO BUS 342361 [2TODDVILLE T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.2538
SINGLE OPN LIN 26 341047-342424(1) | OPEN LINE FROM BUS 341047 [2BALLTOWN 69.000] TO BUS 342424 [2W BARDST J 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.72852 | 51.2436 | 1 | 11.9528
SINGLE OPN LIN 27 341050-342295(1) | OPEN LINE FROM BUS 341050 [2BANK LCK 69.000] TO BUS 342295 [2STANLY P J169.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.84063 | 56.9779 | 1 | 13.3486
SINGLE OPN LIN 28 341053-341056(1) | OPEN LINE FROM BUS 341053 [2BARD SHOP 69.000] TO BUS 341056 [2BARD SHOP T69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.65199 | 47.4852 | 1 | 11.0844
SINGLE OPN LIN 29 341056-341407(1) | OPEN LINE FROM BUS 341056 [2BARD SHOP T69.000] TO BUS 341407 [2E BARDSTOWN69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.0892
SINGLE OPN LIN 30 341056-342424(1) | OPEN LINE FROM BUS 341056 [2BARD SHOP T69.000] TO BUS 342424 [2W BARDST J 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.7626
SINGLE OPN LIN 31 341059-341275(1) | OPEN LINE FROM BUS 341059 [2BARREN CO 69.000] TO BUS 341275 [2CAVE CITY J69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.0424
SINGLE OPN LIN 32 341059-341542(1) | OPEN LINE FROM BUS 341059 [2BARREN CO 69.000] TO BUS 341542 [2GOODNIGHT 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.3811
SINGLE OPN LIN 33 341059-341651(1) | OPEN LINE FROM BUS 341059 [2BARREN CO 69.000] TO BUS 341651 [2HORSECAVE J69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.62381 | 24.769
SINGLE OPN LIN 34 341059-342694(1) | OPEN LINE FROM BUS 341059 [2BARREN CO 69.000] TO BUS 342694 [5BARREN CO 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.9221
SINGLE OPN LIN 35 341062-341269(1) | OPEN LINE FROM BUS 341062 [2BASS 69.000] TO BUS 341269 [2CASEY CO 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.16763 | 20.7522 | 1 | 4.6051
SINGLE OPN LIN 36 341065-341068(1) | OPEN LINE FROM BUS 341065 [2BEAM 69.000] TO BUS 341068 [2BEAM T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.39595 | 34.8982 | 1 | 8.1995
SINGLE OPN LIN 37 341068-341215(1) | OPEN LINE FROM BUS 341068 [2BEAM T 69.000] TO BUS 341215 [2BULLITT CO 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.3991
SINGLE OPN LIN 38 341068-342253(1) | OPEN LINE FROM BUS 341068 [2BEAM T 69.000] TO BUS 342253 [2SHEPHEVIL J69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.15531 | 3.0312
SINGLE OPN LIN 39 341071-341074(1) | OPEN LINE FROM BUS 341071 [2BEATTYV 69.000] TO BUS 341074 [2BEATTYV D 69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.83865 | 56.6057 | 2 | 13.0124
SINGLE OPN LIN 40 341071-341077(1) | OPEN LINE FROM BUS 341071 [2BEATTYV 69.000] TO BUS 341077 [2BEATTYV J 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 4.4411
SINGLE OPN LIN 41 341071-342520(1) | OPEN LINE FROM BUS 341071 [2BEATTYV 69.000] TO BUS 342520 [2ZACHARIAH 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.2902
SINGLE OPN LIN 42 341074-341992(1) | OPEN LINE FROM BUS 341074 [2BEATTYV D 69.000] TO BUS 341992 [2OAKDALE 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.19684 | 24.2861 | 1 | 5.3401
SINGLE OPN LIN 43 341077-341173(1) | OPEN LINE FROM BUS 341077 [2BEATTYV J 69.000] TO BUS 341173 [2BOONEVIL T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 4.5148
SINGLE OPN LIN 44 341080-341149(1) | OPEN LINE FROM BUS 341080 [2BECKTON 69.000] TO BUS 341149 [2BON AYR 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.7623
SINGLE OPN LIN 45 341080-342445(1) | OPEN LINE FROM BUS 341080 [2BECKTON 69.000] TO BUS 342445 [2W GLASGOW T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.37748 | 8.0921
SINGLE OPN LIN 46 341089-342500(1) | OPEN LINE FROM BUS 341089 [2BEKAERT 69.000] TO BUS 342500 [2WIELAND 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.0982
SINGLE OPN LIN 47 341092-341095(1) | OPEN LINE FROM BUS 341092 [2BELLVIEW 69.000] TO BUS 341095 [2BELLVIEW T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.19539 | 23.5578 | 1 | 5.1645
SINGLE OPN LIN 48 341095-341164(1) | OPEN LINE FROM BUS 341095 [2BELLVIEW T 69.000] TO BUS 341164 [2BOONE CO 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.7634
SINGLE OPN LIN 49 341095-341227(1) | OPEN LINE FROM BUS 341095 [2BELLVIEW T 69.000] TO BUS 341227 [2BURLINGTN T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.5325
SINGLE OPN LIN 50 341098-342433(1) | OPEN LINE FROM BUS 341098 [2BEREAKU T 69.000] TO BUS 342433 [2W BEREA J 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 1.3656
SINGLE OPN LIN 51 341104-341107(1) | OPEN LINE FROM BUS 341104 [2BIG BONE 69.000] TO BUS 341107 [2BIG BONE T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 17.2948 | 1 | 3.3535
SINGLE OPN LIN 52 341107-341164(1) | OPEN LINE FROM BUS 341107 [2BIG BONE T 69.000] TO BUS 341164 [2BOONE CO 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6792
SINGLE OPN LIN 53 341107-341917(1) | OPEN LINE FROM BUS 341107 [2BIG BONE T 69.000] TO BUS 341917 [2MUNK 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.113
SINGLE OPN LIN 54 341110-341113(1) | OPEN LINE FROM BUS 341110 [2BIG CREEK 69.000] TO BUS 341113 [2BIG CREEK T69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.55346 | 42.3962 | 2 | 9.4652
SINGLE OPN LIN 55 341110-341439(1) | OPEN LINE FROM BUS 341110 [2BIG CREEK 69.000] TO BUS 341439 [2ELK MT IP 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.17853 | 22.583 | 1 | 4.7318
SINGLE OPN LIN 56 341113-341464(1) | OPEN LINE FROM BUS 341113 [2BIG CREEK T69.000] TO BUS 341464 [2FALL ROCK 69.000] CKT 1 | TRUE | Met convergence tolerances | 4 | 0.75675 | 52.6094 | 3 | 11.8301
SINGLE OPN LIN 57 341113-342001(1) | OPEN LINE FROM BUS 341113 [2BIG CREEK T69.000] TO BUS 342001 [2ONEIDA 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 15.8391 | 1 | 2.365
SINGLE OPN LIN 58 341114-341115(1) | OPEN LINE FROM BUS 341114 [2BIG HILL 69.000] TO BUS 341115 [2BIG HILL T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.20876 | 24.5422 | 1 | 5.202
SINGLE OPN LIN 59 341115-342223(1) | OPEN LINE FROM BUS 341115 [2BIG HILL T 69.000] TO BUS 342223 [2SAND GAP T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.5606
SINGLE OPN LIN 60 341115-342346(1) | OPEN LINE FROM BUS 341115 [2BIG HILL T 69.000] TO BUS 342346 [2THREE LINKS69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6539
SINGLE OPN LIN 61 341116-341119(1) | OPEN LINE FROM BUS 341116 [2BIG WOODS 69.000] TO BUS 341119 [2BIG WOODS J69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.20736 | 24.8131 | 1 | 5.4642
SINGLE OPN LIN 62 341119-341620(1) | OPEN LINE FROM BUS 341119 [2BIG WOODS J69.000] TO BUS 341620 [2HILDA 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 3.1851
SINGLE OPN LIN 63 341119-342088(1) | OPEN LINE FROM BUS 341119 [2BIG WOODS J69.000] TO BUS 342088 [2PLUMMR L T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.15632 | 5.3365
SINGLE OPN LIN 64 341122-341125(1) | OPEN LINE FROM BUS 341122 [2BILL WELL T69.000] TO BUS 341125 [2BILL WELLS 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.39966 | 34.9145 | 1 | 7.6338
SINGLE OPN LIN 65 341122-341692(1) | OPEN LINE FROM BUS 341122 [2BILL WELL T69.000] TO BUS 341692 [2JENNY WIL T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 4.2969
SINGLE OPN LIN 66 341122-341860(1) | OPEN LINE FROM BUS 341122 [2BILL WELL T69.000] TO BUS 341860 [2MIDDL CRK T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.1736
SINGLE OPN LIN 67 341131-341134(1) | OPEN LINE FROM BUS 341131 [2BLEVINS V T69.000] TO BUS 341134 [2BLEVINS VAL69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14177 | 16.57 | 1 | 2.7272
SINGLE OPN LIN 68 341131-341644(1) | OPEN LINE FROM BUS 341131 [2BLEVINS V T69.000] TO BUS 341644 [2HOPE 69.000] CKT 1 | FALSE | Iteration limit exceeded | 0 | 2.579 | 23.6382
SINGLE OPN LIN 69 341131-342112(1) | OPEN LINE FROM BUS 341131 [2BLEVINS V T69.000] TO BUS 342112 [2PRESTON T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.20835 | 4.864
SINGLE OPN LIN 70 341137-341296(1) | OPEN LINE FROM BUS 341137 [2BLOOMFLD 69.000] TO BUS 341296 [2CHAPLIN T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.3436
SINGLE OPN LIN 71 341137-341935(1) | OPEN LINE FROM BUS 341137 [2BLOOMFLD 69.000] TO BUS 341935 [2N SPRINGFLD69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6263
SINGLE OPN LIN 72 341140-341143(1) | OPEN LINE FROM BUS 341140 [2BLUE G PW 69.000] TO BUS 341143 [2BLUE G PW T69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.67123 | 48.1838 | 1 | 11.2397
SINGLE OPN LIN 73 341143-342019(1) | OPEN LINE FROM BUS 341143 [2BLUE G PW T69.000] TO BUS 342019 [2OWENS IL J 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.6328
SINGLE OPN LIN 74 341143-342508(1) | OPEN LINE FROM BUS 341143 [2BLUE G PW T69.000] TO BUS 342508 [2WOODLAWN 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.5225
SINGLE OPN LIN 75 341149-341272(1) | OPEN LINE FROM BUS 341149 [2BON AYR 69.000] TO BUS 341272 [2CAVE CITY 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.3047
SINGLE OPN LIN 76 341152-341155(1) | OPEN LINE FROM BUS 341152 [2BONANZA 69.000] TO BUS 341155 [2BONANZA T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.15255 | 20.1863 | 1 | 4.0496
SINGLE OPN LIN 77 341155-341803(1) | OPEN LINE FROM BUS 341155 [2BONANZA T 69.000] TO BUS 341803 [2MAGOFFIN CO69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.61956 | 9.5535
SINGLE OPN LIN 78 341155-341860(1) | OPEN LINE FROM BUS 341155 [2BONANZA T 69.000] TO BUS 341860 [2MIDDL CRK T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.1453
SINGLE OPN LIN 79 341158-341161(1) | OPEN LINE FROM BUS 341158 [2BONNIV DIST69.000] TO BUS 341161 [2BONNIV EK 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.19603 | 14.7007
SINGLE OPN LIN 80 341158-341908(1) | OPEN LINE FROM BUS 341158 [2BONNIV DIST69.000] TO BUS 341908 [2MUNFVIL EK 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.1888 | 14.6126
SINGLE OPN LIN 81 341161-342403(1) | OPEN LINE FROM BUS 341161 [2BONNIV EK 69.000] TO BUS 342403 [2UPTON T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.9227
SINGLE OPN LIN 82 341164-341167(1) | OPEN LINE FROM BUS 341164 [2BOONE CO 69.000] TO BUS 341167 [2BOONE DIST 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.76272 | 52.8566 | 1 | 12.5148
SINGLE OPN LIN 83 341164-342388(1) | OPEN LINE FROM BUS 341164 [2BOONE CO 69.000] TO BUS 342388 [2TURKEY FT J69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.5927
SINGLE OPN LIN 84 341164-342466(1) | OPEN LINE FROM BUS 341164 [2BOONE CO 69.000] TO BUS 342466 [2W R SMOOT 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.24351 | 17.6444 | 1 | 23.4435
SINGLE OPN LIN 85 341164-342559(1) | OPEN LINE FROM BUS 341164 [2BOONE CO 69.000] TO BUS 342559 [4BOONE CO 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.3908
SINGLE OPN LIN 86 341170-341173(1) | OPEN LINE FROM BUS 341170 [2BOONEVIL 69.000] TO BUS 341173 [2BOONEVIL T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.16687 | 21.1277 | 1 | 4.449
SINGLE OPN LIN 87 341173-342196(1) | OPEN LINE FROM BUS 341173 [2BOONEVIL T 69.000] TO BUS 342196 [2WHITE OAK 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 3.0414
SINGLE OPN LIN 88 341179-341746(1) | OPEN LINE FROM BUS 341179 [2BOSTONKU 69.000] TO BUS 341746 [2LEBANON J 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6808
SINGLE OPN LIN 89 341179-342514(1) | OPEN LINE FROM BUS 341179 [2BOSTONKU 69.000] TO BUS 342514 [2WOOSLEY 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6696
SINGLE OPN LIN 90 341185-341614(1) | OPEN LINE FROM BUS 341185 [2BOWEN 69.000] TO BUS 341614 [2HIGH ROCK 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 4.5842
SINGLE OPN LIN 91 341185-342100(1) | OPEN LINE FROM BUS 341185 [2BOWEN 69.000] TO BUS 342100 [2POWELL CO 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 5.3067
SINGLE OPN LIN 92 341188-341488(1) | OPEN LINE FROM BUS 341188 [2BRACKEN CO 69.000] TO BUS 341488 [2FOUR OAKS T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.5048
SINGLE OPN LIN 93 341188-341587(1) | OPEN LINE FROM BUS 341188 [2BRACKEN CO 69.000] TO BUS 341587 [2GRIFFIN J 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.4478
SINGLE OPN LIN 94 341194-342385(1) | OPEN LINE FROM BUS 341194 [2BRISTOW 69.000] TO BUS 342385 [2TURKEY FT 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.3797
SINGLE OPN LIN 95 341194-342388(1) | OPEN LINE FROM BUS 341194 [2BRISTOW 69.000] TO BUS 342388 [2TURKEY FT J69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.15082 | 2.4641
SINGLE OPN LIN 96 341197-341818(1) | OPEN LINE FROM BUS 341197 [2BRODHEAD 69.000] TO BUS 341818 [2MARETBURG T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.1189
SINGLE OPN LIN 97 341197-342349(1) | OPEN LINE FROM BUS 341197 [2BRODHEAD 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.4349
SINGLE OPN LIN 98 341200-341920(1) | OPEN LINE FROM BUS 341200 [2BROMLEYEK 69.000] TO BUS 341920 [2MUNK J 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.46364 | 5.4209
SINGLE OPN LIN 99 341200-342010(1) | OPEN LINE FROM BUS 341200 [2BROMLEYEK 69.000] TO BUS 342010 [2OWEN CO J1 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.36601 | 18.182
SINGLE OPN LIN 100 341203-341206(1) | OPEN LINE FROM BUS 341203 [2BRONSTON 69.000] TO BUS 341206 [2BRONSTON T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.82207 | 56.1937 | 1 | 13.1724
SINGLE OPN LIN 101 341206-341347(1) | OPEN LINE FROM BUS 341206 [2BRONSTON T 69.000] TO BUS 341347 [2COOPER DIST69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.3481
SINGLE OPN LIN 102 341206-341392(1) | OPEN LINE FROM BUS 341206 [2BRONSTON T 69.000] TO BUS 341392 [2DENNY 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.3652
SINGLE OPN LIN 103 341209-341210(1) | OPEN LINE FROM BUS 341209 [2BROUGTWN T 69.000] TO BUS 341210 [2BROUGHT TWN69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.16699 | 20.9693 | 1 | 4.4578
SINGLE OPN LIN 104 341209-341617(1) | OPEN LINE FROM BUS 341209 [2BROUGTWN T 69.000] TO BUS 341617 [2HIGHLAND EK69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.337
SINGLE OPN LIN 105 341209-342367(1) | OPEN LINE FROM BUS 341209 [2BROUGTWN T 69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.5452
SINGLE OPN LIN 106 341212-341774(1) | OPEN LINE FROM BUS 341212 [2BUDD 69.000] TO BUS 341774 [2LOGAN 2 T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.3326
SINGLE OPN LIN 107 341212-342500(1) | OPEN LINE FROM BUS 341212 [2BUDD 69.000] TO BUS 342500 [2WIELAND 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.7055
SINGLE OPN LIN 108 341215-341281(1) | OPEN LINE FROM BUS 341215 [2BULLITT CO 69.000] TO BUS 341281 [2CEDAR GR 69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.37097 | 25.531 | 2 | 34.729
SINGLE OPN LIN 109 341215-341389(1) | OPEN LINE FROM BUS 341215 [2BULLITT CO 69.000] TO BUS 341389 [2DEATSVILL T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.9662
SINGLE OPN LIN 110 341215-342700(1) | OPEN LINE FROM BUS 341215 [2BULLITT CO 69.000] TO BUS 342700 [5BULLITT CO 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.86901 | 34.3913
SINGLE OPN LIN 111 341218-341227(1) | OPEN LINE FROM BUS 341218 [2BULLITTSVIL69.000] TO BUS 341227 [2BURLINGTN T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.4187
SINGLE OPN LIN 112 341218-341605(1) | OPEN LINE FROM BUS 341218 [2BULLITTSVIL69.000] TO BUS 341605 [2HEBRON 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.16036 | 2.5328
SINGLE OPN LIN 113 341224-341227(1) | OPEN LINE FROM BUS 341224 [2BURLINGTN 69.000] TO BUS 341227 [2BURLINGTN T69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.40456 | 35.1256 | 1 | 8.1595
SINGLE OPN LIN 114 341233-341974(1) | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 341974 [2NORWOOD T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.731
SINGLE OPN LIN 115 341233-342286(1) | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.39884 | 19.2831
SINGLE OPN LIN 116 341248-341608(1) | OPEN LINE FROM BUS 341248 [2CAMPTON 69.000] TO BUS 341608 [2HELECHAW 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.3462
SINGLE OPN LIN 117 341248-342520(1) | OPEN LINE FROM BUS 341248 [2CAMPTON 69.000] TO BUS 342520 [2ZACHARIAH 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14991 | 6.5995
SINGLE OPN LIN 118 341251-341254(1) | OPEN LINE FROM BUS 341251 [2CANE RIDG 69.000] TO BUS 341254 [2CANE RIDG T69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 3.0539 | 1 | 0.37481
SINGLE OPN LIN 119 341254-341872(1) | OPEN LINE FROM BUS 341254 [2CANE RIDG T69.000] TO BUS 341872 [2MILLB-CRL J69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.2794 | 4.9612
SINGLE OPN LIN 120 341254-342259(1) | OPEN LINE FROM BUS 341254 [2CANE RIDG T69.000] TO BUS 342259 [2SIDEVIEW 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.27798 | 4.9544
SINGLE OPN LIN 121 341260-342013(1) | OPEN LINE FROM BUS 341260 [2CARSON 69.000] TO BUS 342013 [2OWEN CO J2 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.22718 | 25.7636 | 1 | 5.8918
SINGLE OPN LIN 122 341263-341266(1) | OPEN LINE FROM BUS 341263 [2CARTER CTY 69.000] TO BUS 341266 [2CARTER CY T69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 18.4244 | 1 | 3.7198
SINGLE OPN LIN 123 341266-342034(1) | OPEN LINE FROM BUS 341266 [2CARTER CY T69.000] TO BUS 342034 [2PACTOLUS T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.4181
SINGLE OPN LIN 124 341266-342475(1) | OPEN LINE FROM BUS 341266 [2CARTER CY T69.000] TO BUS 342475 [2WARNOCK 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.0967
SINGLE OPN LIN 125 341269-342064(1) | OPEN LINE FROM BUS 341269 [2CASEY CO 69.000] TO BUS 342064 [2PEYTONS ST 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.708
SINGLE OPN LIN 126 341269-342703(1) | OPEN LINE FROM BUS 341269 [2CASEY CO 69.000] TO BUS 342703 [5CASEY CO 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 3.3681
SINGLE OPN LIN 127 341272-341275(1) | OPEN LINE FROM BUS 341272 [2CAVE CITY 69.000] TO BUS 341275 [2CAVE CITY J69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.0313
SINGLE OPN LIN 128 341275-342241(1) | OPEN LINE FROM BUS 341275 [2CAVE CITY J69.000] TO BUS 342241 [2SEYMOUR T 69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.15028 | 18.564 | 1 | 3.7942
SINGLE OPN LIN 129 341281-342082(1) | OPEN LINE FROM BUS 341281 [2CEDAR GR 69.000] TO BUS 342082 [2PLEAS GRV 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.27307 | 19.5582 | 1 | 26.1472
SINGLE OPN LIN 130 341287-341713(1) | OPEN LINE FROM BUS 341287 [2CENT HARDIN69.000] TO BUS 341713 [2KARGLE 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.7376
SINGLE OPN LIN 131 341287-342307(1) | OPEN LINE FROM BUS 341287 [2CENT HARDIN69.000] TO BUS 342307 [2STEPHENSBRG69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.44396 | 20.8368
SINGLE OPN LIN 132 341287-342568(1) | OPEN LINE FROM BUS 341287 [2CENT HARDIN69.000] TO BUS 342568 [4CENT HARDIN138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.18295 | 2.6406
SINGLE OPN LIN 133 341293-341296(1) | OPEN LINE FROM BUS 341293 [2CHAPLIN 69.000] TO BUS 341296 [2CHAPLIN T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.16362 | 14.9502 | 1 | 1.4053
SINGLE OPN LIN 134 341296-342262(1) | OPEN LINE FROM BUS 341296 [2CHAPLIN T 69.000] TO BUS 342262 [2SINAI 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.15129 | 3.0985
SINGLE OPN LIN 135 341299-341989(1) | OPEN LINE FROM BUS 341299 [2CHARTERS 69.000] TO BUS 341989 [2OAK RIDGE T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.7466
SINGLE OPN LIN 136 341299-342124(1) | OPEN LINE FROM BUS 341299 [2CHARTERS 69.000] TO BUS 342124 [2RECTORVILLE69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.7016
SINGLE OPN LIN 137 341302-341305(1) | OPEN LINE FROM BUS 341302 [2CLAY CITY 69.000] TO BUS 341305 [2CLAY CITY T69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.43656 | 36.778 | 1 | 8.5542
SINGLE OPN LIN 138 341305-341593(1) | OPEN LINE FROM BUS 341305 [2CLAY CITY T69.000] TO BUS 341593 [2HARDWCRK T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.5562
SINGLE OPN LIN 139 341305-341599(1) | OPEN LINE FROM BUS 341305 [2CLAY CITY T69.000] TO BUS 341599 [2HARGETT T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.7126
SINGLE OPN LIN 140 341308-341314(1) | OPEN LINE FROM BUS 341308 [2CLAY LCK 69.000] TO BUS 341314 [2CLAY LCK SW69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.25971 | 28.0564 | 1 | 6.1845
SINGLE OPN LIN 141 341311-341314(1) | OPEN LINE FROM BUS 341311 [2CLAY LCK J 69.000] TO BUS 341314 [2CLAY LCK SW69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.25968 | 28.1195 | 1 | 6.1845
SINGLE OPN LIN 142 341311-342184(1) | OPEN LINE FROM BUS 341311 [2CLAY LCK J 69.000] TO BUS 342184 [2S ANDERSON 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.4137 | 19.0188
SINGLE OPN LIN 143 341311-342406(1) | OPEN LINE FROM BUS 341311 [2CLAY LCK J 69.000] TO BUS 342406 [2VAN ARSDELL69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.37163 | 17.9539
SINGLE OPN LIN 144 341317-341390(1) | OPEN LINE FROM BUS 341317 [2CLAY VILLAG69.000] TO BUS 341390 [2DEFOE TAP 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.82533 | 5.9428
SINGLE OPN LIN 145 341320-341512(1) | OPEN LINE FROM BUS 341320 [2COBURG 69.000] TO BUS 341512 [2GARLIN T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.3587
SINGLE OPN LIN 146 341323-341335(1) | OPEN LINE FROM BUS 341323 [2COBURG J 69.000] TO BUS 341335 [2COLUMBIA 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.8985
SINGLE OPN LIN 147 341323-341512(1) | OPEN LINE FROM BUS 341323 [2COBURG J 69.000] TO BUS 341512 [2GARLIN T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.8938
SINGLE OPN LIN 148 341323-342235(1) | OPEN LINE FROM BUS 341323 [2COBURG J 69.000] TO BUS 342235 [2SEWELTN J 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6076
SINGLE OPN LIN 149 341326-341488(1) | OPEN LINE FROM BUS 341326 [2COLEMANSVIL69.000] TO BUS 341488 [2FOUR OAKS T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14643 | 2.2454
SINGLE OPN LIN 150 341326-342133(1) | OPEN LINE FROM BUS 341326 [2COLEMANSVIL69.000] TO BUS 342133 [2RENAKER 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.2151
SINGLE OPN LIN 151 341329-341332(1) | OPEN LINE FROM BUS 341329 [2COLESBURG 69.000] TO BUS 341332 [2COLESBURG J69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 16.5689 | 1 | 2.9494
SINGLE OPN LIN 152 341332-341944(1) | OPEN LINE FROM BUS 341332 [2COLESBURG J69.000] TO BUS 341944 [2NELSON CO 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.5292
SINGLE OPN LIN 153 341332-342155(1) | OPEN LINE FROM BUS 341332 [2COLESBURG J69.000] TO BUS 342155 [2ROANOKE T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.446
SINGLE OPN LIN 154 341335-341370(1) | OPEN LINE FROM BUS 341335 [2COLUMBIA 69.000] TO BUS 341370 [2COLUMB S KU69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.14287 | 7.7795 | 2 | 10.7
SINGLE OPN LIN 155 341335-342436(1) | OPEN LINE FROM BUS 341335 [2COLUMBIA 69.000] TO BUS 342436 [2W COLUMBI T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.7082
SINGLE OPN LIN 156 341338-341341(1) | OPEN LINE FROM BUS 341338 [2CONWAY 69.000] TO BUS 341341 [2CONWAY T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.16355 | 20.4542 | 1 | 4.2596
SINGLE OPN LIN 157 341341-342346(1) | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342346 [2THREE LINKS69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.0108
SINGLE OPN LIN 158 341341-342349(1) | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.5942
SINGLE OPN LIN 159 341342-341343(1) | OPEN LINE FROM BUS 341342 [2CONTOWN T 69.000] TO BUS 341343 [2CONTOWN 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 15.5132 | 1 | 2.2548
SINGLE OPN LIN 160 341342-341761(1) | OPEN LINE FROM BUS 341342 [2CONTOWN T 69.000] TO BUS 341761 [2LIBERTY J 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.6318
SINGLE OPN LIN 161 341342-342067(1) | OPEN LINE FROM BUS 341342 [2CONTOWN T 69.000] TO BUS 342067 [2PHIL 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.6061
SINGLE OPN LIN 162 341344-341347(1) | OPEN LINE FROM BUS 341344 [2COOPER 69.000] TO BUS 341347 [2COOPER DIST69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.3532
SINGLE OPN LIN 163 341344-342286(1) | OPEN LINE FROM BUS 341344 [2COOPER 69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.3414
SINGLE OPN LIN 164 341344-342286(2) | OPEN LINE FROM BUS 341344 [2COOPER 69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 2 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.3414
SINGLE OPN LIN 165 341344-342715(1) | OPEN LINE FROM BUS 341344 [2COOPER 69.000] TO BUS 342715 [5COOPER1 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6453
SINGLE OPN LIN 166 341350-342067(1) | OPEN LINE FROM BUS 341350 [2CRESTON 69.000] TO BUS 342067 [2PHIL 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.22205 | 25.5897 | 1 | 5.7798
SINGLE OPN LIN 167 341353-341356(1) | OPEN LINE FROM BUS 341353 [2CROCKETT 69.000] TO BUS 341356 [2CROCKETT T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 17.7831 | 1 | 3.3314
SINGLE OPN LIN 168 341356-341653(1) | OPEN LINE FROM BUS 341356 [2CROCKETT T 69.000] TO BUS 341653 [2HOT MIX R T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6215
SINGLE OPN LIN 169 341356-342265(1) | OPEN LINE FROM BUS 341356 [2CROCKETT T 69.000] TO BUS 342265 [2SKAGGS 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 3.6116
SINGLE OPN LIN 170 341359-341362(1) | OPEN LINE FROM BUS 341359 [2CROOKSVIL 69.000] TO BUS 341362 [2CROOKSVIL T69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.32808 | 31.8109 | 2 | 7.195
SINGLE OPN LIN 171 341359-342288(1) | OPEN LINE FROM BUS 341359 [2CROOKSVIL 69.000] TO BUS 342288 [2SPEEDWELL 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.17514 | 14.9878 | 1 | 1.3
SINGLE OPN LIN 172 341362-341406(1) | OPEN LINE FROM BUS 341362 [2CROOKSVIL T69.000] TO BUS 341406 [2DUNCAN LN T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.1392
SINGLE OPN LIN 173 341362-341611(1) | OPEN LINE FROM BUS 341362 [2CROOKSVIL T69.000] TO BUS 341611 [2HICKORY PL 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.8035
SINGLE OPN LIN 174 341366-341370(1) | OPEN LINE FROM BUS 341366 [2COLUMB KU 69.000] TO BUS 341370 [2COLUMB S KU69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.59273 | 28.177 | 1 | 6.29
SINGLE OPN LIN 175 341377-341602(1) | OPEN LINE FROM BUS 341377 [2CYNTHIA TIE69.000] TO BUS 341602 [2HEADQTRS 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.27452 | 3.0094
SINGLE OPN LIN 176 341377-342355(1) | OPEN LINE FROM BUS 341377 [2CYNTHIA TIE69.000] TO BUS 342355 [2THREE M T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.4478 | 4.2379
SINGLE OPN LIN 177 341379-342256(1) | OPEN LINE FROM BUS 341379 [2DAHL ROAD 69.000] TO BUS 342256 [2SHOPVILLE 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.393
SINGLE OPN LIN 178 341380-341959(1) | OPEN LINE FROM BUS 341380 [2DALE 69.000] TO BUS 341959 [2NEWBY 1 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.2231
SINGLE OPN LIN 179 341380-341962(1) | OPEN LINE FROM BUS 341380 [2DALE 69.000] TO BUS 341962 [2NEWBY 2 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.7162
SINGLE OPN LIN 180 341380-342574(1) | OPEN LINE FROM BUS 341380 [2DALE 69.000] TO BUS 342574 [4DALE 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.4962
SINGLE OPN LIN 181 341381-341382(1) | OPEN LINE FROM BUS 341381 [2DAV LANE 69.000] TO BUS 341382 [2DAV LANE T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.95831 | 62.8115 | 1 | 14
SINGLE OPN LIN 182 341382-341734(1) | OPEN LINE FROM BUS 341382 [2DAV LANE T 69.000] TO BUS 341734 [2LAUR C IP T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.5649
SINGLE OPN LIN 183 341382-342451(1) | OPEN LINE FROM BUS 341382 [2DAV LANE T 69.000] TO BUS 342451 [2W LONDON 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.5679
SINGLE OPN LIN 184 341383-341467(1) | OPEN LINE FROM BUS 341383 [2DAVIS 69.000] TO BUS 341467 [2FAYETTE 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.1253
SINGLE OPN LIN 185 341383-341965(1) | OPEN LINE FROM BUS 341383 [2DAVIS 69.000] TO BUS 341965 [2NICHOLASVIL69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.9127
SINGLE OPN LIN 186 341386-341389(1) | OPEN LINE FROM BUS 341386 [2DEATSVIL 69.000] TO BUS 341389 [2DEATSVILL T69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.38173 | 34.212 | 1 | 7.9864
SINGLE OPN LIN 187 341389-341707(1) | OPEN LINE FROM BUS 341389 [2DEATSVILL T69.000] TO BUS 341707 [2JOE TICH T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.913
SINGLE OPN LIN 188 341390-341391(1) | OPEN LINE FROM BUS 341390 [2DEFOE TAP 69.000] TO BUS 341391 [2DEFOE 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.15949 | 19.338 | 1 | 4.021
SINGLE OPN LIN 189 341390-341950(1) | OPEN LINE FROM BUS 341390 [2DEFOE TAP 69.000] TO BUS 341950 [2NEW CASTLE 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.3913
SINGLE OPN LIN 190 341392-341578(1) | OPEN LINE FROM BUS 341392 [2DENNY 69.000] TO BUS 341578 [2GREGORY R T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.7193
SINGLE OPN LIN 191 341392-342499(1) | OPEN LINE FROM BUS 341392 [2DENNY 69.000] TO BUS 342499 [2WIBORG T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.6918
SINGLE OPN LIN 192 341392-342727(1) | OPEN LINE FROM BUS 341392 [2DENNY 69.000] TO BUS 342727 [5DENNY 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6132
SINGLE OPN LIN 193 341394-341479(1) | OPEN LINE FROM BUS 341394 [2PATRIOT PW 69.000] TO BUS 341479 [2S BOUND RD 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.26135 | 28.3201 | 1 | 6.5271
SINGLE OPN LIN 194 341394-342151(1) | OPEN LINE FROM BUS 341394 [2PATRIOT PW 69.000] TO BUS 342151 [2RINEYVILLE 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.21082 | 24.8914 | 1 | 5.6071
SINGLE OPN LIN 195 341394-342157(1) | OPEN LINE FROM BUS 341394 [2PATRIOT PW 69.000] TO BUS 342157 [2ROGERSVIL J69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.7605
SINGLE OPN LIN 196 341394-342274(1) | OPEN LINE FROM BUS 341394 [2PATRIOT PW 69.000] TO BUS 342274 [2SMITHRVIL T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.2909
SINGLE OPN LIN 197 341398-341605(1) | OPEN LINE FROM BUS 341398 [2DOWNING 69.000] TO BUS 341605 [2HEBRON 69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.24722 | 17.832 | 2 | 23.5626
SINGLE OPN LIN 198 341398-341880(1) | OPEN LINE FROM BUS 341398 [2DOWNING 69.000] TO BUS 341880 [2MINEOLA PKE69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.75215 | 51.9801 | 1 | 12.222
SINGLE OPN LIN 199 341400-342091(1) | OPEN LINE FROM BUS 341400 [2DRAVO 69.000] TO BUS 342091 [2PLUMVILLE 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 15.9066 | 1 | 2.641
SINGLE OPN LIN 200 341401-341842(1) | OPEN LINE FROM BUS 341401 [2DURO 69.000] TO BUS 341842 [2MBUSA T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.47549 | 38.7875 | 1 | 8.9714
SINGLE OPN LIN 201 341404-341842(1) | OPEN LINE FROM BUS 341404 [2DURO T 69.000] TO BUS 341842 [2MBUSA T 69.000] CKT 1 | TRUE | Met convergence tolerances | 3 | 0.24563 | 17.9257 | 2 | 23.5079
SINGLE OPN LIN 202 341404-342295(1) | OPEN LINE FROM BUS 341404 [2DURO T 69.000] TO BUS 342295 [2STANLY P J169.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.7375
SINGLE OPN LIN 203 341404-342388(1) | OPEN LINE FROM BUS 341404 [2DURO T 69.000] TO BUS 342388 [2TURKEY FT J69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.17384 | 2.6127
SINGLE OPN LIN 204 341405-341406(1) | OPEN LINE FROM BUS 341405 [2DUNCANNO LN69.000] TO BUS 341406 [2DUNCAN LN T69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14788 | 18.5328 | 1 | 3.7451
SINGLE OPN LIN 205 341407-342019(1) | OPEN LINE FROM BUS 341407 [2E BARDSTOWN69.000] TO BUS 342019 [2OWENS IL J 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.48 | 19.7702
SINGLE OPN LIN 206 341410-341929(1) | OPEN LINE FROM BUS 341410 [2E BERNSTADT69.000] TO BUS 341929 [2N LONDON 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.32864 | 31.7463 | 1 | 6.944
SINGLE OPN LIN 207 341416-342076(1) | OPEN LINE FROM BUS 341416 [2E PINE KNOT69.000] TO BUS 342076 [2PINE KNOT 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.1606 | 20.1953 | 1 | 4.2639
SINGLE OPN LIN 208 341419-341422(1) | OPEN LINE FROM BUS 341419 [2E SOMERSE T69.000] TO BUS 341422 [2E SOMERSET 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.43338 | 36.6302 | 1 | 8.3699
SINGLE OPN LIN 209 341419-341941(1) | OPEN LINE FROM BUS 341419 [2E SOMERSE T69.000] TO BUS 341941 [2NELSN VAL T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.3997
SINGLE OPN LIN 210 341419-341974(1) | OPEN LINE FROM BUS 341419 [2E SOMERSE T69.000] TO BUS 341974 [2NORWOOD T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.3657
SINGLE OPN LIN 211 341425-341428(1) | OPEN LINE FROM BUS 341425 [2EBERLE 69.000] TO BUS 341428 [2EBERLE T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.182 | 22.5882 | 1 | 4.738
SINGLE OPN LIN 212 341428-341809(1) | OPEN LINE FROM BUS 341428 [2EBERLE T 69.000] TO BUS 341809 [2MAPLESVIL T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.03
SINGLE OPN LIN 213 341431-341434(1) | OPEN LINE FROM BUS 341431 [2EDM-JBGAL J69.000] TO BUS 341434 [2EDM-JBGAL T69.000] CKT 1 | TRUE | Met convergence tolerances | 3 | 0.4566 | 38.0272 | 2 | 8.9524
SINGLE OPN LIN 214 341431-341728(1) | OPEN LINE FROM BUS 341431 [2EDM-JBGAL J69.000] TO BUS 341728 [2KNOB LICK 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.6377
SINGLE OPN LIN 215 341431-342322(1) | OPEN LINE FROM BUS 341431 [2EDM-JBGAL J69.000] TO BUS 342322 [2SUMM SHADE 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.8943
SINGLE OPN LIN 216 341434-341437(1) | OPEN LINE FROM BUS 341434 [2EDM-JBGAL T69.000] TO BUS 341437 [2EDMON IND P69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.15853 | 15.0353 | 1 | 1.5349
SINGLE OPN LIN 217 341434-341680(1) | OPEN LINE FROM BUS 341434 [2EDM-JBGAL T69.000] TO BUS 341680 [2JB GALLOWAY69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.33006 | 32.0693 | 1 | 7.4175
SINGLE OPN LIN 218 341443-341446(1) | OPEN LINE FROM BUS 341443 [2ELLIO CO PT69.000] TO BUS 341446 [2ELLIOT CO P69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.65577 | 47.8589 | 1 | 10.6457
SINGLE OPN LIN 219 341443-341953(1) | OPEN LINE FROM BUS 341443 [2ELLIO CO PT69.000] TO BUS 341953 [2NEW FOUNDL 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.1039
SINGLE OPN LIN 220 341449-342163(1) | OPEN LINE FROM BUS 341449 [2ELLIOTTVILL69.000] TO BUS 342163 [2ROWAN CO 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.25792 | 28.2682 | 1 | 6.2363
SINGLE OPN LIN 221 341455-341458(1) | OPEN LINE FROM BUS 341455 [2ETOWN EK1 69.000] TO BUS 341458 [2ETOWN EK2 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.24122 | 3.0767
SINGLE OPN LIN 222 341455-342274(1) | OPEN LINE FROM BUS 341455 [2ETOWN EK1 69.000] TO BUS 342274 [2SMITHRVIL T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.5209
SINGLE OPN LIN 223 341455-342379(1) | OPEN LINE FROM BUS 341455 [2ETOWN EK1 69.000] TO BUS 342379 [2TUNNEL H T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.3844
SINGLE OPN LIN 224 341458-342340(1) | OPEN LINE FROM BUS 341458 [2ETOWN EK2 69.000] TO BUS 342340 [2THARP T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.35954 | 3.9743
SINGLE OPN LIN 225 341461-341797(1) | OPEN LINE FROM BUS 341461 [2FALCON EK 69.000] TO BUS 341797 [2MAGGARD 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14984 | 4.9243
SINGLE OPN LIN 226 341461-342310(1) | OPEN LINE FROM BUS 341461 [2FALCON EK 69.000] TO BUS 342310 [2SUBLETT 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 4.3621
SINGLE OPN LIN 227 341464-341569(1) | OPEN LINE FROM BUS 341464 [2FALL ROCK 69.000] TO BUS 341569 [2GREENBRIA T69.000] CKT 1 | TRUE | Met convergence tolerances | 5 | 0.3706 | 33.5612 | 1 | 7.3931
SINGLE OPN LIN 228 341464-342391(1) | OPEN LINE FROM BUS 341464 [2FALL ROCK 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.5428
SINGLE OPN LIN 229 341464-342730(1) | OPEN LINE FROM BUS 341464 [2FALL ROCK 69.000] TO BUS 342730 [5FALL ROCK 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.25182 | 7.6516
SINGLE OPN LIN 230 341467-342580(1) | OPEN LINE FROM BUS 341467 [2FAYETTE 69.000] TO BUS 342580 [4FAYETTE 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.176
SINGLE OPN LIN 231 341470-341473(1) | OPEN LINE FROM BUS 341470 [2FLOYD EK 69.000] TO BUS 341473 [2FLOYD-SFL T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.27798 | 7.0974
SINGLE OPN LIN 232 341470-342511(1) | OPEN LINE FROM BUS 341470 [2FLOYD EK 69.000] TO BUS 342511 [2WOODSTOCK 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.896
SINGLE OPN LIN 233 341473-342115(1) | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.40055 | 18.3658
SINGLE OPN LIN 234 341473-342193(1) | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342193 [2S FLOYD 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.31049 | 30.9 | 1 | 7.0517
SINGLE OPN LIN 235 341476-341899(1) | OPEN LINE FROM BUS 341476 [2FOGG PIKE 69.000] TO BUS 341899 [2MT STERLING69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.16825 | 21.0036 | 1 | 4.504
SINGLE OPN LIN 236 341476-342130(1) | OPEN LINE FROM BUS 341476 [2FOGG PIKE 69.000] TO BUS 342130 [2REID VILLAG69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.16827 | 21.0238 | 1 | 4.504
SINGLE OPN LIN 237 341485-341488(1) | OPEN LINE FROM BUS 341485 [2FOUR OAKS 69.000] TO BUS 341488 [2FOUR OAKS T69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.68459 | 46.8579 | 2 | 11.1208
SINGLE OPN LIN 238 341485-341550(1) | OPEN LINE FROM BUS 341485 [2FOUR OAKS 69.000] TO BUS 341550 [2FALMOUTH KU69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.43268 | 21.9759 | 1 | 4.56
SINGLE OPN LIN 239 341491-341548(1) | OPEN LINE FROM BUS 341491 [2FOX HOLLOW 69.000] TO BUS 341548 [2GORIN PRK J69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 3.3924
SINGLE OPN LIN 240 341491-342037(1) | OPEN LINE FROM BUS 341491 [2FOX HOLLOW 69.000] TO BUS 342037 [2PARKWAY 1 69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.74804 | 52.8306 | 2 | 12.671
SINGLE OPN LIN 241 341491-342043(1) | OPEN LINE FROM BUS 341491 [2FOX HOLLOW 69.000] TO BUS 342043 [2PARKWAY 2 T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.2012
SINGLE OPN LIN 242 341491-342049(1) | OPEN LINE FROM BUS 341491 [2FOX HOLLOW 69.000] TO BUS 342049 [2PATTON RD J69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.4421
SINGLE OPN LIN 243 341491-342732(1) | OPEN LINE FROM BUS 341491 [2FOX HOLLOW 69.000] TO BUS 342732 [5FOX HOLLOW 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.54306 | 21.9746
SINGLE OPN LIN 244 341494-341497(1) | OPEN LINE FROM BUS 341494 [2FREDRIKBG T69.000] TO BUS 341497 [2FREDRIKBRG 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.1643 | 20.0012 | 1 | 4.135
SINGLE OPN LIN 245 341494-341935(1) | OPEN LINE FROM BUS 341494 [2FREDRIKBG T69.000] TO BUS 341935 [2N SPRINGFLD69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.7086
SINGLE OPN LIN 246 341494-342508(1) | OPEN LINE FROM BUS 341494 [2FREDRIKBG T69.000] TO BUS 342508 [2WOODLAWN 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.5911
SINGLE OPN LIN 247 341500-341644(1) | OPEN LINE FROM BUS 341500 [2FRENCHBURG 69.000] TO BUS 341644 [2HOPE 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.4287 | 9.8845
SINGLE OPN LIN 248 341500-341824(1) | OPEN LINE FROM BUS 341500 [2FRENCHBURG 69.000] TO BUS 341824 [2MARIBA T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.1323
SINGLE OPN LIN 249 341503-341506(1) | OPEN LINE FROM BUS 341503 [2GAP OF RG T69.000] TO BUS 341506 [2GAP OF RIDG69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.54242 | 42.0505 | 1 | 9.8439
SINGLE OPN LIN 250 341503-341578(1) | OPEN LINE FROM BUS 341503 [2GAP OF RG T69.000] TO BUS 341578 [2GREGORY R T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6327
SINGLE OPN LIN 251 341503-341887(1) | OPEN LINE FROM BUS 341503 [2GAP OF RG T69.000] TO BUS 341887 [2MONTICELLO 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.1932
SINGLE OPN LIN 252 341509-341512(1) | OPEN LINE FROM BUS 341509 [2GARLIN 69.000] TO BUS 341512 [2GARLIN T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.24093 | 26.7474 | 1 | 5.8713
SINGLE OPN LIN 253 341515-341732(1) | OPEN LINE FROM BUS 341515 [2GARRARD CO 69.000] TO BUS 341732 [2LANCASTER T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6472
SINGLE OPN LIN 254 341515-942410(1) | OPEN LINE FROM BUS 341515 [2GARRARD CO 69.000] TO BUS 942410 [AE2-254 TAP 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.56164 | 23.1064
SINGLE OPN LIN 255 341518-341521(1) | OPEN LINE FROM BUS 341518 [2GARRARD KU 69.000] TO BUS 341521 [2GARRARDKU T69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 1.9815
SINGLE OPN LIN 256 341521-341806(1) | OPEN LINE FROM BUS 341521 [2GARRARDKU T69.000] TO BUS 341806 [2MANCHESTER 69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.14287 | 1.6753
SINGLE OPN LIN 257 341530-342043(1) | OPEN LINE FROM BUS 341530 [2GLASGO-CLEV69.000] TO BUS 342043 [2PARKWAY 2 T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.1996
SINGLE OPN LIN 258 341530-342445(1) | OPEN LINE FROM BUS 341530 [2GLASGO-CLEV69.000] TO BUS 342445 [2W GLASGOW T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.1991
SINGLE OPN LIN 259 341533-341632(1) | OPEN LINE FROM BUS 341533 [2GLENDALE 69.000] TO BUS 341632 [2HODGENVILLE69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.31724 | 4.7965
SINGLE OPN LIN 260 341533-342307(1) | OPEN LINE FROM BUS 341533 [2GLENDALE 69.000] TO BUS 342307 [2STEPHENSBRG69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.1244
SINGLE OPN LIN 261 341536-341623(1) | OPEN LINE FROM BUS 341536 [2GODDARD 69.000] TO BUS 341623 [2HILLSBORO 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.46857 | 19.774
SINGLE OPN LIN 262 341536-341989(1) | OPEN LINE FROM BUS 341536 [2GODDARD 69.000] TO BUS 341989 [2OAK RIDGE T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.54108 | 3.5565
SINGLE OPN LIN 263 341536-342088(1) | OPEN LINE FROM BUS 341536 [2GODDARD 69.000] TO BUS 342088 [2PLUMMR L T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.76204 | 11.4148
SINGLE OPN LIN 264 341536-342589(1) | OPEN LINE FROM BUS 341536 [2GODDARD 69.000] TO BUS 342589 [4GODDARD 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.47344 | 20.1065
SINGLE OPN LIN 265 341539-341686(1) | OPEN LINE FROM BUS 341539 [2GOLDBUG 69.000] TO BUS 341686 [2JELLICO C T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.3205
SINGLE OPN LIN 266 341542-341548(1) | OPEN LINE FROM BUS 341542 [2GOODNIGHT 69.000] TO BUS 341548 [2GORIN PRK J69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 3.4661
SINGLE OPN LIN 267 341551-341587(1) | OPEN LINE FROM BUS 341551 [2GRANTS LICK69.000] TO BUS 341587 [2GRIFFIN J 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.0437
SINGLE OPN LIN 268 341551-342298(1) | OPEN LINE FROM BUS 341551 [2GRANTS LICK69.000] TO BUS 342298 [2STANLY P J269.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.5142 | 4.8937
SINGLE OPN LIN 269 341554-341752(1) | OPEN LINE FROM BUS 341554 [2GRAYSON J 69.000] TO BUS 341752 [2LEON 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.39095 | 7.0433
SINGLE OPN LIN 270 341554-342034(1) | OPEN LINE FROM BUS 341554 [2GRAYSON J 69.000] TO BUS 342034 [2PACTOLUS T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.2415
SINGLE OPN LIN 271 341563-341575(1) | OPEN LINE FROM BUS 341563 [2GREEN CO 69.000] TO BUS 341575 [2GREENSBURG 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.7909
SINGLE OPN LIN 272 341563-342325(1) | OPEN LINE FROM BUS 341563 [2GREEN CO 69.000] TO BUS 342325 [2SUMMERSVIL 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.7611
SINGLE OPN LIN 273 341563-342733(1) | OPEN LINE FROM BUS 341563 [2GREEN CO 69.000] TO BUS 342733 [5GREEN CO 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.4777
SINGLE OPN LIN 274 341569-341572(1) | OPEN LINE FROM BUS 341569 [2GREENBRIA T69.000] TO BUS 341572 [2GREENBRIAR 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.35728 | 33.2294 | 1 | 7.3931
SINGLE OPN LIN 275 341569-341806(1) | OPEN LINE FROM BUS 341569 [2GREENBRIA T69.000] TO BUS 341806 [2MANCHESTER 69.000] CKT 1 | TRUE | Met convergence tolerances | 3 | 0.14287 | 1.8086
SINGLE OPN LIN 276 341575-341854(1) | OPEN LINE FROM BUS 341575 [2GREENSBURG 69.000] TO BUS 341854 [2MCKINNY T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.4036
SINGLE OPN LIN 277 341578-341581(1) | OPEN LINE FROM BUS 341578 [2GREGORY R T69.000] TO BUS 341581 [2GREGORY RD 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 15.1769 | 1 | 1.8519
SINGLE OPN LIN 278 341584-341587(1) | OPEN LINE FROM BUS 341584 [2GRIFFIN 69.000] TO BUS 341587 [2GRIFFIN J 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.38717 | 34.3711 | 1 | 7.6275
SINGLE OPN LIN 279 341590-341593(1) | OPEN LINE FROM BUS 341590 [2HARDWCRK 69.000] TO BUS 341593 [2HARDWCRK T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 15.2103 | 1 | 1.8746
SINGLE OPN LIN 280 341593-342301(1) | OPEN LINE FROM BUS 341593 [2HARDWCRK T 69.000] TO BUS 342301 [2STANTON 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6136
SINGLE OPN LIN 281 341596-341599(1) | OPEN LINE FROM BUS 341596 [2HARGETT 69.000] TO BUS 341599 [2HARGETT T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.15243 | 19.0728 | 1 | 3.9751
SINGLE OPN LIN 282 341599-342370(1) | OPEN LINE FROM BUS 341599 [2HARGETT T 69.000] TO BUS 342370 [2TRAPP 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.9455
SINGLE OPN LIN 283 341602-341872(1) | OPEN LINE FROM BUS 341602 [2HEADQTRS 69.000] TO BUS 341872 [2MILLB-CRL J69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.7851
SINGLE OPN LIN 284 341602-342280(1) | OPEN LINE FROM BUS 341602 [2HEADQTRS 69.000] TO BUS 342280 [2SNOW HILL 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.7039
SINGLE OPN LIN 285 341605-342595(1) | OPEN LINE FROM BUS 341605 [2HEBRON 69.000] TO BUS 342595 [4HEBRON 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.17922 | 5.3397
SINGLE OPN LIN 286 341608-342313(1) | OPEN LINE FROM BUS 341608 [2HELECHAW 69.000] TO BUS 342313 [2SUBLETT J 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.0992
SINGLE OPN LIN 287 341611-342103(1) | OPEN LINE FROM BUS 341611 [2HICKORY PL 69.000] TO BUS 342103 [2PPG 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.4379
SINGLE OPN LIN 288 341614-342520(1) | OPEN LINE FROM BUS 341614 [2HIGH ROCK 69.000] TO BUS 342520 [2ZACHARIAH 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 4.6449
SINGLE OPN LIN 289 341617-341896(1) | OPEN LINE FROM BUS 341617 [2HIGHLAND EK69.000] TO BUS 341896 [2MT OLIVE J 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.4687
SINGLE OPN LIN 290 341620-342163(1) | OPEN LINE FROM BUS 341620 [2HILDA 69.000] TO BUS 342163 [2ROWAN CO 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.9767
SINGLE OPN LIN 291 341623-342052(1) | OPEN LINE FROM BUS 341623 [2HILLSBORO 69.000] TO BUS 342052 [2PEASTICKS 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.42004 | 18.2711
SINGLE OPN LIN 292 341632-341800(1) | OPEN LINE FROM BUS 341632 [2HODGENVILLE69.000] TO BUS 341800 [2MAGNOLIA 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.0576
SINGLE OPN LIN 293 341632-342316(1) | OPEN LINE FROM BUS 341632 [2HODGENVILLE69.000] TO BUS 342316 [2SULPHUR CRK69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.6973
SINGLE OPN LIN 294 341638-342199(1) | OPEN LINE FROM BUS 341638 [2HOLLOWAY J 69.000] TO BUS 342199 [2S JESSAM J 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6089
SINGLE OPN LIN 295 341638-342463(1) | OPEN LINE FROM BUS 341638 [2HOLLOWAY J 69.000] TO BUS 342463 [2W NICHVIL T69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.24273 | 17.5896 | 1 | 23.1559
SINGLE OPN LIN 296 341641-341887(1) | OPEN LINE FROM BUS 341641 [2HOMESTEAD S69.000] TO BUS 341887 [2MONTICELLO 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.89709 | 59.7973 | 1 | 14.1787
SINGLE OPN LIN 297 341644-341683(1) | OPEN LINE FROM BUS 341644 [2HOPE 69.000] TO BUS 341683 [2JEFFERSNVIL69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.6757
SINGLE OPN LIN 298 341647-341650(1) | OPEN LINE FROM BUS 341647 [2HORSE CV KU69.000] TO BUS 341650 [2HORSECAVE T69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.49541 | 28.9454 | 1 | 46.06
SINGLE OPN LIN 299 341650-341651(Z1) | OPEN LINE FROM BUS 341650 [2HORSECAVE T69.000] TO BUS 341651 [2HORSECAVE J69.000] CKT Z1 | TRUE | Met convergence tolerances | 2 | 0.49521 | 28.9804 | 1 | 46.06
SINGLE OPN LIN 300 341651-341914(1) | OPEN LINE FROM BUS 341651 [2HORSECAVE J69.000] TO BUS 341914 [2MUNFVILKU T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.1462
SINGLE OPN LIN 301 341653-341656(1) | OPEN LINE FROM BUS 341653 [2HOT MIX R T69.000] TO BUS 341656 [2HOT MIX RD 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.20813 | 24.9609 | 1 | 5.3326
SINGLE OPN LIN 302 341653-341890(1) | OPEN LINE FROM BUS 341653 [2HOT MIX R T69.000] TO BUS 341890 [2MORGAN CO 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.5086
SINGLE OPN LIN 303 341659-341662(1) | OPEN LINE FROM BUS 341659 [2HT ADAMS 69.000] TO BUS 341662 [2HT ADAMS T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.26724 | 28.5606 | 1 | 6.0761
SINGLE OPN LIN 304 341662-341671(1) | OPEN LINE FROM BUS 341662 [2HT ADAMS T 69.000] TO BUS 341671 [2HUNT FARM J69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 3.3364
SINGLE OPN LIN 305 341662-341857(1) | OPEN LINE FROM BUS 341662 [2HT ADAMS T 69.000] TO BUS 341857 [2MERCR IND 69.000] CKT 1 | FALSE | Iteration limit exceeded | 0 | 1.6032 | 21.3387
SINGLE OPN LIN 306 341665-341701(1) | OPEN LINE FROM BUS 341665 [2HUNT 69.000] TO BUS 341701 [2JK SMITH 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.1366
SINGLE OPN LIN 307 341665-341869(1) | OPEN LINE FROM BUS 341665 [2HUNT 69.000] TO BUS 341869 [2MILL HUNT T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.22328 | 2.8003
SINGLE OPN LIN 308 341665-342596(1) | OPEN LINE FROM BUS 341665 [2HUNT 69.000] TO BUS 342596 [4HUNT 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.26068 | 3.0844
SINGLE OPN LIN 309 341671-342061(1) | OPEN LINE FROM BUS 341671 [2HUNT FARM J69.000] TO BUS 342061 [2PERRYVILLE 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.2922
SINGLE OPN LIN 310 341677-341890(1) | OPEN LINE FROM BUS 341677 [2INDEX 69.000] TO BUS 341890 [2MORGAN CO 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.3344 | 31.933 | 1 | 6.9677
SINGLE OPN LIN 311 341683-342100(1) | OPEN LINE FROM BUS 341683 [2JEFFERSNVIL69.000] TO BUS 342100 [2POWELL CO 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.15109 | 3.9501
SINGLE OPN LIN 312 341686-341689(1) | OPEN LINE FROM BUS 341686 [2JELLICO C T69.000] TO BUS 341689 [2JELLICO CRK69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 15.2461 | 1 | 1.9129
SINGLE OPN LIN 313 341686-342076(1) | OPEN LINE FROM BUS 341686 [2JELLICO C T69.000] TO BUS 342076 [2PINE KNOT 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.509
SINGLE OPN LIN 314 341692-341695(1) | OPEN LINE FROM BUS 341692 [2JENNY WIL T69.000] TO BUS 341695 [2JENNY WILEY69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.22689 | 25.7431 | 1 | 5.4657
SINGLE OPN LIN 315 341692-342343(1) | OPEN LINE FROM BUS 341692 [2JENNY WIL T69.000] TO BUS 342343 [2THELMA 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.41627 | 20.4178
SINGLE OPN LIN 316 341701-342370(1) | OPEN LINE FROM BUS 341701 [2JK SMITH 69.000] TO BUS 342370 [2TRAPP 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.129
SINGLE OPN LIN 317 341704-341707(1) | OPEN LINE FROM BUS 341704 [2JOE TICH 69.000] TO BUS 341707 [2JOE TICH T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.38455 | 34.3527 | 1 | 7.9884
SINGLE OPN LIN 318 341707-342427(1) | OPEN LINE FROM BUS 341707 [2JOE TICH T 69.000] TO BUS 342427 [2W BARDSTWN 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6069
SINGLE OPN LIN 319 341716-341722(1) | OPEN LINE FROM BUS 341716 [2KEAVY 69.000] TO BUS 341722 [2KEAVY 2 T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.65335 | 47.4626 | 1 | 10.7978
SINGLE OPN LIN 320 341719-341740(1) | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.0285
SINGLE OPN LIN 321 341719-342073(1) | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.0061
SINGLE OPN LIN 322 341722-341740(1) | OPEN LINE FROM BUS 341722 [2KEAVY 2 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.4012
SINGLE OPN LIN 323 341722-342187(1) | OPEN LINE FROM BUS 341722 [2KEAVY 2 T 69.000] TO BUS 342187 [2S CORBIN 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.3178
SINGLE OPN LIN 324 341725-342007(1) | OPEN LINE FROM BUS 341725 [2KEITH 69.000] TO BUS 342007 [2OWEN CO 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.5595
SINGLE OPN LIN 325 341725-342058(1) | OPEN LINE FROM BUS 341725 [2KEITH 69.000] TO BUS 342058 [2PENN 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.1524
SINGLE OPN LIN 326 341728-341854(1) | OPEN LINE FROM BUS 341728 [2KNOB LICK 69.000] TO BUS 341854 [2MCKINNY T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.28023 | 4.177
SINGLE OPN LIN 327 341731-341732(1) | OPEN LINE FROM BUS 341731 [2LANCASTER 69.000] TO BUS 341732 [2LANCASTER T69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.20176 | 24.2185 | 1 | 5.5024
SINGLE OPN LIN 328 341732-341959(1) | OPEN LINE FROM BUS 341732 [2LANCASTER T69.000] TO BUS 341959 [2NEWBY 1 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.4394
SINGLE OPN LIN 329 341734-341737(1) | OPEN LINE FROM BUS 341734 [2LAUR C IP T69.000] TO BUS 341737 [2LAUR CO IP 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.54305 | 41.8556 | 1 | 9.26
SINGLE OPN LIN 330 341734-341929(1) | OPEN LINE FROM BUS 341734 [2LAUR C IP T69.000] TO BUS 341929 [2N LONDON 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.0813
SINGLE OPN LIN 331 341740-342754(1) | OPEN LINE FROM BUS 341740 [2LAUREL CO 69.000] TO BUS 342754 [5LAUREL CO 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.7347
SINGLE OPN LIN 332 341746-342253(1) | OPEN LINE FROM BUS 341746 [2LEBANON J 69.000] TO BUS 342253 [2SHEPHEVIL J69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.1991 | 2.6327
SINGLE OPN LIN 333 341749-342058(1) | OPEN LINE FROM BUS 341749 [2LEES LICK 69.000] TO BUS 342058 [2PENN 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.8226
SINGLE OPN LIN 334 341749-342133(1) | OPEN LINE FROM BUS 341749 [2LEES LICK 69.000] TO BUS 342133 [2RENAKER 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.7025
SINGLE OPN LIN 335 341755-341758(1) | OPEN LINE FROM BUS 341755 [2LIBER CH T 69.000] TO BUS 341758 [2LIBERT CHUR69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.17395 | 22.2159 | 1 | 4.8231
SINGLE OPN LIN 336 341761-341767(1) | OPEN LINE FROM BUS 341761 [2LIBERTY J 69.000] TO BUS 341767 [2LIBERTYKU T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.5028
SINGLE OPN LIN 337 341761-341896(1) | OPEN LINE FROM BUS 341761 [2LIBERTY J 69.000] TO BUS 341896 [2MT OLIVE J 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.2103
SINGLE OPN LIN 338 341761-342760(1) | OPEN LINE FROM BUS 341761 [2LIBERTY J 69.000] TO BUS 342760 [5LIBERTY J 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.3326
SINGLE OPN LIN 339 341764-341767(1) | OPEN LINE FROM BUS 341764 [2LIBERTY KU 69.000] TO BUS 341767 [2LIBERTYKU T69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.71435 | 31.802 | 1 | 7.68
SINGLE OPN LIN 340 341767-342064(1) | OPEN LINE FROM BUS 341767 [2LIBERTYKU T69.000] TO BUS 342064 [2PEYTONS ST 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.3273
SINGLE OPN LIN 341 341772-341774(1) | OPEN LINE FROM BUS 341772 [2LOGAN 69.000] TO BUS 341774 [2LOGAN 2 T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.84929 | 57.2396 | 1 | 13.452
SINGLE OPN LIN 342 341774-341775(1) | OPEN LINE FROM BUS 341774 [2LOGAN 2 T 69.000] TO BUS 341775 [2LOGAN TAP 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.45491 | 19.8839
SINGLE OPN LIN 343 341775-342247(1) | OPEN LINE FROM BUS 341775 [2LOGAN TAP 69.000] TO BUS 342247 [2SHELBY CO 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.45462 | 20.0154
SINGLE OPN LIN 344 341776-342208(1) | OPEN LINE FROM BUS 341776 [2LORETTO 69.000] TO BUS 342208 [2S SPRINGF T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.4672
SINGLE OPN LIN 345 341776-342316(1) | OPEN LINE FROM BUS 341776 [2LORETTO 69.000] TO BUS 342316 [2SULPHUR CRK69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.0345
SINGLE OPN LIN 346 341779-341782(1) | OPEN LINE FROM BUS 341779 [2LOW GAP 69.000] TO BUS 341782 [2LOW GAP T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 19.6313 | 1 | 4.1103
SINGLE OPN LIN 347 341782-342475(1) | OPEN LINE FROM BUS 341782 [2LOW GAP T 69.000] TO BUS 342475 [2WARNOCK 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.37468 | 12.7863
SINGLE OPN LIN 348 341785-341788(1) | OPEN LINE FROM BUS 341785 [2LYMAN BW 69.000] TO BUS 341788 [2LYMAN BW T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.30389 | 30.5256 | 1 | 7.0814
SINGLE OPN LIN 349 341788-342155(1) | OPEN LINE FROM BUS 341788 [2LYMAN BW T 69.000] TO BUS 342155 [2ROANOKE T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6218
SINGLE OPN LIN 350 341788-342379(1) | OPEN LINE FROM BUS 341788 [2LYMAN BW T 69.000] TO BUS 342379 [2TUNNEL H T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.4562
SINGLE OPN LIN 351 341791-341794(1) | OPEN LINE FROM BUS 341791 [2MACKVIL KU 69.000] TO BUS 341794 [2MACKVILKU T69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 3.7993 | 1 | 0.45
SINGLE OPN LIN 352 341794-341935(1) | OPEN LINE FROM BUS 341794 [2MACKVILKU T69.000] TO BUS 341935 [2N SPRINGFLD69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.3149
SINGLE OPN LIN 353 341794-342061(1) | OPEN LINE FROM BUS 341794 [2MACKVILKU T69.000] TO BUS 342061 [2PERRYVILLE 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.3181
SINGLE OPN LIN 354 341797-342265(1) | OPEN LINE FROM BUS 341797 [2MAGGARD 69.000] TO BUS 342265 [2SKAGGS 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.17852 | 5.9456
SINGLE OPN LIN 355 341800-342325(1) | OPEN LINE FROM BUS 341800 [2MAGNOLIA 69.000] TO BUS 342325 [2SUMMERSVIL 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.9707
SINGLE OPN LIN 356 341803-342310(1) | OPEN LINE FROM BUS 341803 [2MAGOFFIN CO69.000] TO BUS 342310 [2SUBLETT 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.2307
SINGLE OPN LIN 357 341803-342313(1) | OPEN LINE FROM BUS 341803 [2MAGOFFIN CO69.000] TO BUS 342313 [2SUBLETT J 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.9546
SINGLE OPN LIN 358 341809-341812(1) | OPEN LINE FROM BUS 341809 [2MAPLESVIL T69.000] TO BUS 341812 [2MAPLESVILLE69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.22827 | 26.4262 | 1 | 5.784
SINGLE OPN LIN 359 341809-341929(1) | OPEN LINE FROM BUS 341809 [2MAPLESVIL T69.000] TO BUS 341929 [2N LONDON 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6316
SINGLE OPN LIN 360 341815-341818(1) | OPEN LINE FROM BUS 341815 [2MARETBURG 69.000] TO BUS 341818 [2MARETBURG T69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.27245 | 28.8948 | 1 | 6.4511
SINGLE OPN LIN 361 341818-342472(1) | OPEN LINE FROM BUS 341818 [2MARETBURG T69.000] TO BUS 342472 [2WALNUT GROV69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.5253
SINGLE OPN LIN 362 341821-341824(1) | OPEN LINE FROM BUS 341821 [2MARIBA 69.000] TO BUS 341824 [2MARIBA T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.175 | 22.2741 | 1 | 4.525
SINGLE OPN LIN 363 341824-341833(1) | OPEN LINE FROM BUS 341824 [2MARIBA T 69.000] TO BUS 341833 [2MAYTOWN T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6834
SINGLE OPN LIN 364 341827-342343(1) | OPEN LINE FROM BUS 341827 [2MARTIN CO 69.000] TO BUS 342343 [2THELMA 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.18001 | 22.6453 | 1 | 4.7105
SINGLE OPN LIN 365 341830-341833(1) | OPEN LINE FROM BUS 341830 [2MAYTOWN 69.000] TO BUS 341833 [2MAYTOWN T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.15821 | 19.9947 | 1 | 3.9033
SINGLE OPN LIN 366 341833-341890(1) | OPEN LINE FROM BUS 341833 [2MAYTOWN T 69.000] TO BUS 341890 [2MORGAN CO 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.5107
SINGLE OPN LIN 367 341836-341953(1) | OPEN LINE FROM BUS 341836 [2MAZIE 69.000] TO BUS 341953 [2NEW FOUNDL 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.8763
SINGLE OPN LIN 368 341836-342265(1) | OPEN LINE FROM BUS 341836 [2MAZIE 69.000] TO BUS 342265 [2SKAGGS 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.1568
SINGLE OPN LIN 369 341839-341842(1) | OPEN LINE FROM BUS 341839 [2MBUSA 69.000] TO BUS 341842 [2MBUSA T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.94146 | 62.2134 | 1 | 14.5365
SINGLE OPN LIN 370 341845-342139(1) | OPEN LINE FROM BUS 341845 [2MCCREARY CO69.000] TO BUS 342139 [2REVELO KU T69.000] CKT 1 | FALSE | Iteration limit exceeded | 0 | 0.60851 | 16.1932
SINGLE OPN LIN 371 341845-342490(1) | OPEN LINE FROM BUS 341845 [2MCCREARY CO69.000] TO BUS 342490 [2WHITLEY CTY69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.9281
SINGLE OPN LIN 372 341845-342778(1) | OPEN LINE FROM BUS 341845 [2MCCREARY CO69.000] TO BUS 342778 [5MCCREARY CO161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.50682 | 21.4644
SINGLE OPN LIN 373 341848-342223(1) | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342223 [2SAND GAP T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6106
SINGLE OPN LIN 374 341848-342391(1) | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.6444 | 10.9178
SINGLE OPN LIN 375 341851-341854(1) | OPEN LINE FROM BUS 341851 [2MCKINNEY 69.000] TO BUS 341854 [2MCKINNY T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.16913 | 20.8058 | 1 | 4.4445
SINGLE OPN LIN 376 341857-342406(1) | OPEN LINE FROM BUS 341857 [2MERCR IND 69.000] TO BUS 342406 [2VAN ARSDELL69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.79293 | 11.2876
SINGLE OPN LIN 377 341860-341863(1) | OPEN LINE FROM BUS 341860 [2MIDDL CRK T69.000] TO BUS 341863 [2MIDDLE CRK 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.24721 | 27.2778 | 1 | 5.746
SINGLE OPN LIN 378 341869-341875(1) | OPEN LINE FROM BUS 341869 [2MILL HUNT T69.000] TO BUS 341875 [2MILLER HUNT69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 15.4889 | 1 | 2.2498
SINGLE OPN LIN 379 341869-342259(1) | OPEN LINE FROM BUS 341869 [2MILL HUNT T69.000] TO BUS 342259 [2SIDEVIEW 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.23014 | 2.8305
SINGLE OPN LIN 380 341872-341878(1) | OPEN LINE FROM BUS 341872 [2MILLB-CRL J69.000] TO BUS 341878 [2MILLERSB EK69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.15041 | 18.888 | 1 | 3.855
SINGLE OPN LIN 381 341887-342268(1) | OPEN LINE FROM BUS 341887 [2MONTICELLO 69.000] TO BUS 342268 [2SLAT 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 3.2067
SINGLE OPN LIN 382 341893-341896(1) | OPEN LINE FROM BUS 341893 [2MT OLIVE 69.000] TO BUS 341896 [2MT OLIVE J 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.16944 | 21.0989 | 1 | 4.6349
SINGLE OPN LIN 383 341908-341914(1) | OPEN LINE FROM BUS 341908 [2MUNFVIL EK 69.000] TO BUS 341914 [2MUNFVILKU T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.4527
SINGLE OPN LIN 384 341911-341914(1) | OPEN LINE FROM BUS 341911 [2MUNFVIL KU 69.000] TO BUS 341914 [2MUNFVILKU T69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.63369 | 27.2393 | 1 | 6.11
SINGLE OPN LIN 385 341917-341998(1) | OPEN LINE FROM BUS 341917 [2MUNK 69.000] TO BUS 341998 [2OAKLEY NOEL69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.0152
SINGLE OPN LIN 386 341920-341998(1) | OPEN LINE FROM BUS 341920 [2MUNK J 69.000] TO BUS 341998 [2OAKLEY NOEL69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.4396
SINGLE OPN LIN 387 341920-342502(1) | OPEN LINE FROM BUS 341920 [2MUNK J 69.000] TO BUS 342502 [2WILLIAMSTWN69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.72817 | 51.4286 | 1 | 12.2435
SINGLE OPN LIN 388 341923-342091(1) | OPEN LINE FROM BUS 341923 [2MURPHYSVIL 69.000] TO BUS 342091 [2PLUMVILLE 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.8603
SINGLE OPN LIN 389 341923-342280(1) | OPEN LINE FROM BUS 341923 [2MURPHYSVIL 69.000] TO BUS 342280 [2SNOW HILL 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 3.6666
SINGLE OPN LIN 390 341935-342208(1) | OPEN LINE FROM BUS 341935 [2N SPRINGFLD69.000] TO BUS 342208 [2S SPRINGF T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.7115
SINGLE OPN LIN 391 341938-342505(1) | OPEN LINE FROM BUS 341938 [2NANCY 69.000] TO BUS 342505 [2WINDSOR 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6078
SINGLE OPN LIN 392 341938-342526(1) | OPEN LINE FROM BUS 341938 [2NANCY 69.000] TO BUS 342526 [2ZOLLICOF T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.15575 | 3.6532
SINGLE OPN LIN 393 341941-341947(1) | OPEN LINE FROM BUS 341941 [2NELSN VAL T69.000] TO BUS 341947 [2NELSON VAL 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.21147 | 24.9962 | 1 | 5.5639
SINGLE OPN LIN 394 341941-341971(1) | OPEN LINE FROM BUS 341941 [2NELSN VAL T69.000] TO BUS 341971 [2NORWOOD 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.5506
SINGLE OPN LIN 395 341944-342424(1) | OPEN LINE FROM BUS 341944 [2NELSON CO 69.000] TO BUS 342424 [2W BARDST J 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.4979
SINGLE OPN LIN 396 341944-342514(1) | OPEN LINE FROM BUS 341944 [2NELSON CO 69.000] TO BUS 342514 [2WOOSLEY 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.9211
SINGLE OPN LIN 397 341950-342007(1) | OPEN LINE FROM BUS 341950 [2NEW CASTLE 69.000] TO BUS 342007 [2OWEN CO 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.70245 | 17.7213
SINGLE OPN LIN 398 341953-342229(1) | OPEN LINE FROM BUS 341953 [2NEW FOUNDL 69.000] TO BUS 342229 [2SANDY HOOK 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 18.3886 | 1 | 3.5476
SINGLE OPN LIN 399 341962-342361(1) | OPEN LINE FROM BUS 341962 [2NEWBY 2 69.000] TO BUS 342361 [2TODDVILLE T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.8726
SINGLE OPN LIN 400 341965-342199(1) | OPEN LINE FROM BUS 341965 [2NICHOLASVIL69.000] TO BUS 342199 [2S JESSAM J 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.659
SINGLE OPN LIN 401 341971-342115(1) | OPEN LINE FROM BUS 341971 [2NORWOOD 69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.19424 | 5.7855
SINGLE OPN LIN 402 341974-342256(1) | OPEN LINE FROM BUS 341974 [2NORWOOD T 69.000] TO BUS 342256 [2SHOPVILLE 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.37786 | 18.0679
SINGLE OPN LIN 403 341977-341983(1) | OPEN LINE FROM BUS 341977 [2OAK HILL 69.000] TO BUS 341983 [2OAK HILL T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.2755 | 29.2516 | 1 | 6.5887
SINGLE OPN LIN 404 341980-341983(1) | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 341983 [2OAK HILL T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.36066 | 17.4727
SINGLE OPN LIN 405 341980-342286(1) | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.3611 | 17.4507
SINGLE OPN LIN 406 341983-342469(1) | OPEN LINE FROM BUS 341983 [2OAK HILL T 69.000] TO BUS 342469 [2W SOMERSET 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.6564
SINGLE OPN LIN 407 341986-341989(1) | OPEN LINE FROM BUS 341986 [2OAK RIDGE 69.000] TO BUS 341989 [2OAK RIDGE T69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.17046 | 21.5019 | 1 | 4.6709
SINGLE OPN LIN 408 342000-342703(1) | OPEN LINE FROM BUS 342000 [5GAS 161.00] TO BUS 342703 [5CASEY CO 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.52555 | 21.9807
SINGLE OPN LIN 409 342000-342760(1) | OPEN LINE FROM BUS 342000 [5GAS 161.00] TO BUS 342760 [5LIBERTY J 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.71086 | 27.8631
SINGLE OPN LIN 410 342007-342008(1) | OPEN LINE FROM BUS 342007 [2OWEN CO 69.000] TO BUS 342008 [4OWEN CO 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.54297 | 22.6359
SINGLE OPN LIN 411 342007-342010(1) | OPEN LINE FROM BUS 342007 [2OWEN CO 69.000] TO BUS 342010 [2OWEN CO J1 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.36581 | 18.1806
SINGLE OPN LIN 412 342007-342013(1) | OPEN LINE FROM BUS 342007 [2OWEN CO 69.000] TO BUS 342013 [2OWEN CO J2 69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.22673 | 25.7957 | 1 | 5.8918
SINGLE OPN LIN 413 342016-342019(1) | OPEN LINE FROM BUS 342016 [2OWENS IL 69.000] TO BUS 342019 [2OWENS IL J 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.35262 | 32.7872 | 1 | 7.503
SINGLE OPN LIN 414 342022-342025(1) | OPEN LINE FROM BUS 342022 [2OWINGSVIL T69.000] TO BUS 342025 [2OWINGVIL KU69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.86915 | 41.3712 | 1 | 9.53
SINGLE OPN LIN 415 342022-342052(1) | OPEN LINE FROM BUS 342022 [2OWINGSVIL T69.000] TO BUS 342052 [2PEASTICKS 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.1477 | 2.214
SINGLE OPN LIN 416 342022-342112(1) | OPEN LINE FROM BUS 342022 [2OWINGSVIL T69.000] TO BUS 342112 [2PRESTON T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.0303
SINGLE OPN LIN 417 342031-342034(1) | OPEN LINE FROM BUS 342031 [2PACTOLUS 69.000] TO BUS 342034 [2PACTOLUS T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.50251 | 39.9842 | 1 | 8.8816
SINGLE OPN LIN 418 342037-342040(1) | OPEN LINE FROM BUS 342037 [2PARKWAY 1 69.000] TO BUS 342040 [2PARKWAY 2 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14177 | 17.3774 | 1 | 3.3429
SINGLE OPN LIN 419 342049-342161(1) | OPEN LINE FROM BUS 342049 [2PATTON RD J69.000] TO BUS 342161 [2ROSEVILLE T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.4189
SINGLE OPN LIN 420 342049-342319(1) | OPEN LINE FROM BUS 342049 [2PATTON RD J69.000] TO BUS 342319 [2SUMM SHAD J69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.3893
SINGLE OPN LIN 421 342067-342505(1) | OPEN LINE FROM BUS 342067 [2PHIL 69.000] TO BUS 342505 [2WINDSOR 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.4507
SINGLE OPN LIN 422 342070-342073(1) | OPEN LINE FROM BUS 342070 [2PINE GROVE 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.58635 | 44.061 | 1 | 9.8481
SINGLE OPN LIN 423 342073-342451(1) | OPEN LINE FROM BUS 342073 [2PINE GRV T 69.000] TO BUS 342451 [2W LONDON 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.0009
SINGLE OPN LIN 424 342076-342139(1) | OPEN LINE FROM BUS 342076 [2PINE KNOT 69.000] TO BUS 342139 [2REVELO KU T69.000] CKT 1 | FALSE | Iteration limit exceeded | 0 | 0.59415 | 16.038
SINGLE OPN LIN 425 342085-342088(1) | OPEN LINE FROM BUS 342085 [2PLUMMR L 69.000] TO BUS 342088 [2PLUMMR L T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.15468 | 19.567 | 1 | 4.0531
SINGLE OPN LIN 426 342091-342124(1) | OPEN LINE FROM BUS 342091 [2PLUMVILLE 69.000] TO BUS 342124 [2RECTORVILLE69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.0958
SINGLE OPN LIN 427 342091-342634(1) | OPEN LINE FROM BUS 342091 [2PLUMVILLE 69.000] TO BUS 342634 [4PLUMVILLE 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.21657 | 2.4061
SINGLE OPN LIN 428 342097-342184(1) | OPEN LINE FROM BUS 342097 [2POWEL TAYL 69.000] TO BUS 342184 [2S ANDERSON 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.22776 | 25.7973 | 1 | 5.6222
SINGLE OPN LIN 429 342100-342301(1) | OPEN LINE FROM BUS 342100 [2POWELL CO 69.000] TO BUS 342301 [2STANTON 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.0117
SINGLE OPN LIN 430 342100-342637(1) | OPEN LINE FROM BUS 342100 [2POWELL CO 69.000] TO BUS 342637 [4POWELL CO 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.50042 | 20.7858
SINGLE OPN LIN 431 342103-342106(1) | OPEN LINE FROM BUS 342103 [2PPG 69.000] TO BUS 342106 [2PPG J 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.3491
SINGLE OPN LIN 432 342109-342112(1) | OPEN LINE FROM BUS 342109 [2PRESTON 69.000] TO BUS 342112 [2PRESTON T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.15589 | 15.1176 | 1 | 1.5083
SINGLE OPN LIN 433 342115-342787(1) | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.47759 | 19.8577
SINGLE OPN LIN 434 342118-342121(1) | OPEN LINE FROM BUS 342118 [2RADCLIFF 69.000] TO BUS 342121 [2T BROWN L T69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.34482 | 32.4745 | 1 | 7.6513
SINGLE OPN LIN 435 342121-342328(1) | OPEN LINE FROM BUS 342121 [2T BROWN L T69.000] TO BUS 342328 [2T BROWN LOG69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.33737 | 32.1506 | 1 | 7.5424
SINGLE OPN LIN 436 342121-342415(1) | OPEN LINE FROM BUS 342121 [2T BROWN L T69.000] TO BUS 342415 [2VINE GROV J69.000] CKT 1 | TRUE | Met convergence tolerances | 3 | 0.96307 | 63.1212 | 2 | 15.1937
SINGLE OPN LIN 437 342127-342265(1) | OPEN LINE FROM BUS 342127 [2REDBUSH 69.000] TO BUS 342265 [2SKAGGS 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.0603
SINGLE OPN LIN 438 342127-342421(1) | OPEN LINE FROM BUS 342127 [2REDBUSH 69.000] TO BUS 342421 [2VOLGA 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.9356
SINGLE OPN LIN 439 342130-342259(1) | OPEN LINE FROM BUS 342130 [2REID VILLAG69.000] TO BUS 342259 [2SIDEVIEW 69.000] CKT 1 | TRUE | Met convergence tolerances | 3 | 0.3507 | 33.3531 | 2 | 7.7983
SINGLE OPN LIN 440 342133-342355(1) | OPEN LINE FROM BUS 342133 [2RENAKER 69.000] TO BUS 342355 [2THREE M T 69.000] CKT 1 | FALSE | Iteration limit exceeded | 0 | 6.1032 | 52.7964
SINGLE OPN LIN 441 342133-342640(1) | OPEN LINE FROM BUS 342133 [2RENAKER 69.000] TO BUS 342640 [4RENAKER 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.4082 | 18.7475
SINGLE OPN LIN 442 342136-342139(1) | OPEN LINE FROM BUS 342136 [2REVELO KU 69.000] TO BUS 342139 [2REVELO KU T69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.17907 | 15.5196 | 1 | 1.8
SINGLE OPN LIN 443 342145-342487(1) | OPEN LINE FROM BUS 342145 [2RICHARDSON 69.000] TO BUS 342487 [2WEBSTER RD 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.84293 | 56.899 | 1 | 13.5187
SINGLE OPN LIN 444 342154-342155(1) | OPEN LINE FROM BUS 342154 [2ROANOKE 69.000] TO BUS 342155 [2ROANOKE T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 17.668 | 1 | 3.4896
SINGLE OPN LIN 445 342157-342418(1) | OPEN LINE FROM BUS 342157 [2ROGERSVIL J69.000] TO BUS 342418 [2VINE GROVE 69.000] CKT 1 | TRUE | Met convergence tolerances | 5 | 0.23646 | 17.4483 | 3 | 23.3966
SINGLE OPN LIN 446 342160-342161(1) | OPEN LINE FROM BUS 342160 [2ROSEVILLE 69.000] TO BUS 342161 [2ROSEVILLE T69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.29592 | 30.4002 | 1 | 7.0525
SINGLE OPN LIN 447 342161-342334(1) | OPEN LINE FROM BUS 342161 [2ROSEVILLE T69.000] TO BUS 342334 [2TEMPLE HILL69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.2897
SINGLE OPN LIN 448 342163-342649(1) | OPEN LINE FROM BUS 342163 [2ROWAN CO 69.000] TO BUS 342649 [4ROWAN CO 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.3571
SINGLE OPN LIN 449 342166-342169(1) | OPEN LINE FROM BUS 342166 [2RUSS SPEK T69.000] TO BUS 342169 [2RUSS SPKU T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 3.7134
SINGLE OPN LIN 450 342166-342172(1) | OPEN LINE FROM BUS 342166 [2RUSS SPEK T69.000] TO BUS 342172 [2RUSS SPR EK69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.64638 | 47.688 | 1 | 11.0494
SINGLE OPN LIN 451 342166-342235(1) | OPEN LINE FROM BUS 342166 [2RUSS SPEK T69.000] TO BUS 342235 [2SEWELTN J 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.9389
SINGLE OPN LIN 452 342169-342175(1) | OPEN LINE FROM BUS 342169 [2RUSS SPKU T69.000] TO BUS 342175 [2RUSS SPR KU69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.59834 | 28.1581 | 1 | 6.4
SINGLE OPN LIN 453 342169-342178(1) | OPEN LINE FROM BUS 342169 [2RUSS SPKU T69.000] TO BUS 342178 [2RUSSEL CO 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.46378 | 19.8117
SINGLE OPN LIN 454 342178-342232(1) | OPEN LINE FROM BUS 342178 [2RUSSEL CO 69.000] TO BUS 342232 [2SEWELLTON 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 3.4156
SINGLE OPN LIN 455 342178-342793(1) | OPEN LINE FROM BUS 342178 [2RUSSEL CO 69.000] TO BUS 342793 [5RUSSEL CO 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.58707 | 23.8037
SINGLE OPN LIN 456 342184-342262(1) | OPEN LINE FROM BUS 342184 [2S ANDERSON 69.000] TO BUS 342262 [2SINAI 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.50268 | 22.2578
SINGLE OPN LIN 457 342186-342424(1) | OPEN LINE FROM BUS 342186 [2S BARDSTWN 69.000] TO BUS 342424 [2W BARDST J 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.4694
SINGLE OPN LIN 458 342186-342427(1) | OPEN LINE FROM BUS 342186 [2S BARDSTWN 69.000] TO BUS 342427 [2W BARDSTWN 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.7157
SINGLE OPN LIN 459 342196-342391(1) | OPEN LINE FROM BUS 342196 [2WHITE OAK 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.0118
SINGLE OPN LIN 460 342199-342202(1) | OPEN LINE FROM BUS 342199 [2S JESSAM J 69.000] TO BUS 342202 [2S JESSAMINE69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.98419 | 63.9596 | 1 | 14.9115
SINGLE OPN LIN 461 342208-342211(1) | OPEN LINE FROM BUS 342208 [2S SPRINGF T69.000] TO BUS 342211 [2S SPRINGFLD69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.18088 | 22.0582 | 1 | 4.6495
SINGLE OPN LIN 462 342214-342217(1) | OPEN LINE FROM BUS 342214 [2SALEM EK 69.000] TO BUS 342217 [2SALEM EK T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.59077 | 44.4507 | 1 | 10.2212
SINGLE OPN LIN 463 342217-342481(1) | OPEN LINE FROM BUS 342217 [2SALEM EK T 69.000] TO BUS 342481 [2WEBB CR R T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6043
SINGLE OPN LIN 464 342217-342505(1) | OPEN LINE FROM BUS 342217 [2SALEM EK T 69.000] TO BUS 342505 [2WINDSOR 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.0383
SINGLE OPN LIN 465 342220-342223(1) | OPEN LINE FROM BUS 342220 [2SAND GAP 69.000] TO BUS 342223 [2SAND GAP T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 16.3699 | 1 | 2.7435
SINGLE OPN LIN 466 342235-342481(1) | OPEN LINE FROM BUS 342235 [2SEWELTN J 69.000] TO BUS 342481 [2WEBB CR R T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.7939
SINGLE OPN LIN 467 342238-342241(1) | OPEN LINE FROM BUS 342238 [2SEYMOUR 69.000] TO BUS 342241 [2SEYMOUR T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.15031 | 18.5507 | 1 | 3.7942
SINGLE OPN LIN 468 342247-342248(1) | OPEN LINE FROM BUS 342247 [2SHELBY CO 69.000] TO BUS 342248 [2SHELBY TAP 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.5024
SINGLE OPN LIN 469 342247-342410(1) | OPEN LINE FROM BUS 342247 [2SHELBY CO 69.000] TO BUS 342410 [2VEECHDALE 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.17947 | 22.6834 | 1 | 5.1171
SINGLE OPN LIN 470 342247-342808(1) | OPEN LINE FROM BUS 342247 [2SHELBY CO 69.000] TO BUS 342808 [5SHELBY CO 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.41086 | 19.2325
SINGLE OPN LIN 471 342250-342253(1) | OPEN LINE FROM BUS 342250 [2SHEPHEVIL 69.000] TO BUS 342253 [2SHEPHEVIL J69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.20766 | 15.5459 | 1 | 20.8315
SINGLE OPN LIN 472 342265-342658(1) | OPEN LINE FROM BUS 342265 [2SKAGGS 69.000] TO BUS 342658 [4SKAGGS 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.28179 | 6.827
SINGLE OPN LIN 473 342268-342478(1) | OPEN LINE FROM BUS 342268 [2SLAT 69.000] TO BUS 342478 [2WAYNE CO 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.40617 | 18.5272
SINGLE OPN LIN 474 342271-342274(1) | OPEN LINE FROM BUS 342271 [2SMITHRSVIL 69.000] TO BUS 342274 [2SMITHRVIL T69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.85982 | 58.3488 | 1 | 13.9816
SINGLE OPN LIN 475 342277-342283(1) | OPEN LINE FROM BUS 342277 [2SNOW 69.000] TO BUS 342283 [2SNOW T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.54683 | 42.7616 | 1 | 9.8435
SINGLE OPN LIN 476 342283-342322(1) | OPEN LINE FROM BUS 342283 [2SNOW T 69.000] TO BUS 342322 [2SUMM SHADE 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.1454 | 3.006
SINGLE OPN LIN 477 342286-342287(1) | OPEN LINE FROM BUS 342286 [2SOMERSET 69.000] TO BUS 342287 [2SOMERSET KU69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.5389
SINGLE OPN LIN 478 342292-342295(1) | OPEN LINE FROM BUS 342292 [2STANLEY PRK69.000] TO BUS 342295 [2STANLY P J169.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.25536 | 3.6906
SINGLE OPN LIN 479 342292-342298(1) | OPEN LINE FROM BUS 342292 [2STANLEY PRK69.000] TO BUS 342298 [2STANLY P J269.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.51379 | 4.8802
SINGLE OPN LIN 480 342292-342667(1) | OPEN LINE FROM BUS 342292 [2STANLEY PRK69.000] TO BUS 342667 [4STANLEY PRK138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.22277 | 2.954
SINGLE OPN LIN 481 342307-342403(1) | OPEN LINE FROM BUS 342307 [2STEPHENSBRG69.000] TO BUS 342403 [2UPTON T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.8165
SINGLE OPN LIN 482 342307-342412(1) | OPEN LINE FROM BUS 342307 [2STEPHENSBRG69.000] TO BUS 342412 [2VERTREES 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.22722 | 25.9884 | 1 | 5.8907
SINGLE OPN LIN 483 342319-342322(1) | OPEN LINE FROM BUS 342319 [2SUMM SHAD J69.000] TO BUS 342322 [2SUMM SHADE 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.5219
SINGLE OPN LIN 484 342319-342334(1) | OPEN LINE FROM BUS 342319 [2SUMM SHAD J69.000] TO BUS 342334 [2TEMPLE HILL69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.3455
SINGLE OPN LIN 485 342322-342436(1) | OPEN LINE FROM BUS 342322 [2SUMM SHADE 69.000] TO BUS 342436 [2W COLUMBI T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.4027
SINGLE OPN LIN 486 342322-342814(1) | OPEN LINE FROM BUS 342322 [2SUMM SHADE 69.000] TO BUS 342814 [5SUMM SHADE 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.41196 | 18.5764
SINGLE OPN LIN 487 342337-342340(1) | OPEN LINE FROM BUS 342337 [2THARP 69.000] TO BUS 342340 [2THARP T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.52619 | 41.6403 | 1 | 10.0175
SINGLE OPN LIN 488 342343-342421(1) | OPEN LINE FROM BUS 342343 [2THELMA 69.000] TO BUS 342421 [2VOLGA 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.715
SINGLE OPN LIN 489 342349-342433(1) | OPEN LINE FROM BUS 342349 [2THREE LNK J69.000] TO BUS 342433 [2W BEREA J 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.37969 | 10.8391
SINGLE OPN LIN 490 342352-342355(1) | OPEN LINE FROM BUS 342352 [2THREE M 69.000] TO BUS 342355 [2THREE M T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.19851 | 15.238 | 1 | 19.4904
SINGLE OPN LIN 491 342358-342361(1) | OPEN LINE FROM BUS 342358 [2TODDVILLE 69.000] TO BUS 342361 [2TODDVILLE T69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.1667 | 20.4333 | 1 | 4.2681
SINGLE OPN LIN 492 342364-342367(1) | OPEN LINE FROM BUS 342364 [2TOMM GOOC 69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.93027 | 61.661 | 1 | 14.7257
SINGLE OPN LIN 493 342367-942410(1) | OPEN LINE FROM BUS 342367 [2TOMM GOOC T69.000] TO BUS 942410 [AE2-254 TAP 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.8623
SINGLE OPN LIN 494 342379-342382(1) | OPEN LINE FROM BUS 342379 [2TUNNEL H T 69.000] TO BUS 342382 [2TUNNEL HILL69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.1563 | 12.6037 | 1 | 16.3905
SINGLE OPN LIN 495 342385-342487(1) | OPEN LINE FROM BUS 342385 [2TURKEY FT 69.000] TO BUS 342487 [2WEBSTER RD 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.15915 | 2.5064
SINGLE OPN LIN 496 342391-342820(1) | OPEN LINE FROM BUS 342391 [2TYNER 69.000] TO BUS 342820 [5TYNER 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.16358 | 5.5223
SINGLE OPN LIN 497 342394-342397(1) | OPEN LINE FROM BUS 342394 [2UPCHURCH 69.000] TO BUS 342397 [2UPCHURCH T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.39999 | 35.259 | 1 | 8.1682
SINGLE OPN LIN 498 342397-342532(1) | OPEN LINE FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.37815 | 18.0624
SINGLE OPN LIN 499 342400-342403(1) | OPEN LINE FROM BUS 342400 [2UPTON 69.000] TO BUS 342403 [2UPTON T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 17.5013 | 1 | 3.4103
SINGLE OPN LIN 500 342415-342418(1) | OPEN LINE FROM BUS 342415 [2VINE GROV J69.000] TO BUS 342418 [2VINE GROVE 69.000] CKT 1 | TRUE | Met convergence tolerances | 4 | 0.96294 | 63.1981 | 2 | 15.1937
SINGLE OPN LIN 501 342430-342433(1) | OPEN LINE FROM BUS 342430 [2W BEREA 69.000] TO BUS 342433 [2W BEREA J 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.37981 | 10.8574
SINGLE OPN LIN 502 342430-342691(1) | OPEN LINE FROM BUS 342430 [2W BEREA 69.000] TO BUS 342691 [4W BEREA 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.4858 | 20.4875
SINGLE OPN LIN 503 342436-342439(1) | OPEN LINE FROM BUS 342436 [2W COLUMBI T69.000] TO BUS 342439 [2W COLUMBIA 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.23588 | 26.5822 | 1 | 5.8725
SINGLE OPN LIN 504 342442-342445(1) | OPEN LINE FROM BUS 342442 [2W GLASGOW 69.000] TO BUS 342445 [2W GLASGOW T69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.76299 | 53.5914 | 1 | 12.7509
SINGLE OPN LIN 505 342460-342463(1) | OPEN LINE FROM BUS 342460 [2W NICHVIL 69.000] TO BUS 342463 [2W NICHVIL T69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.24274 | 17.7081 | 1 | 23.1559
SINGLE OPN LIN 506 342469-342526(1) | OPEN LINE FROM BUS 342469 [2W SOMERSET 69.000] TO BUS 342526 [2ZOLLICOF T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.5411
SINGLE OPN LIN 507 342472-342511(1) | OPEN LINE FROM BUS 342472 [2WALNUT GROV69.000] TO BUS 342511 [2WOODSTOCK 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.5923
SINGLE OPN LIN 508 342478-342532(1) | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.37889 | 18.0668
SINGLE OPN LIN 509 342478-342535(1) | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342535 [2ZULA T 69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.40375 | 35.448 | 1 | 8.451
SINGLE OPN LIN 510 342478-342823(1) | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.57284 | 23.1516
SINGLE OPN LIN 511 342481-342484(1) | OPEN LINE FROM BUS 342481 [2WEBB CR R T69.000] TO BUS 342484 [2WEBB CR RDS69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.21529 | 25.1705 | 1 | 5.4721
SINGLE OPN LIN 512 342490-342493(1) | OPEN LINE FROM BUS 342490 [2WHITLEY CTY69.000] TO BUS 342493 [2WHITLY C KU69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.35965 | 19.1939 | 1 | 3.81
SINGLE OPN LIN 513 342490-342499(1) | OPEN LINE FROM BUS 342490 [2WHITLEY CTY69.000] TO BUS 342499 [2WIBORG T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 3.091
SINGLE OPN LIN 514 342496-342499(1) | OPEN LINE FROM BUS 342496 [2WIBORG 69.000] TO BUS 342499 [2WIBORG T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.38586 | 34.5469 | 1 | 8.0737
SINGLE OPN LIN 515 342523-342526(1) | OPEN LINE FROM BUS 342523 [2ZOLLICOF 69.000] TO BUS 342526 [2ZOLLICOF T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.15274 | 19.1224 | 1 | 3.8925
SINGLE OPN LIN 516 342529-342535(1) | OPEN LINE FROM BUS 342529 [2ZULA 69.000] TO BUS 342535 [2ZULA T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.4037 | 35.4803 | 1 | 8.451
SINGLE OPN LIN 517 342538-342616(1) | OPEN LINE FROM BUS 342538 [4ARGENTUM 138.00] TO BUS 342616 [4LOVE HYDRO 138.00] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.52079 | 30.588
SINGLE OPN LIN 518 342541-342544(1) | OPEN LINE FROM BUS 342541 [4AVON 138.00] TO BUS 342544 [4AVON-R 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.62199 | 25.0289
SINGLE OPN LIN 519 342541-342556(1) | OPEN LINE FROM BUS 342541 [4AVON 138.00] TO BUS 342556 [4BECKNERV T 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 4.4326
SINGLE OPN LIN 520 342541-342580(1) | OPEN LINE FROM BUS 342541 [4AVON 138.00] TO BUS 342580 [4FAYETTE 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.0732
SINGLE OPN LIN 521 342541-342631(1) | OPEN LINE FROM BUS 342541 [4AVON 138.00] TO BUS 342631 [4PARIS T 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.5175
SINGLE OPN LIN 522 342541-342829(1) | OPEN LINE FROM BUS 342541 [4AVON 138.00] TO BUS 342829 [7AVON 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.84061 | 33.7103
SINGLE OPN LIN 523 342550-342559(1) | OPEN LINE FROM BUS 342550 [4BAVARIAN LF138.00] TO BUS 342559 [4BOONE CO 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.20293 | 2.6442
SINGLE OPN LIN 524 342550-342640(1) | OPEN LINE FROM BUS 342550 [4BAVARIAN LF138.00] TO BUS 342640 [4RENAKER 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.17522 | 2.6705
SINGLE OPN LIN 525 342553-342556(1) | OPEN LINE FROM BUS 342553 [4BECKNERV 138.00] TO BUS 342556 [4BECKNERV T 138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.15454 | 14.9775 | 1 | 1.593
SINGLE OPN LIN 526 342556-342565(1) | OPEN LINE FROM BUS 342556 [4BECKNERV T 138.00] TO BUS 342565 [4BOONESBOR T138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 4.1093
SINGLE OPN LIN 527 342559-342646(1) | OPEN LINE FROM BUS 342559 [4BOONE CO 138.00] TO BUS 342646 [4RICHWOOD T 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.5123 | 8.6315
SINGLE OPN LIN 528 342559-342673(1) | OPEN LINE FROM BUS 342559 [4BOONE CO 138.00] TO BUS 342673 [4STERLNG T 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.40317 | 21.0468
SINGLE OPN LIN 529 342565-342574(1) | OPEN LINE FROM BUS 342565 [4BOONESBOR T138.00] TO BUS 342574 [4DALE 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.24458 | 2.7066
SINGLE OPN LIN 530 342571-342589(1) | OPEN LINE FROM BUS 342571 [4CRANSTON 138.00] TO BUS 342589 [4GODDARD 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.70192 | 26.9498
SINGLE OPN LIN 531 342571-342649(1) | OPEN LINE FROM BUS 342571 [4CRANSTON 138.00] TO BUS 342649 [4ROWAN CO 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.50262 | 21.9064
SINGLE OPN LIN 532 342574-342596(1) | OPEN LINE FROM BUS 342574 [4DALE 138.00] TO BUS 342596 [4HUNT 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.0532
SINGLE OPN LIN 533 342574-342676(1) | OPEN LINE FROM BUS 342574 [4DALE 138.00] TO BUS 342676 [4THREE FK T 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.0445
SINGLE OPN LIN 534 342577-342607(1) | OPEN LINE FROM BUS 342577 [4FAWKES EK 138.00] TO BUS 342607 [4JK SMITH 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.53197 | 21.3506
SINGLE OPN LIN 535 342577-342676(1) | OPEN LINE FROM BUS 342577 [4FAWKES EK 138.00] TO BUS 342676 [4THREE FK T 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.9814
SINGLE OPN LIN 536 342577-342691(1) | OPEN LINE FROM BUS 342577 [4FAWKES EK 138.00] TO BUS 342691 [4W BEREA 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.48934 | 20.4448
SINGLE OPN LIN 537 342583-342589(1) | OPEN LINE FROM BUS 342583 [4FLEMINGSBRG138.00] TO BUS 342589 [4GODDARD 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.45643 | 19.4467
SINGLE OPN LIN 538 342583-342664(1) | OPEN LINE FROM BUS 342583 [4FLEMINGSBRG138.00] TO BUS 342664 [4SPURLOCK 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.50572 | 20.8842
SINGLE OPN LIN 539 342586-342587(1) | OPEN LINE FROM BUS 342586 [4GALLATIN CO138.00] TO BUS 342587 [1GALLATIN CO34.500] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.23419 | 17.3133 | 1 | 23.73
SINGLE OPN LIN 540 342586-342673(1) | OPEN LINE FROM BUS 342586 [4GALLATIN CO138.00] TO BUS 342673 [4STERLNG T 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.43219 | 21.7299
SINGLE OPN LIN 541 342589-342634(1) | OPEN LINE FROM BUS 342589 [4GODDARD 138.00] TO BUS 342634 [4PLUMVILLE 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 4.6343
SINGLE OPN LIN 542 342596-342607(1) | OPEN LINE FROM BUS 342596 [4HUNT 138.00] TO BUS 342607 [4JK SMITH 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.46716 | 20.2841
SINGLE OPN LIN 543 342598-342664(1) | OPEN LINE FROM BUS 342598 [4INLAND C T 138.00] TO BUS 342664 [4SPURLOCK 138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.31816 | 22.2978 | 1 | 31.2332
SINGLE OPN LIN 544 342601-342604(1) | OPEN LINE FROM BUS 342601 [4JACKSNVIL 138.00] TO BUS 342604 [4JACKSNVIL T138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 17.3072 | 1 | 3.3691
SINGLE OPN LIN 545 342604-342631(1) | OPEN LINE FROM BUS 342604 [4JACKSNVIL T138.00] TO BUS 342631 [4PARIS T 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.9497
SINGLE OPN LIN 546 342604-342640(1) | OPEN LINE FROM BUS 342604 [4JACKSNVIL T138.00] TO BUS 342640 [4RENAKER 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.0232
SINGLE OPN LIN 547 342607-342610(1) | OPEN LINE FROM BUS 342607 [4JK SMITH 138.00] TO BUS 342610 [4JK SMITH 21138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.16332 | 2.2118
SINGLE OPN LIN 548 342607-342613(1) | OPEN LINE FROM BUS 342607 [4JK SMITH 138.00] TO BUS 342613 [4JK SMITH 22138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.15998 | 2.1921
SINGLE OPN LIN 549 342607-342637(1) | OPEN LINE FROM BUS 342607 [4JK SMITH 138.00] TO BUS 342637 [4POWELL CO 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.8057 | 30.221
SINGLE OPN LIN 550 342607-342688(1) | OPEN LINE FROM BUS 342607 [4JK SMITH 138.00] TO BUS 342688 [4UNION CTY T138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.62502 | 24.2591
SINGLE OPN LIN 551 342610-342832(1) | OPEN LINE FROM BUS 342610 [4JK SMITH 21138.00] TO BUS 342832 [7JK SMITH 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.16591 | 2.2428
SINGLE OPN LIN 552 342613-342832(1) | OPEN LINE FROM BUS 342613 [4JK SMITH 22138.00] TO BUS 342832 [7JK SMITH 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.16084 | 2.2099
SINGLE OPN LIN 553 342622-342625(1) | OPEN LINE FROM BUS 342622 [4MAYSVIL I T138.00] TO BUS 342625 [4MAYSVIL IND138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.37049 | 33.6735 | 1 | 8.0269
SINGLE OPN LIN 554 342622-342634(1) | OPEN LINE FROM BUS 342622 [4MAYSVIL I T138.00] TO BUS 342634 [4PLUMVILLE 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.46467 | 19.9499
SINGLE OPN LIN 555 342622-342664(1) | OPEN LINE FROM BUS 342622 [4MAYSVIL I T138.00] TO BUS 342664 [4SPURLOCK 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.50651 | 20.7751
SINGLE OPN LIN 556 342637-342784(1) | OPEN LINE FROM BUS 342637 [4POWELL CO 138.00] TO BUS 342784 [5POWELL CO 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.43242 | 18.6436
SINGLE OPN LIN 557 342640-342664(1) | OPEN LINE FROM BUS 342640 [4RENAKER 138.00] TO BUS 342664 [4SPURLOCK 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.1644
SINGLE OPN LIN 558 342643-342646(1) | OPEN LINE FROM BUS 342643 [4RICHWOOD 138.00] TO BUS 342646 [4RICHWOOD T 138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.6573 | 47.7837 | 1 | 11.3427
SINGLE OPN LIN 559 342646-342667(1) | OPEN LINE FROM BUS 342646 [4RICHWOOD T 138.00] TO BUS 342667 [4STANLEY PRK138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.7004
SINGLE OPN LIN 560 342649-342658(1) | OPEN LINE FROM BUS 342649 [4ROWAN CO 138.00] TO BUS 342658 [4SKAGGS 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.18894 | 5.7889
SINGLE OPN LIN 561 342661-342664(1) | OPEN LINE FROM BUS 342661 [4SPUR-KENT-R138.00] TO BUS 342664 [4SPURLOCK 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.55552 | 23.3424
SINGLE OPN LIN 562 342664-342667(1) | OPEN LINE FROM BUS 342664 [4SPURLOCK 138.00] TO BUS 342667 [4STANLEY PRK138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14574 | 2.4058
SINGLE OPN LIN 563 342664-342838(1) | OPEN LINE FROM BUS 342664 [4SPURLOCK 138.00] TO BUS 342838 [7SPURLOCK 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.29875 | 2.3993
SINGLE OPN LIN 564 342664-342838(2) | OPEN LINE FROM BUS 342664 [4SPURLOCK 138.00] TO BUS 342838 [7SPURLOCK 345.00] CKT 2 | TRUE | Met convergence tolerances | 0 | 0.18362 | 1.9424
SINGLE OPN LIN 565 342664-342838(3) | OPEN LINE FROM BUS 342664 [4SPURLOCK 138.00] TO BUS 342838 [7SPURLOCK 345.00] CKT 3 | TRUE | Met convergence tolerances | 0 | 0.26817 | 2.2898
SINGLE OPN LIN 566 342670-342673(1) | OPEN LINE FROM BUS 342670 [4STERLING 138.00] TO BUS 342673 [4STERLNG T 138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.29133 | 29.8245 | 1 | 6.9793
SINGLE OPN LIN 567 342676-342679(1) | OPEN LINE FROM BUS 342676 [4THREE FK T 138.00] TO BUS 342679 [4THREE FORKS138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 16.7216 | 1 | 3.0944
SINGLE OPN LIN 568 342685-342688(1) | OPEN LINE FROM BUS 342685 [4UNION CITY 138.00] TO BUS 342688 [4UNION CTY T138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.25167 | 27.7769 | 1 | 6.4748
SINGLE OPN LIN 569 342694-342814(1) | OPEN LINE FROM BUS 342694 [5BARREN CO 161.00] TO BUS 342814 [5SUMM SHADE 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.9005
SINGLE OPN LIN 570 342697-342780(1) | OPEN LINE FROM BUS 342697 [5BEATTYV J 161.00] TO BUS 342780 [5MILL CRK T 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.42079 | 18.4462
SINGLE OPN LIN 571 342700-342819(1) | OPEN LINE FROM BUS 342700 [5BULLITT CO 161.00] TO BUS 342819 [5TAYLORSV T 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.57506 | 23.962
SINGLE OPN LIN 572 342703-342769(1) | OPEN LINE FROM BUS 342703 [5CASEY CO 161.00] TO BUS 342769 [5MARION CO 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.4818 | 20.2363
SINGLE OPN LIN 573 342715-342718(1) | OPEN LINE FROM BUS 342715 [5COOPER1 161.00] TO BUS 342718 [5COOPER2 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.3221
SINGLE OPN LIN 574 342715-342790(1) | OPEN LINE FROM BUS 342715 [5COOPER1 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.7551
SINGLE OPN LIN 575 342715-342799(1) | OPEN LINE FROM BUS 342715 [5COOPER1 161.00] TO BUS 342799 [5S OAKHILL 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.8229
SINGLE OPN LIN 576 342718-342727(1) | OPEN LINE FROM BUS 342718 [5COOPER2 161.00] TO BUS 342727 [5DENNY 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6048
SINGLE OPN LIN 577 342718-342757(1) | OPEN LINE FROM BUS 342718 [5COOPER2 161.00] TO BUS 342757 [5LAUREL DAM 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.55388 | 22.2525
SINGLE OPN LIN 578 342721-342724(1) | OPEN LINE FROM BUS 342721 [5DARWIN TH 161.00] TO BUS 342724 [5DARWIN TH T161.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.99432 | 64.5618 | 1 | 15.3905
SINGLE OPN LIN 579 342724-342766(1) | OPEN LINE FROM BUS 342724 [5DARWIN TH T161.00] TO BUS 342766 [5LITTLE MT T161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.46562 | 20.6957
SINGLE OPN LIN 580 342724-342808(1) | OPEN LINE FROM BUS 342724 [5DARWIN TH T161.00] TO BUS 342808 [5SHELBY CO 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.41417 | 19.3028
SINGLE OPN LIN 581 342730-342820(1) | OPEN LINE FROM BUS 342730 [5FALL ROCK 161.00] TO BUS 342820 [5TYNER 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.23435 | 6.1834
SINGLE OPN LIN 582 342733-342814(1) | OPEN LINE FROM BUS 342733 [5GREEN CO 161.00] TO BUS 342814 [5SUMM SHADE 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.8332
SINGLE OPN LIN 583 342733-342817(1) | OPEN LINE FROM BUS 342733 [5GREEN CO 161.00] TO BUS 342817 [5TAYLOR CO J161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.778
SINGLE OPN LIN 584 342736-342739(1) | OPEN LINE FROM BUS 342736 [5GREEN HAL T161.00] TO BUS 342739 [5GREEN HALL 161.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 16.1136 | 1 | 2.6482
SINGLE OPN LIN 585 342736-342820(1) | OPEN LINE FROM BUS 342736 [5GREEN HAL T161.00] TO BUS 342820 [5TYNER 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.44269 | 19.4872
SINGLE OPN LIN 586 342742-342745(1) | OPEN LINE FROM BUS 342742 [5JABEZ 161.00] TO BUS 342745 [5JABEZ T 161.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.15817 | 19.8916 | 1 | 4.1686
SINGLE OPN LIN 587 342745-342751(1) | OPEN LINE FROM BUS 342745 [5JABEZ T 161.00] TO BUS 342751 [5JAMESTOWN T161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.0249
SINGLE OPN LIN 588 342745-342799(1) | OPEN LINE FROM BUS 342745 [5JABEZ T 161.00] TO BUS 342799 [5S OAKHILL 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.0002
SINGLE OPN LIN 589 342748-342751(1) | OPEN LINE FROM BUS 342748 [5JAMESTOWN 161.00] TO BUS 342751 [5JAMESTOWN T161.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.27736 | 29.4408 | 1 | 6.8602
SINGLE OPN LIN 590 342751-342796(1) | OPEN LINE FROM BUS 342751 [5JAMESTOWN T161.00] TO BUS 342796 [5RUSSEL CO J161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.1588
SINGLE OPN LIN 591 342754-342757(1) | OPEN LINE FROM BUS 342754 [5LAUREL CO 161.00] TO BUS 342757 [5LAUREL DAM 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.55204 | 22.1589
SINGLE OPN LIN 592 342754-342781(1) | OPEN LINE FROM BUS 342754 [5LAUREL CO 161.00] TO BUS 342781 [5PITTSBURG 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.3696
SINGLE OPN LIN 593 342760-342790(1) | OPEN LINE FROM BUS 342760 [5LIBERTY J 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.58942 | 23.1552
SINGLE OPN LIN 594 342763-342766(1) | OPEN LINE FROM BUS 342763 [5LITTLE MT 161.00] TO BUS 342766 [5LITTLE MT T161.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.18996 | 22.8686 | 1 | 5.1178
SINGLE OPN LIN 595 342766-342819(1) | OPEN LINE FROM BUS 342766 [5LITTLE MT T161.00] TO BUS 342819 [5TAYLORSV T 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.49802 | 21.6709
SINGLE OPN LIN 596 342769-342770(1) | OPEN LINE FROM BUS 342769 [5MARION CO 161.00] TO BUS 342770 [4MARION CO 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.46677 | 19.9198
SINGLE OPN LIN 597 342769-342775(1) | OPEN LINE FROM BUS 342769 [5MARION CO 161.00] TO BUS 342775 [5MARION IP T161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.4945 | 20.2415
SINGLE OPN LIN 598 342772-342797(1) | OPEN LINE FROM BUS 342772 [5MARION IP 161.00] TO BUS 342797 [5S MARION IT161.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.30537 | 31.0428 | 1 | 7.3059
SINGLE OPN LIN 599 342775-342797(1) | OPEN LINE FROM BUS 342775 [5MARION IP T161.00] TO BUS 342797 [5S MARION IT161.00] CKT 1 | TRUE | Met convergence tolerances | 3 | 0.40344 | 27.5674 | 2 | 37.708
SINGLE OPN LIN 600 342775-342805(1) | OPEN LINE FROM BUS 342775 [5MARION IP T161.00] TO BUS 342805 [5SALOMA T 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.8401
SINGLE OPN LIN 601 342779-342780(1) | OPEN LINE FROM BUS 342779 [5MILLER CRK 161.00] TO BUS 342780 [5MILL CRK T 161.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 16.9062 | 1 | 3.1325
SINGLE OPN LIN 602 342780-342784(1) | OPEN LINE FROM BUS 342780 [5MILL CRK T 161.00] TO BUS 342784 [5POWELL CO 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.43547 | 18.6953
SINGLE OPN LIN 603 342781-342820(1) | OPEN LINE FROM BUS 342781 [5PITTSBURG 161.00] TO BUS 342820 [5TYNER 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.997
SINGLE OPN LIN 604 342787-342790(1) | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.47978 | 19.9398
SINGLE OPN LIN 605 342793-342796(1) | OPEN LINE FROM BUS 342793 [5RUSSEL CO 161.00] TO BUS 342796 [5RUSSEL CO J161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.58965 | 23.8057
SINGLE OPN LIN 606 342797-342798(1) | OPEN LINE FROM BUS 342797 [5S MARION IT161.00] TO BUS 342798 [5S MARION IP161.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.31916 | 22.4854 | 1 | 30.4021
SINGLE OPN LIN 607 342802-342805(1) | OPEN LINE FROM BUS 342802 [5SALOMA 161.00] TO BUS 342805 [5SALOMA T 161.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.68573 | 50.1293 | 1 | 12.0099
SINGLE OPN LIN 608 342805-342817(1) | OPEN LINE FROM BUS 342805 [5SALOMA T 161.00] TO BUS 342817 [5TAYLOR CO J161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.0297
SINGLE OPN LIN 609 342818-342819(1) | OPEN LINE FROM BUS 342818 [5TAYLORSVILL161.00] TO BUS 342819 [5TAYLORSV T 161.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.55082 | 42.3517 | 1 | 10.0637
SINGLE OPN LIN 610 342829-342835(1) | OPEN LINE FROM BUS 342829 [7AVON 345.00] TO BUS 342835 [7N CLARK 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.85288 | 34.3472
SINGLE OPN LIN 611 342832-342835(1) | OPEN LINE FROM BUS 342832 [7JK SMITH 345.00] TO BUS 342835 [7N CLARK 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.25564 | 3.0323
SINGLE OPN LIN 612 342832-342841(1) | OPEN LINE FROM BUS 342832 [7JK SMITH 345.00] TO BUS 342841 [7W GARRARDEK345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.34651 | 16.6474
SINGLE OPN LIN 613 342835-342838(1) | OPEN LINE FROM BUS 342835 [7N CLARK 345.00] TO BUS 342838 [7SPURLOCK 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.58988 | 28.7382
SINGLE OPN LIN 614 942410-942411(1) | OPEN LINE FROM BUS 942410 [AE2-254 TAP 69.000] TO BUS 942411 [AE2-254 C O169.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.63862 | 37.7737
SINGLE OPN LIN 615 942411-942412(1) | OPEN LINE FROM BUS 942411 [AE2-254 C O169.000] TO BUS 942412 [AE2-254 E O169.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.27238 | 15.58
SINGLE OPN TIE 616 341020-243725(1) | OPEN LINE FROM BUS 341020 [2ARGENTUM 69.000] TO BUS 243725 [05GRAYSB 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.471
SINGLE OPN TIE 617 341071-324430(1) | OPEN LINE FROM BUS 341071 [2BEATTYV 69.000] TO BUS 324430 [2BEATTYVI KU69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.52
SINGLE OPN TIE 618 341089-325102(1) | OPEN LINE FROM BUS 341089 [2BEKAERT 69.000] TO BUS 325102 [2W SHELBY 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.0571
SINGLE OPN TIE 619 341161-324213(1) | OPEN LINE FROM BUS 341161 [2BONNIV EK 69.000] TO BUS 324213 [4BONNIEVILLE138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6562
SINGLE OPN TIE 620 341188-324463(1) | OPEN LINE FROM BUS 341188 [2BRACKEN CO 69.000] TO BUS 324463 [2CARNTOWN 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.15083 | 2.2314
SINGLE OPN TIE 621 341188-324722(1) | OPEN LINE FROM BUS 341188 [2BRACKEN CO 69.000] TO BUS 324722 [2SHARON KU 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.16303 | 2.4583
SINGLE OPN TIE 622 341317-324474(1) | OPEN LINE FROM BUS 341317 [2CLAY VILLAG69.000] TO BUS 324474 [2CLAY VILG T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.56716 | 8.0184
SINGLE OPN TIE 623 341320-324830(1) | OPEN LINE FROM BUS 341320 [2COBURG 69.000] TO BUS 324830 [2CAMPBELV EK69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.7296
SINGLE OPN TIE 624 341406-324530(1) | OPEN LINE FROM BUS 341406 [2DUNCAN LN T69.000] TO BUS 324530 [2FAWKES 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.143
SINGLE OPN TIE 625 341407-324425(1) | OPEN LINE FROM BUS 341407 [2E BARDSTOWN69.000] TO BUS 324425 [2BARDT IND T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.37717 | 17.8976
SINGLE OPN TIE 626 341461-243721(Z1) | OPEN LINE FROM BUS 341461 [2FALCON EK 69.000] TO BUS 243721 [05FALCON 69.000] CKT Z1 | TRUE | Met convergence tolerances | 1 | 0.7143 | 50.4246 | 1 | 10.79
SINGLE OPN TIE 627 341515-324600(1) | OPEN LINE FROM BUS 341515 [2GARRARD CO 69.000] TO BUS 324600 [2LANCASTR KU69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.1604
SINGLE OPN TIE 628 341539-324784(1) | OPEN LINE FROM BUS 341539 [2GOLDBUG 69.000] TO BUS 324784 [2WOFFORD 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6041
SINGLE OPN TIE 629 341554-243726(1) | OPEN LINE FROM BUS 341554 [2GRAYSON J 69.000] TO BUS 243726 [05GRAYSO 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.63476 | 45.8404 | 1 | 9.905
SINGLE OPN TIE 630 341563-324554(1) | OPEN LINE FROM BUS 341563 [2GREEN CO 69.000] TO BUS 324554 [2GRENSBRG KU69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6992
SINGLE OPN TIE 631 341605-251579(1) | OPEN LINE FROM BUS 341605 [2HEBRON 69.000] TO BUS 251579 [08HEBRON 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.5713
SINGLE OPN TIE 632 341608-243812(Z1) | OPEN LINE FROM BUS 341608 [2HELECHAW 69.000] TO BUS 243812 [05LEE C 69.000] CKT Z1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6032
SINGLE OPN TIE 633 341632-324575(1) | OPEN LINE FROM BUS 341632 [2HODGENVILLE69.000] TO BUS 324575 [2HODGENV KU 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.003
SINGLE OPN TIE 634 341632-324660(1) | OPEN LINE FROM BUS 341632 [2HODGENVILLE69.000] TO BUS 324660 [2NEW HAVEN 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.56
SINGLE OPN TIE 635 341713-324519(1) | OPEN LINE FROM BUS 341713 [2KARGLE 69.000] TO BUS 324519 [2ETOWN KU 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.7664
SINGLE OPN TIE 636 341740-324576(1) | OPEN LINE FROM BUS 341740 [2LAUREL CO 69.000] TO BUS 324576 [2HOPEWELL 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 3.6603
SINGLE OPN TIE 637 341752-243737(Z1) | OPEN LINE FROM BUS 341752 [2LEON 69.000] TO BUS 243737 [05LEONKY 69.000] CKT Z1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.7876
SINGLE OPN TIE 638 341755-324527(1) | OPEN LINE FROM BUS 341755 [2LIBER CH T 69.000] TO BUS 324527 [2FARLEY KU 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 3.5134
SINGLE OPN TIE 639 341890-246973(Z1) | OPEN LINE FROM BUS 341890 [2MORGAN CO 69.000] TO BUS 246973 [05MORGCO 69.000] CKT Z1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.4494
SINGLE OPN TIE 640 341923-324717(1) | OPEN LINE FROM BUS 341923 [2MURPHYSVIL 69.000] TO BUS 324717 [2SARDIS TAP 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.9246
SINGLE OPN TIE 641 341923-325019(1) | OPEN LINE FROM BUS 341923 [2MURPHYSVIL 69.000] TO BUS 325019 [2KENTON-6 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.8209
SINGLE OPN TIE 642 341929-324662(1) | OPEN LINE FROM BUS 341929 [2N LONDON 69.000] TO BUS 324662 [2N LONDON KU69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.8737
SINGLE OPN TIE 643 341935-324736(1) | OPEN LINE FROM BUS 341935 [2N SPRINGFLD69.000] TO BUS 324736 [2SPRINGFL KU69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.9416
SINGLE OPN TIE 644 341944-324288(1) | OPEN LINE FROM BUS 341944 [2NELSON CO 69.000] TO BUS 324288 [4NELSON CO 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.28526 | 3.8759
SINGLE OPN TIE 645 342007-324455(1) | OPEN LINE FROM BUS 342007 [2OWEN CO 69.000] TO BUS 324455 [2BROMLEY 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.0671
SINGLE OPN TIE 646 342008-324290(1) | OPEN LINE FROM BUS 342008 [4OWEN CO 138.00] TO BUS 324290 [4OWEN CO TAP138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.54651 | 22.5728
SINGLE OPN TIE 647 342055-243742(1) | OPEN LINE FROM BUS 342055 [2PELFREY 69.000] TO BUS 243742 [05CORYSS 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14648 | 18.2576 | 1 | 3.5497
SINGLE OPN TIE 648 342058-324951(1) | OPEN LINE FROM BUS 342058 [2PENN 69.000] TO BUS 324951 [2SCOTT CO 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.24712 | 16.1864
SINGLE OPN TIE 649 342133-324492(1) | OPEN LINE FROM BUS 342133 [2RENAKER 69.000] TO BUS 324492 [2CYNTHIAN SW69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.5963
SINGLE OPN TIE 650 342157-324708(1) | OPEN LINE FROM BUS 342157 [2ROGERSVIL J69.000] TO BUS 324708 [2ROGERSVILLE69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.23133 | 3.2424
SINGLE OPN TIE 651 342184-324445(1) | OPEN LINE FROM BUS 342184 [2S ANDERSON 69.000] TO BUS 324445 [2BONDS MILL 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.3087
SINGLE OPN TIE 652 342184-324445(2) | OPEN LINE FROM BUS 342184 [2S ANDERSON 69.000] TO BUS 324445 [2BONDS MILL 69.000] CKT 2 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.3087
SINGLE OPN TIE 653 342218-247897(Z1) | OPEN LINE FROM BUS 342218 [2SALT LICK 138.00] TO BUS 247897 [05SNAG FK SS138.00] CKT Z1 | TRUE | Met convergence tolerances | 1 | 0.16476 | 20.9266 | 1 | 4.2393
SINGLE OPN TIE 654 342232-324787(1) | OPEN LINE FROM BUS 342232 [2SEWELLTON 69.000] TO BUS 324787 [2UNION UNDWR69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.427
SINGLE OPN TIE 655 342248-324718(1) | OPEN LINE FROM BUS 342248 [2SHELBY TAP 69.000] TO BUS 324718 [2SHELBY CO T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.5024
SINGLE OPN TIE 656 342287-324531(1) | OPEN LINE FROM BUS 342287 [2SOMERSET KU69.000] TO BUS 324531 [2FERGUSON SO69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.8268
SINGLE OPN TIE 657 342287-324737(1) | OPEN LINE FROM BUS 342287 [2SOMERSET KU69.000] TO BUS 324737 [2SOMERSET SO69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.8079
SINGLE OPN TIE 658 342307-324509(1) | OPEN LINE FROM BUS 342307 [2STEPHENSBRG69.000] TO BUS 324509 [2EASTVIEW 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.51
SINGLE OPN TIE 659 342340-324519(1) | OPEN LINE FROM BUS 342340 [2THARP T 69.000] TO BUS 324519 [2ETOWN KU 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.4509 | 19.8947
SINGLE OPN TIE 660 342343-246971(1) | OPEN LINE FROM BUS 342343 [2THELMA 69.000] TO BUS 246971 [05THELM2 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.51601 | 24.1233
SINGLE OPN TIE 661 342454-251315(1) | OPEN LINE FROM BUS 342454 [2W M SMITH 69.000] TO BUS 251315 [08EKSMTH 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 18.0374 | 1 | 3.651
SINGLE OPN TIE 662 342487-250148(1) | OPEN LINE FROM BUS 342487 [2WEBSTER RD 69.000] TO BUS 250148 [08EKPWEB 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.3962
SINGLE OPN TIE 663 342538-243688(1) | OPEN LINE FROM BUS 342538 [4ARGENTUM 138.00] TO BUS 243688 [05S.PORT MTR138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.9784
SINGLE OPN TIE 664 342544-324275(1) | OPEN LINE FROM BUS 342544 [4AVON-R 138.00] TO BUS 324275 [4LOUDON AVE 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.62224 | 24.8714
SINGLE OPN TIE 665 342547-324210(1) | OPEN LINE FROM BUS 342547 [4BAKER LN 138.00] TO BUS 324210 [4BAKER LANE 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.41646 | 19.672
SINGLE OPN TIE 666 342559-250054(1) | OPEN LINE FROM BUS 342559 [4BOONE CO 138.00] TO BUS 250054 [08LONGBR 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.7002
SINGLE OPN TIE 667 342565-325925(1) | OPEN LINE FROM BUS 342565 [4BOONESBOR T138.00] TO BUS 325925 [4BOONSBORO N138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.64721 | 25.4616
SINGLE OPN TIE 668 342568-324047(1) | OPEN LINE FROM BUS 342568 [4CENT HARDIN138.00] TO BUS 324047 [4BLACKBRANCH138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.46153 | 21.0457
SINGLE OPN TIE 669 342568-324261(1) | OPEN LINE FROM BUS 342568 [4CENT HARDIN138.00] TO BUS 324261 [4HARDIN CO 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.25841 | 16.4954
SINGLE OPN TIE 670 342577-324247(1) | OPEN LINE FROM BUS 342577 [4FAWKES EK 138.00] TO BUS 324247 [4FAWKES TAP 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.2469
SINGLE OPN TIE 671 342577-324248(1) | OPEN LINE FROM BUS 342577 [4FAWKES EK 138.00] TO BUS 324248 [4FAWKES KU 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.2538
SINGLE OPN TIE 672 342586-324253(1) | OPEN LINE FROM BUS 342586 [4GALLATIN CO138.00] TO BUS 324253 [4GHENT 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.62354 | 25.8376
SINGLE OPN TIE 673 342595-250152(1) | OPEN LINE FROM BUS 342595 [4HEBRON 138.00] TO BUS 250152 [08HEBRNG 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.4365
SINGLE OPN TIE 674 342607-342918(1) | OPEN LINE FROM BUS 342607 [4JK SMITH 138.00] TO BUS 342918 [1JKCT 1G 13.800] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.19898 | 11.1905
SINGLE OPN TIE 675 342607-342921(1) | OPEN LINE FROM BUS 342607 [4JK SMITH 138.00] TO BUS 342921 [1JKCT 2G 13.800] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.19892 | 11.2129
SINGLE OPN TIE 676 342607-342924(1) | OPEN LINE FROM BUS 342607 [4JK SMITH 138.00] TO BUS 342924 [1JKCT 3G 13.800] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.19902 | 11.1962
SINGLE OPN TIE 677 342607-342927(1) | OPEN LINE FROM BUS 342607 [4JK SMITH 138.00] TO BUS 342927 [1JKCT 4G 13.800] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.89322 | 53.0179
SINGLE OPN TIE 678 342607-342930(1) | OPEN LINE FROM BUS 342607 [4JK SMITH 138.00] TO BUS 342930 [1JKCT 5G 13.800] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.89321 | 53.5488
SINGLE OPN TIE 679 342607-342933(1) | OPEN LINE FROM BUS 342607 [4JK SMITH 138.00] TO BUS 342933 [1JKCT 6G 13.800] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.89323 | 53.0627
SINGLE OPN TIE 680 342607-342936(1) | OPEN LINE FROM BUS 342607 [4JK SMITH 138.00] TO BUS 342936 [1JKCT 7G 13.800] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.89322 | 53.0461
SINGLE OPN TIE 681 342616-342948(1) | OPEN LINE FROM BUS 342616 [4LOVE HYDRO 138.00] TO BUS 342948 [1LOVE HYDRO 4.1600] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.52034 | 30.7022
SINGLE OPN TIE 682 342631-324328(1) | OPEN LINE FROM BUS 342631 [4PARIS T 138.00] TO BUS 324328 [4PARIS 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.51994 | 21.6258
SINGLE OPN TIE 683 342649-324302(1) | OPEN LINE FROM BUS 342649 [4ROWAN CO 138.00] TO BUS 324302 [4RODBURN 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.9222
SINGLE OPN TIE 684 342661-324267(1) | OPEN LINE FROM BUS 342661 [4SPUR-KENT-R138.00] TO BUS 324267 [4KENTON 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.55603 | 23.3299
SINGLE OPN TIE 685 342664-342957(1) | OPEN LINE FROM BUS 342664 [4SPURLOCK 138.00] TO BUS 342957 [1SPURLK1G 22.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.80462 | 44.2787 | 1 | 44
SINGLE OPN TIE 686 342688-324276(1) | OPEN LINE FROM BUS 342688 [4UNION CTY T138.00] TO BUS 324276 [4LAKE REBA T138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.59788 | 23.2802
SINGLE OPN TIE 687 342697-324138(1) | OPEN LINE FROM BUS 342697 [5BEATTYV J 161.00] TO BUS 324138 [5DELVINTA 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.2559
SINGLE OPN TIE 688 342697-324430(1) | OPEN LINE FROM BUS 342697 [5BEATTYV J 161.00] TO BUS 324430 [2BEATTYVI KU69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.8457
SINGLE OPN TIE 689 342700-326975(1) | OPEN LINE FROM BUS 342700 [5BULLITT CO 161.00] TO BUS 326975 [5CEDAR GRV 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.87402 | 36.1864
SINGLE OPN TIE 690 342700-326998(1) | OPEN LINE FROM BUS 342700 [5BULLITT CO 161.00] TO BUS 326998 [5BULLITT TAP161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.2776
SINGLE OPN TIE 691 342718-324141(1) | OPEN LINE FROM BUS 342718 [5COOPER2 161.00] TO BUS 324141 [5ELIHU 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.2606
SINGLE OPN TIE 692 342732-361603(1) | OPEN LINE FROM BUS 342732 [5FOX HOLLOW 161.00] TO BUS 361603 [5E GLASGOW T161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.54687 | 22.1502
SINGLE OPN TIE 693 342736-324138(1) | OPEN LINE FROM BUS 342736 [5GREEN HAL T161.00] TO BUS 324138 [5DELVINTA 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.4587 | 19.8149
SINGLE OPN TIE 694 342757-342945(1) | OPEN LINE FROM BUS 342757 [5LAUREL DAM 161.00] TO BUS 342945 [1LAUREL 1G 13.800] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 2.6853
SINGLE OPN TIE 695 342770-324271(1) | OPEN LINE FROM BUS 342770 [4MARION CO 138.00] TO BUS 324271 [4LEBANON 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.46788 | 19.9698
SINGLE OPN TIE 696 342778-360473(1) | OPEN LINE FROM BUS 342778 [5MCCREARY CO161.00] TO BUS 360473 [5JELLICO TN 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.2221
SINGLE OPN TIE 697 342778-360486(1) | OPEN LINE FROM BUS 342778 [5MCCREARY CO161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.2292
SINGLE OPN TIE 698 342778-361579(1) | OPEN LINE FROM BUS 342778 [5MCCREARY CO161.00] TO BUS 361579 [5WINFIELD TN161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.0787
SINGLE OPN TIE 699 342781-324688(1) | OPEN LINE FROM BUS 342781 [5PITTSBURG 161.00] TO BUS 324688 [2PITTSBRG KU69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.39386 | 18.1592
SINGLE OPN TIE 700 342796-360448(1) | OPEN LINE FROM BUS 342796 [5RUSSEL CO J161.00] TO BUS 360448 [5WOLF CRK HP161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.70999 | 27.7987
SINGLE OPN TIE 701 342814-360334(1) | OPEN LINE FROM BUS 342814 [5SUMM SHADE 161.00] TO BUS 360334 [5SUMMER SHAD161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.2649
SINGLE OPN TIE 702 342814-361788(1) | OPEN LINE FROM BUS 342814 [5SUMM SHADE 161.00] TO BUS 361788 [5SUM SHAD TP161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.2516
SINGLE OPN TIE 703 342817-325921(1) | OPEN LINE FROM BUS 342817 [5TAYLOR CO J161.00] TO BUS 325921 [5TAYLOR CO 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.46132 | 20.0302
SINGLE OPN TIE 704 342823-360486(1) | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.57528 | 22.9693
SINGLE OPN TIE 705 342832-342939-342942(1) | OPEN LINE FROM BUS 342832 [7JK SMITH 345.00] TO BUS 342939 [1JKCT 9G 13.800] TO BUS 342942 [1JKCT 10G 13.800] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.32916 | 15.0814 | 2 | 6
SINGLE OPN TIE 706 342838-249581(1) | OPEN LINE FROM BUS 342838 [7SPURLOCK 345.00] TO BUS 249581 [08MELDAL 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.3346 | 2.9313
SINGLE OPN TIE 707 342838-253077(1) | OPEN LINE FROM BUS 342838 [7SPURLOCK 345.00] TO BUS 253077 [09STUART 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.19768 | 13.0099
SINGLE OPN TIE 708 342838-342960(1) | OPEN LINE FROM BUS 342838 [7SPURLOCK 345.00] TO BUS 342960 [1SPURLK2G 22.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.17993 | 12.2269 | 1 | 45
SINGLE OPN TIE 709 342838-342963(1) | OPEN LINE FROM BUS 342838 [7SPURLOCK 345.00] TO BUS 342963 [1SPURLK3G 18.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.76952 | 42.2676 | 1 | 20
SINGLE OPN TIE 710 342838-342966(1) | OPEN LINE FROM BUS 342838 [7SPURLOCK 345.00] TO BUS 342966 [1SPURLK4G 18.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.70698 | 38.9002 | 1 | 38
SINGLE OPN TIE 711 342841-325074(Z1) | OPEN LINE FROM BUS 342841 [7W GARRARDEK345.00] TO BUS 325074 [7W GARRARDKU345.00] CKT Z1 | TRUE | Met convergence tolerances | 0 | 0.33444 | 16.8925
SINGLE OPN TIE 712 342844-384157(1) | OPEN LINE FROM BUS 342844 [8SOUTHGEN 500.00] TO BUS 384157 [8MILLER8 500.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 1.336
SINGLE OPN TIE 713 342847-243205(1) | OPEN LINE FROM BUS 342847 [9NORTHGEN 765.00] TO BUS 243205 [05COOK 765.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 6.1441
BARREN CO - HORSECAVE 69 SS | OPEN BRANCH FROM BUS 341059 [2BARREN CO 69.000] TO BUS 341651 [2HORSECAVE J69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.1712
OPEN BRANCH FROM BUS 341651 [2HORSECAVE J69.000] TO BUS 341914 [2MUNFVILKU T69.000] CKT 1
CLOSE BRANCH FROM BUS 341650 [2HORSECAVE T69.000] TO BUS 342241 [2SEYMOUR T 69.000] CKT 1
CAVE CITY J-SEYMOUR T 69 SS | OPEN BRANCH FROM BUS 341275 [2CAVE CITY J69.000] TO BUS 342241 [2SEYMOUR T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6011
CLOSE BRANCH FROM BUS 341650 [2HORSECAVE T69.000] TO BUS 342241 [2SEYMOUR T 69.000] CKT 1
CAVE CITY - CAVE CITY JCT 69 SS | OPEN BRANCH FROM BUS 341272 [2CAVE CITY 69.000] TO BUS 341275 [2CAVE CITY J69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14177 | 1.9939
OPEN BRANCH FROM BUS 341059 [2BARREN CO 69.000] TO BUS 341275 [2CAVE CITY J69.000] CKT 1
OPEN BRANCH FROM BUS 341275 [2CAVE CITY J69.000] TO BUS 342241 [2SEYMOUR T 69.000] CKT 1
CLOSE BRANCH FROM BUS 341650 [2HORSECAVE T69.000] TO BUS 342241 [2SEYMOUR T 69.000] CKT 1
FOX HOLLOW - PARKWAY1 69 SS | OPEN BRANCH FROM BUS 341491 [2FOX HOLLOW 69.000] TO BUS 342037 [2PARKWAY 1 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.4222
CLOSE BRANCH FROM BUS 342040 [2PARKWAY 2 69.000] TO BUS 342043 [2PARKWAY 2 T69.000] CKT 1
WAYNE CO - ZULA TAP 69 SS | OPEN BRANCH FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342535 [2ZULA T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.3306
CLOSE BRANCH FROM BUS 342532 [2ZULA J NO 69.000] TO BUS 342535 [2ZULA T 69.000] CKT 1
KU GARRARD T-MANCHESTER 69 SS | OPEN BRANCH FROM BUS 341521 [2GARRARDKU T69.000] TO BUS 341806 [2MANCHESTER 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.3924
CLOSE BRANCH FROM BUS 341521 [2GARRARDKU T69.000] TO BUS 341439 [2ELK MT IP 69.000] CKT 1
GREEN BRIAR T-MANCHESTER 69 SS | OPEN BRANCH FROM BUS 341569 [2GREENBRIA T69.000] TO BUS 341806 [2MANCHESTER 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.3902
CLOSE BRANCH FROM BUS 341521 [2GARRARDKU T69.000] TO BUS 341439 [2ELK MT IP 69.000] CKT 1
FALL ROCK-GREEN BRIAR T 69 SS | OPEN BRANCH FROM BUS 341464 [2FALL ROCK 69.000] TO BUS 341569 [2GREENBRIA T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.7723
CLOSE BRANCH FROM BUS 341521 [2GARRARDKU T69.000] TO BUS 341439 [2ELK MT IP 69.000] CKT 1
BIG CREEK - BIG CREEK TAP 69 SS | OPEN BRANCH FROM BUS 341110 [2BIG CREEK 69.000] TO BUS 341113 [2BIG CREEK T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.8101
CLOSE BRANCH FROM BUS 341521 [2GARRARDKU T69.000] TO BUS 341439 [2ELK MT IP 69.000] CKT 1
FALL ROCK - BIG CREEK TAP 69 SS | OPEN BRANCH FROM BUS 341113 [2BIG CREEK T69.000] TO BUS 341464 [2FALL ROCK 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.8868
CLOSE BRANCH FROM BUS 341521 [2GARRARDKU T69.000] TO BUS 341439 [2ELK MT IP 69.000] CKT 1
BIG CREEK - ELK MT 69 SS | OPEN BRANCH FROM BUS 341110 [2BIG CREEK 69.000] TO BUS 341439 [2ELK MT IP 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6449
CLOSE BRANCH FROM BUS 341521 [2GARRARDKU T69.000] TO BUS 341439 [2ELK MT IP 69.000] CKT 1
CLAY LICK JCT - S ANDERSON 69 SS | OPEN BRANCH FROM BUS 341311 [2CLAY LCK J 69.000] TO BUS 342184 [2S ANDERSON 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 4.0381
OPEN BRANCH FROM BUS 341857 [2MERCR IND 69.000] TO BUS 342406 [2VAN ARSDELL69.000] CKT 1
CLOSE BRANCH FROM BUS 325087 [2CLAY LICK T69.000] TO BUS 341314 [2CLAY LCK SW69.000] CKT 1
CLAY LICK J-CLAY LICK SW 69 SS | OPEN BRANCH FROM BUS 341311 [2CLAY LCK J 69.000] TO BUS 341314 [2CLAY LCK SW69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.7591
CLOSE BRANCH FROM BUS 325087 [2CLAY LICK T69.000] TO BUS 341314 [2CLAY LCK SW69.000] CKT 1
OWEN CO - OWEN CO JCT 2 69 SS | OPEN BRANCH FROM BUS 342007 [2OWEN CO 69.000] TO BUS 342013 [2OWEN CO J2 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.2533
CLOSE BRANCH FROM BUS 342010 [2OWEN CO J1 69.000] TO BUS 342013 [2OWEN CO J2 69.000] CKT 1
OWEN CO JCT 1 - BROMLEY EK 69 SS | OPEN BRANCH FROM BUS 341200 [2BROMLEYEK 69.000] TO BUS 342010 [2OWEN CO J1 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.35765 | 18.7472
CLOSE BRANCH FROM BUS 342133 [2RENAKER 69.000] TO BUS 342502 [2WILLIAMSTWN69.000] CKT 1
BROMLEY EK - MUNK JCT 69 SS | OPEN BRANCH FROM BUS 341200 [2BROMLEYEK 69.000] TO BUS 341920 [2MUNK J 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.47837 | 5.3201
CLOSE BRANCH FROM BUS 342133 [2RENAKER 69.000] TO BUS 342502 [2WILLIAMSTWN69.000] CKT 1
MUNK JCT - WILLIAMSTOWN 69 SS | OPEN BRANCH FROM BUS 341920 [2MUNK J 69.000] TO BUS 342502 [2WILLIAMSTWN69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.33588 | 18.0553
OPEN BRANCH FROM BUS 341200 [2BROMLEYEK 69.000] TO BUS 341920 [2MUNK J 69.000] CKT 1
OPEN BRANCH FROM BUS 341920 [2MUNK J 69.000] TO BUS 341998 [2OAKLEY NOEL69.000] CKT 1
CLOSE BRANCH FROM BUS 342133 [2RENAKER 69.000] TO BUS 342502 [2WILLIAMSTWN69.000] CKT 1
RENAKER - THREE M 69 SS | OPEN BRANCH FROM BUS 342133 [2RENAKER 69.000] TO BUS 342355 [2THREE M T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.4237
OPEN BRANCH FROM BUS 341377 [2CYNTHIA TIE69.000] TO BUS 341602 [2HEADQTRS 69.000] CKT 1
CLOSE BRANCH FROM BUS 325085 [2CYNTHI EK T69.000] TO BUS 341377 [2CYNTHIA TIE69.000] CKT 1
KU W FRANKFORT BRDGPT1 69 SS | OPEN BRANCH FROM BUS 324765 [2W FRANKFORT69.000] TO BUS 326973 [2BRIDGPRT 1 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.4361
CLOSE BRANCH FROM BUS 326973 [2BRIDGPRT 1 69.000] TO BUS 326974 [2BRIDGPRT 2 69.000] CKT Z0
BRIDGEPORT J-BRDGPT2 69 SS | OPEN BRANCH FROM BUS 326528 [2BRIDGEPORT 69.000] TO BUS 326974 [2BRIDGPRT 2 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.248
CLOSE BRANCH FROM BUS 326973 [2BRIDGPRT 1 69.000] TO BUS 326974 [2BRIDGPRT 2 69.000] CKT Z0
STANLEY PARKER - BANK LICK 69 SS | OPEN BRANCH FROM BUS 341050 [2BANK LCK 69.000] TO BUS 342295 [2STANLY P J169.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14177 | 1.3654
OPEN BRANCH FROM BUS 342292 [2STANLEY PRK69.000] TO BUS 342295 [2STANLY P J169.000] CKT 1
OPEN BRANCH FROM BUS 341404 [2DURO T 69.000] TO BUS 342295 [2STANLY P J169.000] CKT 1
CLOSE BRANCH FROM BUS 341050 [2BANK LCK 69.000] TO BUS 342298 [2STANLY P J269.000] CKT 1
BEATTYVILLE-BEATTYVLLE D SS | OPEN BRANCH FROM BUS 341071 [2BEATTYV 69.000] TO BUS 341074 [2BEATTYV D 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.5681
CLOSE BRANCH FROM BUS 341074 [2BEATTYV D 69.000] TO BUS 341077 [2BEATTYV J 69.000] CKT 1
BEATTYVILLE DIST - OAKDALE 69 SS | OPEN BRANCH FROM BUS 341071 [2BEATTYV 69.000] TO BUS 341077 [2BEATTYV J 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.5689
CLOSE BRANCH FROM BUS 341074 [2BEATTYV D 69.000] TO BUS 341077 [2BEATTYV J 69.000] CKT 1
SHELBY CO BUS SS | OPEN LINE FROM BUS 342247 [2SHELBY CO 69.000] TO BUS 342248 [2SHELBY TAP 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.16004 | 21.8135 | 1 | 5.1171
OPEN LINE FROM BUS 342247 [2SHELBY CO 69.000] TO BUS 342410 [2VEECHDALE 69.000] CKT 1
OPEN LINE FROM BUS 342247 [2SHELBY CO 69.000] TO BUS 342808 [5SHELBY CO 161.00] CKT 1
OPEN LINE FROM BUS 342247 [2SHELBY CO 69.000] TO BUS 341775 [2LOGAN TAP 69.000] CKT 1
CLOSE BRANCH FROM BUS 342248 [2SHELBY TAP 69.000] TO BUS 341775 [2LOGAN TAP 69.000] CKT 1
EKPC_P1-2_OWEN-PENN69 | OPEN BRANCH FROM BUS 342007 [2OWEN CO 69.000] TO BUS 341725 [2KEITH 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.41894 | 35.9964 | 1 | 8.2574
OPEN BRANCH FROM BUS 342058 [2PENN 69.000] TO BUS 341725 [2KEITH 69.000] CKT 1
EKPC_P1-2_PENN-RENAKER69 | OPEN BRANCH FROM BUS 342058 [2PENN 69.000] TO BUS 341749 [2LEES LICK 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.25569 | 27.7335 | 1 | 6.1828
OPEN BRANCH FROM BUS 342133 [2RENAKER 69.000] TO BUS 341749 [2LEES LICK 69.000] CKT 1
EKPC_P1-2_BOONE-HEBRON69 | OPEN BRANCH FROM BUS 341164 [2BOONE CO 69.000] TO BUS 341167 [2BOONE DIST 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.39449 | 26.8093 | 4 | 36.1052
OPEN LINE FROM BUS 341095 [2BELLVIEW T 69.000] TO BUS 341164 [2BOONE CO 69.000] CKT 1
OPEN LINE FROM BUS 341095 [2BELLVIEW T 69.000] TO BUS 341227 [2BURLINGTN T69.000] CKT 1
OPEN LINE FROM BUS 341095 [2BELLVIEW T 69.000] TO BUS 341092 [2BELLVIEW 69.000] CKT 1
OPEN BRANCH FROM BUS 341224 [2BURLINGTN 69.000] TO BUS 341227 [2BURLINGTN T69.000] CKT 1
OPEN BRANCH FROM BUS 341218 [2BULLITTSVIL69.000] TO BUS 341227 [2BURLINGTN T69.000] CKT 1
OPEN BRANCH FROM BUS 341218 [2BULLITTSVIL69.000] TO BUS 341605 [2HEBRON 69.000] CKT 1
EKPC_P1-2_BOON-OWN-REN69 | OPEN BRANCH FROM BUS 341107 [2BIG BONE T 69.000] TO BUS 341164 [2BOONE CO 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.42973 | 29.1067 | 5 | 39.7354
OPEN BRANCH FROM BUS 341104 [2BIG BONE 69.000] TO BUS 341107 [2BIG BONE T 69.000] CKT 1
OPEN BRANCH FROM BUS 341107 [2BIG BONE T 69.000] TO BUS 341917 [2MUNK 69.000] CKT 1
OPEN BRANCH FROM BUS 341917 [2MUNK 69.000] TO BUS 341998 [2OAKLEY NOEL69.000] CKT 1
OPEN BRANCH FROM BUS 341920 [2MUNK J 69.000] TO BUS 341998 [2OAKLEY NOEL69.000] CKT 1
OPEN BRANCH FROM BUS 341920 [2MUNK J 69.000] TO BUS 342502 [2WILLIAMSTWN69.000] CKT 1
OPEN BRANCH FROM BUS 341200 [2BROMLEYEK 69.000] TO BUS 341920 [2MUNK J 69.000] CKT 1
OPEN BRANCH FROM BUS 341200 [2BROMLEYEK 69.000] TO BUS 342010 [2OWEN CO J1 69.000] CKT 1
OPEN BRANCH FROM BUS 342007 [2OWEN CO 69.000] TO BUS 342010 [2OWEN CO J1 69.000] CKT 1
EKPC_P1-2_T FTJ-WEB RD69 | OPEN BRANCH FROM BUS 341194 [2BRISTOW 69.000] TO BUS 342388 [2TURKEY FT J69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.26117 | 18.732 | 2 | 24.7743
OPEN BRANCH FROM BUS 341194 [2BRISTOW 69.000] TO BUS 342385 [2TURKEY FT 69.000] CKT 1
OPEN BRANCH FROM BUS 342385 [2TURKEY FT 69.000] TO BUS 342487 [2WEBSTER RD 69.000] CKT 1
EKPC_P1-2_TFTJ- ST PRK69 | OPEN BRANCH FROM BUS 341404 [2DURO T 69.000] TO BUS 342388 [2TURKEY FT J69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.40237 | 27.4119 | 3 | 36.8565
OPEN BRANCH FROM BUS 341404 [2DURO T 69.000] TO BUS 341842 [2MBUSA T 69.000] CKT 1
OPEN BRANCH FROM BUS 341839 [2MBUSA 69.000] TO BUS 341842 [2MBUSA T 69.000] CKT 1
OPEN BRANCH FROM BUS 341401 [2DURO 69.000] TO BUS 341842 [2MBUSA T 69.000] CKT 1
OPEN BRANCH FROM BUS 341404 [2DURO T 69.000] TO BUS 342295 [2STANLY P J169.000] CKT 1
OPEN BRANCH FROM BUS 341050 [2BANK LCK 69.000] TO BUS 342295 [2STANLY P J169.000] CKT 1
OPEN BRANCH FROM BUS 342292 [2STANLEY PRK69.000] TO BUS 342295 [2STANLY P J169.000] CKT 1
EKPC_P1-2_ST PRK-BRAK 69 | OPEN BRANCH FROM BUS 342292 [2STANLEY PRK69.000] TO BUS 342298 [2STANLY P J269.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.30902 | 21.5979 | 2 | 28.4895
OPEN BRANCH FROM BUS 341551 [2GRANTS LICK69.000] TO BUS 342298 [2STANLY P J269.000] CKT 1
OPEN BRANCH FROM BUS 341551 [2GRANTS LICK69.000] TO BUS 341587 [2GRIFFIN J 69.000] CKT 1
OPEN BRANCH FROM BUS 341188 [2BRACKEN CO 69.000] TO BUS 341587 [2GRIFFIN J 69.000] CKT 1
EKPC_P1-2_OWN-CARSON 69 | OPEN BRANCH FROM BUS 342007 [2OWEN CO 69.000] TO BUS 342013 [2OWEN CO J2 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.22673 | 25.7957 | 1 | 5.8918
OPEN BRANCH FROM BUS 341260 [2CARSON 69.000] TO BUS 342013 [2OWEN CO J2 69.000] CKT 1
EKPC_P1-2_OWN-CLY VILL69 | OPEN BRANCH FROM BUS 341950 [2NEW CASTLE 69.000] TO BUS 342007 [2OWEN CO 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.49517 | 39.5253 | 2 | 9.3274
OPEN BRANCH FROM BUS 341390 [2DEFOE TAP 69.000] TO BUS 341950 [2NEW CASTLE 69.000] CKT 1
OPEN BRANCH FROM BUS 341390 [2DEFOE TAP 69.000] TO BUS 341391 [2DEFOE 69.000] CKT 1
OPEN BRANCH FROM BUS 341317 [2CLAY VILLAG69.000] TO BUS 341390 [2DEFOE TAP 69.000] CKT 1
EKPC_P1-2_BRAK- REN 69 | OPEN BRANCH FROM BUS 341188 [2BRACKEN CO 69.000] TO BUS 341488 [2FOUR OAKS T69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.19123 | 13.9625 | 3 | 18.9036
OPEN BRANCH FROM BUS 341485 [2FOUR OAKS 69.000] TO BUS 341488 [2FOUR OAKS T69.000] CKT 1
OPEN BRANCH FROM BUS 341485 [2FOUR OAKS 69.000] TO BUS 341550 [2FALMOUTH KU69.000] CKT 1
OPEN BRANCH FROM BUS 341326 [2COLEMANSVIL69.000] TO BUS 341488 [2FOUR OAKS T69.000] CKT 1
OPEN BRANCH FROM BUS 341326 [2COLEMANSVIL69.000] TO BUS 342133 [2RENAKER 69.000] CKT 1
EKPC_P1-2_BRAK- KU KEN69 | OPEN BRANCH FROM BUS 324722 [2SHARON KU 69.000] TO BUS 341188 [2BRACKEN CO 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14177 | 9.2775 | 2 | 13.28
OPEN BRANCH FROM BUS 324195 [2AUGUSTA 69.000] TO BUS 324722 [2SHARON KU 69.000] CKT 1
OPEN BRANCH FROM BUS 324589 [2KENTON 688 69.000] TO BUS 324722 [2SHARON KU 69.000] CKT 1
EKPC_P1-2_PLUM-GODDARD69 | OPEN BRANCH FROM BUS 342091 [2PLUMVILLE 69.000] TO BUS 342124 [2RECTORVILLE69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.2165 | 16.3044 | 3 | 21.3618
OPEN BRANCH FROM BUS 341299 [2CHARTERS 69.000] TO BUS 342124 [2RECTORVILLE69.000] CKT 1
OPEN BRANCH FROM BUS 341299 [2CHARTERS 69.000] TO BUS 341989 [2OAK RIDGE T69.000] CKT 1
OPEN BRANCH FROM BUS 341986 [2OAK RIDGE 69.000] TO BUS 341989 [2OAK RIDGE T69.000] CKT 1
OPEN BRANCH FROM BUS 341536 [2GODDARD 69.000] TO BUS 341989 [2OAK RIDGE T69.000] CKT 1
EKPC_P1-2_MURPH - HQ 69 | OPEN BRANCH FROM BUS 341923 [2MURPHYSVIL 69.000] TO BUS 342280 [2SNOW HILL 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.15945 | 20.3937 | 1 | 4.4062
OPEN BRANCH FROM BUS 341602 [2HEADQTRS 69.000] TO BUS 342280 [2SNOW HILL 69.000] CKT 1
EKPC_P1-2_MURPH-MILLBG69 | OPEN BRANCH FROM BUS 324717 [2SARDIS TAP 69.000] TO BUS 341923 [2MURPHYSVIL 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.16506 | 15.2108 | 1 | 1.36
OPEN BRANCH FROM BUS 324717 [2SARDIS TAP 69.000] TO BUS 326549 [2SARDIS 69.000] CKT 1
OPEN BRANCH FROM BUS 324642 [2MILLERSBURG69.000] TO BUS 324717 [2SARDIS TAP 69.000] CKT 1
EKPC_P1-2_MURPH-KU KEN69 | OPEN BRANCH FROM BUS 325019 [2KENTON-6 69.000] TO BUS 341923 [2MURPHYSVIL 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.74751 | 33.8601 | 1 | 8.38
OPEN BRANCH FROM BUS 324589 [2KENTON 688 69.000] TO BUS 325019 [2KENTON-6 69.000] CKT 1
EKPC_P1-2_ARGEN - LEON69 | OPEN BRANCH FROM BUS 341020 [2ARGENTUM 69.000] TO BUS 341782 [2LOW GAP T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.3556 | 23.3476 | 5 | 31.3664
OPEN BRANCH FROM BUS 341779 [2LOW GAP 69.000] TO BUS 341782 [2LOW GAP T 69.000] CKT 1
OPEN BRANCH FROM BUS 341782 [2LOW GAP T 69.000] TO BUS 342475 [2WARNOCK 69.000] CKT 1
OPEN BRANCH FROM BUS 341266 [2CARTER CY T69.000] TO BUS 342475 [2WARNOCK 69.000] CKT 1
OPEN BRANCH FROM BUS 341263 [2CARTER CTY 69.000] TO BUS 341266 [2CARTER CY T69.000] CKT 1
OPEN BRANCH FROM BUS 341266 [2CARTER CY T69.000] TO BUS 342034 [2PACTOLUS T 69.000] CKT 1
OPEN BRANCH FROM BUS 342031 [2PACTOLUS 69.000] TO BUS 342034 [2PACTOLUS T 69.000] CKT 1
OPEN BRANCH FROM BUS 341554 [2GRAYSON J 69.000] TO BUS 342034 [2PACTOLUS T 69.000] CKT 1
OPEN BRANCH FROM BUS 243726 [05GRAYSO 69.000] TO BUS 341554 [2GRAYSON J 69.000] CKT 1
OPEN BRANCH FROM BUS 341554 [2GRAYSON J 69.000] TO BUS 341752 [2LEON 69.000] CKT 1
EKPC_P1-2_LEON-SKAGGS 69 | OPEN BRANCH FROM BUS 341002 [2AIRPORT RD 69.000] TO BUS 341752 [2LEON 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.27264 | 19.3693 | 5 | 24.5368
OPEN BRANCH FROM BUS 341002 [2AIRPORT RD 69.000] TO BUS 341443 [2ELLIO CO PT69.000] CKT 1
OPEN BRANCH FROM BUS 341443 [2ELLIO CO PT69.000] TO BUS 341446 [2ELLIOT CO P69.000] CKT 1
OPEN BRANCH FROM BUS 341443 [2ELLIO CO PT69.000] TO BUS 341953 [2NEW FOUNDL 69.000] CKT 1
OPEN BRANCH FROM BUS 341953 [2NEW FOUNDL 69.000] TO BUS 342229 [2SANDY HOOK 69.000] CKT 1
OPEN BRANCH FROM BUS 341836 [2MAZIE 69.000] TO BUS 341953 [2NEW FOUNDL 69.000] CKT 1
OPEN BRANCH FROM BUS 341836 [2MAZIE 69.000] TO BUS 342265 [2SKAGGS 69.000] CKT 1
EKPC_P1-2_FIN-SHL-SHBV69 | OPEN BRANCH FROM BUS 324718 [2SHELBY CO T69.000] TO BUS 342248 [2SHELBY TAP 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.21023 | 13.7248 | 1 | 21.57
OPEN BRANCH FROM BUS 324536 [2FINCHVILLE 69.000] TO BUS 324718 [2SHELBY CO T69.000] CKT 1
OPEN BRANCH FROM BUS 324718 [2SHELBY CO T69.000] TO BUS 324726 [2SHELBYVIL S69.000] CKT 1
OPEN BRANCH FROM BUS 324726 [2SHELBYVIL S69.000] TO BUS 324727 [2SHELBYVILLE69.000] CKT 1
EKPC_P1-2_SHL-BUD-BKRT69 | OPEN BRANCH FROM BUS 341775 [2LOGAN TAP 69.000] TO BUS 342247 [2SHELBY CO 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.66045 | 43.2994 | 3 | 59.1255
OPEN BRANCH FROM BUS 341775 [2LOGAN TAP 69.000] TO BUS 341774 [2LOGAN 2 T 69.000] CKT 1
OPEN BRANCH FROM BUS 341772 [2LOGAN 69.000] TO BUS 341774 [2LOGAN 2 T 69.000] CKT 1
OPEN BRANCH FROM BUS 341212 [2BUDD 69.000] TO BUS 341774 [2LOGAN 2 T 69.000] CKT 1
OPEN LINE FROM BUS 342500 [2WIELAND 69.000] TO BUS 341089 [2BEKAERT 69.000] CKT 1
OPEN LINE FROM BUS 342500 [2WIELAND 69.000] TO BUS 341212 [2BUDD 69.000] CKT 1
EKPC_P1-2_REN - HQ 69 | OPEN BRANCH FROM BUS 342133 [2RENAKER 69.000] TO BUS 342355 [2THREE M T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.19826 | 15.0895 | 1 | 19.4904
OPEN BRANCH FROM BUS 342352 [2THREE M 69.000] TO BUS 342355 [2THREE M T 69.000] CKT 1
OPEN BRANCH FROM BUS 341377 [2CYNTHIA TIE69.000] TO BUS 342355 [2THREE M T 69.000] CKT 1
OPEN BRANCH FROM BUS 341377 [2CYNTHIA TIE69.000] TO BUS 341602 [2HEADQTRS 69.000] CKT 1
EKPC_P1-2_GODD - HOPE 69 | OPEN BRANCH FROM BUS 341536 [2GODDARD 69.000] TO BUS 341623 [2HILLSBORO 69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.27071 | 18.0015 | 5 | 25.9322
OPEN BRANCH FROM BUS 342022 [2OWINGSVIL T69.000] TO BUS 342052 [2PEASTICKS 69.000] CKT 1
OPEN BRANCH FROM BUS 342022 [2OWINGSVIL T69.000] TO BUS 342025 [2OWINGVIL KU69.000] CKT 1
OPEN BRANCH FROM BUS 342022 [2OWINGSVIL T69.000] TO BUS 342112 [2PRESTON T 69.000] CKT 1
OPEN BRANCH FROM BUS 342109 [2PRESTON 69.000] TO BUS 342112 [2PRESTON T 69.000] CKT 1
OPEN BRANCH FROM BUS 341131 [2BLEVINS V T69.000] TO BUS 342112 [2PRESTON T 69.000] CKT 1
OPEN BRANCH FROM BUS 341131 [2BLEVINS V T69.000] TO BUS 341134 [2BLEVINS VAL69.000] CKT 1
OPEN BRANCH FROM BUS 341131 [2BLEVINS V T69.000] TO BUS 341644 [2HOPE 69.000] CKT 1
EKPC_P1-2_GODD - ROW 69 | OPEN BRANCH FROM BUS 341536 [2GODDARD 69.000] TO BUS 342088 [2PLUMMR L T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.31027 | 21.9231 | 3 | 28.3855
OPEN BRANCH FROM BUS 342085 [2PLUMMR L 69.000] TO BUS 342088 [2PLUMMR L T 69.000] CKT 1
OPEN BRANCH FROM BUS 341119 [2BIG WOODS J69.000] TO BUS 342088 [2PLUMMR L T 69.000] CKT 1
OPEN BRANCH FROM BUS 341116 [2BIG WOODS 69.000] TO BUS 341119 [2BIG WOODS J69.000] CKT 1
OPEN BRANCH FROM BUS 341119 [2BIG WOODS J69.000] TO BUS 341620 [2HILDA 69.000] CKT 1
OPEN BRANCH FROM BUS 341620 [2HILDA 69.000] TO BUS 342163 [2ROWAN CO 69.000] CKT 1
EKPC_P1-2_BULL-W BARDJ69 | OPEN BRANCH FROM BUS 341215 [2BULLITT CO 69.000] TO BUS 341389 [2DEATSVILL T69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.3268 | 22.883 | 4 | 30.7499
OPEN BRANCH FROM BUS 341386 [2DEATSVIL 69.000] TO BUS 341389 [2DEATSVILL T69.000] CKT 1
OPEN BRANCH FROM BUS 341389 [2DEATSVILL T69.000] TO BUS 341707 [2JOE TICH T 69.000] CKT 1
OPEN BRANCH FROM BUS 341704 [2JOE TICH 69.000] TO BUS 341707 [2JOE TICH T 69.000] CKT 1
OPEN BRANCH FROM BUS 341707 [2JOE TICH T 69.000] TO BUS 342427 [2W BARDSTWN 69.000] CKT 1
OPEN BRANCH FROM BUS 342186 [2S BARDSTWN 69.000] TO BUS 342427 [2W BARDSTWN 69.000] CKT 1
OPEN BRANCH FROM BUS 342186 [2S BARDSTWN 69.000] TO BUS 342424 [2W BARDST J 69.000] CKT 1
EKPC_P1-2_BULL - NELS 69 | OPEN BRANCH FROM BUS 341068 [2BEAM T 69.000] TO BUS 341215 [2BULLITT CO 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.41323 | 28.1411 | 4 | 38.612
OPEN BRANCH FROM BUS 341065 [2BEAM 69.000] TO BUS 341068 [2BEAM T 69.000] CKT 1
OPEN BRANCH FROM BUS 341068 [2BEAM T 69.000] TO BUS 342253 [2SHEPHEVIL J69.000] CKT 1
OPEN BRANCH FROM BUS 342250 [2SHEPHEVIL 69.000] TO BUS 342253 [2SHEPHEVIL J69.000] CKT 1
OPEN BRANCH FROM BUS 341746 [2LEBANON J 69.000] TO BUS 342253 [2SHEPHEVIL J69.000] CKT 1
OPEN BRANCH FROM BUS 341179 [2BOSTONKU 69.000] TO BUS 341746 [2LEBANON J 69.000] CKT 1
OPEN BRANCH FROM BUS 341179 [2BOSTONKU 69.000] TO BUS 342514 [2WOOSLEY 69.000] CKT 1
OPEN BRANCH FROM BUS 341944 [2NELSON CO 69.000] TO BUS 342514 [2WOOSLEY 69.000] CKT 1
EKPC_P1-2_N SPR -S AND69 | OPEN BRANCH FROM BUS 341137 [2BLOOMFLD 69.000] TO BUS 341935 [2N SPRINGFLD69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.16647 | 13.0962 | 3 | 16.5085
OPEN BRANCH FROM BUS 341137 [2BLOOMFLD 69.000] TO BUS 341296 [2CHAPLIN T 69.000] CKT 1
OPEN BRANCH FROM BUS 341293 [2CHAPLIN 69.000] TO BUS 341296 [2CHAPLIN T 69.000] CKT 1
OPEN BRANCH FROM BUS 341296 [2CHAPLIN T 69.000] TO BUS 342262 [2SINAI 69.000] CKT 1
OPEN BRANCH FROM BUS 342184 [2S ANDERSON 69.000] TO BUS 342262 [2SINAI 69.000] CKT 1
EKPC_P1-2_HNTFMJ-S AND69 | OPEN BRANCH FROM BUS 341662 [2HT ADAMS T 69.000] TO BUS 341671 [2HUNT FARM J69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.27716 | 19.6253 | 4 | 25.6544
OPEN BRANCH FROM BUS 341659 [2HT ADAMS 69.000] TO BUS 341662 [2HT ADAMS T 69.000] CKT 1
OPEN BRANCH FROM BUS 341662 [2HT ADAMS T 69.000] TO BUS 341857 [2MERCR IND 69.000] CKT 1
OPEN BRANCH FROM BUS 341857 [2MERCR IND 69.000] TO BUS 342406 [2VAN ARSDELL69.000] CKT 1
OPEN BRANCH FROM BUS 341311 [2CLAY LCK J 69.000] TO BUS 342406 [2VAN ARSDELL69.000] CKT 1
OPEN BRANCH FROM BUS 341311 [2CLAY LCK J 69.000] TO BUS 341314 [2CLAY LCK SW69.000] CKT 1
OPEN BRANCH FROM BUS 341308 [2CLAY LCK 69.000] TO BUS 341314 [2CLAY LCK SW69.000] CKT 1
OPEN BRANCH FROM BUS 341311 [2CLAY LCK J 69.000] TO BUS 342184 [2S ANDERSON 69.000] CKT 1
EKPC_P1-2_BKR LN-FAY 69 | OPEN BRANCH FROM BUS 341041 [2BAKER LN 69.000] TO BUS 341638 [2HOLLOWAY J 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.57057 | 37.5762 | 4 | 51.005
OPEN BRANCH FROM BUS 341638 [2HOLLOWAY J 69.000] TO BUS 342463 [2W NICHVIL T69.000] CKT 1
OPEN BRANCH FROM BUS 342460 [2W NICHVIL 69.000] TO BUS 342463 [2W NICHVIL T69.000] CKT 1
OPEN BRANCH FROM BUS 341638 [2HOLLOWAY J 69.000] TO BUS 342199 [2S JESSAM J 69.000] CKT 1
OPEN BRANCH FROM BUS 342199 [2S JESSAM J 69.000] TO BUS 342202 [2S JESSAMINE69.000] CKT 1
OPEN BRANCH FROM BUS 341965 [2NICHOLASVIL69.000] TO BUS 342199 [2S JESSAM J 69.000] CKT 1
OPEN BRANCH FROM BUS 341383 [2DAVIS 69.000] TO BUS 341965 [2NICHOLASVIL69.000] CKT 1
OPEN BRANCH FROM BUS 341383 [2DAVIS 69.000] TO BUS 341467 [2FAYETTE 69.000] CKT 1
EKPC_P1-2_HQ-HUNT 69 | OPEN BRANCH FROM BUS 341665 [2HUNT 69.000] TO BUS 341869 [2MILL HUNT T69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.18685 | 14.4456 | 6 | 19.0628
OPEN BRANCH FROM BUS 341869 [2MILL HUNT T69.000] TO BUS 341875 [2MILLER HUNT69.000] CKT 1
OPEN BRANCH FROM BUS 341869 [2MILL HUNT T69.000] TO BUS 342259 [2SIDEVIEW 69.000] CKT 1
OPEN BRANCH FROM BUS 342130 [2REID VILLAG69.000] TO BUS 342259 [2SIDEVIEW 69.000] CKT 1
OPEN BRANCH FROM BUS 341476 [2FOGG PIKE 69.000] TO BUS 342130 [2REID VILLAG69.000] CKT 1
OPEN BRANCH FROM BUS 341476 [2FOGG PIKE 69.000] TO BUS 341899 [2MT STERLING69.000] CKT 1
OPEN BRANCH FROM BUS 341254 [2CANE RIDG T69.000] TO BUS 342259 [2SIDEVIEW 69.000] CKT 1
OPEN BRANCH FROM BUS 341251 [2CANE RIDG 69.000] TO BUS 341254 [2CANE RIDG T69.000] CKT 1
OPEN BRANCH FROM BUS 341254 [2CANE RIDG T69.000] TO BUS 341872 [2MILLB-CRL J69.000] CKT 1
OPEN BRANCH FROM BUS 341872 [2MILLB-CRL J69.000] TO BUS 341878 [2MILLERSB EK69.000] CKT 1
OPEN BRANCH FROM BUS 341602 [2HEADQTRS 69.000] TO BUS 341872 [2MILLB-CRL J69.000] CKT 1
EKPC_P1-2_HUNT-POWELL 69 | OPEN BRANCH FROM BUS 341665 [2HUNT 69.000] TO BUS 341701 [2JK SMITH 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.31075 | 21.9431 | 5 | 28.9586
OPEN BRANCH FROM BUS 341701 [2JK SMITH 69.000] TO BUS 342370 [2TRAPP 69.000] CKT 1
OPEN BRANCH FROM BUS 341599 [2HARGETT T 69.000] TO BUS 342370 [2TRAPP 69.000] CKT 1
OPEN BRANCH FROM BUS 341596 [2HARGETT 69.000] TO BUS 341599 [2HARGETT T 69.000] CKT 1
OPEN BRANCH FROM BUS 341305 [2CLAY CITY T69.000] TO BUS 341599 [2HARGETT T 69.000] CKT 1
OPEN BRANCH FROM BUS 341302 [2CLAY CITY 69.000] TO BUS 341305 [2CLAY CITY T69.000] CKT 1
OPEN BRANCH FROM BUS 341305 [2CLAY CITY T69.000] TO BUS 341593 [2HARDWCRK T 69.000] CKT 1
OPEN BRANCH FROM BUS 341590 [2HARDWCRK 69.000] TO BUS 341593 [2HARDWCRK T 69.000] CKT 1
OPEN BRANCH FROM BUS 341593 [2HARDWCRK T 69.000] TO BUS 342301 [2STANTON 69.000] CKT 1
OPEN BRANCH FROM BUS 342100 [2POWELL CO 69.000] TO BUS 342301 [2STANTON 69.000] CKT 1
EKPC_P1-2_DALE-HTFRMJ69 | OPEN BRANCH FROM BUS 341380 [2DALE 69.000] TO BUS 341962 [2NEWBY 2 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.48075 | 39.0545 | 2 | 9.299
OPEN BRANCH FROM BUS 342361 [2TODDVILLE T69.000] TO BUS 341962 [2NEWBY 2 69.000] CKT 1
OPEN BRANCH FROM BUS 342358 [2TODDVILLE 69.000] TO BUS 342361 [2TODDVILLE T69.000] CKT 1
OPEN BRANCH FROM BUS 341044 [2BALLARD 69.000] TO BUS 342361 [2TODDVILLE T69.000] CKT 1
OPEN BRANCH FROM BUS 341044 [2BALLARD 69.000] TO BUS 341671 [2HUNT FARM J69.000] CKT 1
EKPC_P1-2_DALE-GARRD 69 | OPEN BRANCH FROM BUS 341380 [2DALE 69.000] TO BUS 341959 [2NEWBY 1 69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.81408 | 55.5915 | 2 | 13.1936
OPEN BRANCH FROM BUS 341732 [2LANCASTER T69.000] TO BUS 341959 [2NEWBY 1 69.000] CKT 1
OPEN BRANCH FROM BUS 341515 [2GARRARD CO 69.000] TO BUS 341732 [2LANCASTER T69.000] CKT 1
EKPC_P1-2_HOPE - POW 69 | OPEN BRANCH FROM BUS 341644 [2HOPE 69.000] TO BUS 341683 [2JEFFERSNVIL69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.15994 | 20.3077 | 1 | 4.5971
OPEN BRANCH FROM BUS 341683 [2JEFFERSNVIL69.000] TO BUS 342100 [2POWELL CO 69.000] CKT 1
EKPC_P1-2_HOPE - MORG 69 | OPEN BRANCH FROM BUS 341500 [2FRENCHBURG 69.000] TO BUS 341644 [2HOPE 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14796 | 12.123 | 3 | 14.6255
OPEN BRANCH FROM BUS 341500 [2FRENCHBURG 69.000] TO BUS 341824 [2MARIBA T 69.000] CKT 1
OPEN BRANCH FROM BUS 341821 [2MARIBA 69.000] TO BUS 341824 [2MARIBA T 69.000] CKT 1
OPEN BRANCH FROM BUS 341824 [2MARIBA T 69.000] TO BUS 341833 [2MAYTOWN T 69.000] CKT 1
OPEN BRANCH FROM BUS 341830 [2MAYTOWN 69.000] TO BUS 341833 [2MAYTOWN T 69.000] CKT 1
OPEN BRANCH FROM BUS 341833 [2MAYTOWN T 69.000] TO BUS 341890 [2MORGAN CO 69.000] CKT 1
EKPC_P1-2_MORG-SKAGGS69 | OPEN BRANCH FROM BUS 341653 [2HOT MIX R T69.000] TO BUS 341890 [2MORGAN CO 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.48074 | 38.9313 | 2 | 8.664
OPEN BRANCH FROM BUS 341653 [2HOT MIX R T69.000] TO BUS 341656 [2HOT MIX RD 69.000] CKT 1
OPEN BRANCH FROM BUS 341356 [2CROCKETT T 69.000] TO BUS 341653 [2HOT MIX R T69.000] CKT 1
OPEN BRANCH FROM BUS 341353 [2CROCKETT 69.000] TO BUS 341356 [2CROCKETT T 69.000] CKT 1
OPEN BRANCH FROM BUS 341356 [2CROCKETT T 69.000] TO BUS 342265 [2SKAGGS 69.000] CKT 1
EKPC_P1-2_SKAGGS-FALC69 | OPEN BRANCH FROM BUS 341797 [2MAGGARD 69.000] TO BUS 342265 [2SKAGGS 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14177 | 17.3276 | 1 | 3.9024
OPEN BRANCH FROM BUS 341461 [2FALCON EK 69.000] TO BUS 341797 [2MAGGARD 69.000] CKT 1
EKPC_P1-2_SKAGGS-THELM69 | OPEN BRANCH FROM BUS 342127 [2REDBUSH 69.000] TO BUS 342265 [2SKAGGS 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.57445 | 43.5993 | 2 | 9.6141
OPEN BRANCH FROM BUS 342127 [2REDBUSH 69.000] TO BUS 342421 [2VOLGA 69.000] CKT 1
OPEN BRANCH FROM BUS 342343 [2THELMA 69.000] TO BUS 342421 [2VOLGA 69.000] CKT 1
EKPC_P1-2_C HAR-KU ETN69 | OPEN BRANCH FROM BUS 341287 [2CENT HARDIN69.000] TO BUS 341713 [2KARGLE 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.17816 | 13.9585 | 1 | 18.7858
OPEN BRANCH FROM BUS 324519 [2ETOWN KU 69.000] TO BUS 341713 [2KARGLE 69.000] CKT 1
EKPC_P1-2_STEPH-HODG 69 | OPEN BRANCH FROM BUS 341533 [2GLENDALE 69.000] TO BUS 342307 [2STEPHENSBRG69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.22719 | 26.1596 | 1 | 5.9756
OPEN BRANCH FROM BUS 341533 [2GLENDALE 69.000] TO BUS 341632 [2HODGENVILLE69.000] CKT 1
EKPC_P1-2_STEPH-BONN 69 | OPEN BRANCH FROM BUS 342307 [2STEPHENSBRG69.000] TO BUS 342403 [2UPTON T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14471 | 18.3381 | 1 | 3.4103
OPEN BRANCH FROM BUS 342400 [2UPTON 69.000] TO BUS 342403 [2UPTON T 69.000] CKT 1
OPEN BRANCH FROM BUS 341161 [2BONNIV EK 69.000] TO BUS 342403 [2UPTON T 69.000] CKT 1
EKPC_P1-2_ETOWN-KU ETN69 | OPEN BRANCH FROM BUS 341455 [2ETOWN EK1 69.000] TO BUS 341458 [2ETOWN EK2 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.17576 | 13.9936 | 2 | 19.4062
OPEN BRANCH FROM BUS 341458 [2ETOWN EK2 69.000] TO BUS 342340 [2THARP T 69.000] CKT 1
OPEN BRANCH FROM BUS 342337 [2THARP 69.000] TO BUS 342340 [2THARP T 69.000] CKT 1
OPEN BRANCH FROM BUS 324519 [2ETOWN KU 69.000] TO BUS 342340 [2THARP T 69.000] CKT 1
EKPC_P1-2_ETWN-ROG-RAD69 | OPEN BRANCH FROM BUS 341455 [2ETOWN EK1 69.000] TO BUS 342274 [2SMITHRVIL T69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.53516 | 35.6217 | 6 | 49.5124
OPEN BRANCH FROM BUS 342271 [2SMITHRSVIL 69.000] TO BUS 342274 [2SMITHRVIL T69.000] CKT 1
OPEN LINE FROM BUS 341394 [2PATRIOT PW 69.000] TO BUS 341479 [2S BOUND RD 69.000] CKT 1
OPEN LINE FROM BUS 341394 [2PATRIOT PW 69.000] TO BUS 342151 [2RINEYVILLE 69.000] CKT 1
OPEN LINE FROM BUS 341394 [2PATRIOT PW 69.000] TO BUS 342157 [2ROGERSVIL J69.000] CKT 1
OPEN LINE FROM BUS 341394 [2PATRIOT PW 69.000] TO BUS 342274 [2SMITHRVIL T69.000] CKT 1
OPEN BRANCH FROM BUS 324708 [2ROGERSVILLE69.000] TO BUS 342157 [2ROGERSVIL J69.000] CKT 1
OPEN BRANCH FROM BUS 342157 [2ROGERSVIL J69.000] TO BUS 342418 [2VINE GROVE 69.000] CKT 1
OPEN BRANCH FROM BUS 342415 [2VINE GROV J69.000] TO BUS 342418 [2VINE GROVE 69.000] CKT 1
OPEN BRANCH FROM BUS 342121 [2T BROWN L T69.000] TO BUS 342415 [2VINE GROV J69.000] CKT 1
OPEN BRANCH FROM BUS 342118 [2RADCLIFF 69.000] TO BUS 342121 [2T BROWN L T69.000] CKT 1
OPEN BRANCH FROM BUS 342121 [2T BROWN L T69.000] TO BUS 342328 [2T BROWN LOG69.000] CKT 1
EKPC_P1-2_ETOWN-NELSN 69 | OPEN BRANCH FROM BUS 341455 [2ETOWN EK1 69.000] TO BUS 342379 [2TUNNEL H T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.3141 | 22.0816 | 4 | 29.911
OPEN BRANCH FROM BUS 342379 [2TUNNEL H T 69.000] TO BUS 342382 [2TUNNEL HILL69.000] CKT 1
OPEN BRANCH FROM BUS 341788 [2LYMAN BW T 69.000] TO BUS 342379 [2TUNNEL H T 69.000] CKT 1
OPEN BRANCH FROM BUS 341785 [2LYMAN BW 69.000] TO BUS 341788 [2LYMAN BW T 69.000] CKT 1
OPEN BRANCH FROM BUS 341788 [2LYMAN BW T 69.000] TO BUS 342155 [2ROANOKE T 69.000] CKT 1
OPEN BRANCH FROM BUS 342154 [2ROANOKE 69.000] TO BUS 342155 [2ROANOKE T 69.000] CKT 1
OPEN BRANCH FROM BUS 341332 [2COLESBURG J69.000] TO BUS 342155 [2ROANOKE T 69.000] CKT 1
OPEN BRANCH FROM BUS 341329 [2COLESBURG 69.000] TO BUS 341332 [2COLESBURG J69.000] CKT 1
OPEN BRANCH FROM BUS 341332 [2COLESBURG J69.000] TO BUS 341944 [2NELSON CO 69.000] CKT 1
EKPC_P1-2_W BARDJ-EBRD69 | OPEN BRANCH FROM BUS 341056 [2BARD SHOP T69.000] TO BUS 342424 [2W BARDST J 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.64932 | 47.7288 | 1 | 11.0844
OPEN BRANCH FROM BUS 341053 [2BARD SHOP 69.000] TO BUS 341056 [2BARD SHOP T69.000] CKT 1
OPEN BRANCH FROM BUS 341056 [2BARD SHOP T69.000] TO BUS 341407 [2E BARDSTOWN69.000] CKT 1
EKPC_P1-2_HODG-GREEN 69 | OPEN BRANCH FROM BUS 341632 [2HODGENVILLE69.000] TO BUS 341800 [2MAGNOLIA 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.8224 | 55.7749 | 2 | 12.9325
OPEN BRANCH FROM BUS 341800 [2MAGNOLIA 69.000] TO BUS 342325 [2SUMMERSVIL 69.000] CKT 1
OPEN BRANCH FROM BUS 341563 [2GREEN CO 69.000] TO BUS 342325 [2SUMMERSVIL 69.000] CKT 1
EKPC_P1-2_HODG-N SPR 69 | OPEN BRANCH FROM BUS 341632 [2HODGENVILLE69.000] TO BUS 342316 [2SULPHUR CRK69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.17124 | 13.3362 | 3 | 16.8904
OPEN BRANCH FROM BUS 341776 [2LORETTO 69.000] TO BUS 342316 [2SULPHUR CRK69.000] CKT 1
OPEN BRANCH FROM BUS 341776 [2LORETTO 69.000] TO BUS 342208 [2S SPRINGF T69.000] CKT 1
OPEN BRANCH FROM BUS 342208 [2S SPRINGF T69.000] TO BUS 342211 [2S SPRINGFLD69.000] CKT 1
OPEN BRANCH FROM BUS 341935 [2N SPRINGFLD69.000] TO BUS 342208 [2S SPRINGF T69.000] CKT 1
EKPC_P1-2_E BARD-N SPR69 | OPEN BRANCH FROM BUS 341407 [2E BARDSTOWN69.000] TO BUS 342019 [2OWENS IL J 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.23655 | 17.3876 | 3 | 22.8777
OPEN BRANCH FROM BUS 342016 [2OWENS IL 69.000] TO BUS 342019 [2OWENS IL J 69.000] CKT 1
OPEN BRANCH FROM BUS 341143 [2BLUE G PW T69.000] TO BUS 342019 [2OWENS IL J 69.000] CKT 1
OPEN BRANCH FROM BUS 341140 [2BLUE G PW 69.000] TO BUS 341143 [2BLUE G PW T69.000] CKT 1
OPEN BRANCH FROM BUS 341143 [2BLUE G PW T69.000] TO BUS 342508 [2WOODLAWN 69.000] CKT 1
OPEN BRANCH FROM BUS 341494 [2FREDRIKBG T69.000] TO BUS 342508 [2WOODLAWN 69.000] CKT 1
OPEN BRANCH FROM BUS 341494 [2FREDRIKBG T69.000] TO BUS 341497 [2FREDRIKBRG 69.000] CKT 1
OPEN BRANCH FROM BUS 341494 [2FREDRIKBG T69.000] TO BUS 341935 [2N SPRINGFLD69.000] CKT 1
EKPC_P1-2_E BRD-KU BRD69 | OPEN BRANCH FROM BUS 324425 [2BARDT IND T69.000] TO BUS 341407 [2E BARDSTOWN69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.15182 | 10.7749 | 1 | 17.37
OPEN BRANCH FROM BUS 324345 [2BARDTWN IND69.000] TO BUS 324425 [2BARDT IND T69.000] CKT 1
OPEN BRANCH FROM BUS 324425 [2BARDT IND T69.000] TO BUS 324426 [2BARDSTOWN 69.000] CKT 1
EKPC_P1-2_HNTFMJ-N SPR69 | OPEN BRANCH FROM BUS 341671 [2HUNT FARM J69.000] TO BUS 342061 [2PERRYVILLE 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.45186 | 37.1682 | 2 | 8.3464
OPEN BRANCH FROM BUS 341794 [2MACKVILKU T69.000] TO BUS 342061 [2PERRYVILLE 69.000] CKT 1
OPEN BRANCH FROM BUS 341791 [2MACKVIL KU 69.000] TO BUS 341794 [2MACKVILKU T69.000] CKT 1
OPEN BRANCH FROM BUS 341794 [2MACKVILKU T69.000] TO BUS 341935 [2N SPRINGFLD69.000] CKT 1
EKPC_P1-2_W BER-THRLJ 69 | OPEN BRANCH FROM BUS 342430 [2W BEREA 69.000] TO BUS 342433 [2W BEREA J 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.37957 | 10.8398
OPEN BRANCH FROM BUS 341098 [2BEREAKU T 69.000] TO BUS 342433 [2W BEREA J 69.000] CKT 1
OPEN BRANCH FROM BUS 342349 [2THREE LNK J69.000] TO BUS 342433 [2W BEREA J 69.000] CKT 1
EKPC_P1-2_W BER-KU FAW69 | OPEN BRANCH FROM BUS 341008 [2ALCAN 69.000] TO BUS 342430 [2W BEREA 69.000] CKT 1 | TRUE | Met convergence tolerances | 3 | 0.65269 | 42.7271 | 6 | 57.8204
OPEN BRANCH FROM BUS 341008 [2ALCAN 69.000] TO BUS 342106 [2PPG J 69.000] CKT 1
OPEN BRANCH FROM BUS 342103 [2PPG 69.000] TO BUS 342106 [2PPG J 69.000] CKT 1
OPEN BRANCH FROM BUS 341611 [2HICKORY PL 69.000] TO BUS 342103 [2PPG 69.000] CKT 1
OPEN BRANCH FROM BUS 341362 [2CROOKSVIL T69.000] TO BUS 341611 [2HICKORY PL 69.000] CKT 1
OPEN BRANCH FROM BUS 341359 [2CROOKSVIL 69.000] TO BUS 341362 [2CROOKSVIL T69.000] CKT 1
OPEN BRANCH FROM BUS 324530 [2FAWKES 69.000] TO BUS 341406 [2DUNCAN LN T69.000] CKT 1
EKPC_P1-2_POW - ZACH 69 | OPEN BRANCH FROM BUS 341185 [2BOWEN 69.000] TO BUS 342100 [2POWELL CO 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14177 | 17.3776 | 2 | 4.1422
OPEN BRANCH FROM BUS 341185 [2BOWEN 69.000] TO BUS 341614 [2HIGH ROCK 69.000] CKT 1
OPEN BRANCH FROM BUS 341614 [2HIGH ROCK 69.000] TO BUS 342520 [2ZACHARIAH 69.000] CKT 1
EKPC_P1-2_ZACH-HELECH69 | OPEN BRANCH FROM BUS 341248 [2CAMPTON 69.000] TO BUS 342520 [2ZACHARIAH 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.32807 | 31.9735 | 1 | 7.9277
OPEN BRANCH FROM BUS 341248 [2CAMPTON 69.000] TO BUS 341608 [2HELECHAW 69.000] CKT 1
EKPC_P1-2_BETYV - OAK 69 | OPEN BRANCH FROM BUS 341071 [2BEATTYV 69.000] TO BUS 341074 [2BEATTYV D 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.83865 | 56.6057 | 2 | 13.0124
OPEN BRANCH FROM BUS 341074 [2BEATTYV D 69.000] TO BUS 341992 [2OAKDALE 69.000] CKT 1
EKPC_P1-2_BETYV - TYN 69 | OPEN BRANCH FROM BUS 341077 [2BEATTYV J 69.000] TO BUS 341071 [2BEATTYV 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.79124 | 54.1152 | 2 | 12.4272
OPEN BRANCH FROM BUS 341173 [2BOONEVIL T 69.000] TO BUS 341077 [2BEATTYV J 69.000] CKT 1
OPEN BRANCH FROM BUS 341170 [2BOONEVIL 69.000] TO BUS 341173 [2BOONEVIL T 69.000] CKT 1
OPEN BRANCH FROM BUS 341173 [2BOONEVIL T 69.000] TO BUS 342196 [2WHITE OAK 69.000] CKT 1
OPEN BRANCH FROM BUS 342196 [2WHITE OAK 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1
EKPC_P1-2_HELECH-MAG 69 | OPEN BRANCH FROM BUS 341608 [2HELECHAW 69.000] TO BUS 342313 [2SUBLETT J 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 2.0984
OPEN BRANCH FROM BUS 341803 [2MAGOFFIN CO69.000] TO BUS 342313 [2SUBLETT J 69.000] CKT 1
EKPC_P1-2_FALC - MAG 69 | OPEN BRANCH FROM BUS 341461 [2FALCON EK 69.000] TO BUS 342310 [2SUBLETT 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.32885 | 31.7302 | 1 | 6.8625
OPEN BRANCH FROM BUS 341803 [2MAGOFFIN CO69.000] TO BUS 342310 [2SUBLETT 69.000] CKT 1
EKPC_P1-2_MAG - THELM 69 | OPEN BRANCH FROM BUS 341155 [2BONANZA T 69.000] TO BUS 341803 [2MAGOFFIN CO69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.24875 | 17.9616 | 4 | 22.895
OPEN BRANCH FROM BUS 341152 [2BONANZA 69.000] TO BUS 341155 [2BONANZA T 69.000] CKT 1
OPEN BRANCH FROM BUS 341155 [2BONANZA T 69.000] TO BUS 341860 [2MIDDL CRK T69.000] CKT 1
OPEN BRANCH FROM BUS 341860 [2MIDDL CRK T69.000] TO BUS 341863 [2MIDDLE CRK 69.000] CKT 1
OPEN BRANCH FROM BUS 341122 [2BILL WELL T69.000] TO BUS 341860 [2MIDDL CRK T69.000] CKT 1
OPEN BRANCH FROM BUS 341122 [2BILL WELL T69.000] TO BUS 341125 [2BILL WELLS 69.000] CKT 1
OPEN BRANCH FROM BUS 341122 [2BILL WELL T69.000] TO BUS 341692 [2JENNY WIL T69.000] CKT 1
OPEN BRANCH FROM BUS 341692 [2JENNY WIL T69.000] TO BUS 341695 [2JENNY WILEY69.000] CKT 1
OPEN BRANCH FROM BUS 341692 [2JENNY WIL T69.000] TO BUS 342343 [2THELMA 69.000] CKT 1
EKPC_P1-2_BONN - BARR 69 | OPEN BRANCH FROM BUS 341158 [2BONNIV DIST69.000] TO BUS 341161 [2BONNIV EK 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.71203 | 41.2031 | 4 | 64.4726
OPEN BRANCH FROM BUS 341158 [2BONNIV DIST69.000] TO BUS 341908 [2MUNFVIL EK 69.000] CKT 1
OPEN BRANCH FROM BUS 341908 [2MUNFVIL EK 69.000] TO BUS 341914 [2MUNFVILKU T69.000] CKT 1
OPEN BRANCH FROM BUS 341911 [2MUNFVIL KU 69.000] TO BUS 341914 [2MUNFVILKU T69.000] CKT 1
OPEN BRANCH FROM BUS 341651 [2HORSECAVE J69.000] TO BUS 341914 [2MUNFVILKU T69.000] CKT 1
OPEN BRANCH FROM BUS 341650 [2HORSECAVE T69.000] TO BUS 341651 [2HORSECAVE J69.000] CKT Z1
OPEN BRANCH FROM BUS 341647 [2HORSE CV KU69.000] TO BUS 341650 [2HORSECAVE T69.000] CKT 1
OPEN BRANCH FROM BUS 341059 [2BARREN CO 69.000] TO BUS 341651 [2HORSECAVE J69.000] CKT 1
EKPC_P1-2_GREEN-SUM SH69 | OPEN BRANCH FROM BUS 341563 [2GREEN CO 69.000] TO BUS 341575 [2GREENSBURG 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.25623 | 18.5253 | 5 | 24.9643
OPEN BRANCH FROM BUS 341575 [2GREENSBURG 69.000] TO BUS 341854 [2MCKINNY T 69.000] CKT 1
OPEN BRANCH FROM BUS 341851 [2MCKINNEY 69.000] TO BUS 341854 [2MCKINNY T 69.000] CKT 1
OPEN BRANCH FROM BUS 341728 [2KNOB LICK 69.000] TO BUS 341854 [2MCKINNY T 69.000] CKT 1
OPEN BRANCH FROM BUS 341431 [2EDM-JBGAL J69.000] TO BUS 341728 [2KNOB LICK 69.000] CKT 1
OPEN BRANCH FROM BUS 341431 [2EDM-JBGAL J69.000] TO BUS 341434 [2EDM-JBGAL T69.000] CKT 1
OPEN BRANCH FROM BUS 341434 [2EDM-JBGAL T69.000] TO BUS 341680 [2JB GALLOWAY69.000] CKT 1
OPEN BRANCH FROM BUS 341434 [2EDM-JBGAL T69.000] TO BUS 341437 [2EDMON IND P69.000] CKT 1
OPEN BRANCH FROM BUS 341431 [2EDM-JBGAL J69.000] TO BUS 342322 [2SUMM SHADE 69.000] CKT 1
EKPC_P1-2_CASEY-LIB J69 | OPEN BRANCH FROM BUS 341269 [2CASEY CO 69.000] TO BUS 342064 [2PEYTONS ST 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.86298 | 54.8576 | 2 | 13.7517
OPEN BRANCH FROM BUS 341767 [2LIBERTYKU T69.000] TO BUS 342064 [2PEYTONS ST 69.000] CKT 1
OPEN BRANCH FROM BUS 341764 [2LIBERTY KU 69.000] TO BUS 341767 [2LIBERTYKU T69.000] CKT 1
OPEN BRANCH FROM BUS 341761 [2LIBERTY J 69.000] TO BUS 341767 [2LIBERTYKU T69.000] CKT 1
EKPC_P1-2_LIB J-GARR69 | OPEN BRANCH FROM BUS 341761 [2LIBERTY J 69.000] TO BUS 341896 [2MT OLIVE J 69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.27708 | 15.7743 | 4 | 29.7961
OPEN BRANCH FROM BUS 341893 [2MT OLIVE 69.000] TO BUS 341896 [2MT OLIVE J 69.000] CKT 1
OPEN BRANCH FROM BUS 341617 [2HIGHLAND EK69.000] TO BUS 341896 [2MT OLIVE J 69.000] CKT 1
OPEN LINE FROM BUS 341209 [2BROUGTWN T 69.000] TO BUS 341210 [2BROUGHT TWN69.000] CKT 1
OPEN LINE FROM BUS 341209 [2BROUGTWN T 69.000] TO BUS 341617 [2HIGHLAND EK69.000] CKT 1
OPEN LINE FROM BUS 341209 [2BROUGTWN T 69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1
OPEN BRANCH FROM BUS 342364 [2TOMM GOOC 69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1
OPEN LINE FROM BUS 942410 [AE2-254 TAP 69.000] TO BUS 942411 [AE2-254 C O169.000] CKT 1
OPEN LINE FROM BUS 942410 [AE2-254 TAP 69.000] TO BUS 341515 [2GARRARD CO 69.000] CKT 1
OPEN LINE FROM BUS 942410 [AE2-254 TAP 69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1
EKPC_P1-2_LIB J-WIND 69 | OPEN BRANCH FROM BUS 341761 [2LIBERTY J 69.000] TO BUS 341342 [2CONTOWN T 69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.85246 | 57.4259 | 3 | 13.8159
OPEN BRANCH FROM BUS 342067 [2PHIL 69.000] TO BUS 341342 [2CONTOWN T 69.000] CKT 1
OPEN BRANCH FROM BUS 341350 [2CRESTON 69.000] TO BUS 342067 [2PHIL 69.000] CKT 1
OPEN BRANCH FROM BUS 342067 [2PHIL 69.000] TO BUS 342505 [2WINDSOR 69.000] CKT 1
EKPC_P1-2_PUL-WAL-SSET69 | OPEN BRANCH FROM BUS 341971 [2NORWOOD 69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.71369 | 46.4235 | 7 | 62.8347
OPEN BRANCH FROM BUS 341941 [2NELSN VAL T69.000] TO BUS 341971 [2NORWOOD 69.000] CKT 1
OPEN BRANCH FROM BUS 341941 [2NELSN VAL T69.000] TO BUS 341947 [2NELSON VAL 69.000] CKT 1
OPEN BRANCH FROM BUS 341419 [2E SOMERSE T69.000] TO BUS 341941 [2NELSN VAL T69.000] CKT 1
OPEN BRANCH FROM BUS 341419 [2E SOMERSE T69.000] TO BUS 341422 [2E SOMERSET 69.000] CKT 1
OPEN BRANCH FROM BUS 341419 [2E SOMERSE T69.000] TO BUS 341974 [2NORWOOD T 69.000] CKT 1
OPEN BRANCH FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 341974 [2NORWOOD T 69.000] CKT 1
OPEN BRANCH FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1
OPEN BRANCH FROM BUS 341974 [2NORWOOD T 69.000] TO BUS 342256 [2SHOPVILLE 69.000] CKT 1
OPEN BRANCH FROM BUS 341032 [2ASAHI M W T69.000] TO BUS 341379 [2DAHL ROAD 69.000] CKT 1
OPEN BRANCH FROM BUS 341379 [2DAHL ROAD 69.000] TO BUS 342256 [2SHOPVILLE 69.000] CKT 1
OPEN BRANCH FROM BUS 341029 [2ASAHI M W 69.000] TO BUS 341032 [2ASAHI M W T69.000] CKT 1
OPEN BRANCH FROM BUS 341032 [2ASAHI M W T69.000] TO BUS 342472 [2WALNUT GROV69.000] CKT 1
EKPC_P1-2_PUL - WOODSTOCK 69 | OPEN BRANCH FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.75992 | 52.8971 | 2 | 12.8925
OPEN BRANCH FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342193 [2S FLOYD 69.000] CKT 1
OPEN BRANCH FROM BUS 341470 [2FLOYD EK 69.000] TO BUS 341473 [2FLOYD-SFL T69.000] CKT 1
OPEN BRANCH FROM BUS 342511 [2WOODSTOCK 69.000] TO BUS 341470 [2FLOYD EK 69.000] CKT 1
EKPC_P1-2_THREELJ- WAL69 | OPEN BRANCH FROM BUS 341197 [2BRODHEAD 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.91697 | 60.9459 | 2 | 14.0445
OPEN BRANCH FROM BUS 341197 [2BRODHEAD 69.000] TO BUS 341818 [2MARETBURG T69.000] CKT 1
OPEN BRANCH FROM BUS 341815 [2MARETBURG 69.000] TO BUS 341818 [2MARETBURG T69.000] CKT 1
OPEN BRANCH FROM BUS 341818 [2MARETBURG T69.000] TO BUS 342472 [2WALNUT GROV69.000] CKT 1
EKPC_P1-2_TYN - N LON 69 | OPEN BRANCH FROM BUS 341017 [2ANNVILLE T 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14836 | 11.9455 | 3 | 14.8766
OPEN BRANCH FROM BUS 341014 [2ANNVILLE 69.000] TO BUS 341017 [2ANNVILLE T 69.000] CKT 1
OPEN BRANCH FROM BUS 341017 [2ANNVILLE T 69.000] TO BUS 341428 [2EBERLE T 69.000] CKT 1
OPEN BRANCH FROM BUS 341425 [2EBERLE 69.000] TO BUS 341428 [2EBERLE T 69.000] CKT 1
OPEN BRANCH FROM BUS 341428 [2EBERLE T 69.000] TO BUS 341809 [2MAPLESVIL T69.000] CKT 1
OPEN BRANCH FROM BUS 341809 [2MAPLESVIL T69.000] TO BUS 341812 [2MAPLESVILLE69.000] CKT 1
OPEN BRANCH FROM BUS 341809 [2MAPLESVIL T69.000] TO BUS 341929 [2N LONDON 69.000] CKT 1
EKPC_P1-2_FALL R-GARR69 | OPEN BRANCH FROM BUS 341464 [2FALL ROCK 69.000] TO BUS 341569 [2GREENBRIA T69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.3706 | 33.5612 | 1 | 7.3931
OPEN BRANCH FROM BUS 341569 [2GREENBRIA T69.000] TO BUS 341572 [2GREENBRIAR 69.000] CKT 1
OPEN BRANCH FROM BUS 341569 [2GREENBRIA T69.000] TO BUS 341806 [2MANCHESTER 69.000] CKT 1
OPEN BRANCH FROM BUS 341521 [2GARRARDKU T69.000] TO BUS 341806 [2MANCHESTER 69.000] CKT 1
OPEN BRANCH FROM BUS 341518 [2GARRARD KU 69.000] TO BUS 341521 [2GARRARDKU T69.000] CKT 1
EKPC_P1-2_FALL R-GOOS 69 | OPEN BRANCH FROM BUS 341113 [2BIG CREEK T69.000] TO BUS 341464 [2FALL ROCK 69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.75675 | 52.6094 | 3 | 11.8301
OPEN BRANCH FROM BUS 341113 [2BIG CREEK T69.000] TO BUS 342001 [2ONEIDA 69.000] CKT 1
OPEN BRANCH FROM BUS 341110 [2BIG CREEK 69.000] TO BUS 341113 [2BIG CREEK T69.000] CKT 1
EKPC_P1-2_BARR- FOX H 69 | OPEN BRANCH FROM BUS 341059 [2BARREN CO 69.000] TO BUS 341542 [2GOODNIGHT 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.45943 | 38.3113 | 1 | 9.2502
OPEN BRANCH FROM BUS 341542 [2GOODNIGHT 69.000] TO BUS 341548 [2GORIN PRK J69.000] CKT 1
OPEN BRANCH FROM BUS 341491 [2FOX HOLLOW 69.000] TO BUS 341548 [2GORIN PRK J69.000] CKT 1
EKPC_P1-2_FOX H-SUMMSH69 | OPEN BRANCH FROM BUS 341491 [2FOX HOLLOW 69.000] TO BUS 342049 [2PATTON RD J69.000] CKT 1 | TRUE | Met convergence tolerances | 4 | 0.87132 | 58.9937 | 2 | 14.1071
OPEN BRANCH FROM BUS 342319 [2SUMM SHAD J69.000] TO BUS 342334 [2TEMPLE HILL69.000] CKT 1
OPEN BRANCH FROM BUS 342049 [2PATTON RD J69.000] TO BUS 342319 [2SUMM SHAD J69.000] CKT 1
OPEN BRANCH FROM BUS 342319 [2SUMM SHAD J69.000] TO BUS 342322 [2SUMM SHADE 69.000] CKT 1
EKPC_P1-2_SUMMSH-SEWJ 69 | OPEN BRANCH FROM BUS 342322 [2SUMM SHADE 69.000] TO BUS 342436 [2W COLUMBI T69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.30517 | 20.176 | 5 | 28.9574
OPEN BRANCH FROM BUS 342436 [2W COLUMBI T69.000] TO BUS 342439 [2W COLUMBIA 69.000] CKT 1
OPEN BRANCH FROM BUS 341335 [2COLUMBIA 69.000] TO BUS 342436 [2W COLUMBI T69.000] CKT 1
OPEN BRANCH FROM BUS 341335 [2COLUMBIA 69.000] TO BUS 341370 [2COLUMB S KU69.000] CKT 1
OPEN BRANCH FROM BUS 341366 [2COLUMB KU 69.000] TO BUS 341370 [2COLUMB S KU69.000] CKT 1
OPEN BRANCH FROM BUS 341323 [2COBURG J 69.000] TO BUS 341335 [2COLUMBIA 69.000] CKT 1
OPEN BRANCH FROM BUS 341323 [2COBURG J 69.000] TO BUS 341512 [2GARLIN T 69.000] CKT 1
OPEN BRANCH FROM BUS 341509 [2GARLIN 69.000] TO BUS 341512 [2GARLIN T 69.000] CKT 1
OPEN BRANCH FROM BUS 341320 [2COBURG 69.000] TO BUS 341512 [2GARLIN T 69.000] CKT 1
OPEN BRANCH FROM BUS 341323 [2COBURG J 69.000] TO BUS 342235 [2SEWELTN J 69.000] CKT 1
EKPC_P1-2_SUMMSH-WAYNE69 | OPEN BRANCH FROM BUS 342283 [2SNOW T 69.000] TO BUS 342322 [2SUMM SHADE 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.37052 | 25.5149 | 4 | 34.544
OPEN BRANCH FROM BUS 342277 [2SNOW 69.000] TO BUS 342283 [2SNOW T 69.000] CKT 1
OPEN BRANCH FROM BUS 341005 [2ALBANY 69.000] TO BUS 342283 [2SNOW T 69.000] CKT 1
OPEN BRANCH FROM BUS 341005 [2ALBANY 69.000] TO BUS 342181 [2S ALBANY 69.000] CKT 1
OPEN BRANCH FROM BUS 341005 [2ALBANY 69.000] TO BUS 342397 [2UPCHURCH T 69.000] CKT 1
OPEN BRANCH FROM BUS 342394 [2UPCHURCH 69.000] TO BUS 342397 [2UPCHURCH T 69.000] CKT 1
OPEN BRANCH FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1
OPEN BRANCH FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1
EKPC_P1-2_WAYNE-ZULA 69 | OPEN BRANCH FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342535 [2ZULA T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.40375 | 35.448 | 1 | 8.451
OPEN BRANCH FROM BUS 342529 [2ZULA 69.000] TO BUS 342535 [2ZULA T 69.000] CKT 1
EKPC_P1-2_SEWJ - RUSS 69 | OPEN BRANCH FROM BUS 342166 [2RUSS SPEK T69.000] TO BUS 342235 [2SEWELTN J 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.15751 | 11.9453 | 2 | 17.4494
OPEN BRANCH FROM BUS 342166 [2RUSS SPEK T69.000] TO BUS 342172 [2RUSS SPR EK69.000] CKT 1
OPEN BRANCH FROM BUS 342166 [2RUSS SPEK T69.000] TO BUS 342169 [2RUSS SPKU T69.000] CKT 1
OPEN BRANCH FROM BUS 342169 [2RUSS SPKU T69.000] TO BUS 342175 [2RUSS SPR KU69.000] CKT 1
OPEN BRANCH FROM BUS 342169 [2RUSS SPKU T69.000] TO BUS 342178 [2RUSSEL CO 69.000] CKT 1
EKPC_P1-2_SEWJ - WIND 69 | OPEN BRANCH FROM BUS 342235 [2SEWELTN J 69.000] TO BUS 342481 [2WEBB CR R T69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.15322 | 12.3039 | 2 | 15.6933
OPEN BRANCH FROM BUS 342481 [2WEBB CR R T69.000] TO BUS 342484 [2WEBB CR RDS69.000] CKT 1
OPEN BRANCH FROM BUS 342217 [2SALEM EK T 69.000] TO BUS 342481 [2WEBB CR R T69.000] CKT 1
OPEN BRANCH FROM BUS 342214 [2SALEM EK 69.000] TO BUS 342217 [2SALEM EK T 69.000] CKT 1
OPEN BRANCH FROM BUS 342217 [2SALEM EK T 69.000] TO BUS 342505 [2WINDSOR 69.000] CKT 1
EKPC_P1-2_RUSS-KU SSET69 | OPEN BRANCH FROM BUS 342178 [2RUSSEL CO 69.000] TO BUS 342232 [2SEWELLTON 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.35025 | 21.424 | 4 | 33.3515
OPEN BRANCH FROM BUS 324787 [2UNION UNDWR69.000] TO BUS 342232 [2SEWELLTON 69.000] CKT 1
OPEN BRANCH FROM BUS 324787 [2UNION UNDWR69.000] TO BUS 324990 [2WAITSBORO 69.000] CKT 1
OPEN BRANCH FROM BUS 324969 [2SMRST 615KU69.000] TO BUS 324990 [2WAITSBORO 69.000] CKT 1
OPEN BRANCH FROM BUS 324737 [2SOMERSET SO69.000] TO BUS 324969 [2SMRST 615KU69.000] CKT 1
OPEN BRANCH FROM BUS 324737 [2SOMERSET SO69.000] TO BUS 342287 [2SOMERSET KU69.000] CKT 1
EKPC_P1-2_WIND - SSET 69 | OPEN BRANCH FROM BUS 341938 [2NANCY 69.000] TO BUS 342505 [2WINDSOR 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.26018 | 18.8042 | 4 | 24.781
OPEN BRANCH FROM BUS 341938 [2NANCY 69.000] TO BUS 342526 [2ZOLLICOF T 69.000] CKT 1
OPEN BRANCH FROM BUS 342523 [2ZOLLICOF 69.000] TO BUS 342526 [2ZOLLICOF T 69.000] CKT 1
OPEN BRANCH FROM BUS 342469 [2W SOMERSET 69.000] TO BUS 342526 [2ZOLLICOF T 69.000] CKT 1
OPEN BRANCH FROM BUS 341983 [2OAK HILL T 69.000] TO BUS 342469 [2W SOMERSET 69.000] CKT 1
OPEN BRANCH FROM BUS 341977 [2OAK HILL 69.000] TO BUS 341983 [2OAK HILL T 69.000] CKT 1
OPEN BRANCH FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 341983 [2OAK HILL T 69.000] CKT 1
OPEN BRANCH FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1
EKPC_P1-2_SSET-KU ELI 69 | OPEN BRANCH FROM BUS 324531 [2FERGUSON SO69.000] TO BUS 342287 [2SOMERSET KU69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.51823 | 23.281 | 1 | 5.58
OPEN BRANCH FROM BUS 324514 [2ELIHU 69.000] TO BUS 324531 [2FERGUSON SO69.000] CKT 1
EKPC_P1-2_COOP-DENNY 69 | OPEN BRANCH FROM BUS 341344 [2COOPER 69.000] TO BUS 341347 [2COOPER DIST69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.82508 | 56.3223 | 1 | 13.1724
OPEN BRANCH FROM BUS 341206 [2BRONSTON T 69.000] TO BUS 341347 [2COOPER DIST69.000] CKT 1
OPEN BRANCH FROM BUS 341203 [2BRONSTON 69.000] TO BUS 341206 [2BRONSTON T 69.000] CKT 1
OPEN BRANCH FROM BUS 341206 [2BRONSTON T 69.000] TO BUS 341392 [2DENNY 69.000] CKT 1
EKPC_P1-2_LAUR-KU FAR69 | OPEN BRANCH FROM BUS 341722 [2KEAVY 2 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.31762 | 22.1294 | 4 | 29.125
OPEN BRANCH FROM BUS 341716 [2KEAVY 69.000] TO BUS 341722 [2KEAVY 2 T 69.000] CKT 1
OPEN BRANCH FROM BUS 341722 [2KEAVY 2 T 69.000] TO BUS 342187 [2S CORBIN 69.000] CKT 1
OPEN BRANCH FROM BUS 341038 [2BACON CRK T69.000] TO BUS 342187 [2S CORBIN 69.000] CKT 1
OPEN BRANCH FROM BUS 341035 [2BACON CRK 69.000] TO BUS 341038 [2BACON CRK T69.000] CKT 1
OPEN BRANCH FROM BUS 341038 [2BACON CRK T69.000] TO BUS 341755 [2LIBER CH T 69.000] CKT 1
OPEN BRANCH FROM BUS 341755 [2LIBER CH T 69.000] TO BUS 341758 [2LIBERT CHUR69.000] CKT 1
OPEN BRANCH FROM BUS 324527 [2FARLEY KU 69.000] TO BUS 341755 [2LIBER CH T 69.000] CKT 1
EKPC_P1-2_LAUR-KU SWTH69 | OPEN BRANCH FROM BUS 324576 [2HOPEWELL 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 9.0948 | 1 | 12.82
OPEN BRANCH FROM BUS 324576 [2HOPEWELL 69.000] TO BUS 324748 [2SWEET HOLLO69.000] CKT 1
EKPC_P1-2_WAYNE-DENNY69 | OPEN BRANCH FROM BUS 342268 [2SLAT 69.000] TO BUS 342478 [2WAYNE CO 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.45391 | 30.7961 | 5 | 42.1992
OPEN BRANCH FROM BUS 341887 [2MONTICELLO 69.000] TO BUS 342268 [2SLAT 69.000] CKT 1
OPEN BRANCH FROM BUS 341641 [2HOMESTEAD S69.000] TO BUS 341887 [2MONTICELLO 69.000] CKT 1
OPEN BRANCH FROM BUS 341503 [2GAP OF RG T69.000] TO BUS 341887 [2MONTICELLO 69.000] CKT 1
OPEN BRANCH FROM BUS 341503 [2GAP OF RG T69.000] TO BUS 341506 [2GAP OF RIDG69.000] CKT 1
OPEN BRANCH FROM BUS 341503 [2GAP OF RG T69.000] TO BUS 341578 [2GREGORY R T69.000] CKT 1
OPEN BRANCH FROM BUS 341578 [2GREGORY R T69.000] TO BUS 341581 [2GREGORY RD 69.000] CKT 1
OPEN BRANCH FROM BUS 341392 [2DENNY 69.000] TO BUS 341578 [2GREGORY R T69.000] CKT 1
EKPC_P1-2_DENNY-MCCRRY69 | OPEN BRANCH FROM BUS 341845 [2MCCREARY CO69.000] TO BUS 342490 [2WHITLEY CTY69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.17104 | 12.9059 | 3 | 18.0054
OPEN BRANCH FROM BUS 342490 [2WHITLEY CTY69.000] TO BUS 342493 [2WHITLY C KU69.000] CKT 1
OPEN BRANCH FROM BUS 342490 [2WHITLEY CTY69.000] TO BUS 342499 [2WIBORG T 69.000] CKT 1
OPEN BRANCH FROM BUS 342496 [2WIBORG 69.000] TO BUS 342499 [2WIBORG T 69.000] CKT 1
OPEN BRANCH FROM BUS 341392 [2DENNY 69.000] TO BUS 342499 [2WIBORG T 69.000] CKT 1
EKPC_P1-2_MCCRY-KUWOFF69 | OPEN BRANCH FROM BUS 341845 [2MCCREARY CO69.000] TO BUS 342139 [2REVELO KU T69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.22228 | 16.259 | 5 | 22.5795
OPEN BRANCH FROM BUS 342136 [2REVELO KU 69.000] TO BUS 342139 [2REVELO KU T69.000] CKT 1
OPEN BRANCH FROM BUS 342076 [2PINE KNOT 69.000] TO BUS 342139 [2REVELO KU T69.000] CKT 1
OPEN BRANCH FROM BUS 341416 [2E PINE KNOT69.000] TO BUS 342076 [2PINE KNOT 69.000] CKT 1
OPEN BRANCH FROM BUS 341686 [2JELLICO C T69.000] TO BUS 342076 [2PINE KNOT 69.000] CKT 1
OPEN BRANCH FROM BUS 341686 [2JELLICO C T69.000] TO BUS 341689 [2JELLICO CRK69.000] CKT 1
OPEN BRANCH FROM BUS 341539 [2GOLDBUG 69.000] TO BUS 341686 [2JELLICO C T69.000] CKT 1
OPEN BRANCH FROM BUS 324784 [2WOFFORD 69.000] TO BUS 341539 [2GOLDBUG 69.000] CKT 1
EKPC_P1-2_CLYV-SHL-FRK69 | OPEN BRANCH FROM BUS 324474 [2CLAY VILG T69.000] TO BUS 341317 [2CLAY VILLAG69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.21516 | 14.1194 | 1 | 21.53
OPEN BRANCH FROM BUS 324474 [2CLAY VILG T69.000] TO BUS 324725 [2SHELBYVIL E69.000] CKT 1
OPEN BRANCH FROM BUS 324725 [2SHELBYVIL E69.000] TO BUS 324727 [2SHELBYVILLE69.000] CKT 1
OPEN BRANCH FROM BUS 324474 [2CLAY VILG T69.000] TO BUS 324765 [2W FRANKFORT69.000] CKT 1
EKPC_P1-2_BULL- PLENTG69 | OPEN BRANCH FROM BUS 341215 [2BULLITT CO 69.000] TO BUS 341281 [2CEDAR GR 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.37097 | 25.531 | 2 | 34.729
OPEN BRANCH FROM BUS 341281 [2CEDAR GR 69.000] TO BUS 342082 [2PLEAS GRV 69.000] CKT 1
EKPC_P1-2_AEPMORG- MOR69 | OPEN BRANCH FROM BUS 243740 [05MOREHE 69.000] TO BUS 246973 [05MORGCO 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.3045
EKPC_P1-2_AEPMORG-INDX69 | OPEN BRANCH FROM BUS 243733 [05INDEX 69.000] TO BUS 246973 [05MORGCO 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.063
EKPC_P1-2_HODG-KU BARD69 | OPEN BRANCH FROM BUS 324660 [2NEW HAVEN 69.000] TO BUS 341632 [2HODGENVILLE69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.24674 | 15.7795 | 4 | 24.36
OPEN BRANCH FROM BUS 324660 [2NEW HAVEN 69.000] TO BUS 324801 [2BARTON 69.000] CKT 1
OPEN BRANCH FROM BUS 324424 [2BARDTWN CTY69.000] TO BUS 324801 [2BARTON 69.000] CKT 1
OPEN BRANCH FROM BUS 324424 [2BARDTWN CTY69.000] TO BUS 326537 [2WOODLAWN KU69.000] CKT 1
OPEN BRANCH FROM BUS 324426 [2BARDSTOWN 69.000] TO BUS 326537 [2WOODLAWN KU69.000] CKT Z1
EKPC_P1-2_HODG-KU ETWN69 | OPEN BRANCH FROM BUS 324575 [2HODGENV KU 69.000] TO BUS 341632 [2HODGENVILLE69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.23059 | 14.9055 | 2 | 23.5
OPEN BRANCH FROM BUS 324521 [2ETOWN 4 69.000] TO BUS 324575 [2HODGENV KU 69.000] CKT 1
OPEN BRANCH FROM BUS 324519 [2ETOWN KU 69.000] TO BUS 324521 [2ETOWN 4 69.000] CKT 1
EKPC_P1-2_N SPR-KU LEB69 | OPEN BRANCH FROM BUS 324736 [2SPRINGFL KU69.000] TO BUS 341935 [2N SPRINGFLD69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 9.0842 | 1 | 13.78
OPEN BRANCH FROM BUS 324606 [2LEBANON 69.000] TO BUS 324736 [2SPRINGFL KU69.000] CKT 1
EKPC_P1-2_BAR-BON-FHOL69 | OPEN BRANCH FROM BUS 341059 [2BARREN CO 69.000] TO BUS 341275 [2CAVE CITY J69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.38609 | 26.7232 | 5 | 36.2684
OPEN BRANCH FROM BUS 341275 [2CAVE CITY J69.000] TO BUS 342241 [2SEYMOUR T 69.000] CKT 1
OPEN BRANCH FROM BUS 342238 [2SEYMOUR 69.000] TO BUS 342241 [2SEYMOUR T 69.000] CKT 1
OPEN BRANCH FROM BUS 341272 [2CAVE CITY 69.000] TO BUS 341275 [2CAVE CITY J69.000] CKT 1
OPEN BRANCH FROM BUS 341149 [2BON AYR 69.000] TO BUS 341272 [2CAVE CITY 69.000] CKT 1
OPEN BRANCH FROM BUS 341080 [2BECKTON 69.000] TO BUS 341149 [2BON AYR 69.000] CKT 1
OPEN BRANCH FROM BUS 341080 [2BECKTON 69.000] TO BUS 342445 [2W GLASGOW T69.000] CKT 1
OPEN BRANCH FROM BUS 342442 [2W GLASGOW 69.000] TO BUS 342445 [2W GLASGOW T69.000] CKT 1
OPEN BRANCH FROM BUS 341530 [2GLASGO-CLEV69.000] TO BUS 342445 [2W GLASGOW T69.000] CKT 1
OPEN BRANCH FROM BUS 341530 [2GLASGO-CLEV69.000] TO BUS 342043 [2PARKWAY 2 T69.000] CKT 1
OPEN BRANCH FROM BUS 341491 [2FOX HOLLOW 69.000] TO BUS 342043 [2PARKWAY 2 T69.000] CKT 1
EKPC_P1-2_FHOL-PARK69 | OPEN BRANCH FROM BUS 341491 [2FOX HOLLOW 69.000] TO BUS 342037 [2PARKWAY 1 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.74804 | 52.8306 | 2 | 12.671
OPEN BRANCH FROM BUS 342037 [2PARKWAY 1 69.000] TO BUS 342040 [2PARKWAY 2 69.000] CKT 1
EKPC_P1-2_GREEN-KUTAY69 | OPEN BRANCH FROM BUS 324554 [2GRENSBRG KU69.000] TO BUS 341563 [2GREEN CO 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.35007 | 22.1975 | 4 | 34.1832
OPEN BRANCH FROM BUS 324554 [2GRENSBRG KU69.000] TO BUS 324830 [2CAMPBELV EK69.000] CKT 1
OPEN BRANCH FROM BUS 324557 [2GR RVR PLAZ69.000] TO BUS 324830 [2CAMPBELV EK69.000] CKT 1
OPEN BRANCH FROM BUS 324557 [2GR RVR PLAZ69.000] TO BUS 324829 [2CAMPBELVIL169.000] CKT 1
OPEN BRANCH FROM BUS 324641 [2MILE LAN TP69.000] TO BUS 324829 [2CAMPBELVIL169.000] CKT 1
OPEN BRANCH FROM BUS 324641 [2MILE LAN TP69.000] TO BUS 326970 [2MILE LAN EK69.000] CKT 1
OPEN BRANCH FROM BUS 324641 [2MILE LAN TP69.000] TO BUS 324751 [2TAYLOR CO 69.000] CKT 1
EKPC_P1-2_NLON-KU NLON69 | OPEN BRANCH FROM BUS 324662 [2N LONDON KU69.000] TO BUS 341929 [2N LONDON 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.32231 | 31.0914 | 1 | 6.944
OPEN BRANCH FROM BUS 341410 [2E BERNSTADT69.000] TO BUS 341929 [2N LONDON 69.000] CKT 1
EKPC_P1-2_DK HEB-HEB 138 | OPEN BRANCH FROM BUS 250152 [08HEBRNG 138.00] TO BUS 342595 [4HEBRON 138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.15484 | 12.2222 | 1 | 16.4491
OPEN BRANCH FROM BUS 341605 [2HEBRON 69.000] TO BUS 342595 [4HEBRON 138.00] CKT 1
EKPC_P1-2_BOONE-BUFF138 | OPEN BRANCH FROM BUS 250054 [08LONGBR 138.00] TO BUS 342559 [4BOONE CO 138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.37707 | 23.9559 | 2 | 33.288
OPEN BRANCH FROM BUS 250054 [08LONGBR 138.00] TO BUS 250077 [08MTZION 138.00] CKT 1
OPEN BRANCH FROM BUS 249991 [08BUFTN1 138.00] TO BUS 250077 [08MTZION 138.00] CKT 1
EKPC_P1-2_BOONE-STANP138 | OPEN BRANCH FROM BUS 342559 [4BOONE CO 138.00] TO BUS 342646 [4RICHWOOD T 138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.65754 | 47.6159 | 1 | 11.3427
OPEN BRANCH FROM BUS 342643 [4RICHWOOD 138.00] TO BUS 342646 [4RICHWOOD T 138.00] CKT 1
OPEN BRANCH FROM BUS 342646 [4RICHWOOD T 138.00] TO BUS 342667 [4STANLEY PRK138.00] CKT 1
EKPC_P1-2_BOONE-GALL138 | OPEN BRANCH FROM BUS 342559 [4BOONE CO 138.00] TO BUS 342673 [4STERLNG T 138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.237 | 29.3048 | 1 | 6.9793
OPEN BRANCH FROM BUS 342670 [4STERLING 138.00] TO BUS 342673 [4STERLNG T 138.00] CKT 1
OPEN BRANCH FROM BUS 342586 [4GALLATIN CO138.00] TO BUS 342673 [4STERLNG T 138.00] CKT 1
EKPC_P1-2_BOONE-REN 138 | OPEN BRANCH FROM BUS 342550 [4BAVARIAN LF138.00] TO BUS 342559 [4BOONE CO 138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.18455 | 23.4183 | 1 | 5.0733
OPEN BRANCH FROM BUS 342550 [4BAVARIAN LF138.00] TO BUS 342640 [4RENAKER 138.00] CKT 1
EKPC_P1-2_OWEN 138/69 | OPEN BRANCH FROM BUS 342008 [4OWEN CO 138.00] TO BUS 342007 [2OWEN CO 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14237 | 7.2721
OPEN BRANCH FROM BUS 324290 [4OWEN CO TAP138.00] TO BUS 342008 [4OWEN CO 138.00] CKT 1
OPEN BRANCH FROM BUS 324253 [4GHENT 138.00] TO BUS 324290 [4OWEN CO TAP138.00] CKT 1
OPEN BRANCH FROM BUS 324290 [4OWEN CO TAP138.00] TO BUS 324305 [4SCOTT CO 138.00] CKT 1
EKPC_P1-2_SPUR-KUKEN 138 | OPEN BRANCH FROM BUS 342661 [4SPUR-KENT-R138.00] TO BUS 342664 [4SPURLOCK 138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.55608 | 23.3168
OPEN BRANCH FROM BUS 324267 [4KENTON 138.00] TO BUS 342661 [4SPUR-KENT-R138.00] CKT 1
EKPC_P1-2_SPUR-PLUM 138 | OPEN BRANCH FROM BUS 342622 [4MAYSVIL I T138.00] TO BUS 342664 [4SPURLOCK 138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.20913 | 27.6737 | 1 | 8.0269
OPEN BRANCH FROM BUS 342622 [4MAYSVIL I T138.00] TO BUS 342625 [4MAYSVIL IND138.00] CKT 1
OPEN BRANCH FROM BUS 342622 [4MAYSVIL I T138.00] TO BUS 342634 [4PLUMVILLE 138.00] CKT 1
EKPC_P1-2_SPUR-GODD 138 | OPEN BRANCH FROM BUS 342583 [4FLEMINGSBRG138.00] TO BUS 342664 [4SPURLOCK 138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.3842 | 35.8952 | 1 | 10.4135
OPEN BRANCH FROM BUS 342583 [4FLEMINGSBRG138.00] TO BUS 342589 [4GODDARD 138.00] CKT 1
EKPC_P1-2_GODD - ROW138 | OPEN BRANCH FROM BUS 342589 [4GODDARD 138.00] TO BUS 342571 [4CRANSTON 138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.22729 | 17.6105 | 1 | 25.3272
OPEN BRANCH FROM BUS 342571 [4CRANSTON 138.00] TO BUS 342649 [4ROWAN CO 138.00] CKT 1
EKPC_P1-2_AVN-PAR-REN138 | OPEN BRANCH FROM BUS 342541 [4AVON 138.00] TO BUS 342631 [4PARIS T 138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.26499 | 18.7145 | 1 | 3.3691
OPEN BRANCH FROM BUS 324328 [4PARIS 138.00] TO BUS 342631 [4PARIS T 138.00] CKT 1
OPEN BRANCH FROM BUS 342604 [4JACKSNVIL T138.00] TO BUS 342631 [4PARIS T 138.00] CKT 1
OPEN BRANCH FROM BUS 342601 [4JACKSNVIL 138.00] TO BUS 342604 [4JACKSNVIL T138.00] CKT 1
OPEN BRANCH FROM BUS 342604 [4JACKSNVIL T138.00] TO BUS 342640 [4RENAKER 138.00] CKT 1
EKPC_P1-2_AVN-BBN-DLE138 | OPEN BRANCH FROM BUS 342541 [4AVON 138.00] TO BUS 342556 [4BECKNERV T 138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.51221 | 21.8176 | 1 | 1.593
OPEN BRANCH FROM BUS 342553 [4BECKNERV 138.00] TO BUS 342556 [4BECKNERV T 138.00] CKT 1
OPEN BRANCH FROM BUS 342556 [4BECKNERV T 138.00] TO BUS 342565 [4BOONESBOR T138.00] CKT 1
OPEN BRANCH FROM BUS 342565 [4BOONESBOR T138.00] TO BUS 325925 [4BOONSBORO N138.00] CKT 1
OPEN BRANCH FROM BUS 324449 [2BOONSBORO N69.000] TO BUS 325925 [4BOONSBORO N138.00] CKT 1
OPEN BRANCH FROM BUS 342565 [4BOONESBOR T138.00] TO BUS 342574 [4DALE 138.00] CKT 1
EKPC_P1-2_AVON-FAY 138 | OPEN BRANCH FROM BUS 342541 [4AVON 138.00] TO BUS 342580 [4FAYETTE 138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14177 | 2.1263
OPEN BRANCH FROM BUS 341467 [2FAYETTE 69.000] TO BUS 342580 [4FAYETTE 138.00] CKT 1
EKPC_P1-2_AVON-LOUD 138 | OPEN BRANCH FROM BUS 342541 [4AVON 138.00] TO BUS 342544 [4AVON-R 138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.62246 | 24.8057
OPEN BRANCH FROM BUS 324275 [4LOUDON AVE 138.00] TO BUS 342544 [4AVON-R 138.00] CKT 1
EKPC_P1-2_DALE-JKSMIT138 | OPEN LINE FROM BUS 342596 [4HUNT 138.00] TO BUS 342607 [4JK SMITH 138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.47985 | 20.634
OPEN LINE FROM BUS 342596 [4HUNT 138.00] TO BUS 341665 [2HUNT 69.000] CKT 1
OPEN LINE FROM BUS 342596 [4HUNT 138.00] TO BUS 342574 [4DALE 138.00] CKT 1
EKPC_P1-2_DALE-FAWK 138 | OPEN BRANCH FROM BUS 342574 [4DALE 138.00] TO BUS 342676 [4THREE FK T 138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14177 | 16.0813 | 1 | 3.0944
OPEN BRANCH FROM BUS 342676 [4THREE FK T 138.00] TO BUS 342679 [4THREE FORKS138.00] CKT 1
OPEN BRANCH FROM BUS 342577 [4FAWKES EK 138.00] TO BUS 342676 [4THREE FK T 138.00] CKT 1
EKPC_P1-2_FAW-W BER 138 | OPEN BRANCH FROM BUS 342577 [4FAWKES EK 138.00] TO BUS 342691 [4W BEREA 138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.48657 | 20.3418
OPEN BRANCH FROM BUS 342430 [2W BEREA 69.000] TO BUS 342691 [4W BEREA 138.00] CKT 1
EKPC_P1-2_JKS 345/138 1 | OPEN BRANCH FROM BUS 342610 [4JK SMITH 21138.00] TO BUS 342832 [7JK SMITH 345.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.16587 | 2.2418
OPEN BRANCH FROM BUS 342607 [4JK SMITH 138.00] TO BUS 342610 [4JK SMITH 21138.00] CKT 1
EKPC_P1-2_JKS 345/138 2 | OPEN BRANCH FROM BUS 342613 [4JK SMITH 22138.00] TO BUS 342832 [7JK SMITH 345.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.16079 | 2.209
OPEN BRANCH FROM BUS 342607 [4JK SMITH 138.00] TO BUS 342613 [4JK SMITH 22138.00] CKT 1
EKPC_P1-2_JKSMTH-REBA138 | OPEN BRANCH FROM BUS 342607 [4JK SMITH 138.00] TO BUS 342688 [4UNION CTY T138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 16.3172 | 1 | 6.4748
OPEN BRANCH FROM BUS 342685 [4UNION CITY 138.00] TO BUS 342688 [4UNION CTY T138.00] CKT 1
OPEN BRANCH FROM BUS 324276 [4LAKE REBA T138.00] TO BUS 342688 [4UNION CTY T138.00] CKT 1
EKPC_P1-2_ROW-SKAG138 | OPEN BRANCH FROM BUS 342649 [4ROWAN CO 138.00] TO BUS 342658 [4SKAGGS 138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.20743 | 6.9041
OPEN BRANCH FROM BUS 342265 [2SKAGGS 69.000] TO BUS 342658 [4SKAGGS 138.00] CKT 1
EKPC_P1-2_CHARD-HRDBG138 | OPEN BRANCH FROM BUS 324047 [4BLACKBRANCH138.00] TO BUS 342568 [4CENT HARDIN138.00] CKT 1 | TRUE | Met convergence tolerances | 4 | 0.78112 | 40.3449 | 2 | 13.22
OPEN LINE FROM BUS 325055 [4RHUDES TP 138.00] TO BUS 325116 [4RHUDES CR 138.00] CKT 1
OPEN LINE FROM BUS 325055 [4RHUDES TP 138.00] TO BUS 324047 [4BLACKBRANCH138.00] CKT 1
OPEN LINE FROM BUS 325055 [4RHUDES TP 138.00] TO BUS 324260 [4HARDINSBURG138.00] CKT 1
EKPC_P1-2_COP-RUS-WLF161 | OPEN BRANCH FROM BUS 342793 [5RUSSEL CO 161.00] TO BUS 342796 [5RUSSEL CO J161.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.1502 | 13.255 | 3 | 21.6984
OPEN BRANCH FROM BUS 342796 [5RUSSEL CO J161.00] TO BUS 360448 [5WOLF CRK HP161.00] CKT 1
OPEN BRANCH FROM BUS 342751 [5JAMESTOWN T161.00] TO BUS 342796 [5RUSSEL CO J161.00] CKT 1
OPEN BRANCH FROM BUS 342748 [5JAMESTOWN 161.00] TO BUS 342751 [5JAMESTOWN T161.00] CKT 1
OPEN BRANCH FROM BUS 342745 [5JABEZ T 161.00] TO BUS 342751 [5JAMESTOWN T161.00] CKT 1
OPEN BRANCH FROM BUS 342742 [5JABEZ 161.00] TO BUS 342745 [5JABEZ T 161.00] CKT 1
OPEN BRANCH FROM BUS 342745 [5JABEZ T 161.00] TO BUS 342799 [5S OAKHILL 161.00] CKT 1
OPEN BRANCH FROM BUS 342715 [5COOPER1 161.00] TO BUS 342799 [5S OAKHILL 161.00] CKT 1
EKPC_P1-2_COOP-DEN161 | OPEN BRANCH FROM BUS 342718 [5COOPER2 161.00] TO BUS 342727 [5DENNY 161.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 1.6086
OPEN BRANCH FROM BUS 341392 [2DENNY 69.000] TO BUS 342727 [5DENNY 161.00] CKT 1
EKPC_P1-2_COP-LIBJ-PU161 | OPEN BRANCH FROM BUS 342715 [5COOPER1 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.71014 | 28.3305
OPEN BRANCH FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1
OPEN BRANCH FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1
OPEN BRANCH FROM BUS 342760 [5LIBERTY J 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1
EKPC_P1-2_LIB-CAS-GAS-MAR161 | OPEN BRANCH FROM BUS 341269 [2CASEY CO 69.000] TO BUS 342703 [5CASEY CO 161.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.5147 | 21.2078
OPEN BRANCH FROM BUS 342703 [5CASEY CO 161.00] TO BUS 342000 [5GAS 161.00] CKT 1
OPEN BRANCH FROM BUS 342703 [5CASEY CO 161.00] TO BUS 342769 [5MARION CO 161.00] CKT 1
EKPC_P1-2_MCCR-WAYNE161 | OPEN BRANCH FROM BUS 342778 [5MCCREARY CO161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.57463 | 22.9666
OPEN BRANCH FROM BUS 360448 [5WOLF CRK HP161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1
OPEN BRANCH FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1
OPEN BRANCH FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1
EKPC_P1-2_LAUR-PIT-TY161 | OPEN BRANCH FROM BUS 342754 [5LAUREL CO 161.00] TO BUS 342781 [5PITTSBURG 161.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.39924 | 18.3552
OPEN BRANCH FROM BUS 324688 [2PITTSBRG KU69.000] TO BUS 342781 [5PITTSBURG 161.00] CKT 1
OPEN BRANCH FROM BUS 342781 [5PITTSBURG 161.00] TO BUS 342820 [5TYNER 161.00] CKT 1
EKPC_P1-2_TYN-DELV161 | OPEN BRANCH FROM BUS 342736 [5GREEN HAL T161.00] TO BUS 342820 [5TYNER 161.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.22031 | 15.9025 | 1 | 2.6482
OPEN BRANCH FROM BUS 342736 [5GREEN HAL T161.00] TO BUS 342739 [5GREEN HALL 161.00] CKT 1
OPEN BRANCH FROM BUS 324138 [5DELVINTA 161.00] TO BUS 342736 [5GREEN HAL T161.00] CKT 1
EKPC_P1-2_TYN-FALLR161 | OPEN BRANCH FROM BUS 342730 [5FALL ROCK 161.00] TO BUS 342820 [5TYNER 161.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.29684 | 8.3893
OPEN BRANCH FROM BUS 341464 [2FALL ROCK 69.000] TO BUS 342730 [5FALL ROCK 161.00] CKT 1
EKPC_P1-2_GRE-TAY-MAR161 | OPEN BRANCH FROM BUS 342733 [5GREEN CO 161.00] TO BUS 342817 [5TAYLOR CO J161.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.51347 | 34.5018 | 3 | 49.718
OPEN BRANCH FROM BUS 342817 [5TAYLOR CO J161.00] TO BUS 325921 [5TAYLOR CO 161.00] CKT 1
OPEN BRANCH FROM BUS 342805 [5SALOMA T 161.00] TO BUS 342817 [5TAYLOR CO J161.00] CKT 1
OPEN BRANCH FROM BUS 342802 [5SALOMA 161.00] TO BUS 342805 [5SALOMA T 161.00] CKT 1
OPEN BRANCH FROM BUS 342775 [5MARION IP T161.00] TO BUS 342805 [5SALOMA T 161.00] CKT 1
OPEN LINE FROM BUS 342797 [5S MARION IT161.00] TO BUS 342798 [5S MARION IP161.00] CKT 1
OPEN LINE FROM BUS 342797 [5S MARION IT161.00] TO BUS 342772 [5MARION IP 161.00] CKT 1
OPEN LINE FROM BUS 342797 [5S MARION IT161.00] TO BUS 342775 [5MARION IP T161.00] CKT 1
OPEN BRANCH FROM BUS 342769 [5MARION CO 161.00] TO BUS 342775 [5MARION IP T161.00] CKT 1
EKPC_P1-2_BARR-SUMSH161 | OPEN BRANCH FROM BUS 342694 [5BARREN CO 161.00] TO BUS 342814 [5SUMM SHADE 161.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14177 | 1.9117
OPEN BRANCH FROM BUS 341059 [2BARREN CO 69.000] TO BUS 342694 [5BARREN CO 161.00] CKT 1
EKPC_P1-2_BULL-SUMSH161 | OPEN LINE FROM BUS 361788 [5SUM SHAD TP161.00] TO BUS 326998 [5BULLITT TAP161.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 3.8387
OPEN LINE FROM BUS 361788 [5SUM SHAD TP161.00] TO BUS 342814 [5SUMM SHADE 161.00] CKT 1
OPEN LINE FROM BUS 361788 [5SUM SHAD TP161.00] TO BUS 360334 [5SUMMER SHAD161.00] CKT 1
EKPC_P1-2_BULL-BLUE L161 | OPEN LINE FROM BUS 326975 [5CEDAR GRV 161.00] TO BUS 342700 [5BULLITT CO 161.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14975 | 13.5496 | 1 | 23.384
OPEN LINE FROM BUS 326975 [5CEDAR GRV 161.00] TO BUS 324134 [5BLUE LICK 161.00] CKT 1
EKPC_P1-2_BULL-SHEL161 | OPEN LINE FROM BUS 342819 [5TAYLORSV T 161.00] TO BUS 342818 [5TAYLORSVILL161.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.29993 | 21.7668 | 3 | 30.572
OPEN LINE FROM BUS 342819 [5TAYLORSV T 161.00] TO BUS 342700 [5BULLITT CO 161.00] CKT 1
OPEN LINE FROM BUS 342819 [5TAYLORSV T 161.00] TO BUS 342766 [5LITTLE MT T161.00] CKT 1
OPEN BRANCH FROM BUS 342763 [5LITTLE MT 161.00] TO BUS 342766 [5LITTLE MT T161.00] CKT 1
OPEN BRANCH FROM BUS 342724 [5DARWIN TH T161.00] TO BUS 342766 [5LITTLE MT T161.00] CKT 1
OPEN BRANCH FROM BUS 342721 [5DARWIN TH 161.00] TO BUS 342724 [5DARWIN TH T161.00] CKT 1
OPEN BRANCH FROM BUS 342724 [5DARWIN TH T161.00] TO BUS 342808 [5SHELBY CO 161.00] CKT 1
OPEN BRANCH FROM BUS 342247 [2SHELBY CO 69.000] TO BUS 342808 [5SHELBY CO 161.00] CKT 1
EKPC_P1-2_POW-BTV-DEL161 | OPEN LINE FROM BUS 342780 [5MILL CRK T 161.00] TO BUS 342784 [5POWELL CO 161.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.19623 | 16.5162 | 1 | 3.1325
OPEN LINE FROM BUS 342780 [5MILL CRK T 161.00] TO BUS 342697 [5BEATTYV J 161.00] CKT 1
OPEN LINE FROM BUS 342780 [5MILL CRK T 161.00] TO BUS 342779 [5MILLER CRK 161.00] CKT 1
OPEN BRANCH FROM BUS 324430 [2BEATTYVI KU69.000] TO BUS 342697 [5BEATTYV J 161.00] CKT 1
OPEN BRANCH FROM BUS 324138 [5DELVINTA 161.00] TO BUS 342697 [5BEATTYV J 161.00] CKT 1
TVA SS-GLASGOW & LAFAYETTE 161 | OPEN LINE FROM BUS 360334 [5SUMMER SHAD161.00] TO BUS 360607 [5S GLASGOW 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.79785 | 30.9487
OPEN LINE FROM BUS 360334 [5SUMMER SHAD161.00] TO BUS 360354 [5LAFAYETT TN161.00] CKT 1
EK-TVA SSHD & SSHD 161 XFMR | OPEN LINE FROM BUS 342814 [5SUMM SHADE 161.00] TO BUS 360334 [5SUMMER SHAD161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.41216 | 18.7036
OPEN BRANCH FROM BUS 342814 [5SUMM SHADE 161.00] TO BUS 342322 [2SUMM SHADE 69.000] CKT 1
EKPC_P1-2_AVON-NCLA345 | OPEN BRANCH FROM BUS 342829 [7AVON 345.00] TO BUS 342835 [7N CLARK 345.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.83893 | 33.831
OPEN BRANCH FROM BUS 342541 [4AVON 138.00] TO BUS 342829 [7AVON 345.00] CKT 1
SINGLE OPN LIN 714 324010-324114(1) | OPEN LINE FROM BUS 324010 [7TRIMBL REAC345.00] TO BUS 324114 [7TRIMBLE CO 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.44962 | 26.5474
SINGLE OPN LIN 715 324021-324103(Z1) | OPEN LINE FROM BUS 324021 [7BLUEGRASS12345.00] TO BUS 324103 [7BUCKNER 345.00] CKT Z1 | TRUE | Met convergence tolerances | 3 | 0.44571 | 7.9171 | 2 | 2.0666
SINGLE OPN LIN 716 324022-324103(Z1) | OPEN LINE FROM BUS 324022 [7BLUEGRASS 3345.00] TO BUS 324103 [7BUCKNER 345.00] CKT Z1 | TRUE | Met convergence tolerances | 2 | 0.38675 | 21.5601 | 1 | 0.6333
SINGLE OPN LIN 717 324029-324030(1) | OPEN LINE FROM BUS 324029 [7TRIMBLE CTA345.00] TO BUS 324030 [7TRIMBLE CTB345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.3291
SINGLE OPN LIN 718 324029-324114(1) | OPEN LINE FROM BUS 324029 [7TRIMBLE CTA345.00] TO BUS 324114 [7TRIMBLE CO 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.9679
SINGLE OPN LIN 719 324030-324114(1) | OPEN LINE FROM BUS 324030 [7TRIMBLE CTB345.00] TO BUS 324114 [7TRIMBLE CO 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.0094
SINGLE OPN LIN 720 324047-325055(1) | OPEN LINE FROM BUS 324047 [4BLACKBRANCH138.00] TO BUS 325055 [4RHUDES TP 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.53363 | 23.4587
SINGLE OPN LIN 721 324048-324437(1) | OPEN LINE FROM BUS 324048 [2PARKWY MINE69.000] TO BUS 324437 [2BEVIER KU 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.5692
SINGLE OPN LIN 722 324048-324584(1) | OPEN LINE FROM BUS 324048 [2PARKWY MINE69.000] TO BUS 324584 [2INDIAN HILL69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.4065
SINGLE OPN LIN 723 324049-324572(1) | OPEN LINE FROM BUS 324049 [2OXFORD COAL69.000] TO BUS 324572 [2HILLSIDE 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.8746
SINGLE OPN LIN 724 324049-324745(1) | OPEN LINE FROM BUS 324049 [2OXFORD COAL69.000] TO BUS 324745 [2STRINGTOWN 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.872
SINGLE OPN LIN 725 324050-324362(1) | OPEN LINE FROM BUS 324050 [2JONESVILLE 69.000] TO BUS 324362 [2RIO 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.17352 | 15.3437 | 1 | 1.59
SINGLE OPN LIN 726 324050-324447(1) | OPEN LINE FROM BUS 324050 [2JONESVILLE 69.000] TO BUS 324447 [2BONNIE KU 69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.25027 | 26.5933 | 2 | 6.1073
SINGLE OPN LIN 727 324051-324173(1) | OPEN LINE FROM BUS 324051 [4MATANZAS 138.00] TO BUS 324173 [5MATANZAS 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.4759
SINGLE OPN LIN 728 324051-324173(2) | OPEN LINE FROM BUS 324051 [4MATANZAS 138.00] TO BUS 324173 [5MATANZAS 161.00] CKT 2 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.4725
SINGLE OPN LIN 729 324051-324255(1) | OPEN LINE FROM BUS 324051 [4MATANZAS 138.00] TO BUS 324255 [4GREEN RIVER138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.3801
SINGLE OPN LIN 730 324051-324291(1) | OPEN LINE FROM BUS 324051 [4MATANZAS 138.00] TO BUS 324291 [4OHIO COUNTY138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.9289
SINGLE OPN LIN 731 324058-324059(1) | OPEN LINE FROM BUS 324058 [2BEAVER DAM 69.000] TO BUS 324059 [2BEAVER DM N69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.96217 | 42.8937 | 2 | 10.67
SINGLE OPN LIN 732 324058-324667(1) | OPEN LINE FROM BUS 324058 [2BEAVER DAM 69.000] TO BUS 324667 [2OHIO COUNTY69.000] CKT 1 | TRUE | Met convergence tolerances | 3 | 0.14971 | 10.7168 | 3 | 16.76
SINGLE OPN LIN 733 324059-324080(1) | OPEN LINE FROM BUS 324059 [2BEAVER DM N69.000] TO BUS 324080 [2HARTFORD 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.55836 | 26.1036 | 1 | 6.07
SINGLE OPN LIN 734 324061-324079(1) | OPEN LINE FROM BUS 324061 [2BORG-WARNER69.000] TO BUS 324079 [2HANSON 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.91282 | 40.6318 | 1 | 9.89
SINGLE OPN LIN 735 324061-324873(1) | OPEN LINE FROM BUS 324061 [2BORG-WARNER69.000] TO BUS 324873 [2HANSON JCT 69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.17152 | 11.8969 | 2 | 18.39
SINGLE OPN LIN 736 324065-324843(1) | OPEN LINE FROM BUS 324065 [2DAWSON 764 69.000] TO BUS 324843 [2DAWSON IND 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.33767 | 18.3151 | 1 | 3.55
SINGLE OPN LIN 737 324067-324512(1) | OPEN LINE FROM BUS 324067 [2EDDYV PRIS 69.000] TO BUS 324512 [2EDDYV PR TP69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.33541 | 18.2665 | 1 | 3.61
SINGLE OPN LIN 738 324068-324349(1) | OPEN LINE FROM BUS 324068 [2E CAMPBELVL69.000] TO BUS 324349 [2CAMPBELVIL269.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.32765 | 31.7591 | 1 | 7.2306
SINGLE OPN LIN 739 324069-324687(1) | OPEN LINE FROM BUS 324069 [2PAYNES ML 69.000] TO BUS 324687 [2PISGAH 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.44094 | 19.7439
SINGLE OPN LIN 740 324069-324763(1) | OPEN LINE FROM BUS 324069 [2PAYNES ML 69.000] TO BUS 324763 [2VERSAILLES 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.4878
SINGLE OPN LIN 741 324075-324702(1) | OPEN LINE FROM BUS 324075 [2GRAHAM 69.000] TO BUS 324702 [2RIVER QUEEN69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.34249 | 18.5326 | 1 | 3.7
SINGLE OPN LIN 742 324077-326594(1) | OPEN LINE FROM BUS 324077 [2GREENVILE W69.000] TO BUS 326594 [2GREENVL 12 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.19375 | 15.7228 | 1 | 1.98
SINGLE OPN LIN 743 324081-326587(1) | OPEN LINE FROM BUS 324081 [2MADSNV GE 69.000] TO BUS 326587 [2MADSNV W TP69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.51495 | 24.3171 | 1 | 5.41
SINGLE OPN LIN 744 324082-324197(1) | OPEN LINE FROM BUS 324082 [2PARIS 4 69.000] TO BUS 324197 [2DETROIT HAR69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 7.7513 | 1 | 10.92
SINGLE OPN LIN 745 324082-324476(1) | OPEN LINE FROM BUS 324082 [2PARIS 4 69.000] TO BUS 324476 [2CMC TAP 69.000] CKT 1 | TRUE | Met convergence tolerances | 5 | 0.31443 | 19.1556 | 5 | 29.88
SINGLE OPN LIN 746 324082-325061(1) | OPEN LINE FROM BUS 324082 [2PARIS 4 69.000] TO BUS 325061 [2CMC 69.000] CKT 1 | TRUE | Met convergence tolerances | 3 | 0.17406 | 11.8299 | 3 | 17.88
SINGLE OPN LIN 747 324083-326587(1) | OPEN LINE FROM BUS 324083 [2MADSNV W 69.000] TO BUS 326587 [2MADSNV W TP69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.1596 | 11.2872 | 1 | 17.4
SINGLE OPN LIN 748 324085-324629(1) | OPEN LINE FROM BUS 324085 [2MARION 4 69.000] TO BUS 324629 [2MARION KU 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.31193 | 17.7223 | 1 | 3.35
SINGLE OPN LIN 749 324086-324096(1) | OPEN LINE FROM BUS 324086 [2MORGANF IND69.000] TO BUS 324096 [2PEA WSH TAP69.000] CKT 1 | TRUE | Met convergence tolerances | 3 | 0.14287 | 2.1799 | 1 | 0.2
SINGLE OPN LIN 750 324086-324671(1) | OPEN LINE FROM BUS 324086 [2MORGANF IND69.000] TO BUS 324671 [2OVERLAD S T69.000] CKT 1 | TRUE | Met convergence tolerances | 4 | 0.45512 | 22.2435 | 2 | 4.87
SINGLE OPN LIN 751 324087-324913(1) | OPEN LINE FROM BUS 324087 [2MT VERN SO 69.000] TO BUS 324913 [2MT VERNON 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.1171
SINGLE OPN LIN 752 324087-324927(1) | OPEN LINE FROM BUS 324087 [2MT VERN SO 69.000] TO BUS 324927 [2PINE HILL T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.1168
SINGLE OPN LIN 753 324090-324095(1) | OPEN LINE FROM BUS 324090 [2OVERLAND NO69.000] TO BUS 324095 [2UNIONTOWN 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 1.5942
SINGLE OPN LIN 754 324091-324096(1) | OPEN LINE FROM BUS 324091 [2OVERLAND SO69.000] TO BUS 324096 [2PEA WSH TAP69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 1.3969
SINGLE OPN LIN 755 324092-324702(1) | OPEN LINE FROM BUS 324092 [2PEABODY RVR69.000] TO BUS 324702 [2RIVER QUEEN69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 1.4265
SINGLE OPN LIN 756 324093-324711(1) | OPEN LINE FROM BUS 324093 [2SPEN CHEMIC69.000] TO BUS 324711 [2SPEN CHEM T69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.65374 | 25.5317 | 1 | 5.83
SINGLE OPN LIN 757 324094-324562(1) | OPEN LINE FROM BUS 324094 [2TURTLE CK T69.000] TO BUS 324562 [2HARLAN KU 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.488
SINGLE OPN LIN 758 324094-324761(1) | OPEN LINE FROM BUS 324094 [2TURTLE CK T69.000] TO BUS 324761 [2VERDA 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.3855
SINGLE OPN LIN 759 324094-325045(1) | OPEN LINE FROM BUS 324094 [2TURTLE CK T69.000] TO BUS 325045 [2TURTLE CRK 69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.2576 | 16.6479 | 2 | 2.7
SINGLE OPN LIN 760 324095-326572(1) | OPEN LINE FROM BUS 324095 [2UNIONTOWN 69.000] TO BUS 326572 [2RIVRVW COAL69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.23843 | 16.3564 | 1 | 2.32
SINGLE OPN LIN 761 324096-324097(1) | OPEN LINE FROM BUS 324096 [2PEA WSH TAP69.000] TO BUS 324097 [2PEAB WASH 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 2.4461 | 1 | 0.2
SINGLE OPN LIN 762 324098-324779(1) | OPEN LINE FROM BUS 324098 [2WEST VACO 69.000] TO BUS 324779 [2WICKLIFFE 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.32963 | 20.5296 | 1 | 34.42
SINGLE OPN LIN 763 324100-324102(1) | OPEN LINE FROM BUS 324100 [7ALCALDE 345.00] TO BUS 324102 [7BROWN NORTH345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.41709 | 16.2617
SINGLE OPN LIN 764 324100-324112(1) | OPEN LINE FROM BUS 324100 [7ALCALDE 345.00] TO BUS 324112 [7PINEVILLE 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.9574
SINGLE OPN LIN 765 324100-324130(1) | OPEN LINE FROM BUS 324100 [7ALCALDE 345.00] TO BUS 324130 [5ALCALDE 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.64974 | 26.4719
SINGLE OPN LIN 766 324101-324107(1) | OPEN LINE FROM BUS 324101 [7BLUE LICK 345.00] TO BUS 324107 [7MIDDLETOWN 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.4633
SINGLE OPN LIN 767 324101-324108(1) | OPEN LINE FROM BUS 324101 [7BLUE LICK 345.00] TO BUS 324108 [7MILL CREEK 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.47682 | 21.1064
SINGLE OPN LIN 768 324101-324134(1) | OPEN LINE FROM BUS 324101 [7BLUE LICK 345.00] TO BUS 324134 [5BLUE LICK 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 7.0684
SINGLE OPN LIN 769 324101-324212(1) | OPEN LINE FROM BUS 324101 [7BLUE LICK 345.00] TO BUS 324212 [4BLUE LICK 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.69655 | 27.9881
SINGLE OPN LIN 770 324102-324106(1) | OPEN LINE FROM BUS 324102 [7BROWN NORTH345.00] TO BUS 324106 [7HARDIN CO 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.77077 | 33.0183
SINGLE OPN LIN 771 324102-324116(1) | OPEN LINE FROM BUS 324102 [7BROWN NORTH345.00] TO BUS 324116 [7W LEXINGTON345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.5145
SINGLE OPN LIN 772 324102-325074(1) | OPEN LINE FROM BUS 324102 [7BROWN NORTH345.00] TO BUS 325074 [7W GARRARDKU345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.19851 | 2.7511
SINGLE OPN LIN 773 324102-325956(1) | OPEN LINE FROM BUS 324102 [7BROWN NORTH345.00] TO BUS 325956 [4BROWN N 2 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.1258
SINGLE OPN LIN 774 324102-325957(2) | OPEN LINE FROM BUS 324102 [7BROWN NORTH345.00] TO BUS 325957 [4BROWN N 1 138.00] CKT 2 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.2251
SINGLE OPN LIN 775 324103-324107(1) | OPEN LINE FROM BUS 324103 [7BUCKNER 345.00] TO BUS 324107 [7MIDDLETOWN 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.16036 | 9.0976
SINGLE OPN LIN 776 324103-324114(1) | OPEN LINE FROM BUS 324103 [7BUCKNER 345.00] TO BUS 324114 [7TRIMBLE CO 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.7996
SINGLE OPN LIN 777 324104-324106(1) | OPEN LINE FROM BUS 324104 [7DAVIESS 345.00] TO BUS 324106 [7HARDIN CO 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.1589 | 9.0545
SINGLE OPN LIN 778 324105-324115(1) | OPEN LINE FROM BUS 324105 [7GHENT 345.00] TO BUS 324115 [7W FRANKFORT345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.1811 | 9.1522
SINGLE OPN LIN 779 324105-324116(1) | OPEN LINE FROM BUS 324105 [7GHENT 345.00] TO BUS 324116 [7W LEXINGTON345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.22044 | 12.1081
SINGLE OPN LIN 780 324105-324253(1) | OPEN LINE FROM BUS 324105 [7GHENT 345.00] TO BUS 324253 [4GHENT 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.5643
SINGLE OPN LIN 781 324105-324253(2) | OPEN LINE FROM BUS 324105 [7GHENT 345.00] TO BUS 324253 [4GHENT 138.00] CKT 2 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.6623
SINGLE OPN LIN 782 324105-326536(1) | OPEN LINE FROM BUS 324105 [7GHENT 345.00] TO BUS 326536 [7GALLATIN 345.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.95735 | 50.4901 | 1 | 362.97
SINGLE OPN LIN 783 324106-324261(1) | OPEN LINE FROM BUS 324106 [7HARDIN CO 345.00] TO BUS 324261 [4HARDIN CO 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.8511
SINGLE OPN LIN 784 324106-324261(2) | OPEN LINE FROM BUS 324106 [7HARDIN CO 345.00] TO BUS 324261 [4HARDIN CO 138.00] CKT 2 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.8012
SINGLE OPN LIN 785 324106-325073(1) | OPEN LINE FROM BUS 324106 [7HARDIN CO 345.00] TO BUS 325073 [7REDMON RD 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.42623 | 18.2337
SINGLE OPN LIN 786 324107-324108(1) | OPEN LINE FROM BUS 324107 [7MIDDLETOWN 345.00] TO BUS 324108 [7MILL CREEK 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.5589
SINGLE OPN LIN 787 324107-324114(1) | OPEN LINE FROM BUS 324107 [7MIDDLETOWN 345.00] TO BUS 324114 [7TRIMBLE CO 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.67511 | 27.9084
SINGLE OPN LIN 788 324107-324281(3) | OPEN LINE FROM BUS 324107 [7MIDDLETOWN 345.00] TO BUS 324281 [4MIDDLETOWN 138.00] CKT 3 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.9624
SINGLE OPN LIN 789 324107-324281(4) | OPEN LINE FROM BUS 324107 [7MIDDLETOWN 345.00] TO BUS 324281 [4MIDDLETOWN 138.00] CKT 4 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.9026
SINGLE OPN LIN 790 324107-324281(5) | OPEN LINE FROM BUS 324107 [7MIDDLETOWN 345.00] TO BUS 324281 [4MIDDLETOWN 138.00] CKT 5 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.9401
SINGLE OPN LIN 791 324107-324281(7) | OPEN LINE FROM BUS 324107 [7MIDDLETOWN 345.00] TO BUS 324281 [4MIDDLETOWN 138.00] CKT 7 | TRUE | Met convergence tolerances | 0 | 0.14287 | 4.8102
SINGLE OPN LIN 792 324108-325073(1) | OPEN LINE FROM BUS 324108 [7MILL CREEK 345.00] TO BUS 325073 [7REDMON RD 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.61387 | 26.8766
SINGLE OPN LIN 793 324108-326001(1) | OPEN LINE FROM BUS 324108 [7MILL CREEK 345.00] TO BUS 326001 [7CANE RUN TP345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.4995
SINGLE OPN LIN 794 324109-324565(1) | OPEN LINE FROM BUS 324109 [7NAS 345.00] TO BUS 324565 [7NAS TAP 345.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.15918 | 13.2895 | 1 | 106.67
SINGLE OPN LIN 795 324110-324289(1) | OPEN LINE FROM BUS 324110 [7NORTHSIDE 345.00] TO BUS 324289 [4NORTHSIDE 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.60426 | 25.858
SINGLE OPN LIN 796 324110-326569(1) | OPEN LINE FROM BUS 324110 [7NORTHSIDE 345.00] TO BUS 326569 [7KENZIG ROAD345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.62537 | 26.501
SINGLE OPN LIN 797 324111-324294(1) | OPEN LINE FROM BUS 324111 [7PADDYS WEST345.00] TO BUS 324294 [4PADDYS WEST138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.52779 | 24.1827
SINGLE OPN LIN 798 324111-326001(1) | OPEN LINE FROM BUS 324111 [7PADDYS WEST345.00] TO BUS 326001 [7CANE RUN TP345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.5774
SINGLE OPN LIN 799 324111-326569(1) | OPEN LINE FROM BUS 324111 [7PADDYS WEST345.00] TO BUS 326569 [7KENZIG ROAD345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.5593
SINGLE OPN LIN 800 324112-324167(1) | OPEN LINE FROM BUS 324112 [7PINEVILLE 345.00] TO BUS 324167 [5PINEVILLE 2161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.55933 | 20.8314
SINGLE OPN LIN 801 324112-325074(1) | OPEN LINE FROM BUS 324112 [7PINEVILLE 345.00] TO BUS 325074 [7W GARRARDKU345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14967 | 3.207
SINGLE OPN LIN 802 324114-324314(5) | OPEN LINE FROM BUS 324114 [7TRIMBLE CO 345.00] TO BUS 324314 [4TRIMBLE CO 138.00] CKT 5 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.524
SINGLE OPN LIN 803 324114-324314(6) | OPEN LINE FROM BUS 324114 [7TRIMBLE CO 345.00] TO BUS 324314 [4TRIMBLE CO 138.00] CKT 6 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.322
SINGLE OPN LIN 804 324115-324319(1) | OPEN LINE FROM BUS 324115 [7W FRANKFORT345.00] TO BUS 324319 [4W FRANKFORT138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.17809 | 9.0416
SINGLE OPN LIN 805 324116-324320(1) | OPEN LINE FROM BUS 324116 [7W LEXINGTON345.00] TO BUS 324320 [4W LEXINGTON138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.17754 | 9.2366
SINGLE OPN LIN 806 324124-326564(1) | OPEN LINE FROM BUS 324124 [2CENTRTOWN S69.000] TO BUS 326564 [2LEW BREC 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.20734 | 15.6092 | 1 | 0.95
SINGLE OPN LIN 807 324130-324141(1) | OPEN LINE FROM BUS 324130 [5ALCALDE 161.00] TO BUS 324141 [5ELIHU 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.61361 | 24.89
SINGLE OPN LIN 808 324130-324143(1) | OPEN LINE FROM BUS 324130 [5ALCALDE 161.00] TO BUS 324143 [5FARLEY 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.3561
SINGLE OPN LIN 809 324131-324139(1) | OPEN LINE FROM BUS 324131 [5ARNOLD 161.00] TO BUS 324139 [5DORCHESTER 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 3.2989
SINGLE OPN LIN 810 324131-324146(1) | OPEN LINE FROM BUS 324131 [5ARNOLD 161.00] TO BUS 324146 [5HARLAN WYE 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.5856
SINGLE OPN LIN 811 324131-324148(1) | OPEN LINE FROM BUS 324131 [5ARNOLD 161.00] TO BUS 324148 [5WOOTON TAP 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.3546
SINGLE OPN LIN 812 324131-324416(1) | OPEN LINE FROM BUS 324131 [5ARNOLD 161.00] TO BUS 324416 [2ARNOLD 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.7088
SINGLE OPN LIN 813 324132-324133(1) | OPEN LINE FROM BUS 324132 [5ARTEMUS TAP161.00] TO BUS 324133 [5ARTEMUS 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.3327
SINGLE OPN LIN 814 324132-324143(1) | OPEN LINE FROM BUS 324132 [5ARTEMUS TAP161.00] TO BUS 324143 [5FARLEY 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.6895
SINGLE OPN LIN 815 324132-324156(1) | OPEN LINE FROM BUS 324132 [5ARTEMUS TAP161.00] TO BUS 324156 [5PINEVILE SW161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.45256 | 19.9717
SINGLE OPN LIN 816 324133-324417(1) | OPEN LINE FROM BUS 324133 [5ARTEMUS 161.00] TO BUS 324417 [2ARTEMUS 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.2314
SINGLE OPN LIN 817 324134-326975(1) | OPEN LINE FROM BUS 324134 [5BLUE LICK 161.00] TO BUS 326975 [5CEDAR GRV 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 7.1741
SINGLE OPN LIN 818 324135-324136(1) | OPEN LINE FROM BUS 324135 [5CORYDON TAP161.00] TO BUS 324136 [5CORYDON 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.7197
SINGLE OPN LIN 819 324135-324144(1) | OPEN LINE FROM BUS 324135 [5CORYDON TAP161.00] TO BUS 324144 [5GREEN RIVER161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6891
SINGLE OPN LIN 820 324135-324153(1) | OPEN LINE FROM BUS 324135 [5CORYDON TAP161.00] TO BUS 324153 [5MORGANFIELD161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.22759 | 15.9905
SINGLE OPN LIN 821 324136-324484(1) | OPEN LINE FROM BUS 324136 [5CORYDON 161.00] TO BUS 324484 [2CORYDON 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.25441 | 4.6248
SINGLE OPN LIN 822 324137-324151(1) | OPEN LINE FROM BUS 324137 [5CRITTENDEN 161.00] TO BUS 324151 [5LIVNGSTN CO161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.2875
SINGLE OPN LIN 823 324137-324153(1) | OPEN LINE FROM BUS 324137 [5CRITTENDEN 161.00] TO BUS 324153 [5MORGANFIELD161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.35217 | 19.7748
SINGLE OPN LIN 824 324137-324486(1) | OPEN LINE FROM BUS 324137 [5CRITTENDEN 161.00] TO BUS 324486 [2CRITTENDEN 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.0005
SINGLE OPN LIN 825 324138-324148(1) | OPEN LINE FROM BUS 324138 [5DELVINTA 161.00] TO BUS 324148 [5WOOTON TAP 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.4333
SINGLE OPN LIN 826 324138-324165(1) | OPEN LINE FROM BUS 324138 [5DELVINTA 161.00] TO BUS 324165 [5W IRVINE T 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.8797
SINGLE OPN LIN 827 324139-324149(1) | OPEN LINE FROM BUS 324139 [5DORCHESTER 161.00] TO BUS 324149 [5IMBODEN 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.3131
SINGLE OPN LIN 828 324139-324503(1) | OPEN LINE FROM BUS 324139 [5DORCHESTER 161.00] TO BUS 324503 [2DORCHESTER 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.7458
SINGLE OPN LIN 829 324139-324503(2) | OPEN LINE FROM BUS 324139 [5DORCHESTER 161.00] TO BUS 324503 [2DORCHESTER 69.000] CKT 2 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6426
SINGLE OPN LIN 830 324140-324160(1) | OPEN LINE FROM BUS 324140 [5EARLINGTN N161.00] TO BUS 324160 [5RIVER QN T 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.5108
SINGLE OPN LIN 831 324140-324164(1) | OPEN LINE FROM BUS 324140 [5EARLINGTN N161.00] TO BUS 324164 [5WALKER 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.5967
SINGLE OPN LIN 832 324140-324506(1) | OPEN LINE FROM BUS 324140 [5EARLINGTN N161.00] TO BUS 324506 [2EARLINGTN N69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.3058
SINGLE OPN LIN 833 324140-325079(1) | OPEN LINE FROM BUS 324140 [5EARLINGTN N161.00] TO BUS 325079 [5N PRINCETON161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.3223
SINGLE OPN LIN 834 324141-324514(1) | OPEN LINE FROM BUS 324141 [5ELIHU 161.00] TO BUS 324514 [2ELIHU 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.5933
SINGLE OPN LIN 835 324141-324514(2) | OPEN LINE FROM BUS 324141 [5ELIHU 161.00] TO BUS 324514 [2ELIHU 69.000] CKT 2 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6096
SINGLE OPN LIN 836 324143-324527(1) | OPEN LINE FROM BUS 324143 [5FARLEY 161.00] TO BUS 324527 [2FARLEY KU 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.67691 | 26.4674
SINGLE OPN LIN 837 324144-324160(1) | OPEN LINE FROM BUS 324144 [5GREEN RIVER161.00] TO BUS 324160 [5RIVER QN T 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.37041 | 17.4044
SINGLE OPN LIN 838 324144-324255(1) | OPEN LINE FROM BUS 324144 [5GREEN RIVER161.00] TO BUS 324255 [4GREEN RIVER138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.5552
SINGLE OPN LIN 839 324144-324255(2) | OPEN LINE FROM BUS 324144 [5GREEN RIVER161.00] TO BUS 324255 [4GREEN RIVER138.00] CKT 2 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.6285
SINGLE OPN LIN 840 324144-324255(3) | OPEN LINE FROM BUS 324144 [5GREEN RIVER161.00] TO BUS 324255 [4GREEN RIVER138.00] CKT 3 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.4572
SINGLE OPN LIN 841 324145-324171(1) | OPEN LINE FROM BUS 324145 [5GRAHAMVILLE161.00] TO BUS 324171 [5GRAHMVILE 1161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.24349 | 18.3836
SINGLE OPN LIN 842 324145-324172(1) | OPEN LINE FROM BUS 324145 [5GRAHAMVILLE161.00] TO BUS 324172 [5GRAHMVILE 2161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.5839
SINGLE OPN LIN 843 324145-324553(1) | OPEN LINE FROM BUS 324145 [5GRAHAMVILLE161.00] TO BUS 324553 [2GRAHAMVILLE69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.3755
SINGLE OPN LIN 844 324145-325069(1) | OPEN LINE FROM BUS 324145 [5GRAHAMVILLE161.00] TO BUS 325069 [5SONG SP TP 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.46917 | 20.2799
SINGLE OPN LIN 845 324145-325077(1) | OPEN LINE FROM BUS 324145 [5GRAHAMVILLE161.00] TO BUS 325077 [5COLEMAN TAP161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.5758
SINGLE OPN LIN 846 324146-324147(1) | OPEN LINE FROM BUS 324146 [5HARLAN WYE 161.00] TO BUS 324147 [5HOWARDS BR 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.8047
SINGLE OPN LIN 847 324146-324155(1) | OPEN LINE FROM BUS 324146 [5HARLAN WYE 161.00] TO BUS 324155 [5PINEVILLE 1161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.8234
SINGLE OPN LIN 848 324146-324157(1) | OPEN LINE FROM BUS 324146 [5HARLAN WYE 161.00] TO BUS 324157 [5POCKET N 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 6.6211
SINGLE OPN LIN 849 324146-324564(1) | OPEN LINE FROM BUS 324146 [5HARLAN WYE 161.00] TO BUS 324564 [2HARLAN WYE 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.211
SINGLE OPN LIN 850 324147-324155(1) | OPEN LINE FROM BUS 324147 [5HOWARDS BR 161.00] TO BUS 324155 [5PINEVILLE 1161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.8413
SINGLE OPN LIN 851 324149-324157(1) | OPEN LINE FROM BUS 324149 [5IMBODEN 161.00] TO BUS 324157 [5POCKET N 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 5.0119
SINGLE OPN LIN 852 324149-324583(1) | OPEN LINE FROM BUS 324149 [5IMBODEN 161.00] TO BUS 324583 [2IMBODEN 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 3.7916
SINGLE OPN LIN 853 324150-324154(1) | OPEN LINE FROM BUS 324150 [5LEBANON JCT161.00] TO BUS 324154 [5PADDYS RUN 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.8584
SINGLE OPN LIN 854 324151-324161(1) | OPEN LINE FROM BUS 324151 [5LIVNGSTN CO161.00] TO BUS 324161 [5S PADUCAH 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.23065 | 16.7528
SINGLE OPN LIN 855 324151-325028(1) | OPEN LINE FROM BUS 324151 [5LIVNGSTN CO161.00] TO BUS 325028 [5ASHWD SL TP161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.30179 | 19.3846
SINGLE OPN LIN 856 324152-324165(1) | OPEN LINE FROM BUS 324152 [5LAKE REBA T161.00] TO BUS 324165 [5W IRVINE T 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 4.7903
SINGLE OPN LIN 857 324152-324276(1) | OPEN LINE FROM BUS 324152 [5LAKE REBA T161.00] TO BUS 324276 [4LAKE REBA T138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 4.5718
SINGLE OPN LIN 858 324153-324645(1) | OPEN LINE FROM BUS 324153 [5MORGANFIELD161.00] TO BUS 324645 [2MORGANFIELD69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.45266 | 19.8568
SINGLE OPN LIN 859 324155-324156(1) | OPEN LINE FROM BUS 324155 [5PINEVILLE 1161.00] TO BUS 324156 [5PINEVILE SW161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.5115
SINGLE OPN LIN 860 324155-324167(Z1) | OPEN LINE FROM BUS 324155 [5PINEVILLE 1161.00] TO BUS 324167 [5PINEVILLE 2161.00] CKT Z1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 5.5567
SINGLE OPN LIN 861 324155-324686(1) | OPEN LINE FROM BUS 324155 [5PINEVILLE 1161.00] TO BUS 324686 [2PINEVILLE 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 3.3915
SINGLE OPN LIN 862 324157-324158(1) | OPEN LINE FROM BUS 324157 [5POCKET N 161.00] TO BUS 324158 [5POCKET 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.7643
SINGLE OPN LIN 863 324158-324689(1) | OPEN LINE FROM BUS 324158 [5POCKET 161.00] TO BUS 324689 [2POCKET 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.8713
SINGLE OPN LIN 864 324159-324160(1) | OPEN LINE FROM BUS 324159 [5RIVER QUEEN161.00] TO BUS 324160 [5RIVER QN T 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.8408
SINGLE OPN LIN 865 324159-324702(1) | OPEN LINE FROM BUS 324159 [5RIVER QUEEN161.00] TO BUS 324702 [2RIVER QUEEN69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.8728
SINGLE OPN LIN 866 324161-324712(1) | OPEN LINE FROM BUS 324161 [5S PADUCAH 161.00] TO BUS 324712 [2SO PADUCAH 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.5565
SINGLE OPN LIN 867 324161-325078(1) | OPEN LINE FROM BUS 324161 [5S PADUCAH 161.00] TO BUS 325078 [5PADUCAH PRI161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.21224 | 17.3195
SINGLE OPN LIN 868 324163-324165(1) | OPEN LINE FROM BUS 324163 [5WEST IRVINE161.00] TO BUS 324165 [5W IRVINE T 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.5516
SINGLE OPN LIN 869 324163-324767(1) | OPEN LINE FROM BUS 324163 [5WEST IRVINE161.00] TO BUS 324767 [2WEST IRVINE69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6606
SINGLE OPN LIN 870 324164-324769(1) | OPEN LINE FROM BUS 324164 [5WALKER 161.00] TO BUS 324769 [2WALKER KU 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.8449
SINGLE OPN LIN 871 324166-324779(1) | OPEN LINE FROM BUS 324166 [5WICKLIFFE 161.00] TO BUS 324779 [2WICKLIFFE 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.46706 | 19.9468
SINGLE OPN LIN 872 324166-325069(1) | OPEN LINE FROM BUS 324166 [5WICKLIFFE 161.00] TO BUS 325069 [5SONG SP TP 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.46973 | 20.0364
SINGLE OPN LIN 873 324167-324686(2) | OPEN LINE FROM BUS 324167 [5PINEVILLE 2161.00] TO BUS 324686 [2PINEVILLE 69.000] CKT 2 | TRUE | Met convergence tolerances | 0 | 0.14177 | 4.4097
SINGLE OPN LIN 874 324191-324603(1) | OPEN LINE FROM BUS 324191 [2LEBANON E T69.000] TO BUS 324603 [2LEBANON CIT69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.41192 | 18.6583
SINGLE OPN LIN 875 324191-324606(1) | OPEN LINE FROM BUS 324191 [2LEBANON E T69.000] TO BUS 324606 [2LEBANON 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.41214 | 18.7072
SINGLE OPN LIN 876 324192-324240(1) | OPEN LINE FROM BUS 324192 [4DAYTON-WALT138.00] TO BUS 324240 [4DAY-WALT TP138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.32069 | 17.7891 | 1 | 3.5
SINGLE OPN LIN 877 324193-324251(1) | OPEN LINE FROM BUS 324193 [4FLEMINGB KU138.00] TO BUS 324251 [4FLEMNB KU T138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.44381 | 22.0275 | 1 | 4.82
SINGLE OPN LIN 878 324195-324722(1) | OPEN LINE FROM BUS 324195 [2AUGUSTA 69.000] TO BUS 324722 [2SHARON KU 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.7101 | 30.2431 | 1 | 7
SINGLE OPN LIN 879 324196-324224(1) | OPEN LINE FROM BUS 324196 [2BOONESB PRK69.000] TO BUS 324224 [2RED HOUSE 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.40012 | 20.2531 | 1 | 4.24
SINGLE OPN LIN 880 324196-324449(1) | OPEN LINE FROM BUS 324196 [2BOONESB PRK69.000] TO BUS 324449 [2BOONSBORO N69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.67479 | 31.3678 | 2 | 7.33
SINGLE OPN LIN 881 324198-324878(1) | OPEN LINE FROM BUS 324198 [2HUNT BOTTOM69.000] TO BUS 324878 [2HUNT BTM TP69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.20978 | 15.8171 | 1 | 2.19
SINGLE OPN LIN 882 324199-324252(1) | OPEN LINE FROM BUS 324199 [2OWENTON 69.000] TO BUS 324252 [2SCHOLLS 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.27602 | 16.8656 | 1 | 2.89
SINGLE OPN LIN 883 324200-324205(1) | OPEN LINE FROM BUS 324200 [4PLSUR RDG T138.00] TO BUS 324205 [4ASHBOTTOM 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.36364 | 17.6552
SINGLE OPN LIN 884 324200-324237(1) | OPEN LINE FROM BUS 324200 [4PLSUR RDG T138.00] TO BUS 324237 [4CANE RUN SW138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.7752
SINGLE OPN LIN 885 324200-324299(1) | OPEN LINE FROM BUS 324200 [4PLSUR RDG T138.00] TO BUS 324299 [4PLEASUR RDG138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.4038
SINGLE OPN LIN 886 324201-324305(1) | OPEN LINE FROM BUS 324201 [4ADAMS 138.00] TO BUS 324305 [4SCOTT CO 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.5264
SINGLE OPN LIN 887 324201-324313(1) | OPEN LINE FROM BUS 324201 [4ADAMS 138.00] TO BUS 324313 [4TOYOTA S 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.5955
SINGLE OPN LIN 888 324201-324315(1) | OPEN LINE FROM BUS 324201 [4ADAMS 138.00] TO BUS 324315 [4TYRONE 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.8048
SINGLE OPN LIN 889 324201-324335(1) | OPEN LINE FROM BUS 324201 [4ADAMS 138.00] TO BUS 324335 [4INNOVATION 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.1112
SINGLE OPN LIN 890 324201-324405(1) | OPEN LINE FROM BUS 324201 [4ADAMS 138.00] TO BUS 324405 [2ADAMS 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.38411 | 7.6856
SINGLE OPN LIN 891 324201-324405(2) | OPEN LINE FROM BUS 324201 [4ADAMS 138.00] TO BUS 324405 [2ADAMS 69.000] CKT 2 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.4762
SINGLE OPN LIN 892 324202-324241(1) | OPEN LINE FROM BUS 324202 [4ALGONQUIN 138.00] TO BUS 324241 [4DIXIE 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.1691
SINGLE OPN LIN 893 324202-324408(1) | OPEN LINE FROM BUS 324202 [4ALGONQUIN 138.00] TO BUS 324408 [2ALGONQUIN 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.3567
SINGLE OPN LIN 894 324203-324258(1) | OPEN LINE FROM BUS 324203 [4AMERICAN AV138.00] TO BUS 324258 [4HAEFLING 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.5837
SINGLE OPN LIN 895 324203-324301(1) | OPEN LINE FROM BUS 324203 [4AMERICAN AV138.00] TO BUS 324301 [4REYNOLDS 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.571
SINGLE OPN LIN 896 324203-324409(1) | OPEN LINE FROM BUS 324203 [4AMERICAN AV138.00] TO BUS 324409 [2AMERICAN AV69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.9199
SINGLE OPN LIN 897 324204-324205(1) | OPEN LINE FROM BUS 324204 [4APPLIANC PK138.00] TO BUS 324205 [4ASHBOTTOM 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.9235
SINGLE OPN LIN 898 324204-324243(1) | OPEN LINE FROM BUS 324204 [4APPLIANC PK138.00] TO BUS 324243 [4ETHEL 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.0364
SINGLE OPN LIN 899 324204-324281(1) | OPEN LINE FROM BUS 324204 [4APPLIANC PK138.00] TO BUS 324281 [4MIDDLETOWN 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.65
SINGLE OPN LIN 900 324205-324237(1) | OPEN LINE FROM BUS 324205 [4ASHBOTTOM 138.00] TO BUS 324237 [4CANE RUN SW138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.36732 | 17.6261
SINGLE OPN LIN 901 324205-324257(1) | OPEN LINE FROM BUS 324205 [4ASHBOTTOM 138.00] TO BUS 324257 [4GRADE LANE 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.38146 | 17.617
SINGLE OPN LIN 902 324205-324279(1) | OPEN LINE FROM BUS 324205 [4ASHBOTTOM 138.00] TO BUS 324279 [4MANSLICK 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6967
SINGLE OPN LIN 903 324205-324419(1) | OPEN LINE FROM BUS 324205 [4ASHBOTTOM 138.00] TO BUS 324419 [2ASHBOT WEST69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.3047
SINGLE OPN LIN 904 324205-325023(2) | OPEN LINE FROM BUS 324205 [4ASHBOTTOM 138.00] TO BUS 325023 [2ASHBOT EAST69.000] CKT 2 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.2446
SINGLE OPN LIN 905 324206-324284(1) | OPEN LINE FROM BUS 324206 [4ASHBY 138.00] TO BUS 324284 [4MILL CREEK 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.8364
SINGLE OPN LIN 906 324206-324299(1) | OPEN LINE FROM BUS 324206 [4ASHBY 138.00] TO BUS 324299 [4PLEASUR RDG138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.1711
SINGLE OPN LIN 907 324207-324218(1) | OPEN LINE FROM BUS 324207 [4BARDSTOWN 138.00] TO BUS 324218 [4BROWN CT 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.733
SINGLE OPN LIN 908 324207-324288(1) | OPEN LINE FROM BUS 324207 [4BARDSTOWN 138.00] TO BUS 324288 [4NELSON CO 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.0222
SINGLE OPN LIN 909 324207-324426(1) | OPEN LINE FROM BUS 324207 [4BARDSTOWN 138.00] TO BUS 324426 [2BARDSTOWN 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.51112 | 22.1288
SINGLE OPN LIN 910 324208-324265(1) | OPEN LINE FROM BUS 324208 [4BEARGRASS 138.00] TO BUS 324265 [4JEFFRSONV T138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.8674
SINGLE OPN LIN 911 324208-324277(1) | OPEN LINE FROM BUS 324208 [4BEARGRASS 138.00] TO BUS 324277 [4LYNDON SO 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.4565
SINGLE OPN LIN 912 324208-324289(1) | OPEN LINE FROM BUS 324208 [4BEARGRASS 138.00] TO BUS 324289 [4NORTHSIDE 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.9973
SINGLE OPN LIN 913 324208-324298(1) | OPEN LINE FROM BUS 324208 [4BEARGRASS 138.00] TO BUS 324298 [4PLAINVIEW T138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.4656
SINGLE OPN LIN 914 324208-324321(1) | OPEN LINE FROM BUS 324208 [4BEARGRASS 138.00] TO BUS 324321 [4WATERSIDE 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.585
SINGLE OPN LIN 915 324208-324321(2) | OPEN LINE FROM BUS 324208 [4BEARGRASS 138.00] TO BUS 324321 [4WATERSIDE 138.00] CKT 2 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.585
SINGLE OPN LIN 916 324208-324429(1) | OPEN LINE FROM BUS 324208 [4BEARGRASS 138.00] TO BUS 324429 [2BEARGRASS 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.45739 | 19.6252
SINGLE OPN LIN 917 324209-324263(1) | OPEN LINE FROM BUS 324209 [4BG PARKWAY 138.00] TO BUS 324263 [4HURSTBORNE 138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.50775 | 29.4539 | 1 | 48.37
SINGLE OPN LIN 918 324210-324262(1) | OPEN LINE FROM BUS 324210 [4BAKER LANE 138.00] TO BUS 324262 [4HIGBY MILL 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.37776 | 18.3431
SINGLE OPN LIN 919 324210-324334(1) | OPEN LINE FROM BUS 324210 [4BAKER LANE 138.00] TO BUS 324334 [4BROWN N 2-R138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.53577 | 22.0361
SINGLE OPN LIN 920 324211-324221(1) | OPEN LINE FROM BUS 324211 [4BLACKWELL 138.00] TO BUS 324221 [4BUTLER 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.30145 | 17.1927
SINGLE OPN LIN 921 324211-324253(1) | OPEN LINE FROM BUS 324211 [4BLACKWELL 138.00] TO BUS 324253 [4GHENT 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.40654 | 19.3053
SINGLE OPN LIN 922 324212-324285(1) | OPEN LINE FROM BUS 324212 [4BLUE LICK 138.00] TO BUS 324285 [4MUD LANE 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.47898 | 20.7671
SINGLE OPN LIN 923 324213-324270(1) | OPEN LINE FROM BUS 324213 [4BONNIEVILLE138.00] TO BUS 324270 [4LEBANON WES138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.20693 | 15.8103
SINGLE OPN LIN 924 324213-324447(1) | OPEN LINE FROM BUS 324213 [4BONNIEVILLE138.00] TO BUS 324447 [2BONNIE KU 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.3786 | 4.2013
SINGLE OPN LIN 925 324213-324800(1) | OPEN LINE FROM BUS 324213 [4BONNIEVILLE138.00] TO BUS 324800 [4MERE TVA 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.26378 | 16.9313
SINGLE OPN LIN 926 324214-324243(1) | OPEN LINE FROM BUS 324214 [4BRECKNRIDGE138.00] TO BUS 324243 [4ETHEL 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.4855
SINGLE OPN LIN 927 324214-324263(1) | OPEN LINE FROM BUS 324214 [4BRECKNRIDGE138.00] TO BUS 324263 [4HURSTBORNE 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.7479
SINGLE OPN LIN 928 324214-324451(1) | OPEN LINE FROM BUS 324214 [4BRECKNRIDGE138.00] TO BUS 324451 [2BRECKNRIDGE69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.9605
SINGLE OPN LIN 929 324215-324237(1) | OPEN LINE FROM BUS 324215 [4BRIDGPOR HE138.00] TO BUS 324237 [4CANE RUN SW138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.3483
SINGLE OPN LIN 930 324215-324284(1) | OPEN LINE FROM BUS 324215 [4BRIDGPOR HE138.00] TO BUS 324284 [4MILL CREEK 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.9996
SINGLE OPN LIN 931 324217-324219(1) | OPEN LINE FROM BUS 324217 [4BROWN PLANT138.00] TO BUS 324219 [4BROWN T1 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.3134
SINGLE OPN LIN 932 324217-324220(1) | OPEN LINE FROM BUS 324217 [4BROWN PLANT138.00] TO BUS 324220 [4BROWN T2 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.2721
SINGLE OPN LIN 933 324217-324239(1) | OPEN LINE FROM BUS 324217 [4BROWN PLANT138.00] TO BUS 324239 [4DANVILE N T138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.4051 | 18.3377
SINGLE OPN LIN 934 324217-324248(1) | OPEN LINE FROM BUS 324217 [4BROWN PLANT138.00] TO BUS 324248 [4FAWKES KU 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.7618
SINGLE OPN LIN 935 324218-324219(1) | OPEN LINE FROM BUS 324218 [4BROWN CT 138.00] TO BUS 324219 [4BROWN T1 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.2526
SINGLE OPN LIN 936 324218-324220(1) | OPEN LINE FROM BUS 324218 [4BROWN CT 138.00] TO BUS 324220 [4BROWN T2 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.2742
SINGLE OPN LIN 937 324218-325957(1) | OPEN LINE FROM BUS 324218 [4BROWN CT 138.00] TO BUS 325957 [4BROWN N 1 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.2521
SINGLE OPN LIN 938 324219-325957(1) | OPEN LINE FROM BUS 324219 [4BROWN T1 138.00] TO BUS 325957 [4BROWN N 1 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.4214
SINGLE OPN LIN 939 324220-325956(1) | OPEN LINE FROM BUS 324220 [4BROWN T2 138.00] TO BUS 325956 [4BROWN N 2 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.3236
SINGLE OPN LIN 940 324221-324225(1) | OPEN LINE FROM BUS 324221 [4BUTLER 138.00] TO BUS 324225 [4CARNTOWN TP138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.29084 | 16.9313
SINGLE OPN LIN 941 324222-324237(1) | OPEN LINE FROM BUS 324222 [4CAMPGROUND 138.00] TO BUS 324237 [4CANE RUN SW138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.4656
SINGLE OPN LIN 942 324222-324295(1) | OPEN LINE FROM BUS 324222 [4CAMPGROUND 138.00] TO BUS 324295 [4PADDYS RUN 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.1829
SINGLE OPN LIN 943 324223-324294(1) | OPEN LINE FROM BUS 324223 [4CANAL 138.00] TO BUS 324294 [4PADDYS WEST138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.259
SINGLE OPN LIN 944 324223-324321(1) | OPEN LINE FROM BUS 324223 [4CANAL 138.00] TO BUS 324321 [4WATERSIDE 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.2677
SINGLE OPN LIN 945 324223-324462(1) | OPEN LINE FROM BUS 324223 [4CANAL 138.00] TO BUS 324462 [2CANAL 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.4846
SINGLE OPN LIN 946 324225-324226(1) | OPEN LINE FROM BUS 324225 [4CARNTOWN TP138.00] TO BUS 324226 [4CARNTOWN 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.1688
SINGLE OPN LIN 947 324225-324267(1) | OPEN LINE FROM BUS 324225 [4CARNTOWN TP138.00] TO BUS 324267 [4KENTON 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.001
SINGLE OPN LIN 948 324226-324463(1) | OPEN LINE FROM BUS 324226 [4CARNTOWN 138.00] TO BUS 324463 [2CARNTOWN 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.1772
SINGLE OPN LIN 949 324227-324274(1) | OPEN LINE FROM BUS 324227 [4CARROLLTON 138.00] TO BUS 324274 [4LOCKPORT 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.905
SINGLE OPN LIN 950 324227-324466(1) | OPEN LINE FROM BUS 324227 [4CARROLLTON 138.00] TO BUS 324466 [2CARROLLTON 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.4464
SINGLE OPN LIN 951 324227-324466(2) | OPEN LINE FROM BUS 324227 [4CARROLLTON 138.00] TO BUS 324466 [2CARROLLTON 69.000] CKT 2 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.5171
SINGLE OPN LIN 952 324227-326512(1) | OPEN LINE FROM BUS 324227 [4CARROLLTON 138.00] TO BUS 326512 [4AIRGAS 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.0521
SINGLE OPN LIN 953 324228-324281(1) | OPEN LINE FROM BUS 324228 [4CENTERFIELD138.00] TO BUS 324281 [4MIDDLETOWN 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6058
SINGLE OPN LIN 954 324228-324469(1) | OPEN LINE FROM BUS 324228 [4CENTERFIELD138.00] TO BUS 324469 [2CENTERFIELD69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.48757 | 20.8081
SINGLE OPN LIN 955 324228-326520(1) | OPEN LINE FROM BUS 324228 [4CENTERFIELD138.00] TO BUS 326520 [4TRIMBLE TR9138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.2633
SINGLE OPN LIN 956 324229-324236(1) | OPEN LINE FROM BUS 324229 [4CLARK CO 138.00] TO BUS 324236 [4RICHMND NO 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.5956
SINGLE OPN LIN 957 324229-324310(1) | OPEN LINE FROM BUS 324229 [4CLARK CO 138.00] TO BUS 324310 [4SPENCER RD 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.30105 | 4.03
SINGLE OPN LIN 958 324229-324472(1) | OPEN LINE FROM BUS 324229 [4CLARK CO 138.00] TO BUS 324472 [2CLARK CO 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.394
SINGLE OPN LIN 959 324230-324262(1) | OPEN LINE FROM BUS 324230 [4CLAYS MILL 138.00] TO BUS 324262 [4HIGBY MILL 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 4.0263
SINGLE OPN LIN 960 324230-325957(1) | OPEN LINE FROM BUS 324230 [4CLAYS MILL 138.00] TO BUS 325957 [4BROWN N 1 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.4424 | 19.5347
SINGLE OPN LIN 961 324231-324256(1) | OPEN LINE FROM BUS 324231 [4CLOVERPORT 138.00] TO BUS 324256 [4GR RVR STL 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.6137
SINGLE OPN LIN 962 324231-324260(1) | OPEN LINE FROM BUS 324231 [4CLOVERPORT 138.00] TO BUS 324260 [4HARDINSBURG138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.5534
SINGLE OPN LIN 963 324231-325132(1) | OPEN LINE FROM BUS 324231 [4CLOVERPORT 138.00] TO BUS 325132 [4GREENSOL TP138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.2233
SINGLE OPN LIN 964 324232-326574(1) | OPEN LINE FROM BUS 324232 [4CANE RN 11A138.00] TO BUS 326574 [4CR11 TAP 138.00] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.50743 | 23.4689 | 1 | 5.4
SINGLE OPN LIN 965 324236-324248(1) | OPEN LINE FROM BUS 324236 [4RICHMND NO 138.00] TO BUS 324248 [4FAWKES KU 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.51088 | 21.3
SINGLE OPN LIN 966 324237-324295(1) | OPEN LINE FROM BUS 324237 [4CANE RUN SW138.00] TO BUS 324295 [4PADDYS RUN 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.4647
SINGLE OPN LIN 967 324237-324488(1) | OPEN LINE FROM BUS 324237 [4CANE RUN SW138.00] TO BUS 324488 [2CANE RUN SW69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.9119
SINGLE OPN LIN 968 324237-324488(2) | OPEN LINE FROM BUS 324237 [4CANE RUN SW138.00] TO BUS 324488 [2CANE RUN SW69.000] CKT 2 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.8842
SINGLE OPN LIN 969 324237-325096(22) | OPEN LINE FROM BUS 324237 [4CANE RUN SW138.00] TO BUS 325096 [4CANERN NGCC138.00] CKT 22 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.7991
SINGLE OPN LIN 970 324237-325096(24) | OPEN LINE FROM BUS 324237 [4CANE RUN SW138.00] TO BUS 325096 [4CANERN NGCC138.00] CKT 24 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.7725
SINGLE OPN LIN 971 324237-325096(25) | OPEN LINE FROM BUS 324237 [4CANE RUN SW138.00] TO BUS 325096 [4CANERN NGCC138.00] CKT 25 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.8374
SINGLE OPN LIN 972 324237-326565(23) | OPEN LINE FROM BUS 324237 [4CANE RUN SW138.00] TO BUS 326565 [4INTRNTL TAP138.00] CKT 23 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.725
SINGLE OPN LIN 973 324237-326574(21) | OPEN LINE FROM BUS 324237 [4CANE RUN SW138.00] TO BUS 326574 [4CR11 TAP 138.00] CKT 21 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.7755
SINGLE OPN LIN 974 324238-324239(1) | OPEN LINE FROM BUS 324238 [4DANVILLE N 138.00] TO BUS 324239 [4DANVILE N T138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.47608 | 20.3884
SINGLE OPN LIN 975 324238-324495(1) | OPEN LINE FROM BUS 324238 [4DANVILLE N 138.00] TO BUS 324495 [2DANVILLE N 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.47607 | 20.0545
SINGLE OPN LIN 976 324239-325121(1) | OPEN LINE FROM BUS 324239 [4DANVILE N T138.00] TO BUS 325121 [4LOGAN TP 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.8076
SINGLE OPN LIN 977 324240-324242(1) | OPEN LINE FROM BUS 324240 [4DAY-WALT TP138.00] TO BUS 324242 [4DOW CORN W 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.2964
SINGLE OPN LIN 978 324240-324287(1) | OPEN LINE FROM BUS 324240 [4DAY-WALT TP138.00] TO BUS 324287 [4NAS TAP 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.4338
SINGLE OPN LIN 979 324241-324295(1) | OPEN LINE FROM BUS 324241 [4DIXIE 138.00] TO BUS 324295 [4PADDYS RUN 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.4669
SINGLE OPN LIN 980 324242-326512(1) | OPEN LINE FROM BUS 324242 [4DOW CORN W 138.00] TO BUS 326512 [4AIRGAS 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.198
SINGLE OPN LIN 981 324243-324518(1) | OPEN LINE FROM BUS 324243 [4ETHEL 138.00] TO BUS 324518 [2ETHEL 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.7007
SINGLE OPN LIN 982 324244-324261(1) | OPEN LINE FROM BUS 324244 [4ETOWN 138.00] TO BUS 324261 [4HARDIN CO 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.9163
SINGLE OPN LIN 983 324244-324288(1) | OPEN LINE FROM BUS 324244 [4ETOWN 138.00] TO BUS 324288 [4NELSON CO 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.50335 | 20.8677
SINGLE OPN LIN 984 324244-324519(1) | OPEN LINE FROM BUS 324244 [4ETOWN 138.00] TO BUS 324519 [2ETOWN KU 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.4916
SINGLE OPN LIN 985 324245-324246(1) | OPEN LINE FROM BUS 324245 [4FARMERS TAP138.00] TO BUS 324246 [4FARMERS 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.322
SINGLE OPN LIN 986 324245-324307(1) | OPEN LINE FROM BUS 324245 [4FARMERS TAP138.00] TO BUS 324307 [4SHARKEY TAP138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.8479
SINGLE OPN LIN 987 324245-324310(1) | OPEN LINE FROM BUS 324245 [4FARMERS TAP138.00] TO BUS 324310 [4SPENCER RD 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.9461
SINGLE OPN LIN 988 324246-324528(1) | OPEN LINE FROM BUS 324246 [4FARMERS 138.00] TO BUS 324528 [2FARMERS 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 3.6239
SINGLE OPN LIN 989 324247-324248(1) | OPEN LINE FROM BUS 324247 [4FAWKES TAP 138.00] TO BUS 324248 [4FAWKES KU 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.2487
SINGLE OPN LIN 990 324247-324276(1) | OPEN LINE FROM BUS 324247 [4FAWKES TAP 138.00] TO BUS 324276 [4LAKE REBA T138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.467
SINGLE OPN LIN 991 324248-324530(1) | OPEN LINE FROM BUS 324248 [4FAWKES KU 138.00] TO BUS 324530 [2FAWKES 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6237
SINGLE OPN LIN 992 324248-324530(2) | OPEN LINE FROM BUS 324248 [4FAWKES KU 138.00] TO BUS 324530 [2FAWKES 69.000] CKT 2 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.7534
SINGLE OPN LIN 993 324249-324257(1) | OPEN LINE FROM BUS 324249 [4FERN VALLEY138.00] TO BUS 324257 [4GRADE LANE 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.4786
SINGLE OPN LIN 994 324249-324292(1) | OPEN LINE FROM BUS 324249 [4FERN VALLEY138.00] TO BUS 324292 [4OKOLONA 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.3956
SINGLE OPN LIN 995 324249-324322(1) | OPEN LINE FROM BUS 324249 [4FERN VALLEY138.00] TO BUS 324322 [4WATTERSON 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.3237
SINGLE OPN LIN 996 324249-324532(1) | OPEN LINE FROM BUS 324249 [4FERN VALLEY138.00] TO BUS 324532 [2FERN VALLEY69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 3.0994
SINGLE OPN LIN 997 324249-324532(2) | OPEN LINE FROM BUS 324249 [4FERN VALLEY138.00] TO BUS 324532 [2FERN VALLEY69.000] CKT 2 | TRUE | Met convergence tolerances | 0 | 0.14177 | 3.0987
SINGLE OPN LIN 998 324250-324306(1) | OPEN LINE FROM BUS 324250 [4E FRANKFORT138.00] TO BUS 324306 [4SHADRACK 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.5515
SINGLE OPN LIN 999 324250-324315(1) | OPEN LINE FROM BUS 324250 [4E FRANKFORT138.00] TO BUS 324315 [4TYRONE 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.50352 | 20.2345
SINGLE OPN LIN 1000 324250-324535(1) | OPEN LINE FROM BUS 324250 [4E FRANKFORT138.00] TO BUS 324535 [2E FRANKFORT69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.8306
SINGLE OPN LIN 1001 324250-324535(2) | OPEN LINE FROM BUS 324250 [4E FRANKFORT138.00] TO BUS 324535 [2E FRANKFORT69.000] CKT 2 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.7937
SINGLE OPN LIN 1002 324251-324254(1) | OPEN LINE FROM BUS 324251 [4FLEMNB KU T138.00] TO BUS 324254 [4GODDARD KU 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.38287 | 17.9965
SINGLE OPN LIN 1003 324251-324323(1) | OPEN LINE FROM BUS 324251 [4FLEMNB KU T138.00] TO BUS 324323 [4WEDONIA 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.41128 | 18.6982
SINGLE OPN LIN 1004 324252-324455(1) | OPEN LINE FROM BUS 324252 [2SCHOLLS 69.000] TO BUS 324455 [2BROMLEY 69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.37447 | 19.3068 | 2 | 3.97
SINGLE OPN LIN 1005 324253-324287(1) | OPEN LINE FROM BUS 324253 [4GHENT 138.00] TO BUS 324287 [4NAS TAP 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.343
SINGLE OPN LIN 1006 324253-324290(1) | OPEN LINE FROM BUS 324253 [4GHENT 138.00] TO BUS 324290 [4OWEN CO TAP138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14462 | 7.3791
SINGLE OPN LIN 1007 324253-324831(1) | OPEN LINE FROM BUS 324253 [4GHENT 138.00] TO BUS 324831 [4WHITE SULPH138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 4.2794
SINGLE OPN LIN 1008 324254-324302(1) | OPEN LINE FROM BUS 324254 [4GODDARD KU 138.00] TO BUS 324302 [4RODBURN 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.38426 | 18.0235
SINGLE OPN LIN 1009 324255-324291(1) | OPEN LINE FROM BUS 324255 [4GREEN RIVER138.00] TO BUS 324291 [4OHIO COUNTY138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.0205
SINGLE OPN LIN 1010 324255-324550(1) | OPEN LINE FROM BUS 324255 [4GREEN RIVER138.00] TO BUS 324550 [2GREEN RIVER69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.463
SINGLE OPN LIN 1011 324255-324550(2) | OPEN LINE FROM BUS 324255 [4GREEN RIVER138.00] TO BUS 324550 [2GREEN RIVER69.000] CKT 2 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.4402
SINGLE OPN LIN 1012 324255-325015(1) | OPEN LINE FROM BUS 324255 [4GREEN RIVER138.00] TO BUS 325015 [4SMITH TAP 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.8929
SINGLE OPN LIN 1013 324256-324551(1) | OPEN LINE FROM BUS 324256 [4GR RVR STL 138.00] TO BUS 324551 [2GR RVR STL 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.3265
SINGLE OPN LIN 1014 324256-325015(1) | OPEN LINE FROM BUS 324256 [4GR RVR STL 138.00] TO BUS 325015 [4SMITH TAP 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.3956
SINGLE OPN LIN 1015 324258-324264(1) | OPEN LINE FROM BUS 324258 [4HAEFLING 138.00] TO BUS 324264 [4IBM NORTHTP138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.7488
SINGLE OPN LIN 1016 324258-324317(1) | OPEN LINE FROM BUS 324258 [4HAEFLING 138.00] TO BUS 324317 [4VILEY ROAD 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.423 | 18.8711
SINGLE OPN LIN 1017 324258-324335(1) | OPEN LINE FROM BUS 324258 [4HAEFLING 138.00] TO BUS 324335 [4INNOVATION 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.5837
SINGLE OPN LIN 1018 324258-324558(1) | OPEN LINE FROM BUS 324258 [4HAEFLING 138.00] TO BUS 324558 [2HAEFLING 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.7871
SINGLE OPN LIN 1019 324258-325100(1) | OPEN LINE FROM BUS 324258 [4HAEFLING 138.00] TO BUS 325100 [4W LEX R1 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.46122 | 19.7164
SINGLE OPN LIN 1020 324259-324278(1) | OPEN LINE FROM BUS 324259 [4HANCOCK 138.00] TO BUS 324278 [4MAGAZINE 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.7456
SINGLE OPN LIN 1021 324259-324561(1) | OPEN LINE FROM BUS 324259 [4HANCOCK 138.00] TO BUS 324561 [2HANCOCK 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.0654
SINGLE OPN LIN 1022 324260-325055(1) | OPEN LINE FROM BUS 324260 [4HARDINSBURG138.00] TO BUS 325055 [4RHUDES TP 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.0494
SINGLE OPN LIN 1023 324261-324303(1) | OPEN LINE FROM BUS 324261 [4HARDIN CO 138.00] TO BUS 324303 [4ROGERSVILLE138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.22
SINGLE OPN LIN 1024 324261-324563(1) | OPEN LINE FROM BUS 324261 [4HARDIN CO 138.00] TO BUS 324563 [2HARDIN CO 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.4908
SINGLE OPN LIN 1025 324261-324563(2) | OPEN LINE FROM BUS 324261 [4HARDIN CO 138.00] TO BUS 324563 [2HARDIN CO 69.000] CKT 2 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6371
SINGLE OPN LIN 1026 324262-324269(1) | OPEN LINE FROM BUS 324262 [4HIGBY MILL 138.00] TO BUS 324269 [4LANSDOWNE 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.8312
SINGLE OPN LIN 1027 324262-324333(1) | OPEN LINE FROM BUS 324262 [4HIGBY MILL 138.00] TO BUS 324333 [4BROWN N 1-R138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.50327 | 21.1183
SINGLE OPN LIN 1028 324262-324568(1) | OPEN LINE FROM BUS 324262 [4HIGBY MILL 138.00] TO BUS 324568 [2HIGBY 618 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.41721 | 8.6615
SINGLE OPN LIN 1029 324262-324569(1) | OPEN LINE FROM BUS 324262 [4HIGBY MILL 138.00] TO BUS 324569 [2HIGBY 608 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.7201
SINGLE OPN LIN 1030 324262-324569(2) | OPEN LINE FROM BUS 324262 [4HIGBY MILL 138.00] TO BUS 324569 [2HIGBY 608 69.000] CKT 2 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.4353
SINGLE OPN LIN 1031 324262-325089(Z1) | OPEN LINE FROM BUS 324262 [4HIGBY MILL 138.00] TO BUS 325089 [4HIGBY MILL2138.00] CKT Z1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.556
SINGLE OPN LIN 1032 324263-324297(1) | OPEN LINE FROM BUS 324263 [4HURSTBORNE 138.00] TO BUS 324297 [4PLAINVIEW 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.48742 | 20.812
SINGLE OPN LIN 1033 324264-324275(1) | OPEN LINE FROM BUS 324264 [4IBM NORTHTP138.00] TO BUS 324275 [4LOUDON AVE 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.7008
SINGLE OPN LIN 1034 324264-326548(1) | OPEN LINE FROM BUS 324264 [4IBM NORTHTP138.00] TO BUS 326548 [4IBM NORTH 138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.25869 | 16.6135 | 1 | 2.67
SINGLE OPN LIN 1035 324265-324289(1) | OPEN LINE FROM BUS 324265 [4JEFFRSONV T138.00] TO BUS 324289 [4NORTHSIDE 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.758
SINGLE OPN LIN 1036 324267-324323(1) | OPEN LINE FROM BUS 324267 [4KENTON 138.00] TO BUS 324323 [4WEDONIA 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.43223 | 19.0676
SINGLE OPN LIN 1037 324267-324589(1) | OPEN LINE FROM BUS 324267 [4KENTON 138.00] TO BUS 324589 [2KENTON 688 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.38934 | 3.951
SINGLE OPN LIN 1038 324267-324882(1) | OPEN LINE FROM BUS 324267 [4KENTON 138.00] TO BUS 324882 [2KENTON 698 69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.34497 | 18.5541 | 1 | 3.7
SINGLE OPN LIN 1039 324268-324284(1) | OPEN LINE FROM BUS 324268 [4KNOB CREEK 138.00] TO BUS 324284 [4MILL CREEK 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.916
SINGLE OPN LIN 1040 324268-324300(1) | OPEN LINE FROM BUS 324268 [4KNOB CREEK 138.00] TO BUS 324300 [4POND CREEK 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.915
SINGLE OPN LIN 1041 324269-324601(1) | OPEN LINE FROM BUS 324269 [4LANSDOWNE 138.00] TO BUS 324601 [2LANSDOWNE 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 4.1962
SINGLE OPN LIN 1042 324270-324271(1) | OPEN LINE FROM BUS 324270 [4LEBANON WES138.00] TO BUS 324271 [4LEBANON 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.22339 | 15.6589
SINGLE OPN LIN 1043 324271-324606(1) | OPEN LINE FROM BUS 324271 [4LEBANON 138.00] TO BUS 324606 [2LEBANON 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.2418
SINGLE OPN LIN 1044 324271-324606(2) | OPEN LINE FROM BUS 324271 [4LEBANON 138.00] TO BUS 324606 [2LEBANON 69.000] CKT 2 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.8363
SINGLE OPN LIN 1045 324271-325121(1) | OPEN LINE FROM BUS 324271 [4LEBANON 138.00] TO BUS 325121 [4LOGAN TP 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.8683
SINGLE OPN LIN 1046 324272-324308(1) | OPEN LINE FROM BUS 324272 [4LEITCHFIELD138.00] TO BUS 324308 [4SHREWSBURY 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.3916 | 18.8764
SINGLE OPN LIN 1047 324272-324609(1) | OPEN LINE FROM BUS 324272 [4LEITCHFIELD138.00] TO BUS 324609 [2LEITCHFIELD69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.38678 | 18.8745
SINGLE OPN LIN 1048 324273-326559(Z1) | OPEN LINE FROM BUS 324273 [4LAKE REBA 138.00] TO BUS 326559 [4BGAD TAP 138.00] CKT Z1 | TRUE | Met convergence tolerances | 0 | 0.38562 | 17.8892
SINGLE OPN LIN 1049 324274-324306(1) | OPEN LINE FROM BUS 324274 [4LOCKPORT 138.00] TO BUS 324306 [4SHADRACK 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.792
SINGLE OPN LIN 1050 324275-324618(1) | OPEN LINE FROM BUS 324275 [4LOUDON AVE 138.00] TO BUS 324618 [2LOUDON 628 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.9671
SINGLE OPN LIN 1051 324276-326559(1) | OPEN LINE FROM BUS 324276 [4LAKE REBA T138.00] TO BUS 326559 [4BGAD TAP 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.40616 | 18.3695
SINGLE OPN LIN 1052 324277-324281(1) | OPEN LINE FROM BUS 324277 [4LYNDON SO 138.00] TO BUS 324281 [4MIDDLETOWN 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 4.0241
SINGLE OPN LIN 1053 324277-324622(1) | OPEN LINE FROM BUS 324277 [4LYNDON SO 138.00] TO BUS 324622 [2LYNDON SO 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.3682
SINGLE OPN LIN 1054 324278-324321(1) | OPEN LINE FROM BUS 324278 [4MAGAZINE 138.00] TO BUS 324321 [4WATERSIDE 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.37603 | 17.7808
SINGLE OPN LIN 1055 324279-324284(1) | OPEN LINE FROM BUS 324279 [4MANSLICK 138.00] TO BUS 324284 [4MILL CREEK 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.2946
SINGLE OPN LIN 1056 324281-324282(1) | OPEN LINE FROM BUS 324281 [4MIDDLETOWN 138.00] TO BUS 324282 [4MIDDLETWN-R138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.55881 | 23.2798
SINGLE OPN LIN 1057 324281-324364(1) | OPEN LINE FROM BUS 324281 [4MIDDLETOWN 138.00] TO BUS 324364 [4OLD HENRY 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.54518 | 22.3662
SINGLE OPN LIN 1058 324281-324637(1) | OPEN LINE FROM BUS 324281 [4MIDDLETOWN 138.00] TO BUS 324637 [2MIDDLETOWN 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.2384
SINGLE OPN LIN 1059 324281-324637(2) | OPEN LINE FROM BUS 324281 [4MIDDLETOWN 138.00] TO BUS 324637 [2MIDDLETOWN 69.000] CKT 2 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.2618
SINGLE OPN LIN 1060 324281-324637(6) | OPEN LINE FROM BUS 324281 [4MIDDLETOWN 138.00] TO BUS 324637 [2MIDDLETOWN 69.000] CKT 6 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.8983
SINGLE OPN LIN 1061 324281-325042(1) | OPEN LINE FROM BUS 324281 [4MIDDLETOWN 138.00] TO BUS 325042 [4JEFERSONTWN138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.56286 | 23.3912
SINGLE OPN LIN 1062 324282-324298(1) | OPEN LINE FROM BUS 324282 [4MIDDLETWN-R138.00] TO BUS 324298 [4PLAINVIEW T138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.55915 | 23.4529
SINGLE OPN LIN 1063 324283-324320(1) | OPEN LINE FROM BUS 324283 [4MIDWAY 138.00] TO BUS 324320 [4W LEXINGTON138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.2281
SINGLE OPN LIN 1064 324283-324831(1) | OPEN LINE FROM BUS 324283 [4MIDWAY 138.00] TO BUS 324831 [4WHITE SULPH138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.5698
SINGLE OPN LIN 1065 324284-324640(7) | OPEN LINE FROM BUS 324284 [4MILL CREEK 138.00] TO BUS 324640 [2MILL CREEK 69.000] CKT 7 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.9818
SINGLE OPN LIN 1066 324284-324640(8) | OPEN LINE FROM BUS 324284 [4MILL CREEK 138.00] TO BUS 324640 [2MILL CREEK 69.000] CKT 8 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.2297
SINGLE OPN LIN 1067 324284-325088(1) | OPEN LINE FROM BUS 324284 [4MILL CREEK 138.00] TO BUS 325088 [4MIL CK YARD138.00] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.26643 | 16.6379 | 1 | 27.23
SINGLE OPN LIN 1068 324285-324292(1) | OPEN LINE FROM BUS 324285 [4MUD LANE 138.00] TO BUS 324292 [4OKOLONA 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.7726
SINGLE OPN LIN 1069 324285-324651(1) | OPEN LINE FROM BUS 324285 [4MUD LANE 138.00] TO BUS 324651 [2MUD LANE 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.43036 | 19.3085
SINGLE OPN LIN 1070 324286-324287(1) | OPEN LINE FROM BUS 324286 [4NAS 138.00] TO BUS 324287 [4NAS TAP 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.1806
SINGLE OPN LIN 1071 324289-325013(1) | OPEN LINE FROM BUS 324289 [4NORTHSIDE 138.00] TO BUS 325013 [4CLIFTY TAP1138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.2565
SINGLE OPN LIN 1072 324290-324305(1) | OPEN LINE FROM BUS 324290 [4OWEN CO TAP138.00] TO BUS 324305 [4SCOTT CO 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.62547 | 24.4274
SINGLE OPN LIN 1073 324291-324667(1) | OPEN LINE FROM BUS 324291 [4OHIO COUNTY138.00] TO BUS 324667 [2OHIO COUNTY69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.40507 | 18.789
SINGLE OPN LIN 1074 324294-324295(1) | OPEN LINE FROM BUS 324294 [4PADDYS WEST138.00] TO BUS 324295 [4PADDYS RUN 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6217
SINGLE OPN LIN 1075 324296-324320(1) | OPEN LINE FROM BUS 324296 [4PISGAH 138.00] TO BUS 324320 [4W LEXINGTON138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.5989
SINGLE OPN LIN 1076 324296-324687(1) | OPEN LINE FROM BUS 324296 [4PISGAH 138.00] TO BUS 324687 [2PISGAH 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.53411 | 21.6596
SINGLE OPN LIN 1077 324296-325857(1) | OPEN LINE FROM BUS 324296 [4PISGAH 138.00] TO BUS 325857 [4BROWN N TIE138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.7298
SINGLE OPN LIN 1078 324297-324298(1) | OPEN LINE FROM BUS 324297 [4PLAINVIEW 138.00] TO BUS 324298 [4PLAINVIEW T138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.58191 | 23.6032
SINGLE OPN LIN 1079 324300-324311(1) | OPEN LINE FROM BUS 324300 [4POND CREEK 138.00] TO BUS 324311 [4TIP TOP 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.63619 | 5.6729
SINGLE OPN LIN 1080 324301-325089(1) | OPEN LINE FROM BUS 324301 [4REYNOLDS 138.00] TO BUS 325089 [4HIGBY MILL2138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.3708
SINGLE OPN LIN 1081 324302-324307(1) | OPEN LINE FROM BUS 324302 [4RODBURN 138.00] TO BUS 324307 [4SHARKEY TAP138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.0985
SINGLE OPN LIN 1082 324303-324708(1) | OPEN LINE FROM BUS 324303 [4ROGERSVILLE138.00] TO BUS 324708 [2ROGERSVILLE69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.35405 | 2.802
SINGLE OPN LIN 1083 324304-324762(1) | OPEN LINE FROM BUS 324304 [2VERSAILLE W69.000] TO BUS 324762 [2VERSAIL W T69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 8.0104 | 1 | 11.32
SINGLE OPN LIN 1084 324305-324951(1) | OPEN LINE FROM BUS 324305 [4SCOTT CO 138.00] TO BUS 324951 [2SCOTT CO 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.3411
SINGLE OPN LIN 1085 324305-324991(1) | OPEN LINE FROM BUS 324305 [4SCOTT CO 138.00] TO BUS 324991 [4ROGERS GAP 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.9217
SINGLE OPN LIN 1086 324307-326556(1) | OPEN LINE FROM BUS 324307 [4SHARKEY TAP138.00] TO BUS 326556 [4N SHARKEY T138.00] CKT 1 | TRUE | Met convergence tolerances | 3 | 0.55828 | 42.7926 | 2 | 9.699
SINGLE OPN LIN 1087 324310-324733(1) | OPEN LINE FROM BUS 324310 [4SPENCER RD 138.00] TO BUS 324733 [2SPENCER RD 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.5511
SINGLE OPN LIN 1088 324310-325009(1) | OPEN LINE FROM BUS 324310 [4SPENCER RD 138.00] TO BUS 325009 [2SPENCER A 69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.21016 | 13.6684 | 1 | 20.32
SINGLE OPN LIN 1089 324311-324976(3) | OPEN LINE FROM BUS 324311 [4TIP TOP 138.00] TO BUS 324976 [2TIP TOP 1 69.000] CKT 3 | TRUE | Met convergence tolerances | 2 | 0.7154 | 27.8852 | 1 | 6.49
SINGLE OPN LIN 1090 324311-325132(1) | OPEN LINE FROM BUS 324311 [4TIP TOP 138.00] TO BUS 325132 [4GREENSOL TP138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.3419
SINGLE OPN LIN 1091 324312-324313(1) | OPEN LINE FROM BUS 324312 [4TOYOTA N 138.00] TO BUS 324313 [4TOYOTA S 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.6082
SINGLE OPN LIN 1092 324312-324991(1) | OPEN LINE FROM BUS 324312 [4TOYOTA N 138.00] TO BUS 324991 [4ROGERS GAP 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.779
SINGLE OPN LIN 1093 324314-326520(Z1) | OPEN LINE FROM BUS 324314 [4TRIMBLE CO 138.00] TO BUS 326520 [4TRIMBLE TR9138.00] CKT Z1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.2973
SINGLE OPN LIN 1094 324315-324755(1) | OPEN LINE FROM BUS 324315 [4TYRONE 138.00] TO BUS 324755 [2TYRONE 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.56286 | 22.4014
SINGLE OPN LIN 1095 324315-325957(1) | OPEN LINE FROM BUS 324315 [4TYRONE 138.00] TO BUS 325957 [4BROWN N 1 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.5078
SINGLE OPN LIN 1096 324316-324759(1) | OPEN LINE FROM BUS 324316 [4VIRGINIA CI138.00] TO BUS 324759 [2VIRGINIA CI69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.2119
SINGLE OPN LIN 1097 324317-325101(1) | OPEN LINE FROM BUS 324317 [4VILEY ROAD 138.00] TO BUS 325101 [4W LEX R2 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.48269 | 20.1202
SINGLE OPN LIN 1098 324318-324764(1) | OPEN LINE FROM BUS 324318 [4WEST CLIFF 138.00] TO BUS 324764 [2WEST CLIFF 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.3415
SINGLE OPN LIN 1099 324318-324764(2) | OPEN LINE FROM BUS 324318 [4WEST CLIFF 138.00] TO BUS 324764 [2WEST CLIFF 69.000] CKT 2 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.3224
SINGLE OPN LIN 1100 324319-324765(1) | OPEN LINE FROM BUS 324319 [4W FRANKFORT138.00] TO BUS 324765 [2W FRANKFORT69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.43375 | 19.0982
SINGLE OPN LIN 1101 324320-325089(1) | OPEN LINE FROM BUS 324320 [4W LEXINGTON138.00] TO BUS 325089 [4HIGBY MILL2138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.3287
SINGLE OPN LIN 1102 324320-325100(1) | OPEN LINE FROM BUS 324320 [4W LEXINGTON138.00] TO BUS 325100 [4W LEX R1 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.46055 | 19.7241
SINGLE OPN LIN 1103 324320-325101(1) | OPEN LINE FROM BUS 324320 [4W LEXINGTON138.00] TO BUS 325101 [4W LEX R2 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.48264 | 20.2525
SINGLE OPN LIN 1104 324322-324771(1) | OPEN LINE FROM BUS 324322 [4WATTERSON 138.00] TO BUS 324771 [2WATTERSON 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.5138
SINGLE OPN LIN 1105 324322-324771(2) | OPEN LINE FROM BUS 324322 [4WATTERSON 138.00] TO BUS 324771 [2WATTERSON 69.000] CKT 2 | TRUE | Met convergence tolerances | 0 | 0.14177 | 3.0264
SINGLE OPN LIN 1106 324322-325042(1) | OPEN LINE FROM BUS 324322 [4WATTERSON 138.00] TO BUS 325042 [4JEFERSONTWN138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.48093 | 21.3094
SINGLE OPN LIN 1107 324328-324680(1) | OPEN LINE FROM BUS 324328 [4PARIS 138.00] TO BUS 324680 [2PARIS KU 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.51608 | 21.5366
SINGLE OPN LIN 1108 324329-324364(1) | OPEN LINE FROM BUS 324329 [4COLLINS 138.00] TO BUS 324364 [4OLD HENRY 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.42268 | 19.3822
SINGLE OPN LIN 1109 324329-324481(1) | OPEN LINE FROM BUS 324329 [4COLLINS 138.00] TO BUS 324481 [2COLLINS 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.42329 | 19.1964
SINGLE OPN LIN 1110 324330-324783(1) | OPEN LINE FROM BUS 324330 [2WINCHES IND69.000] TO BUS 324783 [2WINCHSTR KU69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.35024 | 21.2886 | 2 | 32.54
SINGLE OPN LIN 1111 324330-325063(1) | OPEN LINE FROM BUS 324330 [2WINCHES IND69.000] TO BUS 325063 [2CORPORAT DR69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.2181 | 14.0944 | 1 | 21.31
SINGLE OPN LIN 1112 324331-324418(1) | OPEN LINE FROM BUS 324331 [2ASHLAND AVE69.000] TO BUS 324418 [2ASHLND AV T69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 9.6983 | 1 | 14.14
SINGLE OPN LIN 1113 324332-325059(1) | OPEN LINE FROM BUS 324332 [2LAKE SHORE 69.000] TO BUS 325059 [2BRYANT RD T69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.26632 | 16.943 | 1 | 25.39
SINGLE OPN LIN 1114 324333-325957(1) | OPEN LINE FROM BUS 324333 [4BROWN N 1-R138.00] TO BUS 325957 [4BROWN N 1 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.50241 | 21.2166
SINGLE OPN LIN 1115 324334-325956(1) | OPEN LINE FROM BUS 324334 [4BROWN N 2-R138.00] TO BUS 325956 [4BROWN N 2 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.53425 | 21.894
SINGLE OPN LIN 1116 324337-324650(1) | OPEN LINE FROM BUS 324337 [2MOUNT TABOR69.000] TO BUS 324650 [2MT TBR T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.21262 | 15.8373 | 1 | 0.99
SINGLE OPN LIN 1117 324338-324339(1) | OPEN LINE FROM BUS 324338 [2SCOTT ST 4 69.000] TO BUS 324339 [2SCOTT ST 1269.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 9.2517 | 1 | 13.4
SINGLE OPN LIN 1118 324338-324952(1) | OPEN LINE FROM BUS 324338 [2SCOTT ST 4 69.000] TO BUS 324952 [2SCOTT ST TP69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.17366 | 11.8724 | 2 | 17.64
SINGLE OPN LIN 1119 324340-324734(1) | OPEN LINE FROM BUS 324340 [2SPINDLETOP 69.000] TO BUS 324734 [2SPINDLETP T69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.16994 | 15.3692 | 1 | 1.54
SINGLE OPN LIN 1120 324341-324781(1) | OPEN LINE FROM BUS 324341 [2WILMORE 69.000] TO BUS 324781 [2WILMORE T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.91918 | 41.7585 | 1 | 10.1
SINGLE OPN LIN 1121 324344-324421(1) | OPEN LINE FROM BUS 324344 [2ATOKA 69.000] TO BUS 324421 [2ATOKA TAP 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.31844 | 17.7956 | 1 | 3.33
SINGLE OPN LIN 1122 324345-324425(1) | OPEN LINE FROM BUS 324345 [2BARDTWN IND69.000] TO BUS 324425 [2BARDT IND T69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.16775 | 11.6773 | 1 | 17.37
SINGLE OPN LIN 1123 324346-324612(1) | OPEN LINE FROM BUS 324346 [2RICHMND E 69.000] TO BUS 324612 [2LAKE REBA 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.996 | 45.6059 | 1 | 11.03
SINGLE OPN LIN 1124 324347-325058(1) | OPEN LINE FROM BUS 324347 [2BEATTY 649 69.000] TO BUS 325058 [2BEATTY 614 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.24885 | 16.5224 | 1 | 2.56
SINGLE OPN LIN 1125 324348-324808(1) | OPEN LINE FROM BUS 324348 [2BRODHEAD CI69.000] TO BUS 324808 [2BRODHEAD KU69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.20972 | 15.8834 | 1 | 2.14
SINGLE OPN LIN 1126 324349-324479(1) | OPEN LINE FROM BUS 324349 [2CAMPBELVIL269.000] TO BUS 324479 [2CAMPBELVL T69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.97852 | 61.105 | 2 | 14.7606
SINGLE OPN LIN 1127 324350-324485(1) | OPEN LINE FROM BUS 324350 [2CRAB ORCHAR69.000] TO BUS 324485 [2CRAB ORCH T69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.16624 | 15.2362 | 1 | 1.41
SINGLE OPN LIN 1128 324351-324354(1) | OPEN LINE FROM BUS 324351 [2ETOWN 3 69.000] TO BUS 324354 [2GATES RUBBR69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.14177 | 9.9055 | 2 | 14.96
SINGLE OPN LIN 1129 324351-324519(1) | OPEN LINE FROM BUS 324351 [2ETOWN 3 69.000] TO BUS 324519 [2ETOWN KU 69.000] CKT 1 | TRUE | Met convergence tolerances | 3 | 0.20182 | 13.5907 | 3 | 21.18
SINGLE OPN LIN 1130 324352-324563(1) | OPEN LINE FROM BUS 324352 [2ETOWN IND 69.000] TO BUS 324563 [2HARDIN CO 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14177 | 8.0157 | 1 | 11.79
SINGLE OPN LIN 1131 324353-324863(1) | OPEN LINE FROM BUS 324353 [2FLORDA TILE69.000] TO BUS 324863 [2FLA TILE T169.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 8.4394 | 1 | 11.99
SINGLE OPN LIN 1132 324354-326561(1) | OPEN LINE FROM BUS 324354 [2GATES RUBBR69.000] TO BUS 326561 [2ETOWN WEST 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14177 | 9.7634 | 1 | 14.78
SINGLE OPN LIN 1133 324355-325054(1) | OPEN LINE FROM BUS 324355 [2HARRDSBRG 469.000] TO BUS 325054 [2HARRDSBRG N69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.14932 | 10.6403 | 2 | 15.97
SINGLE OPN LIN 1134 324355-326578(1) | OPEN LINE FROM BUS 324355 [2HARRDSBRG 469.000] TO BUS 326578 [2HARRDSBRG 169.000] CKT 1 | TRUE | Met convergence tolerances | 3 | 0.17372 | 11.9007 | 3 | 18.07
SINGLE OPN LIN 1135 324356-325054(1) | OPEN LINE FROM BUS 324356 [2HARRDSBRG1269.000] TO BUS 325054 [2HARRDSBRG N69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.71344 | 32.844 | 1 | 7.67
SINGLE OPN LIN 1136 324357-324600(1) | OPEN LINE FROM BUS 324357 [2LANCASTER 169.000] TO BUS 324600 [2LANCASTR KU69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.51354 | 24.5394 | 1 | 5.49
SINGLE OPN LIN 1137 324358-324914(1) | OPEN LINE FROM BUS 324358 [2M-V CLARKSN69.000] TO BUS 324914 [2M-V CLARK T69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.24619 | 16.4388 | 1 | 2.49
SINGLE OPN LIN 1138 324359-324913(1) | OPEN LINE FROM BUS 324359 [2MT VERN 58969.000] TO BUS 324913 [2MT VERNON 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.40669 | 20.5839 | 1 | 4.26
SINGLE OPN LIN 1139 324360-324927(1) | OPEN LINE FROM BUS 324360 [2PINE HILL 69.000] TO BUS 324927 [2PINE HILL T69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.19012 | 15.2471 | 1 | 1.07
SINGLE OPN LIN 1140 324361-324935(1) | OPEN LINE FROM BUS 324361 [2RADCLIFF KU69.000] TO BUS 324935 [2RADCLF KU T69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.7233 | 32.6631 | 1 | 7.78
SINGLE OPN LIN 1141 324363-324957(1) | OPEN LINE FROM BUS 324363 [2SHELB CI KU69.000] TO BUS 324957 [2SHELBY CI T69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.17933 | 13.0978 | 2 | 18.0267
SINGLE OPN LIN 1142 324363-326518(1) | OPEN LINE FROM BUS 324363 [2SHELB CI KU69.000] TO BUS 326518 [2SHELB CI EK69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.87493 | 58.2993 | 1 | 13.6767
SINGLE OPN LIN 1143 324372-324514(1) | OPEN LINE FROM BUS 324372 [2BURNSIDE 69.000] TO BUS 324514 [2ELIHU 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.52301 | 24.876 | 1 | 5.59
SINGLE OPN LIN 1144 324373-324814(1) | OPEN LINE FROM BUS 324373 [2CATRON CRK 69.000] TO BUS 324814 [2CATRON CK T69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.19599 | 15.2904 | 1 | 1.04
SINGLE OPN LIN 1145 324374-324376(1) | OPEN LINE FROM BUS 324374 [2CROCKETT KU69.000] TO BUS 324376 [2DEER BRANCH69.000] CKT 1 | TRUE | Met convergence tolerances | 4 | 0.17279 | 16.5389 | 3 | 3.0037
SINGLE OPN LIN 1146 324374-325083(1) | OPEN LINE FROM BUS 324374 [2CROCKETT KU69.000] TO BUS 325083 [2ALEX CK TAP69.000] CKT 1 | TRUE | Met convergence tolerances | 3 | 0.15323 | 14.9693 | 2 | 1.6337
SINGLE OPN LIN 1147 324375-324442(1) | OPEN LINE FROM BUS 324375 [2DAYHOIT 69.000] TO BUS 324442 [2BLEDSOE TAP69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.24881 | 16.4751 | 1 | 2.59
SINGLE OPN LIN 1148 324376-324813(1) | OPEN LINE FROM BUS 324376 [2DEER BRANCH69.000] TO BUS 324813 [2CARY 69.000] CKT 1 | TRUE | Met convergence tolerances | 5 | 0.21824 | 17.7275 | 4 | 3.5737
SINGLE OPN LIN 1149 324377-325083(1) | OPEN LINE FROM BUS 324377 [2GARDNER 69.000] TO BUS 325083 [2ALEX CK TAP69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 2.4691 | 1 | 0.27
SINGLE OPN LIN 1150 324378-324636(1) | OPEN LINE FROM BUS 324378 [2MIDDLBO780 69.000] TO BUS 324636 [2MIDDLESBORO69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.97133 | 44.0296 | 1 | 10.53
SINGLE OPN LIN 1151 324380-324393(1) | OPEN LINE FROM BUS 324380 [2DANIEL BRAN69.000] TO BUS 324393 [2ROSE HILL 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.33758 | 18.3461 | 1 | 3.59
SINGLE OPN LIN 1152 324380-324945(1) | OPEN LINE FROM BUS 324380 [2DANIEL BRAN69.000] TO BUS 324945 [2ROSE HILL T69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.44022 | 19.8512 | 2 | 4.08
SINGLE OPN LIN 1153 324381-325001(1) | OPEN LINE FROM BUS 324381 [2WILLAMSBURG69.000] TO BUS 325001 [2WILLMBRG SW69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.2911 | 17.3225 | 1 | 2.98
SINGLE OPN LIN 1154 324382-325001(1) | OPEN LINE FROM BUS 324382 [2WILLMBRG SO69.000] TO BUS 325001 [2WILLMBRG SW69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 9.1353 | 1 | 13.08
SINGLE OPN LIN 1155 324384-324549(1) | OPEN LINE FROM BUS 324384 [2APPALACHIA 69.000] TO BUS 324549 [2GORGE 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.23954 | 16.3488 | 1 | 2.5
SINGLE OPN LIN 1156 324385-324549(1) | OPEN LINE FROM BUS 324385 [2BIG STONE G69.000] TO BUS 324549 [2GORGE 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 8.4627 | 1 | 12.29
SINGLE OPN LIN 1157 324386-324388(1) | OPEN LINE FROM BUS 324386 [2DIXIANA 69.000] TO BUS 324388 [2CRITICAL FK69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.38944 | 20.0521 | 1 | 4.13
SINGLE OPN LIN 1158 324387-324392(1) | OPEN LINE FROM BUS 324387 [2ADDINGTON 69.000] TO BUS 324392 [2ROCKY FORK 69.000] CKT 1 | TRUE | Met convergence tolerances | 4 | 0.43049 | 21.3958 | 3 | 4.57
SINGLE OPN LIN 1159 324387-325064(1) | OPEN LINE FROM BUS 324387 [2ADDINGTON 69.000] TO BUS 325064 [2LAUREL GROV69.000] CKT 1 | TRUE | Met convergence tolerances | 5 | 0.49804 | 23.8193 | 4 | 5.31
SINGLE OPN LIN 1160 324388-325031(1) | OPEN LINE FROM BUS 324388 [2CRITICAL FK69.000] TO BUS 325031 [2LIPPS 69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.38945 | 20.0413 | 1 | 4.13
SINGLE OPN LIN 1161 324389-324851(1) | OPEN LINE FROM BUS 324389 [2DWINA 69.000] TO BUS 324851 [2DWINA TAP 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.22719 | 15.895 | 1 | 0.8
SINGLE OPN LIN 1162 324390-324391(1) | OPEN LINE FROM BUS 324390 [2PENNINGTON 69.000] TO BUS 324391 [2POOR VALLEY69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.21185 | 15.8006 | 1 | 0.97
SINGLE OPN LIN 1163 324391-324689(1) | OPEN LINE FROM BUS 324391 [2POOR VALLEY69.000] TO BUS 324689 [2POCKET 69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.56732 | 26.3278 | 2 | 6.15
SINGLE OPN LIN 1164 324392-325031(1) | OPEN LINE FROM BUS 324392 [2ROCKY FORK 69.000] TO BUS 325031 [2LIPPS 69.000] CKT 1 | TRUE | Met convergence tolerances | 3 | 0.41781 | 20.9211 | 2 | 4.42
SINGLE OPN LIN 1165 324394-324977(1) | OPEN LINE FROM BUS 324394 [2TOMS CREEK 69.000] TO BUS 324977 [2TOMS CRK TP69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.52772 | 25.7114 | 1 | 5.62
SINGLE OPN LIN 1166 324395-325005(1) | OPEN LINE FROM BUS 324395 [2WISE 69.000] TO BUS 325005 [2WISE TAP 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.56582 | 27.1747 | 1 | 6.07
SINGLE OPN LIN 1167 324400-324510(1) | OPEN LINE FROM BUS 324400 [2WHAS TAP 69.000] TO BUS 324510 [2EASTWOOD 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.882
SINGLE OPN LIN 1168 324400-324775(1) | OPEN LINE FROM BUS 324400 [2WHAS TAP 69.000] TO BUS 324775 [2WHAS 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.8345
SINGLE OPN LIN 1169 324400-325022(1) | OPEN LINE FROM BUS 324400 [2WHAS TAP 69.000] TO BUS 325022 [2EASTWOOD W 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.1664
SINGLE OPN LIN 1170 324401-324541(1) | OPEN LINE FROM BUS 324401 [2FREYS HIL J69.000] TO BUS 324541 [2FORD 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.41168 | 19.0497
SINGLE OPN LIN 1171 324401-324545(1) | OPEN LINE FROM BUS 324401 [2FREYS HIL J69.000] TO BUS 324545 [2FREYS HILL 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.334
SINGLE OPN LIN 1172 324401-324785(1) | OPEN LINE FROM BUS 324401 [2FREYS HIL J69.000] TO BUS 324785 [2WORTHINGTON69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.55632 | 22.8782
SINGLE OPN LIN 1173 324402-324859(1) | OPEN LINE FROM BUS 324402 [2FAIRMOUNT T69.000] TO BUS 324859 [2FAIRMOUNT 169.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.20569 | 13.4083 | 1 | 21.19
SINGLE OPN LIN 1174 324403-324469(1) | OPEN LINE FROM BUS 324403 [2CRESTWOOD T69.000] TO BUS 324469 [2CENTERFIELD69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.8052
SINGLE OPN LIN 1175 324403-324487(1) | OPEN LINE FROM BUS 324403 [2CRESTWOOD T69.000] TO BUS 324487 [2CRESTWOOD 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.8472
SINGLE OPN LIN 1176 324403-324616(1) | OPEN LINE FROM BUS 324403 [2CRESTWOOD T69.000] TO BUS 324616 [2LONG RUN 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.5512
SINGLE OPN LIN 1177 324404-324622(1) | OPEN LINE FROM BUS 324404 [2LYNDON TAP 69.000] TO BUS 324622 [2LYNDON SO 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.8064
SINGLE OPN LIN 1178 324404-324623(1) | OPEN LINE FROM BUS 324404 [2LYNDON TAP 69.000] TO BUS 324623 [2LYNDON 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 3.1338
SINGLE OPN LIN 1179 324404-324750(1) | OPEN LINE FROM BUS 324404 [2LYNDON TAP 69.000] TO BUS 324750 [2TAYLOR LG 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.1733
SINGLE OPN LIN 1180 324405-324547(1) | OPEN LINE FROM BUS 324405 [2ADAMS 69.000] TO BUS 324547 [2GEORGETOWN 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.5666
SINGLE OPN LIN 1181 324405-326989(1) | OPEN LINE FROM BUS 324405 [2ADAMS 69.000] TO BUS 326989 [2LONG LICK 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.7431
SINGLE OPN LIN 1182 324406-324637(1) | OPEN LINE FROM BUS 324406 [2AIKEN 69.000] TO BUS 324637 [2MIDDLETOWN 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.55289 | 22.7098
SINGLE OPN LIN 1183 324406-324673(1) | OPEN LINE FROM BUS 324406 [2AIKEN 69.000] TO BUS 324673 [2OXMOOR 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 3.0475
SINGLE OPN LIN 1184 324406-325022(1) | OPEN LINE FROM BUS 324406 [2AIKEN 69.000] TO BUS 325022 [2EASTWOOD W 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.8244
SINGLE OPN LIN 1185 324407-324755(1) | OPEN LINE FROM BUS 324407 [2ALEXANDER 69.000] TO BUS 324755 [2TYRONE 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.4894
SINGLE OPN LIN 1186 324407-324955(1) | OPEN LINE FROM BUS 324407 [2ALEXANDER 69.000] TO BUS 324955 [2SHANNON RUN69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.3657
SINGLE OPN LIN 1187 324408-324552(1) | OPEN LINE FROM BUS 324408 [2ALGONQUIN 69.000] TO BUS 324552 [2GRADY 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.4487
SINGLE OPN LIN 1188 324408-324625(1) | OPEN LINE FROM BUS 324408 [2ALGONQUIN 69.000] TO BUS 324625 [2MAGAZINE 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6779
SINGLE OPN LIN 1189 324408-324649(1) | OPEN LINE FROM BUS 324408 [2ALGONQUIN 69.000] TO BUS 324649 [2MORRIS FORM69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.6983
SINGLE OPN LIN 1190 324408-324719(1) | OPEN LINE FROM BUS 324408 [2ALGONQUIN 69.000] TO BUS 324719 [2SEMINOLE 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.0413
SINGLE OPN LIN 1191 324408-324739(1) | OPEN LINE FROM BUS 324408 [2ALGONQUIN 69.000] TO BUS 324739 [2STEWART 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.9137
SINGLE OPN LIN 1192 324409-324632(1) | OPEN LINE FROM BUS 324409 [2AMERICAN AV69.000] TO BUS 324632 [2UK MED CENT69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.833
SINGLE OPN LIN 1193 324409-324683(1) | OPEN LINE FROM BUS 324409 [2AMERICAN AV69.000] TO BUS 324683 [2PICADOME 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.3184
SINGLE OPN LIN 1194 324409-324772(1) | OPEN LINE FROM BUS 324409 [2AMERICAN AV69.000] TO BUS 324772 [2UK WEST 2 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.5308
SINGLE OPN LIN 1195 324411-324440(1) | OPEN LINE FROM BUS 324411 [2ANDOVER TAP69.000] TO BUS 324440 [2BLACK MOUNT69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.159
SINGLE OPN LIN 1196 324411-324583(1) | OPEN LINE FROM BUS 324411 [2ANDOVER TAP69.000] TO BUS 324583 [2IMBODEN 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 3.2677
SINGLE OPN LIN 1197 324411-324670(1) | OPEN LINE FROM BUS 324411 [2ANDOVER TAP69.000] TO BUS 324670 [2OSAKA EAST 69.000] CKT 1 | TRUE | Met convergence tolerances | 5 | 0.40863 | 21.0217 | 2 | 4.33
SINGLE OPN LIN 1198 324412-324670(1) | OPEN LINE FROM BUS 324412 [2ANDOVER 69.000] TO BUS 324670 [2OSAKA EAST 69.000] CKT 1 | TRUE | Met convergence tolerances | 4 | 0.36898 | 19.5963 | 1 | 3.87
SINGLE OPN LIN 1199 324413-324414(1) | OPEN LINE FROM BUS 324413 [2AO SMITH TP69.000] TO BUS 324414 [2AO SMITH 69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.92253 | 50.531 | 2 | 11.8228
SINGLE OPN LIN 1200 324413-324461(1) | OPEN LINE FROM BUS 324413 [2AO SMITH TP69.000] TO BUS 324461 [2CAMARGO 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.4934
SINGLE OPN LIN 1201 324413-324733(1) | OPEN LINE FROM BUS 324413 [2AO SMITH TP69.000] TO BUS 324733 [2SPENCER RD 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.0307
SINGLE OPN LIN 1202 324414-326531(1) | OPEN LINE FROM BUS 324414 [2AO SMITH 69.000] TO BUS 326531 [2HINKSTON 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.1452 | 18.2733 | 1 | 3.5628
SINGLE OPN LIN 1203 324415-324593(1) | OPEN LINE FROM BUS 324415 [2APPOLO FUEL69.000] TO BUS 324593 [2KU PARK 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.16576 | 6.2921
SINGLE OPN LIN 1204 324415-324636(1) | OPEN LINE FROM BUS 324415 [2APPOLO FUEL69.000] TO BUS 324636 [2MIDDLESBORO69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.3052
SINGLE OPN LIN 1205 324416-324433(1) | OPEN LINE FROM BUS 324416 [2ARNOLD 69.000] TO BUS 324433 [2BENHAM 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.0111
SINGLE OPN LIN 1206 324416-324490(1) | OPEN LINE FROM BUS 324416 [2ARNOLD 69.000] TO BUS 324490 [2CUMBERLAND 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6217
SINGLE OPN LIN 1207 324417-324423(1) | OPEN LINE FROM BUS 324417 [2ARTEMUS 69.000] TO BUS 324423 [2BARBOURVILE69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.302
SINGLE OPN LIN 1208 324418-324632(1) | OPEN LINE FROM BUS 324418 [2ASHLND AV T69.000] TO BUS 324632 [2UK MED CENT69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.4127
SINGLE OPN LIN 1209 324418-324934(1) | OPEN LINE FROM BUS 324418 [2ASHLND AV T69.000] TO BUS 324934 [2RACE STREET69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.3393
SINGLE OPN LIN 1210 324419-325024(1) | OPEN LINE FROM BUS 324419 [2ASHBOT WEST69.000] TO BUS 325024 [2ASHBOT SPRK69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6889
SINGLE OPN LIN 1211 324421-324450(1) | OPEN LINE FROM BUS 324421 [2ATOKA TAP 69.000] TO BUS 324450 [2BOYLE CO 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.5234
SINGLE OPN LIN 1212 324421-324495(1) | OPEN LINE FROM BUS 324421 [2ATOKA TAP 69.000] TO BUS 324495 [2DANVILLE N 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.5265
SINGLE OPN LIN 1213 324422-324508(1) | OPEN LINE FROM BUS 324422 [2AVON T2 69.000] TO BUS 324508 [2EASTLAND 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.7084
SINGLE OPN LIN 1214 324422-324680(1) | OPEN LINE FROM BUS 324422 [2AVON T2 69.000] TO BUS 324680 [2PARIS KU 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.713
SINGLE OPN LIN 1215 324422-325081(1) | OPEN LINE FROM BUS 324422 [2AVON T2 69.000] TO BUS 325081 [2BRIAR HILL 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.38989 | 20.1519 | 1 | 4.05
SINGLE OPN LIN 1216 324423-324438(1) | OPEN LINE FROM BUS 324423 [2BARBOURVILE69.000] TO BUS 324438 [2BIMBLE 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.3025
SINGLE OPN LIN 1217 324424-324801(1) | OPEN LINE FROM BUS 324424 [2BARDTWN CTY69.000] TO BUS 324801 [2BARTON 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6729
SINGLE OPN LIN 1218 324424-326537(1) | OPEN LINE FROM BUS 324424 [2BARDTWN CTY69.000] TO BUS 326537 [2WOODLAWN KU69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.42885 | 6.5718
SINGLE OPN LIN 1219 324425-324426(1) | OPEN LINE FROM BUS 324425 [2BARDT IND T69.000] TO BUS 324426 [2BARDSTOWN 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.49076 | 21.0055
SINGLE OPN LIN 1220 324426-324525(1) | OPEN LINE FROM BUS 324426 [2BARDSTOWN 69.000] TO BUS 324525 [2FAIRFIELD 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.8876
SINGLE OPN LIN 1221 324426-326537(Z1) | OPEN LINE FROM BUS 324426 [2BARDSTOWN 69.000] TO BUS 326537 [2WOODLAWN KU69.000] CKT Z1 | TRUE | Met convergence tolerances | 0 | 0.16271 | 3.0312
SINGLE OPN LIN 1222 324427-324779(1) | OPEN LINE FROM BUS 324427 [2BARDWELL 69.000] TO BUS 324779 [2WICKLIFFE 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.2953
SINGLE OPN LIN 1223 324427-324823(1) | OPEN LINE FROM BUS 324427 [2BARDWELL 69.000] TO BUS 324823 [2CLINTON 58169.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.0969
SINGLE OPN LIN 1224 324428-324778(1) | OPEN LINE FROM BUS 324428 [2BARLOW 69.000] TO BUS 324778 [2WICKLIFE CI69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.6506
SINGLE OPN LIN 1225 324428-324864(1) | OPEN LINE FROM BUS 324428 [2BARLOW 69.000] TO BUS 324864 [2FORRESTDALE69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.9966
SINGLE OPN LIN 1226 324429-324453(1) | OPEN LINE FROM BUS 324429 [2BEARGRASS 69.000] TO BUS 324453 [2BEARGRS PMP69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.4418
SINGLE OPN LIN 1227 324429-324475(1) | OPEN LINE FROM BUS 324429 [2BEARGRASS 69.000] TO BUS 324475 [2CLIFTON 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.3981
SINGLE OPN LIN 1228 324429-324624(1) | OPEN LINE FROM BUS 324429 [2BEARGRASS 69.000] TO BUS 324624 [2MADISON LGE69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.5163
SINGLE OPN LIN 1229 324429-324710(1) | OPEN LINE FROM BUS 324429 [2BEARGRASS 69.000] TO BUS 324710 [2RVR CITY SH69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.9734
SINGLE OPN LIN 1230 324430-325058(1) | OPEN LINE FROM BUS 324430 [2BEATTYVI KU69.000] TO BUS 325058 [2BEATTY 614 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.4419
SINGLE OPN LIN 1231 324432-324558(1) | OPEN LINE FROM BUS 324432 [2BELT LINE 69.000] TO BUS 324558 [2HAEFLING 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.7459
SINGLE OPN LIN 1232 324432-324879(1) | OPEN LINE FROM BUS 324432 [2BELT LINE 69.000] TO BUS 324879 [2IBM 998 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6324
SINGLE OPN LIN 1233 324433-324621(1) | OPEN LINE FROM BUS 324433 [2BENHAM 69.000] TO BUS 324621 [2LYNCH 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.9754
SINGLE OPN LIN 1234 324434-324435(1) | OPEN LINE FROM BUS 324434 [2BEREA TAP 69.000] TO BUS 324435 [2BEREA NORTH69.000] CKT 1 | TRUE | Met convergence tolerances | 4 | 0.24541 | 15.5781 | 3 | 23.7
SINGLE OPN LIN 1235 324434-324668(1) | OPEN LINE FROM BUS 324434 [2BEREA TAP 69.000] TO BUS 324668 [2OKONITE 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6043
SINGLE OPN LIN 1236 324435-324805(1) | OPEN LINE FROM BUS 324435 [2BEREA NORTH69.000] TO BUS 324805 [2BEREA 2 69.000] CKT 1 | TRUE | Met convergence tolerances | 3 | 0.14287 | 8.9109 | 2 | 12.69
SINGLE OPN LIN 1237 324436-324676(1) | OPEN LINE FROM BUS 324436 [2BEREA EK TP69.000] TO BUS 324676 [2PAINT LICK 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.19907 | 15.4366 | 1 | 1.03
SINGLE OPN LIN 1238 324436-324805(1) | OPEN LINE FROM BUS 324436 [2BEREA EK TP69.000] TO BUS 324805 [2BEREA 2 69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.19895 | 15.4017 | 1 | 1.03
SINGLE OPN LIN 1239 324437-324745(1) | OPEN LINE FROM BUS 324437 [2BEVIER KU 69.000] TO BUS 324745 [2STRINGTOWN 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.7462
SINGLE OPN LIN 1240 324438-324515(1) | OPEN LINE FROM BUS 324438 [2BIMBLE 69.000] TO BUS 324515 [2EMANUEL TAP69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.44225 | 19.6051
SINGLE OPN LIN 1241 324438-324573(1) | OPEN LINE FROM BUS 324438 [2BIMBLE 69.000] TO BUS 324573 [2HINKLE 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.3403
SINGLE OPN LIN 1242 324439-324518(1) | OPEN LINE FROM BUS 324439 [2BISHOP 69.000] TO BUS 324518 [2ETHEL 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.6364
SINGLE OPN LIN 1243 324439-324532(1) | OPEN LINE FROM BUS 324439 [2BISHOP 69.000] TO BUS 324532 [2FERN VALLEY69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.713
SINGLE OPN LIN 1244 324440-324621(1) | OPEN LINE FROM BUS 324440 [2BLACK MOUNT69.000] TO BUS 324621 [2LYNCH 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.2082
SINGLE OPN LIN 1245 324441-324503(1) | OPEN LINE FROM BUS 324441 [2BLACKWOOD 69.000] TO BUS 324503 [2DORCHESTER 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6888
SINGLE OPN LIN 1246 324441-324802(1) | OPEN LINE FROM BUS 324441 [2BLACKWOOD 69.000] TO BUS 324802 [2BEAR BRANCH69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6962
SINGLE OPN LIN 1247 324442-324497(1) | OPEN LINE FROM BUS 324442 [2BLEDSOE TAP69.000] TO BUS 324497 [2DAYHOIT TAP69.000] CKT 1 | TRUE | Met convergence tolerances | 4 | 0.33534 | 31.3442 | 3 | 7.5901
SINGLE OPN LIN 1248 324442-325008(1) | OPEN LINE FROM BUS 324442 [2BLEDSOE TAP69.000] TO BUS 325008 [2BLEDSOE 69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.17393 | 22.4615 | 2 | 5.0001
SINGLE OPN LIN 1249 324443-324789(1) | OPEN LINE FROM BUS 324443 [2BLUE LICK 69.000] TO BUS 324789 [2BLUE LCK TP69.000] CKT 1 | TRUE | Met convergence tolerances | 6 | 0.65914 | 41.2714 | 4 | 60.4574
SINGLE OPN LIN 1250 324444-324651(1) | OPEN LINE FROM BUS 324444 [2BLUELICK EK69.000] TO BUS 324651 [2MUD LANE 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6365
SINGLE OPN LIN 1251 324444-324788(1) | OPEN LINE FROM BUS 324444 [2BLUELICK EK69.000] TO BUS 324788 [2BROOKS EK T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.5777
SINGLE OPN LIN 1252 324445-324620(1) | OPEN LINE FROM BUS 324445 [2BONDS MILL 69.000] TO BUS 324620 [2LAWRENCEBRG69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.9861
SINGLE OPN LIN 1253 324445-324732(1) | OPEN LINE FROM BUS 324445 [2BONDS MILL 69.000] TO BUS 324732 [2SOUTHVILLE 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.47963 | 38.7104 | 1 | 8.7902
SINGLE OPN LIN 1254 324445-324863(1) | OPEN LINE FROM BUS 324445 [2BONDS MILL 69.000] TO BUS 324863 [2FLA TILE T169.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.8583
SINGLE OPN LIN 1255 324445-325087(1) | OPEN LINE FROM BUS 324445 [2BONDS MILL 69.000] TO BUS 325087 [2CLAY LICK T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.7657
SINGLE OPN LIN 1256 324446-324824(1) | OPEN LINE FROM BUS 324446 [2BOND 69.000] TO BUS 324824 [2CLINCH VALL69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.5532
SINGLE OPN LIN 1257 324446-324977(1) | OPEN LINE FROM BUS 324446 [2BOND 69.000] TO BUS 324977 [2TOMS CRK TP69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.4817
SINGLE OPN LIN 1258 324447-324731(1) | OPEN LINE FROM BUS 324447 [2BONNIE KU 69.000] TO BUS 324731 [2SONORA TAP 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.4669
SINGLE OPN LIN 1259 324448-324782(1) | OPEN LINE FROM BUS 324448 [2BOONE AVE 69.000] TO BUS 324782 [2WINCHEST SO69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.48008 | 20.6087
SINGLE OPN LIN 1260 324448-325004(1) | OPEN LINE FROM BUS 324448 [2BOONE AVE 69.000] TO BUS 325004 [2WINCHES WTR69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.53303 | 21.6366
SINGLE OPN LIN 1261 324449-325004(1) | OPEN LINE FROM BUS 324449 [2BOONSBORO N69.000] TO BUS 325004 [2WINCHES WTR69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.58518 | 23.252
SINGLE OPN LIN 1262 324449-325925(1) | OPEN LINE FROM BUS 324449 [2BOONSBORO N69.000] TO BUS 325925 [4BOONSBORO N138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.64401 | 25.3143
SINGLE OPN LIN 1263 324450-324494(1) | OPEN LINE FROM BUS 324450 [2BOYLE CO 69.000] TO BUS 324494 [2DANVILLE 1 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.3073
SINGLE OPN LIN 1264 324451-324574(1) | OPEN LINE FROM BUS 324451 [2BRECKNRIDGE69.000] TO BUS 324574 [2HILLCREST 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.7774
SINGLE OPN LIN 1265 324451-324673(1) | OPEN LINE FROM BUS 324451 [2BRECKNRIDGE69.000] TO BUS 324673 [2OXMOOR 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.5576
SINGLE OPN LIN 1266 324453-324475(1) | OPEN LINE FROM BUS 324453 [2BEARGRS PMP69.000] TO BUS 324475 [2CLIFTON 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.4452
SINGLE OPN LIN 1267 324455-324966(1) | OPEN LINE FROM BUS 324455 [2BROMLEY 69.000] TO BUS 324966 [2SPARTA KU 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.79789 | 9.437
SINGLE OPN LIN 1268 324456-324465(1) | OPEN LINE FROM BUS 324456 [2BRUSH CREEK69.000] TO BUS 324465 [2CARPENTER T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.9851
SINGLE OPN LIN 1269 324456-324593(1) | OPEN LINE FROM BUS 324456 [2BRUSH CREEK69.000] TO BUS 324593 [2KU PARK 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.9986
SINGLE OPN LIN 1270 324457-324610(1) | OPEN LINE FROM BUS 324457 [2BUCHANAN 69.000] TO BUS 324610 [2LEX PLANT 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.3835
SINGLE OPN LIN 1271 324457-324986(1) | OPEN LINE FROM BUS 324457 [2BUCHANAN 69.000] TO BUS 324986 [2W HIGH T2 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.3694
SINGLE OPN LIN 1272 324458-324501(1) | OPEN LINE FROM BUS 324458 [2BUENA VISTA69.000] TO BUS 324501 [2DIX DAM 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.1655
SINGLE OPN LIN 1273 324458-324546(1) | OPEN LINE FROM BUS 324458 [2BUENA VISTA69.000] TO BUS 324546 [2GARRARD CT 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.1634
SINGLE OPN LIN 1274 324459-324626(1) | OPEN LINE FROM BUS 324459 [2BUSH TAP 69.000] TO BUS 324626 [2MANCHEST SO69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.79598 | 37.1118 | 2 | 8.3
SINGLE OPN LIN 1275 324459-326533(1) | OPEN LINE FROM BUS 324459 [2BUSH TAP 69.000] TO BUS 326533 [2BUSH EKPC 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.25816 | 27.9121 | 1 | 5.967
SINGLE OPN LIN 1276 324460-324686(1) | OPEN LINE FROM BUS 324460 [2CALLOWAY 69.000] TO BUS 324686 [2PINEVILLE 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.93
SINGLE OPN LIN 1277 324460-324706(1) | OPEN LINE FROM BUS 324460 [2CALLOWAY 69.000] TO BUS 324706 [2ROCKY BRNCH69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.6228
SINGLE OPN LIN 1278 324461-324912(1) | OPEN LINE FROM BUS 324461 [2CAMARGO 69.000] TO BUS 324912 [2MT STERL KU69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.4349
SINGLE OPN LIN 1279 324462-324499(1) | OPEN LINE FROM BUS 324462 [2CANAL 69.000] TO BUS 324499 [2DEL PARK 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.7506
SINGLE OPN LIN 1280 324462-324624(1) | OPEN LINE FROM BUS 324462 [2CANAL 69.000] TO BUS 324624 [2MADISON LGE69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.7205
SINGLE OPN LIN 1281 324462-324625(1) | OPEN LINE FROM BUS 324462 [2CANAL 69.000] TO BUS 324625 [2MAGAZINE 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6769
SINGLE OPN LIN 1282 324462-324665(1) | OPEN LINE FROM BUS 324462 [2CANAL 69.000] TO BUS 324665 [2OHIO FALL 169.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.46281 | 24.0893
SINGLE OPN LIN 1283 324462-324666(1) | OPEN LINE FROM BUS 324462 [2CANAL 69.000] TO BUS 324666 [2OHIO FALL 269.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.46276 | 24.425
SINGLE OPN LIN 1284 324464-324615(1) | OPEN LINE FROM BUS 324464 [2CARON 69.000] TO BUS 324615 [2LONDON 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6061
SINGLE OPN LIN 1285 324464-324860(1) | OPEN LINE FROM BUS 324464 [2CARON 69.000] TO BUS 324860 [2FARISTON 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.4529
SINGLE OPN LIN 1286 324465-324784(1) | OPEN LINE FROM BUS 324465 [2CARPENTER T69.000] TO BUS 324784 [2WOFFORD 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.4238
SINGLE OPN LIN 1287 324465-326535(1) | OPEN LINE FROM BUS 324465 [2CARPENTER T69.000] TO BUS 326535 [2CARPENTER 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.72062 | 50.6873 | 1 | 11.7579
SINGLE OPN LIN 1288 324466-324602(1) | OPEN LINE FROM BUS 324466 [2CARROLLTON 69.000] TO BUS 324602 [2LAWRENCE TP69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.38546 | 18.3803
SINGLE OPN LIN 1289 324466-324634(1) | OPEN LINE FROM BUS 324466 [2CARROLLTON 69.000] TO BUS 324634 [2METAL+THERM69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.16546 | 2.9937
SINGLE OPN LIN 1290 324467-324528(1) | OPEN LINE FROM BUS 324467 [2CAVE RUN TP69.000] TO BUS 324528 [2FARMERS 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.4197
SINGLE OPN LIN 1291 324467-324714(1) | OPEN LINE FROM BUS 324467 [2CAVE RUN TP69.000] TO BUS 324714 [2SALT LICK 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.4259
SINGLE OPN LIN 1292 324467-326538(1) | OPEN LINE FROM BUS 324467 [2CAVE RUN TP69.000] TO BUS 326538 [2CAVE RUN 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.16533 | 14.9897 | 1 | 1.4141
SINGLE OPN LIN 1293 324468-324572(1) | OPEN LINE FROM BUS 324468 [2CENTRL CI S69.000] TO BUS 324572 [2HILLSIDE 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.5355
SINGLE OPN LIN 1294 324468-324817(1) | OPEN LINE FROM BUS 324468 [2CENTRL CI S69.000] TO BUS 324817 [2CENTRAL CIT69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14704 | 2.4677
SINGLE OPN LIN 1295 324469-324681(1) | OPEN LINE FROM BUS 324469 [2CENTERFIELD69.000] TO BUS 324681 [2PENAL FARM 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.501
SINGLE OPN LIN 1296 324469-324682(1) | OPEN LINE FROM BUS 324469 [2CENTERFIELD69.000] TO BUS 324682 [2PENAL TAP 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.56404 | 22.9236
SINGLE OPN LIN 1297 324470-324486(1) | OPEN LINE FROM BUS 324470 [2CERRO-SALEM69.000] TO BUS 324486 [2CRITTENDEN 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 3.3545
SINGLE OPN LIN 1298 324470-324948(1) | OPEN LINE FROM BUS 324470 [2CERRO-SALEM69.000] TO BUS 324948 [2SALEM KU 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 3.2909
SINGLE OPN LIN 1299 324471-324777(1) | OPEN LINE FROM BUS 324471 [2CHRISTIAN 69.000] TO BUS 324777 [2WHEATCROFT 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.4095
SINGLE OPN LIN 1300 324471-324822(1) | OPEN LINE FROM BUS 324471 [2CHRISTIAN 69.000] TO BUS 324822 [2CLAY KU 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.4005
SINGLE OPN LIN 1301 324472-324540(1) | OPEN LINE FROM BUS 324472 [2CLARK CO 69.000] TO BUS 324540 [2FOGG PIKE T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 5.1804
SINGLE OPN LIN 1302 324472-324749(1) | OPEN LINE FROM BUS 324472 [2CLARK CO 69.000] TO BUS 324749 [2SYLVANIA 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.7769
SINGLE OPN LIN 1303 324473-324561(1) | OPEN LINE FROM BUS 324473 [2CLAY LGE 69.000] TO BUS 324561 [2HANCOCK 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6551
SINGLE OPN LIN 1304 324473-324570(1) | OPEN LINE FROM BUS 324473 [2CLAY LGE 69.000] TO BUS 324570 [2HIGHLAND 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.5446
SINGLE OPN LIN 1305 324473-324624(1) | OPEN LINE FROM BUS 324473 [2CLAY LGE 69.000] TO BUS 324624 [2MADISON LGE69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6563
SINGLE OPN LIN 1306 324474-324725(1) | OPEN LINE FROM BUS 324474 [2CLAY VILG T69.000] TO BUS 324725 [2SHELBYVIL E69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.6154
SINGLE OPN LIN 1307 324474-324765(1) | OPEN LINE FROM BUS 324474 [2CLAY VILG T69.000] TO BUS 324765 [2W FRANKFORT69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.9672
SINGLE OPN LIN 1308 324475-324574(1) | OPEN LINE FROM BUS 324475 [2CLIFTON 69.000] TO BUS 324574 [2HILLCREST 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.5129
SINGLE OPN LIN 1309 324476-324581(1) | OPEN LINE FROM BUS 324476 [2CMC TAP 69.000] TO BUS 324581 [2HUGHES LANE69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.1667 | 3.541
SINGLE OPN LIN 1310 324476-324680(1) | OPEN LINE FROM BUS 324476 [2CMC TAP 69.000] TO BUS 324680 [2PARIS KU 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.48385 | 20.8072
SINGLE OPN LIN 1311 324477-324502(1) | OPEN LINE FROM BUS 324477 [2CAMP BRECKN69.000] TO BUS 324502 [2DIXON KU 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.7544
SINGLE OPN LIN 1312 324477-324645(1) | OPEN LINE FROM BUS 324477 [2CAMP BRECKN69.000] TO BUS 324645 [2MORGANFIELD69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.325
SINGLE OPN LIN 1313 324478-324516(1) | OPEN LINE FROM BUS 324478 [2CAMPBELBURG69.000] TO BUS 324516 [2EMINENCE KU69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.343
SINGLE OPN LIN 1314 324478-324828(1) | OPEN LINE FROM BUS 324478 [2CAMPBELBURG69.000] TO BUS 324828 [2CAMPBBRG KU69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.5203
SINGLE OPN LIN 1315 324479-324751(1) | OPEN LINE FROM BUS 324479 [2CAMPBELVL T69.000] TO BUS 324751 [2TAYLOR CO 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6515
SINGLE OPN LIN 1316 324479-324889(1) | OPEN LINE FROM BUS 324479 [2CAMPBELVL T69.000] TO BUS 324889 [2LEBANON SO 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.0737
SINGLE OPN LIN 1317 324480-324515(1) | OPEN LINE FROM BUS 324480 [2CMPGND EK T69.000] TO BUS 324515 [2EMANUEL TAP69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.5256
SINGLE OPN LIN 1318 324480-324615(1) | OPEN LINE FROM BUS 324480 [2CMPGND EK T69.000] TO BUS 324615 [2LONDON 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 3.4337
SINGLE OPN LIN 1319 324480-326521(1) | OPEN LINE FROM BUS 324480 [2CMPGND EK T69.000] TO BUS 326521 [2CAMPGRND EK69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.63604 | 46.4787 | 1 | 10.5141
SINGLE OPN LIN 1320 324481-324487(1) | OPEN LINE FROM BUS 324481 [2COLLINS 69.000] TO BUS 324487 [2CRESTWOOD 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.7687
SINGLE OPN LIN 1321 324481-324541(1) | OPEN LINE FROM BUS 324481 [2COLLINS 69.000] TO BUS 324541 [2FORD 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.5412
SINGLE OPN LIN 1322 324482-324748(1) | OPEN LINE FROM BUS 324482 [2CORBIN EAST69.000] TO BUS 324748 [2SWEET HOLLO69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.2749
SINGLE OPN LIN 1323 324482-324832(1) | OPEN LINE FROM BUS 324482 [2CORBIN EAST69.000] TO BUS 324832 [2CORBIN 1 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.382
SINGLE OPN LIN 1324 324484-324571(1) | OPEN LINE FROM BUS 324484 [2CORYDON 69.000] TO BUS 324571 [2HIGHLAND MI69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.3366
SINGLE OPN LIN 1325 324484-324711(1) | OPEN LINE FROM BUS 324484 [2CORYDON 69.000] TO BUS 324711 [2SPEN CHEM T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.4593
SINGLE OPN LIN 1326 324485-324600(1) | OPEN LINE FROM BUS 324485 [2CRAB ORCH T69.000] TO BUS 324600 [2LANCASTR KU69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.35464 | 17.2786
SINGLE OPN LIN 1327 324485-324808(1) | OPEN LINE FROM BUS 324485 [2CRAB ORCH T69.000] TO BUS 324808 [2BRODHEAD KU69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.15272 | 5.4633
SINGLE OPN LIN 1328 324486-324628(1) | OPEN LINE FROM BUS 324486 [2CRITTENDEN 69.000] TO BUS 324628 [2MARION SO 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.9969
SINGLE OPN LIN 1329 324488-324529(1) | OPEN LINE FROM BUS 324488 [2CANE RUN SW69.000] TO BUS 324529 [2FARNSLEY 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.3423
SINGLE OPN LIN 1330 324488-324724(1) | OPEN LINE FROM BUS 324488 [2CANE RUN SW69.000] TO BUS 324724 [2SHIVELY 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.4915
SINGLE OPN LIN 1331 324488-324739(1) | OPEN LINE FROM BUS 324488 [2CANE RUN SW69.000] TO BUS 324739 [2STEWART 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6028
SINGLE OPN LIN 1332 324489-324654(1) | OPEN LINE FROM BUS 324489 [2CUMB FALL T69.000] TO BUS 324654 [2MT VIC EK J69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 3.2254
SINGLE OPN LIN 1333 324489-324784(1) | OPEN LINE FROM BUS 324489 [2CUMB FALL T69.000] TO BUS 324784 [2WOFFORD 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.4007
SINGLE OPN LIN 1334 324489-325034(1) | OPEN LINE FROM BUS 324489 [2CUMB FALL T69.000] TO BUS 325034 [2CUMBER FALL69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.41062 | 35.5982 | 1 | 8.1243
SINGLE OPN LIN 1335 324490-324827(1) | OPEN LINE FROM BUS 324490 [2CUMBERLAND 69.000] TO BUS 324827 [2CLOVERLICK 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.5555
SINGLE OPN LIN 1336 324491-324837(1) | OPEN LINE FROM BUS 324491 [2CYNTHIAN SO69.000] TO BUS 324837 [2CYNTHIAN KU69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.45133 | 4.1932
SINGLE OPN LIN 1337 324491-325085(1) | OPEN LINE FROM BUS 324491 [2CYNTHIAN SO69.000] TO BUS 325085 [2CYNTHI EK T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.66374 | 5.5027
SINGLE OPN LIN 1338 324492-324595(1) | OPEN LINE FROM BUS 324492 [2CYNTHIAN SW69.000] TO BUS 324595 [2KAWNEER 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.5707
SINGLE OPN LIN 1339 324493-324518(1) | OPEN LINE FROM BUS 324493 [2DAHLIA 69.000] TO BUS 324518 [2ETHEL 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.9074
SINGLE OPN LIN 1340 324493-324570(1) | OPEN LINE FROM BUS 324493 [2DAHLIA 69.000] TO BUS 324570 [2HIGHLAND 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.6264
SINGLE OPN LIN 1341 324494-324840(1) | OPEN LINE FROM BUS 324494 [2DANVILLE 1 69.000] TO BUS 324840 [2DANVILLE E 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6481
SINGLE OPN LIN 1342 324495-326579(1) | OPEN LINE FROM BUS 324495 [2DANVILLE N 69.000] TO BUS 326579 [2HARRDSBRG 269.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.1695
SINGLE OPN LIN 1343 324496-324767(1) | OPEN LINE FROM BUS 324496 [2DARK HOLLOW69.000] TO BUS 324767 [2WEST IRVINE69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.9403
SINGLE OPN LIN 1344 324496-324880(1) | OPEN LINE FROM BUS 324496 [2DARK HOLLOW69.000] TO BUS 324880 [2IRVINE 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6337
SINGLE OPN LIN 1345 324497-324564(1) | OPEN LINE FROM BUS 324497 [2DAYHOIT TAP69.000] TO BUS 324564 [2HARLAN WYE 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.4503
SINGLE OPN LIN 1346 324497-324588(1) | OPEN LINE FROM BUS 324497 [2DAYHOIT TAP69.000] TO BUS 324588 [2KENTENIA 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.39
SINGLE OPN LIN 1347 324498-324621(1) | OPEN LINE FROM BUS 324498 [2DAYS BRANCH69.000] TO BUS 324621 [2LYNCH 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.5804
SINGLE OPN LIN 1348 324498-324876(1) | OPEN LINE FROM BUS 324498 [2DAYS BRANCH69.000] TO BUS 324876 [2HOLMES MILL69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6551
SINGLE OPN LIN 1349 324499-324552(1) | OPEN LINE FROM BUS 324499 [2DEL PARK 69.000] TO BUS 324552 [2GRADY 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.7895
SINGLE OPN LIN 1350 324500-324924(1) | OPEN LINE FROM BUS 324500 [2DELAPLAIN T69.000] TO BUS 324924 [2OXFORD 69.000] CKT 1 | TRUE | Met convergence tolerances | 4 | 0.29453 | 18.4481 | 3 | 27.4566
SINGLE OPN LIN 1351 324501-324764(1) | OPEN LINE FROM BUS 324501 [2DIX DAM 69.000] TO BUS 324764 [2WEST CLIFF 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.223
SINGLE OPN LIN 1352 324502-324658(1) | OPEN LINE FROM BUS 324502 [2DIXON KU 69.000] TO BUS 324658 [2NEBO 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.6075
SINGLE OPN LIN 1353 324503-325064(1) | OPEN LINE FROM BUS 324503 [2DORCHESTER 69.000] TO BUS 325064 [2LAUREL GROV69.000] CKT 1 | TRUE | Met convergence tolerances | 6 | 0.52145 | 24.7151 | 5 | 5.56
SINGLE OPN LIN 1354 324504-324662(1) | OPEN LINE FROM BUS 324504 [2E BERNST KU69.000] TO BUS 324662 [2N LONDON KU69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.0319
SINGLE OPN LIN 1355 324504-324927(1) | OPEN LINE FROM BUS 324504 [2E BERNST KU69.000] TO BUS 324927 [2PINE HILL T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.1215
SINGLE OPN LIN 1356 324505-324506(1) | OPEN LINE FROM BUS 324505 [2E DIAMOND 69.000] TO BUS 324506 [2EARLINGTN N69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.7434
SINGLE OPN LIN 1357 324505-324947(1) | OPEN LINE FROM BUS 324505 [2E DIAMOND 69.000] TO BUS 324947 [2RUMSEY 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.5941
SINGLE OPN LIN 1358 324506-324769(1) | OPEN LINE FROM BUS 324506 [2EARLINGTN N69.000] TO BUS 324769 [2WALKER KU 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.7495
SINGLE OPN LIN 1359 324506-324954(1) | OPEN LINE FROM BUS 324506 [2EARLINGTN N69.000] TO BUS 324954 [2SENTRY TAP 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.9566
SINGLE OPN LIN 1360 324507-324769(1) | OPEN LINE FROM BUS 324507 [2EARLINGTON 69.000] TO BUS 324769 [2WALKER KU 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.3704
SINGLE OPN LIN 1361 324507-324850(1) | OPEN LINE FROM BUS 324507 [2EARLINGTON 69.000] TO BUS 324850 [2DOZIER H 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.712
SINGLE OPN LIN 1362 324508-324617(1) | OPEN LINE FROM BUS 324508 [2EASTLAND 69.000] TO BUS 324617 [2LOUDON 618 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.0322
SINGLE OPN LIN 1363 324509-324914(1) | OPEN LINE FROM BUS 324509 [2EASTVIEW 69.000] TO BUS 324914 [2M-V CLARK T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.5702
SINGLE OPN LIN 1364 324510-324729(1) | OPEN LINE FROM BUS 324510 [2EASTWOOD 69.000] TO BUS 324729 [2SIMPSONVILL69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.8776
SINGLE OPN LIN 1365 324511-324584(1) | OPEN LINE FROM BUS 324511 [2ECHOLS 69.000] TO BUS 324584 [2INDIAN HILL69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.7792
SINGLE OPN LIN 1366 324511-324959(1) | OPEN LINE FROM BUS 324511 [2ECHOLS 69.000] TO BUS 324959 [2SIMMONS 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.795
SINGLE OPN LIN 1367 324512-324693(1) | OPEN LINE FROM BUS 324512 [2EDDYV PR TP69.000] TO BUS 324693 [2PRINCETON 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.9317
SINGLE OPN LIN 1368 324513-324693(1) | OPEN LINE FROM BUS 324513 [2EDDYVILLE 69.000] TO BUS 324693 [2PRINCETON 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6216
SINGLE OPN LIN 1369 324513-324885(1) | OPEN LINE FROM BUS 324513 [2EDDYVILLE 69.000] TO BUS 324885 [2KUTTAWA 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.3064
SINGLE OPN LIN 1370 324514-324531(1) | OPEN LINE FROM BUS 324514 [2ELIHU 69.000] TO BUS 324531 [2FERGUSON SO69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.0116
SINGLE OPN LIN 1371 324514-324654(1) | OPEN LINE FROM BUS 324514 [2ELIHU 69.000] TO BUS 324654 [2MT VIC EK J69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 3.6545
SINGLE OPN LIN 1372 324514-324962(1) | OPEN LINE FROM BUS 324514 [2ELIHU 69.000] TO BUS 324962 [2SOMERSET 1 69.000] CKT 1 | TRUE | Met convergence tolerances | 4 | 0.14287 | 9.8475 | 4 | 14.55
SINGLE OPN LIN 1373 324515-326530(1) | OPEN LINE FROM BUS 324515 [2EMANUEL TAP69.000] TO BUS 326530 [2EMANUEL 69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.94132 | 61.6989 | 2 | 14.3956
SINGLE OPN LIN 1374 324516-324585(1) | OPEN LINE FROM BUS 324516 [2EMINENCE KU69.000] TO BUS 324585 [2JERICHO 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.9977
SINGLE OPN LIN 1375 324516-324727(1) | OPEN LINE FROM BUS 324516 [2EMINENCE KU69.000] TO BUS 324727 [2SHELBYVILLE69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.8179
SINGLE OPN LIN 1376 324517-325005(1) | OPEN LINE FROM BUS 324517 [2ESSERVILLE 69.000] TO BUS 325005 [2WISE TAP 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.85
SINGLE OPN LIN 1377 324518-324657(1) | OPEN LINE FROM BUS 324518 [2ETHEL 69.000] TO BUS 324657 [2NACHAND 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.4443
SINGLE OPN LIN 1378 324519-324520(1) | OPEN LINE FROM BUS 324519 [2ETOWN KU 69.000] TO BUS 324520 [2ETOWN 2 TAP69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.4038
SINGLE OPN LIN 1379 324519-324521(1) | OPEN LINE FROM BUS 324519 [2ETOWN KU 69.000] TO BUS 324521 [2ETOWN 4 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.39998 | 18.0172
SINGLE OPN LIN 1380 324519-324563(1) | OPEN LINE FROM BUS 324519 [2ETOWN KU 69.000] TO BUS 324563 [2HARDIN CO 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.33811 | 3.2177
SINGLE OPN LIN 1381 324519-324563(2) | OPEN LINE FROM BUS 324519 [2ETOWN KU 69.000] TO BUS 324563 [2HARDIN CO 69.000] CKT 2 | TRUE | Met convergence tolerances | 0 | 0.33811 | 3.2177
SINGLE OPN LIN 1382 324520-326555(1) | OPEN LINE FROM BUS 324520 [2ETOWN 2 TAP69.000] TO BUS 326555 [2RINEYVIL RD69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.3959
SINGLE OPN LIN 1383 324521-324575(1) | OPEN LINE FROM BUS 324521 [2ETOWN 4 69.000] TO BUS 324575 [2HODGENV KU 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.17186 | 2.9766
SINGLE OPN LIN 1384 324522-324523(1) | OPEN LINE FROM BUS 324522 [2EVARTS TAP 69.000] TO BUS 324523 [2EVARTS 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 4.0303
SINGLE OPN LIN 1385 324522-324692(1) | OPEN LINE FROM BUS 324522 [2EVARTS TAP 69.000] TO BUS 324692 [2POWELL MTN 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.5604
SINGLE OPN LIN 1386 324522-324761(1) | OPEN LINE FROM BUS 324522 [2EVARTS TAP 69.000] TO BUS 324761 [2VERDA 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.3404
SINGLE OPN LIN 1387 324523-324798(1) | OPEN LINE FROM BUS 324523 [2EVARTS 69.000] TO BUS 324798 [2BAILEY CRK 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.9554
SINGLE OPN LIN 1388 324524-325009(1) | OPEN LINE FROM BUS 324524 [2EWINGTON 69.000] TO BUS 325009 [2SPENCER A 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.20975 | 13.6555 | 1 | 20.32
SINGLE OPN LIN 1389 324525-324974(1) | OPEN LINE FROM BUS 324525 [2FAIRFIELD 69.000] TO BUS 324974 [2TAYLRV EK T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.8156
SINGLE OPN LIN 1390 324526-324730(1) | OPEN LINE FROM BUS 324526 [2FAIRMOUNT 269.000] TO BUS 324730 [2SMYRNA 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.23864 | 15.2067 | 1 | 23.62
SINGLE OPN LIN 1391 324527-324704(1) | OPEN LINE FROM BUS 324527 [2FARLEY KU 69.000] TO BUS 324704 [2ROCKHOLD 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.5539
SINGLE OPN LIN 1392 324527-324758(1) | OPEN LINE FROM BUS 324527 [2FARLEY KU 69.000] TO BUS 324758 [2US STEEL 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.57173 | 23.0681
SINGLE OPN LIN 1393 324528-324647(1) | OPEN LINE FROM BUS 324528 [2FARMERS 69.000] TO BUS 324647 [2MOREHEAD W 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.4335
SINGLE OPN LIN 1394 324529-324675(1) | OPEN LINE FROM BUS 324529 [2FARNSLEY 69.000] TO BUS 324675 [2PADDYS RUN 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.4255
SINGLE OPN LIN 1395 324529-324724(1) | OPEN LINE FROM BUS 324529 [2FARNSLEY 69.000] TO BUS 324724 [2SHIVELY 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.3852
SINGLE OPN LIN 1396 324530-324701(1) | OPEN LINE FROM BUS 324530 [2FAWKES 69.000] TO BUS 324701 [2RICHMND 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6453
SINGLE OPN LIN 1397 324533-324535(1) | OPEN LINE FROM BUS 324533 [2FRANKFORT 169.000] TO BUS 324535 [2E FRANKFORT69.000] CKT 1 | TRUE | Met convergence tolerances | 6 | 0.14287 | 9.9005 | 3 | 14.48
SINGLE OPN LIN 1398 324534-324535(1) | OPEN LINE FROM BUS 324534 [2FRANKFORT 269.000] TO BUS 324535 [2E FRANKFORT69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.5103
SINGLE OPN LIN 1399 324534-324762(1) | OPEN LINE FROM BUS 324534 [2FRANKFORT 269.000] TO BUS 324762 [2VERSAIL W T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6114
SINGLE OPN LIN 1400 324535-326528(1) | OPEN LINE FROM BUS 324535 [2E FRANKFORT69.000] TO BUS 326528 [2BRIDGEPORT 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.3067
SINGLE OPN LIN 1401 324536-324653(1) | OPEN LINE FROM BUS 324536 [2FINCHVILLE 69.000] TO BUS 324653 [2M-V SIMPSON69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.9289
SINGLE OPN LIN 1402 324536-324718(1) | OPEN LINE FROM BUS 324536 [2FINCHVILLE 69.000] TO BUS 324718 [2SHELBY CO T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.9829
SINGLE OPN LIN 1403 324536-324752(1) | OPEN LINE FROM BUS 324536 [2FINCHVILLE 69.000] TO BUS 324752 [2TAYLORSV KU69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.8259
SINGLE OPN LIN 1404 324537-324620(1) | OPEN LINE FROM BUS 324537 [2FLA TILE T269.000] TO BUS 324620 [2LAWRENCEBRG69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.1908
SINGLE OPN LIN 1405 324537-324755(1) | OPEN LINE FROM BUS 324537 [2FLA TILE T269.000] TO BUS 324755 [2TYRONE 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.2018
SINGLE OPN LIN 1406 324538-324561(1) | OPEN LINE FROM BUS 324538 [2FLOYD 69.000] TO BUS 324561 [2HANCOCK 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.3905
SINGLE OPN LIN 1407 324538-324614(1) | OPEN LINE FROM BUS 324538 [2FLOYD 69.000] TO BUS 324614 [2LOCUST TAP 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.1362
SINGLE OPN LIN 1408 324539-324601(1) | OPEN LINE FROM BUS 324539 [2FMC 69.000] TO BUS 324601 [2LANSDOWNE 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.0644
SINGLE OPN LIN 1409 324539-324613(1) | OPEN LINE FROM BUS 324539 [2FMC 69.000] TO BUS 324613 [2LK SHORE TP69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.1335
SINGLE OPN LIN 1410 324540-324912(1) | OPEN LINE FROM BUS 324540 [2FOGG PIKE T69.000] TO BUS 324912 [2MT STERL KU69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 5.0298
SINGLE OPN LIN 1411 324541-324637(1) | OPEN LINE FROM BUS 324541 [2FORD 69.000] TO BUS 324637 [2MIDDLETOWN 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.0661
SINGLE OPN LIN 1412 324542-324588(1) | OPEN LINE FROM BUS 324542 [2FORESTER CR69.000] TO BUS 324588 [2KENTENIA 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.3604
SINGLE OPN LIN 1413 324542-324706(1) | OPEN LINE FROM BUS 324542 [2FORESTER CR69.000] TO BUS 324706 [2ROCKY BRNCH69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.362
SINGLE OPN LIN 1414 324543-324686(1) | OPEN LINE FROM BUS 324543 [2FOUR MILE 69.000] TO BUS 324686 [2PINEVILLE 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.1438
SINGLE OPN LIN 1415 324543-324813(1) | OPEN LINE FROM BUS 324543 [2FOUR MILE 69.000] TO BUS 324813 [2CARY 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.0798
SINGLE OPN LIN 1416 324544-324693(1) | OPEN LINE FROM BUS 324544 [2FREDONIA QU69.000] TO BUS 324693 [2PRINCETON 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.3441
SINGLE OPN LIN 1417 324544-324865(1) | OPEN LINE FROM BUS 324544 [2FREDONIA QU69.000] TO BUS 324865 [2FREDONIA 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.6764
SINGLE OPN LIN 1418 324545-324623(1) | OPEN LINE FROM BUS 324545 [2FREYS HILL 69.000] TO BUS 324623 [2LYNDON 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.3001
SINGLE OPN LIN 1419 324546-324600(1) | OPEN LINE FROM BUS 324546 [2GARRARD CT 69.000] TO BUS 324600 [2LANCASTR KU69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.162
SINGLE OPN LIN 1420 324547-324890(1) | OPEN LINE FROM BUS 324547 [2GEORGETOWN 69.000] TO BUS 324890 [2LEMONS MILL69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.2603
SINGLE OPN LIN 1421 324549-324583(1) | OPEN LINE FROM BUS 324549 [2GORGE 69.000] TO BUS 324583 [2IMBODEN 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.3569
SINGLE OPN LIN 1422 324549-324894(1) | OPEN LINE FROM BUS 324549 [2GORGE 69.000] TO BUS 324894 [2E STONE G T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6438
SINGLE OPN LIN 1423 324550-324652(1) | OPEN LINE FROM BUS 324550 [2GREEN RIVER69.000] TO BUS 324652 [2MUHLENBRG P69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6187
SINGLE OPN LIN 1424 324550-324709(1) | OPEN LINE FROM BUS 324550 [2GREEN RIVER69.000] TO BUS 324709 [2RVR QUEEN T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.6669
SINGLE OPN LIN 1425 324550-324723(1) | OPEN LINE FROM BUS 324550 [2GREEN RIVER69.000] TO BUS 324723 [2SHAVER CHAP69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.30403 | 5.5159
SINGLE OPN LIN 1426 324550-325082(1) | OPEN LINE FROM BUS 324550 [2GREEN RIVER69.000] TO BUS 325082 [2ARMSTR BREC69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 1.4377 | 1 | 3.51
SINGLE OPN LIN 1427 324550-326513(1) | OPEN LINE FROM BUS 324550 [2GREEN RIVER69.000] TO BUS 326513 [2EQAL M BREC69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.3443
SINGLE OPN LIN 1428 324551-324786(1) | OPEN LINE FROM BUS 324551 [2GR RVR STL 69.000] TO BUS 324786 [2ZION 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 3.7948
SINGLE OPN LIN 1429 324551-324947(1) | OPEN LINE FROM BUS 324551 [2GR RVR STL 69.000] TO BUS 324947 [2RUMSEY 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.1427 | 4.0121
SINGLE OPN LIN 1430 324552-324675(1) | OPEN LINE FROM BUS 324552 [2GRADY 69.000] TO BUS 324675 [2PADDYS RUN 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.7099
SINGLE OPN LIN 1431 324553-324864(1) | OPEN LINE FROM BUS 324553 [2GRAHAMVILLE69.000] TO BUS 324864 [2FORRESTDALE69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.3827
SINGLE OPN LIN 1432 324554-324830(1) | OPEN LINE FROM BUS 324554 [2GRENSBRG KU69.000] TO BUS 324830 [2CAMPBELV EK69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.5584
SINGLE OPN LIN 1433 324555-324716(1) | OPEN LINE FROM BUS 324555 [2VA CTY REAC69.000] TO BUS 324716 [2SANDY RIDGE69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 3.9659
SINGLE OPN LIN 1434 324555-324759(1) | OPEN LINE FROM BUS 324555 [2VA CTY REAC69.000] TO BUS 324759 [2VIRGINIA CI69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 3.9014
SINGLE OPN LIN 1435 324556-324702(1) | OPEN LINE FROM BUS 324556 [2GREENV W TP69.000] TO BUS 324702 [2RIVER QUEEN69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.7713
SINGLE OPN LIN 1436 324556-324870(1) | OPEN LINE FROM BUS 324556 [2GREENV W TP69.000] TO BUS 324870 [2GREENVILLE 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.3632
SINGLE OPN LIN 1437 324556-326593(1) | OPEN LINE FROM BUS 324556 [2GREENV W TP69.000] TO BUS 326593 [2GREENVIL N 69.000] CKT 1 | TRUE | Met convergence tolerances | 3 | 0.14522 | 10.4682 | 3 | 16.31
SINGLE OPN LIN 1438 324557-324829(1) | OPEN LINE FROM BUS 324557 [2GR RVR PLAZ69.000] TO BUS 324829 [2CAMPBELVIL169.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.8717
SINGLE OPN LIN 1439 324557-324830(1) | OPEN LINE FROM BUS 324557 [2GR RVR PLAZ69.000] TO BUS 324830 [2CAMPBELV EK69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.9522
SINGLE OPN LIN 1440 324558-324734(1) | OPEN LINE FROM BUS 324558 [2HAEFLING 69.000] TO BUS 324734 [2SPINDLETP T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.8289
SINGLE OPN LIN 1441 324558-324766(1) | OPEN LINE FROM BUS 324558 [2HAEFLING 69.000] TO BUS 324766 [2W HIGH T1 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.5591
SINGLE OPN LIN 1442 324559-324797(1) | OPEN LINE FROM BUS 324559 [2HALEY 69.000] TO BUS 324797 [2AVON T1 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.774
SINGLE OPN LIN 1443 324559-326586(1) | OPEN LINE FROM BUS 324559 [2HALEY 69.000] TO BUS 326586 [2HUME RD TAP69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.5877
SINGLE OPN LIN 1444 324560-324689(1) | OPEN LINE FROM BUS 324560 [2HAMBLIN TAP69.000] TO BUS 324689 [2POCKET 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 3.8263
SINGLE OPN LIN 1445 324560-324815(1) | OPEN LINE FROM BUS 324560 [2HAMBLIN TAP69.000] TO BUS 324815 [2CAWOOD 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.9543
SINGLE OPN LIN 1446 324560-325041(1) | OPEN LINE FROM BUS 324560 [2HAMBLIN TAP69.000] TO BUS 325041 [2STONE TVA 69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.62292 | 29.2999 | 1 | 6.81
SINGLE OPN LIN 1447 324562-324564(1) | OPEN LINE FROM BUS 324562 [2HARLAN KU 69.000] TO BUS 324564 [2HARLAN WYE 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6925
SINGLE OPN LIN 1448 324563-324731(1) | OPEN LINE FROM BUS 324563 [2HARDIN CO 69.000] TO BUS 324731 [2SONORA TAP 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.5067
SINGLE OPN LIN 1449 324565-324566(1) | OPEN LINE FROM BUS 324565 [7NAS TAP 345.00] TO BUS 324566 [7NAS 222 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.2542
SINGLE OPN LIN 1450 324567-324780(1) | OPEN LINE FROM BUS 324567 [2HIGBY MIL 269.000] TO BUS 324780 [2WIL DOWN T169.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.5985
SINGLE OPN LIN 1451 324568-324569(1) | OPEN LINE FROM BUS 324568 [2HIGBY 618 69.000] TO BUS 324569 [2HIGBY 608 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.3519
SINGLE OPN LIN 1452 324568-324713(1) | OPEN LINE FROM BUS 324568 [2HIGBY 618 69.000] TO BUS 324713 [2SO ELKHORN 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.1129
SINGLE OPN LIN 1453 324568-324742(1) | OPEN LINE FROM BUS 324568 [2HIGBY 618 69.000] TO BUS 324742 [2STONEWALL T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.18806 | 3.8628
SINGLE OPN LIN 1454 324569-324632(1) | OPEN LINE FROM BUS 324569 [2HIGBY 608 69.000] TO BUS 324632 [2UK MED CENT69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.5644
SINGLE OPN LIN 1455 324571-324671(1) | OPEN LINE FROM BUS 324571 [2HIGHLAND MI69.000] TO BUS 324671 [2OVERLAD S T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.3325
SINGLE OPN LIN 1456 324572-324691(1) | OPEN LINE FROM BUS 324572 [2HILLSIDE 69.000] TO BUS 324691 [2POWDERLY 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.5639
SINGLE OPN LIN 1457 324573-324741(1) | OPEN LINE FROM BUS 324573 [2HINKLE 69.000] TO BUS 324741 [2STINKIN CRK69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.7357
SINGLE OPN LIN 1458 324576-324748(1) | OPEN LINE FROM BUS 324576 [2HOPEWELL 69.000] TO BUS 324748 [2SWEET HOLLO69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.9386
SINGLE OPN LIN 1459 324577-324693(1) | OPEN LINE FROM BUS 324577 [2HARDESTY A 69.000] TO BUS 324693 [2PRINCETON 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.4921
SINGLE OPN LIN 1460 324577-324769(1) | OPEN LINE FROM BUS 324577 [2HARDESTY A 69.000] TO BUS 324769 [2WALKER KU 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.4908
SINGLE OPN LIN 1461 324578-324690(1) | OPEN LINE FROM BUS 324578 [2HARDESTY B 69.000] TO BUS 324690 [2DAWSON TAP 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.5661
SINGLE OPN LIN 1462 324578-324769(1) | OPEN LINE FROM BUS 324578 [2HARDESTY B 69.000] TO BUS 324769 [2WALKER KU 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6136
SINGLE OPN LIN 1463 324579-324580(1) | OPEN LINE FROM BUS 324579 [2HARMNY LAND69.000] TO BUS 324580 [2HARRODS CRK69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.2577
SINGLE OPN LIN 1464 324579-324960(1) | OPEN LINE FROM BUS 324579 [2HARMNY LAND69.000] TO BUS 324960 [2SKYLIGHT 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.7291
SINGLE OPN LIN 1465 324580-324750(1) | OPEN LINE FROM BUS 324580 [2HARRODS CRK69.000] TO BUS 324750 [2TAYLOR LG 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.42185 | 19.2707
SINGLE OPN LIN 1466 324580-324785(1) | OPEN LINE FROM BUS 324580 [2HARRODS CRK69.000] TO BUS 324785 [2WORTHINGTON69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.5428
SINGLE OPN LIN 1467 324581-324586(1) | OPEN LINE FROM BUS 324581 [2HUGHES LANE69.000] TO BUS 324586 [2JOYLAND 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.9005
SINGLE OPN LIN 1468 324582-324610(1) | OPEN LINE FROM BUS 324582 [2IBM 69.000] TO BUS 324610 [2LEX PLANT 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.4606
SINGLE OPN LIN 1469 324582-324879(1) | OPEN LINE FROM BUS 324582 [2IBM 69.000] TO BUS 324879 [2IBM 998 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.602
SINGLE OPN LIN 1470 324583-324591(1) | OPEN LINE FROM BUS 324583 [2IMBODEN 69.000] TO BUS 324591 [2KEOKEE TAP 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.2361
SINGLE OPN LIN 1471 324584-324659(1) | OPEN LINE FROM BUS 324584 [2INDIAN HILL69.000] TO BUS 324659 [2NELSON 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.3389
SINGLE OPN LIN 1472 324585-324598(1) | OPEN LINE FROM BUS 324585 [2JERICHO 69.000] TO BUS 324598 [2LA GRANGE E69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.8468
SINGLE OPN LIN 1473 324586-324610(1) | OPEN LINE FROM BUS 324586 [2JOYLAND 69.000] TO BUS 324610 [2LEX PLANT 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.5689
SINGLE OPN LIN 1474 324587-324702(1) | OPEN LINE FROM BUS 324587 [2KEN AMERICA69.000] TO BUS 324702 [2RIVER QUEEN69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.2962
SINGLE OPN LIN 1475 324587-324709(1) | OPEN LINE FROM BUS 324587 [2KEN AMERICA69.000] TO BUS 324709 [2RVR QUEEN T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.2924
SINGLE OPN LIN 1476 324589-324722(1) | OPEN LINE FROM BUS 324589 [2KENTON 688 69.000] TO BUS 324722 [2SHARON KU 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.143 | 2.1565
SINGLE OPN LIN 1477 324589-324899(1) | OPEN LINE FROM BUS 324589 [2KENTON 688 69.000] TO BUS 324899 [2MAYSVILLE E69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.62148 | 28.7237 | 2 | 6.8
SINGLE OPN LIN 1478 324589-325019(1) | OPEN LINE FROM BUS 324589 [2KENTON 688 69.000] TO BUS 325019 [2KENTON-6 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 4.1783
SINGLE OPN LIN 1479 324590-324719(1) | OPEN LINE FROM BUS 324590 [2KENWOOD 69.000] TO BUS 324719 [2SEMINOLE 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.7399
SINGLE OPN LIN 1480 324590-325023(1) | OPEN LINE FROM BUS 324590 [2KENWOOD 69.000] TO BUS 325023 [2ASHBOT EAST69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.788
SINGLE OPN LIN 1481 324591-324592(1) | OPEN LINE FROM BUS 324591 [2KEOKEE TAP 69.000] TO BUS 324592 [2KEOKEE TVA 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.2344
SINGLE OPN LIN 1482 324592-324689(1) | OPEN LINE FROM BUS 324592 [2KEOKEE TVA 69.000] TO BUS 324689 [2POCKET 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.4475
SINGLE OPN LIN 1483 324593-324686(1) | OPEN LINE FROM BUS 324593 [2KU PARK 69.000] TO BUS 324686 [2PINEVILLE 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.4698 | 20.1894
SINGLE OPN LIN 1484 324593-324741(1) | OPEN LINE FROM BUS 324593 [2KU PARK 69.000] TO BUS 324741 [2STINKIN CRK69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.0631
SINGLE OPN LIN 1485 324595-324837(1) | OPEN LINE FROM BUS 324595 [2KAWNEER 69.000] TO BUS 324837 [2CYNTHIAN KU69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.3118
SINGLE OPN LIN 1486 324597-324764(1) | OPEN LINE FROM BUS 324597 [2KY ST HOSP 69.000] TO BUS 324764 [2WEST CLIFF 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.042
SINGLE OPN LIN 1487 324597-324840(1) | OPEN LINE FROM BUS 324597 [2KY ST HOSP 69.000] TO BUS 324840 [2DANVILLE E 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.8574
SINGLE OPN LIN 1488 324598-324682(1) | OPEN LINE FROM BUS 324598 [2LA GRANGE E69.000] TO BUS 324682 [2PENAL TAP 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.47062 | 19.9555
SINGLE OPN LIN 1489 324599-324600(1) | OPEN LINE FROM BUS 324599 [2LANCASTER 269.000] TO BUS 324600 [2LANCASTR KU69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.1815
SINGLE OPN LIN 1490 324599-324971(1) | OPEN LINE FROM BUS 324599 [2LANCASTER 269.000] TO BUS 324971 [2STANFORD NO69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.1787
SINGLE OPN LIN 1491 324601-324650(1) | OPEN LINE FROM BUS 324601 [2LANSDOWNE 69.000] TO BUS 324650 [2MT TBR T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.0355
SINGLE OPN LIN 1492 324601-324780(1) | OPEN LINE FROM BUS 324601 [2LANSDOWNE 69.000] TO BUS 324780 [2WIL DOWN T169.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.4112
SINGLE OPN LIN 1493 324602-324828(1) | OPEN LINE FROM BUS 324602 [2LAWRENCE TP69.000] TO BUS 324828 [2CAMPBBRG KU69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.38273 | 18.3705
SINGLE OPN LIN 1494 324602-324888(1) | OPEN LINE FROM BUS 324602 [2LAWRENCE TP69.000] TO BUS 324888 [2LAWRENCE 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 2.95 | 1 | 0.32
SINGLE OPN LIN 1495 324603-324605(1) | OPEN LINE FROM BUS 324603 [2LEBANON CIT69.000] TO BUS 324605 [2LEBANON EK 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.8799
SINGLE OPN LIN 1496 324604-324606(1) | OPEN LINE FROM BUS 324604 [2LEBANON IND69.000] TO BUS 324606 [2LEBANON 69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.1532 | 10.8498 | 2 | 16.46
SINGLE OPN LIN 1497 324604-325020(1) | OPEN LINE FROM BUS 324604 [2LEBANON IND69.000] TO BUS 325020 [2LEBANON E 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 9.4318 | 1 | 14.02
SINGLE OPN LIN 1498 324605-324889(1) | OPEN LINE FROM BUS 324605 [2LEBANON EK 69.000] TO BUS 324889 [2LEBANON SO 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6596
SINGLE OPN LIN 1499 324606-324736(1) | OPEN LINE FROM BUS 324606 [2LEBANON 69.000] TO BUS 324736 [2SPRINGFL KU69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.40283 | 18.9085
SINGLE OPN LIN 1500 324607-324608(1) | OPEN LINE FROM BUS 324607 [2LEITCHF CIT69.000] TO BUS 324608 [2LEITCHF E 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.24175 | 3.0708
SINGLE OPN LIN 1501 324607-324609(1) | OPEN LINE FROM BUS 324607 [2LEITCHF CIT69.000] TO BUS 324609 [2LEITCHFIELD69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.2598 | 3.4786
SINGLE OPN LIN 1502 324608-324992(1) | OPEN LINE FROM BUS 324608 [2LEITCHF E 69.000] TO BUS 324992 [2WARREN TIE 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.5046
SINGLE OPN LIN 1503 324609-324643(1) | OPEN LINE FROM BUS 324609 [2LEITCHFIELD69.000] TO BUS 324643 [2MILL WOOD 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.20532 | 15.5326
SINGLE OPN LIN 1504 324609-325040(1) | OPEN LINE FROM BUS 324609 [2LEITCHFIELD69.000] TO BUS 325040 [2LEITCHF TVA69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.3095
SINGLE OPN LIN 1505 324609-325040(2) | OPEN LINE FROM BUS 324609 [2LEITCHFIELD69.000] TO BUS 325040 [2LEITCHF TVA69.000] CKT 2 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.3095
SINGLE OPN LIN 1506 324610-324617(1) | OPEN LINE FROM BUS 324610 [2LEX PLANT 69.000] TO BUS 324617 [2LOUDON 618 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.4486
SINGLE OPN LIN 1507 324610-324674(1) | OPEN LINE FROM BUS 324610 [2LEX PLANT 69.000] TO BUS 324674 [2PROC & GAMB69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.3424
SINGLE OPN LIN 1508 324611-324618(1) | OPEN LINE FROM BUS 324611 [2LIBERTY RD 69.000] TO BUS 324618 [2LOUDON 628 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.4301
SINGLE OPN LIN 1509 324611-324891(1) | OPEN LINE FROM BUS 324611 [2LIBERTY RD 69.000] TO BUS 324891 [2LEX WATER 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.5041
SINGLE OPN LIN 1510 324612-324701(1) | OPEN LINE FROM BUS 324612 [2LAKE REBA 69.000] TO BUS 324701 [2RICHMND 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.3389
SINGLE OPN LIN 1511 324612-324768(1) | OPEN LINE FROM BUS 324612 [2LAKE REBA 69.000] TO BUS 324768 [2WACO 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.4523
SINGLE OPN LIN 1512 324613-324618(1) | OPEN LINE FROM BUS 324613 [2LK SHORE TP69.000] TO BUS 324618 [2LOUDON 628 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.5213
SINGLE OPN LIN 1513 324613-325059(1) | OPEN LINE FROM BUS 324613 [2LK SHORE TP69.000] TO BUS 325059 [2BRYANT RD T69.000] CKT 1 | TRUE | Met convergence tolerances | 3 | 0.7471 | 42.2693 | 2 | 66.56
SINGLE OPN LIN 1514 324614-324719(1) | OPEN LINE FROM BUS 324614 [2LOCUST TAP 69.000] TO BUS 324719 [2SEMINOLE 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.4975
SINGLE OPN LIN 1515 324614-326545(1) | OPEN LINE FROM BUS 324614 [2LOCUST TAP 69.000] TO BUS 326545 [2LOCUST LGE 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.20131 | 13.2866 | 1 | 20.82
SINGLE OPN LIN 1516 324615-324688(1) | OPEN LINE FROM BUS 324615 [2LONDON 69.000] TO BUS 324688 [2PITTSBRG KU69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.37847 | 18.5555
SINGLE OPN LIN 1517 324616-324775(1) | OPEN LINE FROM BUS 324616 [2LONG RUN 69.000] TO BUS 324775 [2WHAS 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.4415
SINGLE OPN LIN 1518 324617-324618(1) | OPEN LINE FROM BUS 324617 [2LOUDON 618 69.000] TO BUS 324618 [2LOUDON 628 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.3117
SINGLE OPN LIN 1519 324618-326586(1) | OPEN LINE FROM BUS 324618 [2LOUDON 628 69.000] TO BUS 326586 [2HUME RD TAP69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.0548
SINGLE OPN LIN 1520 324619-324998(1) | OPEN LINE FROM BUS 324619 [2LOWER MIL C69.000] TO BUS 324998 [2WEST CO 2 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.5107
SINGLE OPN LIN 1521 324621-326523(1) | OPEN LINE FROM BUS 324621 [2LYNCH 69.000] TO BUS 326523 [2ARKLAND JCT69.000] CKT 1 | TRUE | Met convergence tolerances | 3 | 0.14292 | 10.4193 | 2 | 14.8183
SINGLE OPN LIN 1522 324622-324637(1) | OPEN LINE FROM BUS 324622 [2LYNDON SO 69.000] TO BUS 324637 [2MIDDLETOWN 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 3.036
SINGLE OPN LIN 1523 324622-324673(1) | OPEN LINE FROM BUS 324622 [2LYNDON SO 69.000] TO BUS 324673 [2OXMOOR 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.4073
SINGLE OPN LIN 1524 324623-324637(1) | OPEN LINE FROM BUS 324623 [2LYNDON 69.000] TO BUS 324637 [2MIDDLETOWN 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 3.3193
SINGLE OPN LIN 1525 324626-324627(1) | OPEN LINE FROM BUS 324626 [2MANCHEST SO69.000] TO BUS 324627 [2MANCHEST KU69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.40725 | 19.1952 | 1 | 3.54
SINGLE OPN LIN 1526 324628-324629(1) | OPEN LINE FROM BUS 324628 [2MARION SO 69.000] TO BUS 324629 [2MARION KU 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.4973
SINGLE OPN LIN 1527 324629-324904(1) | OPEN LINE FROM BUS 324629 [2MARION KU 69.000] TO BUS 324904 [2MEXICO KU 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 3.3224
SINGLE OPN LIN 1528 324630-324862(1) | OPEN LINE FROM BUS 324630 [2MADSNV LP E69.000] TO BUS 324862 [2FIES CITY 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.5825
SINGLE OPN LIN 1529 324631-324658(1) | OPEN LINE FROM BUS 324631 [2MADSNV LP W69.000] TO BUS 324658 [2NEBO 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.3631
SINGLE OPN LIN 1530 324633-324636(1) | OPEN LINE FROM BUS 324633 [2MELDRUM 69.000] TO BUS 324636 [2MIDDLESBORO69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.4753
SINGLE OPN LIN 1531 324633-324684(1) | OPEN LINE FROM BUS 324633 [2MELDRUM 69.000] TO BUS 324684 [2PINEVIL 72269.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6499
SINGLE OPN LIN 1532 324634-324849(1) | OPEN LINE FROM BUS 324634 [2METAL+THERM69.000] TO BUS 324849 [2DOW CORNING69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.6515
SINGLE OPN LIN 1533 324636-324874(1) | OPEN LINE FROM BUS 324636 [2MIDDLESBORO69.000] TO BUS 324874 [2HARROGATE 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.20414 | 15.8623 | 1 | 2.06
SINGLE OPN LIN 1534 324637-324653(1) | OPEN LINE FROM BUS 324637 [2MIDDLETOWN 69.000] TO BUS 324653 [2M-V SIMPSON69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.9411
SINGLE OPN LIN 1535 324638-324706(1) | OPEN LINE FROM BUS 324638 [2MILL CRK KU69.000] TO BUS 324706 [2ROCKY BRNCH69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.2873
SINGLE OPN LIN 1536 324638-324813(1) | OPEN LINE FROM BUS 324638 [2MILL CRK KU69.000] TO BUS 324813 [2CARY 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.6302
SINGLE OPN LIN 1537 324639-324642(1) | OPEN LINE FROM BUS 324639 [2MILLRSB624 69.000] TO BUS 324642 [2MILLERSBURG69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.50395 | 4.8241
SINGLE OPN LIN 1538 324639-324812(1) | OPEN LINE FROM BUS 324639 [2MILLRSB624 69.000] TO BUS 324812 [2CARLISLE 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.6164 | 28.5027 | 1 | 6.61
SINGLE OPN LIN 1539 324639-325035(1) | OPEN LINE FROM BUS 324639 [2MILLRSB624 69.000] TO BUS 325035 [2BLUE SOL TP69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.66326 | 5.5081
SINGLE OPN LIN 1540 324641-324751(1) | OPEN LINE FROM BUS 324641 [2MILE LAN TP69.000] TO BUS 324751 [2TAYLOR CO 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.6848
SINGLE OPN LIN 1541 324641-324829(1) | OPEN LINE FROM BUS 324641 [2MILE LAN TP69.000] TO BUS 324829 [2CAMPBELVIL169.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.7315
SINGLE OPN LIN 1542 324641-326970(1) | OPEN LINE FROM BUS 324641 [2MILE LAN TP69.000] TO BUS 326970 [2MILE LAN EK69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.53934 | 41.8083 | 1 | 9.7611
SINGLE OPN LIN 1543 324642-324677(1) | OPEN LINE FROM BUS 324642 [2MILLERSBURG69.000] TO BUS 324677 [2PARIS 12 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.3648
SINGLE OPN LIN 1544 324642-324679(1) | OPEN LINE FROM BUS 324642 [2MILLERSBURG69.000] TO BUS 324679 [2PARIS 3 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.552
SINGLE OPN LIN 1545 324642-324717(1) | OPEN LINE FROM BUS 324642 [2MILLERSBURG69.000] TO BUS 324717 [2SARDIS TAP 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.0531
SINGLE OPN LIN 1546 324643-324811(1) | OPEN LINE FROM BUS 324643 [2MILL WOOD 69.000] TO BUS 324811 [2CANEYVL JCT69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.20706 | 15.5006
SINGLE OPN LIN 1547 324644-324645(1) | OPEN LINE FROM BUS 324644 [2MORGANFLD 469.000] TO BUS 324645 [2MORGANFIELD69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.288
SINGLE OPN LIN 1548 324644-324776(1) | OPEN LINE FROM BUS 324644 [2MORGANFLD 469.000] TO BUS 324776 [2WHEATCROF T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.8398
SINGLE OPN LIN 1549 324645-324671(1) | OPEN LINE FROM BUS 324645 [2MORGANFIELD69.000] TO BUS 324671 [2OVERLAD S T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.3478
SINGLE OPN LIN 1550 324645-326546(1) | OPEN LINE FROM BUS 324645 [2MORGANFIELD69.000] TO BUS 326546 [2SUNOCO TAP 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.3769
SINGLE OPN LIN 1551 324645-326572(1) | OPEN LINE FROM BUS 324645 [2MORGANFIELD69.000] TO BUS 326572 [2RIVRVW COAL69.000] CKT 1 | TRUE | Met convergence tolerances | 3 | 0.33327 | 20.4351 | 2 | 32.99
SINGLE OPN LIN 1552 324646-324707(1) | OPEN LINE FROM BUS 324646 [2MOREHEAD E 69.000] TO BUS 324707 [2RODBURN 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.7642
SINGLE OPN LIN 1553 324646-324910(1) | OPEN LINE FROM BUS 324646 [2MOREHEAD E 69.000] TO BUS 324910 [2MOREHEAD 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.6601
SINGLE OPN LIN 1554 324647-324910(1) | OPEN LINE FROM BUS 324647 [2MOREHEAD W 69.000] TO BUS 324910 [2MOREHEAD 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.6379
SINGLE OPN LIN 1555 324648-324664(1) | OPEN LINE FROM BUS 324648 [2MORTONS GAP69.000] TO BUS 324664 [2OAK HILL KU69.000] CKT 1 | TRUE | Met convergence tolerances | 9 | 0.96959 | 40.9333 | 4 | 9.78
SINGLE OPN LIN 1556 324648-324769(1) | OPEN LINE FROM BUS 324648 [2MORTONS GAP69.000] TO BUS 324769 [2WALKER KU 69.000] CKT 1 | TRUE | Met convergence tolerances | 10 | 0.14177 | 8.4023 | 5 | 12.07
SINGLE OPN LIN 1557 324649-324675(1) | OPEN LINE FROM BUS 324649 [2MORRIS FORM69.000] TO BUS 324675 [2PADDYS RUN 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.289
SINGLE OPN LIN 1558 324650-324891(1) | OPEN LINE FROM BUS 324650 [2MT TBR T 69.000] TO BUS 324891 [2LEX WATER 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.3694
SINGLE OPN LIN 1559 324652-324817(1) | OPEN LINE FROM BUS 324652 [2MUHLENBRG P69.000] TO BUS 324817 [2CENTRAL CIT69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.4793
SINGLE OPN LIN 1560 324655-324748(1) | OPEN LINE FROM BUS 324655 [2N CORBIN T 69.000] TO BUS 324748 [2SWEET HOLLO69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.1476
SINGLE OPN LIN 1561 324655-324791(1) | OPEN LINE FROM BUS 324655 [2N CORBIN T 69.000] TO BUS 324791 [2AISIN 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.4337
SINGLE OPN LIN 1562 324655-326542(1) | OPEN LINE FROM BUS 324655 [2N CORBIN T 69.000] TO BUS 326542 [2N CORBIN 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.25915 | 28.121 | 1 | 6.1092
SINGLE OPN LIN 1563 324656-324968(1) | OPEN LINE FROM BUS 324656 [2N MADISON T69.000] TO BUS 324968 [2SPEAR STA B69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6095
SINGLE OPN LIN 1564 324657-324771(1) | OPEN LINE FROM BUS 324657 [2NACHAND 69.000] TO BUS 324771 [2WATTERSON 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.1873
SINGLE OPN LIN 1565 324658-324774(1) | OPEN LINE FROM BUS 324658 [2NEBO 69.000] TO BUS 324774 [2WEBCOAL 4 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.2979
SINGLE OPN LIN 1566 324658-324776(1) | OPEN LINE FROM BUS 324658 [2NEBO 69.000] TO BUS 324776 [2WHEATCROF T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.3148
SINGLE OPN LIN 1567 324658-324931(1) | OPEN LINE FROM BUS 324658 [2NEBO 69.000] TO BUS 324931 [2PROVIDNCE E69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.741
SINGLE OPN LIN 1568 324659-326513(1) | OPEN LINE FROM BUS 324659 [2NELSON 69.000] TO BUS 326513 [2EQAL M BREC69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.347
SINGLE OPN LIN 1569 324660-324801(1) | OPEN LINE FROM BUS 324660 [2NEW HAVEN 69.000] TO BUS 324801 [2BARTON 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.5808
SINGLE OPN LIN 1570 324661-324989(1) | OPEN LINE FROM BUS 324661 [2NICHLSV 7 69.000] TO BUS 324989 [2W NICHSV T 69.000] CKT 1 | TRUE | Met convergence tolerances | 5 | 0.24871 | 15.8859 | 3 | 23.79
SINGLE OPN LIN 1571 324662-324688(1) | OPEN LINE FROM BUS 324662 [2N LONDON KU69.000] TO BUS 324688 [2PITTSBRG KU69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.4035
SINGLE OPN LIN 1572 324663-324826(1) | OPEN LINE FROM BUS 324663 [2NORTON EAST69.000] TO BUS 324826 [2CLINCH V SW69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.49
SINGLE OPN LIN 1573 324667-324703(1) | OPEN LINE FROM BUS 324667 [2OHIO COUNTY69.000] TO BUS 324703 [2RIVERVIEW 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.8602
SINGLE OPN LIN 1574 324667-324770(1) | OPEN LINE FROM BUS 324667 [2OHIO COUNTY69.000] TO BUS 324770 [2WARREN 4 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.7127
SINGLE OPN LIN 1575 324668-324936(1) | OPEN LINE FROM BUS 324668 [2OKONITE 69.000] TO BUS 324936 [2RICHMND IND69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.6046
SINGLE OPN LIN 1576 324672-324916(1) | OPEN LINE FROM BUS 324672 [2OXFORD EK T69.000] TO BUS 324916 [2NEWTOWN TAP69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.25251 | 27.4531 | 1 | 5.9966
SINGLE OPN LIN 1577 324674-324934(1) | OPEN LINE FROM BUS 324674 [2PROC & GAMB69.000] TO BUS 324934 [2RACE STREET69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.3141
SINGLE OPN LIN 1578 324677-324680(1) | OPEN LINE FROM BUS 324677 [2PARIS 12 69.000] TO BUS 324680 [2PARIS KU 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 3.7448
SINGLE OPN LIN 1579 324678-324679(1) | OPEN LINE FROM BUS 324678 [2PARIS CITY 69.000] TO BUS 324679 [2PARIS 3 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.692
SINGLE OPN LIN 1580 324678-324680(1) | OPEN LINE FROM BUS 324678 [2PARIS CITY 69.000] TO BUS 324680 [2PARIS KU 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.7195
SINGLE OPN LIN 1581 324681-324960(1) | OPEN LINE FROM BUS 324681 [2PENAL FARM 69.000] TO BUS 324960 [2SKYLIGHT 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.5219
SINGLE OPN LIN 1582 324682-324887(1) | OPEN LINE FROM BUS 324682 [2PENAL TAP 69.000] TO BUS 324887 [2LA GRANG PE69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.86803 | 38.9391 | 1 | 9.59
SINGLE OPN LIN 1583 324683-324866(1) | OPEN LINE FROM BUS 324683 [2PICADOME 69.000] TO BUS 324866 [2GE LAMP 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.2822
SINGLE OPN LIN 1584 324684-324686(1) | OPEN LINE FROM BUS 324684 [2PINEVIL 72269.000] TO BUS 324686 [2PINEVILLE 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.3309
SINGLE OPN LIN 1585 324687-324694(1) | OPEN LINE FROM BUS 324687 [2PISGAH 69.000] TO BUS 324694 [2PARKR MIL T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.7133
SINGLE OPN LIN 1586 324689-324738(1) | OPEN LINE FROM BUS 324689 [2POCKET 69.000] TO BUS 324738 [2SAINT CHARL69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.5652
SINGLE OPN LIN 1587 324689-324744(1) | OPEN LINE FROM BUS 324689 [2POCKET 69.000] TO BUS 324744 [2STRAGHT CRK69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.793
SINGLE OPN LIN 1588 324690-324747(1) | OPEN LINE FROM BUS 324690 [2DAWSON TAP 69.000] TO BUS 324747 [2SUNSET MINE69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.5128
SINGLE OPN LIN 1589 324690-324843(1) | OPEN LINE FROM BUS 324690 [2DAWSON TAP 69.000] TO BUS 324843 [2DAWSON IND 69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.51884 | 24.5533 | 2 | 5.57
SINGLE OPN LIN 1590 324691-324870(1) | OPEN LINE FROM BUS 324691 [2POWDERLY 69.000] TO BUS 324870 [2GREENVILLE 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.3363
SINGLE OPN LIN 1591 324692-324738(1) | OPEN LINE FROM BUS 324692 [2POWELL MTN 69.000] TO BUS 324738 [2SAINT CHARL69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.5428
SINGLE OPN LIN 1592 324693-324747(1) | OPEN LINE FROM BUS 324693 [2PRINCETON 69.000] TO BUS 324747 [2SUNSET MINE69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.5244
SINGLE OPN LIN 1593 324694-324884(1) | OPEN LINE FROM BUS 324694 [2PARKR MIL T69.000] TO BUS 324884 [2KUNKEL 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.4546
SINGLE OPN LIN 1594 324694-324930(1) | OPEN LINE FROM BUS 324694 [2PARKR MIL T69.000] TO BUS 324930 [2PARKER MILL69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6382
SINGLE OPN LIN 1595 324695-324749(1) | OPEN LINE FROM BUS 324695 [2PARKER SEAL69.000] TO BUS 324749 [2SYLVANIA 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.4649
SINGLE OPN LIN 1596 324695-324783(1) | OPEN LINE FROM BUS 324695 [2PARKER SEAL69.000] TO BUS 324783 [2WINCHSTR KU69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.4769
SINGLE OPN LIN 1597 324696-324706(1) | OPEN LINE FROM BUS 324696 [2PUCKETT CRK69.000] TO BUS 324706 [2ROCKY BRNCH69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.6901
SINGLE OPN LIN 1598 324696-324792(1) | OPEN LINE FROM BUS 324696 [2PUCKETT CRK69.000] TO BUS 324792 [2ALVA 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.5671
SINGLE OPN LIN 1599 324698-324708(1) | OPEN LINE FROM BUS 324698 [2RADCLIFF SO69.000] TO BUS 324708 [2ROGERSVILLE69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.2838
SINGLE OPN LIN 1600 324698-326555(1) | OPEN LINE FROM BUS 324698 [2RADCLIFF SO69.000] TO BUS 326555 [2RINEYVIL RD69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.3335
SINGLE OPN LIN 1601 324699-324768(1) | OPEN LINE FROM BUS 324699 [2RICE STA TP69.000] TO BUS 324768 [2WACO 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.4224
SINGLE OPN LIN 1602 324699-326552(1) | OPEN LINE FROM BUS 324699 [2RICE STA TP69.000] TO BUS 326552 [2SE COAL TP 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6386
SINGLE OPN LIN 1603 324700-324938(1) | OPEN LINE FROM BUS 324700 [2RICHMND SO 69.000] TO BUS 324938 [2RICHMND 3 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.7084
SINGLE OPN LIN 1604 324703-324959(1) | OPEN LINE FROM BUS 324703 [2RIVERVIEW 69.000] TO BUS 324959 [2SIMMONS 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.824
SINGLE OPN LIN 1605 324704-324784(1) | OPEN LINE FROM BUS 324704 [2ROCKHOLD 69.000] TO BUS 324784 [2WOFFORD 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6348
SINGLE OPN LIN 1606 324705-324783(1) | OPEN LINE FROM BUS 324705 [2ROCKWELL 69.000] TO BUS 324783 [2WINCHSTR KU69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.0796
SINGLE OPN LIN 1607 324705-324855(1) | OPEN LINE FROM BUS 324705 [2ROCKWELL 69.000] TO BUS 324855 [2EKPC OFF TP69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.16087 | 3.3208
SINGLE OPN LIN 1608 324708-324944(1) | OPEN LINE FROM BUS 324708 [2ROGERSVILLE69.000] TO BUS 324944 [2ROGERSV 60569.000] CKT 1 | TRUE | Met convergence tolerances | 4 | 0.18408 | 12.536 | 3 | 19.32
SINGLE OPN LIN 1609 324709-324981(1) | OPEN LINE FROM BUS 324709 [2RVR QUEEN T69.000] TO BUS 324981 [2TEXAS GAS T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.5278
SINGLE OPN LIN 1610 324710-324750(1) | OPEN LINE FROM BUS 324710 [2RVR CITY SH69.000] TO BUS 324750 [2TAYLOR LG 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.7049
SINGLE OPN LIN 1611 324711-324790(1) | OPEN LINE FROM BUS 324711 [2SPEN CHEM T69.000] TO BUS 324790 [2AIRLINE RD 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.838
SINGLE OPN LIN 1612 324712-324825(1) | OPEN LINE FROM BUS 324712 [2SO PADUCAH 69.000] TO BUS 324825 [2CLINTON KU 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.3118
SINGLE OPN LIN 1613 324713-324955(1) | OPEN LINE FROM BUS 324713 [2SO ELKHORN 69.000] TO BUS 324955 [2SHANNON RUN69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.526
SINGLE OPN LIN 1614 324714-324733(1) | OPEN LINE FROM BUS 324714 [2SALT LICK 69.000] TO BUS 324733 [2SPENCER RD 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.459
SINGLE OPN LIN 1615 324715-324721(1) | OPEN LINE FROM BUS 324715 [2SALVISA 69.000] TO BUS 324721 [2SHAKERTOWN 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.792
SINGLE OPN LIN 1616 324715-325087(1) | OPEN LINE FROM BUS 324715 [2SALVISA 69.000] TO BUS 325087 [2CLAY LICK T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.7662
SINGLE OPN LIN 1617 324716-324977(1) | OPEN LINE FROM BUS 324716 [2SANDY RIDGE69.000] TO BUS 324977 [2TOMS CRK TP69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 3.3967
SINGLE OPN LIN 1618 324717-326549(1) | OPEN LINE FROM BUS 324717 [2SARDIS TAP 69.000] TO BUS 326549 [2SARDIS 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.16805 | 15.1985 | 1 | 1.36
SINGLE OPN LIN 1619 324718-324726(1) | OPEN LINE FROM BUS 324718 [2SHELBY CO T69.000] TO BUS 324726 [2SHELBYVIL S69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6255
SINGLE OPN LIN 1620 324719-324724(1) | OPEN LINE FROM BUS 324719 [2SEMINOLE 69.000] TO BUS 324724 [2SHIVELY 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6619
SINGLE OPN LIN 1621 324721-324764(1) | OPEN LINE FROM BUS 324721 [2SHAKERTOWN 69.000] TO BUS 324764 [2WEST CLIFF 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.8743
SINGLE OPN LIN 1622 324723-325086(1) | OPEN LINE FROM BUS 324723 [2SHAVER CHAP69.000] TO BUS 325086 [2KEN AMERI 269.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.7643
SINGLE OPN LIN 1623 324725-324727(1) | OPEN LINE FROM BUS 324725 [2SHELBYVIL E69.000] TO BUS 324727 [2SHELBYVILLE69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.153
SINGLE OPN LIN 1624 324726-324727(1) | OPEN LINE FROM BUS 324726 [2SHELBYVIL S69.000] TO BUS 324727 [2SHELBYVILLE69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.4779
SINGLE OPN LIN 1625 324727-325102(1) | OPEN LINE FROM BUS 324727 [2SHELBYVILLE69.000] TO BUS 325102 [2W SHELBY 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6197
SINGLE OPN LIN 1626 324728-324781(1) | OPEN LINE FROM BUS 324728 [2SHUN PIKE 69.000] TO BUS 324781 [2WILMORE T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.80138 | 34.0707 | 1 | 8.09
SINGLE OPN LIN 1627 324729-325102(1) | OPEN LINE FROM BUS 324729 [2SIMPSONVILL69.000] TO BUS 325102 [2W SHELBY 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.34596 | 6.0879
SINGLE OPN LIN 1628 324731-326547(1) | OPEN LINE FROM BUS 324731 [2SONORA TAP 69.000] TO BUS 326547 [2SONORA 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.39431 | 19.9353 | 1 | 4.15
SINGLE OPN LIN 1629 324734-324848(1) | OPEN LINE FROM BUS 324734 [2SPINDLETP T69.000] TO BUS 324848 [2DONERAIL 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.8111
SINGLE OPN LIN 1630 324735-324794(1) | OPEN LINE FROM BUS 324735 [2SOUTH POINT69.000] TO BUS 324794 [2ASHLND PIPE69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.7876
SINGLE OPN LIN 1631 324737-324969(1) | OPEN LINE FROM BUS 324737 [2SOMERSET SO69.000] TO BUS 324969 [2SMRST 615KU69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.3678
SINGLE OPN LIN 1632 324740-324788(1) | OPEN LINE FROM BUS 324740 [2SOUTH PARK 69.000] TO BUS 324788 [2BROOKS EK T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.5476
SINGLE OPN LIN 1633 324740-325024(1) | OPEN LINE FROM BUS 324740 [2SOUTH PARK 69.000] TO BUS 325024 [2ASHBOT SPRK69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.9173
SINGLE OPN LIN 1634 324742-324866(1) | OPEN LINE FROM BUS 324742 [2STONEWALL T69.000] TO BUS 324866 [2GE LAMP 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.9817
SINGLE OPN LIN 1635 324742-324972(1) | OPEN LINE FROM BUS 324742 [2STONEWALL T69.000] TO BUS 324972 [2STONEWALL 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.8748
SINGLE OPN LIN 1636 324743-324759(1) | OPEN LINE FROM BUS 324743 [2SAINT PAUL 69.000] TO BUS 324759 [2VIRGINIA CI69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.151
SINGLE OPN LIN 1637 324743-324851(1) | OPEN LINE FROM BUS 324743 [2SAINT PAUL 69.000] TO BUS 324851 [2DWINA TAP 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.4418
SINGLE OPN LIN 1638 324744-324876(1) | OPEN LINE FROM BUS 324744 [2STRAGHT CRK69.000] TO BUS 324876 [2HOLMES MILL69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.7206
SINGLE OPN LIN 1639 324746-326546(1) | OPEN LINE FROM BUS 324746 [2SUNOCO 69.000] TO BUS 326546 [2SUNOCO TAP 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.17189 | 15.3461 | 1 | 1.51
SINGLE OPN LIN 1640 324751-325921(1) | OPEN LINE FROM BUS 324751 [2TAYLOR CO 69.000] TO BUS 325921 [5TAYLOR CO 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.45929 | 19.9554
SINGLE OPN LIN 1641 324752-324974(1) | OPEN LINE FROM BUS 324752 [2TAYLORSV KU69.000] TO BUS 324974 [2TAYLRV EK T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.7964
SINGLE OPN LIN 1642 324754-324928(1) | OPEN LINE FROM BUS 324754 [2TUNNEL H KU69.000] TO BUS 324928 [2POOLE 69.000] CKT 1 | TRUE | Met convergence tolerances | 5 | 0.46947 | 22.7763 | 4 | 5.05
SINGLE OPN LIN 1643 324755-324762(1) | OPEN LINE FROM BUS 324755 [2TYRONE 69.000] TO BUS 324762 [2VERSAIL W T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.8565
SINGLE OPN LIN 1644 324755-324920(1) | OPEN LINE FROM BUS 324755 [2TYRONE 69.000] TO BUS 324920 [2NINEVAH TAP69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.2946
SINGLE OPN LIN 1645 324755-324985(1) | OPEN LINE FROM BUS 324755 [2TYRONE 69.000] TO BUS 324985 [2VSAIL BYPAS69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6858
SINGLE OPN LIN 1646 324756-324772(1) | OPEN LINE FROM BUS 324756 [2UK WEST 1 69.000] TO BUS 324772 [2UK WEST 2 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.4443
SINGLE OPN LIN 1647 324756-324952(1) | OPEN LINE FROM BUS 324756 [2UK WEST 1 69.000] TO BUS 324952 [2SCOTT ST TP69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.4189
SINGLE OPN LIN 1648 324757-324941(1) | OPEN LINE FROM BUS 324757 [2UPR MIL CRK69.000] TO BUS 324941 [2RIVERPORT 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.308
SINGLE OPN LIN 1649 324758-324833(1) | OPEN LINE FROM BUS 324758 [2US STEEL 69.000] TO BUS 324833 [2CORBIN 2 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.48034 | 20.3938
SINGLE OPN LIN 1650 324760-324838(1) | OPEN LINE FROM BUS 324760 [2VAKSDAHL AV69.000] TO BUS 324838 [2DANV IND TP69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.163
SINGLE OPN LIN 1651 324763-324985(1) | OPEN LINE FROM BUS 324763 [2VERSAILLES 69.000] TO BUS 324985 [2VSAIL BYPAS69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.1946
SINGLE OPN LIN 1652 324764-326578(1) | OPEN LINE FROM BUS 324764 [2WEST CLIFF 69.000] TO BUS 326578 [2HARRDSBRG 169.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.39062 | 18.2105
SINGLE OPN LIN 1653 324765-326528(1) | OPEN LINE FROM BUS 324765 [2W FRANKFORT69.000] TO BUS 326528 [2BRIDGEPORT 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.627
SINGLE OPN LIN 1654 324765-326973(1) | OPEN LINE FROM BUS 324765 [2W FRANKFORT69.000] TO BUS 326973 [2BRIDGPRT 1 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.41319 | 35.9068 | 1 | 8.5298
SINGLE OPN LIN 1655 324766-324952(1) | OPEN LINE FROM BUS 324766 [2W HIGH T1 69.000] TO BUS 324952 [2SCOTT ST TP69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.3855
SINGLE OPN LIN 1656 324767-326552(Z1) | OPEN LINE FROM BUS 324767 [2WEST IRVINE69.000] TO BUS 326552 [2SE COAL TP 69.000] CKT Z1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6491
SINGLE OPN LIN 1657 324770-324946(1) | OPEN LINE FROM BUS 324770 [2WARREN 4 69.000] TO BUS 324946 [2ROSINE JCT 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.9496
SINGLE OPN LIN 1658 324774-324993(1) | OPEN LINE FROM BUS 324774 [2WEBCOAL 4 69.000] TO BUS 324993 [2WARRIOR CL 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.3014
SINGLE OPN LIN 1659 324776-324777(1) | OPEN LINE FROM BUS 324776 [2WHEATCROF T69.000] TO BUS 324777 [2WHEATCROFT 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.3944
SINGLE OPN LIN 1660 324777-324973(1) | OPEN LINE FROM BUS 324777 [2WHEATCROFT 69.000] TO BUS 324973 [2STURGIS 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.5804
SINGLE OPN LIN 1661 324778-324779(1) | OPEN LINE FROM BUS 324778 [2WICKLIFE CI69.000] TO BUS 324779 [2WICKLIFFE 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.5217
SINGLE OPN LIN 1662 324782-324783(1) | OPEN LINE FROM BUS 324782 [2WINCHEST SO69.000] TO BUS 324783 [2WINCHSTR KU69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.45796 | 19.7071
SINGLE OPN LIN 1663 324784-325001(1) | OPEN LINE FROM BUS 324784 [2WOFFORD 69.000] TO BUS 325001 [2WILLMBRG SW69.000] CKT 1 | TRUE | Met convergence tolerances | 3 | 0.1558 | 10.9359 | 2 | 16.06
SINGLE OPN LIN 1664 324786-324790(1) | OPEN LINE FROM BUS 324786 [2ZION 69.000] TO BUS 324790 [2AIRLINE RD 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 4.5628
SINGLE OPN LIN 1665 324787-324990(1) | OPEN LINE FROM BUS 324787 [2UNION UNDWR69.000] TO BUS 324990 [2WAITSBORO 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.4988
SINGLE OPN LIN 1666 324788-324809(1) | OPEN LINE FROM BUS 324788 [2BROOKS EK T69.000] TO BUS 324809 [2BROOKS EKPC69.000] CKT 1 | TRUE | Met convergence tolerances | 3 | 0.34524 | 22.5568 | 2 | 32.8721
SINGLE OPN LIN 1667 324789-324806(1) | OPEN LINE FROM BUS 324789 [2BLUE LCK TP69.000] TO BUS 324806 [2BEULAH EKPC69.000] CKT 1 | TRUE | Met convergence tolerances | 4 | 0.52199 | 34.6399 | 3 | 47.9074
SINGLE OPN LIN 1668 324789-325021(1) | OPEN LINE FROM BUS 324789 [2BLUE LCK TP69.000] TO BUS 325021 [2CONESTOGA 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 8.4903 | 1 | 12.55
SINGLE OPN LIN 1669 324791-324860(1) | OPEN LINE FROM BUS 324791 [2AISIN 69.000] TO BUS 324860 [2FARISTON 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.5676
SINGLE OPN LIN 1670 324792-324819(1) | OPEN LINE FROM BUS 324792 [2ALVA 69.000] TO BUS 324819 [2CHUNKLIC BR69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.5711
SINGLE OPN LIN 1671 324794-324987(1) | OPEN LINE FROM BUS 324794 [2ASHLND PIPE69.000] TO BUS 324987 [2W HICKMAN 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.2679
SINGLE OPN LIN 1672 324795-324922(1) | OPEN LINE FROM BUS 324795 [2ASHBYBRG PU69.000] TO BUS 324922 [2ONTON 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.20639 | 4.0217 | 1 | 0.57
SINGLE OPN LIN 1673 324797-324855(1) | OPEN LINE FROM BUS 324797 [2AVON T1 69.000] TO BUS 324855 [2EKPC OFF TP69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.8536
SINGLE OPN LIN 1674 324798-324875(1) | OPEN LINE FROM BUS 324798 [2BAILEY CRK 69.000] TO BUS 324875 [2HIGHSPLINT 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.737
SINGLE OPN LIN 1675 324799-324931(1) | OPEN LINE FROM BUS 324799 [2BARNHILL 69.000] TO BUS 324931 [2PROVIDNCE E69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.3538
SINGLE OPN LIN 1676 324799-324932(1) | OPEN LINE FROM BUS 324799 [2BARNHILL 69.000] TO BUS 324932 [2PROVIDENCE 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.353
SINGLE OPN LIN 1677 324802-324871(1) | OPEN LINE FROM BUS 324802 [2BEAR BRANCH69.000] TO BUS 324871 [2HAMER 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6447
SINGLE OPN LIN 1678 324803-324907(1) | OPEN LINE FROM BUS 324803 [2BEAR TRACK 69.000] TO BUS 324907 [2MILLER CRK 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.3985
SINGLE OPN LIN 1679 324803-325058(1) | OPEN LINE FROM BUS 324803 [2BEAR TRACK 69.000] TO BUS 325058 [2BEATTY 614 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.3932
SINGLE OPN LIN 1680 324804-324908(1) | OPEN LINE FROM BUS 324804 [2BEDFORD TAP69.000] TO BUS 324908 [2MILTON 69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.51187 | 39.2042 | 2 | 9.6895
SINGLE OPN LIN 1681 324804-325033(1) | OPEN LINE FROM BUS 324804 [2BEDFORD TAP69.000] TO BUS 325033 [2BEDFORD KU 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.24392 | 16.3258 | 1 | 2.55
SINGLE OPN LIN 1682 324806-324925(1) | OPEN LINE FROM BUS 324806 [2BEULAH EKPC69.000] TO BUS 324925 [2PLEAS GRV T69.000] CKT 1 | TRUE | Met convergence tolerances | 3 | 0.40335 | 27.6031 | 2 | 37.343
SINGLE OPN LIN 1683 324808-324913(1) | OPEN LINE FROM BUS 324808 [2BRODHEAD KU69.000] TO BUS 324913 [2MT VERNON 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 4.9113
SINGLE OPN LIN 1684 324809-324958(1) | OPEN LINE FROM BUS 324809 [2BROOKS EKPC69.000] TO BUS 324958 [2SHEPHRDSV T69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.78113 | 35.135 | 1 | 8.36
SINGLE OPN LIN 1685 324810-324947(1) | OPEN LINE FROM BUS 324810 [2CALHOUN 69.000] TO BUS 324947 [2RUMSEY 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.24253 | 16.3709 | 1 | 2.53
SINGLE OPN LIN 1686 324811-324946(1) | OPEN LINE FROM BUS 324811 [2CANEYVL JCT69.000] TO BUS 324946 [2ROSINE JCT 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.22469 | 15.9301
SINGLE OPN LIN 1687 324814-324956(1) | OPEN LINE FROM BUS 324814 [2CATRON CK T69.000] TO BUS 324956 [2SHAWNEE GAS69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.19592 | 15.2811 | 1 | 1.04
SINGLE OPN LIN 1688 324815-325007(1) | OPEN LINE FROM BUS 324815 [2CAWOOD 69.000] TO BUS 325007 [2YANCY TAP 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.563
SINGLE OPN LIN 1689 324816-324970(1) | OPEN LINE FROM BUS 324816 [2CEMETARY RD69.000] TO BUS 324970 [2STANFORD KU69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 17.2047 | 1 | 3.2549
SINGLE OPN LIN 1690 324818-324827(1) | OPEN LINE FROM BUS 324818 [2CHAD TAP 69.000] TO BUS 324827 [2CLOVERLICK 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.4962
SINGLE OPN LIN 1691 324818-324978(1) | OPEN LINE FROM BUS 324818 [2CHAD TAP 69.000] TO BUS 324978 [2TOTZ 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.4416
SINGLE OPN LIN 1692 324819-324945(1) | OPEN LINE FROM BUS 324819 [2CHUNKLIC BR69.000] TO BUS 324945 [2ROSE HILL T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.5811
SINGLE OPN LIN 1693 324820-324850(1) | OPEN LINE FROM BUS 324820 [2ISLAND MINE69.000] TO BUS 324850 [2DOZIER H 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.8198
SINGLE OPN LIN 1694 324820-324981(1) | OPEN LINE FROM BUS 324820 [2ISLAND MINE69.000] TO BUS 324981 [2TEXAS GAS T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.9739
SINGLE OPN LIN 1695 324821-324914(1) | OPEN LINE FROM BUS 324821 [2CLARKSON 69.000] TO BUS 324914 [2M-V CLARK T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.636
SINGLE OPN LIN 1696 324821-324992(1) | OPEN LINE FROM BUS 324821 [2CLARKSON 69.000] TO BUS 324992 [2WARREN TIE 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.5007
SINGLE OPN LIN 1697 324822-324996(1) | OPEN LINE FROM BUS 324822 [2CLAY KU 69.000] TO BUS 324996 [2DOTIKI TAP 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.4131
SINGLE OPN LIN 1698 324823-324825(1) | OPEN LINE FROM BUS 324823 [2CLINTON 58169.000] TO BUS 324825 [2CLINTON KU 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.3385
SINGLE OPN LIN 1699 324824-325005(1) | OPEN LINE FROM BUS 324824 [2CLINCH VALL69.000] TO BUS 325005 [2WISE TAP 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.2075
SINGLE OPN LIN 1700 324826-324999(1) | OPEN LINE FROM BUS 324826 [2CLINCH V SW69.000] TO BUS 324999 [2WHTE OAK KU69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.482
SINGLE OPN LIN 1701 324832-324833(1) | OPEN LINE FROM BUS 324832 [2CORBIN 1 69.000] TO BUS 324833 [2CORBIN 2 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.38527 | 18.4241
SINGLE OPN LIN 1702 324836-324853(1) | OPEN LINE FROM BUS 324836 [2BENS BRANCH69.000] TO BUS 324853 [2E STONE GAP69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.60376 | 28.0362 | 1 | 6.55
SINGLE OPN LIN 1703 324836-324894(1) | OPEN LINE FROM BUS 324836 [2BENS BRANCH69.000] TO BUS 324894 [2E STONE G T69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.61023 | 28.1048 | 1 | 6.55
SINGLE OPN LIN 1704 324838-324957(1) | OPEN LINE FROM BUS 324838 [2DANV IND TP69.000] TO BUS 324957 [2SHELBY CI T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.1632
SINGLE OPN LIN 1705 324839-324909(1) | OPEN LINE FROM BUS 324839 [2DANVILE IND69.000] TO BUS 324909 [2MINR FARM T69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.19982 | 13.2653 | 1 | 20.27
SINGLE OPN LIN 1706 324841-324909(1) | OPEN LINE FROM BUS 324841 [2DANVILLE W 69.000] TO BUS 324909 [2MINR FARM T69.000] CKT 1 | TRUE | Met convergence tolerances | 3 | 0.27163 | 17.0818 | 2 | 26.36
SINGLE OPN LIN 1707 324842-324967(1) | OPEN LINE FROM BUS 324842 [2DAVIS TAP 69.000] TO BUS 324967 [2SPEAR STA A69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.4213
SINGLE OPN LIN 1708 324842-324987(1) | OPEN LINE FROM BUS 324842 [2DAVIS TAP 69.000] TO BUS 324987 [2W HICKMAN 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.4203
SINGLE OPN LIN 1709 324844-324943(1) | OPEN LINE FROM BUS 324844 [2DELAPLAIN 69.000] TO BUS 324943 [2ROGERS GAP 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.2352 | 15.0048 | 1 | 22.92
SINGLE OPN LIN 1710 324845-324962(1) | OPEN LINE FROM BUS 324845 [2DENHAM ST 69.000] TO BUS 324962 [2SOMERSET 1 69.000] CKT 1 | TRUE | Met convergence tolerances | 3 | 0.14287 | 8.1242 | 3 | 11.6
SINGLE OPN LIN 1711 324845-324963(1) | OPEN LINE FROM BUS 324845 [2DENHAM ST 69.000] TO BUS 324963 [2SOMERSET 2 69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.33981 | 18.4345 | 2 | 3.56
SINGLE OPN LIN 1712 324846-324932(1) | OPEN LINE FROM BUS 324846 [2DIAMOND 69.000] TO BUS 324932 [2PROVIDENCE 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.4012
SINGLE OPN LIN 1713 324846-324996(1) | OPEN LINE FROM BUS 324846 [2DIAMOND 69.000] TO BUS 324996 [2DOTIKI TAP 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.4037
SINGLE OPN LIN 1714 324847-324973(1) | OPEN LINE FROM BUS 324847 [2DODGE HILL 69.000] TO BUS 324973 [2STURGIS 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.9895
SINGLE OPN LIN 1715 324847-326546(1) | OPEN LINE FROM BUS 324847 [2DODGE HILL 69.000] TO BUS 326546 [2SUNOCO TAP 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.1452
SINGLE OPN LIN 1716 324848-324877(1) | OPEN LINE FROM BUS 324848 [2DONERAIL 69.000] TO BUS 324877 [2HOOVER KU 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.594
SINGLE OPN LIN 1717 324849-324867(1) | OPEN LINE FROM BUS 324849 [2DOW CORNING69.000] TO BUS 324867 [2GHENT 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.645
SINGLE OPN LIN 1718 324851-324999(1) | OPEN LINE FROM BUS 324851 [2DWINA TAP 69.000] TO BUS 324999 [2WHTE OAK KU69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.4916
SINGLE OPN LIN 1719 324852-324885(1) | OPEN LINE FROM BUS 324852 [2DYCUSBURG 69.000] TO BUS 324885 [2KUTTAWA 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.3069
SINGLE OPN LIN 1720 324852-324949(1) | OPEN LINE FROM BUS 324852 [2DYCUSBURG 69.000] TO BUS 324949 [2SALEM 673 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.3177
SINGLE OPN LIN 1721 324855-326541(1) | OPEN LINE FROM BUS 324855 [2EKPC OFF TP69.000] TO BUS 326541 [2EKPC OFFICE69.000] CKT 1 | TRUE | Met convergence tolerances | 4 | 0.65254 | 26.2851 | 3 | 5.01
SINGLE OPN LIN 1722 324856-324880(1) | OPEN LINE FROM BUS 324856 [2ESTIL ST CO69.000] TO BUS 324880 [2IRVINE 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.409
SINGLE OPN LIN 1723 324856-324907(1) | OPEN LINE FROM BUS 324856 [2ESTIL ST CO69.000] TO BUS 324907 [2MILLER CRK 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.4028
SINGLE OPN LIN 1724 324857-324858(1) | OPEN LINE FROM BUS 324857 [2ETOWN 2 69.000] TO BUS 324858 [2ETOWN 5 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.34987 | 21.1271 | 1 | 33.95
SINGLE OPN LIN 1725 324862-325086(1) | OPEN LINE FROM BUS 324862 [2FIES CITY 69.000] TO BUS 325086 [2KEN AMERI 269.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.5631
SINGLE OPN LIN 1726 324863-324920(1) | OPEN LINE FROM BUS 324863 [2FLA TILE T169.000] TO BUS 324920 [2NINEVAH TAP69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.9168
SINGLE OPN LIN 1727 324865-324904(1) | OPEN LINE FROM BUS 324865 [2FREDONIA 69.000] TO BUS 324904 [2MEXICO KU 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 3.1494
SINGLE OPN LIN 1728 324867-324911(1) | OPEN LINE FROM BUS 324867 [2GHENT 69.000] TO BUS 324911 [2MARKLAND DM69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.5841
SINGLE OPN LIN 1729 324871-324894(1) | OPEN LINE FROM BUS 324871 [2HAMER 69.000] TO BUS 324894 [2E STONE G T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6211
SINGLE OPN LIN 1730 324873-324896(1) | OPEN LINE FROM BUS 324873 [2HANSON JCT 69.000] TO BUS 324896 [2MADSNV E 69.000] CKT 1 | TRUE | Met convergence tolerances | 3 | 0.1715 | 11.8542 | 2 | 18.39
SINGLE OPN LIN 1731 324875-324942(1) | OPEN LINE FROM BUS 324875 [2HIGHSPLINT 69.000] TO BUS 324942 [2ROBBINS 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.5027
SINGLE OPN LIN 1732 324877-324890(1) | OPEN LINE FROM BUS 324877 [2HOOVER KU 69.000] TO BUS 324890 [2LEMONS MILL69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.5086
SINGLE OPN LIN 1733 324878-324908(1) | OPEN LINE FROM BUS 324878 [2HUNT BTM TP69.000] TO BUS 324908 [2MILTON 69.000] CKT 1 | TRUE | Met convergence tolerances | 3 | 0.96639 | 61.4256 | 3 | 15.3605
SINGLE OPN LIN 1734 324881-324942(1) | OPEN LINE FROM BUS 324881 [2JACKS CREEK69.000] TO BUS 324942 [2ROBBINS 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.4529
SINGLE OPN LIN 1735 324881-324978(1) | OPEN LINE FROM BUS 324881 [2JACKS CREEK69.000] TO BUS 324978 [2TOTZ 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.4449
SINGLE OPN LIN 1736 324884-324979(1) | OPEN LINE FROM BUS 324884 [2KUNKEL 69.000] TO BUS 324979 [2TRAFTON AVE69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.4025
SINGLE OPN LIN 1737 324886-324967(1) | OPEN LINE FROM BUS 324886 [2KY RIVER 69.000] TO BUS 324967 [2SPEAR STA A69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.4206
SINGLE OPN LIN 1738 324886-324968(1) | OPEN LINE FROM BUS 324886 [2KY RIVER 69.000] TO BUS 324968 [2SPEAR STA B69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6128
SINGLE OPN LIN 1739 324892-324945(1) | OPEN LINE FROM BUS 324892 [2LIGGETT 69.000] TO BUS 324945 [2ROSE HILL T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.559
SINGLE OPN LIN 1740 324892-325007(1) | OPEN LINE FROM BUS 324892 [2LIGGETT 69.000] TO BUS 325007 [2YANCY TAP 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.5638
SINGLE OPN LIN 1741 324893-324897(1) | OPEN LINE FROM BUS 324893 [2MADSNV GE T69.000] TO BUS 324897 [2MADSNV N 69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.21851 | 14.4052 | 2 | 22.6
SINGLE OPN LIN 1742 324893-326587(1) | OPEN LINE FROM BUS 324893 [2MADSNV GE T69.000] TO BUS 326587 [2MADSNV W TP69.000] CKT 1 | TRUE | Met convergence tolerances | 3 | 0.22061 | 14.4472 | 2 | 22.81
SINGLE OPN LIN 1743 324895-324897(1) | OPEN LINE FROM BUS 324895 [2MADSNV HO 69.000] TO BUS 324897 [2MADSNV N 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.92496 | 39.071 | 1 | 9.41
SINGLE OPN LIN 1744 324896-324902(1) | OPEN LINE FROM BUS 324896 [2MADSNV E 69.000] TO BUS 324902 [2MCCOY AVE 69.000] CKT 1 | TRUE | Met convergence tolerances | 4 | 0.2634 | 16.7202 | 3 | 26.78
SINGLE OPN LIN 1745 324898-324954(1) | OPEN LINE FROM BUS 324898 [2MANITOU 69.000] TO BUS 324954 [2SENTRY TAP 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.3394
SINGLE OPN LIN 1746 324898-324993(1) | OPEN LINE FROM BUS 324898 [2MANITOU 69.000] TO BUS 324993 [2WARRIOR CL 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.3124
SINGLE OPN LIN 1747 324899-324900(1) | OPEN LINE FROM BUS 324899 [2MAYSVILLE E69.000] TO BUS 324900 [2MAYSVILLE M69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.33222 | 18.2405 | 1 | 3.56
SINGLE OPN LIN 1748 324903-324964(1) | OPEN LINE FROM BUS 324903 [2MCKEE ROAD 69.000] TO BUS 324964 [2SOMERSET 3 69.000] CKT 1 | TRUE | Met convergence tolerances | 5 | 0.14287 | 9.6638 | 3 | 14.03
SINGLE OPN LIN 1749 324903-324965(1) | OPEN LINE FROM BUS 324903 [2MCKEE ROAD 69.000] TO BUS 324965 [2SOMERSET NO69.000] CKT 1 | TRUE | Met convergence tolerances | 4 | 0.44102 | 21.6764 | 2 | 4.59
SINGLE OPN LIN 1750 324909-325032(1) | OPEN LINE FROM BUS 324909 [2MINR FARM T69.000] TO BUS 325032 [2MINOR FARM 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.57764 | 27.0014 | 1 | 6.09
SINGLE OPN LIN 1751 324911-324994(1) | OPEN LINE FROM BUS 324911 [2MARKLAND DM69.000] TO BUS 324994 [2WARSAW KU 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.5852
SINGLE OPN LIN 1752 324915-325006(1) | OPEN LINE FROM BUS 324915 [2MT WAS EK J69.000] TO BUS 325006 [2W MT WSH EK69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.24636 | 17.7717 | 1 | 23.6017
SINGLE OPN LIN 1753 324916-324924(1) | OPEN LINE FROM BUS 324916 [2NEWTOWN TAP69.000] TO BUS 324924 [2OXFORD 69.000] CKT 1 | TRUE | Met convergence tolerances | 3 | 0.76248 | 50.3716 | 2 | 11.7766
SINGLE OPN LIN 1754 324916-325027(1) | OPEN LINE FROM BUS 324916 [2NEWTOWN TAP69.000] TO BUS 325027 [2NEWTOWN 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.5656 | 26.7964 | 1 | 5.78
SINGLE OPN LIN 1755 324917-324918(1) | OPEN LINE FROM BUS 324917 [2NICHLSV 3 69.000] TO BUS 324918 [2NICHLSV 4&569.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.55254 | 23.9809 | 1 | 5.05
SINGLE OPN LIN 1756 324917-324980(1) | OPEN LINE FROM BUS 324917 [2NICHLSV 3 69.000] TO BUS 324980 [2RJ CORMAN 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 1.4172
SINGLE OPN LIN 1757 324918-324919(1) | OPEN LINE FROM BUS 324918 [2NICHLSV 4&569.000] TO BUS 324919 [2NICHLSV 6&869.000] CKT 1 | TRUE | Met convergence tolerances | 3 | 0.16124 | 11.1662 | 2 | 16.39
SINGLE OPN LIN 1758 324919-324989(1) | OPEN LINE FROM BUS 324919 [2NICHLSV 6&869.000] TO BUS 324989 [2W NICHSV T 69.000] CKT 1 | TRUE | Met convergence tolerances | 4 | 0.24871 | 16.01 | 3 | 23.79
SINGLE OPN LIN 1759 324920-326529(1) | OPEN LINE FROM BUS 324920 [2NINEVAH TAP69.000] TO BUS 326529 [2NINEVAH 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.26733 | 28.4508 | 1 | 6.3826
SINGLE OPN LIN 1760 324922-326563(1) | OPEN LINE FROM BUS 324922 [2ONTON 69.000] TO BUS 326563 [2ADVENT MINE69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.17731 | 15.4411 | 2 | 1.69
SINGLE OPN LIN 1761 324925-325006(1) | OPEN LINE FROM BUS 324925 [2PLEAS GRV T69.000] TO BUS 325006 [2W MT WSH EK69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.40343 | 27.2985 | 2 | 37.343
SINGLE OPN LIN 1762 324928-324953(1) | OPEN LINE FROM BUS 324928 [2POOLE 69.000] TO BUS 324953 [2SEBREE 69.000] CKT 1 | TRUE | Met convergence tolerances | 4 | 0.41376 | 20.7477 | 3 | 4.41
SINGLE OPN LIN 1763 324930-324972(1) | OPEN LINE FROM BUS 324930 [2PARKER MILL69.000] TO BUS 324972 [2STONEWALL 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.2749
SINGLE OPN LIN 1764 324934-324984(1) | OPEN LINE FROM BUS 324934 [2RACE STREET69.000] TO BUS 324984 [2VINE STREET69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.2713
SINGLE OPN LIN 1765 324935-324944(1) | OPEN LINE FROM BUS 324935 [2RADCLF KU T69.000] TO BUS 324944 [2ROGERSV 60569.000] CKT 1 | TRUE | Met convergence tolerances | 3 | 0.14177 | 7.8708 | 2 | 11.39
SINGLE OPN LIN 1766 324935-324982(1) | OPEN LINE FROM BUS 324935 [2RADCLF KU T69.000] TO BUS 324982 [2VINE GRV KU69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.34157 | 18.4301 | 1 | 3.61
SINGLE OPN LIN 1767 324936-324940(1) | OPEN LINE FROM BUS 324936 [2RICHMND IND69.000] TO BUS 324940 [2RICHMND J 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.0487
SINGLE OPN LIN 1768 324937-324939(1) | OPEN LINE FROM BUS 324937 [2RICHMND 2 69.000] TO BUS 324939 [2RICHMND 4 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.62837 | 29.5079 | 1 | 6.79
SINGLE OPN LIN 1769 324938-324940(1) | OPEN LINE FROM BUS 324938 [2RICHMND 3 69.000] TO BUS 324940 [2RICHMND J 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.0378
SINGLE OPN LIN 1770 324941-324975(1) | OPEN LINE FROM BUS 324941 [2RIVERPORT 69.000] TO BUS 324975 [2TERRY 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.2974
SINGLE OPN LIN 1771 324948-324949(1) | OPEN LINE FROM BUS 324948 [2SALEM KU 69.000] TO BUS 324949 [2SALEM 673 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.4364
SINGLE OPN LIN 1772 324950-325084(1) | OPEN LINE FROM BUS 324950 [2SCIENC HILL69.000] TO BUS 325084 [2FLOYD EKP T69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.23476 | 16.2627 | 1 | 2.37
SINGLE OPN LIN 1773 324951-326989(1) | OPEN LINE FROM BUS 324951 [2SCOTT CO 69.000] TO BUS 326989 [2LONG LICK 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.7834
SINGLE OPN LIN 1774 324953-326563(1) | OPEN LINE FROM BUS 324953 [2SEBREE 69.000] TO BUS 326563 [2ADVENT MINE69.000] CKT 1 | TRUE | Met convergence tolerances | 3 | 0.17759 | 15.435 | 2 | 1.69
SINGLE OPN LIN 1775 324954-325762(1) | OPEN LINE FROM BUS 324954 [2SENTRY TAP 69.000] TO BUS 325762 [2WARRIOR TAP69.000] CKT 1 | TRUE | Met convergence tolerances | 3 | 0.59806 | 27.6429 | 2 | 6.45
SINGLE OPN LIN 1776 324957-324970(1) | OPEN LINE FROM BUS 324957 [2SHELBY CI T69.000] TO BUS 324970 [2STANFORD KU69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.2437
SINGLE OPN LIN 1777 324958-325043(1) | OPEN LINE FROM BUS 324958 [2SHEPHRDSV T69.000] TO BUS 325043 [2SHEPHERDSV 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.781 | 35.1631 | 1 | 8.36
SINGLE OPN LIN 1778 324959-326564(1) | OPEN LINE FROM BUS 324959 [2SIMMONS 69.000] TO BUS 326564 [2LEW BREC 69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.19458 | 15.1649 | 2 | 1.09
SINGLE OPN LIN 1779 324961-324963(1) | OPEN LINE FROM BUS 324961 [2SOMERSET GE69.000] TO BUS 324963 [2SOMERSET 2 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 2.0279 | 1 | 0.18
SINGLE OPN LIN 1780 324966-324994(1) | OPEN LINE FROM BUS 324966 [2SPARTA KU 69.000] TO BUS 324994 [2WARSAW KU 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.79604 | 9.4501
SINGLE OPN LIN 1781 324969-324990(1) | OPEN LINE FROM BUS 324969 [2SMRST 615KU69.000] TO BUS 324990 [2WAITSBORO 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.368
SINGLE OPN LIN 1782 324970-324971(1) | OPEN LINE FROM BUS 324970 [2STANFORD KU69.000] TO BUS 324971 [2STANFORD NO69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6316
SINGLE OPN LIN 1783 324975-324997(1) | OPEN LINE FROM BUS 324975 [2TERRY 69.000] TO BUS 324997 [2WEST CO 1 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.1866
SINGLE OPN LIN 1784 324979-324986(1) | OPEN LINE FROM BUS 324979 [2TRAFTON AVE69.000] TO BUS 324986 [2W HIGH T2 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.368
SINGLE OPN LIN 1785 324981-325062(1) | OPEN LINE FROM BUS 324981 [2TEXAS GAS T69.000] TO BUS 325062 [2TEXAS GAS 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.25136 | 16.568 | 1 | 2.64
SINGLE OPN LIN 1786 324984-324988(1) | OPEN LINE FROM BUS 324984 [2VINE STREET69.000] TO BUS 324988 [2WEST HIGH 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.3085
SINGLE OPN LIN 1787 324994-325025(1) | OPEN LINE FROM BUS 324994 [2WARSAW KU 69.000] TO BUS 325025 [2WARSAW EAST69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.20747 | 15.9012 | 1 | 2.05
SINGLE OPN LIN 1788 324995-325084(1) | OPEN LINE FROM BUS 324995 [2WAYNESBURG 69.000] TO BUS 325084 [2FLOYD EKP T69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.23484 | 16.2693 | 1 | 2.37
SINGLE OPN LIN 1789 324996-325010(1) | OPEN LINE FROM BUS 324996 [2DOTIKI TAP 69.000] TO BUS 325010 [2WEBCOAL 2 69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.31501 | 4.791 | 1 | 0.62
SINGLE OPN LIN 1790 324997-324998(1) | OPEN LINE FROM BUS 324997 [2WEST CO 1 69.000] TO BUS 324998 [2WEST CO 2 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.4865
SINGLE OPN LIN 1791 325002-325003(Z1) | OPEN LINE FROM BUS 325002 [2WILS DOWN 169.000] TO BUS 325003 [2WILS DOWN 269.000] CKT Z1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.275
SINGLE OPN LIN 1792 325008-325026(1) | OPEN LINE FROM BUS 325008 [2BLEDSOE 69.000] TO BUS 325026 [2PINE MOUNTN69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 15.7718 | 1 | 2.4546
SINGLE OPN LIN 1793 325010-325011(1) | OPEN LINE FROM BUS 325010 [2WEBCOAL 2 69.000] TO BUS 325011 [2DOTIKI 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 1.3411
SINGLE OPN LIN 1794 325017-325018(1) | OPEN LINE FROM BUS 325017 [2CMWA 69.000] TO BUS 325018 [2CLA 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.69715 | 32.4602 | 1 | 7.49
SINGLE OPN LIN 1795 325018-325061(1) | OPEN LINE FROM BUS 325018 [2CLA 69.000] TO BUS 325061 [2CMC 69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.14287 | 9.4399 | 2 | 13.8
SINGLE OPN LIN 1796 325023-325024(1) | OPEN LINE FROM BUS 325023 [2ASHBOT EAST69.000] TO BUS 325024 [2ASHBOT SPRK69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.5669
SINGLE OPN LIN 1797 325028-325047(1) | OPEN LINE FROM BUS 325028 [5ASHWD SL TP161.00] TO BUS 325047 [5ASHWOOD 161.00] CKT 1 | TRUE | Met convergence tolerances | 4 | 0.60544 | 32.1722 | 1 | 1.4
SINGLE OPN LIN 1798 325028-326589(1) | OPEN LINE FROM BUS 325028 [5ASHWD SL TP161.00] TO BUS 326589 [5N PRN LIV R161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.2527
SINGLE OPN LIN 1799 325035-325050(1) | OPEN LINE FROM BUS 325035 [2BLUE SOL TP69.000] TO BUS 325050 [2BLUE SOLAR 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 1.4115
SINGLE OPN LIN 1800 325035-325085(1) | OPEN LINE FROM BUS 325035 [2BLUE SOL TP69.000] TO BUS 325085 [2CYNTHI EK T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.66362 | 5.5082
SINGLE OPN LIN 1801 325041-325068(1) | OPEN LINE FROM BUS 325041 [2STONE TVA 69.000] TO BUS 325068 [2HAMBLIN 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.62289 | 29.3997 | 1 | 6.81
SINGLE OPN LIN 1802 325044-326565(1) | OPEN LINE FROM BUS 325044 [4INTRNTL 138.00] TO BUS 326565 [4INTRNTL TAP138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.29895 | 18.299 | 1 | 30.17
SINGLE OPN LIN 1803 325045-325092(1) | OPEN LINE FROM BUS 325045 [2TURTLE CRK 69.000] TO BUS 325092 [2COAL GOOD 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.23529 | 16.2898 | 1 | 2.45
SINGLE OPN LIN 1804 325055-325116(1) | OPEN LINE FROM BUS 325055 [4RHUDES TP 138.00] TO BUS 325116 [4RHUDES CR 138.00] CKT 1 | TRUE | Met convergence tolerances | 4 | 0.14287 | 13.4273 | 1 | 0.16
SINGLE OPN LIN 1805 325057-325088(1) | OPEN LINE FROM BUS 325057 [4KOSMOS CEME138.00] TO BUS 325088 [4MIL CK YARD138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.26642 | 16.6361 | 1 | 27.23
SINGLE OPN LIN 1806 325059-325060(1) | OPEN LINE FROM BUS 325059 [2BRYANT RD T69.000] TO BUS 325060 [2BRYANT ROAD69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.45178 | 26.7595 | 1 | 41.17
SINGLE OPN LIN 1807 325075-325077(Z1) | OPEN LINE FROM BUS 325075 [5KMPA COLEMN161.00] TO BUS 325077 [5COLEMAN TAP161.00] CKT Z1 | TRUE | Met convergence tolerances | 1 | 0.66287 | 38.4027 | 1 | 66.99
SINGLE OPN LIN 1808 325077-325078(1) | OPEN LINE FROM BUS 325077 [5COLEMAN TAP161.00] TO BUS 325078 [5PADUCAH PRI161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.24514 | 18.7171
SINGLE OPN LIN 1809 325078-326562(1) | OPEN LINE FROM BUS 325078 [5PADUCAH PRI161.00] TO BUS 326562 [2PAD PRI 62469.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.4687
SINGLE OPN LIN 1810 325078-326596(1) | OPEN LINE FROM BUS 325078 [5PADUCAH PRI161.00] TO BUS 326596 [2PAD PRI 61469.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.4684
SINGLE OPN LIN 1811 325079-326589(1) | OPEN LINE FROM BUS 325079 [5N PRINCETON161.00] TO BUS 326589 [5N PRN LIV R161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.257
SINGLE OPN LIN 1812 325079-326591(1) | OPEN LINE FROM BUS 325079 [5N PRINCETON161.00] TO BUS 326591 [5W PRINCETON161.00] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.23464 | 15.2416 | 2 | 25.2
SINGLE OPN LIN 1813 325083-326544(1) | OPEN LINE FROM BUS 325083 [2ALEX CK TAP69.000] TO BUS 326544 [2ALEX CREEK 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.17259 | 15.0311 | 1 | 1.3637
SINGLE OPN LIN 1814 325096-326002(1) | OPEN LINE FROM BUS 325096 [4CANERN NGCC138.00] TO BUS 326002 [7CANERN NGCC345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.2903
SINGLE OPN LIN 1815 325096-326565(23) | OPEN LINE FROM BUS 325096 [4CANERN NGCC138.00] TO BUS 326565 [4INTRNTL TAP138.00] CKT 23 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.9958
SINGLE OPN LIN 1816 325096-326566(71) | OPEN LINE FROM BUS 325096 [4CANERN NGCC138.00] TO BUS 326566 [4CANE RUN 71138.00] CKT 71 | TRUE | Met convergence tolerances | 2 | 0.60923 | 26.9977 | 1 | 7.5
SINGLE OPN LIN 1817 325096-326567(72) | OPEN LINE FROM BUS 325096 [4CANERN NGCC138.00] TO BUS 326567 [4CANE RUN 72138.00] CKT 72 | TRUE | Met convergence tolerances | 2 | 0.61687 | 27.1733 | 1 | 6
SINGLE OPN LIN 1818 325096-326568(7S) | OPEN LINE FROM BUS 325096 [4CANERN NGCC138.00] TO BUS 326568 [4CANE RUN 7S138.00] CKT 7S | TRUE | Met convergence tolerances | 2 | 0.74353 | 30.466
SINGLE OPN LIN 1819 325096-326574(21) | OPEN LINE FROM BUS 325096 [4CANERN NGCC138.00] TO BUS 326574 [4CR11 TAP 138.00] CKT 21 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.9302
SINGLE OPN LIN 1820 325761-325762(1) | OPEN LINE FROM BUS 325761 [2WARRIOR PRP69.000] TO BUS 325762 [2WARRIOR TAP69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.57927 | 26.8931 | 1 | 6.24
SINGLE OPN LIN 1821 325762-325767(1) | OPEN LINE FROM BUS 325762 [2WARRIOR TAP69.000] TO BUS 325767 [2SENTRY 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 2.3779 | 1 | 0.21
SINGLE OPN LIN 1822 325857-325956(Z1) | OPEN LINE FROM BUS 325857 [4BROWN N TIE138.00] TO BUS 325956 [4BROWN N 2 138.00] CKT Z1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.3369
SINGLE OPN LIN 1823 325857-325957(Z1) | OPEN LINE FROM BUS 325857 [4BROWN N TIE138.00] TO BUS 325957 [4BROWN N 1 138.00] CKT Z1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.5252
SINGLE OPN LIN 1824 326001-326002(1) | OPEN LINE FROM BUS 326001 [7CANE RUN TP345.00] TO BUS 326002 [7CANERN NGCC345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.1643
SINGLE OPN LIN 1825 326517-326523(1) | OPEN LINE FROM BUS 326517 [2OVEN FORK 69.000] TO BUS 326523 [2ARKLAND JCT69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 10.0567 | 1 | 14.3636
SINGLE OPN LIN 1826 326523-326534(1) | OPEN LINE FROM BUS 326523 [2ARKLAND JCT69.000] TO BUS 326534 [2ARKLAND 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.22317 | 4.6964 | 1 | 0.45468
SINGLE OPN LIN 1827 326524-326527(1) | OPEN LINE FROM BUS 326524 [2VAN METER 69.000] TO BUS 326527 [2TREEHAVEN T69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 15.7174 | 1 | 2.3496
SINGLE OPN LIN 1828 326525-326527(1) | OPEN LINE FROM BUS 326525 [2TREEHAVEN 69.000] TO BUS 326527 [2TREEHAVEN T69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 15.2226 | 1 | 1.8784
SINGLE OPN LIN 1829 326526-326556(1) | OPEN LINE FROM BUS 326526 [4N SHARKEY 138.00] TO BUS 326556 [4N SHARKEY T138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.17964 | 15.0226 | 1 | 1.2322
SINGLE OPN LIN 1830 326527-326541(1) | OPEN LINE FROM BUS 326527 [2TREEHAVEN T69.000] TO BUS 326541 [2EKPC OFFICE69.000] CKT 1 | TRUE | Met convergence tolerances | 3 | 0.16429 | 20.574 | 2 | 4.228
SINGLE OPN LIN 1831 326528-326974(1) | OPEN LINE FROM BUS 326528 [2BRIDGEPORT 69.000] TO BUS 326974 [2BRIDGPRT 2 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.22025 | 25.4114 | 1 | 5.8078
SINGLE OPN LIN 1832 326530-326539(1) | OPEN LINE FROM BUS 326530 [2EMANUEL 69.000] TO BUS 326539 [2GIRDLER 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.17618 | 21.7259 | 1 | 4.6408
SINGLE OPN LIN 1833 326532-326556(1) | OPEN LINE FROM BUS 326532 [4SHARKEY 138.00] TO BUS 326556 [4N SHARKEY T138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.4531 | 37.6253 | 1 | 8.4668
SINGLE OPN LIN 1834 326552-326553(1) | OPEN LINE FROM BUS 326552 [2SE COAL TP 69.000] TO BUS 326553 [2SE COAL 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 1.8065 | 1 | 0.11
SINGLE OPN LIN 1835 326559-326560(1) | OPEN LINE FROM BUS 326559 [4BGAD TAP 138.00] TO BUS 326560 [4BG ARMY DEP138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.44809 | 21.9518 | 1 | 4.8
SINGLE OPN LIN 1836 326562-326596(Z1) | OPEN LINE FROM BUS 326562 [2PAD PRI 62469.000] TO BUS 326596 [2PAD PRI 61469.000] CKT Z1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.5613
SINGLE OPN LIN 1837 326571-326586(1) | OPEN LINE FROM BUS 326571 [2HUME RD 69.000] TO BUS 326586 [2HUME RD TAP69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14322 | 10.2356 | 1 | 15.02
SINGLE OPN LIN 1838 326578-326579(1) | OPEN LINE FROM BUS 326578 [2HARRDSBRG 169.000] TO BUS 326579 [2HARRDSBRG 269.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.5546
SINGLE OPN LIN 1839 326578-326584(1) | OPEN LINE FROM BUS 326578 [2HARRDSBRG 169.000] TO BUS 326584 [2CORNG7462_369.000] CKT 1 | TRUE | Met convergence tolerances | 3 | 0.35671 | 19.0985 | 2 | 3.74
SINGLE OPN LIN 1840 326579-326580(1) | OPEN LINE FROM BUS 326579 [2HARRDSBRG 269.000] TO BUS 326580 [2CORNIG 825369.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.4264 | 21.445 | 1 | 4.51
SINGLE OPN LIN 1841 326582-326583(1) | OPEN LINE FROM BUS 326582 [2CORNG8251_269.000] TO BUS 326583 [2CORNIG 746169.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.29071 | 17.2909 | 1 | 3.01
SINGLE OPN LIN 1842 326583-326584(1) | OPEN LINE FROM BUS 326583 [2CORNIG 746169.000] TO BUS 326584 [2CORNG7462_369.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.29067 | 17.2958 | 1 | 3.01
SINGLE OPN LIN 1843 326591-326592(1) | OPEN LINE FROM BUS 326591 [5W PRINCETON161.00] TO BUS 326592 [5E PRINCETON161.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.94971 | 42.036 | 1 | 10.7
SINGLE OPN LIN 1844 326593-326594(1) | OPEN LINE FROM BUS 326593 [2GREENVIL N 69.000] TO BUS 326594 [2GREENVL 12 69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.7143 | 32.4725 | 2 | 7.85
SINGLE OPN TIE 1845 324010-248000(1) | OPEN LINE FROM BUS 324010 [7TRIMBL REAC345.00] TO BUS 248000 [06CLIFTY 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.45007 | 26.7175
SINGLE OPN TIE 1846 324021-324044(1) | OPEN LINE FROM BUS 324021 [7BLUEGRASS12345.00] TO BUS 324044 [1BLUEGRASS 118.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.38681 | 21.5929 | 1 | 0.6333
SINGLE OPN TIE 1847 324021-324045(1) | OPEN LINE FROM BUS 324021 [7BLUEGRASS12345.00] TO BUS 324045 [1BLUEGRASS 218.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.38713 | 21.4873 | 1 | 1.4333
SINGLE OPN TIE 1848 324022-324046(1) | OPEN LINE FROM BUS 324022 [7BLUEGRASS 3345.00] TO BUS 324046 [1BLUEGRASS 318.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.38682 | 21.6083 | 1 | 0.6333
SINGLE OPN TIE 1850 324104-324113(1) | OPEN LINE FROM BUS 324104 [7DAVIESS 345.00] TO BUS 324113 [7SMITH 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.73297 | 28.998
SINGLE OPN TIE 1851 324104-340561(1) | OPEN LINE FROM BUS 324104 [7DAVIESS 345.00] TO BUS 340561 [7WILSON 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.20991 | 12.5576
SINGLE OPN TIE 1852 324104-340563(1) | OPEN LINE FROM BUS 324104 [7DAVIESS 345.00] TO BUS 340563 [7COLEMAN 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.15741 | 3.7756
SINGLE OPN TIE 1853 324105-249501(1) | OPEN LINE FROM BUS 324105 [7GHENT 345.00] TO BUS 249501 [08BATESV 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.99384 | 40.8109
SINGLE OPN TIE 1854 324105-249532(1) | OPEN LINE FROM BUS 324105 [7GHENT 345.00] TO BUS 249532 [08TRIMBL 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.66421 | 31.4162
SINGLE OPN TIE 1855 324108-324284-326550(5) | OPEN LINE FROM BUS 324108 [7MILL CREEK 345.00] TO BUS 324284 [4MILL CREEK 138.00] TO BUS 326550 [1MC TR5 TERT13.800] CKT 5 | TRUE | Met convergence tolerances | 1 | 0.14287 | 3.2519
SINGLE OPN TIE 1856 324108-324284-326551(6) | OPEN LINE FROM BUS 324108 [7MILL CREEK 345.00] TO BUS 324284 [4MILL CREEK 138.00] TO BUS 326551 [1MC TR6 TERT13.800] CKT 6 | TRUE | Met convergence tolerances | 1 | 0.14287 | 3.0464
SINGLE OPN TIE 1857 324112-324072(1) | OPEN LINE FROM BUS 324112 [7PINEVILLE 345.00] TO BUS 324072 [8PINEVILLE 500.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.605
SINGLE OPN TIE 1858 324114-249520(1) | OPEN LINE FROM BUS 324114 [7TRIMBLE CO 345.00] TO BUS 249520 [08SPEED 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.92356 | 38.4626
SINGLE OPN TIE 1859 324114-249532(1) | OPEN LINE FROM BUS 324114 [7TRIMBLE CO 345.00] TO BUS 249532 [08TRIMBL 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.66385 | 31.4146
SINGLE OPN TIE 1863 324144-340553(1) | OPEN LINE FROM BUS 324144 [5GREEN RIVER161.00] TO BUS 340553 [5WLSNBR 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.63079 | 24.9976
SINGLE OPN TIE 1864 324148-243668(1) | OPEN LINE FROM BUS 324148 [5WOOTON TAP 161.00] TO BUS 243668 [05WOOTON 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.33932 | 17.9085
SINGLE OPN TIE 1865 324150-360334(1) | OPEN LINE FROM BUS 324150 [5LEBANON JCT161.00] TO BUS 360334 [5SUMMER SHAD161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.7156
SINGLE OPN TIE 1866 324151-360125(1) | OPEN LINE FROM BUS 324151 [5LIVNGSTN CO161.00] TO BUS 360125 [5CALVERT KY 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.8383
SINGLE OPN TIE 1867 324151-360127(1) | OPEN LINE FROM BUS 324151 [5LIVNGSTN CO161.00] TO BUS 360127 [5KENTUCKY HP161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.8124
SINGLE OPN TIE 1868 324156-360452(1) | OPEN LINE FROM BUS 324156 [5PINEVILE SW161.00] TO BUS 360452 [5PINEVILL KY161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.4463
SINGLE OPN TIE 1869 324157-324073(1) | OPEN LINE FROM BUS 324157 [5POCKET N 161.00] TO BUS 324073 [8POCKET N 500.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.81202 | 31.0996
SINGLE OPN TIE 1870 324171-351003(1) | OPEN LINE FROM BUS 324171 [5GRAHMVILE 1161.00] TO BUS 351003 [5JOPPA TS 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.24329 | 18.3097
SINGLE OPN TIE 1871 324172-351002(1) | OPEN LINE FROM BUS 324172 [5GRAHMVILE 2161.00] TO BUS 351002 [5JOPPA S 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.24243 | 2.2169
SINGLE OPN TIE 1872 324173-340553(1) | OPEN LINE FROM BUS 324173 [5MATANZAS 161.00] TO BUS 340553 [5WLSNBR 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.162
SINGLE OPN TIE 1873 324173-340624(1) | OPEN LINE FROM BUS 324173 [5MATANZAS 161.00] TO BUS 340624 [5BRTAP 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.8686
SINGLE OPN TIE 1875 324211-251561(1) | OPEN LINE FROM BUS 324211 [4BLACKWELL 138.00] TO BUS 251561 [08BLACKW 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.5578
SINGLE OPN TIE 1877 324217-325012(1) | OPEN LINE FROM BUS 324217 [4BROWN PLANT138.00] TO BUS 325012 [1BROWN SOLAR13.200] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.94953 | 38.0349
SINGLE OPN TIE 1878 324227-248009(1) | OPEN LINE FROM BUS 324227 [4CARROLLTON 138.00] TO BUS 248009 [06CLIFTY 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.905
SINGLE OPN TIE 1879 324231-253623(1) | OPEN LINE FROM BUS 324231 [4CLOVERPORT 138.00] TO BUS 253623 [10CANTAP 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14492 | 2.9814
SINGLE OPN TIE 1880 324231-340615(1) | OPEN LINE FROM BUS 324231 [4CLOVERPORT 138.00] TO BUS 340615 [4N.HARD 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.5007
SINGLE OPN TIE 1881 324232-324399(1) | OPEN LINE FROM BUS 324232 [4CANE RN 11A138.00] TO BUS 324399 [1CANERN11 14.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.50756 | 23.5075 | 1 | 5.4
SINGLE OPN TIE 1884 324253-249723(1) | OPEN LINE FROM BUS 324253 [4GHENT 138.00] TO BUS 249723 [08FAIRVW 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.62446 | 27.962
SINGLE OPN TIE 1886 324256-324309(1) | OPEN LINE FROM BUS 324256 [4GR RVR STL 138.00] TO BUS 324309 [4SMITH 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.282
SINGLE OPN TIE 1887 324260-340615(1) | OPEN LINE FROM BUS 324260 [4HARDINSBURG138.00] TO BUS 340615 [4N.HARD 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.5994
SINGLE OPN TIE 1889 324265-249763(1) | OPEN LINE FROM BUS 324265 [4JEFFRSONV T138.00] TO BUS 249763 [08JEFF 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.1275
SINGLE OPN TIE 1890 324267-247508(1) | OPEN LINE FROM BUS 324267 [4KENTON 138.00] TO BUS 247508 [05SARDINIA 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.22675 | 3.2535
SINGLE OPN TIE 1892 324268-324170(1) | OPEN LINE FROM BUS 324268 [4KNOB CREEK 138.00] TO BUS 324170 [1KNOB CRK 34.500] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.97858 | 60.9034 | 1 | 15.4897
SINGLE OPN TIE 1899 324289-249789(1) | OPEN LINE FROM BUS 324289 [4NORTHSIDE 138.00] TO BUS 249789 [08LOUCMJ 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.8608
SINGLE OPN TIE 1901 324294-249730(1) | OPEN LINE FROM BUS 324294 [4PADDYS WEST138.00] TO BUS 249730 [08GALAGH 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.67299 | 31.1283
SINGLE OPN TIE 1902 324295-324431(4A) | OPEN LINE FROM BUS 324295 [4PADDYS RUN 138.00] TO BUS 324431 [1PADDYR1 14.000] CKT 4A | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.8372
SINGLE OPN TIE 1903 324295-324596(5) | OPEN LINE FROM BUS 324295 [4PADDYS RUN 138.00] TO BUS 324596 [1PADDYR2A 14.000] CKT 5 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.5083
SINGLE OPN TIE 1904 324295-324675-324635(3) | OPEN LINE FROM BUS 324295 [4PADDYS RUN 138.00] TO BUS 324675 [2PADDYS RUN 69.000] TO BUS 324635 [1PADDYR2B 14.000] CKT 3 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.2342
SINGLE OPN TIE 1906 324311-324366(1) | OPEN LINE FROM BUS 324311 [4TIP TOP 138.00] TO BUS 324366 [1TIPTOP 1 34.500] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.71224 | 32.3885 | 1 | 7.84
SINGLE OPN TIE 1907 324311-324753-326511(2) | OPEN LINE FROM BUS 324311 [4TIP TOP 138.00] TO BUS 324753 [2TIP TOP 2 69.000] TO BUS 326511 [1TIPTOP 34.500] CKT 2 | TRUE | Met convergence tolerances | 2 | 0.14573 | 10.45 | 2 | 16.19
SINGLE OPN TIE 1908 324316-242605(1) | OPEN LINE FROM BUS 324316 [4VIRGINIA CI138.00] TO BUS 242605 [05CLNCHR 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.2691
SINGLE OPN TIE 1910 324405-326500(1) | OPEN LINE FROM BUS 324405 [2ADAMS 69.000] TO BUS 326500 [1ADAMS 34.500] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.14287 | 1.5132
SINGLE OPN TIE 1911 324412-326501(1) | OPEN LINE FROM BUS 324412 [2ANDOVER 69.000] TO BUS 326501 [1ANDOVE 34.500] CKT 1 | TRUE | Met convergence tolerances | 3 | 0.369 | 19.6031 | 1 | 3.87
SINGLE OPN TIE 1915 324437-324063(1) | OPEN LINE FROM BUS 324437 [2BEVIER KU 69.000] TO BUS 324063 [1BEVIER 34.500] CKT 1 | TRUE | Met convergence tolerances | 7 | 0.58902 | 27.1571 | 4 | 6.28
SINGLE OPN TIE 1918 324446-324397(1) | OPEN LINE FROM BUS 324446 [2BOND 69.000] TO BUS 324397 [1BOND 23.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.36907 | 19.374 | 1 | 3.82
SINGLE OPN TIE 1923 324503-324398(1) | OPEN LINE FROM BUS 324503 [2DORCHESTER 69.000] TO BUS 324398 [1DORCHEST 23.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.35631 | 18.9827 | 1 | 3.75
SINGLE OPN TIE 1924 324503-326504(1) | OPEN LINE FROM BUS 324503 [2DORCHESTER 69.000] TO BUS 326504 [1DORCHE 34.500] CKT 1 | TRUE | Met convergence tolerances | 8 | 0.14287 | 4.2524 | 2 | 0.22
SINGLE OPN TIE 1925 324507-324123(1) | OPEN LINE FROM BUS 324507 [2EARLINGTON 69.000] TO BUS 324123 [1EARLINGT 34.500] CKT 1 | TRUE | Met convergence tolerances | 7 | 0.34123 | 18.4031 | 3 | 3.56
SINGLE OPN TIE 1927 324512-362916(1) | OPEN LINE FROM BUS 324512 [2EDDYV PR TP69.000] TO BUS 362916 [2KY DAM 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.0585
SINGLE OPN TIE 1933 324533-326505(1) | OPEN LINE FROM BUS 324533 [2FRANKFORT 169.000] TO BUS 326505 [1FFRT 34.500] CKT 1 | TRUE | Met convergence tolerances | 5 | 0.14287 | 9.9023 | 3 | 14.48
SINGLE OPN TIE 1934 324550-324128(1) | OPEN LINE FROM BUS 324550 [2GREEN RIVER69.000] TO BUS 324128 [1GREEN RIVER34.500] CKT 1 | TRUE | Met convergence tolerances | 6 | 0.62704 | 26.5495 | 3 | 6.09
SINGLE OPN TIE 1935 324551-324669(1) | OPEN LINE FROM BUS 324551 [2GR RVR STL 69.000] TO BUS 324669 [2OMU 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.5671
SINGLE OPN TIE 1937 324574-324043(1) | OPEN LINE FROM BUS 324574 [2HILLCREST 69.000] TO BUS 324043 [1ZORN 13.800] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 1.3972
SINGLE OPN TIE 1940 324578-324142(1) | OPEN LINE FROM BUS 324578 [2HARDESTY B 69.000] TO BUS 324142 [1HARDSTY 34.500] CKT 1 | TRUE | Met convergence tolerances | 4 | 0.28063 | 17.0532 | 2 | 2.91
SINGLE OPN TIE 1941 324583-324168(1) | OPEN LINE FROM BUS 324583 [2IMBODEN 69.000] TO BUS 324168 [1IMBODEN 34.500] CKT 1 | TRUE | Met convergence tolerances | 6 | 0.14287 | 4.8672 | 2 | 0.62
SINGLE OPN TIE 1945 324664-326507(1) | OPEN LINE FROM BUS 324664 [2OAK HILL KU69.000] TO BUS 326507 [1OAK HI 34.500] CKT 1 | TRUE | Met convergence tolerances | 8 | 0.96953 | 40.9906 | 4 | 9.78
SINGLE OPN TIE 1948 324689-324184(1) | OPEN LINE FROM BUS 324689 [2POCKET 69.000] TO BUS 324184 [1POCKET 34.500] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.14287 | 3.2929 | 2 | 0.35
SINGLE OPN TIE 1949 324693-326509(1) | OPEN LINE FROM BUS 324693 [2PRINCETON 69.000] TO BUS 326509 [1PRINCE 34.500] CKT 1 | TRUE | Met convergence tolerances | 5 | 0.3726 | 19.3947 | 3 | 3.86
SINGLE OPN TIE 1950 324707-243740(Z1) | OPEN LINE FROM BUS 324707 [2RODBURN 69.000] TO BUS 243740 [05MOREHE 69.000] CKT Z1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.7677
SINGLE OPN TIE 1952 324712-362116(1) | OPEN LINE FROM BUS 324712 [2SO PADUCAH 69.000] TO BUS 362116 [2KY HYDRO 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.5902
SINGLE OPN TIE 1959 324764-324368(1) | OPEN LINE FROM BUS 324764 [2WEST CLIFF 69.000] TO BUS 324368 [1W CLIFF 34.500] CKT 1 | TRUE | Met convergence tolerances | 4 | 0.41294 | 18.6118 | 1 | 0.42
SINGLE OPN TIE 1962 324803-324057(1) | OPEN LINE FROM BUS 324803 [2BEAR TRACK 69.000] TO BUS 324057 [1BEAR TRA 34.500] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.14287 | 2.1896 | 1 | 0.18
SINGLE OPN TIE 1964 324947-324190(1) | OPEN LINE FROM BUS 324947 [2RUMSEY 69.000] TO BUS 324190 [1RUMSEY 34.500] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 1.5652
SINGLE OPN TIE 1965 324948-324883(1) | OPEN LINE FROM BUS 324948 [2SALEM KU 69.000] TO BUS 324883 [1SALEM 34.500] CKT 1 | TRUE | Met convergence tolerances | 3 | 0.21416 | 16.0349 | 1 | 2.22
SINGLE OPN TIE 1967 325013-248009(1) | OPEN LINE FROM BUS 325013 [4CLIFTY TAP1138.00] TO BUS 248009 [06CLIFTY 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.0916
SINGLE OPN TIE 1968 325014-248009(1) | OPEN LINE FROM BUS 325014 [4CLIFTY TAP2138.00] TO BUS 248009 [06CLIFTY 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.32934 | 18.2582
SINGLE OPN TIE 1969 325014-250057(1) | OPEN LINE FROM BUS 325014 [4CLIFTY TAP2138.00] TO BUS 250057 [08M.FORT 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.32988 | 18.2617
SINGLE OPN TIE 1970 325015-324309(1) | OPEN LINE FROM BUS 325015 [4SMITH TAP 138.00] TO BUS 324309 [4SMITH 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.2728
SINGLE OPN TIE 1972 325047-325046(1) | OPEN LINE FROM BUS 325047 [5ASHWOOD 161.00] TO BUS 325046 [1ASHWOOD COL34.500] CKT 1 | TRUE | Met convergence tolerances | 3 | 0.60546 | 32.1854 | 1 | 1.4
SINGLE OPN TIE 1973 325073-340651(1) | OPEN LINE FROM BUS 325073 [7REDMON RD 345.00] TO BUS 340651 [OTTERCRK345 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.40348 | 19.535
SINGLE OPN TIE 1976 325116-325117(1) | OPEN LINE FROM BUS 325116 [4RHUDES CR 138.00] TO BUS 325117 [1RHUDES COL 34.500] CKT 1 | TRUE | Met convergence tolerances | 3 | 0.14287 | 13.4352 | 1 | 0.16
SINGLE OPN TIE 1979 326569-248830(1) | OPEN LINE FROM BUS 326569 [7KENZIG ROAD345.00] TO BUS 248830 [07RAMSY5 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.17784 | 9.3341
SINGLE OPN TIE 1980 326569-249520(1) | OPEN LINE FROM BUS 326569 [7KENZIG ROAD345.00] TO BUS 249520 [08SPEED 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.6824
SINGLE OPN TIE 1981 326596-324697(1) | OPEN LINE FROM BUS 326596 [2PAD PRI 61469.000] TO BUS 324697 [1KMPA PAD2 13.800] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.29231 | 15.0642 | 1 | 1.144
SINGLE OPN TIE 1982 326596-324933(1) | OPEN LINE FROM BUS 326596 [2PAD PRI 61469.000] TO BUS 324933 [1KMPA PAD1 13.800] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.2923 | 15.1754 | 1 | 1.144
SINGLE OPN TIE 1985 326998-361788(1) | OPEN LINE FROM BUS 326998 [5BULLITT TAP161.00] TO BUS 361788 [5SUM SHAD TP161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.8329
MERE SWS | REMOVE SWSHUNT FROM BUS 324800 [4MERE TVA 138.00] | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.6892
B-69-51 | CLOSE BRANCH FROM BUS 324939 [2RICHMND 4 69.000] TO BUS 324940 [2RICHMND J 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.1041
OPEN BRANCH FROM BUS 324936 [2RICHMND IND69.000] TO BUS 324940 [2RICHMND J 69.000] CKT 1
OPEN BRANCH FROM BUS 324530 [2FAWKES 69.000] TO BUS 324700 [2RICHMND SO 69.000] CKT 1
B-69-446 | OPEN BRANCH FROM BUS 324631 [2MADSNV LP W69.000] TO BUS 324893 [2MADSNV GE T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.4013
CLOSE BRANCH FROM BUS 324873 [2HANSON JCT 69.000] TO BUS 324895 [2MADSNV HO 69.000] CKT 1
B-69-65 | OPEN BRANCH FROM BUS 324630 [2MADSNV LP E69.000] TO BUS 324902 [2MCCOY AVE 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.3922
CLOSE BRANCH FROM BUS 324873 [2HANSON JCT 69.000] TO BUS 324895 [2MADSNV HO 69.000] CKT 1
B-69-63 | OPEN BRANCH FROM BUS 324631 [2MADSNV LP W69.000] TO BUS 324893 [2MADSNV GE T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.4073
OPEN BRANCH FROM BUS 324506 [2EARLINGTN N69.000] TO BUS 324631 [2MADSNV LP W69.000] CKT 1
CLOSE BRANCH FROM BUS 324873 [2HANSON JCT 69.000] TO BUS 324895 [2MADSNV HO 69.000] CKT 1
B-69-66 | OPEN BRANCH FROM BUS 324630 [2MADSNV LP E69.000] TO BUS 324902 [2MCCOY AVE 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.3936
OPEN BRANCH FROM BUS 324630 [2MADSNV LP E69.000] TO BUS 324506 [2EARLINGTN N69.000] CKT 1
CLOSE BRANCH FROM BUS 324873 [2HANSON JCT 69.000] TO BUS 324895 [2MADSNV HO 69.000] CKT 1
B-69-53 | CLOSE BRANCH FROM BUS 324824 [2CLINCH VALL69.000] TO BUS 324826 [2CLINCH V SW69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.4954
OPEN BRANCH FROM BUS 324743 [2SAINT PAUL 69.000] TO BUS 324851 [2DWINA TAP 69.000] CKT 1
OPEN BRANCH FROM BUS 324663 [2NORTON EAST69.000] TO BUS 324503 [2DORCHESTER 69.000] CKT 1
B-69-36 | CLOSE BRANCH FROM BUS 324492 [2CYNTHIAN SW69.000] TO BUS 324672 [2OXFORD EK T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14515 | 4.7617
OPEN BRANCH FROM BUS 324405 [2ADAMS 69.000] TO BUS 324500 [2DELAPLAIN T69.000] CKT 1
B-69-49 | OPEN BRANCH FROM BUS 324943 [2ROGERS GAP 69.000] TO BUS 324951 [2SCOTT CO 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.9176
CLOSE BRANCH FROM BUS 324844 [2DELAPLAIN 69.000] TO BUS 324500 [2DELAPLAIN T69.000] CKT 1
B-69-37 | OPEN BRANCH FROM BUS 324568 [2HIGBY 618 69.000] TO BUS 325000 [2WIL DOWN T269.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.16135 | 4.4059
CLOSE BRANCH FROM BUS 341383 [2DAVIS 69.000] TO BUS 324842 [2DAVIS TAP 69.000] CKT 1
OPEN BRANCH FROM BUS 324842 [2DAVIS TAP 69.000] TO BUS 324967 [2SPEAR STA A69.000] CKT 1
OPEN BRANCH FROM BUS 325000 [2WIL DOWN T269.000] TO BUS 324735 [2SOUTH POINT69.000] CKT 1
B-69-11 | OPEN BRANCH FROM BUS 324735 [2SOUTH POINT69.000] TO BUS 325000 [2WIL DOWN T269.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.16042 | 4.3677
CLOSE BRANCH FROM BUS 341383 [2DAVIS 69.000] TO BUS 324842 [2DAVIS TAP 69.000] CKT 1
OPEN BRANCH FROM BUS 324842 [2DAVIS TAP 69.000] TO BUS 324967 [2SPEAR STA A69.000] CKT 1
B-69-50 | OPEN BRANCH FROM BUS 324434 [2BEREA TAP 69.000] TO BUS 324612 [2LAKE REBA 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.22388 | 4.3407
CLOSE BRANCH FROM BUS 324436 [2BEREA EK TP69.000] TO BUS 341098 [2BEREAKU T 69.000] CKT 1
OPEN BRANCH FROM BUS 324435 [2BEREA NORTH69.000] TO BUS 324434 [2BEREA TAP 69.000] CKT 1
B-69-316A | OPEN BRANCH FROM BUS 324212 [4BLUE LICK 138.00] TO BUS 324443 [2BLUE LICK 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 3.1971
CLOSE BRANCH FROM BUS 324958 [2SHEPHRDSV T69.000] TO BUS 325021 [2CONESTOGA 69.000] CKT 1
CLOSE BRANCH FROM BUS 324915 [2MT WAS EK J69.000] TO BUS 324402 [2FAIRMOUNT T69.000] CKT 1
CLOSE BRANCH FROM BUS 342082 [2PLEAS GRV 69.000] TO BUS 324925 [2PLEAS GRV T69.000] CKT 1
OPEN BRANCH FROM BUS 324925 [2PLEAS GRV T69.000] TO BUS 324806 [2BEULAH EKPC69.000] CKT 1
OPEN BRANCH FROM BUS 324915 [2MT WAS EK J69.000] TO BUS 325006 [2W MT WSH EK69.000] CKT 1
B-69-9 | OPEN BRANCH FROM BUS 324450 [2BOYLE CO 69.000] TO BUS 324760 [2VAKSDAHL AV69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.8073
CLOSE BRANCH FROM BUS 324838 [2DANV IND TP69.000] TO BUS 324839 [2DANVILE IND69.000] CKT 1
OPEN BRANCH FROM BUS 324970 [2STANFORD KU69.000] TO BUS 324957 [2SHELBY CI T69.000] CKT 1
SW-1000 | OPEN BRANCH FROM BUS 324275 [4LOUDON AVE 138.00] TO BUS 324617 [2LOUDON 618 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.1984
OPEN BRANCH FROM BUS 324618 [2LOUDON 628 69.000] TO BUS 324617 [2LOUDON 618 69.000] CKT 1
B-69-47 | OPEN BRANCH FROM BUS 325002 [2WILS DOWN 169.000] TO BUS 324780 [2WIL DOWN T169.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.3786
B-69-48 | OPEN BRANCH FROM BUS 325003 [2WILS DOWN 269.000] TO BUS 325000 [2WIL DOWN T269.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.2705
B-69-52 | OPEN BRANCH FROM BUS 324701 [2RICHMND 69.000] TO BUS 324937 [2RICHMND 2 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.7121
CLOSE BRANCH FROM BUS 324939 [2RICHMND 4 69.000] TO BUS 324940 [2RICHMND J 69.000] CKT 1
B-69-56 | OPEN BRANCH FROM BUS 324564 [2HARLAN WYE 69.000] TO BUS 324956 [2SHAWNEE GAS69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.3063
CLOSE BRANCH FROM BUS 325007 [2YANCY TAP 69.000] TO BUS 324814 [2CATRON CK T69.000] CKT 1
B-69-57 | OPEN BRANCH FROM BUS 324615 [2LONDON 69.000] TO BUS 324459 [2BUSH TAP 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.5596
CLOSE BRANCH FROM BUS 324627 [2MANCHEST KU69.000] TO BUS 341806 [2MANCHESTER 69.000] CKT 1
B-69-58 | OPEN BRANCH FROM BUS 324965 [2SOMERSET NO69.000] TO BUS 324950 [2SCIENC HILL69.000] CKT 1 | TRUE | Met convergence tolerances | 3 | 0.44105 | 21.6603 | 2 | 4.59
B-69-60 | OPEN BRANCH FROM BUS 324514 [2ELIHU 69.000] TO BUS 324964 [2SOMERSET 3 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6979
CLOSE BRANCH FROM BUS 324961 [2SOMERSET GE69.000] TO BUS 324965 [2SOMERSET NO69.000] CKT 1
B-69-61 | OPEN BRANCH FROM BUS 324495 [2DANVILLE N 69.000] TO BUS 324841 [2DANVILLE W 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6578
CLOSE BRANCH FROM BUS 324838 [2DANV IND TP69.000] TO BUS 324839 [2DANVILE IND69.000] CKT 1
B-69-62 | OPEN BRANCH FROM BUS 324858 [2ETOWN 5 69.000] TO BUS 324519 [2ETOWN KU 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.21054 | 3.061
CLOSE BRANCH FROM BUS 324520 [2ETOWN 2 TAP69.000] TO BUS 324857 [2ETOWN 2 69.000] CKT 1
B-69-318 | OPEN BRANCH FROM BUS 324651 [2MUD LANE 69.000] TO BUS 324730 [2SMYRNA 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 5.6071
CLOSE BRANCH FROM BUS 324526 [2FAIRMOUNT 269.000] TO BUS 324859 [2FAIRMOUNT 169.000] CKT 1
B-69-319 | OPEN BRANCH FROM BUS 324466 [2CARROLLTON 69.000] TO BUS 324878 [2HUNT BTM TP69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.5515
CLOSE BRANCH FROM BUS 325033 [2BEDFORD KU 69.000] TO BUS 324888 [2LAWRENCE 69.000] CKT 1
B-69-67 | OPEN BRANCH FROM BUS 324899 [2MAYSVILLE E69.000] TO BUS 324589 [2KENTON 688 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.201
CLOSE BRANCH FROM BUS 324901 [2MAYSVILLE W69.000] TO BUS 324900 [2MAYSVILLE M69.000] CKT 1
B-69-693 | OPEN BRANCH FROM BUS 324901 [2MAYSVILLE W69.000] TO BUS 324882 [2KENTON 698 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.342 | 18.4683 | 1 | 3.7
B-69-69 | OPEN BRANCH FROM BUS 324639 [2MILLRSB624 69.000] TO BUS 324812 [2CARLISLE 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.277
CLOSE BRANCH FROM BUS 341878 [2MILLERSB EK69.000] TO BUS 324812 [2CARLISLE 69.000] CKT 1
B-69-72 | OPEN BRANCH FROM BUS 324797 [2AVON T1 69.000] TO BUS 324796 [2AVON 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.4307
CLOSE BRANCH FROM BUS 324796 [2AVON 69.000] TO BUS 325081 [2BRIAR HILL 69.000] CKT Z1
B-69-74 | OPEN BRANCH FROM BUS 324988 [2WEST HIGH 69.000] TO BUS 324766 [2W HIGH T1 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.3642
CLOSE BRANCH FROM BUS 324988 [2WEST HIGH 69.000] TO BUS 324986 [2W HIGH T2 69.000] CKT 1
B-69-76 | OPEN BRANCH FROM BUS 324753 [2TIP TOP 2 69.000] TO BUS 324807 [2BRANDENBURG69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.609
CLOSE BRANCH FROM BUS 324921 [2ARCH CHEM 69.000] TO BUS 324807 [2BRANDENBURG69.000] CKT 1
B-69-77 | OPEN BRANCH FROM BUS 324976 [2TIP TOP 1 69.000] TO BUS 324921 [2ARCH CHEM 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.5843
CLOSE BRANCH FROM BUS 324921 [2ARCH CHEM 69.000] TO BUS 324807 [2BRANDENBURG69.000] CKT 1
B-69-73 | OPEN BRANCH FROM BUS 324988 [2WEST HIGH 69.000] TO BUS 324766 [2W HIGH T1 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.4193
B-69-10 | OPEN BRANCH FROM BUS 324503 [2DORCHESTER 69.000] TO BUS 324517 [2ESSERVILLE 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.19846 | 12.3227
CLOSE BRANCH FROM BUS 324824 [2CLINCH VALL69.000] TO BUS 324826 [2CLINCH V SW69.000] CKT 1
OPEN BRANCH FROM BUS 324824 [2CLINCH VALL69.000] TO BUS 324446 [2BOND 69.000] CKT 1
B-345-449 | OPEN LINE FROM BUS 324565 [7NAS TAP 345.00] TO BUS 324566 [7NAS 222 345.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.15917 | 13.2411 | 1 | 106.67
OPEN LINE FROM BUS 324565 [7NAS TAP 345.00] TO BUS 324105 [7GHENT 345.00] CKT 1
OPEN LINE FROM BUS 324565 [7NAS TAP 345.00] TO BUS 324109 [7NAS 345.00] CKT 1
B-138-123 | OPEN LINE FROM BUS 324319 [4W FRANKFORT138.00] TO BUS 324765 [2W FRANKFORT69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.18073 | 9.1346
OPEN LINE FROM BUS 324319 [4W FRANKFORT138.00] TO BUS 324115 [7W FRANKFORT345.00] CKT 1
OPEN LINE FROM BUS 324319 [4W FRANKFORT138.00] TO BUS 324250 [4E FRANKFORT138.00] CKT 1
B-69-322 | OPEN BRANCH FROM BUS 324484 [2CORYDON 69.000] TO BUS 324754 [2TUNNEL H KU69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 3.001
CLOSE BRANCH FROM BUS 324810 [2CALHOUN 69.000] TO BUS 324795 [2ASHBYBRG PU69.000] CKT 1
B-69-324 | OPEN BRANCH FROM BUS 324567 [2HIGBY MIL 269.000] TO BUS 324780 [2WIL DOWN T169.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 1.5185
OPEN BRANCH FROM BUS 324569 [2HIGBY 608 69.000] TO BUS 324567 [2HIGBY MIL 269.000] CKT 1
OPEN BRANCH FROM BUS 325002 [2WILS DOWN 169.000] TO BUS 324780 [2WIL DOWN T169.000] CKT 1
B-69-79 | OPEN BRANCH FROM BUS 324217 [4BROWN PLANT138.00] TO BUS 324318 [4WEST CLIFF 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.3473
OPEN BRANCH FROM BUS 324318 [4WEST CLIFF 138.00] TO BUS 324764 [2WEST CLIFF 69.000] CKT 1
B-69-80 | OPEN BRANCH FROM BUS 324217 [4BROWN PLANT138.00] TO BUS 324318 [4WEST CLIFF 138.00] CKT 2 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.3222
OPEN BRANCH FROM BUS 324318 [4WEST CLIFF 138.00] TO BUS 324764 [2WEST CLIFF 69.000] CKT 2
B-69-325 | OPEN BRANCH FROM BUS 324771 [2WATTERSON 69.000] TO BUS 324402 [2FAIRMOUNT T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 5.1895
CLOSE BRANCH FROM BUS 324526 [2FAIRMOUNT 269.000] TO BUS 324859 [2FAIRMOUNT 169.000] CKT 1
B-69-327 | OPEN LINE FROM BUS 326559 [4BGAD TAP 138.00] TO BUS 326560 [4BG ARMY DEP138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.33523 | 18.4696 | 1 | 4.8
OPEN LINE FROM BUS 326559 [4BGAD TAP 138.00] TO BUS 324273 [4LAKE REBA 138.00] CKT Z1
OPEN LINE FROM BUS 326559 [4BGAD TAP 138.00] TO BUS 324276 [4LAKE REBA T138.00] CKT 1
OPEN BRANCH FROM BUS 324273 [4LAKE REBA 138.00] TO BUS 324612 [2LAKE REBA 69.000] CKT 1
B-138-115 | OPEN LINE FROM BUS 324308 [4SHREWSBURY 138.00] TO BUS 324800 [4MERE TVA 138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.64262 | 26.5069
OPEN LINE FROM BUS 324308 [4SHREWSBURY 138.00] TO BUS 324272 [4LEITCHFIELD138.00] CKT 1
OPEN LINE FROM BUS 324308 [4SHREWSBURY 138.00] TO BUS 324291 [4OHIO COUNTY138.00] CKT 1
B-69-448 | OPEN BRANCH FROM BUS 324530 [2FAWKES 69.000] TO BUS 324656 [2N MADISON T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 3.9978
CLOSE BRANCH FROM BUS 324842 [2DAVIS TAP 69.000] TO BUS 341383 [2DAVIS 69.000] CKT 1
OPEN BRANCH FROM BUS 324987 [2W HICKMAN 69.000] TO BUS 324842 [2DAVIS TAP 69.000] CKT 1
B-161-131 | OPEN BRANCH FROM BUS 324154 [5PADDYS RUN 161.00] TO BUS 324295 [4PADDYS RUN 138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 3.8872
OPEN LINE FROM BUS 324154 [5PADDYS RUN 161.00] TO BUS 324150 [5LEBANON JCT161.00] CKT 1
B-69-334 | OPEN BRANCH FROM BUS 324569 [2HIGBY 608 69.000] TO BUS 324661 [2NICHLSV 7 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.8199
CLOSE BRANCH FROM BUS 324728 [2SHUN PIKE 69.000] TO BUS 324980 [2RJ CORMAN 69.000] CKT 1
B-69-335 | OPEN BRANCH FROM BUS 324501 [2DIX DAM 69.000] TO BUS 324781 [2WILMORE T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.4654
CLOSE BRANCH FROM BUS 324728 [2SHUN PIKE 69.000] TO BUS 324980 [2RJ CORMAN 69.000] CKT 1
B-138-447 | OPEN LINE FROM BUS 324307 [4SHARKEY TAP138.00] TO BUS 326556 [4N SHARKEY T138.00] CKT 1 | TRUE | Met convergence tolerances | 3 | 0.51287 | 40.5941 | 2 | 9.699
OPEN LINE FROM BUS 324307 [4SHARKEY TAP138.00] TO BUS 324245 [4FARMERS TAP138.00] CKT 1
OPEN LINE FROM BUS 324307 [4SHARKEY TAP138.00] TO BUS 324302 [4RODBURN 138.00] CKT 1
OPEN LINE FROM BUS 324245 [4FARMERS TAP138.00] TO BUS 324246 [4FARMERS 138.00] CKT 1
OPEN LINE FROM BUS 324245 [4FARMERS TAP138.00] TO BUS 324310 [4SPENCER RD 138.00] CKT 1
OPEN LINE FROM BUS 324246 [4FARMERS 138.00] TO BUS 324528 [2FARMERS 69.000] CKT 1
OPEN BRANCH FROM BUS 324707 [2RODBURN 69.000] TO BUS 243740 [05MOREHE 69.000] CKT Z1
B-69-330 | OPEN BRANCH FROM BUS 324707 [2RODBURN 69.000] TO BUS 243740 [05MOREHE 69.000] CKT Z1 | TRUE | Met convergence tolerances | 3 | 0.51027 | 41.0328 | 2 | 9.699
OPEN LINE FROM BUS 324245 [4FARMERS TAP138.00] TO BUS 324246 [4FARMERS 138.00] CKT 1
OPEN LINE FROM BUS 324245 [4FARMERS TAP138.00] TO BUS 324307 [4SHARKEY TAP138.00] CKT 1
OPEN LINE FROM BUS 324245 [4FARMERS TAP138.00] TO BUS 324310 [4SPENCER RD 138.00] CKT 1
OPEN LINE FROM BUS 324307 [4SHARKEY TAP138.00] TO BUS 326556 [4N SHARKEY T138.00] CKT 1
OPEN LINE FROM BUS 324307 [4SHARKEY TAP138.00] TO BUS 324302 [4RODBURN 138.00] CKT 1
B-69-332 | OPEN BRANCH FROM BUS 341059 [2BARREN CO 69.000] TO BUS 341651 [2HORSECAVE J69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.1712
OPEN BRANCH FROM BUS 341914 [2MUNFVILKU T69.000] TO BUS 341651 [2HORSECAVE J69.000] CKT 1
CLOSE BRANCH FROM BUS 342241 [2SEYMOUR T 69.000] TO BUS 341650 [2HORSECAVE T69.000] CKT 1
B-69-337 | OPEN BRANCH FROM BUS 324640 [2MILL CREEK 69.000] TO BUS 324619 [2LOWER MIL C69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.5239
B-69-338 | OPEN BRANCH FROM BUS 324488 [2CANE RUN SW69.000] TO BUS 324757 [2UPR MIL CRK69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.3156
B-69-450 | OPEN BRANCH FROM BUS 324302 [4RODBURN 138.00] TO BUS 324707 [2RODBURN 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.5998
OPEN BRANCH FROM BUS 324707 [2RODBURN 69.000] TO BUS 243740 [05MOREHE 69.000] CKT Z1
B-500-97 | OPEN LINE FROM BUS 324073 [8POCKET N 500.00] TO BUS 324157 [5POCKET N 161.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.16781 | 8.5564
OPEN LINE FROM BUS 324073 [8POCKET N 500.00] TO BUS 360102 [8PHIPPS B NP500.00] CKT 1
OPEN LINE FROM BUS 324073 [8POCKET N 500.00] TO BUS 324072 [8PINEVILLE 500.00] CKT 1
OPEN LINE FROM BUS 324072 [8PINEVILLE 500.00] TO BUS 324112 [7PINEVILLE 345.00] CKT 1
B-69-339 | OPEN LINE FROM BUS 326528 [2BRIDGEPORT 69.000] TO BUS 326974 [2BRIDGPRT 2 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 2.3041
OPEN LINE FROM BUS 326528 [2BRIDGEPORT 69.000] TO BUS 324535 [2E FRANKFORT69.000] CKT 1
OPEN LINE FROM BUS 326528 [2BRIDGEPORT 69.000] TO BUS 324765 [2W FRANKFORT69.000] CKT 1
CLOSE BRANCH FROM BUS 326973 [2BRIDGPRT 1 69.000] TO BUS 326974 [2BRIDGPRT 2 69.000] CKT Z0
B-69-340 | OPEN BRANCH FROM BUS 324765 [2W FRANKFORT69.000] TO BUS 326973 [2BRIDGPRT 1 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.4361
CLOSE BRANCH FROM BUS 326973 [2BRIDGPRT 1 69.000] TO BUS 326974 [2BRIDGPRT 2 69.000] CKT Z0
BB-2000 | OPEN LINE FROM BUS 324236 [4RICHMND NO 138.00] TO BUS 324229 [4CLARK CO 138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.63591 | 27.2228 | 1 | 8.1
OPEN LINE FROM BUS 324236 [4RICHMND NO 138.00] TO BUS 324248 [4FAWKES KU 138.00] CKT 1
BB-1366 | OPEN LINE FROM BUS 324994 [2WARSAW KU 69.000] TO BUS 325025 [2WARSAW EAST69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 8.698 | 6 | 12.64
OPEN LINE FROM BUS 324994 [2WARSAW KU 69.000] TO BUS 324911 [2MARKLAND DM69.000] CKT 1
OPEN LINE FROM BUS 324994 [2WARSAW KU 69.000] TO BUS 324966 [2SPARTA KU 69.000] CKT 1
OPEN LINE FROM BUS 324966 [2SPARTA KU 69.000] TO BUS 324455 [2BROMLEY 69.000] CKT 1
OPEN LINE FROM BUS 324455 [2BROMLEY 69.000] TO BUS 342007 [2OWEN CO 69.000] CKT 1
OPEN LINE FROM BUS 324455 [2BROMLEY 69.000] TO BUS 324252 [2SCHOLLS 69.000] CKT 1
OPEN LINE FROM BUS 324252 [2SCHOLLS 69.000] TO BUS 324199 [2OWENTON 69.000] CKT 1
BB-1452 | OPEN LINE FROM BUS 324634 [2METAL+THERM69.000] TO BUS 324849 [2DOW CORNING69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 7.0789 | 4 | 10.12
OPEN LINE FROM BUS 324634 [2METAL+THERM69.000] TO BUS 324466 [2CARROLLTON 69.000] CKT 1
OPEN LINE FROM BUS 324849 [2DOW CORNING69.000] TO BUS 324867 [2GHENT 69.000] CKT 1
OPEN LINE FROM BUS 324867 [2GHENT 69.000] TO BUS 324911 [2MARKLAND DM69.000] CKT 1
OPEN LINE FROM BUS 324911 [2MARKLAND DM69.000] TO BUS 324994 [2WARSAW KU 69.000] CKT 1
BB-1386 | OPEN LINE FROM BUS 324602 [2LAWRENCE TP69.000] TO BUS 324828 [2CAMPBBRG KU69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.69599 | 47.9468 | 3 | 12.5211
OPEN LINE FROM BUS 324602 [2LAWRENCE TP69.000] TO BUS 324888 [2LAWRENCE 69.000] CKT 1
OPEN LINE FROM BUS 324602 [2LAWRENCE TP69.000] TO BUS 324466 [2CARROLLTON 69.000] CKT 1
OPEN LINE FROM BUS 324828 [2CAMPBBRG KU69.000] TO BUS 324478 [2CAMPBELBURG69.000] CKT 1
OPEN LINE FROM BUS 324478 [2CAMPBELBURG69.000] TO BUS 324516 [2EMINENCE KU69.000] CKT 1
BB-1456 | OPEN LINE FROM BUS 324534 [2FRANKFORT 269.000] TO BUS 324535 [2E FRANKFORT69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 8.018 | 1 | 11.32
OPEN LINE FROM BUS 324534 [2FRANKFORT 269.000] TO BUS 324762 [2VERSAIL W T69.000] CKT 1
OPEN LINE FROM BUS 324762 [2VERSAIL W T69.000] TO BUS 324304 [2VERSAILLE W69.000] CKT 1
OPEN LINE FROM BUS 324762 [2VERSAIL W T69.000] TO BUS 324755 [2TYRONE 69.000] CKT 1
BB-1280 | OPEN LINE FROM BUS 324547 [2GEORGETOWN 69.000] TO BUS 324890 [2LEMONS MILL69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.80762 | 45.3658 | 5 | 71.7
OPEN LINE FROM BUS 324547 [2GEORGETOWN 69.000] TO BUS 324405 [2ADAMS 69.000] CKT 1
OPEN LINE FROM BUS 324890 [2LEMONS MILL69.000] TO BUS 324877 [2HOOVER KU 69.000] CKT 1
OPEN LINE FROM BUS 324877 [2HOOVER KU 69.000] TO BUS 324848 [2DONERAIL 69.000] CKT 1
OPEN LINE FROM BUS 324848 [2DONERAIL 69.000] TO BUS 324734 [2SPINDLETP T69.000] CKT 1
OPEN LINE FROM BUS 324734 [2SPINDLETP T69.000] TO BUS 324340 [2SPINDLETOP 69.000] CKT 1
OPEN LINE FROM BUS 324734 [2SPINDLETP T69.000] TO BUS 324558 [2HAEFLING 69.000] CKT 1
BB-1479 | OPEN LINE FROM BUS 324763 [2VERSAILLES 69.000] TO BUS 324985 [2VSAIL BYPAS69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.34713 | 20.9585 | 2 | 32.77
OPEN LINE FROM BUS 324763 [2VERSAILLES 69.000] TO BUS 324069 [2PAYNES ML 69.000] CKT 1
OPEN LINE FROM BUS 324985 [2VSAIL BYPAS69.000] TO BUS 324755 [2TYRONE 69.000] CKT 1
BB-1317 | OPEN LINE FROM BUS 324722 [2SHARON KU 69.000] TO BUS 341188 [2BRACKEN CO 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14177 | 9.2775 | 2 | 13.28
OPEN LINE FROM BUS 324722 [2SHARON KU 69.000] TO BUS 324195 [2AUGUSTA 69.000] CKT 1
OPEN LINE FROM BUS 324722 [2SHARON KU 69.000] TO BUS 324589 [2KENTON 688 69.000] CKT 1
BB-1225 | OPEN LINE FROM BUS 324297 [4PLAINVIEW 138.00] TO BUS 324298 [4PLAINVIEW T138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.26665 | 16.778 | 1 | 29.5
OPEN LINE FROM BUS 324297 [4PLAINVIEW 138.00] TO BUS 324263 [4HURSTBORNE 138.00] CKT 1
BB-1373 | OPEN LINE FROM BUS 324492 [2CYNTHIAN SW69.000] TO BUS 324595 [2KAWNEER 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.24642 | 15.5704 | 4 | 23.68
OPEN LINE FROM BUS 324492 [2CYNTHIAN SW69.000] TO BUS 342133 [2RENAKER 69.000] CKT 1
OPEN LINE FROM BUS 324595 [2KAWNEER 69.000] TO BUS 324837 [2CYNTHIAN KU69.000] CKT 1
OPEN LINE FROM BUS 324837 [2CYNTHIAN KU69.000] TO BUS 324491 [2CYNTHIAN SO69.000] CKT 1
OPEN LINE FROM BUS 324491 [2CYNTHIAN SO69.000] TO BUS 325085 [2CYNTHI EK T69.000] CKT 1
OPEN LINE FROM BUS 325085 [2CYNTHI EK T69.000] TO BUS 325035 [2BLUE SOL TP69.000] CKT 1
OPEN LINE FROM BUS 324812 [2CARLISLE 69.000] TO BUS 324639 [2MILLRSB624 69.000] CKT 1
BB-1073 | OPEN LINE FROM BUS 324156 [5PINEVILE SW161.00] TO BUS 360452 [5PINEVILL KY161.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.44972 | 19.889
OPEN LINE FROM BUS 324156 [5PINEVILE SW161.00] TO BUS 324132 [5ARTEMUS TAP161.00] CKT 1
OPEN LINE FROM BUS 324156 [5PINEVILE SW161.00] TO BUS 324155 [5PINEVILLE 1161.00] CKT 1
BB-1493 | OPEN LINE FROM BUS 324677 [2PARIS 12 69.000] TO BUS 324680 [2PARIS KU 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 8.8421 | 1 | 12.9696
OPEN LINE FROM BUS 324677 [2PARIS 12 69.000] TO BUS 324642 [2MILLERSBURG69.000] CKT 1
BB-1494 | OPEN LINE FROM BUS 324679 [2PARIS 3 69.000] TO BUS 324642 [2MILLERSBURG69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.87788 | 37.9238 | 2 | 9.09
OPEN LINE FROM BUS 324679 [2PARIS 3 69.000] TO BUS 324678 [2PARIS CITY 69.000] CKT 1
OPEN LINE FROM BUS 324678 [2PARIS CITY 69.000] TO BUS 324680 [2PARIS KU 69.000] CKT 1
BB-1495 | OPEN LINE FROM BUS 324717 [2SARDIS TAP 69.000] TO BUS 326549 [2SARDIS 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.16506 | 15.2108 | 1 | 1.36
OPEN LINE FROM BUS 324717 [2SARDIS TAP 69.000] TO BUS 341923 [2MURPHYSVIL 69.000] CKT 1
OPEN LINE FROM BUS 324717 [2SARDIS TAP 69.000] TO BUS 324642 [2MILLERSBURG69.000] CKT 1
BB-1395 | OPEN LINE FROM BUS 324586 [2JOYLAND 69.000] TO BUS 324610 [2LEX PLANT 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.57893 | 33.0148 | 7 | 52.94
OPEN LINE FROM BUS 324586 [2JOYLAND 69.000] TO BUS 324581 [2HUGHES LANE69.000] CKT 1
OPEN LINE FROM BUS 324581 [2HUGHES LANE69.000] TO BUS 324476 [2CMC TAP 69.000] CKT 1
OPEN LINE FROM BUS 324476 [2CMC TAP 69.000] TO BUS 324680 [2PARIS KU 69.000] CKT 1
OPEN LINE FROM BUS 324476 [2CMC TAP 69.000] TO BUS 324082 [2PARIS 4 69.000] CKT 1
OPEN LINE FROM BUS 324197 [2DETROIT HAR69.000] TO BUS 324082 [2PARIS 4 69.000] CKT 1
OPEN LINE FROM BUS 325018 [2CLA 69.000] TO BUS 325061 [2CMC 69.000] CKT 1
OPEN LINE FROM BUS 325018 [2CLA 69.000] TO BUS 325017 [2CMWA 69.000] CKT 1
OPEN LINE FROM BUS 325061 [2CMC 69.000] TO BUS 324082 [2PARIS 4 69.000] CKT 1
BB-1318 | OPEN LINE FROM BUS 326571 [2HUME RD 69.000] TO BUS 326586 [2HUME RD TAP69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.37208 | 22.6994 | 6 | 41.05
OPEN LINE FROM BUS 324559 [2HALEY 69.000] TO BUS 324797 [2AVON T1 69.000] CKT 1
OPEN LINE FROM BUS 324559 [2HALEY 69.000] TO BUS 326586 [2HUME RD TAP69.000] CKT 1
OPEN LINE FROM BUS 324705 [2ROCKWELL 69.000] TO BUS 324783 [2WINCHSTR KU69.000] CKT 1
OPEN LINE FROM BUS 324705 [2ROCKWELL 69.000] TO BUS 324855 [2EKPC OFF TP69.000] CKT 1
OPEN LINE FROM BUS 324797 [2AVON T1 69.000] TO BUS 324855 [2EKPC OFF TP69.000] CKT 1
OPEN LINE FROM BUS 324797 [2AVON T1 69.000] TO BUS 324796 [2AVON 69.000] CKT 1
OPEN LINE FROM BUS 324855 [2EKPC OFF TP69.000] TO BUS 326541 [2EKPC OFFICE69.000] CKT 1
OPEN LINE FROM BUS 326541 [2EKPC OFFICE69.000] TO BUS 326527 [2TREEHAVEN T69.000] CKT 1
OPEN LINE FROM BUS 326527 [2TREEHAVEN T69.000] TO BUS 326524 [2VAN METER 69.000] CKT 1
OPEN LINE FROM BUS 326527 [2TREEHAVEN T69.000] TO BUS 326525 [2TREEHAVEN 69.000] CKT 1
BB-1352 | OPEN LINE FROM BUS 325004 [2WINCHES WTR69.000] TO BUS 324448 [2BOONE AVE 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.20716 | 13.5622 | 3 | 23.16
OPEN LINE FROM BUS 325004 [2WINCHES WTR69.000] TO BUS 324449 [2BOONSBORO N69.000] CKT 1
OPEN LINE FROM BUS 324448 [2BOONE AVE 69.000] TO BUS 324782 [2WINCHEST SO69.000] CKT 1
OPEN LINE FROM BUS 324782 [2WINCHEST SO69.000] TO BUS 324783 [2WINCHSTR KU69.000] CKT 1
BB-1405 | OPEN LINE FROM BUS 325063 [2CORPORAT DR69.000] TO BUS 324330 [2WINCHES IND69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.35024 | 21.2886 | 2 | 32.54
OPEN LINE FROM BUS 324330 [2WINCHES IND69.000] TO BUS 324783 [2WINCHSTR KU69.000] CKT 1
BB-1301 | OPEN LINE FROM BUS 324540 [2FOGG PIKE T69.000] TO BUS 324912 [2MT STERL KU69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.44467 | 26.2328 | 4 | 40.1228
OPEN LINE FROM BUS 324540 [2FOGG PIKE T69.000] TO BUS 324472 [2CLARK CO 69.000] CKT 1
OPEN LINE FROM BUS 324912 [2MT STERL KU69.000] TO BUS 324461 [2CAMARGO 69.000] CKT 1
OPEN LINE FROM BUS 324461 [2CAMARGO 69.000] TO BUS 324413 [2AO SMITH TP69.000] CKT 1
OPEN LINE FROM BUS 324413 [2AO SMITH TP69.000] TO BUS 324414 [2AO SMITH 69.000] CKT 1
OPEN LINE FROM BUS 324413 [2AO SMITH TP69.000] TO BUS 324733 [2SPENCER RD 69.000] CKT 1
OPEN LINE FROM BUS 324414 [2AO SMITH 69.000] TO BUS 326531 [2HINKSTON 69.000] CKT 1
BB-1387 | OPEN LINE FROM BUS 324467 [2CAVE RUN TP69.000] TO BUS 324528 [2FARMERS 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.23778 | 18.7431 | 2 | 3.8041
OPEN LINE FROM BUS 324467 [2CAVE RUN TP69.000] TO BUS 324714 [2SALT LICK 69.000] CKT 1
OPEN LINE FROM BUS 324467 [2CAVE RUN TP69.000] TO BUS 326538 [2CAVE RUN 69.000] CKT 1
OPEN LINE FROM BUS 324714 [2SALT LICK 69.000] TO BUS 324733 [2SPENCER RD 69.000] CKT 1
BB-1443 | OPEN LINE FROM BUS 324647 [2MOREHEAD W 69.000] TO BUS 324910 [2MOREHEAD 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.21426 | 13.8689 | 3 | 20.89
OPEN LINE FROM BUS 324647 [2MOREHEAD W 69.000] TO BUS 324528 [2FARMERS 69.000] CKT 1
OPEN LINE FROM BUS 324910 [2MOREHEAD 69.000] TO BUS 324646 [2MOREHEAD E 69.000] CKT 1
OPEN LINE FROM BUS 324646 [2MOREHEAD E 69.000] TO BUS 324707 [2RODBURN 69.000] CKT 1
BB-1335 | OPEN LINE FROM BUS 324432 [2BELT LINE 69.000] TO BUS 324558 [2HAEFLING 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.45938 | 26.9452 | 3 | 42.14
OPEN LINE FROM BUS 324432 [2BELT LINE 69.000] TO BUS 324879 [2IBM 998 69.000] CKT 1
OPEN LINE FROM BUS 324879 [2IBM 998 69.000] TO BUS 324582 [2IBM 69.000] CKT 1
OPEN LINE FROM BUS 324582 [2IBM 69.000] TO BUS 324610 [2LEX PLANT 69.000] CKT 1
BB-1298 | OPEN LINE FROM BUS 324756 [2UK WEST 1 69.000] TO BUS 324772 [2UK WEST 2 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.61307 | 35.279 | 5 | 55.35
OPEN LINE FROM BUS 324756 [2UK WEST 1 69.000] TO BUS 324952 [2SCOTT ST TP69.000] CKT 1
OPEN LINE FROM BUS 324772 [2UK WEST 2 69.000] TO BUS 324409 [2AMERICAN AV69.000] CKT 1
OPEN LINE FROM BUS 324952 [2SCOTT ST TP69.000] TO BUS 324338 [2SCOTT ST 4 69.000] CKT 1
OPEN LINE FROM BUS 324952 [2SCOTT ST TP69.000] TO BUS 324766 [2W HIGH T1 69.000] CKT 1
OPEN LINE FROM BUS 324338 [2SCOTT ST 4 69.000] TO BUS 324339 [2SCOTT ST 1269.000] CKT 1
OPEN LINE FROM BUS 324766 [2W HIGH T1 69.000] TO BUS 324988 [2WEST HIGH 69.000] CKT 1
OPEN LINE FROM BUS 324766 [2W HIGH T1 69.000] TO BUS 324558 [2HAEFLING 69.000] CKT 1
OPEN LINE FROM BUS 324988 [2WEST HIGH 69.000] TO BUS 324984 [2VINE STREET69.000] CKT 1
BB-1369 | OPEN LINE FROM BUS 324457 [2BUCHANAN 69.000] TO BUS 324610 [2LEX PLANT 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.24086 | 15.3368 | 3 | 24.23
OPEN LINE FROM BUS 324457 [2BUCHANAN 69.000] TO BUS 324986 [2W HIGH T2 69.000] CKT 1
OPEN LINE FROM BUS 324986 [2W HIGH T2 69.000] TO BUS 324979 [2TRAFTON AVE69.000] CKT 1
OPEN LINE FROM BUS 324979 [2TRAFTON AVE69.000] TO BUS 324884 [2KUNKEL 69.000] CKT 1
OPEN LINE FROM BUS 324884 [2KUNKEL 69.000] TO BUS 324694 [2PARKR MIL T69.000] CKT 1
OPEN LINE FROM BUS 324694 [2PARKR MIL T69.000] TO BUS 324930 [2PARKER MILL69.000] CKT 1
OPEN LINE FROM BUS 324694 [2PARKR MIL T69.000] TO BUS 324687 [2PISGAH 69.000] CKT 1
BB-1297 | OPEN LINE FROM BUS 324683 [2PICADOME 69.000] TO BUS 324866 [2GE LAMP 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.73918 | 41.9419 | 3 | 66.32
OPEN LINE FROM BUS 324683 [2PICADOME 69.000] TO BUS 324409 [2AMERICAN AV69.000] CKT 1
OPEN LINE FROM BUS 324866 [2GE LAMP 69.000] TO BUS 324742 [2STONEWALL T69.000] CKT 1
OPEN LINE FROM BUS 324742 [2STONEWALL T69.000] TO BUS 324972 [2STONEWALL 69.000] CKT 1
OPEN LINE FROM BUS 324742 [2STONEWALL T69.000] TO BUS 324568 [2HIGBY 618 69.000] CKT 1
OPEN LINE FROM BUS 324972 [2STONEWALL 69.000] TO BUS 324930 [2PARKER MILL69.000] CKT 1
BB-1288 | OPEN LINE FROM BUS 324713 [2SO ELKHORN 69.000] TO BUS 324955 [2SHANNON RUN69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.3106 | 20.039 | 3 | 29.0898
OPEN LINE FROM BUS 324713 [2SO ELKHORN 69.000] TO BUS 324568 [2HIGBY 618 69.000] CKT 1
OPEN LINE FROM BUS 324955 [2SHANNON RUN69.000] TO BUS 324407 [2ALEXANDER 69.000] CKT 1
OPEN LINE FROM BUS 324407 [2ALEXANDER 69.000] TO BUS 324755 [2TYRONE 69.000] CKT 1
BB-1468 | OPEN LINE FROM BUS 324567 [2HIGBY MIL 269.000] TO BUS 324569 [2HIGBY 608 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 9.4864 | 1 | 13.9
OPEN LINE FROM BUS 324567 [2HIGBY MIL 269.000] TO BUS 324780 [2WIL DOWN T169.000] CKT 1
OPEN LINE FROM BUS 324780 [2WIL DOWN T169.000] TO BUS 325002 [2WILS DOWN 169.000] CKT 1
OPEN LINE FROM BUS 324780 [2WIL DOWN T169.000] TO BUS 324601 [2LANSDOWNE 69.000] CKT 1
OPEN LINE FROM BUS 325002 [2WILS DOWN 169.000] TO BUS 325003 [2WILS DOWN 269.000] CKT Z1
BB-1315 | OPEN LINE FROM BUS 325000 [2WIL DOWN T269.000] TO BUS 325003 [2WILS DOWN 269.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.66911 | 38.7061 | 6 | 59.9799
OPEN LINE FROM BUS 325000 [2WIL DOWN T269.000] TO BUS 324568 [2HIGBY 618 69.000] CKT 1
OPEN LINE FROM BUS 325000 [2WIL DOWN T269.000] TO BUS 324735 [2SOUTH POINT69.000] CKT 1
OPEN LINE FROM BUS 325003 [2WILS DOWN 269.000] TO BUS 325002 [2WILS DOWN 169.000] CKT Z1
OPEN LINE FROM BUS 324735 [2SOUTH POINT69.000] TO BUS 324794 [2ASHLND PIPE69.000] CKT 1
OPEN LINE FROM BUS 324794 [2ASHLND PIPE69.000] TO BUS 324987 [2W HICKMAN 69.000] CKT 1
OPEN LINE FROM BUS 324987 [2W HICKMAN 69.000] TO BUS 324842 [2DAVIS TAP 69.000] CKT 1
OPEN LINE FROM BUS 324842 [2DAVIS TAP 69.000] TO BUS 324967 [2SPEAR STA A69.000] CKT 1
OPEN LINE FROM BUS 324967 [2SPEAR STA A69.000] TO BUS 324886 [2KY RIVER 69.000] CKT 1
OPEN LINE FROM BUS 324886 [2KY RIVER 69.000] TO BUS 324968 [2SPEAR STA B69.000] CKT 1
OPEN LINE FROM BUS 324968 [2SPEAR STA B69.000] TO BUS 324656 [2N MADISON T69.000] CKT 1
OPEN LINE FROM BUS 324656 [2N MADISON T69.000] TO BUS 324530 [2FAWKES 69.000] CKT 1
BB-1482 | OPEN LINE FROM BUS 324650 [2MT TBR T 69.000] TO BUS 324891 [2LEX WATER 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.56223 | 32.5579 | 3 | 50.82
OPEN LINE FROM BUS 324650 [2MT TBR T 69.000] TO BUS 324337 [2MOUNT TABOR69.000] CKT 1
OPEN LINE FROM BUS 324650 [2MT TBR T 69.000] TO BUS 324601 [2LANSDOWNE 69.000] CKT 1
OPEN LINE FROM BUS 324891 [2LEX WATER 69.000] TO BUS 324611 [2LIBERTY RD 69.000] CKT 1
OPEN LINE FROM BUS 324611 [2LIBERTY RD 69.000] TO BUS 324618 [2LOUDON 628 69.000] CKT 1
BB-1368 | OPEN LINE FROM BUS 324539 [2FMC 69.000] TO BUS 324601 [2LANSDOWNE 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 14.3911 | 3 | 82.74
OPEN LINE FROM BUS 324539 [2FMC 69.000] TO BUS 324613 [2LK SHORE TP69.000] CKT 1
OPEN LINE FROM BUS 324613 [2LK SHORE TP69.000] TO BUS 324618 [2LOUDON 628 69.000] CKT 1
OPEN LINE FROM BUS 324613 [2LK SHORE TP69.000] TO BUS 325059 [2BRYANT RD T69.000] CKT 1
OPEN LINE FROM BUS 325059 [2BRYANT RD T69.000] TO BUS 325060 [2BRYANT ROAD69.000] CKT 1
OPEN LINE FROM BUS 325059 [2BRYANT RD T69.000] TO BUS 324332 [2LAKE SHORE 69.000] CKT 1
BB-1312 | OPEN LINE FROM BUS 324674 [2PROC & GAMB69.000] TO BUS 324934 [2RACE STREET69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.83089 | 37.9765 | 1 | 8.89
OPEN LINE FROM BUS 324674 [2PROC & GAMB69.000] TO BUS 324610 [2LEX PLANT 69.000] CKT 1
BB-1313 | OPEN LINE FROM BUS 324984 [2VINE STREET69.000] TO BUS 324988 [2WEST HIGH 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.26373 | 16.5355 | 2 | 25.37
OPEN LINE FROM BUS 324984 [2VINE STREET69.000] TO BUS 324934 [2RACE STREET69.000] CKT 1
OPEN LINE FROM BUS 324418 [2ASHLND AV T69.000] TO BUS 324632 [2UK MED CENT69.000] CKT 1
OPEN LINE FROM BUS 324418 [2ASHLND AV T69.000] TO BUS 324934 [2RACE STREET69.000] CKT 1
OPEN LINE FROM BUS 324418 [2ASHLND AV T69.000] TO BUS 324331 [2ASHLAND AVE69.000] CKT 1
BB-1319 | OPEN LINE FROM BUS 324422 [2AVON T2 69.000] TO BUS 324508 [2EASTLAND 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 8.0838 | 2 | 11.25
OPEN LINE FROM BUS 324422 [2AVON T2 69.000] TO BUS 324680 [2PARIS KU 69.000] CKT 1
OPEN LINE FROM BUS 324422 [2AVON T2 69.000] TO BUS 325081 [2BRIAR HILL 69.000] CKT 1
OPEN LINE FROM BUS 324508 [2EASTLAND 69.000] TO BUS 324617 [2LOUDON 618 69.000] CKT 1
BB-1323 | OPEN LINE FROM BUS 324823 [2CLINTON 58169.000] TO BUS 324825 [2CLINTON KU 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.73675 | 33.0179 | 2 | 8.22
OPEN LINE FROM BUS 324823 [2CLINTON 58169.000] TO BUS 324427 [2BARDWELL 69.000] CKT 1
OPEN LINE FROM BUS 324427 [2BARDWELL 69.000] TO BUS 324779 [2WICKLIFFE 69.000] CKT 1
BB-1325 | OPEN LINE FROM BUS 324864 [2FORRESTDALE69.000] TO BUS 324428 [2BARLOW 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 8.4832 | 3 | 13.05
OPEN LINE FROM BUS 324864 [2FORRESTDALE69.000] TO BUS 324553 [2GRAHAMVILLE69.000] CKT 1
OPEN LINE FROM BUS 324428 [2BARLOW 69.000] TO BUS 324778 [2WICKLIFE CI69.000] CKT 1
OPEN LINE FROM BUS 324778 [2WICKLIFE CI69.000] TO BUS 324779 [2WICKLIFFE 69.000] CKT 1
BB-1407 | OPEN LINE FROM BUS 324628 [2MARION SO 69.000] TO BUS 324629 [2MARION KU 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 9.7776 | 5 | 15.35
OPEN LINE FROM BUS 324628 [2MARION SO 69.000] TO BUS 324486 [2CRITTENDEN 69.000] CKT 1
OPEN LINE FROM BUS 324629 [2MARION KU 69.000] TO BUS 324904 [2MEXICO KU 69.000] CKT 1
OPEN LINE FROM BUS 324629 [2MARION KU 69.000] TO BUS 324085 [2MARION 4 69.000] CKT 1
OPEN LINE FROM BUS 324904 [2MEXICO KU 69.000] TO BUS 324865 [2FREDONIA 69.000] CKT 1
OPEN LINE FROM BUS 324865 [2FREDONIA 69.000] TO BUS 324544 [2FREDONIA QU69.000] CKT 1
OPEN LINE FROM BUS 324544 [2FREDONIA QU69.000] TO BUS 324693 [2PRINCETON 69.000] CKT 1
BB-1356 | OPEN LINE FROM BUS 324760 [2VAKSDAHL AV69.000] TO BUS 324838 [2DANV IND TP69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.43636 | 26.6992 | 7 | 40.1016
OPEN LINE FROM BUS 324760 [2VAKSDAHL AV69.000] TO BUS 324450 [2BOYLE CO 69.000] CKT 1
OPEN LINE FROM BUS 324838 [2DANV IND TP69.000] TO BUS 324957 [2SHELBY CI T69.000] CKT 1
OPEN LINE FROM BUS 324957 [2SHELBY CI T69.000] TO BUS 324970 [2STANFORD KU69.000] CKT 1
OPEN LINE FROM BUS 324957 [2SHELBY CI T69.000] TO BUS 324363 [2SHELB CI KU69.000] CKT 1
OPEN LINE FROM BUS 324363 [2SHELB CI KU69.000] TO BUS 326518 [2SHELB CI EK69.000] CKT 1
OPEN LINE FROM BUS 324970 [2STANFORD KU69.000] TO BUS 324971 [2STANFORD NO69.000] CKT 1
OPEN LINE FROM BUS 324970 [2STANFORD KU69.000] TO BUS 324816 [2CEMETARY RD69.000] CKT 1
OPEN LINE FROM BUS 324971 [2STANFORD NO69.000] TO BUS 324599 [2LANCASTER 269.000] CKT 1
OPEN LINE FROM BUS 324599 [2LANCASTER 269.000] TO BUS 324600 [2LANCASTR KU69.000] CKT 1
BB-1316 | OPEN LINE FROM BUS 324421 [2ATOKA TAP 69.000] TO BUS 324450 [2BOYLE CO 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.28911 | 17.036 | 1 | 3.33
OPEN LINE FROM BUS 324421 [2ATOKA TAP 69.000] TO BUS 324495 [2DANVILLE N 69.000] CKT 1
OPEN LINE FROM BUS 324421 [2ATOKA TAP 69.000] TO BUS 324344 [2ATOKA 69.000] CKT 1
BB-1370 | OPEN LINE FROM BUS 324458 [2BUENA VISTA69.000] TO BUS 324501 [2DIX DAM 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.71198 | 31.8687 | 2 | 7.71
OPEN LINE FROM BUS 324458 [2BUENA VISTA69.000] TO BUS 324546 [2GARRARD CT 69.000] CKT 1
OPEN LINE FROM BUS 324546 [2GARRARD CT 69.000] TO BUS 324600 [2LANCASTR KU69.000] CKT 1
BB-1349 | OPEN LINE FROM BUS 324731 [2SONORA TAP 69.000] TO BUS 326547 [2SONORA 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.36656 | 18.6762 | 1 | 4.15
OPEN LINE FROM BUS 324731 [2SONORA TAP 69.000] TO BUS 324447 [2BONNIE KU 69.000] CKT 1
OPEN LINE FROM BUS 324731 [2SONORA TAP 69.000] TO BUS 324563 [2HARDIN CO 69.000] CKT 1
BB-1320 | OPEN LINE FROM BUS 326537 [2WOODLAWN KU69.000] TO BUS 324424 [2BARDTWN CTY69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.24674 | 15.7795 | 4 | 24.36
OPEN LINE FROM BUS 326537 [2WOODLAWN KU69.000] TO BUS 324426 [2BARDSTOWN 69.000] CKT Z1
OPEN LINE FROM BUS 324424 [2BARDTWN CTY69.000] TO BUS 324801 [2BARTON 69.000] CKT 1
OPEN LINE FROM BUS 324801 [2BARTON 69.000] TO BUS 324660 [2NEW HAVEN 69.000] CKT 1
OPEN LINE FROM BUS 324660 [2NEW HAVEN 69.000] TO BUS 341632 [2HODGENVILLE69.000] CKT 1
BB-1434 | OPEN LINE FROM BUS 324521 [2ETOWN 4 69.000] TO BUS 324575 [2HODGENV KU 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.23059 | 14.9055 | 2 | 23.5
OPEN LINE FROM BUS 324521 [2ETOWN 4 69.000] TO BUS 324519 [2ETOWN KU 69.000] CKT 1
OPEN LINE FROM BUS 324575 [2HODGENV KU 69.000] TO BUS 341632 [2HODGENVILLE69.000] CKT 1
BB-1285 | OPEN LINE FROM BUS 324786 [2ZION 69.000] TO BUS 324790 [2AIRLINE RD 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 8.5502 | 3 | 12.57
OPEN LINE FROM BUS 324786 [2ZION 69.000] TO BUS 324551 [2GR RVR STL 69.000] CKT 1
OPEN LINE FROM BUS 324790 [2AIRLINE RD 69.000] TO BUS 324711 [2SPEN CHEM T69.000] CKT 1
OPEN LINE FROM BUS 324711 [2SPEN CHEM T69.000] TO BUS 324093 [2SPEN CHEMIC69.000] CKT 1
OPEN LINE FROM BUS 324711 [2SPEN CHEM T69.000] TO BUS 324484 [2CORYDON 69.000] CKT 1
BB-1401 | OPEN LINE FROM BUS 324477 [2CAMP BRECKN69.000] TO BUS 324502 [2DIXON KU 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.60996 | 28.0672 | 2 | 6.63
OPEN LINE FROM BUS 324477 [2CAMP BRECKN69.000] TO BUS 324645 [2MORGANFIELD69.000] CKT 1
OPEN LINE FROM BUS 324502 [2DIXON KU 69.000] TO BUS 324658 [2NEBO 69.000] CKT 1
MORG-WHT-NEB | OPEN LINE FROM BUS 324776 [2WHEATCROF T69.000] TO BUS 324777 [2WHEATCROFT 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.33173 | 18.2208 | 1 | 3.6
OPEN LINE FROM BUS 324776 [2WHEATCROF T69.000] TO BUS 324644 [2MORGANFLD 469.000] CKT 1
OPEN LINE FROM BUS 324776 [2WHEATCROF T69.000] TO BUS 324658 [2NEBO 69.000] CKT 1
OPEN LINE FROM BUS 324644 [2MORGANFLD 469.000] TO BUS 324645 [2MORGANFIELD69.000] CKT 1
BB-1302 | OPEN LINE FROM BUS 324549 [2GORGE 69.000] TO BUS 324583 [2IMBODEN 69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.24759 | 15.6472 | 5 | 24.3
OPEN LINE FROM BUS 324549 [2GORGE 69.000] TO BUS 324894 [2E STONE G T69.000] CKT 1
OPEN LINE FROM BUS 324549 [2GORGE 69.000] TO BUS 324384 [2APPALACHIA 69.000] CKT 1
OPEN LINE FROM BUS 324549 [2GORGE 69.000] TO BUS 324385 [2BIG STONE G69.000] CKT 1
OPEN LINE FROM BUS 324853 [2E STONE GAP69.000] TO BUS 324836 [2BENS BRANCH69.000] CKT 1
OPEN LINE FROM BUS 324871 [2HAMER 69.000] TO BUS 324894 [2E STONE G T69.000] CKT 1
OPEN LINE FROM BUS 324871 [2HAMER 69.000] TO BUS 324802 [2BEAR BRANCH69.000] CKT 1
OPEN LINE FROM BUS 324802 [2BEAR BRANCH69.000] TO BUS 324441 [2BLACKWOOD 69.000] CKT 1
OPEN LINE FROM BUS 324441 [2BLACKWOOD 69.000] TO BUS 324503 [2DORCHESTER 69.000] CKT 1
BB-1400 | OPEN LINE FROM BUS 324663 [2NORTON EAST69.000] TO BUS 324826 [2CLINCH V SW69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.54838 | 26.1552 | 3 | 5.86
OPEN LINE FROM BUS 324663 [2NORTON EAST69.000] TO BUS 324503 [2DORCHESTER 69.000] CKT 1
OPEN LINE FROM BUS 324826 [2CLINCH V SW69.000] TO BUS 324999 [2WHTE OAK KU69.000] CKT 1
OPEN LINE FROM BUS 324999 [2WHTE OAK KU69.000] TO BUS 324851 [2DWINA TAP 69.000] CKT 1
OPEN LINE FROM BUS 324851 [2DWINA TAP 69.000] TO BUS 324389 [2DWINA 69.000] CKT 1
OPEN LINE FROM BUS 324851 [2DWINA TAP 69.000] TO BUS 324743 [2SAINT PAUL 69.000] CKT 1
BB-1344 | OPEN LINE FROM BUS 324977 [2TOMS CRK TP69.000] TO BUS 324394 [2TOMS CREEK 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.66166 | 31.362 | 2 | 7.22
OPEN LINE FROM BUS 324977 [2TOMS CRK TP69.000] TO BUS 324446 [2BOND 69.000] CKT 1
OPEN LINE FROM BUS 324977 [2TOMS CRK TP69.000] TO BUS 324716 [2SANDY RIDGE69.000] CKT 1
OPEN LINE FROM BUS 324716 [2SANDY RIDGE69.000] TO BUS 324555 [2VA CTY REAC69.000] CKT 1
BB-1473 | OPEN LINE FROM BUS 324591 [2KEOKEE TAP 69.000] TO BUS 324592 [2KEOKEE TVA 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14177 | 2.2756 | 2 | 1.21
OPEN LINE FROM BUS 324591 [2KEOKEE TAP 69.000] TO BUS 324583 [2IMBODEN 69.000] CKT 1
OPEN LINE FROM BUS 324592 [2KEOKEE TVA 69.000] TO BUS 324689 [2POCKET 69.000] CKT 1
BB-1420 | OPEN LINE FROM BUS 324498 [2DAYS BRANCH69.000] TO BUS 324621 [2LYNCH 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.46765 | 22.8199 | 3 | 5.06
OPEN LINE FROM BUS 324498 [2DAYS BRANCH69.000] TO BUS 324876 [2HOLMES MILL69.000] CKT 1
OPEN LINE FROM BUS 324876 [2HOLMES MILL69.000] TO BUS 324744 [2STRAGHT CRK69.000] CKT 1
OPEN LINE FROM BUS 324744 [2STRAGHT CRK69.000] TO BUS 324689 [2POCKET 69.000] CKT 1
BB-1306 | OPEN LINE FROM BUS 324433 [2BENHAM 69.000] TO BUS 324621 [2LYNCH 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 1.8891 | 1 | 0.99
OPEN LINE FROM BUS 324433 [2BENHAM 69.000] TO BUS 324416 [2ARNOLD 69.000] CKT 1
BB-1307 | OPEN LINE FROM BUS 324490 [2CUMBERLAND 69.000] TO BUS 324827 [2CLOVERLICK 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.2192 | 15.059 | 7 | 21.4794
OPEN LINE FROM BUS 324490 [2CUMBERLAND 69.000] TO BUS 324416 [2ARNOLD 69.000] CKT 1
OPEN LINE FROM BUS 324827 [2CLOVERLICK 69.000] TO BUS 324818 [2CHAD TAP 69.000] CKT 1
OPEN LINE FROM BUS 324818 [2CHAD TAP 69.000] TO BUS 324978 [2TOTZ 69.000] CKT 1
OPEN LINE FROM BUS 324978 [2TOTZ 69.000] TO BUS 324881 [2JACKS CREEK69.000] CKT 1
OPEN LINE FROM BUS 324881 [2JACKS CREEK69.000] TO BUS 324942 [2ROBBINS 69.000] CKT 1
OPEN LINE FROM BUS 324942 [2ROBBINS 69.000] TO BUS 324875 [2HIGHSPLINT 69.000] CKT 1
OPEN LINE FROM BUS 324875 [2HIGHSPLINT 69.000] TO BUS 324798 [2BAILEY CRK 69.000] CKT 1
OPEN LINE FROM BUS 324798 [2BAILEY CRK 69.000] TO BUS 324523 [2EVARTS 69.000] CKT 1
BB-1415 | OPEN LINE FROM BUS 324562 [2HARLAN KU 69.000] TO BUS 324564 [2HARLAN WYE 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 7.4831 | 5 | 10.99
OPEN LINE FROM BUS 324562 [2HARLAN KU 69.000] TO BUS 324094 [2TURTLE CK T69.000] CKT 1
OPEN LINE FROM BUS 324094 [2TURTLE CK T69.000] TO BUS 324761 [2VERDA 69.000] CKT 1
OPEN LINE FROM BUS 324094 [2TURTLE CK T69.000] TO BUS 325045 [2TURTLE CRK 69.000] CKT 1
OPEN LINE FROM BUS 325045 [2TURTLE CRK 69.000] TO BUS 325092 [2COAL GOOD 69.000] CKT 1
OPEN LINE FROM BUS 324761 [2VERDA 69.000] TO BUS 324522 [2EVARTS TAP 69.000] CKT 1
OPEN LINE FROM BUS 324522 [2EVARTS TAP 69.000] TO BUS 324523 [2EVARTS 69.000] CKT 1
OPEN LINE FROM BUS 324522 [2EVARTS TAP 69.000] TO BUS 324692 [2POWELL MTN 69.000] CKT 1
OPEN LINE FROM BUS 324692 [2POWELL MTN 69.000] TO BUS 324738 [2SAINT CHARL69.000] CKT 1
OPEN LINE FROM BUS 324738 [2SAINT CHARL69.000] TO BUS 324689 [2POCKET 69.000] CKT 1
BB-1342 | OPEN LINE FROM BUS 324497 [2DAYHOIT TAP69.000] TO BUS 324564 [2HARLAN WYE 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.64225 | 44.7707 | 4 | 10.9001
OPEN LINE FROM BUS 324497 [2DAYHOIT TAP69.000] TO BUS 324588 [2KENTENIA 69.000] CKT 1
OPEN LINE FROM BUS 324497 [2DAYHOIT TAP69.000] TO BUS 324442 [2BLEDSOE TAP69.000] CKT 1
OPEN LINE FROM BUS 324442 [2BLEDSOE TAP69.000] TO BUS 325008 [2BLEDSOE 69.000] CKT 1
OPEN LINE FROM BUS 324442 [2BLEDSOE TAP69.000] TO BUS 324375 [2DAYHOIT 69.000] CKT 1
OPEN LINE FROM BUS 325008 [2BLEDSOE 69.000] TO BUS 325026 [2PINE MOUNTN69.000] CKT 1
OPEN LINE FROM BUS 324588 [2KENTENIA 69.000] TO BUS 324542 [2FORESTER CR69.000] CKT 1
OPEN LINE FROM BUS 324542 [2FORESTER CR69.000] TO BUS 324706 [2ROCKY BRNCH69.000] CKT 1
BB-1287 | OPEN LINE FROM BUS 324543 [2FOUR MILE 69.000] TO BUS 324686 [2PINEVILLE 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.60138 | 32.7718 | 7 | 7.8237
OPEN LINE FROM BUS 324543 [2FOUR MILE 69.000] TO BUS 324813 [2CARY 69.000] CKT 1
OPEN LINE FROM BUS 324813 [2CARY 69.000] TO BUS 324376 [2DEER BRANCH69.000] CKT 1
OPEN LINE FROM BUS 324813 [2CARY 69.000] TO BUS 324638 [2MILL CRK KU69.000] CKT 1
OPEN LINE FROM BUS 324376 [2DEER BRANCH69.000] TO BUS 324374 [2CROCKETT KU69.000] CKT 1
OPEN LINE FROM BUS 324374 [2CROCKETT KU69.000] TO BUS 325083 [2ALEX CK TAP69.000] CKT 1
OPEN LINE FROM BUS 325083 [2ALEX CK TAP69.000] TO BUS 326544 [2ALEX CREEK 69.000] CKT 1
OPEN LINE FROM BUS 325083 [2ALEX CK TAP69.000] TO BUS 324377 [2GARDNER 69.000] CKT 1
OPEN LINE FROM BUS 324638 [2MILL CRK KU69.000] TO BUS 324706 [2ROCKY BRNCH69.000] CKT 1
BB-1491 | OPEN LINE FROM BUS 324684 [2PINEVIL 72269.000] TO BUS 324686 [2PINEVILLE 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 8.4631 | 2 | 12.36
OPEN LINE FROM BUS 324684 [2PINEVIL 72269.000] TO BUS 324633 [2MELDRUM 69.000] CKT 1
OPEN LINE FROM BUS 324633 [2MELDRUM 69.000] TO BUS 324636 [2MIDDLESBORO69.000] CKT 1
BB-1303 | OPEN LINE FROM BUS 324415 [2APPOLO FUEL69.000] TO BUS 324593 [2KU PARK 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 2.3472 | 1 | 0.11
OPEN LINE FROM BUS 324415 [2APPOLO FUEL69.000] TO BUS 324636 [2MIDDLESBORO69.000] CKT 1
BB-1374 | OPEN LINE FROM BUS 324460 [2CALLOWAY 69.000] TO BUS 324686 [2PINEVILLE 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.51627 | 20.5936 | 1 | 4.32
OPEN LINE FROM BUS 324460 [2CALLOWAY 69.000] TO BUS 324706 [2ROCKY BRNCH69.000] CKT 1
BB-1367 | OPEN LINE FROM BUS 324456 [2BRUSH CREEK69.000] TO BUS 324465 [2CARPENTER T69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.71908 | 50.4605 | 2 | 11.9079
OPEN LINE FROM BUS 324456 [2BRUSH CREEK69.000] TO BUS 324593 [2KU PARK 69.000] CKT 1
OPEN LINE FROM BUS 324465 [2CARPENTER T69.000] TO BUS 324784 [2WOFFORD 69.000] CKT 1
OPEN LINE FROM BUS 324465 [2CARPENTER T69.000] TO BUS 326535 [2CARPENTER 69.000] CKT 1
BB-1339 | OPEN LINE FROM BUS 324573 [2HINKLE 69.000] TO BUS 324741 [2STINKIN CRK69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.35001 | 31.4118 | 2 | 8.1632
OPEN LINE FROM BUS 324573 [2HINKLE 69.000] TO BUS 324438 [2BIMBLE 69.000] CKT 1
OPEN LINE FROM BUS 324741 [2STINKIN CRK69.000] TO BUS 324593 [2KU PARK 69.000] CKT 1
BB-1308 | OPEN LINE FROM BUS 324423 [2BARBOURVILE69.000] TO BUS 324438 [2BIMBLE 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.18923 | 12.6295 | 1 | 19.37
OPEN LINE FROM BUS 324423 [2BARBOURVILE69.000] TO BUS 324417 [2ARTEMUS 69.000] CKT 1
BB-1338 | OPEN LINE FROM BUS 324515 [2EMANUEL TAP69.000] TO BUS 326530 [2EMANUEL 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.25793 | 18.4836 | 3 | 24.9097
OPEN LINE FROM BUS 324515 [2EMANUEL TAP69.000] TO BUS 324438 [2BIMBLE 69.000] CKT 1
OPEN LINE FROM BUS 324515 [2EMANUEL TAP69.000] TO BUS 324480 [2CMPGND EK T69.000] CKT 1
OPEN LINE FROM BUS 326530 [2EMANUEL 69.000] TO BUS 326539 [2GIRDLER 69.000] CKT 1
OPEN LINE FROM BUS 324480 [2CMPGND EK T69.000] TO BUS 324615 [2LONDON 69.000] CKT 1
OPEN LINE FROM BUS 324480 [2CMPGND EK T69.000] TO BUS 326521 [2CAMPGRND EK69.000] CKT 1
BB-1404 | OPEN LINE FROM BUS 324758 [2US STEEL 69.000] TO BUS 324833 [2CORBIN 2 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.42024 | 24.7219 | 4 | 39.57
OPEN LINE FROM BUS 324758 [2US STEEL 69.000] TO BUS 324527 [2FARLEY KU 69.000] CKT 1
OPEN LINE FROM BUS 324833 [2CORBIN 2 69.000] TO BUS 324832 [2CORBIN 1 69.000] CKT 1
OPEN LINE FROM BUS 324832 [2CORBIN 1 69.000] TO BUS 324482 [2CORBIN EAST69.000] CKT 1
OPEN LINE FROM BUS 324482 [2CORBIN EAST69.000] TO BUS 324748 [2SWEET HOLLO69.000] CKT 1
BB-1442 | OPEN LINE FROM BUS 324704 [2ROCKHOLD 69.000] TO BUS 324784 [2WOFFORD 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.21068 | 24.5695 | 1 | 5.3769
OPEN LINE FROM BUS 324704 [2ROCKHOLD 69.000] TO BUS 324527 [2FARLEY KU 69.000] CKT 1
BB-1513 | OPEN LINE FROM BUS 341755 [2LIBER CH T 69.000] TO BUS 341758 [2LIBERT CHUR69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.31762 | 22.1294 | 4 | 29.125
OPEN LINE FROM BUS 341755 [2LIBER CH T 69.000] TO BUS 324527 [2FARLEY KU 69.000] CKT 1
OPEN LINE FROM BUS 341755 [2LIBER CH T 69.000] TO BUS 341038 [2BACON CRK T69.000] CKT 1
OPEN LINE FROM BUS 341038 [2BACON CRK T69.000] TO BUS 342187 [2S CORBIN 69.000] CKT 1
OPEN LINE FROM BUS 341038 [2BACON CRK T69.000] TO BUS 341035 [2BACON CRK 69.000] CKT 1
OPEN LINE FROM BUS 342187 [2S CORBIN 69.000] TO BUS 341722 [2KEAVY 2 T 69.000] CKT 1
OPEN LINE FROM BUS 341722 [2KEAVY 2 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1
OPEN LINE FROM BUS 341722 [2KEAVY 2 T 69.000] TO BUS 341716 [2KEAVY 69.000] CKT 1
BB-1408 | OPEN LINE FROM BUS 324654 [2MT VIC EK J69.000] TO BUS 324489 [2CUMB FALL T69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.52862 | 41.7212 | 2 | 9.6082
OPEN LINE FROM BUS 324654 [2MT VIC EK J69.000] TO BUS 324514 [2ELIHU 69.000] CKT 1
OPEN LINE FROM BUS 324489 [2CUMB FALL T69.000] TO BUS 324784 [2WOFFORD 69.000] CKT 1
OPEN LINE FROM BUS 324489 [2CUMB FALL T69.000] TO BUS 325034 [2CUMBER FALL69.000] CKT 1
BB-1286 | OPEN LINE FROM BUS 324464 [2CARON 69.000] TO BUS 324615 [2LONDON 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.38597 | 23.1981 | 4 | 34.6892
OPEN LINE FROM BUS 324464 [2CARON 69.000] TO BUS 324860 [2FARISTON 69.000] CKT 1
OPEN LINE FROM BUS 324860 [2FARISTON 69.000] TO BUS 324791 [2AISIN 69.000] CKT 1
OPEN LINE FROM BUS 324791 [2AISIN 69.000] TO BUS 324655 [2N CORBIN T 69.000] CKT 1
OPEN LINE FROM BUS 324655 [2N CORBIN T 69.000] TO BUS 324748 [2SWEET HOLLO69.000] CKT 1
OPEN LINE FROM BUS 324655 [2N CORBIN T 69.000] TO BUS 326542 [2N CORBIN 69.000] CKT 1
BB-1365 | OPEN LINE FROM BUS 324927 [2PINE HILL T69.000] TO BUS 324087 [2MT VERN SO 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.61465 | 27.0598 | 2 | 5.74
OPEN LINE FROM BUS 324927 [2PINE HILL T69.000] TO BUS 324360 [2PINE HILL 69.000] CKT 1
OPEN LINE FROM BUS 324927 [2PINE HILL T69.000] TO BUS 324504 [2E BERNST KU69.000] CKT 1
OPEN LINE FROM BUS 324504 [2E BERNST KU69.000] TO BUS 324662 [2N LONDON KU69.000] CKT 1
BB-1486 | OPEN LINE FROM BUS 324768 [2WACO 69.000] TO BUS 324612 [2LAKE REBA 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.72429 | 48.626 | 3 | 11.7144
OPEN LINE FROM BUS 324768 [2WACO 69.000] TO BUS 324699 [2RICE STA TP69.000] CKT 1
OPEN LINE FROM BUS 324699 [2RICE STA TP69.000] TO BUS 326552 [2SE COAL TP 69.000] CKT 1
OPEN LINE FROM BUS 326552 [2SE COAL TP 69.000] TO BUS 326553 [2SE COAL 69.000] CKT 1
OPEN LINE FROM BUS 326552 [2SE COAL TP 69.000] TO BUS 324767 [2WEST IRVINE69.000] CKT Z1
BB-1322 | OPEN LINE FROM BUS 324525 [2FAIRFIELD 69.000] TO BUS 324974 [2TAYLRV EK T69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 7.5694 | 2 | 10.8
OPEN LINE FROM BUS 324525 [2FAIRFIELD 69.000] TO BUS 324426 [2BARDSTOWN 69.000] CKT 1
OPEN LINE FROM BUS 324974 [2TAYLRV EK T69.000] TO BUS 324752 [2TAYLORSV KU69.000] CKT 1
OPEN LINE FROM BUS 324752 [2TAYLORSV KU69.000] TO BUS 324536 [2FINCHVILLE 69.000] CKT 1
BB-1379 | OPEN LINE FROM BUS 324643 [2MILL WOOD 69.000] TO BUS 324811 [2CANEYVL JCT69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.32139 | 17.3115 | 3 | 14.21
OPEN LINE FROM BUS 324643 [2MILL WOOD 69.000] TO BUS 324609 [2LEITCHFIELD69.000] CKT 1
OPEN LINE FROM BUS 324811 [2CANEYVL JCT69.000] TO BUS 324946 [2ROSINE JCT 69.000] CKT 1
OPEN LINE FROM BUS 324946 [2ROSINE JCT 69.000] TO BUS 324770 [2WARREN 4 69.000] CKT 1
OPEN LINE FROM BUS 324770 [2WARREN 4 69.000] TO BUS 324667 [2OHIO COUNTY69.000] CKT 1
BB-1391 | OPEN LINE FROM BUS 324682 [2PENAL TAP 69.000] TO BUS 324887 [2LA GRANG PE69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.46275 | 27.5271 | 3 | 44.5411
OPEN LINE FROM BUS 324682 [2PENAL TAP 69.000] TO BUS 324469 [2CENTERFIELD69.000] CKT 1
OPEN LINE FROM BUS 324682 [2PENAL TAP 69.000] TO BUS 324598 [2LA GRANGE E69.000] CKT 1
OPEN LINE FROM BUS 324598 [2LA GRANGE E69.000] TO BUS 324585 [2JERICHO 69.000] CKT 1
OPEN LINE FROM BUS 324585 [2JERICHO 69.000] TO BUS 324516 [2EMINENCE KU69.000] CKT 1
BB-1403 | OPEN LINE FROM BUS 324604 [2LEBANON IND69.000] TO BUS 324606 [2LEBANON 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.67279 | 39.4433 | 7 | 61.3983
OPEN LINE FROM BUS 324604 [2LEBANON IND69.000] TO BUS 325020 [2LEBANON E 69.000] CKT 1
OPEN LINE FROM BUS 324603 [2LEBANON CIT69.000] TO BUS 324605 [2LEBANON EK 69.000] CKT 1
OPEN LINE FROM BUS 324603 [2LEBANON CIT69.000] TO BUS 324191 [2LEBANON E T69.000] CKT 1
OPEN LINE FROM BUS 324605 [2LEBANON EK 69.000] TO BUS 324889 [2LEBANON SO 69.000] CKT 1
OPEN LINE FROM BUS 324889 [2LEBANON SO 69.000] TO BUS 324479 [2CAMPBELVL T69.000] CKT 1
OPEN LINE FROM BUS 324479 [2CAMPBELVL T69.000] TO BUS 324751 [2TAYLOR CO 69.000] CKT 1
OPEN LINE FROM BUS 324479 [2CAMPBELVL T69.000] TO BUS 324349 [2CAMPBELVIL269.000] CKT 1
OPEN LINE FROM BUS 324349 [2CAMPBELVIL269.000] TO BUS 324068 [2E CAMPBELVL69.000] CKT 1
BB-1390 | OPEN LINE FROM BUS 324652 [2MUHLENBRG P69.000] TO BUS 324817 [2CENTRAL CIT69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.15341 | 10.9505 | 3 | 17.36
OPEN LINE FROM BUS 324652 [2MUHLENBRG P69.000] TO BUS 324550 [2GREEN RIVER69.000] CKT 1
OPEN LINE FROM BUS 324817 [2CENTRAL CIT69.000] TO BUS 324468 [2CENTRL CI S69.000] CKT 1
OPEN LINE FROM BUS 324468 [2CENTRL CI S69.000] TO BUS 324572 [2HILLSIDE 69.000] CKT 1
BB-1425 | OPEN LINE FROM BUS 326546 [2SUNOCO TAP 69.000] TO BUS 324645 [2MORGANFIELD69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.72982 | 32.975 | 2 | 7.85
OPEN LINE FROM BUS 326546 [2SUNOCO TAP 69.000] TO BUS 324746 [2SUNOCO 69.000] CKT 1
OPEN LINE FROM BUS 326546 [2SUNOCO TAP 69.000] TO BUS 324847 [2DODGE HILL 69.000] CKT 1
OPEN LINE FROM BUS 324847 [2DODGE HILL 69.000] TO BUS 324973 [2STURGIS 69.000] CKT 1
OPEN LINE FROM BUS 324973 [2STURGIS 69.000] TO BUS 324777 [2WHEATCROFT 69.000] CKT 1
BB-1436 | OPEN LINE FROM BUS 324520 [2ETOWN 2 TAP69.000] TO BUS 326555 [2RINEYVIL RD69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.84404 | 33.0726 | 2 | 7.89
OPEN LINE FROM BUS 324520 [2ETOWN 2 TAP69.000] TO BUS 324519 [2ETOWN KU 69.000] CKT 1
OPEN LINE FROM BUS 326555 [2RINEYVIL RD69.000] TO BUS 324698 [2RADCLIFF SO69.000] CKT 1
OPEN LINE FROM BUS 324698 [2RADCLIFF SO69.000] TO BUS 324708 [2ROGERSVILLE69.000] CKT 1
BB-1321 | OPEN LINE FROM BUS 324425 [2BARDT IND T69.000] TO BUS 324426 [2BARDSTOWN 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.15182 | 10.7749 | 1 | 17.37
OPEN LINE FROM BUS 324425 [2BARDT IND T69.000] TO BUS 341407 [2E BARDSTOWN69.000] CKT 1
OPEN LINE FROM BUS 324425 [2BARDT IND T69.000] TO BUS 324345 [2BARDTWN IND69.000] CKT 1
BB-1343 | OPEN LINE FROM BUS 324517 [2ESSERVILLE 69.000] TO BUS 325005 [2WISE TAP 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.24563 | 15.5434 | 3 | 24.01
OPEN LINE FROM BUS 324517 [2ESSERVILLE 69.000] TO BUS 324503 [2DORCHESTER 69.000] CKT 1
OPEN LINE FROM BUS 325005 [2WISE TAP 69.000] TO BUS 324395 [2WISE 69.000] CKT 1
OPEN LINE FROM BUS 325005 [2WISE TAP 69.000] TO BUS 324824 [2CLINCH VALL69.000] CKT 1
OPEN LINE FROM BUS 324824 [2CLINCH VALL69.000] TO BUS 324446 [2BOND 69.000] CKT 1
BB-1300 | OPEN LINE FROM BUS 324440 [2BLACK MOUNT69.000] TO BUS 324621 [2LYNCH 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.39986 | 20.4474 | 2 | 4.33
OPEN LINE FROM BUS 324440 [2BLACK MOUNT69.000] TO BUS 324411 [2ANDOVER TAP69.000] CKT 1
OPEN LINE FROM BUS 324411 [2ANDOVER TAP69.000] TO BUS 324583 [2IMBODEN 69.000] CKT 1
OPEN LINE FROM BUS 324411 [2ANDOVER TAP69.000] TO BUS 324670 [2OSAKA EAST 69.000] CKT 1
OPEN LINE FROM BUS 324670 [2OSAKA EAST 69.000] TO BUS 324412 [2ANDOVER 69.000] CKT 1
OPEN LINE FROM BUS 324412 [2ANDOVER 69.000] TO BUS 326501 [1ANDOVE 34.500] CKT 1
OPEN LINE FROM BUS 326501 [1ANDOVE 34.500] TO BUS 324179 [1MUDLICK 34.500] CKT 1
OPEN LINE FROM BUS 326501 [1ANDOVE 34.500] TO BUS 324369 [1WENTZ 34.500] CKT 1
BB-1294 | OPEN LINE FROM BUS 324696 [2PUCKETT CRK69.000] TO BUS 324706 [2ROCKY BRNCH69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 9.8205 | 6 | 14.71
OPEN LINE FROM BUS 324696 [2PUCKETT CRK69.000] TO BUS 324792 [2ALVA 69.000] CKT 1
OPEN LINE FROM BUS 324792 [2ALVA 69.000] TO BUS 324819 [2CHUNKLIC BR69.000] CKT 1
OPEN LINE FROM BUS 325041 [2STONE TVA 69.000] TO BUS 325068 [2HAMBLIN 69.000] CKT 1
OPEN LINE FROM BUS 325041 [2STONE TVA 69.000] TO BUS 324560 [2HAMBLIN TAP69.000] CKT 1
OPEN LINE FROM BUS 324819 [2CHUNKLIC BR69.000] TO BUS 324945 [2ROSE HILL T69.000] CKT 1
OPEN LINE FROM BUS 324945 [2ROSE HILL T69.000] TO BUS 324380 [2DANIEL BRAN69.000] CKT 1
OPEN LINE FROM BUS 324945 [2ROSE HILL T69.000] TO BUS 324892 [2LIGGETT 69.000] CKT 1
OPEN LINE FROM BUS 324380 [2DANIEL BRAN69.000] TO BUS 324393 [2ROSE HILL 69.000] CKT 1
OPEN LINE FROM BUS 324892 [2LIGGETT 69.000] TO BUS 325007 [2YANCY TAP 69.000] CKT 1
OPEN LINE FROM BUS 325007 [2YANCY TAP 69.000] TO BUS 324815 [2CAWOOD 69.000] CKT 1
OPEN LINE FROM BUS 324815 [2CAWOOD 69.000] TO BUS 324560 [2HAMBLIN TAP69.000] CKT 1
OPEN LINE FROM BUS 324560 [2HAMBLIN TAP69.000] TO BUS 324689 [2POCKET 69.000] CKT 1
BB-1327 | OPEN LINE FROM BUS 324430 [2BEATTYVI KU69.000] TO BUS 325058 [2BEATTY 614 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 8.0425 | 4 | 12.44
OPEN LINE FROM BUS 324430 [2BEATTYVI KU69.000] TO BUS 341071 [2BEATTYV 69.000] CKT 1
OPEN LINE FROM BUS 324430 [2BEATTYVI KU69.000] TO BUS 342697 [5BEATTYV J 161.00] CKT 1
OPEN LINE FROM BUS 324347 [2BEATTY 649 69.000] TO BUS 325058 [2BEATTY 614 69.000] CKT 1
OPEN LINE FROM BUS 324803 [2BEAR TRACK 69.000] TO BUS 324907 [2MILLER CRK 69.000] CKT 1
OPEN LINE FROM BUS 324803 [2BEAR TRACK 69.000] TO BUS 325058 [2BEATTY 614 69.000] CKT 1
OPEN LINE FROM BUS 324803 [2BEAR TRACK 69.000] TO BUS 324057 [1BEAR TRA 34.500] CKT 1
OPEN LINE FROM BUS 324057 [1BEAR TRA 34.500] TO BUS 324383 [1YEL RK N 34.500] CKT 1
OPEN LINE FROM BUS 324856 [2ESTIL ST CO69.000] TO BUS 324880 [2IRVINE 69.000] CKT 1
OPEN LINE FROM BUS 324856 [2ESTIL ST CO69.000] TO BUS 324907 [2MILLER CRK 69.000] CKT 1
OPEN LINE FROM BUS 324880 [2IRVINE 69.000] TO BUS 324496 [2DARK HOLLOW69.000] CKT 1
OPEN LINE FROM BUS 324496 [2DARK HOLLOW69.000] TO BUS 324767 [2WEST IRVINE69.000] CKT 1
BB-1336 | OPEN LINE FROM BUS 324434 [2BEREA TAP 69.000] TO BUS 324435 [2BEREA NORTH69.000] CKT 1 | TRUE | Met convergence tolerances | 4 | 0.23805 | 15.3135 | 3 | 23.7
OPEN LINE FROM BUS 324434 [2BEREA TAP 69.000] TO BUS 324612 [2LAKE REBA 69.000] CKT 1
OPEN LINE FROM BUS 324434 [2BEREA TAP 69.000] TO BUS 324668 [2OKONITE 69.000] CKT 1
BB-1446 | OPEN LINE FROM BUS 324700 [2RICHMND SO 69.000] TO BUS 324938 [2RICHMND 3 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.55507 | 32.049 | 3 | 50.86
OPEN LINE FROM BUS 324700 [2RICHMND SO 69.000] TO BUS 324530 [2FAWKES 69.000] CKT 1
OPEN LINE FROM BUS 324938 [2RICHMND 3 69.000] TO BUS 324940 [2RICHMND J 69.000] CKT 1
OPEN LINE FROM BUS 324940 [2RICHMND J 69.000] TO BUS 324936 [2RICHMND IND69.000] CKT 1
OPEN LINE FROM BUS 324936 [2RICHMND IND69.000] TO BUS 324668 [2OKONITE 69.000] CKT 1
BB-1514 | OPEN LINE FROM BUS 341362 [2CROOKSVIL T69.000] TO BUS 341406 [2DUNCAN LN T69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.60988 | 40.919 | 5 | 54.0753
OPEN LINE FROM BUS 341362 [2CROOKSVIL T69.000] TO BUS 341611 [2HICKORY PL 69.000] CKT 1
OPEN LINE FROM BUS 341362 [2CROOKSVIL T69.000] TO BUS 341359 [2CROOKSVIL 69.000] CKT 1
OPEN LINE FROM BUS 341359 [2CROOKSVIL 69.000] TO BUS 342288 [2SPEEDWELL 69.000] CKT 1
OPEN LINE FROM BUS 341611 [2HICKORY PL 69.000] TO BUS 342103 [2PPG 69.000] CKT 1
OPEN LINE FROM BUS 342103 [2PPG 69.000] TO BUS 342106 [2PPG J 69.000] CKT 1
OPEN LINE FROM BUS 342106 [2PPG J 69.000] TO BUS 341008 [2ALCAN 69.000] CKT 1
OPEN LINE FROM BUS 341008 [2ALCAN 69.000] TO BUS 342430 [2W BEREA 69.000] CKT 1
BB-1345 | OPEN LINE FROM BUS 325087 [2CLAY LICK T69.000] TO BUS 324445 [2BONDS MILL 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.34863 | 18.0005 | 2 | 4.12
OPEN LINE FROM BUS 325087 [2CLAY LICK T69.000] TO BUS 324715 [2SALVISA 69.000] CKT 1
OPEN LINE FROM BUS 324715 [2SALVISA 69.000] TO BUS 324721 [2SHAKERTOWN 69.000] CKT 1
OPEN LINE FROM BUS 324721 [2SHAKERTOWN 69.000] TO BUS 324764 [2WEST CLIFF 69.000] CKT 1
BB-1361 | OPEN LINE FROM BUS 326528 [2BRIDGEPORT 69.000] TO BUS 326974 [2BRIDGPRT 2 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.19837 | 24.0646 | 1 | 5.8078
OPEN LINE FROM BUS 326528 [2BRIDGEPORT 69.000] TO BUS 324535 [2E FRANKFORT69.000] CKT 1
OPEN LINE FROM BUS 326528 [2BRIDGEPORT 69.000] TO BUS 324765 [2W FRANKFORT69.000] CKT 1
BB-3000 | OPEN LINE FROM BUS 324511 [2ECHOLS 69.000] TO BUS 324584 [2INDIAN HILL69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.49298 | 20.0787 | 5 | 3.76
OPEN LINE FROM BUS 324511 [2ECHOLS 69.000] TO BUS 324959 [2SIMMONS 69.000] CKT 1
OPEN LINE FROM BUS 324959 [2SIMMONS 69.000] TO BUS 326564 [2LEW BREC 69.000] CKT 1
OPEN LINE FROM BUS 324959 [2SIMMONS 69.000] TO BUS 324703 [2RIVERVIEW 69.000] CKT 1
OPEN LINE FROM BUS 326564 [2LEW BREC 69.000] TO BUS 324124 [2CENTRTOWN S69.000] CKT 1
OPEN LINE FROM BUS 324703 [2RIVERVIEW 69.000] TO BUS 324667 [2OHIO COUNTY69.000] CKT 1
BB-1337 | OPEN LINE FROM BUS 324049 [2OXFORD COAL69.000] TO BUS 324572 [2HILLSIDE 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 8.247 | 7 | 12.27
OPEN LINE FROM BUS 324049 [2OXFORD COAL69.000] TO BUS 324745 [2STRINGTOWN 69.000] CKT 1
OPEN LINE FROM BUS 324745 [2STRINGTOWN 69.000] TO BUS 324437 [2BEVIER KU 69.000] CKT 1
OPEN LINE FROM BUS 324060 [1BEECH CR 34.500] TO BUS 324056 [1BCH CR T 34.500] CKT 1
OPEN LINE FROM BUS 324062 [1BEECHMNT 34.500] TO BUS 324056 [1BCH CR T 34.500] CKT 1
OPEN LINE FROM BUS 324048 [2PARKWY MINE69.000] TO BUS 324437 [2BEVIER KU 69.000] CKT 1
OPEN LINE FROM BUS 324048 [2PARKWY MINE69.000] TO BUS 324584 [2INDIAN HILL69.000] CKT 1
OPEN LINE FROM BUS 324437 [2BEVIER KU 69.000] TO BUS 324063 [1BEVIER 34.500] CKT 1
OPEN LINE FROM BUS 324063 [1BEVIER 34.500] TO BUS 324187 [1REED M T 34.500] CKT 1
OPEN LINE FROM BUS 324187 [1REED M T 34.500] TO BUS 324188 [1REED MIN 34.500] CKT 1
OPEN LINE FROM BUS 324187 [1REED M T 34.500] TO BUS 324122 [1DRAKESBO 34.500] CKT 1
OPEN LINE FROM BUS 324122 [1DRAKESBO 34.500] TO BUS 324056 [1BCH CR T 34.500] CKT 1
BB-1432 | OPEN LINE FROM BUS 326513 [2EQAL M BREC69.000] TO BUS 324550 [2GREEN RIVER69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.19308 | 15.3892 | 1 | 0.98
OPEN LINE FROM BUS 326513 [2EQAL M BREC69.000] TO BUS 324659 [2NELSON 69.000] CKT 1
OPEN LINE FROM BUS 324659 [2NELSON 69.000] TO BUS 324584 [2INDIAN HILL69.000] CKT 1
BB-1461 | OPEN LINE FROM BUS 324691 [2POWDERLY 69.000] TO BUS 324870 [2GREENVILLE 69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.24179 | 15.7265 | 5 | 25.21
OPEN LINE FROM BUS 324691 [2POWDERLY 69.000] TO BUS 324572 [2HILLSIDE 69.000] CKT 1
OPEN LINE FROM BUS 324870 [2GREENVILLE 69.000] TO BUS 324556 [2GREENV W TP69.000] CKT 1
OPEN LINE FROM BUS 324556 [2GREENV W TP69.000] TO BUS 324702 [2RIVER QUEEN69.000] CKT 1
OPEN LINE FROM BUS 324556 [2GREENV W TP69.000] TO BUS 326593 [2GREENVIL N 69.000] CKT 1
OPEN LINE FROM BUS 324077 [2GREENVILE W69.000] TO BUS 326594 [2GREENVL 12 69.000] CKT 1
BB-1353 | OPEN LINE FROM BUS 324630 [2MADSNV LP E69.000] TO BUS 324862 [2FIES CITY 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.47361 | 27.9603 | 6 | 45.93
OPEN LINE FROM BUS 324630 [2MADSNV LP E69.000] TO BUS 324902 [2MCCOY AVE 69.000] CKT 1
OPEN LINE FROM BUS 324630 [2MADSNV LP E69.000] TO BUS 324506 [2EARLINGTN N69.000] CKT 1
OPEN LINE FROM BUS 325086 [2KEN AMERI 269.000] TO BUS 324723 [2SHAVER CHAP69.000] CKT 1
OPEN LINE FROM BUS 325086 [2KEN AMERI 269.000] TO BUS 324862 [2FIES CITY 69.000] CKT 1
OPEN LINE FROM BUS 324723 [2SHAVER CHAP69.000] TO BUS 324550 [2GREEN RIVER69.000] CKT 1
OPEN LINE FROM BUS 324902 [2MCCOY AVE 69.000] TO BUS 324896 [2MADSNV E 69.000] CKT 1
OPEN LINE FROM BUS 324896 [2MADSNV E 69.000] TO BUS 324873 [2HANSON JCT 69.000] CKT 1
OPEN LINE FROM BUS 324873 [2HANSON JCT 69.000] TO BUS 324061 [2BORG-WARNER69.000] CKT 1
OPEN LINE FROM BUS 324061 [2BORG-WARNER69.000] TO BUS 324079 [2HANSON 69.000] CKT 1
BB-1457 | OPEN LINE FROM BUS 324505 [2E DIAMOND 69.000] TO BUS 324506 [2EARLINGTN N69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.57212 | 26.463 | 2 | 5.92
OPEN LINE FROM BUS 324505 [2E DIAMOND 69.000] TO BUS 324947 [2RUMSEY 69.000] CKT 1
OPEN LINE FROM BUS 324947 [2RUMSEY 69.000] TO BUS 324190 [1RUMSEY 34.500] CKT 1
OPEN LINE FROM BUS 324947 [2RUMSEY 69.000] TO BUS 324551 [2GR RVR STL 69.000] CKT 1
OPEN LINE FROM BUS 324947 [2RUMSEY 69.000] TO BUS 324810 [2CALHOUN 69.000] CKT 1
B-69-41 | OPEN LINE FROM BUS 324709 [2RVR QUEEN T69.000] TO BUS 324981 [2TEXAS GAS T69.000] CKT 1 | TRUE | Met convergence tolerances | 7 | 0.17316 | 11.9432 | 8 | 18.71
OPEN LINE FROM BUS 324709 [2RVR QUEEN T69.000] TO BUS 324550 [2GREEN RIVER69.000] CKT 1
OPEN LINE FROM BUS 324709 [2RVR QUEEN T69.000] TO BUS 324587 [2KEN AMERICA69.000] CKT 1
OPEN LINE FROM BUS 324587 [2KEN AMERICA69.000] TO BUS 324702 [2RIVER QUEEN69.000] CKT 1
OPEN LINE FROM BUS 324981 [2TEXAS GAS T69.000] TO BUS 325062 [2TEXAS GAS 69.000] CKT 1
OPEN LINE FROM BUS 324981 [2TEXAS GAS T69.000] TO BUS 324820 [2ISLAND MINE69.000] CKT 1
OPEN LINE FROM BUS 324820 [2ISLAND MINE69.000] TO BUS 324850 [2DOZIER H 69.000] CKT 1
OPEN LINE FROM BUS 324850 [2DOZIER H 69.000] TO BUS 324507 [2EARLINGTON 69.000] CKT 1
OPEN LINE FROM BUS 324507 [2EARLINGTON 69.000] TO BUS 324769 [2WALKER KU 69.000] CKT 1
OPEN LINE FROM BUS 324507 [2EARLINGTON 69.000] TO BUS 324123 [1EARLINGT 34.500] CKT 1
BB-1299 | OPEN LINE FROM BUS 324954 [2SENTRY TAP 69.000] TO BUS 325762 [2WARRIOR TAP69.000] CKT 1 | TRUE | Met convergence tolerances | 3 | 0.14287 | 9.8978 | 4 | 15.03
OPEN LINE FROM BUS 324954 [2SENTRY TAP 69.000] TO BUS 324506 [2EARLINGTN N69.000] CKT 1
OPEN LINE FROM BUS 324954 [2SENTRY TAP 69.000] TO BUS 324898 [2MANITOU 69.000] CKT 1
OPEN LINE FROM BUS 324898 [2MANITOU 69.000] TO BUS 324993 [2WARRIOR CL 69.000] CKT 1
OPEN LINE FROM BUS 324993 [2WARRIOR CL 69.000] TO BUS 324774 [2WEBCOAL 4 69.000] CKT 1
OPEN LINE FROM BUS 324774 [2WEBCOAL 4 69.000] TO BUS 324658 [2NEBO 69.000] CKT 1
BB-1428 | OPEN LINE FROM BUS 324631 [2MADSNV LP W69.000] TO BUS 324658 [2NEBO 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.46999 | 27.7141 | 4 | 45.41
OPEN LINE FROM BUS 324631 [2MADSNV LP W69.000] TO BUS 324893 [2MADSNV GE T69.000] CKT 1
OPEN LINE FROM BUS 324631 [2MADSNV LP W69.000] TO BUS 324506 [2EARLINGTN N69.000] CKT 1
OPEN LINE FROM BUS 324893 [2MADSNV GE T69.000] TO BUS 324897 [2MADSNV N 69.000] CKT 1
OPEN LINE FROM BUS 324893 [2MADSNV GE T69.000] TO BUS 326587 [2MADSNV W TP69.000] CKT 1
OPEN LINE FROM BUS 324081 [2MADSNV GE 69.000] TO BUS 326587 [2MADSNV W TP69.000] CKT 1
OPEN LINE FROM BUS 324083 [2MADSNV W 69.000] TO BUS 326587 [2MADSNV W TP69.000] CKT 1
OPEN LINE FROM BUS 324895 [2MADSNV HO 69.000] TO BUS 324897 [2MADSNV N 69.000] CKT 1
BB-1428A | OPEN LINE FROM BUS 324631 [2MADSNV LP W69.000] TO BUS 324658 [2NEBO 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.46999 | 27.7141 | 4 | 45.41
OPEN LINE FROM BUS 324631 [2MADSNV LP W69.000] TO BUS 324893 [2MADSNV GE T69.000] CKT 1
OPEN LINE FROM BUS 324631 [2MADSNV LP W69.000] TO BUS 324506 [2EARLINGTN N69.000] CKT 1
OPEN LINE FROM BUS 324893 [2MADSNV GE T69.000] TO BUS 324897 [2MADSNV N 69.000] CKT 1
OPEN LINE FROM BUS 324893 [2MADSNV GE T69.000] TO BUS 326587 [2MADSNV W TP69.000] CKT 1
OPEN LINE FROM BUS 324081 [2MADSNV GE 69.000] TO BUS 326587 [2MADSNV W TP69.000] CKT 1
OPEN LINE FROM BUS 324083 [2MADSNV W 69.000] TO BUS 326587 [2MADSNV W TP69.000] CKT 1
OPEN LINE FROM BUS 324897 [2MADSNV N 69.000] TO BUS 324895 [2MADSNV HO 69.000] CKT 1
B-69-40 | OPEN LINE FROM BUS 324769 [2WALKER KU 69.000] TO BUS 324164 [5WALKER 161.00] CKT 1 | TRUE | Met convergence tolerances | 10 | 0.14287 | 9.0341 | 5 | 12.07
OPEN LINE FROM BUS 324769 [2WALKER KU 69.000] TO BUS 324506 [2EARLINGTN N69.000] CKT 1
OPEN LINE FROM BUS 324769 [2WALKER KU 69.000] TO BUS 324507 [2EARLINGTON 69.000] CKT 1
OPEN LINE FROM BUS 324769 [2WALKER KU 69.000] TO BUS 324577 [2HARDESTY A 69.000] CKT 1
OPEN LINE FROM BUS 324769 [2WALKER KU 69.000] TO BUS 324578 [2HARDESTY B 69.000] CKT 1
OPEN LINE FROM BUS 324769 [2WALKER KU 69.000] TO BUS 324648 [2MORTONS GAP69.000] CKT 1
BB-1464 | OPEN LINE FROM BUS 324577 [2HARDESTY A 69.000] TO BUS 324693 [2PRINCETON 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 1.533
OPEN LINE FROM BUS 324577 [2HARDESTY A 69.000] TO BUS 324769 [2WALKER KU 69.000] CKT 1
BB-1410 | OPEN LINE FROM BUS 324747 [2SUNSET MINE69.000] TO BUS 324690 [2DAWSON TAP 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.96131 | 48.4776 | 6 | 11.833
OPEN LINE FROM BUS 324747 [2SUNSET MINE69.000] TO BUS 324693 [2PRINCETON 69.000] CKT 1
OPEN LINE FROM BUS 324843 [2DAWSON IND 69.000] TO BUS 324065 [2DAWSON 764 69.000] CKT 1
OPEN LINE FROM BUS 324843 [2DAWSON IND 69.000] TO BUS 324690 [2DAWSON TAP 69.000] CKT 1
OPEN LINE FROM BUS 324578 [2HARDESTY B 69.000] TO BUS 324690 [2DAWSON TAP 69.000] CKT 1
OPEN LINE FROM BUS 324578 [2HARDESTY B 69.000] TO BUS 324769 [2WALKER KU 69.000] CKT 1
OPEN LINE FROM BUS 324578 [2HARDESTY B 69.000] TO BUS 324142 [1HARDSTY 34.500] CKT 1
OPEN LINE FROM BUS 324142 [1HARDSTY 34.500] TO BUS 324720 [1SIXTHVEIN 34.500] CKT 1
OPEN LINE FROM BUS 324720 [1SIXTHVEIN 34.500] TO BUS 324129 [1HARDST J 34.500] CKT 1
OPEN LINE FROM BUS 324129 [1HARDST J 34.500] TO BUS 324182 [1OUTWOOD 34.500] CKT 1
BB-1326 | OPEN LINE FROM BUS 324931 [2PROVIDNCE E69.000] TO BUS 324658 [2NEBO 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 7.6611 | 6 | 11.04
OPEN LINE FROM BUS 324931 [2PROVIDNCE E69.000] TO BUS 324799 [2BARNHILL 69.000] CKT 1
OPEN LINE FROM BUS 324996 [2DOTIKI TAP 69.000] TO BUS 325010 [2WEBCOAL 2 69.000] CKT 1
OPEN LINE FROM BUS 324996 [2DOTIKI TAP 69.000] TO BUS 324822 [2CLAY KU 69.000] CKT 1
OPEN LINE FROM BUS 324996 [2DOTIKI TAP 69.000] TO BUS 324846 [2DIAMOND 69.000] CKT 1
OPEN LINE FROM BUS 325010 [2WEBCOAL 2 69.000] TO BUS 325011 [2DOTIKI 69.000] CKT 1
OPEN LINE FROM BUS 324799 [2BARNHILL 69.000] TO BUS 324932 [2PROVIDENCE 69.000] CKT 1
OPEN LINE FROM BUS 324932 [2PROVIDENCE 69.000] TO BUS 324846 [2DIAMOND 69.000] CKT 1
OPEN LINE FROM BUS 324822 [2CLAY KU 69.000] TO BUS 324471 [2CHRISTIAN 69.000] CKT 1
OPEN LINE FROM BUS 324471 [2CHRISTIAN 69.000] TO BUS 324777 [2WHEATCROFT 69.000] CKT 1
BB-1406 | OPEN LINE FROM BUS 324571 [2HIGHLAND MI69.000] TO BUS 324671 [2OVERLAD S T69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.48609 | 23.2998 | 3 | 5.2
OPEN LINE FROM BUS 324571 [2HIGHLAND MI69.000] TO BUS 324484 [2CORYDON 69.000] CKT 1
OPEN LINE FROM BUS 324671 [2OVERLAD S T69.000] TO BUS 324086 [2MORGANF IND69.000] CKT 1
OPEN LINE FROM BUS 324671 [2OVERLAD S T69.000] TO BUS 324645 [2MORGANFIELD69.000] CKT 1
OPEN LINE FROM BUS 324086 [2MORGANF IND69.000] TO BUS 324096 [2PEA WSH TAP69.000] CKT 1
OPEN LINE FROM BUS 324091 [2OVERLAND SO69.000] TO BUS 324096 [2PEA WSH TAP69.000] CKT 1
B-69-42 | OPEN LINE FROM BUS 324718 [2SHELBY CO T69.000] TO BUS 324726 [2SHELBYVIL S69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.21023 | 13.7248 | 1 | 21.57
OPEN LINE FROM BUS 324718 [2SHELBY CO T69.000] TO BUS 342248 [2SHELBY TAP 69.000] CKT 1
OPEN LINE FROM BUS 324718 [2SHELBY CO T69.000] TO BUS 324536 [2FINCHVILLE 69.000] CKT 1
OPEN LINE FROM BUS 324726 [2SHELBYVIL S69.000] TO BUS 324727 [2SHELBYVILLE69.000] CKT 1
BB-1399 | OPEN LINE FROM BUS 324725 [2SHELBYVIL E69.000] TO BUS 324727 [2SHELBYVILLE69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.43496 | 26.8431 | 4 | 40.5588
OPEN LINE FROM BUS 324725 [2SHELBYVIL E69.000] TO BUS 324474 [2CLAY VILG T69.000] CKT 1
OPEN LINE FROM BUS 324474 [2CLAY VILG T69.000] TO BUS 324765 [2W FRANKFORT69.000] CKT 1
OPEN LINE FROM BUS 324474 [2CLAY VILG T69.000] TO BUS 341317 [2CLAY VILLAG69.000] CKT 1
OPEN LINE FROM BUS 341317 [2CLAY VILLAG69.000] TO BUS 341390 [2DEFOE TAP 69.000] CKT 1
OPEN LINE FROM BUS 341950 [2NEW CASTLE 69.000] TO BUS 342007 [2OWEN CO 69.000] CKT 1
OPEN LINE FROM BUS 341950 [2NEW CASTLE 69.000] TO BUS 341390 [2DEFOE TAP 69.000] CKT 1
BB-1346 | OPEN LINE FROM BUS 324620 [2LAWRENCEBRG69.000] TO BUS 324445 [2BONDS MILL 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.26211 | 16.4 | 1 | 25.37
OPEN LINE FROM BUS 324620 [2LAWRENCEBRG69.000] TO BUS 324537 [2FLA TILE T269.000] CKT 1
OPEN LINE FROM BUS 324537 [2FLA TILE T269.000] TO BUS 324755 [2TYRONE 69.000] CKT 1
B-69-78 | OPEN LINE FROM BUS 324404 [2LYNDON TAP 69.000] TO BUS 324622 [2LYNDON SO 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 2.8929
OPEN LINE FROM BUS 324404 [2LYNDON TAP 69.000] TO BUS 324623 [2LYNDON 69.000] CKT 1
OPEN LINE FROM BUS 324404 [2LYNDON TAP 69.000] TO BUS 324750 [2TAYLOR LG 69.000] CKT 1
BB-1332 | OPEN LINE FROM BUS 324710 [2RVR CITY SH69.000] TO BUS 324750 [2TAYLOR LG 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.17741 | 15.3072 | 1 | 2.73
OPEN LINE FROM BUS 324710 [2RVR CITY SH69.000] TO BUS 324429 [2BEARGRASS 69.000] CKT 1
BB-1402 | OPEN LINE FROM BUS 324641 [2MILE LAN TP69.000] TO BUS 324751 [2TAYLOR CO 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.49541 | 30.789 | 5 | 45.7526
OPEN LINE FROM BUS 324641 [2MILE LAN TP69.000] TO BUS 324829 [2CAMPBELVIL169.000] CKT 1
OPEN LINE FROM BUS 324641 [2MILE LAN TP69.000] TO BUS 326970 [2MILE LAN EK69.000] CKT 1
OPEN LINE FROM BUS 324829 [2CAMPBELVIL169.000] TO BUS 324557 [2GR RVR PLAZ69.000] CKT 1
OPEN LINE FROM BUS 324557 [2GR RVR PLAZ69.000] TO BUS 324830 [2CAMPBELV EK69.000] CKT 1
OPEN LINE FROM BUS 324830 [2CAMPBELV EK69.000] TO BUS 341320 [2COBURG 69.000] CKT 1
OPEN LINE FROM BUS 324830 [2CAMPBELV EK69.000] TO BUS 324554 [2GRENSBRG KU69.000] CKT 1
OPEN LINE FROM BUS 324554 [2GRENSBRG KU69.000] TO BUS 341563 [2GREEN CO 69.000] CKT 1
BB-1398 | OPEN LINE FROM BUS 324607 [2LEITCHF CIT69.000] TO BUS 324608 [2LEITCHF E 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.23013 | 15.0256 | 5 | 22.49
OPEN LINE FROM BUS 324607 [2LEITCHF CIT69.000] TO BUS 324609 [2LEITCHFIELD69.000] CKT 1
OPEN LINE FROM BUS 324608 [2LEITCHF E 69.000] TO BUS 324992 [2WARREN TIE 69.000] CKT 1
OPEN LINE FROM BUS 324992 [2WARREN TIE 69.000] TO BUS 324821 [2CLARKSON 69.000] CKT 1
OPEN LINE FROM BUS 324821 [2CLARKSON 69.000] TO BUS 324914 [2M-V CLARK T69.000] CKT 1
OPEN LINE FROM BUS 324914 [2M-V CLARK T69.000] TO BUS 324358 [2M-V CLARKSN69.000] CKT 1
OPEN LINE FROM BUS 324914 [2M-V CLARK T69.000] TO BUS 324509 [2EASTVIEW 69.000] CKT 1
OPEN LINE FROM BUS 324509 [2EASTVIEW 69.000] TO BUS 342307 [2STEPHENSBRG69.000] CKT 1
BB-1453 | OPEN LINE FROM BUS 324614 [2LOCUST TAP 69.000] TO BUS 324719 [2SEMINOLE 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.20131 | 13.2197 | 1 | 20.82
OPEN LINE FROM BUS 324614 [2LOCUST TAP 69.000] TO BUS 326545 [2LOCUST LGE 69.000] CKT 1
OPEN LINE FROM BUS 324614 [2LOCUST TAP 69.000] TO BUS 324538 [2FLOYD 69.000] CKT 1
BB-1274 | OPEN LINE FROM BUS 324444 [2BLUELICK EK69.000] TO BUS 324651 [2MUD LANE 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.45002 | 29.2049 | 3 | 41.9486
OPEN LINE FROM BUS 324444 [2BLUELICK EK69.000] TO BUS 324788 [2BROOKS EK T69.000] CKT 1
OPEN LINE FROM BUS 324788 [2BROOKS EK T69.000] TO BUS 324809 [2BROOKS EKPC69.000] CKT 1
OPEN LINE FROM BUS 324788 [2BROOKS EK T69.000] TO BUS 324740 [2SOUTH PARK 69.000] CKT 1
OPEN LINE FROM BUS 324809 [2BROOKS EKPC69.000] TO BUS 324958 [2SHEPHRDSV T69.000] CKT 1
OPEN LINE FROM BUS 324958 [2SHEPHRDSV T69.000] TO BUS 325043 [2SHEPHERDSV 69.000] CKT 1
BB-1277 | OPEN LINE FROM BUS 324616 [2LONG RUN 69.000] TO BUS 324775 [2WHAS 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.49149 | 28.9327 | 2 | 47.4524
OPEN LINE FROM BUS 324616 [2LONG RUN 69.000] TO BUS 324403 [2CRESTWOOD T69.000] CKT 1
OPEN LINE FROM BUS 324403 [2CRESTWOOD T69.000] TO BUS 324469 [2CENTERFIELD69.000] CKT 1
OPEN LINE FROM BUS 324403 [2CRESTWOOD T69.000] TO BUS 324487 [2CRESTWOOD 69.000] CKT 1
OPEN LINE FROM BUS 324487 [2CRESTWOOD 69.000] TO BUS 324481 [2COLLINS 69.000] CKT 1
BB-1289 | OPEN LINE FROM BUS 324649 [2MORRIS FORM69.000] TO BUS 324675 [2PADDYS RUN 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.52431 | 24.1859 | 1 | 5.64
OPEN LINE FROM BUS 324649 [2MORRIS FORM69.000] TO BUS 324408 [2ALGONQUIN 69.000] CKT 1
BB-1328 | OPEN LINE FROM BUS 324453 [2BEARGRS PMP69.000] TO BUS 324475 [2CLIFTON 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 1.4206
OPEN LINE FROM BUS 324453 [2BEARGRS PMP69.000] TO BUS 324429 [2BEARGRASS 69.000] CKT 1
BB-1272 | OPEN LINE FROM BUS 325022 [2EASTWOOD W 69.000] TO BUS 324400 [2WHAS TAP 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.31049 | 19.0009 | 2 | 32.25
OPEN LINE FROM BUS 325022 [2EASTWOOD W 69.000] TO BUS 324406 [2AIKEN 69.000] CKT 1
OPEN LINE FROM BUS 324400 [2WHAS TAP 69.000] TO BUS 324510 [2EASTWOOD 69.000] CKT 1
OPEN LINE FROM BUS 324400 [2WHAS TAP 69.000] TO BUS 324775 [2WHAS 69.000] CKT 1
OPEN LINE FROM BUS 324775 [2WHAS 69.000] TO BUS 324616 [2LONG RUN 69.000] CKT 1
B-69-45 | OPEN LINE FROM BUS 324662 [2N LONDON KU69.000] TO BUS 324688 [2PITTSBRG KU69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 3.332
OPEN LINE FROM BUS 324662 [2N LONDON KU69.000] TO BUS 341929 [2N LONDON 69.000] CKT 1
OPEN LINE FROM BUS 324662 [2N LONDON KU69.000] TO BUS 324504 [2E BERNST KU69.000] CKT 1
BB-1512 | OPEN LINE FROM BUS 342340 [2THARP T 69.000] TO BUS 324519 [2ETOWN KU 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.17576 | 13.9936 | 2 | 19.4062
OPEN LINE FROM BUS 342340 [2THARP T 69.000] TO BUS 341458 [2ETOWN EK2 69.000] CKT 1
OPEN LINE FROM BUS 342340 [2THARP T 69.000] TO BUS 342337 [2THARP 69.000] CKT 1
OPEN LINE FROM BUS 341458 [2ETOWN EK2 69.000] TO BUS 341455 [2ETOWN EK1 69.000] CKT 1
BB-1470 | OPEN LINE FROM BUS 324579 [2HARMNY LAND69.000] TO BUS 324580 [2HARRODS CRK69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.1559 | 10.9532 | 1 | 16.27
OPEN LINE FROM BUS 324579 [2HARMNY LAND69.000] TO BUS 324960 [2SKYLIGHT 69.000] CKT 1
BB-1430 | OPEN LINE FROM BUS 324729 [2SIMPSONVILL69.000] TO BUS 325102 [2W SHELBY 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.145 | 10.3905 | 1 | 16.53
OPEN LINE FROM BUS 324729 [2SIMPSONVILL69.000] TO BUS 324510 [2EASTWOOD 69.000] CKT 1
BB-1450 | OPEN LINE FROM BUS 324653 [2M-V SIMPSON69.000] TO BUS 324536 [2FINCHVILLE 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.17569 | 15.49 | 1 | 2.43
OPEN LINE FROM BUS 324653 [2M-V SIMPSON69.000] TO BUS 324637 [2MIDDLETOWN 69.000] CKT 1
BB-1424 | OPEN LINE FROM BUS 324737 [2SOMERSET SO69.000] TO BUS 324969 [2SMRST 615KU69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.35025 | 21.424 | 4 | 33.3515
OPEN LINE FROM BUS 324737 [2SOMERSET SO69.000] TO BUS 342287 [2SOMERSET KU69.000] CKT 1
OPEN LINE FROM BUS 324969 [2SMRST 615KU69.000] TO BUS 324990 [2WAITSBORO 69.000] CKT 1
OPEN LINE FROM BUS 324990 [2WAITSBORO 69.000] TO BUS 324787 [2UNION UNDWR69.000] CKT 1
OPEN LINE FROM BUS 324787 [2UNION UNDWR69.000] TO BUS 342232 [2SEWELLTON 69.000] CKT 1
OPEN LINE FROM BUS 342232 [2SEWELLTON 69.000] TO BUS 342178 [2RUSSEL CO 69.000] CKT 1
BB-1393 | OPEN LINE FROM BUS 324470 [2CERRO-SALEM69.000] TO BUS 324486 [2CRITTENDEN 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 9.7969 | 5 | 14.99
OPEN LINE FROM BUS 324470 [2CERRO-SALEM69.000] TO BUS 324948 [2SALEM KU 69.000] CKT 1
OPEN LINE FROM BUS 324948 [2SALEM KU 69.000] TO BUS 324949 [2SALEM 673 69.000] CKT 1
OPEN LINE FROM BUS 324948 [2SALEM KU 69.000] TO BUS 324883 [1SALEM 34.500] CKT 1
OPEN LINE FROM BUS 324053 [13 RVR RK 34.500] TO BUS 324070 [1BISSEL B 34.500] CKT 1
OPEN LINE FROM BUS 324070 [1BISSEL B 34.500] TO BUS 324883 [1SALEM 34.500] CKT 1
OPEN LINE FROM BUS 324949 [2SALEM 673 69.000] TO BUS 324852 [2DYCUSBURG 69.000] CKT 1
OPEN LINE FROM BUS 324852 [2DYCUSBURG 69.000] TO BUS 324885 [2KUTTAWA 69.000] CKT 1
OPEN LINE FROM BUS 324885 [2KUTTAWA 69.000] TO BUS 324513 [2EDDYVILLE 69.000] CKT 1
OPEN LINE FROM BUS 324513 [2EDDYVILLE 69.000] TO BUS 324693 [2PRINCETON 69.000] CKT 1
BB-1392 | OPEN LINE FROM BUS 324681 [2PENAL FARM 69.000] TO BUS 324960 [2SKYLIGHT 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.75381 | 29.6522 | 1 | 6.86
OPEN LINE FROM BUS 324681 [2PENAL FARM 69.000] TO BUS 324469 [2CENTERFIELD69.000] CKT 1
OPEN LINE FROM BUS 324960 [2SKYLIGHT 69.000] TO BUS 324579 [2HARMNY LAND69.000] CKT 1
BB-1375 | OPEN LINE FROM BUS 324499 [2DEL PARK 69.000] TO BUS 324552 [2GRADY 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.26893 | 16.7563 | 1 | 26.99
OPEN LINE FROM BUS 324499 [2DEL PARK 69.000] TO BUS 324462 [2CANAL 69.000] CKT 1
B-69-136 | OPEN LINE FROM BUS 324406 [2AIKEN 69.000] TO BUS 324637 [2MIDDLETOWN 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.51608 | 29.896 | 1 | 51.44
OPEN LINE FROM BUS 324406 [2AIKEN 69.000] TO BUS 324673 [2OXMOOR 69.000] CKT 1
OPEN LINE FROM BUS 324406 [2AIKEN 69.000] TO BUS 325022 [2EASTWOOD W 69.000] CKT 1
B-69-137 | OPEN LINE FROM BUS 324561 [2HANCOCK 69.000] TO BUS 324259 [4HANCOCK 138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 2.0492
OPEN LINE FROM BUS 324561 [2HANCOCK 69.000] TO BUS 324473 [2CLAY LGE 69.000] CKT 1
OPEN LINE FROM BUS 324561 [2HANCOCK 69.000] TO BUS 324538 [2FLOYD 69.000] CKT 1
B-69-140 | OPEN LINE FROM BUS 324401 [2FREYS HIL J69.000] TO BUS 324541 [2FORD 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.59781 | 24.238
OPEN LINE FROM BUS 324401 [2FREYS HIL J69.000] TO BUS 324545 [2FREYS HILL 69.000] CKT 1
OPEN LINE FROM BUS 324401 [2FREYS HIL J69.000] TO BUS 324785 [2WORTHINGTON69.000] CKT 1
B-69-141 | OPEN LINE FROM BUS 324623 [2LYNDON 69.000] TO BUS 324637 [2MIDDLETOWN 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14929 | 10.6794 | 1 | 17.24
OPEN LINE FROM BUS 324623 [2LYNDON 69.000] TO BUS 324404 [2LYNDON TAP 69.000] CKT 1
OPEN LINE FROM BUS 324623 [2LYNDON 69.000] TO BUS 324545 [2FREYS HILL 69.000] CKT 1
BB-1364 | OPEN LINE FROM BUS 324485 [2CRAB ORCH T69.000] TO BUS 324600 [2LANCASTR KU69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.78211 | 32.7574 | 3 | 7.81
OPEN LINE FROM BUS 324485 [2CRAB ORCH T69.000] TO BUS 324808 [2BRODHEAD KU69.000] CKT 1
OPEN LINE FROM BUS 324485 [2CRAB ORCH T69.000] TO BUS 324350 [2CRAB ORCHAR69.000] CKT 1
OPEN LINE FROM BUS 324808 [2BRODHEAD KU69.000] TO BUS 324913 [2MT VERNON 69.000] CKT 1
OPEN LINE FROM BUS 324808 [2BRODHEAD KU69.000] TO BUS 324348 [2BRODHEAD CI69.000] CKT 1
OPEN LINE FROM BUS 324359 [2MT VERN 58969.000] TO BUS 324913 [2MT VERNON 69.000] CKT 1
OPEN LINE FROM BUS 324913 [2MT VERNON 69.000] TO BUS 324087 [2MT VERN SO 69.000] CKT 1
BB-1355 | OPEN LINE FROM BUS 324597 [2KY ST HOSP 69.000] TO BUS 324764 [2WEST CLIFF 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.35901 | 19.1595 | 1 | 4.35
OPEN LINE FROM BUS 324597 [2KY ST HOSP 69.000] TO BUS 324840 [2DANVILLE E 69.000] CKT 1
BB-1354 | OPEN LINE FROM BUS 324494 [2DANVILLE 1 69.000] TO BUS 324840 [2DANVILLE E 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.32454 | 19.6672 | 3 | 31.41
OPEN LINE FROM BUS 324494 [2DANVILLE 1 69.000] TO BUS 324450 [2BOYLE CO 69.000] CKT 1
OPEN LINE FROM BUS 324840 [2DANVILLE E 69.000] TO BUS 324597 [2KY ST HOSP 69.000] CKT 1
OPEN LINE FROM BUS 324597 [2KY ST HOSP 69.000] TO BUS 324764 [2WEST CLIFF 69.000] CKT 1
BB-1270 | OPEN LINE FROM BUS 324665 [2OHIO FALL 169.000] TO BUS 324234 [1OHIO FALL 114.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.46281 | 24.0893
OPEN LINE FROM BUS 324665 [2OHIO FALL 169.000] TO BUS 324462 [2CANAL 69.000] CKT 1
BB-1271 | OPEN LINE FROM BUS 324666 [2OHIO FALL 269.000] TO BUS 324235 [1OHIO FALL 214.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.46276 | 24.425
OPEN LINE FROM BUS 324666 [2OHIO FALL 269.000] TO BUS 324462 [2CANAL 69.000] CKT 1
BB-1275 | OPEN LINE FROM BUS 324740 [2SOUTH PARK 69.000] TO BUS 324788 [2BROOKS EK T69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.15849 | 11.1197 | 1 | 17.61
OPEN LINE FROM BUS 324740 [2SOUTH PARK 69.000] TO BUS 325024 [2ASHBOT SPRK69.000] CKT 1
PRIN-KYD-PAD | OPEN LINE FROM BUS 324512 [2EDDYV PR TP69.000] TO BUS 324693 [2PRINCETON 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.40558 | 20.591 | 2 | 27.29
OPEN LINE FROM BUS 324512 [2EDDYV PR TP69.000] TO BUS 362916 [2KY DAM 69.000] CKT 1
OPEN LINE FROM BUS 324512 [2EDDYV PR TP69.000] TO BUS 324067 [2EDDYV PRIS 69.000] CKT 1
OPEN LINE FROM BUS 362916 [2KY DAM 69.000] TO BUS 362116 [2KY HYDRO 69.000] CKT Z1
OPEN LINE FROM BUS 362116 [2KY HYDRO 69.000] TO BUS 360127 [5KENTUCKY HP161.00] TO BUS 364456 [1KY HYDRO H113.800] CKT 1
OPEN LINE FROM BUS 362116 [2KY HYDRO 69.000] TO BUS 324712 [2SO PADUCAH 69.000] CKT 1
B-69-46 | OPEN BRANCH FROM BUS 324167 [5PINEVILLE 2161.00] TO BUS 324686 [2PINEVILLE 69.000] CKT 2 | TRUE | Met convergence tolerances | 0 | 0.46273 | 19.9843
OPEN BRANCH FROM BUS 324686 [2PINEVILLE 69.000] TO BUS 324593 [2KU PARK 69.000] CKT 1
P1-1000 | OPEN LINE FROM BUS 324695 [2PARKER SEAL69.000] TO BUS 324749 [2SYLVANIA 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.1915 | 11.9793 | 2 | 16.63
OPEN LINE FROM BUS 324695 [2PARKER SEAL69.000] TO BUS 324783 [2WINCHSTR KU69.000] CKT 1
OPEN LINE FROM BUS 324749 [2SYLVANIA 69.000] TO BUS 324472 [2CLARK CO 69.000] CKT 1
P1-1001 | OPEN LINE FROM BUS 324648 [2MORTONS GAP69.000] TO BUS 324664 [2OAK HILL KU69.000] CKT 1 | TRUE | Met convergence tolerances | 9 | 0.14177 | 8.4023 | 5 | 12.07
OPEN LINE FROM BUS 324648 [2MORTONS GAP69.000] TO BUS 324769 [2WALKER KU 69.000] CKT 1
B-69-25 | OPEN LINE FROM BUS 324141 [5ELIHU 161.00] TO BUS 324514 [2ELIHU 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.76508 | 31.1681
OPEN LINE FROM BUS 324141 [5ELIHU 161.00] TO BUS 324514 [2ELIHU 69.000] CKT 2
OPEN LINE FROM BUS 324141 [5ELIHU 161.00] TO BUS 342718 [5COOPER2 161.00] CKT 1
OPEN LINE FROM BUS 324141 [5ELIHU 161.00] TO BUS 324130 [5ALCALDE 161.00] CKT 1
BB-1164 | OPEN LINE FROM BUS 324306 [4SHADRACK 138.00] TO BUS 324250 [4E FRANKFORT138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.64921 | 25.9891 | 2 | 6.75
OPEN LINE FROM BUS 324306 [4SHADRACK 138.00] TO BUS 324274 [4LOCKPORT 138.00] CKT 1
OPEN LINE FROM BUS 324274 [4LOCKPORT 138.00] TO BUS 324227 [4CARROLLTON 138.00] CKT 1
BB-1097 | OPEN LINE FROM BUS 326512 [4AIRGAS 138.00] TO BUS 324227 [4CARROLLTON 138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.84204 | 33.763 | 1 | 8.51
OPEN LINE FROM BUS 326512 [4AIRGAS 138.00] TO BUS 324242 [4DOW CORN W 138.00] CKT 1
B-138-114 | OPEN LINE FROM BUS 324290 [4OWEN CO TAP138.00] TO BUS 324305 [4SCOTT CO 138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14284 | 7.3017
OPEN LINE FROM BUS 324290 [4OWEN CO TAP138.00] TO BUS 342008 [4OWEN CO 138.00] CKT 1
OPEN LINE FROM BUS 324290 [4OWEN CO TAP138.00] TO BUS 324253 [4GHENT 138.00] CKT 1
B-138-119 | OPEN LINE FROM BUS 324307 [4SHARKEY TAP138.00] TO BUS 326556 [4N SHARKEY T138.00] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.55448 | 42.4518 | 2 | 9.699
OPEN LINE FROM BUS 324307 [4SHARKEY TAP138.00] TO BUS 324245 [4FARMERS TAP138.00] CKT 1
OPEN LINE FROM BUS 324307 [4SHARKEY TAP138.00] TO BUS 324302 [4RODBURN 138.00] CKT 1
OPEN LINE FROM BUS 324245 [4FARMERS TAP138.00] TO BUS 324246 [4FARMERS 138.00] CKT 1
OPEN LINE FROM BUS 324245 [4FARMERS TAP138.00] TO BUS 324310 [4SPENCER RD 138.00] CKT 1
OPEN LINE FROM BUS 324246 [4FARMERS 138.00] TO BUS 324528 [2FARMERS 69.000] CKT 1
OPEN LINE FROM BUS 326532 [4SHARKEY 138.00] TO BUS 326556 [4N SHARKEY T138.00] CKT 1
B-138-113 | OPEN LINE FROM BUS 324323 [4WEDONIA 138.00] TO BUS 324251 [4FLEMNB KU T138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.93469 | 31.1185 | 2 | 8.4
OPEN LINE FROM BUS 324323 [4WEDONIA 138.00] TO BUS 324267 [4KENTON 138.00] CKT 1
OPEN LINE FROM BUS 324251 [4FLEMNB KU T138.00] TO BUS 324254 [4GODDARD KU 138.00] CKT 1
OPEN LINE FROM BUS 324251 [4FLEMNB KU T138.00] TO BUS 324193 [4FLEMINGB KU138.00] CKT 1
OPEN LINE FROM BUS 324254 [4GODDARD KU 138.00] TO BUS 324302 [4RODBURN 138.00] CKT 1
B-138-118 | OPEN LINE FROM BUS 324225 [4CARNTOWN TP138.00] TO BUS 324226 [4CARNTOWN 138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.36854 | 17.9904 | 1 | 3.23
OPEN LINE FROM BUS 324225 [4CARNTOWN TP138.00] TO BUS 324267 [4KENTON 138.00] CKT 1
OPEN LINE FROM BUS 324225 [4CARNTOWN TP138.00] TO BUS 324221 [4BUTLER 138.00] CKT 1
OPEN LINE FROM BUS 324221 [4BUTLER 138.00] TO BUS 324211 [4BLACKWELL 138.00] CKT 1
BB-1179 | OPEN LINE FROM BUS 324287 [4NAS TAP 138.00] TO BUS 324240 [4DAY-WALT TP138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.24076 | 16.6697 | 1 | 3.5
OPEN LINE FROM BUS 324287 [4NAS TAP 138.00] TO BUS 324253 [4GHENT 138.00] CKT 1
OPEN LINE FROM BUS 324287 [4NAS TAP 138.00] TO BUS 324286 [4NAS 138.00] CKT 1
OPEN LINE FROM BUS 324240 [4DAY-WALT TP138.00] TO BUS 324242 [4DOW CORN W 138.00] CKT 1
OPEN LINE FROM BUS 324240 [4DAY-WALT TP138.00] TO BUS 324192 [4DAYTON-WALT138.00] CKT 1
BB-1192 | OPEN LINE FROM BUS 324283 [4MIDWAY 138.00] TO BUS 324320 [4W LEXINGTON138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.58592 | 24.935 | 1 | 6.61
OPEN LINE FROM BUS 324283 [4MIDWAY 138.00] TO BUS 324831 [4WHITE SULPH138.00] CKT 1
BB-1201 | OPEN LINE FROM BUS 326548 [4IBM NORTH 138.00] TO BUS 324264 [4IBM NORTHTP138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.27609 | 16.8866 | 1 | 2.67
OPEN LINE FROM BUS 324264 [4IBM NORTHTP138.00] TO BUS 324275 [4LOUDON AVE 138.00] CKT 1
OPEN LINE FROM BUS 324264 [4IBM NORTHTP138.00] TO BUS 324258 [4HAEFLING 138.00] CKT 1
BB-1203 | OPEN LINE FROM BUS 324317 [4VILEY ROAD 138.00] TO BUS 325101 [4W LEX R2 138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.2248 | 14.5115 | 1 | 24.27
OPEN LINE FROM BUS 324317 [4VILEY ROAD 138.00] TO BUS 324258 [4HAEFLING 138.00] CKT 1
BB-1240 | OPEN LINE FROM BUS 326559 [4BGAD TAP 138.00] TO BUS 326560 [4BG ARMY DEP138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.33523 | 18.4696 | 1 | 4.8
OPEN LINE FROM BUS 326559 [4BGAD TAP 138.00] TO BUS 324273 [4LAKE REBA 138.00] CKT Z1
OPEN LINE FROM BUS 326559 [4BGAD TAP 138.00] TO BUS 324276 [4LAKE REBA T138.00] CKT 1
OPEN LINE FROM BUS 324273 [4LAKE REBA 138.00] TO BUS 324612 [2LAKE REBA 69.000] CKT 1
B-138-122 | OPEN LINE FROM BUS 324296 [4PISGAH 138.00] TO BUS 324320 [4W LEXINGTON138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.56168 | 22.9195
OPEN LINE FROM BUS 324296 [4PISGAH 138.00] TO BUS 324687 [2PISGAH 69.000] CKT 1
OPEN LINE FROM BUS 324296 [4PISGAH 138.00] TO BUS 325857 [4BROWN N TIE138.00] CKT 1
BB-1143 | OPEN LINE FROM BUS 324230 [4CLAYS MILL 138.00] TO BUS 324262 [4HIGBY MILL 138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.17628 | 12.0642 | 1 | 19.88
OPEN LINE FROM BUS 324230 [4CLAYS MILL 138.00] TO BUS 325957 [4BROWN N 1 138.00] CKT 1
BB-1049 | OPEN LINE FROM BUS 325077 [5COLEMAN TAP161.00] TO BUS 325078 [5PADUCAH PRI161.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.67327 | 39.6751 | 1 | 66.99
OPEN LINE FROM BUS 325077 [5COLEMAN TAP161.00] TO BUS 324145 [5GRAHAMVILLE161.00] CKT 1
OPEN LINE FROM BUS 325077 [5COLEMAN TAP161.00] TO BUS 325075 [5KMPA COLEMN161.00] CKT Z1
B-138-111 | OPEN LINE FROM BUS 324239 [4DANVILE N T138.00] TO BUS 325121 [4LOGAN TP 138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.48497 | 20.5586
OPEN LINE FROM BUS 324239 [4DANVILE N T138.00] TO BUS 324217 [4BROWN PLANT138.00] CKT 1
OPEN LINE FROM BUS 324239 [4DANVILE N T138.00] TO BUS 324238 [4DANVILLE N 138.00] CKT 1
B-161-125 | OPEN LINE FROM BUS 324132 [5ARTEMUS TAP161.00] TO BUS 324133 [5ARTEMUS 161.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.44934 | 19.6714
OPEN LINE FROM BUS 324132 [5ARTEMUS TAP161.00] TO BUS 324143 [5FARLEY 161.00] CKT 1
OPEN LINE FROM BUS 324132 [5ARTEMUS TAP161.00] TO BUS 324156 [5PINEVILE SW161.00] CKT 1
OPEN LINE FROM BUS 324133 [5ARTEMUS 161.00] TO BUS 324417 [2ARTEMUS 69.000] CKT 1
B-138-21 | OPEN LINE FROM BUS 324288 [4NELSON CO 138.00] TO BUS 341944 [2NELSON CO 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.51028 | 21.1966
OPEN LINE FROM BUS 324288 [4NELSON CO 138.00] TO BUS 324207 [4BARDSTOWN 138.00] CKT 1
OPEN LINE FROM BUS 324288 [4NELSON CO 138.00] TO BUS 324244 [4ETOWN 138.00] CKT 1
BB-1133 | OPEN LINE FROM BUS 324270 [4LEBANON WES138.00] TO BUS 324271 [4LEBANON 138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.86724 | 33.6962 | 1 | 6.91
OPEN LINE FROM BUS 324270 [4LEBANON WES138.00] TO BUS 324213 [4BONNIEVILLE138.00] CKT 1
B-161-126 | OPEN LINE FROM BUS 324149 [5IMBODEN 161.00] TO BUS 324157 [5POCKET N 161.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 5.476
OPEN LINE FROM BUS 324149 [5IMBODEN 161.00] TO BUS 324583 [2IMBODEN 69.000] CKT 1
OPEN LINE FROM BUS 324149 [5IMBODEN 161.00] TO BUS 324139 [5DORCHESTER 161.00] CKT 1
BB-1063 | OPEN LINE FROM BUS 324147 [5HOWARDS BR 161.00] TO BUS 324155 [5PINEVILLE 1161.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 2.0236 | 1 | 0.21
OPEN LINE FROM BUS 324147 [5HOWARDS BR 161.00] TO BUS 324146 [5HARLAN WYE 161.00] CKT 1
B-161-24 | OPEN LINE FROM BUS 324148 [5WOOTON TAP 161.00] TO BUS 243668 [05WOOTON 161.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.33805 | 17.9815
OPEN LINE FROM BUS 324148 [5WOOTON TAP 161.00] TO BUS 324131 [5ARNOLD 161.00] CKT 1
OPEN LINE FROM BUS 324148 [5WOOTON TAP 161.00] TO BUS 324138 [5DELVINTA 161.00] CKT 1
B-161-23 | OPEN LINE FROM BUS 342697 [5BEATTYV J 161.00] TO BUS 342780 [5MILL CRK T 161.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.45452 | 19.0493
OPEN LINE FROM BUS 342697 [5BEATTYV J 161.00] TO BUS 324138 [5DELVINTA 161.00] CKT 1
OPEN LINE FROM BUS 342697 [5BEATTYV J 161.00] TO BUS 324430 [2BEATTYVI KU69.000] CKT 1
B-161-124 | OPEN LINE FROM BUS 324165 [5W IRVINE T 161.00] TO BUS 324138 [5DELVINTA 161.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 5.269
OPEN LINE FROM BUS 324165 [5W IRVINE T 161.00] TO BUS 324152 [5LAKE REBA T161.00] CKT 1
OPEN LINE FROM BUS 324165 [5W IRVINE T 161.00] TO BUS 324163 [5WEST IRVINE161.00] CKT 1
OPEN LINE FROM BUS 324163 [5WEST IRVINE161.00] TO BUS 324767 [2WEST IRVINE69.000] CKT 1
BB-1509 | OPEN LINE FROM BUS 342736 [5GREEN HAL T161.00] TO BUS 342739 [5GREEN HALL 161.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.22031 | 15.9025 | 1 | 2.6482
OPEN LINE FROM BUS 342736 [5GREEN HAL T161.00] TO BUS 342820 [5TYNER 161.00] CKT 1
OPEN LINE FROM BUS 342736 [5GREEN HAL T161.00] TO BUS 324138 [5DELVINTA 161.00] CKT 1
B-138-112 | OPEN LINE FROM BUS 324247 [4FAWKES TAP 138.00] TO BUS 324248 [4FAWKES KU 138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 1.4737
OPEN LINE FROM BUS 324247 [4FAWKES TAP 138.00] TO BUS 324276 [4LAKE REBA T138.00] CKT 1
OPEN LINE FROM BUS 324247 [4FAWKES TAP 138.00] TO BUS 342577 [4FAWKES EK 138.00] CKT 1
BB-1239 | OPEN LINE FROM BUS 342688 [4UNION CTY T138.00] TO BUS 324276 [4LAKE REBA T138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 16.3172 | 1 | 6.4748
OPEN LINE FROM BUS 342688 [4UNION CTY T138.00] TO BUS 342607 [4JK SMITH 138.00] CKT 1
OPEN LINE FROM BUS 342688 [4UNION CTY T138.00] TO BUS 342685 [4UNION CITY 138.00] CKT 1
BB-1216 | OPEN LINE FROM BUS 324047 [4BLACKBRANCH138.00] TO BUS 325055 [4RHUDES TP 138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.95397 | 42.9526 | 1 | 13.06
OPEN LINE FROM BUS 324047 [4BLACKBRANCH138.00] TO BUS 342568 [4CENT HARDIN138.00] CKT 1
BB-1019 | OPEN LINE FROM BUS 324115 [7W FRANKFORT345.00] TO BUS 324319 [4W FRANKFORT138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.17903 | 9.1307
OPEN LINE FROM BUS 324115 [7W FRANKFORT345.00] TO BUS 324105 [7GHENT 345.00] CKT 1
B-138-97 | OPEN LINE FROM BUS 342565 [4BOONESBOR T138.00] TO BUS 342574 [4DALE 138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.51221 | 21.8176 | 1 | 1.593
OPEN LINE FROM BUS 342565 [4BOONESBOR T138.00] TO BUS 325925 [4BOONSBORO N138.00] CKT 1
OPEN LINE FROM BUS 342565 [4BOONESBOR T138.00] TO BUS 342556 [4BECKNERV T 138.00] CKT 1
OPEN LINE FROM BUS 325925 [4BOONSBORO N138.00] TO BUS 324449 [2BOONSBORO N69.000] CKT 1
OPEN LINE FROM BUS 342556 [4BECKNERV T 138.00] TO BUS 342541 [4AVON 138.00] CKT 1
OPEN LINE FROM BUS 342556 [4BECKNERV T 138.00] TO BUS 342553 [4BECKNERV 138.00] CKT 1
B-161-108 | OPEN LINE FROM BUS 324160 [5RIVER QN T 161.00] TO BUS 324140 [5EARLINGTN N161.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14177 | 1.7263
OPEN LINE FROM BUS 324160 [5RIVER QN T 161.00] TO BUS 324144 [5GREEN RIVER161.00] CKT 1
OPEN LINE FROM BUS 324160 [5RIVER QN T 161.00] TO BUS 324159 [5RIVER QUEEN161.00] CKT 1
OPEN LINE FROM BUS 324159 [5RIVER QUEEN161.00] TO BUS 324702 [2RIVER QUEEN69.000] CKT 1
BB-1057 | OPEN LINE FROM BUS 324164 [5WALKER 161.00] TO BUS 324769 [2WALKER KU 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 1.852
OPEN LINE FROM BUS 324164 [5WALKER 161.00] TO BUS 324140 [5EARLINGTN N161.00] CKT 1
B-161-106 | OPEN LINE FROM BUS 324135 [5CORYDON TAP161.00] TO BUS 324136 [5CORYDON 161.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 2.1076
OPEN LINE FROM BUS 324135 [5CORYDON TAP161.00] TO BUS 324144 [5GREEN RIVER161.00] CKT 1
OPEN LINE FROM BUS 324135 [5CORYDON TAP161.00] TO BUS 324153 [5MORGANFIELD161.00] CKT 1
OPEN LINE FROM BUS 324136 [5CORYDON 161.00] TO BUS 324484 [2CORYDON 69.000] CKT 1
B-161-128 | OPEN LINE FROM BUS 342817 [5TAYLOR CO J161.00] TO BUS 325921 [5TAYLOR CO 161.00] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.51501 | 34.5576 | 3 | 49.718
OPEN LINE FROM BUS 342817 [5TAYLOR CO J161.00] TO BUS 342733 [5GREEN CO 161.00] CKT 1
OPEN LINE FROM BUS 342817 [5TAYLOR CO J161.00] TO BUS 342805 [5SALOMA T 161.00] CKT 1
OPEN LINE FROM BUS 325921 [5TAYLOR CO 161.00] TO BUS 324751 [2TAYLOR CO 69.000] CKT 1
OPEN LINE FROM BUS 342805 [5SALOMA T 161.00] TO BUS 342775 [5MARION IP T161.00] CKT 1
OPEN LINE FROM BUS 342805 [5SALOMA T 161.00] TO BUS 342802 [5SALOMA 161.00] CKT 1
OPEN LINE FROM BUS 342775 [5MARION IP T161.00] TO BUS 342797 [5S MARION IT161.00] CKT 1
OPEN LINE FROM BUS 342775 [5MARION IP T161.00] TO BUS 342769 [5MARION CO 161.00] CKT 1
OPEN LINE FROM BUS 342772 [5MARION IP 161.00] TO BUS 342797 [5S MARION IT161.00] CKT 1
B-69-18 | OPEN LINE FROM BUS 324271 [4LEBANON 138.00] TO BUS 324606 [2LEBANON 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.75447 | 29.6922
OPEN LINE FROM BUS 324271 [4LEBANON 138.00] TO BUS 324606 [2LEBANON 69.000] CKT 2
OPEN LINE FROM BUS 324271 [4LEBANON 138.00] TO BUS 325121 [4LOGAN TP 138.00] CKT 1
OPEN LINE FROM BUS 324271 [4LEBANON 138.00] TO BUS 342770 [4MARION CO 138.00] CKT 1
OPEN LINE FROM BUS 324271 [4LEBANON 138.00] TO BUS 324270 [4LEBANON WES138.00] CKT 1
B-69-19 | OPEN LINE FROM BUS 324213 [4BONNIEVILLE138.00] TO BUS 324270 [4LEBANON WES138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.30337 | 17.5099
OPEN LINE FROM BUS 324213 [4BONNIEVILLE138.00] TO BUS 324800 [4MERE TVA 138.00] CKT 1
OPEN LINE FROM BUS 324213 [4BONNIEVILLE138.00] TO BUS 324447 [2BONNIE KU 69.000] CKT 1
OPEN LINE FROM BUS 324213 [4BONNIEVILLE138.00] TO BUS 341161 [2BONNIV EK 69.000] CKT 1
B-138-28 | OPEN LINE FROM BUS 324200 [4PLSUR RDG T138.00] TO BUS 324205 [4ASHBOTTOM 138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.36996 | 17.3444
OPEN LINE FROM BUS 324200 [4PLSUR RDG T138.00] TO BUS 324237 [4CANE RUN SW138.00] CKT 1
OPEN LINE FROM BUS 324200 [4PLSUR RDG T138.00] TO BUS 324299 [4PLEASUR RDG138.00] CKT 1
BB-1228 | OPEN LINE FROM BUS 324268 [4KNOB CREEK 138.00] TO BUS 324284 [4MILL CREEK 138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.99209 | 61.5316 | 1 | 15.4897
OPEN LINE FROM BUS 324268 [4KNOB CREEK 138.00] TO BUS 324300 [4POND CREEK 138.00] CKT 1
OPEN LINE FROM BUS 324268 [4KNOB CREEK 138.00] TO BUS 324170 [1KNOB CRK 34.500] CKT 1
OPEN LINE FROM BUS 324300 [4POND CREEK 138.00] TO BUS 324311 [4TIP TOP 138.00] CKT 1
BB-1229 | OPEN LINE FROM BUS 325088 [4MIL CK YARD138.00] TO BUS 324284 [4MILL CREEK 138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.26643 | 16.6379 | 1 | 27.23
OPEN LINE FROM BUS 325088 [4MIL CK YARD138.00] TO BUS 325057 [4KOSMOS CEME138.00] CKT 1
BB-1066 | OPEN LINE FROM BUS 324154 [5PADDYS RUN 161.00] TO BUS 324295 [4PADDYS RUN 138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 9.2959 | 1 | 13.58
OPEN LINE FROM BUS 324154 [5PADDYS RUN 161.00] TO BUS 324150 [5LEBANON JCT161.00] CKT 1
OPEN LINE FROM BUS 324150 [5LEBANON JCT161.00] TO BUS 360334 [5SUMMER SHAD161.00] CKT 1
BB-1026 | OPEN LINE FROM BUS 324110 [7NORTHSIDE 345.00] TO BUS 326569 [7KENZIG ROAD345.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.61513 | 26.0641
OPEN LINE FROM BUS 324110 [7NORTHSIDE 345.00] TO BUS 324289 [4NORTHSIDE 138.00] CKT 1
B-345-475 | OPEN LINE FROM BUS 326001 [7CANE RUN TP345.00] TO BUS 326002 [7CANERN NGCC345.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14177 | 1.536
OPEN LINE FROM BUS 326001 [7CANE RUN TP345.00] TO BUS 324108 [7MILL CREEK 345.00] CKT 1
OPEN LINE FROM BUS 326001 [7CANE RUN TP345.00] TO BUS 324111 [7PADDYS WEST345.00] CKT 1
BB-1139 | OPEN LINE FROM BUS 324215 [4BRIDGPOR HE138.00] TO BUS 324237 [4CANE RUN SW138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.53272 | 25.1616 | 1 | 5.9
OPEN LINE FROM BUS 324215 [4BRIDGPOR HE138.00] TO BUS 324284 [4MILL CREEK 138.00] CKT 1
B-138-130 | OPEN LINE FROM BUS 324228 [4CENTERFIELD138.00] TO BUS 324281 [4MIDDLETOWN 138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.26495 | 16.9057 | 1 | 29.64
OPEN LINE FROM BUS 324228 [4CENTERFIELD138.00] TO BUS 326520 [4TRIMBLE TR9138.00] CKT 1
OPEN LINE FROM BUS 324228 [4CENTERFIELD138.00] TO BUS 324469 [2CENTERFIELD69.000] CKT 1
B-138-12 | OPEN BRANCH FROM BUS 324328 [4PARIS 138.00] TO BUS 324680 [2PARIS KU 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.26149 | 18.649 | 1 | 3.3691
OPEN LINE FROM BUS 342631 [4PARIS T 138.00] TO BUS 324328 [4PARIS 138.00] CKT 1
OPEN LINE FROM BUS 342631 [4PARIS T 138.00] TO BUS 342541 [4AVON 138.00] CKT 1
OPEN LINE FROM BUS 342631 [4PARIS T 138.00] TO BUS 342604 [4JACKSNVIL T138.00] CKT 1
OPEN LINE FROM BUS 342601 [4JACKSNVIL 138.00] TO BUS 342604 [4JACKSNVIL T138.00] CKT 1
OPEN LINE FROM BUS 342604 [4JACKSNVIL T138.00] TO BUS 342640 [4RENAKER 138.00] CKT 1
B-69-13 | OPEN LINE FROM BUS 324229 [4CLARK CO 138.00] TO BUS 324310 [4SPENCER RD 138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.15148 | 2.8154
OPEN LINE FROM BUS 324229 [4CLARK CO 138.00] TO BUS 324472 [2CLARK CO 69.000] CKT 1
OPEN LINE FROM BUS 324229 [4CLARK CO 138.00] TO BUS 324236 [4RICHMND NO 138.00] CKT 1
B-69-15 | OPEN LINE FROM BUS 324203 [4AMERICAN AV138.00] TO BUS 324258 [4HAEFLING 138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14177 | 1.6289
OPEN LINE FROM BUS 324203 [4AMERICAN AV138.00] TO BUS 324301 [4REYNOLDS 138.00] CKT 1
OPEN LINE FROM BUS 324203 [4AMERICAN AV138.00] TO BUS 324409 [2AMERICAN AV69.000] CKT 1
B-69-20 | OPEN LINE FROM BUS 324244 [4ETOWN 138.00] TO BUS 324261 [4HARDIN CO 138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.49709 | 20.6596
OPEN LINE FROM BUS 324244 [4ETOWN 138.00] TO BUS 324288 [4NELSON CO 138.00] CKT 1
OPEN LINE FROM BUS 324244 [4ETOWN 138.00] TO BUS 324519 [2ETOWN KU 69.000] CKT 1
B-69-26 | OPEN LINE FROM BUS 324143 [5FARLEY 161.00] TO BUS 324527 [2FARLEY KU 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.67248 | 26.2576
OPEN LINE FROM BUS 324143 [5FARLEY 161.00] TO BUS 324130 [5ALCALDE 161.00] CKT 1
OPEN LINE FROM BUS 324143 [5FARLEY 161.00] TO BUS 324132 [5ARTEMUS TAP161.00] CKT 1
B-69-29 | OPEN LINE FROM BUS 324243 [4ETHEL 138.00] TO BUS 324518 [2ETHEL 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.19427 | 12.9199 | 1 | 21.25
OPEN LINE FROM BUS 324243 [4ETHEL 138.00] TO BUS 324204 [4APPLIANC PK138.00] CKT 1
OPEN LINE FROM BUS 324243 [4ETHEL 138.00] TO BUS 324214 [4BRECKNRIDGE138.00] CKT 1
B-69-30 | OPEN LINE FROM BUS 324277 [4LYNDON SO 138.00] TO BUS 324281 [4MIDDLETOWN 138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.24532 | 15.6304 | 1 | 26.2
OPEN LINE FROM BUS 324277 [4LYNDON SO 138.00] TO BUS 324622 [2LYNDON SO 69.000] CKT 1
OPEN LINE FROM BUS 324277 [4LYNDON SO 138.00] TO BUS 324208 [4BEARGRASS 138.00] CKT 1
B-69-31 | OPEN LINE FROM BUS 324285 [4MUD LANE 138.00] TO BUS 324292 [4OKOLONA 138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.63379 | 36.3239 | 1 | 62.72
OPEN LINE FROM BUS 324285 [4MUD LANE 138.00] TO BUS 324651 [2MUD LANE 69.000] CKT 1
OPEN LINE FROM BUS 324285 [4MUD LANE 138.00] TO BUS 324212 [4BLUE LICK 138.00] CKT 1
BB-1205 | OPEN LINE FROM BUS 324259 [4HANCOCK 138.00] TO BUS 324278 [4MAGAZINE 138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 8.5841 | 1 | 13.05
OPEN LINE FROM BUS 324259 [4HANCOCK 138.00] TO BUS 324561 [2HANCOCK 69.000] CKT 1
BB-1187 | OPEN LINE FROM BUS 324292 [4OKOLONA 138.00] TO BUS 324249 [4FERN VALLEY138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.26338 | 16.6272 | 1 | 26.56
OPEN LINE FROM BUS 324292 [4OKOLONA 138.00] TO BUS 324285 [4MUD LANE 138.00] CKT 1
BB-1136 | OPEN LINE FROM BUS 324214 [4BRECKNRIDGE138.00] TO BUS 324243 [4ETHEL 138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 2.9459
OPEN LINE FROM BUS 324214 [4BRECKNRIDGE138.00] TO BUS 324263 [4HURSTBORNE 138.00] CKT 1
OPEN LINE FROM BUS 324214 [4BRECKNRIDGE138.00] TO BUS 324451 [2BRECKNRIDGE69.000] CKT 1
BB-1112 | OPEN LINE FROM BUS 324299 [4PLEASUR RDG138.00] TO BUS 324200 [4PLSUR RDG T138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.37787 | 22.4973 | 1 | 37.32
OPEN LINE FROM BUS 324299 [4PLEASUR RDG138.00] TO BUS 324206 [4ASHBY 138.00] CKT 1
BB-1098 | OPEN LINE FROM BUS 324241 [4DIXIE 138.00] TO BUS 324295 [4PADDYS RUN 138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.30168 | 18.5465 | 1 | 30.86
OPEN LINE FROM BUS 324241 [4DIXIE 138.00] TO BUS 324202 [4ALGONQUIN 138.00] CKT 1
BB-1075 | OPEN LINE FROM BUS 324158 [5POCKET 161.00] TO BUS 324689 [2POCKET 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 2.8728
OPEN LINE FROM BUS 324158 [5POCKET 161.00] TO BUS 324157 [5POCKET N 161.00] CKT 1
BB-1062 | OPEN LINE FROM BUS 324166 [5WICKLIFFE 161.00] TO BUS 324779 [2WICKLIFFE 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.46709 | 19.962
OPEN LINE FROM BUS 324166 [5WICKLIFFE 161.00] TO BUS 325069 [5SONG SP TP 161.00] CKT 1
BB-1060 | OPEN LINE FROM BUS 324171 [5GRAHMVILE 1161.00] TO BUS 351003 [5JOPPA TS 161.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.2431 | 18.3647
OPEN LINE FROM BUS 324171 [5GRAHMVILE 1161.00] TO BUS 324145 [5GRAHAMVILLE161.00] CKT 1
BB-1061 | OPEN LINE FROM BUS 324172 [5GRAHMVILE 2161.00] TO BUS 351002 [5JOPPA S 161.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.24228 | 2.2148
OPEN LINE FROM BUS 324172 [5GRAHMVILE 2161.00] TO BUS 324145 [5GRAHAMVILLE161.00] CKT 1
B-69-135 | OPEN LINE FROM BUS 324416 [2ARNOLD 69.000] TO BUS 324433 [2BENHAM 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 5.4711
OPEN LINE FROM BUS 324416 [2ARNOLD 69.000] TO BUS 324490 [2CUMBERLAND 69.000] CKT 1
OPEN LINE FROM BUS 324416 [2ARNOLD 69.000] TO BUS 324131 [5ARNOLD 161.00] CKT 1
B-69-132 | OPEN LINE FROM BUS 324207 [4BARDSTOWN 138.00] TO BUS 324218 [4BROWN CT 138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.52861 | 21.3677
OPEN LINE FROM BUS 324207 [4BARDSTOWN 138.00] TO BUS 324288 [4NELSON CO 138.00] CKT 1
OPEN LINE FROM BUS 324207 [4BARDSTOWN 138.00] TO BUS 324426 [2BARDSTOWN 69.000] CKT 1
B-138-120 | OPEN LINE FROM BUS 324219 [4BROWN T1 138.00] TO BUS 325957 [4BROWN N 1 138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 1.3147
OPEN LINE FROM BUS 324219 [4BROWN T1 138.00] TO BUS 324217 [4BROWN PLANT138.00] CKT 1
OPEN LINE FROM BUS 324219 [4BROWN T1 138.00] TO BUS 324218 [4BROWN CT 138.00] CKT 1
B-138-121 | OPEN LINE FROM BUS 324220 [4BROWN T2 138.00] TO BUS 325956 [4BROWN N 2 138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14177 | 1.3455
OPEN LINE FROM BUS 324220 [4BROWN T2 138.00] TO BUS 324217 [4BROWN PLANT138.00] CKT 1
OPEN LINE FROM BUS 324220 [4BROWN T2 138.00] TO BUS 324218 [4BROWN CT 138.00] CKT 1
B-138-109 | OPEN LINE FROM BUS 324282 [4MIDDLETWN-R138.00] TO BUS 324298 [4PLAINVIEW T138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.63909 | 25.7905
OPEN LINE FROM BUS 324282 [4MIDDLETWN-R138.00] TO BUS 324281 [4MIDDLETOWN 138.00] CKT 1
OPEN LINE FROM BUS 324298 [4PLAINVIEW T138.00] TO BUS 324208 [4BEARGRASS 138.00] CKT 1
OPEN LINE FROM BUS 324298 [4PLAINVIEW T138.00] TO BUS 324297 [4PLAINVIEW 138.00] CKT 1
BB-1226 | OPEN LINE FROM BUS 325042 [4JEFERSONTWN138.00] TO BUS 324281 [4MIDDLETOWN 138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.27658 | 17.3177 | 1 | 30.39
OPEN LINE FROM BUS 325042 [4JEFERSONTWN138.00] TO BUS 324322 [4WATTERSON 138.00] CKT 1
BB-1001 | OPEN LINE FROM BUS 324072 [8PINEVILLE 500.00] TO BUS 324073 [8POCKET N 500.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14177 | 2.7439
OPEN LINE FROM BUS 324072 [8PINEVILLE 500.00] TO BUS 324112 [7PINEVILLE 345.00] CKT 1
B-345-100 | OPEN LINE FROM BUS 324100 [7ALCALDE 345.00] TO BUS 324102 [7BROWN NORTH345.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.64215 | 26.7016
OPEN LINE FROM BUS 324100 [7ALCALDE 345.00] TO BUS 324112 [7PINEVILLE 345.00] CKT 1
OPEN LINE FROM BUS 324100 [7ALCALDE 345.00] TO BUS 324130 [5ALCALDE 161.00] CKT 1
B-161-107 | OPEN LINE FROM BUS 324137 [5CRITTENDEN 161.00] TO BUS 324151 [5LIVNGSTN CO161.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14177 | 2.335
OPEN LINE FROM BUS 324137 [5CRITTENDEN 161.00] TO BUS 324153 [5MORGANFIELD161.00] CKT 1
OPEN LINE FROM BUS 324137 [5CRITTENDEN 161.00] TO BUS 324486 [2CRITTENDEN 69.000] CKT 1
B-138-110 | OPEN LINE FROM BUS 324265 [4JEFFRSONV T138.00] TO BUS 324289 [4NORTHSIDE 138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 2.7822
OPEN LINE FROM BUS 324265 [4JEFFRSONV T138.00] TO BUS 249763 [08JEFF 138.00] CKT 1
OPEN LINE FROM BUS 324265 [4JEFFRSONV T138.00] TO BUS 324208 [4BEARGRASS 138.00] CKT 1
B-138-117 | OPEN LINE FROM BUS 324210 [4BAKER LANE 138.00] TO BUS 324262 [4HIGBY MILL 138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.61396 | 24.9561
OPEN LINE FROM BUS 324210 [4BAKER LANE 138.00] TO BUS 324334 [4BROWN N 2-R138.00] CKT 1
OPEN LINE FROM BUS 324210 [4BAKER LANE 138.00] TO BUS 342547 [4BAKER LN 138.00] CKT 1
OPEN LINE FROM BUS 324334 [4BROWN N 2-R138.00] TO BUS 325956 [4BROWN N 2 138.00] CKT 1
B-161-84 | OPEN LINE FROM BUS 340624 [5BRTAP 161.00] TO BUS 324173 [5MATANZAS 161.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 3.2346
OPEN LINE FROM BUS 340624 [5BRTAP 161.00] TO BUS 340616 [5N.HARD 161.00] CKT 1
B-138-116 | OPEN LINE FROM BUS 248009 [06CLIFTY 138.00] TO BUS 324227 [4CARROLLTON 138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.50901 | 19.6131
OPEN LINE FROM BUS 248009 [06CLIFTY 138.00] TO BUS 325013 [4CLIFTY TAP1138.00] CKT 1
OPEN LINE FROM BUS 248009 [06CLIFTY 138.00] TO BUS 325014 [4CLIFTY TAP2138.00] CKT 1
OPEN LINE FROM BUS 248009 [06CLIFTY 138.00] TO BUS 248008 [06CLIFTX 138.00] CKT SR
B-345-101 | OPEN BRANCH FROM BUS 324107 [7MIDDLETOWN 345.00] TO BUS 324101 [7BLUE LICK 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.6916 | 27.4239
OPEN BRANCH FROM BUS 324101 [7BLUE LICK 345.00] TO BUS 324212 [4BLUE LICK 138.00] CKT 1
B-345-102 | OPEN BRANCH FROM BUS 324108 [7MILL CREEK 345.00] TO BUS 324101 [7BLUE LICK 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14934 | 7.8212
OPEN BRANCH FROM BUS 324101 [7BLUE LICK 345.00] TO BUS 324134 [5BLUE LICK 161.00] CKT 1
B-69-133 | OPEN BRANCH FROM BUS 324112 [7PINEVILLE 345.00] TO BUS 324167 [5PINEVILLE 2161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.57526 | 21.5736
OPEN BRANCH FROM BUS 324167 [5PINEVILLE 2161.00] TO BUS 324686 [2PINEVILLE 69.000] CKT 2
BB-1074 | OPEN LINE FROM BUS 360452 [5PINEVILL KY161.00] TO BUS 360633 [5SWEET GUM 161.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.74587 | 29.1185
OPEN LINE FROM BUS 360452 [5PINEVILL KY161.00] TO BUS 324156 [5PINEVILE SW161.00] CKT 1
OPEN LINE FROM BUS 360452 [5PINEVILL KY161.00] TO BUS 243667 [05STINNE 161.00] CKT 1
BB-1132 | OPEN LINE FROM BUS 324333 [4BROWN N 1-R138.00] TO BUS 325957 [4BROWN N 1 138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.50331 | 21.1386
OPEN LINE FROM BUS 324333 [4BROWN N 1-R138.00] TO BUS 324262 [4HIGBY MILL 138.00] CKT 1
BB-1218 | OPEN BRANCH FROM BUS 340616 [5N.HARD 161.00] TO BUS 340615 [4N.HARD 138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 1.6776
OPEN BRANCH FROM BUS 340615 [4N.HARD 138.00] TO BUS 324231 [4CLOVERPORT 138.00] CKT 1
OPEN BRANCH FROM BUS 340615 [4N.HARD 138.00] TO BUS 324260 [4HARDINSBURG138.00] CKT 1
BB-2021 | OPEN LINE FROM BUS 249532 [08TRIMBL 345.00] TO BUS 324105 [7GHENT 345.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.66435 | 31.3801
OPEN LINE FROM BUS 249532 [08TRIMBL 345.00] TO BUS 324114 [7TRIMBLE CO 345.00] CKT 1
BB-1245B | OPEN LINE FROM BUS 249789 [08LOUCMJ 138.00] TO BUS 249850 [08SPEED 138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 7.5888 | 1 | 10.049
OPEN LINE FROM BUS 249789 [08LOUCMJ 138.00] TO BUS 324289 [4NORTHSIDE 138.00] CKT 1
OPEN LINE FROM BUS 249789 [08LOUCMJ 138.00] TO BUS 249788 [08LOUCEM 138.00] CKT 1
B-69-35 | OPEN BRANCH FROM BUS 324322 [4WATTERSON 138.00] TO BUS 324771 [2WATTERSON 69.000] CKT 2 | TRUE | Met convergence tolerances | 0 | 0.47879 | 21.2839
OPEN BRANCH FROM BUS 324322 [4WATTERSON 138.00] TO BUS 325042 [4JEFERSONTWN138.00] CKT 1
B-69-32 | OPEN BRANCH FROM BUS 324249 [4FERN VALLEY138.00] TO BUS 324532 [2FERN VALLEY69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.4772
OPEN BRANCH FROM BUS 324249 [4FERN VALLEY138.00] TO BUS 324257 [4GRADE LANE 138.00] CKT 1
B-69-33 | OPEN BRANCH FROM BUS 324249 [4FERN VALLEY138.00] TO BUS 324532 [2FERN VALLEY69.000] CKT 2 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6965
OPEN BRANCH FROM BUS 324249 [4FERN VALLEY138.00] TO BUS 324292 [4OKOLONA 138.00] CKT 1
OPEN BRANCH FROM BUS 324249 [4FERN VALLEY138.00] TO BUS 324322 [4WATTERSON 138.00] CKT 1
P1-1002 | OPEN BRANCH FROM BUS 324105 [7GHENT 345.00] TO BUS 324116 [7W LEXINGTON345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.29141 | 15.4695
OPEN BRANCH FROM BUS 324116 [7W LEXINGTON345.00] TO BUS 324320 [4W LEXINGTON138.00] CKT 1
P1-2-1004 | OPEN LINE FROM BUS 326565 [4INTRNTL TAP138.00] TO BUS 324237 [4CANE RUN SW138.00] CKT 23 | TRUE | Met convergence tolerances | 1 | 0.29391 | 18.1943 | 1 | 30.17
OPEN LINE FROM BUS 326565 [4INTRNTL TAP138.00] TO BUS 325044 [4INTRNTL 138.00] CKT 1
OPEN LINE FROM BUS 326565 [4INTRNTL TAP138.00] TO BUS 325096 [4CANERN NGCC138.00] CKT 23
P1-2-1005 | OPEN LINE FROM BUS 326574 [4CR11 TAP 138.00] TO BUS 324232 [4CANE RN 11A138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.46018 | 22.4391 | 1 | 5.4
OPEN LINE FROM BUS 326574 [4CR11 TAP 138.00] TO BUS 324237 [4CANE RUN SW138.00] CKT 21
OPEN LINE FROM BUS 326574 [4CR11 TAP 138.00] TO BUS 325096 [4CANERN NGCC138.00] CKT 21
OPEN LINE FROM BUS 324232 [4CANE RN 11A138.00] TO BUS 324399 [1CANERN11 14.000] CKT 1
SINGLE OPN LIN 1986 242691-243088(1) | OPEN LINE FROM BUS 242691 [05KENOVA 138.00] TO BUS 243088 [05S.POINT1 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.1494
SINGLE OPN LIN 1987 242927-242938(1) | OPEN LINE FROM BUS 242927 [05MARQUI 765.00] TO BUS 242938 [05MARQUI 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.16871 | 8.9586
SINGLE OPN LIN 1988 242938-243034(2) | OPEN LINE FROM BUS 242938 [05MARQUI 345.00] TO BUS 243034 [05MARQUI 138.00] CKT 2 | TRUE | Met convergence tolerances | 0 | 0.15647 | 5.0849
SINGLE OPN LIN 1989 242938-243034(3) | OPEN LINE FROM BUS 242938 [05MARQUI 345.00] TO BUS 243034 [05MARQUI 138.00] CKT 3 | TRUE | Met convergence tolerances | 0 | 0.15759 | 5.0559
SINGLE OPN LIN 1990 242938-246888(1) | OPEN LINE FROM BUS 242938 [05MARQUI 345.00] TO BUS 246888 [05BIERSR 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.3878 | 21.6008
SINGLE OPN LIN 1991 242982-243047(1) | OPEN LINE FROM BUS 242982 [05CENPOR 138.00] TO BUS 243047 [05N PORT 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.45
SINGLE OPN LIN 1992 242988-242992(1) | OPEN LINE FROM BUS 242988 [05DOGWOO 138.00] TO BUS 242992 [05E WHEE 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.16746 | 2.8099
SINGLE OPN LIN 1993 242988-243042(1) | OPEN LINE FROM BUS 242988 [05DOGWOO 138.00] TO BUS 243042 [05MILLBR PK1138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.21295 | 3.2706
SINGLE OPN LIN 1994 243013-243069(1) | OPEN LINE FROM BUS 243013 [05GAVIN1 138.00] TO BUS 243069 [05FIREBR 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.3709
SINGLE OPN LIN 1995 243019-243102(1) | OPEN LINE FROM BUS 243019 [05HILLSB 138.00] TO BUS 243102 [05SINK SP8SS138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.19265 | 6.1295
SINGLE OPN LIN 1996 243042-243047(1) | OPEN LINE FROM BUS 243042 [05MILLBR PK1138.00] TO BUS 243047 [05N PORT 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.7779
SINGLE OPN LIN 1997 243042-243069(1) | OPEN LINE FROM BUS 243042 [05MILLBR PK1138.00] TO BUS 243069 [05FIREBR 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.1502
SINGLE OPN LIN 1998 243042-243173(5) | OPEN LINE FROM BUS 243042 [05MILLBR PK1138.00] TO BUS 243173 [05MILLBRK 69.000] CKT 5 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.5216
SINGLE OPN LIN 1999 243047-243087(1) | OPEN LINE FROM BUS 243047 [05N PORT 138.00] TO BUS 243087 [05S LUCA 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14378 | 2.4708
SINGLE OPN LIN 2000 243047-243819(1) | OPEN LINE FROM BUS 243047 [05N PORT 138.00] TO BUS 243819 [05N PORTSM 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 5.9016
SINGLE OPN LIN 2001 243069-246782(1) | OPEN LINE FROM BUS 243069 [05FIREBR 138.00] TO BUS 246782 [05FIREBRCK 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.29113 | 13.0245
SINGLE OPN LIN 2002 243088-243184(2) | OPEN LINE FROM BUS 243088 [05S.POINT1 138.00] TO BUS 243184 [05S POINT 34.500] CKT 2 | TRUE | Met convergence tolerances | 0 | 0.76757 | 8.2076
SINGLE OPN LIN 2003 243167-243171(1) | OPEN LINE FROM BUS 243167 [05FRANKLIN 69.000] TO BUS 243171 [05HAYPRTRDSS69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 5.6878
SINGLE OPN LIN 2004 243167-243178(1) | OPEN LINE FROM BUS 243167 [05FRANKLIN 69.000] TO BUS 243178 [05GINAT C SS69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.3511
SINGLE OPN LIN 2005 243167-243725(1) | OPEN LINE FROM BUS 243167 [05FRANKLIN 69.000] TO BUS 243725 [05GRAYSB 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 3.5712
SINGLE OPN LIN 2006 243171-243183(1) | OPEN LINE FROM BUS 243171 [05HAYPRTRDSS69.000] TO BUS 243183 [05WHEELRBR 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.0266
SINGLE OPN LIN 2007 243173-243181(1) | OPEN LINE FROM BUS 243173 [05MILLBRK 69.000] TO BUS 243181 [05SCIOTOVI 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.5431
SINGLE OPN LIN 2008 243173-243597(1) | OPEN LINE FROM BUS 243173 [05MILLBRK 69.000] TO BUS 243597 [05ASHLEY 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.7854
SINGLE OPN LIN 2009 243173-246916(1) | OPEN LINE FROM BUS 243173 [05MILLBRK 69.000] TO BUS 246916 [05CORNRSTN 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.3589
SINGLE OPN LIN 2010 243173-246917(1) | OPEN LINE FROM BUS 243173 [05MILLBRK 69.000] TO BUS 246917 [05RUHLMAN 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.4129
SINGLE OPN LIN 2011 243176-243178(1) | OPEN LINE FROM BUS 243176 [05N HAVERH 69.000] TO BUS 243178 [05GINAT C SS69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.7182
SINGLE OPN LIN 2012 243178-247476(1) | OPEN LINE FROM BUS 243178 [05GINAT C SS69.000] TO BUS 247476 [05PLYMOUTHHT69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.29932 | 20.4023 | 1 | 4.054
SINGLE OPN LIN 2013 243181-243183(1) | OPEN LINE FROM BUS 243181 [05SCIOTOVI 69.000] TO BUS 243183 [05WHEELRBR 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6761
SINGLE OPN LIN 2014 243618-247072(1) | OPEN LINE FROM BUS 243618 [05STUART 69.000] TO BUS 247072 [05RAVNSS 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14654 | 2.4021
SINGLE OPN LIN 2015 243656-243808(1) | OPEN LINE FROM BUS 243656 [05BEAVC1EQ 999.00] TO BUS 243808 [05BEAVERCR 46.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.6079
SINGLE OPN LIN 2016 243657-243808(1) | OPEN LINE FROM BUS 243657 [05BEAVC2EQ 999.00] TO BUS 243808 [05BEAVERCR 46.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.3335
SINGLE OPN LIN 2017 243663-243702(1) | OPEN LINE FROM BUS 243663 [05THELMAEQ 999.00] TO BUS 243702 [05THELMA 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.3468
SINGLE OPN LIN 2018 243663-243750(1) | OPEN LINE FROM BUS 243663 [05THELMAEQ 999.00] TO BUS 243750 [05THELM1 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.49064 | 8.9746
SINGLE OPN LIN 2019 243663-243811(1) | OPEN LINE FROM BUS 243663 [05THELMAEQ 999.00] TO BUS 243811 [05THELMA 46.000] CKT 1 | FALSE | Iteration limit exceeded | 0 | 1.781 | 45.3469
SINGLE OPN LIN 2020 243678-243679(1) | OPEN LINE FROM BUS 243678 [05BSANDX 138.00] TO BUS 243679 [05BUSSYV 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.16775 | 8.5883
SINGLE OPN LIN 2021 243679-243702(1) | OPEN LINE FROM BUS 243679 [05BUSSYV 138.00] TO BUS 243702 [05THELMA 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.98526 | 38.9717
SINGLE OPN LIN 2022 243684-243702(1) | OPEN LINE FROM BUS 243684 [05DEWEY 138.00] TO BUS 243702 [05THELMA 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.54271 | 9.8096
SINGLE OPN LIN 2023 243684-243804(1) | OPEN LINE FROM BUS 243684 [05DEWEY 138.00] TO BUS 243804 [05DEWEY 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.816
SINGLE OPN LIN 2024 243684-244008(1) | OPEN LINE FROM BUS 243684 [05DEWEY 138.00] TO BUS 244008 [05STANVILLE1138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 5.0219
SINGLE OPN LIN 2025 243688-244686(Z1) | OPEN LINE FROM BUS 243688 [05S.PORT MTR138.00] TO BUS 244686 [05VANCEBURG 138.00] CKT Z1 | TRUE | Met convergence tolerances | 1 | 0.45965 | 31.0345 | 1 | 6.945
SINGLE OPN LIN 2026 243702-246971(1) | OPEN LINE FROM BUS 243702 [05THELMA 138.00] TO BUS 246971 [05THELM2 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.0509
SINGLE OPN LIN 2027 243712-243716(1) | OPEN LINE FROM BUS 243712 [05CANNONSB 69.000] TO BUS 243716 [05COALTON 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.895
SINGLE OPN LIN 2028 243714-243727(1) | OPEN LINE FROM BUS 243714 [05CHAVIES 69.000] TO BUS 243727 [05HADDIX 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.23277 | 7.2594
SINGLE OPN LIN 2029 243716-243732(1) | OPEN LINE FROM BUS 243716 [05COALTON 69.000] TO BUS 243732 [05HITCHI 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.42203 | 20.3752
SINGLE OPN LIN 2030 243716-243743(1) | OPEN LINE FROM BUS 243716 [05COALTON 69.000] TO BUS 243743 [05PRINCESS 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 5.227
SINGLE OPN LIN 2031 243724-243737(1) | OPEN LINE FROM BUS 243724 [05GRAHN 69.000] TO BUS 243737 [05LEONKY 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6991
SINGLE OPN LIN 2032 243724-243742(1) | OPEN LINE FROM BUS 243724 [05GRAHN 69.000] TO BUS 243742 [05CORYSS 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.8395
SINGLE OPN LIN 2033 243727-243734(1) | OPEN LINE FROM BUS 243727 [05HADDIX 69.000] TO BUS 243734 [05JACKSON 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.799
SINGLE OPN LIN 2034 243728-243740(1) | OPEN LINE FROM BUS 243728 [05HAYWAR 69.000] TO BUS 243740 [05MOREHE 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.6475
SINGLE OPN LIN 2035 243728-243741(1) | OPEN LINE FROM BUS 243728 [05HAYWAR 69.000] TO BUS 243741 [05OLIVEHIL 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.0593
SINGLE OPN LIN 2036 243732-243737(1) | OPEN LINE FROM BUS 243732 [05HITCHI 69.000] TO BUS 243737 [05LEONKY 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.35502 | 18.5489
SINGLE OPN LIN 2037 243733-243812(1) | OPEN LINE FROM BUS 243733 [05INDEX 69.000] TO BUS 243812 [05LEE C 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.3262
SINGLE OPN LIN 2039 243734-243812(1) | OPEN LINE FROM BUS 243734 [05JACKSON 69.000] TO BUS 243812 [05LEE C 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.9955
SINGLE OPN LIN 2041 243741-243742(1) | OPEN LINE FROM BUS 243741 [05OLIVEHIL 69.000] TO BUS 243742 [05CORYSS 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.9011
SINGLE OPN LIN 2042 243750-244632(1) | OPEN LINE FROM BUS 243750 [05THELM1 69.000] TO BUS 244632 [05W.PNTSVL 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.7795
SINGLE OPN LIN 2043 243758-243759(1) | OPEN LINE FROM BUS 243758 [05MIDDLECR 46.000] TO BUS 243759 [05PRESTNSB 46.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.28926 | 6.9912 | 1 | 0.906
SINGLE OPN LIN 2044 243808-244592(1) | OPEN LINE FROM BUS 243808 [05BEAVERCR 46.000] TO BUS 244592 [05BURTON 46.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.19183 | 5.9396
SINGLE OPN LIN 2045 243808-244616(1) | OPEN LINE FROM BUS 243808 [05BEAVERCR 46.000] TO BUS 244616 [05MCKINNEY 46.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.0895
SINGLE OPN LIN 2046 244632-246970(1) | OPEN LINE FROM BUS 244632 [05W.PNTSVL 69.000] TO BUS 246970 [05MAYOTRL 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.727
SINGLE OPN LIN 2047 246970-246971(1) | OPEN LINE FROM BUS 246970 [05MAYOTRL 69.000] TO BUS 246971 [05THELM2 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.7451
SINGLE OPN TIE 2048 242691-242835(1) | OPEN LINE FROM BUS 242691 [05KENOVA 138.00] TO BUS 242835 [05TRISTA 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.6744
SINGLE OPN TIE 2049 242691-244720(1) | OPEN LINE FROM BUS 242691 [05KENOVA 138.00] TO BUS 244720 [05KENOVA H 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.4155
SINGLE OPN TIE 2050 242918-244965(EQ) | OPEN LINE FROM BUS 242918 [05SPOIN4EQ 999.00] TO BUS 244965 [05S POINT 69.000] CKT EQ | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.4389
SINGLE OPN TIE 2051 242918-245615(4) | OPEN LINE FROM BUS 242918 [05SPOIN4EQ 999.00] TO BUS 245615 [05S.POINT2 138.00] CKT 4 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.471
SINGLE OPN TIE 2052 242927-242924(1) | OPEN LINE FROM BUS 242927 [05MARQUI 765.00] TO BUS 242924 [05HANG R 765.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.16717 | 9.3131
SINGLE OPN TIE 2053 242938-248005(1) | OPEN LINE FROM BUS 242938 [05MARQUI 345.00] TO BUS 248005 [06KYGER 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.5006
SINGLE OPN TIE 2054 242938-248005(2) | OPEN LINE FROM BUS 242938 [05MARQUI 345.00] TO BUS 248005 [06KYGER 345.00] CKT 2 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.777
SINGLE OPN TIE 2055 242938-248013(1) | OPEN LINE FROM BUS 242938 [05MARQUI 345.00] TO BUS 248013 [06PIERCE 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14335 | 1.9883
SINGLE OPN TIE 2056 242938-253077(1) | OPEN LINE FROM BUS 242938 [05MARQUI 345.00] TO BUS 253077 [09STUART 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.32293 | 2.5669
SINGLE OPN TIE 2057 242982-243815(2) | OPEN LINE FROM BUS 242982 [05CENPOR 138.00] TO BUS 243815 [05CENPORTS 69.000] CKT 2 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.1894
SINGLE OPN TIE 2058 242992-243124(1) | OPEN LINE FROM BUS 242992 [05E WHEE 138.00] TO BUS 243124 [05TEXEAS 138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.29519 | 19.7997 | 1 | 25.5
SINGLE OPN TIE 2059 242992-243968(1) | OPEN LINE FROM BUS 242992 [05E WHEE 138.00] TO BUS 243968 [05IRONWOODSS138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.0411
SINGLE OPN TIE 2060 243013-242698(1) | OPEN LINE FROM BUS 243013 [05GAVIN1 138.00] TO BUS 242698 [05LAKIN 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.9312
SINGLE OPN TIE 2061 243013-242807(1) | OPEN LINE FROM BUS 243013 [05GAVIN1 138.00] TO BUS 242807 [05SPORN 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.8193
SINGLE OPN TIE 2062 243013-243611(1) | OPEN LINE FROM BUS 243013 [05GAVIN1 138.00] TO BUS 243611 [05CARTWRT SS138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.5576
SINGLE OPN TIE 2063 243013-243766(ZC) | OPEN LINE FROM BUS 243013 [05GAVIN1 138.00] TO BUS 243766 [05LIGHTSTONL138.00] CKT ZC | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.336
SINGLE OPN TIE 2064 243013-243766(ZD) | OPEN LINE FROM BUS 243013 [05GAVIN1 138.00] TO BUS 243766 [05LIGHTSTONL138.00] CKT ZD | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.336
SINGLE OPN TIE 2065 243013-244949(1) | OPEN LINE FROM BUS 243013 [05GAVIN1 138.00] TO BUS 244949 [05GAVIN 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.7539
SINGLE OPN TIE 2066 243013-244949(2) | OPEN LINE FROM BUS 243013 [05GAVIN1 138.00] TO BUS 244949 [05GAVIN 69.000] CKT 2 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.7833
SINGLE OPN TIE 2067 243013-246324(Z1) | OPEN LINE FROM BUS 243013 [05GAVIN1 138.00] TO BUS 246324 [05GAVIN_CAP 138.00] CKT Z1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 1.336
SINGLE OPN TIE 2068 243019-242787(1) | OPEN LINE FROM BUS 243019 [05HILLSB 138.00] TO BUS 242787 [05MIDDLEB SS138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.20213 | 3.8018
SINGLE OPN TIE 2069 243019-246911(1) | OPEN LINE FROM BUS 243019 [05HILLSB 138.00] TO BUS 246911 [05HIGHLA 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.6362
SINGLE OPN TIE 2070 243019-246946(1) | OPEN LINE FROM BUS 243019 [05HILLSB 138.00] TO BUS 246946 [05WLDCAT 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.5257 | 21.6593
SINGLE OPN TIE 2071 243019-249995(1) | OPEN LINE FROM BUS 243019 [05HILLSB 138.00] TO BUS 249995 [08CLINCO 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.5581
SINGLE OPN TIE 2072 243034-243501(1) | OPEN LINE FROM BUS 243034 [05MARQUI 138.00] TO BUS 243501 [05E.BEAV 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 3.0807
SINGLE OPN TIE 2073 243034-243544(2) | OPEN LINE FROM BUS 243034 [05MARQUI 138.00] TO BUS 243544 [05MILPRD 138.00] CKT 2 | TRUE | Met convergence tolerances | 0 | 0.23103 | 4.9346
SINGLE OPN TIE 2074 243034-245632(1) | OPEN LINE FROM BUS 243034 [05MARQUI 138.00] TO BUS 245632 [05ARBOLES 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.6184
SINGLE OPN TIE 2075 243042-245948(Z1) | OPEN LINE FROM BUS 243042 [05MILLBR PK1138.00] TO BUS 245948 [05MILLBR PK2138.00] CKT Z1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.336
SINGLE OPN TIE 2076 243042-245949(Z1) | OPEN LINE FROM BUS 243042 [05MILLBR PK1138.00] TO BUS 245949 [05MLBRPK_ARG138.00] CKT Z1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.336
SINGLE OPN TIE 2077 243064-242929(2) | OPEN LINE FROM BUS 243064 [05NPROCT 138.00] TO BUS 242929 [05NPROCT 765.00] CKT 2 | TRUE | Met convergence tolerances | 0 | 0.14706 | 7.4092
SINGLE OPN TIE 2078 243064-242999(1) | OPEN LINE FROM BUS 243064 [05NPROCT 138.00] TO BUS 242999 [05EPROCT 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.16913 | 2.5572
SINGLE OPN TIE 2079 243064-243193(1) | OPEN LINE FROM BUS 243064 [05NPROCT 138.00] TO BUS 243193 [05VIKING SS 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.6162
SINGLE OPN TIE 2080 243064-243675(1) | OPEN LINE FROM BUS 243064 [05NPROCT 138.00] TO BUS 243675 [05BELLF1 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.0604
SINGLE OPN TIE 2081 243064-245615(1) | OPEN LINE FROM BUS 243064 [05NPROCT 138.00] TO BUS 245615 [05S.POINT2 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.17067 | 2.5924
SINGLE OPN TIE 2082 243064-245664(1) | OPEN LINE FROM BUS 243064 [05NPROCT 138.00] TO BUS 245664 [05E.HUNTING1138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.5315
SINGLE OPN TIE 2083 243064-290186(2) | OPEN LINE FROM BUS 243064 [05NPROCT 138.00] TO BUS 290186 [05N.CHESPK 138.00] CKT 2 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.527
SINGLE OPN TIE 2084 243087-243140(1) | OPEN LINE FROM BUS 243087 [05S LUCA 138.00] TO BUS 243140 [05WAKEFL 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.15322 | 2.5719
SINGLE OPN TIE 2085 243088-245615(Z1) | OPEN LINE FROM BUS 243088 [05S.POINT1 138.00] TO BUS 245615 [05S.POINT2 138.00] CKT Z1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.1466
SINGLE OPN TIE 2086 243088-245948(1) | OPEN LINE FROM BUS 243088 [05S.POINT1 138.00] TO BUS 245948 [05MILLBR PK2138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.6363
SINGLE OPN TIE 2087 243102-244942(Z1) | OPEN LINE FROM BUS 243102 [05SINK SP8SS138.00] TO BUS 244942 [05SINK SP8 138.00] CKT Z1 | TRUE | Met convergence tolerances | 1 | 0.14177 | 4.5315 | 1 | 3.365
SINGLE OPN TIE 2088 243102-245948(1) | OPEN LINE FROM BUS 243102 [05SINK SP8SS138.00] TO BUS 245948 [05MILLBR PK2138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.4181
SINGLE OPN TIE 2089 243171-290138(1) | OPEN LINE FROM BUS 243171 [05HAYPRTRDSS69.000] TO BUS 290138 [05KOT COAL 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14177 | 2.1009 | 1 | 1.05
SINGLE OPN TIE 2090 243173-246850(1) | OPEN LINE FROM BUS 243173 [05MILLBRK 69.000] TO BUS 246850 [05TYGART 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.6236
SINGLE OPN TIE 2091 243176-243164(1) | OPEN LINE FROM BUS 243176 [05N HAVERH 69.000] TO BUS 243164 [05DCHEMTAP 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.5719
SINGLE OPN TIE 2092 243176-243827(1) | OPEN LINE FROM BUS 243176 [05N HAVERH 69.000] TO BUS 243827 [05SUNCOKE 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.87334 | 49.1192 | 1 | 10.95
SINGLE OPN TIE 2093 243176-247033(1) | OPEN LINE FROM BUS 243176 [05N HAVERH 69.000] TO BUS 247033 [05HAVERHSS 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.3372
SINGLE OPN TIE 2094 243184-244719(1) | OPEN LINE FROM BUS 243184 [05S POINT 34.500] TO BUS 244719 [05VIRGINIA 34.500] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.0945
SINGLE OPN TIE 2095 243184-244968(1) | OPEN LINE FROM BUS 243184 [05S POINT 34.500] TO BUS 244968 [05SPTETHNO 34.500] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.3413
SINGLE OPN TIE 2096 243184-244968(2) | OPEN LINE FROM BUS 243184 [05S POINT 34.500] TO BUS 244968 [05SPTETHNO 34.500] CKT 2 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.3367
SINGLE OPN TIE 2097 243453-243454(1) | OPEN LINE FROM BUS 243453 [05BEATTY 345.00] TO BUS 243454 [05BIXBY 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.27536 | 3.4222
SINGLE OPN TIE 2098 243453-243469(3) | OPEN LINE FROM BUS 243453 [05BEATTY 345.00] TO BUS 243469 [05BEATTY 138.00] CKT 3 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.0384
SINGLE OPN TIE 2099 243453-243469(4) | OPEN LINE FROM BUS 243453 [05BEATTY 345.00] TO BUS 243469 [05BEATTY 138.00] CKT 4 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.037
SINGLE OPN TIE 2100 243453-244022(1) | OPEN LINE FROM BUS 243453 [05BEATTY 345.00] TO BUS 244022 [05COLE 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.24035 | 5.9052
SINGLE OPN TIE 2101 243453-245769(1) | OPEN LINE FROM BUS 243453 [05BEATTY 345.00] TO BUS 245769 [05ADKINS 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.20535 | 11.0985
SINGLE OPN TIE 2102 243453-253248(1) | OPEN LINE FROM BUS 243453 [05BEATTY 345.00] TO BUS 253248 [09MDISON 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.7822
SINGLE OPN TIE 2103 243597-246741(1) | OPEN LINE FROM BUS 243597 [05ASHLEY 69.000] TO BUS 246741 [05PEDRO 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.9263
SINGLE OPN TIE 2104 243618-253076(1) | OPEN LINE FROM BUS 243618 [05STUART 69.000] TO BUS 253076 [09STUART 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14683 | 2.3997
SINGLE OPN TIE 2105 243656-243671(1) | OPEN LINE FROM BUS 243656 [05BEAVC1EQ 999.00] TO BUS 243671 [05BEAVER CR1138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 4.3434
SINGLE OPN TIE 2106 243657-243708(1) | OPEN LINE FROM BUS 243657 [05BEAVC2EQ 999.00] TO BUS 243708 [05BEAVERCR 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.3488
SINGLE OPN TIE 2107 243657-244688(1) | OPEN LINE FROM BUS 243657 [05BEAVC2EQ 999.00] TO BUS 244688 [05BEAVER CR2138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.99
SINGLE OPN TIE 2108 243678-243669(SR) | OPEN LINE FROM BUS 243678 [05BSANDX 138.00] TO BUS 243669 [05B SAND 138.00] CKT SR | TRUE | Met convergence tolerances | 0 | 0.16806 | 8.7577
SINGLE OPN TIE 2109 243688-245949(1) | OPEN LINE FROM BUS 243688 [05S.PORT MTR138.00] TO BUS 245949 [05MLBRPK_ARG138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6005
SINGLE OPN TIE 2111 243712-244727(1) | OPEN LINE FROM BUS 243712 [05CANNONSB 69.000] TO BUS 244727 [05S.NEAL 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.8454
SINGLE OPN TIE 2112 243714-243710(1) | OPEN LINE FROM BUS 243714 [05CHAVIES 69.000] TO BUS 243710 [05BONNYMAN 69.000] CKT 1 | FALSE | Iteration limit exceeded | 0 | 0.52345 | 15.5183
SINGLE OPN TIE 2119 243743-244670(1) | OPEN LINE FROM BUS 243743 [05PRINCESS 69.000] TO BUS 244670 [05HOODSCRK 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.0042
SINGLE OPN TIE 2120 243759-243753(1) | OPEN LINE FROM BUS 243759 [05PRESTNSB 46.000] TO BUS 243753 [05ALLEN 46.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.4708
SINGLE OPN TIE 2121 243759-243754(1) | OPEN LINE FROM BUS 243759 [05PRESTNSB 46.000] TO BUS 243754 [05EPRESTNS 46.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.5403
SINGLE OPN TIE 2122 243759-247415(1) | OPEN LINE FROM BUS 243759 [05PRESTNSB 46.000] TO BUS 247415 [05JENWILEYSS46.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 3.1163
SINGLE OPN TIE 2123 243804-244575(1) | OPEN LINE FROM BUS 243804 [05DEWEY 69.000] TO BUS 244575 [05PEVLER 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.1591
SINGLE OPN TIE 2124 243811-243756(1) | OPEN LINE FROM BUS 243811 [05THELMA 46.000] TO BUS 243756 [05KENWDTAP 46.000] CKT 1 | FALSE | Iteration limit exceeded | 0 | 2.857 | 44.6788
SINGLE OPN TIE 2126 243819-243822(1) | OPEN LINE FROM BUS 243819 [05N PORTSM 69.000] TO BUS 243822 [05ROSEMNT SS69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.8576
SINGLE OPN TIE 2127 243819-243826(1) | OPEN LINE FROM BUS 243819 [05N PORTSM 69.000] TO BUS 243826 [05ORTELCRN 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.5856
SINGLE OPN TIE 2128 244008-242915(Z1) | OPEN LINE FROM BUS 244008 [05STANVILLE1138.00] TO BUS 242915 [05STANVILLE2138.00] CKT Z1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 4.3336
SINGLE OPN TIE 2129 244592-244599(1) | OPEN LINE FROM BUS 244592 [05BURTON 46.000] TO BUS 244599 [05ELWOOD 46.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 3.7742
SINGLE OPN TIE 2130 244616-244626(1) | OPEN LINE FROM BUS 244616 [05MCKINNEY 46.000] TO BUS 244626 [05SALSBURY 46.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.804
SINGLE OPN TIE 2131 246782-247061(1) | OPEN LINE FROM BUS 246782 [05FIREBRCK 69.000] TO BUS 247061 [05JEFFERSNSS69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.18338 | 7.1328
SINGLE OPN TIE 2132 246782-247062(1) | OPEN LINE FROM BUS 246782 [05FIREBRCK 69.000] TO BUS 247062 [05BLOOM SS 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 5.2519
SINGLE OPN TIE 2133 246888-243454(1) | OPEN LINE FROM BUS 246888 [05BIERSR 345.00] TO BUS 243454 [05BIXBY 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.31519 | 2.9384
SINGLE OPN TIE 2134 246888-246889(1) | OPEN LINE FROM BUS 246888 [05BIERSR 345.00] TO BUS 246889 [05BIERSR 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.19014 | 9.8788
SINGLE OPN TIE 2135 246916-243815(1) | OPEN LINE FROM BUS 246916 [05CORNRSTN 69.000] TO BUS 243815 [05CENPORTS 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.2825
SINGLE OPN TIE 2136 246917-243815(1) | OPEN LINE FROM BUS 246917 [05RUHLMAN 69.000] TO BUS 243815 [05CENPORTS 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.4953
SINGLE OPN TIE 2139 247072-246790(1) | OPEN LINE FROM BUS 247072 [05RAVNSS 69.000] TO BUS 246790 [05BROWNHLS 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.18379 | 2.4863
SINGLE OPN TIE 2140 247072-247073(1) | OPEN LINE FROM BUS 247072 [05RAVNSS 69.000] TO BUS 247073 [05RAVEN 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.35845 | 24.5769 | 1 | 5.183
SINGLE OPN LIN 2141 249564-249991(1) | OPEN LINE FROM BUS 249564 [08BUFTN1 345.00] TO BUS 249991 [08BUFTN1 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.6511
SINGLE OPN LIN 2142 249564-249991(46) | OPEN LINE FROM BUS 249564 [08BUFTN1 345.00] TO BUS 249991 [08BUFTN1 138.00] CKT 46 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.6773
SINGLE OPN LIN 2143 249566-249570(1) | OPEN LINE FROM BUS 249566 [08FOSTER 345.00] TO BUS 249570 [08P.UNON 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.2132
SINGLE OPN LIN 2144 249566-249578(1) | OPEN LINE FROM BUS 249566 [08FOSTER 345.00] TO BUS 249578 [08HILCRT 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.77011 | 31.5429
SINGLE OPN LIN 2145 249566-249582(1) | OPEN LINE FROM BUS 249566 [08FOSTER 345.00] TO BUS 249582 [08GARVER 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.24332 | 5.2669
SINGLE OPN LIN 2146 249567-249575(1) | OPEN LINE FROM BUS 249567 [08M.FORT 345.00] TO BUS 249575 [08TERMNL 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.4564 | 5.7033
SINGLE OPN LIN 2147 249567-250057(10) | OPEN LINE FROM BUS 249567 [08M.FORT 345.00] TO BUS 250057 [08M.FORT 138.00] CKT 10 | TRUE | Met convergence tolerances | 0 | 0.16874 | 3.105
SINGLE OPN LIN 2148 249567-250057(9) | OPEN LINE FROM BUS 249567 [08M.FORT 345.00] TO BUS 250057 [08M.FORT 138.00] CKT 9 | TRUE | Met convergence tolerances | 0 | 0.16963 | 3.1063
SINGLE OPN LIN 2149 249570-249575(1) | OPEN LINE FROM BUS 249570 [08P.UNON 345.00] TO BUS 249575 [08TERMNL 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.4351 | 6.2619
SINGLE OPN LIN 2150 249570-249577(1) | OPEN LINE FROM BUS 249570 [08P.UNON 345.00] TO BUS 249577 [08ZIMER 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.16532 | 8.4641
SINGLE OPN LIN 2151 249570-250082(1) | OPEN LINE FROM BUS 249570 [08P.UNON 345.00] TO BUS 250082 [08P.UN1 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14192 | 3.0273
SINGLE OPN LIN 2152 249570-250083(1) | OPEN LINE FROM BUS 249570 [08P.UNON 345.00] TO BUS 250083 [08P.UN2 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.16575 | 3.0151
SINGLE OPN LIN 2153 249571-249573(1) | OPEN LINE FROM BUS 249571 [08REDBK1 345.00] TO BUS 249573 [08SGROVE 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.93127 | 37.2423
SINGLE OPN LIN 2154 249571-249575(1) | OPEN LINE FROM BUS 249571 [08REDBK1 345.00] TO BUS 249575 [08TERMNL 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.6048
SINGLE OPN LIN 2155 249573-249577(1) | OPEN LINE FROM BUS 249573 [08SGROVE 345.00] TO BUS 249577 [08ZIMER 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.29758 | 15.8985
SINGLE OPN LIN 2156 249573-250097(1) | OPEN LINE FROM BUS 249573 [08SGROVE 345.00] TO BUS 250097 [08SGROVE 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.63113 | 25.1878
SINGLE OPN LIN 2157 249577-249580(Z1) | OPEN LINE FROM BUS 249577 [08ZIMER 345.00] TO BUS 249580 [08ZIMERG 345.00] CKT Z1 | TRUE | Met convergence tolerances | 3 | 0.14287 | 1.4841
SINGLE OPN LIN 2158 249577-249581(1) | OPEN LINE FROM BUS 249577 [08ZIMER 345.00] TO BUS 249581 [08MELDAL 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.2019 | 2.0417
SINGLE OPN LIN 2159 249578-250136(1) | OPEN LINE FROM BUS 249578 [08HILCRT 345.00] TO BUS 250136 [08HILCRT 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.1708
SINGLE OPN LIN 2160 249580-251968(1H) | OPEN LINE FROM BUS 249580 [08ZIMERG 345.00] TO BUS 251968 [08ZIMRHP 26.000] CKT 1H | TRUE | Met convergence tolerances | 1 | 0.54151 | 30.564
SINGLE OPN LIN 2161 249580-251969(1L) | OPEN LINE FROM BUS 249580 [08ZIMERG 345.00] TO BUS 251969 [08ZIMRLP 22.000] CKT 1L | TRUE | Met convergence tolerances | 1 | 0.36506 | 17.216
SINGLE OPN LIN 2162 249581-250145(1) | OPEN LINE FROM BUS 249581 [08MELDAL 345.00] TO BUS 250145 [08MELDAL 138.00] CKT 1 | TRUE | Met convergence tolerances | 5 | 0.42842 | 12.6391
SINGLE OPN LIN 2163 249990-250021(1) | OPEN LINE FROM BUS 249990 [08BROWN 138.00] TO BUS 250021 [08ESTWD2 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.8798
SINGLE OPN LIN 2164 249991-250028(1) | OPEN LINE FROM BUS 249991 [08BUFTN1 138.00] TO BUS 250028 [08FLRNC2 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.71713 | 28.2067
SINGLE OPN LIN 2165 249991-250077(1) | OPEN LINE FROM BUS 249991 [08BUFTN1 138.00] TO BUS 250077 [08MTZION 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.17572 | 2.5564
SINGLE OPN LIN 2166 249991-250148(1) | OPEN LINE FROM BUS 249991 [08BUFTN1 138.00] TO BUS 250148 [08EKPWEB 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.4814
SINGLE OPN LIN 2167 249991-251279(2) | OPEN LINE FROM BUS 249991 [08BUFTN1 138.00] TO BUS 251279 [08BUFTN2 69.000] CKT 2 | TRUE | Met convergence tolerances | 0 | 0.14287 | 4.5105
SINGLE OPN LIN 2168 249999-250007(1) | OPEN LINE FROM BUS 249999 [08CNSTNC 138.00] TO BUS 250007 [08CRSNT1 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.1163
SINGLE OPN LIN 2169 249999-250044(1) | OPEN LINE FROM BUS 249999 [08CNSTNC 138.00] TO BUS 250044 [08HEBRN2 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14453 | 3.823
SINGLE OPN LIN 2170 250016-250057(1) | OPEN LINE FROM BUS 250016 [08EBNZR 138.00] TO BUS 250057 [08M.FORT 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.5017
SINGLE OPN LIN 2171 250044-250152(Z1) | OPEN LINE FROM BUS 250044 [08HEBRN2 138.00] TO BUS 250152 [08HEBRNG 138.00] CKT Z1 | TRUE | Met convergence tolerances | 0 | 0.16061 | 4.1606
SINGLE OPN LIN 2172 250045-250151(Z1) | OPEN LINE FROM BUS 250045 [08HEBRN1 138.00] TO BUS 250151 [08HEBTAP 138.00] CKT Z1 | TRUE | Met convergence tolerances | 1 | 0.99756 | 62.3572 | 1 | 15.088
SINGLE OPN LIN 2173 250054-250077(1) | OPEN LINE FROM BUS 250054 [08LONGBR 138.00] TO BUS 250077 [08MTZION 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6695
SINGLE OPN LIN 2174 250057-250058(1) | OPEN LINE FROM BUS 250057 [08M.FORT 138.00] TO BUS 250058 [08M.FTGT 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.752
SINGLE OPN LIN 2175 250057-250060(1) | OPEN LINE FROM BUS 250057 [08M.FORT 138.00] TO BUS 250060 [08MDWAY1 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 4.339
SINGLE OPN LIN 2176 250057-250070(1) | OPEN LINE FROM BUS 250057 [08M.FORT 138.00] TO BUS 250070 [08MRGAN1 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.16853 | 5.8313
SINGLE OPN LIN 2177 250057-250131(1) | OPEN LINE FROM BUS 250057 [08M.FORT 138.00] TO BUS 250131 [08WILEY2 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 5.3452
SINGLE OPN LIN 2178 250057-250151(1) | OPEN LINE FROM BUS 250057 [08M.FORT 138.00] TO BUS 250151 [08HEBTAP 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.36835 | 5.1153
SINGLE OPN LIN 2179 250058-251378(1) | OPEN LINE FROM BUS 250058 [08M.FTGT 138.00] TO BUS 251378 [08M.FTGT 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.8702
SINGLE OPN LIN 2180 250136-250141(1) | OPEN LINE FROM BUS 250136 [08HILCRT 138.00] TO BUS 250141 [08SCEAST 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.21816 | 2.608
SINGLE OPN LIN 2181 250145-250154(1) | OPEN LINE FROM BUS 250145 [08MELDAL 138.00] TO BUS 250154 [08MELDLS 138.00] CKT 1 | TRUE | Met convergence tolerances | 4 | 0.42881 | 12.6289
SINGLE OPN LIN 2182 250151-250152(Z1) | OPEN LINE FROM BUS 250151 [08HEBTAP 138.00] TO BUS 250152 [08HEBRNG 138.00] CKT Z1 | TRUE | Met convergence tolerances | 0 | 0.36119 | 5.1411
SINGLE OPN LIN 2183 250154-251970(T1) | OPEN LINE FROM BUS 250154 [08MELDLS 138.00] TO BUS 251970 [08MELDL1 13.800] CKT T1 | TRUE | Met convergence tolerances | 1 | 0.47551 | 25.9183
SINGLE OPN LIN 2184 250154-251971(T2) | OPEN LINE FROM BUS 250154 [08MELDLS 138.00] TO BUS 251971 [08MELDL2 13.800] CKT T2 | TRUE | Met convergence tolerances | 1 | 0.47551 | 25.9183
SINGLE OPN LIN 2185 250154-251972(T3) | OPEN LINE FROM BUS 250154 [08MELDLS 138.00] TO BUS 251972 [08MELDL3 13.800] CKT T3 | TRUE | Met convergence tolerances | 1 | 0.47551 | 25.9183
SINGLE OPN LIN 2186 251276-251469(1) | OPEN LINE FROM BUS 251276 [08BROWER 69.000] TO BUS 251469 [08T28652 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14177 | 3.428 | 1 | 2.239
SINGLE OPN LIN 2187 251291-251301(1) | OPEN LINE FROM BUS 251291 [08CNSTNC 69.000] TO BUS 251301 [08CWW-BN 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.4679
SINGLE OPN LIN 2188 251291-251315(1) | OPEN LINE FROM BUS 251291 [08CNSTNC 69.000] TO BUS 251315 [08EKSMTH 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.1062
SINGLE OPN LIN 2189 251301-251310(1) | OPEN LINE FROM BUS 251301 [08CWW-BN 69.000] TO BUS 251310 [08DRYCRK 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.5541
SINGLE OPN LIN 2190 251314-251315(1) | OPEN LINE FROM BUS 251314 [08EKDOWN 69.000] TO BUS 251315 [08EKSMTH 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.0076
SINGLE OPN LIN 2191 251314-251467(1) | OPEN LINE FROM BUS 251314 [08EKDOWN 69.000] TO BUS 251467 [08T15268 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.9817
SINGLE OPN LIN 2192 251367-251368(Z1) | OPEN LINE FROM BUS 251367 [08LEVIA 69.000] TO BUS 251368 [08LEVIB 69.000] CKT Z1 | TRUE | Met convergence tolerances | 3 | 0.20359 | 14.3769 | 3 | 18.983
SINGLE OPN LIN 2193 251367-251467(1) | OPEN LINE FROM BUS 251367 [08LEVIA 69.000] TO BUS 251467 [08T15268 69.000] CKT 1 | TRUE | Met convergence tolerances | 4 | 0.26136 | 17.4255 | 4 | 23.631
SINGLE OPN LIN 2194 251378-251406(1) | OPEN LINE FROM BUS 251378 [08M.FTGT 69.000] TO BUS 251406 [08MONSTW 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.45371 | 30.0388 | 1 | 6.923
SINGLE OPN LIN 2195 251378-251469(1) | OPEN LINE FROM BUS 251378 [08M.FTGT 69.000] TO BUS 251469 [08T28652 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.7208
SINGLE OPN LIN 2196 251378-251579(1) | OPEN LINE FROM BUS 251378 [08M.FTGT 69.000] TO BUS 251579 [08HEBRON 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.434
SINGLE OPN LIN 2197 251467-251579(1) | OPEN LINE FROM BUS 251467 [08T15268 69.000] TO BUS 251579 [08HEBRON 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.6912
SINGLE OPN LIN 2198 251468-251469(1) | OPEN LINE FROM BUS 251468 [08T28651 69.000] TO BUS 251469 [08T28652 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.7297
SINGLE OPN TIE 2199 249564-248002(1) | OPEN LINE FROM BUS 249564 [08BUFTN1 345.00] TO BUS 248002 [06DEARB2 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.19502 | 9.7611
SINGLE OPN TIE 2200 249564-248013(1) | OPEN LINE FROM BUS 249564 [08BUFTN1 345.00] TO BUS 248013 [06PIERCE 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.16429 | 2.3879
SINGLE OPN TIE 2201 249566-248013(1) | OPEN LINE FROM BUS 249566 [08FOSTER 345.00] TO BUS 248013 [06PIERCE 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.1434 | 7.6544
SINGLE OPN TIE 2202 249566-250029(1) | OPEN LINE FROM BUS 249566 [08FOSTER 345.00] TO BUS 250029 [08FOSTER 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.0572
SINGLE OPN TIE 2203 249566-253006(1) | OPEN LINE FROM BUS 249566 [08FOSTER 345.00] TO BUS 253006 [09BATH 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.92323 | 48.3521
SINGLE OPN TIE 2204 249566-253079(1) | OPEN LINE FROM BUS 249566 [08FOSTER 345.00] TO BUS 253079 [09SUGRCK 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.20704 | 11.9494
SINGLE OPN TIE 2205 249567-243233(1) | OPEN LINE FROM BUS 249567 [08M.FORT 345.00] TO BUS 243233 [05TANNER 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.29614 | 16.6788
SINGLE OPN TIE 2206 249567-249576(1) | OPEN LINE FROM BUS 249567 [08M.FORT 345.00] TO BUS 249576 [08WODSDL 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.38698 | 4.7098
SINGLE OPN TIE 2207 249567-251950(7) | OPEN LINE FROM BUS 249567 [08M.FORT 345.00] TO BUS 251950 [08M.FRT7 22.000] CKT 7 | TRUE | Met convergence tolerances | 1 | 0.37412 | 15.4953
SINGLE OPN TIE 2208 249567-251951(8) | OPEN LINE FROM BUS 249567 [08M.FORT 345.00] TO BUS 251951 [08M.FRT8 22.000] CKT 8 | TRUE | Met convergence tolerances | 1 | 0.37383 | 15.626
SINGLE OPN TIE 2209 249567-253090(1) | OPEN LINE FROM BUS 249567 [08M.FORT 345.00] TO BUS 253090 [09WMILTN 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.3346 | 16.7923
SINGLE OPN TIE 2210 249571-250092(1) | OPEN LINE FROM BUS 249571 [08REDBK1 345.00] TO BUS 250092 [08REDBK1 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.20099 | 3.3215
SINGLE OPN TIE 2211 249571-250093(1) | OPEN LINE FROM BUS 249571 [08REDBK1 345.00] TO BUS 250093 [08REDBK2 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14995 | 2.9043
SINGLE OPN TIE 2212 249575-249565(1) | OPEN LINE FROM BUS 249575 [08TERMNL 345.00] TO BUS 249565 [08EBEND 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.16115 | 8.5181
SINGLE OPN TIE 2213 249575-250117(1) | OPEN LINE FROM BUS 249575 [08TERMNL 345.00] TO BUS 250117 [08TRMNL1 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 3.3424
SINGLE OPN TIE 2214 249575-250118(1) | OPEN LINE FROM BUS 249575 [08TERMNL 345.00] TO BUS 250118 [08TRMNL2 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.18074 | 3.5787
SINGLE OPN TIE 2215 249578-253077(1) | OPEN LINE FROM BUS 249578 [08HILCRT 345.00] TO BUS 253077 [09STUART 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.79605 | 32.8349
SINGLE OPN TIE 2217 249582-249574(1) | OPEN LINE FROM BUS 249582 [08GARVER 345.00] TO BUS 249574 [08TDHNTR 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.37119 | 3.0713
SINGLE OPN TIE 2218 249582-249583(1) | OPEN LINE FROM BUS 249582 [08GARVER 345.00] TO BUS 249583 [08NTEGEN 345.00] CKT 1 | TRUE | Met convergence tolerances | 3 | 0.28641 | 15.6463
SINGLE OPN TIE 2219 249582-250162(1) | OPEN LINE FROM BUS 249582 [08GARVER 345.00] TO BUS 250162 [08GARVER 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.28619 | 4.263
SINGLE OPN TIE 2220 249990-253076(1) | OPEN LINE FROM BUS 249990 [08BROWN 138.00] TO BUS 253076 [09STUART 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.19355 | 2.3696
SINGLE OPN TIE 2221 249990-251277-251792(1) | OPEN LINE FROM BUS 249990 [08BROWN 138.00] TO BUS 251277 [08BROWN 69.000] TO BUS 251792 [08BROWN 34.500] CKT 1 | TRUE | Met convergence tolerances | 18 | 0.23908 | 16.2557 | 8 | 52.287
SINGLE OPN TIE 2222 249991-251278(1) | OPEN LINE FROM BUS 249991 [08BUFTN1 138.00] TO BUS 251278 [08BUFTN1 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.3829
SINGLE OPN TIE 2223 249991-251278-252039(1) | OPEN LINE FROM BUS 249991 [08BUFTN1 138.00] TO BUS 251278 [08BUFTN1 69.000] TO BUS 252039 [08BUFTN1 12.470] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.8714
SINGLE OPN TIE 2224 250007-250014(1) | OPEN LINE FROM BUS 250007 [08CRSNT1 138.00] TO BUS 250014 [08DNLSN1 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.9141
SINGLE OPN TIE 2225 250007-250124(1) | OPEN LINE FROM BUS 250007 [08CRSNT1 138.00] TO BUS 250124 [08WENDEA 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.0881
SINGLE OPN TIE 2226 250016-250061(1) | OPEN LINE FROM BUS 250016 [08EBNZR 138.00] TO BUS 250061 [08MDWAY2 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6022
SINGLE OPN TIE 2227 250016-251311(1) | OPEN LINE FROM BUS 250016 [08EBNZR 138.00] TO BUS 251311 [08EBNZR1 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.9381
SINGLE OPN TIE 2228 250016-251312(1) | OPEN LINE FROM BUS 250016 [08EBNZR 138.00] TO BUS 251312 [08EBNZR2 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.26011 | 6.3481
SINGLE OPN TIE 2229 250016-251793(1) | OPEN LINE FROM BUS 250016 [08EBNZR 138.00] TO BUS 251793 [08EBNZR6 34.500] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.39146 | 24.6973 | 1 | 34.168
SINGLE OPN TIE 2230 250021-250020(Z1) | OPEN LINE FROM BUS 250021 [08ESTWD2 138.00] TO BUS 250020 [08ESTWD1 138.00] CKT Z1 | TRUE | Met convergence tolerances | 0 | 0.15825 | 2.1463
SINGLE OPN TIE 2231 250028-250027(Z1) | OPEN LINE FROM BUS 250028 [08FLRNC2 138.00] TO BUS 250027 [08FLRNC1 138.00] CKT Z1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.1479
SINGLE OPN TIE 2233 250057-249736(1) | OPEN LINE FROM BUS 250057 [08M.FORT 138.00] TO BUS 249736 [08GRDALE 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.42913 | 17.7024
SINGLE OPN TIE 2235 250058-251960-251961(18) | OPEN LINE FROM BUS 250058 [08M.FTGT 138.00] TO BUS 251960 [08MFTGT1 13.800] TO BUS 251961 [08MFTGT2 13.800] CKT 18 | TRUE | Met convergence tolerances | 1 | 0.14287 | 1.8034
SINGLE OPN TIE 2236 250060-250048(1) | OPEN LINE FROM BUS 250060 [08MDWAY1 138.00] TO BUS 250048 [08KLEMN1 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.4892
SINGLE OPN TIE 2237 250070-250032(1) | OPEN LINE FROM BUS 250070 [08MRGAN1 138.00] TO BUS 250032 [08FRFLD1 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.4266
SINGLE OPN TIE 2238 250082-249985(1) | OPEN LINE FROM BUS 250082 [08P.UN1 138.00] TO BUS 249985 [08BECKET 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.2579
SINGLE OPN TIE 2239 250082-250050(1) | OPEN LINE FROM BUS 250082 [08P.UN1 138.00] TO BUS 250050 [08KMPER1 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.2284
SINGLE OPN TIE 2240 250082-250067(1) | OPEN LINE FROM BUS 250082 [08P.UN1 138.00] TO BUS 250067 [08MLHSR2 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.8234
SINGLE OPN TIE 2241 250082-250096(1) | OPEN LINE FROM BUS 250082 [08P.UN1 138.00] TO BUS 250096 [08SEWARD 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.238
SINGLE OPN TIE 2242 250082-250157(1) | OPEN LINE FROM BUS 250082 [08P.UN1 138.00] TO BUS 250157 [08CORNTP 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.20133 | 5.1693
SINGLE OPN TIE 2243 250082-251428-251798(1) | OPEN LINE FROM BUS 250082 [08P.UN1 138.00] TO BUS 251428 [08P.UNN1 69.000] TO BUS 251798 [08PORTU6 34.500] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 4.2404
SINGLE OPN TIE 2244 250083-250013(1) | OPEN LINE FROM BUS 250083 [08P.UN2 138.00] TO BUS 250013 [08DIMICK 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14865 | 1.9533
SINGLE OPN TIE 2245 250083-250065(1) | OPEN LINE FROM BUS 250083 [08P.UN2 138.00] TO BUS 250065 [08MILIKN 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.8383
SINGLE OPN TIE 2246 250083-250160(1) | OPEN LINE FROM BUS 250083 [08P.UN2 138.00] TO BUS 250160 [08PROVID 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.4051
SINGLE OPN TIE 2247 250083-251429(1) | OPEN LINE FROM BUS 250083 [08P.UN2 138.00] TO BUS 251429 [08P.UNN2 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 4.6068
SINGLE OPN TIE 2248 250083-251798(1) | OPEN LINE FROM BUS 250083 [08P.UN2 138.00] TO BUS 251798 [08PORTU6 34.500] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.33499 | 21.641 | 1 | 29.482
SINGLE OPN TIE 2249 250083-252045(5) | OPEN LINE FROM BUS 250083 [08P.UN2 138.00] TO BUS 252045 [08PORTU2 12.470] CKT 5 | TRUE | Met convergence tolerances | 1 | 0.33156 | 21.4039 | 1 | 29.183
SINGLE OPN TIE 2250 250083-251428-252045(1) | OPEN LINE FROM BUS 250083 [08P.UN2 138.00] TO BUS 251428 [08P.UNN1 69.000] TO BUS 252045 [08PORTU2 12.470] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.4933
SINGLE OPN TIE 2251 250097-249988(1) | OPEN LINE FROM BUS 250097 [08SGROVE 138.00] TO BUS 249988 [08BKJ135 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.8598
SINGLE OPN TIE 2252 250097-250042(1) | OPEN LINE FROM BUS 250097 [08SGROVE 138.00] TO BUS 250042 [08HANDS1 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.3529
SINGLE OPN TIE 2253 250097-250052(1) | OPEN LINE FROM BUS 250097 [08SGROVE 138.00] TO BUS 250052 [08KYUNIV 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.19451 | 4.8088
SINGLE OPN TIE 2254 250097-250053(1) | OPEN LINE FROM BUS 250097 [08SGROVE 138.00] TO BUS 250053 [08LAFARG 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 4.1175
SINGLE OPN TIE 2255 250131-250032(1) | OPEN LINE FROM BUS 250131 [08WILEY2 138.00] TO BUS 250032 [08FRFLD1 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.3127
SINGLE OPN TIE 2256 250131-250068(1) | OPEN LINE FROM BUS 250131 [08WILEY2 138.00] TO BUS 250068 [08MPLKL1 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6512
SINGLE OPN TIE 2257 250131-250155(1) | OPEN LINE FROM BUS 250131 [08WILEY2 138.00] TO BUS 250155 [08WILCAP 138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14177 | 2.4231
SINGLE OPN TIE 2258 250131-251826(1) | OPEN LINE FROM BUS 250131 [08WILEY2 138.00] TO BUS 251826 [WILLEY 1 34.500] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.63423 | 38.2876 | 2 | 54.101
SINGLE OPN TIE 2259 250136-250166(Z1) | OPEN LINE FROM BUS 250136 [08HILCRT 138.00] TO BUS 250166 [08HLCRTC 138.00] CKT Z1 | TRUE | Met convergence tolerances | 3 | 0.97338 | 53.2187 | 1 | 1.001
SINGLE OPN TIE 2260 250141-250020(1) | OPEN LINE FROM BUS 250141 [08SCEAST 138.00] TO BUS 250020 [08ESTWD1 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.19068 | 2.4233
SINGLE OPN TIE 2261 250148-250043(1) | OPEN LINE FROM BUS 250148 [08EKPWEB 138.00] TO BUS 250043 [08HANDS2 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.537
SINGLE OPN TIE 2264 251279-251527(1) | OPEN LINE FROM BUS 251279 [08BUFTN2 69.000] TO BUS 251527 [08TP6763 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.6561
SINGLE OPN TIE 2265 251279-251543(1) | OPEN LINE FROM BUS 251279 [08BUFTN2 69.000] TO BUS 251543 [08VILLA 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.1378
SINGLE OPN TIE 2266 251310-251284(1) | OPEN LINE FROM BUS 251310 [08DRYCRK 69.000] TO BUS 251284 [08ATLAS 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.9128
SINGLE OPN TIE 2268 251368-251373(1) | OPEN LINE FROM BUS 251368 [08LEVIB 69.000] TO BUS 251373 [08LMBRG1 69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.16669 | 11.9265 | 2 | 15.571
SINGLE OPN TIE 2269 251405-251449(1) | OPEN LINE FROM BUS 251405 [08MONSTE 69.000] TO BUS 251449 [08SAYLPK 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 1.8953 | 1 | 4.793
SINGLE OPN TIE 2270 251468-251414(1) | OPEN LINE FROM BUS 251468 [08T28651 69.000] TO BUS 251414 [08NEUMAN 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.6337
SINGLE OPN LIN 2272 360112-360450(1) | OPEN LINE FROM BUS 360112 [5RUGBY TN 161.00] TO BUS 360450 [5HUNTSVL TN 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 4.0065
SINGLE OPN LIN 2273 360145-360473(1) | OPEN LINE FROM BUS 360145 [5ROYAL BLUE 161.00] TO BUS 360473 [5JELLICO TN 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.1898
SINGLE OPN LIN 2274 360145-361771(1) | OPEN LINE FROM BUS 360145 [5ROYAL BLUE 161.00] TO BUS 361771 [5ROYL BLU SS161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.187
SINGLE OPN LIN 2275 360333-361113(1) | OPEN LINE FROM BUS 360333 [5GLASGOW KY 161.00] TO BUS 361113 [5GLASGOW TP 161.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 3.694 | 1 | 24.03
SINGLE OPN LIN 2276 360334-360354(1) | OPEN LINE FROM BUS 360334 [5SUMMER SHAD161.00] TO BUS 360354 [5LAFAYETT TN161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.70561 | 28.4131
SINGLE OPN LIN 2277 360334-360448(1) | OPEN LINE FROM BUS 360334 [5SUMMER SHAD161.00] TO BUS 360448 [5WOLF CRK HP161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.5782
SINGLE OPN LIN 2278 360334-361064(1) | OPEN LINE FROM BUS 360334 [5SUMMER SHAD161.00] TO BUS 361064 [5TOMPKNSV TP161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.3768
SINGLE OPN LIN 2279 360334-361788(1) | OPEN LINE FROM BUS 360334 [5SUMMER SHAD161.00] TO BUS 361788 [5SUM SHAD TP161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.2613
SINGLE OPN LIN 2280 360338-361139(1) | OPEN LINE FROM BUS 360338 [5SCOTTSVL KY161.00] TO BUS 361139 [5S SCOTTSVLE161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.5466
SINGLE OPN LIN 2281 360342-362499(1) | OPEN LINE FROM BUS 360342 [5LIVINGST TN161.00] TO BUS 362499 [2LIVINGST TN69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 1.336
SINGLE OPN LIN 2282 360354-361139(1) | OPEN LINE FROM BUS 360354 [5LAFAYETT TN161.00] TO BUS 361139 [5S SCOTTSVLE161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.0766
SINGLE OPN LIN 2283 360354-361265(1) | OPEN LINE FROM BUS 360354 [5LAFAYETT TN161.00] TO BUS 361265 [5HARTSVLE TP161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.57767 | 24.6435
SINGLE OPN LIN 2284 360354-361558(1) | OPEN LINE FROM BUS 360354 [5LAFAYETT TN161.00] TO BUS 361558 [5E SUMNER TP161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.4969
SINGLE OPN LIN 2285 360445-360450(1) | OPEN LINE FROM BUS 360445 [5BRAYTOWN TN161.00] TO BUS 360450 [5HUNTSVL TN 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.39723 | 19.8619
SINGLE OPN LIN 2286 360448-360486(1) | OPEN LINE FROM BUS 360448 [5WOLF CRK HP161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.1992
SINGLE OPN LIN 2287 360448-361618(1) | OPEN LINE FROM BUS 360448 [5WOLF CRK HP161.00] TO BUS 361618 [5KELSEY RD 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.2202
SINGLE OPN LIN 2288 360448-361666(1) | OPEN LINE FROM BUS 360448 [5WOLF CRK HP161.00] TO BUS 361666 [5BURKSVLTP 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6942
SINGLE OPN LIN 2289 360448-364620(1) | OPEN LINE FROM BUS 360448 [5WOLF CRK HP161.00] TO BUS 364620 [1WOLFCR H1-213.800] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14177 | 1.5119
SINGLE OPN LIN 2290 360448-364621(2) | OPEN LINE FROM BUS 360448 [5WOLF CRK HP161.00] TO BUS 364621 [1WOLFCR H3-413.800] CKT 2 | TRUE | Met convergence tolerances | 1 | 0.14177 | 1.5101
SINGLE OPN LIN 2291 360448-364622(3) | OPEN LINE FROM BUS 360448 [5WOLF CRK HP161.00] TO BUS 364622 [1WOLFCR H5-613.800] CKT 3 | TRUE | Met convergence tolerances | 1 | 0.14177 | 1.5101
SINGLE OPN LIN 2292 360450-361580(1) | OPEN LINE FROM BUS 360450 [5HUNTSVL TN 161.00] TO BUS 361580 [5ONEIDA TN 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.5481
SINGLE OPN LIN 2293 360450-361618(1) | OPEN LINE FROM BUS 360450 [5HUNTSVL TN 161.00] TO BUS 361618 [5KELSEY RD 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.2414
SINGLE OPN LIN 2294 360454-361771(1) | OPEN LINE FROM BUS 360454 [5CARYVILL TN161.00] TO BUS 361771 [5ROYL BLU SS161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.3034
SINGLE OPN LIN 2295 360509-361246(1) | OPEN LINE FROM BUS 360509 [5W TOMPKINSV161.00] TO BUS 361246 [5W TOMPKINST161.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 2.1391 | 1 | 8.69
SINGLE OPN LIN 2296 361064-361246(1) | OPEN LINE FROM BUS 361064 [5TOMPKNSV TP161.00] TO BUS 361246 [5W TOMPKINST161.00] CKT 1 | TRUE | Met convergence tolerances | 3 | 0.14287 | 4.5826 | 2 | 32.27
SINGLE OPN LIN 2297 361064-361666(1) | OPEN LINE FROM BUS 361064 [5TOMPKNSV TP161.00] TO BUS 361666 [5BURKSVLTP 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.4564
SINGLE OPN LIN 2298 361113-361735(1) | OPEN LINE FROM BUS 361113 [5GLASGOW TP 161.00] TO BUS 361735 [5TRANSPARK 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.75058 | 29.597
SINGLE OPN LIN 2299 361114-361735(1) | OPEN LINE FROM BUS 361114 [5BRISTOW TAP161.00] TO BUS 361735 [5TRANSPARK 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.83061 | 31.5976
SINGLE OPN LIN 2300 361117-361246(1) | OPEN LINE FROM BUS 361117 [5TOMPKNSV PS161.00] TO BUS 361246 [5W TOMPKINST161.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 3.6633 | 1 | 23.58
SINGLE OPN LIN 2301 361265-361266(1) | OPEN LINE FROM BUS 361265 [5HARTSVLE TP161.00] TO BUS 361266 [5HARTSVLE TN161.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 1.5556 | 1 | 4.93
SINGLE OPN LIN 2302 361267-361558(1) | OPEN LINE FROM BUS 361267 [5WESTMORELD 161.00] TO BUS 361558 [5E SUMNER TP161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.3131
SINGLE OPN LIN 2303 361558-361559(1) | OPEN LINE FROM BUS 361558 [5E SUMNER TP161.00] TO BUS 361559 [5E SUMNER TN161.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 2.2499 | 1 | 13.7
SINGLE OPN LIN 2304 361579-361580(1) | OPEN LINE FROM BUS 361579 [5WINFIELD TN161.00] TO BUS 361580 [5ONEIDA TN 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.2215
SINGLE OPN LIN 2305 361603-361604(1) | OPEN LINE FROM BUS 361603 [5E GLASGOW T161.00] TO BUS 361604 [5E GLASGOW 161.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 4.5625 | 1 | 29.12
SINGLE OPN LIN 2306 361618-361619(1) | OPEN LINE FROM BUS 361618 [5KELSEY RD 161.00] TO BUS 361619 [5BYRDSTOWN 161.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 2.2308 | 1 | 11.11
SINGLE OPN LIN 2307 361666-361667(1) | OPEN LINE FROM BUS 361666 [5BURKSVLTP 161.00] TO BUS 361667 [5BURKESVL KY161.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 2.6494 | 1 | 14.07
SINGLE OPN LIN 2308 362058-362059(1) | OPEN LINE FROM BUS 362058 [2MOSS TN TAP69.000] TO BUS 362059 [2TOMPKINSVL 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.6023
SINGLE OPN LIN 2309 362058-362061(1) | OPEN LINE FROM BUS 362058 [2MOSS TN TAP69.000] TO BUS 362061 [2DALE HOLLOW69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.2138
SINGLE OPN LIN 2310 362058-363060(1) | OPEN LINE FROM BUS 362058 [2MOSS TN TAP69.000] TO BUS 363060 [2MOSS TN 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 1.1273 | 1 | 6.39
SINGLE OPN LIN 2311 362059-362060(1) | OPEN LINE FROM BUS 362059 [2TOMPKINSVL 69.000] TO BUS 362060 [2SUMMER SHAD69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.2747
SINGLE OPN LIN 2312 362060-362061(1) | OPEN LINE FROM BUS 362060 [2SUMMER SHAD69.000] TO BUS 362061 [2DALE HOLLOW69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.4091
SINGLE OPN LIN 2313 362061-364614(1) | OPEN LINE FROM BUS 362061 [2DALE HOLLOW69.000] TO BUS 364614 [1DALE HOL H113.800] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 2.314
SINGLE OPN LIN 2314 362061-364615(2) | OPEN LINE FROM BUS 362061 [2DALE HOLLOW69.000] TO BUS 364615 [1DALE HOL H213.800] CKT 2 | TRUE | Met convergence tolerances | 1 | 0.14287 | 2.314
SINGLE OPN LIN 2315 362061-364616(3) | OPEN LINE FROM BUS 362061 [2DALE HOLLOW69.000] TO BUS 364616 [1DALE HOL H313.800] CKT 3 | TRUE | Met convergence tolerances | 1 | 0.14287 | 2.314
SINGLE OPN TIE 2316 360112-361287(1) | OPEN LINE FROM BUS 360112 [5RUGBY TN 161.00] TO BUS 361287 [5JAMESTWN TN161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.9993
SINGLE OPN TIE 2319 360334-360607(1) | OPEN LINE FROM BUS 360334 [5SUMMER SHAD161.00] TO BUS 360607 [5S GLASGOW 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.0284
SINGLE OPN TIE 2320 360334-362060-362483(2) | OPEN LINE FROM BUS 360334 [5SUMMER SHAD161.00] TO BUS 362060 [2SUMMER SHAD69.000] TO BUS 362483 [1SUMMER SHAD13.200] CKT 2 | TRUE | Met convergence tolerances | 8 | 0.14287 | 2.2305 | 5 | 40.92
SINGLE OPN TIE 2321 360338-361553(1) | OPEN LINE FROM BUS 360338 [5SCOTTSVL KY161.00] TO BUS 361553 [5N SCOTTSVLE161.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 2.755 | 1 | 18.74
SINGLE OPN TIE 2322 360338-361621(1) | OPEN LINE FROM BUS 360338 [5SCOTTSVL KY161.00] TO BUS 361621 [5ALVATON TP 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.6628
SINGLE OPN TIE 2323 360342-361617(1) | OPEN LINE FROM BUS 360342 [5LIVINGST TN161.00] TO BUS 361617 [5MONROE TAP 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.7367
SINGLE OPN TIE 2324 360342-361731(1) | OPEN LINE FROM BUS 360342 [5LIVINGST TN161.00] TO BUS 361731 [5RICKMAN TAP161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.0741
SINGLE OPN TIE 2325 360352-360349(2) | OPEN LINE FROM BUS 360352 [5GALLATIN F1161.00] TO BUS 360349 [5LEBANON TN 161.00] CKT 2 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.4665
SINGLE OPN TIE 2326 360352-360382(1) | OPEN LINE FROM BUS 360352 [5GALLATIN F1161.00] TO BUS 360382 [5HOEGANAES 161.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 3.2199 | 1 | 39.7
SINGLE OPN TIE 2327 360352-360773(1) | OPEN LINE FROM BUS 360352 [5GALLATIN F1161.00] TO BUS 360773 [5WILSON #2 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.5767
SINGLE OPN TIE 2328 360352-361128(1) | OPEN LINE FROM BUS 360352 [5GALLATIN F1161.00] TO BUS 361128 [5LEBANON IPT161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.2981
SINGLE OPN TIE 2329 360352-361714(1) | OPEN LINE FROM BUS 360352 [5GALLATIN F1161.00] TO BUS 361714 [5GAL SCRB TP161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.406
SINGLE OPN TIE 2330 360352-361827(1) | OPEN LINE FROM BUS 360352 [5GALLATIN F1161.00] TO BUS 361827 [5W TROUSDALE161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.62083 | 25.7697
SINGLE OPN TIE 2331 360352-364121(1) | OPEN LINE FROM BUS 360352 [5GALLATIN F1161.00] TO BUS 364121 [1GALLATIN F124.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.41757 | 5.2449 | 1 | 15
SINGLE OPN TIE 2332 360352-364122(2) | OPEN LINE FROM BUS 360352 [5GALLATIN F1161.00] TO BUS 364122 [1GALLATIN F224.000] CKT 2 | TRUE | Met convergence tolerances | 1 | 0.41757 | 5.2449 | 1 | 15
SINGLE OPN TIE 2333 360352-364221-364222(T1) | OPEN LINE FROM BUS 360352 [5GALLATIN F1161.00] TO BUS 364221 [1GALLATIN T113.800] TO BUS 364222 [1GALLATIN T213.800] CKT T1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 1.3361
SINGLE OPN TIE 2334 360352-364223-364224(T2) | OPEN LINE FROM BUS 360352 [5GALLATIN F1161.00] TO BUS 364223 [1GALLATIN T313.800] TO BUS 364224 [1GALLATIN T413.800] CKT T2 | TRUE | Met convergence tolerances | 1 | 0.18084 | 2.3788
SINGLE OPN TIE 2335 360445-361542(1) | OPEN LINE FROM BUS 360445 [5BRAYTOWN TN161.00] TO BUS 361542 [5WINDROCK 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.42038 | 20.766
SINGLE OPN TIE 2337 360454-361330(1) | OPEN LINE FROM BUS 360454 [5CARYVILL TN161.00] TO BUS 361330 [5JACKSBRO TP161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.187
SINGLE OPN TIE 2341 361113-360607(1) | OPEN LINE FROM BUS 361113 [5GLASGOW TP 161.00] TO BUS 360607 [5S GLASGOW 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.64242 | 25.6035
SINGLE OPN TIE 2342 361114-360332(1) | OPEN LINE FROM BUS 361114 [5BRISTOW TAP161.00] TO BUS 360332 [5E BOWLGREEN161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.94816 | 36.0851
SINGLE OPN TIE 2343 361114-360335(1) | OPEN LINE FROM BUS 361114 [5BRISTOW TAP161.00] TO BUS 360335 [5BRISTOW KY 161.00] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.14287 | 3.5036 | 2 | 23.66
SINGLE OPN TIE 2344 361265-361827(1) | OPEN LINE FROM BUS 361265 [5HARTSVLE TP161.00] TO BUS 361827 [5W TROUSDALE161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.58802 | 24.8709
SINGLE OPN TIE 2345 361267-360530(1) | OPEN LINE FROM BUS 361267 [5WESTMORELD 161.00] TO BUS 360530 [5ANGELTOWN 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 3.6249
SINGLE OPN TIE 2348 361603-360607(1) | OPEN LINE FROM BUS 361603 [5E GLASGOW T161.00] TO BUS 360607 [5S GLASGOW 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.7734 | 30.6076
SINGLE OPN LIN 2352 253006-253027(1) | OPEN LINE FROM BUS 253006 [09BATH 345.00] TO BUS 253027 [09GREENE 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.20158 | 2.5955
SINGLE OPN LIN 2353 253013-253014(1) | OPEN LINE FROM BUS 253013 [09CLINTO 69.000] TO BUS 253014 [09CLINTO 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.778
SINGLE OPN LIN 2354 253013-253014(2) | OPEN LINE FROM BUS 253013 [09CLINTO 69.000] TO BUS 253014 [09CLINTO 345.00] CKT 2 | TRUE | Met convergence tolerances | 0 | 0.28605 | 2.6582
SINGLE OPN LIN 2355 253013-253094(1) | OPEN LINE FROM BUS 253013 [09CLINTO 69.000] TO BUS 253094 [09WILMNG 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14925 | 2.3706
SINGLE OPN LIN 2356 253013-253094(2) | OPEN LINE FROM BUS 253013 [09CLINTO 69.000] TO BUS 253094 [09WILMNG 69.000] CKT 2 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.1634
SINGLE OPN LIN 2357 253014-253027(1) | OPEN LINE FROM BUS 253014 [09CLINTO 345.00] TO BUS 253027 [09GREENE 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.22974 | 11.8047
SINGLE OPN LIN 2358 253026-253027(1) | OPEN LINE FROM BUS 253026 [09GREENE 138.00] TO BUS 253027 [09GREENE 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.34661 | 12.0713
SINGLE OPN LIN 2359 253026-253027(2) | OPEN LINE FROM BUS 253026 [09GREENE 138.00] TO BUS 253027 [09GREENE 345.00] CKT 2 | TRUE | Met convergence tolerances | 0 | 0.36198 | 12.6054
SINGLE OPN LIN 2360 253027-253079(1) | OPEN LINE FROM BUS 253027 [09GREENE 345.00] TO BUS 253079 [09SUGRCK 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.19066 | 2.8175
SINGLE OPN LIN 2361 253076-253077(1) | OPEN LINE FROM BUS 253076 [09STUART 138.00] TO BUS 253077 [09STUART 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.23193 | 2.39
SINGLE OPN LIN 2362 253077-253100(1) | OPEN LINE FROM BUS 253077 [09STUART 345.00] TO BUS 253100 [09ATLNTA 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.22783 | 12.2714
SINGLE OPN LIN 2363 253099-253100(1) | OPEN LINE FROM BUS 253099 [09ATLNTA 69.000] TO BUS 253100 [09ATLNTA 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.23094 | 2.1353
SINGLE OPN LIN 2364 253099-253181(1) | OPEN LINE FROM BUS 253099 [09ATLNTA 69.000] TO BUS 253181 [09NHOLLN 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.24041 | 3.3147
SINGLE OPN TIE 2366 253006-253005(1) | OPEN LINE FROM BUS 253006 [09BATH 345.00] TO BUS 253005 [09BATH 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.20013 | 7.7636
SINGLE OPN TIE 2367 253006-253005(2) | OPEN LINE FROM BUS 253006 [09BATH 345.00] TO BUS 253005 [09BATH 138.00] CKT 2 | TRUE | Met convergence tolerances | 0 | 0.20013 | 7.7636
SINGLE OPN TIE 2368 253006-253047(1) | OPEN LINE FROM BUS 253006 [09BATH 345.00] TO BUS 253047 [09MIAMI 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.54224 | 9.0694
SINGLE OPN TIE 2369 253014-253310(1) | OPEN LINE FROM BUS 253014 [09CLINTO 345.00] TO BUS 253310 [AC1-085 POI 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.29074 | 16.5027
SINGLE OPN TIE 2370 253026-238623(1) | OPEN LINE FROM BUS 253026 [09GREENE 138.00] TO BUS 238623 [02CLARK 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.15722 | 2.0233
SINGLE OPN TIE 2371 253026-253002(1) | OPEN LINE FROM BUS 253026 [09GREENE 138.00] TO BUS 253002 [09AIRWAY 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.15242 | 4.3739
SINGLE OPN TIE 2372 253026-253040(1) | OPEN LINE FROM BUS 253026 [09GREENE 138.00] TO BUS 253040 [09KNOLLW 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.2021 | 6.9656
SINGLE OPN TIE 2373 253026-253062(1) | OPEN LINE FROM BUS 253026 [09GREENE 138.00] TO BUS 253062 [09OVERL1 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.17585 | 6.558
SINGLE OPN TIE 2374 253026-253083(1) | OPEN LINE FROM BUS 253026 [09GREENE 138.00] TO BUS 253083 [09TREBEI 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 1.4601
SINGLE OPN TIE 2375 253026-253107(1) | OPEN LINE FROM BUS 253026 [09GREENE 138.00] TO BUS 253107 [09ALPHA 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 1.9921
SINGLE OPN TIE 2376 253027-253248(1) | OPEN LINE FROM BUS 253027 [09GREENE 345.00] TO BUS 253248 [09MDISON 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.874
SINGLE OPN TIE 2381 253077-253310(1) | OPEN LINE FROM BUS 253077 [09STUART 345.00] TO BUS 253310 [AC1-085 POI 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.18431 | 11.2707
SINGLE OPN TIE 2382 253077-253352(1) | OPEN LINE FROM BUS 253077 [09STUART 345.00] TO BUS 253352 [AB1-169 MAIN345.00] CKT 1 | TRUE | Met convergence tolerances | 7 | 0.79508 | 37.0725 | 2 | 19.2
SINGLE OPN TIE 2385 253079-253078(1) | OPEN LINE FROM BUS 253079 [09SUGRCK 345.00] TO BUS 253078 [09SUGRCK 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 3.0885
SINGLE OPN TIE 2386 253079-253078(2) | OPEN LINE FROM BUS 253079 [09SUGRCK 345.00] TO BUS 253078 [09SUGRCK 138.00] CKT 2 | TRUE | Met convergence tolerances | 0 | 0.14177 | 3.1887
SINGLE OPN TIE 2387 253094-253043(1) | OPEN LINE FROM BUS 253094 [09WILMNG 69.000] TO BUS 253043 [09MRTNSV 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.20727 | 6.7491
SINGLE OPN TIE 2388 253094-253115(1) | OPEN LINE FROM BUS 253094 [09WILMNG 69.000] TO BUS 253115 [09AIRPRK 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14502 | 3.8978
SINGLE OPN TIE 2389 253094-253131(1) | OPEN LINE FROM BUS 253094 [09WILMNG 69.000] TO BUS 253131 [09COL ST 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.78521 | 37.0978 | 1 | 31.894
SINGLE OPN TIE 2390 253094-253237(1) | OPEN LINE FROM BUS 253094 [09WILMNG 69.000] TO BUS 253237 [09WEBBRD 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.6012
SINGLE OPN TIE 2391 253099-253322(1) | OPEN LINE FROM BUS 253099 [09ATLNTA 69.000] TO BUS 253322 [AC1-069 MAIN69.000] CKT 1 | TRUE | Met convergence tolerances | 5 | 0.49323 | 22.683 | 1 | 0.119
SINGLE OPN TIE 2392 253099-253330(1) | OPEN LINE FROM BUS 253099 [09ATLNTA 69.000] TO BUS 253330 [AC1-068 MAIN69.000] CKT 1 | TRUE | Met convergence tolerances | 5 | 0.49323 | 22.683 | 1 | 0.119
SINGLE OPN TIE 2393 253099-253335(1) | OPEN LINE FROM BUS 253099 [09ATLNTA 69.000] TO BUS 253335 [AC1-165 MAIN69.000] CKT 1 | TRUE | Met convergence tolerances | 5 | 0.4585 | 22.3178 | 1 | 0.119
SINGLE OPN TIE 2394 253099-253340(1) | OPEN LINE FROM BUS 253099 [09ATLNTA 69.000] TO BUS 253340 [AC1-166 MAIN69.000] CKT 1 | TRUE | Met convergence tolerances | 5 | 0.4585 | 22.3178 | 1 | 0.119
SINGLE OPN TIE 2395 253100-245769(1) | OPEN LINE FROM BUS 253100 [09ATLNTA 345.00] TO BUS 245769 [05ADKINS 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.24986 | 13.4884
SINGLE OPN TIE 2396 253181-253201(1) | OPEN LINE FROM BUS 253181 [09NHOLLN 69.000] TO BUS 253201 [09ROBINS 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.21995 | 3.1103
SINGLE OPN LIN 2397 248005-248013(1) | OPEN LINE FROM BUS 248005 [06KYGER 345.00] TO BUS 248013 [06PIERCE 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.29024 | 4.0967
SINGLE OPN TIE 2398 248005-242528(1) | OPEN LINE FROM BUS 248005 [06KYGER 345.00] TO BUS 242528 [05SPORN 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.63806 | 31.9911
SINGLE OPN TIE 2401 248005-248027-248026(1) | OPEN LINE FROM BUS 248005 [06KYGER 345.00] TO BUS 248027 [06KYGER 1LP 15.500] TO BUS 248026 [06KYGER 1HP 15.500] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.84076 | 34.2296 | 2 | 18
SINGLE OPN TIE 2402 248005-248029-248028(1) | OPEN LINE FROM BUS 248005 [06KYGER 345.00] TO BUS 248029 [06KYGER 2LP 15.500] TO BUS 248028 [06KYGER 2HP 15.500] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.22322 | 7.3305 | 2 | 18
SINGLE OPN TIE 2403 248005-248031-248030(1) | OPEN LINE FROM BUS 248005 [06KYGER 345.00] TO BUS 248031 [06KYGER 3LP 15.500] TO BUS 248030 [06KYGER 3HP 15.500] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.84661 | 34.3594 | 2 | 18
SINGLE OPN TIE 2404 248005-248033-248032(1) | OPEN LINE FROM BUS 248005 [06KYGER 345.00] TO BUS 248033 [06KYGER 4LP 15.500] TO BUS 248032 [06KYGER 4HP 15.500] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.84859 | 34.3552 | 2 | 18
SINGLE OPN TIE 2405 248005-248035-248034(1) | OPEN LINE FROM BUS 248005 [06KYGER 345.00] TO BUS 248035 [06KYGER 5LP 15.500] TO BUS 248034 [06KYGER 5HP 15.500] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.84574 | 34.3917 | 2 | 18
SINGLE OPN TIE 2406 248009-248008(SR) | OPEN LINE FROM BUS 248009 [06CLIFTY 138.00] TO BUS 248008 [06CLIFTX 138.00] CKT SR | TRUE | Met convergence tolerances | 0 | 0.38942 | 18.4828
SINGLE OPN TIE 2411 248013-248000(1) | OPEN LINE FROM BUS 248013 [06PIERCE 345.00] TO BUS 248000 [06CLIFTY 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.1465 | 7.3177
SINGLE OPN TIE 2412 248013-248000(2) | OPEN LINE FROM BUS 248013 [06PIERCE 345.00] TO BUS 248000 [06CLIFTY 345.00] CKT 2 | TRUE | Met convergence tolerances | 0 | 0.1465 | 7.3177
SINGLE OPN TIE 2413 248013-248001(1) | OPEN LINE FROM BUS 248013 [06PIERCE 345.00] TO BUS 248001 [06DEARB1 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.26786 | 3.0292
SINGLE OPN TIE 2416 248013-250086(17) | OPEN LINE FROM BUS 248013 [06PIERCE 345.00] TO BUS 250086 [08PIERCE 138.00] CKT 17 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.3093
SINGLE OPN TIE 2417 248013-250143(18) | OPEN LINE FROM BUS 248013 [06PIERCE 345.00] TO BUS 250143 [08PRCE18 138.00] CKT 18 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.5559
SINGLE OPN TIE 2418 249736-249754(1) | OPEN LINE FROM BUS 249736 [08GRDALE 138.00] TO BUS 249754 [08HEHIDN 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.58453 | 20.5382

## Summary
ACCC SOLUTION SUMMARY
2022 SUMMER 50/50 2021 TEP R20200403
LG&E AND KU SERVICES COMPANY THU APR 02 14:12:44 2020
ACCC output file = H:\Transmission planning\2022 Gas Study\Alt 3A\2023S Alt3 212MW_Cooper1&2 - Ngen_2032S 22Series_R2_Cooper1&2-Ngen_Gas Alt 3 212MW.sav.acc
Saved Case file = H:\Transmission planning\2022 Gas Study\Alt 3A\2023S Alt3 212MW_Cooper1&2 - Ngen_2032S 22Series_R2_Cooper1&2-Ngen_Gas Alt 3 212MW.sav.sav
DFAX file = H:\Transmission planning\2022 Gas Study\Alt 3A\2023S Alt3 212MW_Cooper1&2 - Ngen_2032S 22Series_R2_Cooper1&2-Ngen_Gas Alt 3 212MW.sav.dfx
Subsystem file = H:\Transmission planning\2022 Gas Study\2022 series_sub_EKPC-LGEE.sub
Monitored Element file = H:\Transmission planning\2022 Gas Study\2022 series_mon_EKPC-LGEE.mon
Contingency Description file = H:\Transmission planning\2022 Gas Study\Alt 3A\2022 series_EKPC&LGE contingency list_2032S_Alt3.con
Number of Ratings = 12
Number of Monitored Branches = 1871
Number of Monitored Interfaces = 0
Number of Contingencies+Base Case = 2753
Number of Voltage Monitored Buses = 1575
Number of Voltage Monitored Records = 3
Number of Voltage Monitored Bus Records = 1575
Number of Voltage Monitored Nodes = 0
Number of Voltage Monitored Node Records = 0
Number of Voltage Monitored All Node Records = 0
Number of Monitored SWD = 0
Number of Buses in the case = 95955
Number of Loads shed due to post contingency = 8
Number of Loads shed due to tripping = 8
Number of Loads shed due to corrective actions = 8
ACCC Results stored in the file are in 'Bus Number Output' form
ACCC Results stored in the file are from 'ACCC' analysis
Number of Areas for which results are stored = 134
Number of Zones for which results are stored = 746
Number of Owners for which results are stored = 345
Number of Voltage levels for which results are stored = 236
Rating Description
Name | DESCRIPTION
RATE1 | RATING SET 1
RATE2 | RATING SET 2
RATE3 | RATING SET 3
RATE4 | RATING SET 4
RATE5 | RATING SET 5
RATE6 | RATING SET 6
RATE7 | RATING SET 7
RATE8 | RATING SET 8
RATE9 | RATING SET 9
RATE10 | RATING SET 10
RATE11 | RATING SET 11
RATE12 | RATING SET 12
Monitored Lines
MON# | LABEL | RATE1 | RATE2 | RATE3 | RATE4 | RATE5 | RATE6 | RATE7 | RATE8 | RATE9 | RATE10 | RATE11 | RATE12
1 | 324010 7TRIMBL REAC345.00 324114 7TRIMBLE CO 345.00 1 | 1134 | 1451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 324021 7BLUEGRASS12345.00 324103 7BUCKNER 345.00 Z1 | 478 | 478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 324022 7BLUEGRASS 3345.00 324103 7BUCKNER 345.00 Z1 | 239 | 239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 324029 7TRIMBLE CTA345.00 324030 7TRIMBLE CTB345.00 1 | 1134 | 1195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 324029 7TRIMBLE CTA345.00 324114 7TRIMBLE CO 345.00 1 | 1134 | 1195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 324030 7TRIMBLE CTB345.00 324114 7TRIMBLE CO 345.00 1 | 1134 | 1195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 324047 4BLACKBRANCH138.00 325055 4RHUDES TP 138.00 1 | 208 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 324048 2PARKWY MINE69.000 324437 2BEVIER KU 69.000 1 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 324048 2PARKWY MINE69.000 324584 2INDIAN HILL69.000 1 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 324049 2OXFORD COAL69.000 324572 2HILLSIDE 69.000 1 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 324049 2OXFORD COAL69.000 324745 2STRINGTOWN 69.000 1 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 324050 2JONESVILLE 69.000 324362 2RIO 69.000 1 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 324050 2JONESVILLE 69.000 324447 2BONNIE KU 69.000 1 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | 324051 4MATANZAS 138.00 324173 5MATANZAS 161.00 1 | 200 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | 324051 4MATANZAS 138.00 324173 5MATANZAS 161.00 2 | 200 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | 324051 4MATANZAS 138.00 324255 4GREEN RIVER138.00 1 | 166 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | 324051 4MATANZAS 138.00 324291 4OHIO COUNTY138.00 1 | 166 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | 324058 2BEAVER DAM 69.000 324059 2BEAVER DM N69.000 1 | 13 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | 324058 2BEAVER DAM 69.000 324667 2OHIO COUNTY69.000 1 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | 324061 2BORG-WARNER69.000 324079 2HANSON 69.000 1 | 18 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | 324061 2BORG-WARNER69.000 324873 2HANSON JCT 69.000 1 | 67 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | 324065 2DAWSON 764 69.000 324843 2DAWSON IND 69.000 1 | 18 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | 324067 2EDDYV PRIS 69.000 324512 2EDDYV PR TP69.000 1 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | 324068 2E CAMPBELVL69.000 324349 2CAMPBELVIL269.000 1 | 54 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | 324069 2PAYNES ML 69.000 324687 2PISGAH 69.000 1 | 80 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | 324069 2PAYNES ML 69.000 324763 2VERSAILLES 69.000 1 | 70 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | 324075 2GRAHAM 69.000 324702 2RIVER QUEEN69.000 1 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | 324077 2GREENVILE W69.000 326594 2GREENVL 12 69.000 1 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | 324081 2MADSNV GE 69.000 326587 2MADSNV W TP69.000 1 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | 324082 2PARIS 4 69.000 324197 2DETROIT HAR69.000 1 | 25 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | 324082 2PARIS 4 69.000 324476 2CMC TAP 69.000 1 | 33 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | 324082 2PARIS 4 69.000 325061 2CMC 69.000 1 | 67 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | 324083 2MADSNV W 69.000 326587 2MADSNV W TP69.000 1 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | 324085 2MARION 4 69.000 324629 2MARION KU 69.000 1 | 18 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
35 | 324086 2MORGANF IND69.000 324096 2PEA WSH TAP69.000 1 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36 | 324086 2MORGANF IND69.000 324671 2OVERLAD S T69.000 1 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | 324087 2MT VERN SO 69.000 324913 2MT VERNON 69.000 1 | 70 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
38 | 324087 2MT VERN SO 69.000 324927 2PINE HILL T69.000 1 | 52 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
39 | 324090 2OVERLAND NO69.000 324095 2UNIONTOWN 69.000 1 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
40 | 324091 2OVERLAND SO69.000 324096 2PEA WSH TAP69.000 1 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
41 | 324092 2PEABODY RVR69.000 324702 2RIVER QUEEN69.000 1 | 18 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
42 | 324093 2SPEN CHEMIC69.000 324711 2SPEN CHEM T69.000 1 | 18 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
43 | 324094 2TURTLE CK T69.000 324562 2HARLAN KU 69.000 1 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
44 | 324094 2TURTLE CK T69.000 324761 2VERDA 69.000 1 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
45 | 324094 2TURTLE CK T69.000 325045 2TURTLE CRK 69.000 1 | 32 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
46 | 324095 2UNIONTOWN 69.000 326572 2RIVRVW COAL69.000 1 | 67 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
47 | 324096 2PEA WSH TAP69.000 324097 2PEAB WASH 69.000 1 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | 324098 2WEST VACO 69.000 324779 2WICKLIFFE 69.000 1 | 67 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
49 | 324100 7ALCALDE 345.00 324102 7BROWN NORTH345.00 1 | 956 | 956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 | 324100 7ALCALDE 345.00 324112 7PINEVILLE 345.00 1 | 956 | 956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51 | 324100 7ALCALDE 345.00 324130 5ALCALDE 161.00 1 | 316 | 405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
52 | 324101 7BLUE LICK 345.00 324107 7MIDDLETOWN 345.00 1 | 867 | 1125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
53 | 324101 7BLUE LICK 345.00 324108 7MILL CREEK 345.00 1 | 867 | 1125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
54 | 324101 7BLUE LICK 345.00 324134 5BLUE LICK 161.00 1 | 450 | 518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
55 | 324101 7BLUE LICK 345.00 324212 4BLUE LICK 138.00 1 | 375 | 478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
56 | 324102 7BROWN NORTH345.00 324106 7HARDIN CO 345.00 1 | 1134 | 1355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
57 | 324102 7BROWN NORTH345.00 324116 7W LEXINGTON345.00 1 | 956 | 956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58 | 324102 7BROWN NORTH345.00 325074 7W GARRARDKU345.00 1 | 1134 | 1195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
59 | 324102 7BROWN NORTH345.00 325956 4BROWN N 2 138.00 1 | 448 | 515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
60 | 324102 7BROWN NORTH345.00 325957 4BROWN N 1 138.00 2 | 450 | 515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
61 | 324103 7BUCKNER 345.00 324107 7MIDDLETOWN 345.00 1 | 1134 | 1370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
62 | 324103 7BUCKNER 345.00 324114 7TRIMBLE CO 345.00 1 | 1134 | 1195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
63 | 324104 7DAVIESS 345.00 324106 7HARDIN CO 345.00 1 | 1134 | 1195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
64 | 324105 7GHENT 345.00 324115 7W FRANKFORT345.00 1 | 701 | 822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
65 | 324105 7GHENT 345.00 324116 7W LEXINGTON345.00 1 | 1134 | 1370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
66 | 324105 7GHENT 345.00 324253 4GHENT 138.00 1 | 448 | 515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
67 | 324105 7GHENT 345.00 324253 4GHENT 138.00 2 | 450 | 518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
68 | 324105 7GHENT 345.00 324565 7NAS TAP 345.00 1 | 814 | 814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
69 | 324105 7GHENT 345.00 326536 7GALLATIN 345.00 1 | 1134 | 1349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | 324106 7HARDIN CO 345.00 324261 4HARDIN CO 138.00 1 | 448 | 515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
71 | 324106 7HARDIN CO 345.00 324261 4HARDIN CO 138.00 2 | 450 | 515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
72 | 324106 7HARDIN CO 345.00 325073 7REDMON RD 345.00 1 | 1134 | 1370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73 | 324107 7MIDDLETOWN 345.00 324108 7MILL CREEK 345.00 1 | 867 | 867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
74 | 324107 7MIDDLETOWN 345.00 324114 7TRIMBLE CO 345.00 1 | 1134 | 1195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
75 | 324107 7MIDDLETOWN 345.00 324281 4MIDDLETOWN 138.00 3 | 448 | 515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
76 | 324107 7MIDDLETOWN 345.00 324281 4MIDDLETOWN 138.00 4 | 448 | 515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
77 | 324107 7MIDDLETOWN 345.00 324281 4MIDDLETOWN 138.00 5 | 448 | 515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78 | 324107 7MIDDLETOWN 345.00 324281 4MIDDLETOWN 138.00 7 | 446 | 518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
79 | 324108 7MILL CREEK 345.00 325073 7REDMON RD 345.00 1 | 1134 | 1370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
80 | 324108 7MILL CREEK 345.00 326001 7CANE RUN TP345.00 1 | 936 | 936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
81 | 324109 7NAS 345.00 324565 7NAS TAP 345.00 1 | 359 | 359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
82 | 324110 7NORTHSIDE 345.00 324289 4NORTHSIDE 138.00 1 | 448 | 478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
83 | 324110 7NORTHSIDE 345.00 326569 7KENZIG ROAD345.00 1 | 1134 | 1146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
84 | 324111 7PADDYS WEST345.00 324294 4PADDYS WEST138.00 1 | 390 | 478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85 | 324111 7PADDYS WEST345.00 326001 7CANE RUN TP345.00 1 | 956 | 956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
86 | 324111 7PADDYS WEST345.00 326569 7KENZIG ROAD345.00 1 | 956 | 956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
87 | 324112 7PINEVILLE 345.00 324167 5PINEVILLE 2161.00 1 | 560 | 644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
88 | 324112 7PINEVILLE 345.00 325074 7W GARRARDKU345.00 1 | 1134 | 1195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
89 | 324114 7TRIMBLE CO 345.00 324314 4TRIMBLE CO 138.00 5 | 224 | 258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90 | 324114 7TRIMBLE CO 345.00 324314 4TRIMBLE CO 138.00 6 | 224 | 258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
91 | 324115 7W FRANKFORT345.00 324319 4W FRANKFORT138.00 1 | 450 | 518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
92 | 324116 7W LEXINGTON345.00 324320 4W LEXINGTON138.00 1 | 448 | 515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
93 | 324124 2CENTRTOWN S69.000 326564 2LEW BREC 69.000 1 | 7 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
94 | 324130 5ALCALDE 161.00 324141 5ELIHU 161.00 1 | 321 | 321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
95 | 324130 5ALCALDE 161.00 324143 5FARLEY 161.00 1 | 194 | 194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
96 | 324131 5ARNOLD 161.00 324139 5DORCHESTER 161.00 1 | 87 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97 | 324131 5ARNOLD 161.00 324146 5HARLAN WYE 161.00 1 | 139 | 139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
98 | 324131 5ARNOLD 161.00 324148 5WOOTON TAP 161.00 1 | 194 | 194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
99 | 324131 5ARNOLD 161.00 324416 2ARNOLD 69.000 1 | 56 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
100 | 324132 5ARTEMUS TAP161.00 324133 5ARTEMUS 161.00 1 | 96 | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
101 | 324132 5ARTEMUS TAP161.00 324143 5FARLEY 161.00 1 | 153 | 153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
102 | 324132 5ARTEMUS TAP161.00 324156 5PINEVILE SW161.00 1 | 164 | 192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
103 | 324133 5ARTEMUS 161.00 324417 2ARTEMUS 69.000 1 | 56 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
104 | 324134 5BLUE LICK 161.00 326975 5CEDAR GRV 161.00 1 | 265 | 338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
105 | 324135 5CORYDON TAP161.00 324136 5CORYDON 161.00 1 | 141 | 141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
106 | 324135 5CORYDON TAP161.00 324144 5GREEN RIVER161.00 1 | 153 | 153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
107 | 324135 5CORYDON TAP161.00 324153 5MORGANFIELD161.00 1 | 141 | 141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
108 | 324136 5CORYDON 161.00 324484 2CORYDON 69.000 1 | 72 | 101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
109 | 324137 5CRITTENDEN 161.00 324151 5LIVNGSTN CO161.00 1 | 194 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
110 | 324137 5CRITTENDEN 161.00 324153 5MORGANFIELD161.00 1 | 194 | 223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
111 | 324137 5CRITTENDEN 161.00 324486 2CRITTENDEN 69.000 1 | 94 | 119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
112 | 324138 5DELVINTA 161.00 324148 5WOOTON TAP 161.00 1 | 194 | 194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
113 | 324138 5DELVINTA 161.00 324165 5W IRVINE T 161.00 1 | 174 | 174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
114 | 324139 5DORCHESTER 161.00 324149 5IMBODEN 161.00 1 | 157 | 157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
115 | 324139 5DORCHESTER 161.00 324503 2DORCHESTER 69.000 1 | 93 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
116 | 324139 5DORCHESTER 161.00 324503 2DORCHESTER 69.000 2 | 93 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
117 | 324140 5EARLINGTN N161.00 324160 5RIVER QN T 161.00 1 | 194 | 223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
118 | 324140 5EARLINGTN N161.00 324164 5WALKER 161.00 1 | 139 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
119 | 324140 5EARLINGTN N161.00 324506 2EARLINGTN N69.000 1 | 135 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
120 | 324140 5EARLINGTN N161.00 325079 5N PRINCETON161.00 1 | 194 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
121 | 324141 5ELIHU 161.00 324514 2ELIHU 69.000 1 | 93 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
122 | 324141 5ELIHU 161.00 324514 2ELIHU 69.000 2 | 93 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
123 | 324143 5FARLEY 161.00 324527 2FARLEY KU 69.000 1 | 140 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
124 | 324144 5GREEN RIVER161.00 324160 5RIVER QN T 161.00 1 | 194 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
125 | 324144 5GREEN RIVER161.00 324255 4GREEN RIVER138.00 1 | 100 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
126 | 324144 5GREEN RIVER161.00 324255 4GREEN RIVER138.00 2 | 100 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
127 | 324144 5GREEN RIVER161.00 324255 4GREEN RIVER138.00 3 | 112 | 129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
128 | 324145 5GRAHAMVILLE161.00 324171 5GRAHMVILE 1161.00 1 | 316 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
129 | 324145 5GRAHAMVILLE161.00 324172 5GRAHMVILE 2161.00 1 | 319 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
130 | 324145 5GRAHAMVILLE161.00 324553 2GRAHAMVILLE69.000 1 | 70 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
131 | 324145 5GRAHAMVILLE161.00 325069 5SONG SP TP 161.00 1 | 114 | 114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
132 | 324145 5GRAHAMVILLE161.00 325077 5COLEMAN TAP161.00 1 | 316 | 405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
133 | 324146 5HARLAN WYE 161.00 324147 5HOWARDS BR 161.00 1 | 175 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
134 | 324146 5HARLAN WYE 161.00 324155 5PINEVILLE 1161.00 1 | 157 | 157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
135 | 324146 5HARLAN WYE 161.00 324157 5POCKET N 161.00 1 | 167 | 167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
136 | 324146 5HARLAN WYE 161.00 324564 2HARLAN WYE 69.000 1 | 93 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
137 | 324147 5HOWARDS BR 161.00 324155 5PINEVILLE 1161.00 1 | 243 | 243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
138 | 324149 5IMBODEN 161.00 324157 5POCKET N 161.00 1 | 204 | 204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
139 | 324149 5IMBODEN 161.00 324583 2IMBODEN 69.000 1 | 139 | 143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
140 | 324150 5LEBANON JCT161.00 324154 5PADDYS RUN 161.00 1 | 146 | 146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
141 | 324151 5LIVNGSTN CO161.00 324161 5S PADUCAH 161.00 1 | 194 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
142 | 324151 5LIVNGSTN CO161.00 325028 5ASHWD SL TP161.00 1 | 194 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
143 | 324152 5LAKE REBA T161.00 324165 5W IRVINE T 161.00 1 | 167 | 194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
144 | 324152 5LAKE REBA T161.00 324276 4LAKE REBA T138.00 1 | 187 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
145 | 324153 5MORGANFIELD161.00 324645 2MORGANFIELD69.000 1 | 94 | 119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
146 | 324154 5PADDYS RUN 161.00 324295 4PADDYS RUN 138.00 1 | 187 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
147 | 324155 5PINEVILLE 1161.00 324156 5PINEVILE SW161.00 1 | 219 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
148 | 324155 5PINEVILLE 1161.00 324167 5PINEVILLE 2161.00 Z1 | 545 | 558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
149 | 324155 5PINEVILLE 1161.00 324686 2PINEVILLE 69.000 1 | 140 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
150 | 324157 5POCKET N 161.00 324158 5POCKET 161.00 1 | 194 | 243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
151 | 324158 5POCKET 161.00 324689 2POCKET 69.000 1 | 187 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
152 | 324159 5RIVER QUEEN161.00 324160 5RIVER QN T 161.00 1 | 164 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
153 | 324159 5RIVER QUEEN161.00 324702 2RIVER QUEEN69.000 1 | 94 | 119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154 | 324161 5S PADUCAH 161.00 324712 2SO PADUCAH 69.000 1 | 50 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155 | 324161 5S PADUCAH 161.00 325078 5PADUCAH PRI161.00 1 | 194 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156 | 324163 5WEST IRVINE161.00 324165 5W IRVINE T 161.00 1 | 194 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
157 | 324163 5WEST IRVINE161.00 324767 2WEST IRVINE69.000 1 | 56 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
158 | 324164 5WALKER 161.00 324769 2WALKER KU 69.000 1 | 112 | 129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
159 | 324166 5WICKLIFFE 161.00 324779 2WICKLIFFE 69.000 1 | 93 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
160 | 324166 5WICKLIFFE 161.00 325069 5SONG SP TP 161.00 1 | 114 | 114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
161 | 324167 5PINEVILLE 2161.00 324686 2PINEVILLE 69.000 2 | 140 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
162 | 324170 1KNOB CRK 34.500 324268 4KNOB CREEK 138.00 1 | 999 | 999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
163 | 324191 2LEBANON E T69.000 324603 2LEBANON CIT69.000 1 | 52 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
164 | 324191 2LEBANON E T69.000 324606 2LEBANON 69.000 1 | 67 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
165 | 324192 4DAYTON-WALT138.00 324240 4DAY-WALT TP138.00 1 | 36 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
166 | 324193 4FLEMINGB KU138.00 324251 4FLEMNB KU T138.00 1 | 32 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
167 | 324195 2AUGUSTA 69.000 324722 2SHARON KU 69.000 1 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
168 | 324196 2BOONESB PRK69.000 324224 2RED HOUSE 69.000 1 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
169 | 324196 2BOONESB PRK69.000 324449 2BOONSBORO N69.000 1 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
170 | 324198 2HUNT BOTTOM69.000 324878 2HUNT BTM TP69.000 1 | 7 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
171 | 324199 2OWENTON 69.000 324252 2SCHOLLS 69.000 1 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
172 | 324200 4PLSUR RDG T138.00 324205 4ASHBOTTOM 138.00 1 | 240 | 306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
173 | 324200 4PLSUR RDG T138.00 324237 4CANE RUN SW138.00 1 | 285 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
174 | 324200 4PLSUR RDG T138.00 324299 4PLEASUR RDG138.00 1 | 266 | 266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | 324201 4ADAMS 138.00 324305 4SCOTT CO 138.00 1 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | 324201 4ADAMS 138.00 324313 4TOYOTA S 138.00 1 | 104 | 131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
177 | 324201 4ADAMS 138.00 324315 4TYRONE 138.00 1 | 140 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
178 | 324201 4ADAMS 138.00 324335 4INNOVATION 138.00 1 | 140 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
179 | 324201 4ADAMS 138.00 324405 2ADAMS 69.000 1 | 93 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
180 | 324201 4ADAMS 138.00 324405 2ADAMS 69.000 2 | 93 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
181 | 324202 4ALGONQUIN 138.00 324241 4DIXIE 138.00 1 | 347 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
182 | 324202 4ALGONQUIN 138.00 324408 2ALGONQUIN 69.000 1 | 120 | 153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
183 | 324203 4AMERICAN AV138.00 324258 4HAEFLING 138.00 1 | 203 | 259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
184 | 324203 4AMERICAN AV138.00 324301 4REYNOLDS 138.00 1 | 203 | 203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
185 | 324203 4AMERICAN AV138.00 324409 2AMERICAN AV69.000 1 | 120 | 153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
186 | 324204 4APPLIANC PK138.00 324205 4ASHBOTTOM 138.00 1 | 187 | 208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
187 | 324204 4APPLIANC PK138.00 324243 4ETHEL 138.00 1 | 287 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
188 | 324204 4APPLIANC PK138.00 324281 4MIDDLETOWN 138.00 1 | 187 | 208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
189 | 324205 4ASHBOTTOM 138.00 324237 4CANE RUN SW138.00 1 | 285 | 294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
190 | 324205 4ASHBOTTOM 138.00 324257 4GRADE LANE 138.00 1 | 347 | 430 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
191 | 324205 4ASHBOTTOM 138.00 324279 4MANSLICK 138.00 1 | 187 | 203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
192 | 324205 4ASHBOTTOM 138.00 324419 2ASHBOT WEST69.000 1 | 94 | 119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
193 | 324205 4ASHBOTTOM 138.00 325023 2ASHBOT EAST69.000 2 | 94 | 119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
194 | 324206 4ASHBY 138.00 324284 4MILL CREEK 138.00 1 | 266 | 266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
195 | 324206 4ASHBY 138.00 324299 4PLEASUR RDG138.00 1 | 222 | 222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
196 | 324207 4BARDSTOWN 138.00 324218 4BROWN CT 138.00 1 | 187 | 208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
197 | 324207 4BARDSTOWN 138.00 324288 4NELSON CO 138.00 1 | 119 | 119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
198 | 324207 4BARDSTOWN 138.00 324426 2BARDSTOWN 69.000 1 | 140 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
199 | 324208 4BEARGRASS 138.00 324265 4JEFFRSONV T138.00 1 | 239 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
200 | 324208 4BEARGRASS 138.00 324277 4LYNDON SO 138.00 1 | 200 | 249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
201 | 324208 4BEARGRASS 138.00 324289 4NORTHSIDE 138.00 1 | 239 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
202 | 324208 4BEARGRASS 138.00 324298 4PLAINVIEW T138.00 1 | 203 | 249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
203 | 324208 4BEARGRASS 138.00 324321 4WATERSIDE 138.00 1 | 203 | 203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
204 | 324208 4BEARGRASS 138.00 324321 4WATERSIDE 138.00 2 | 203 | 203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
205 | 324208 4BEARGRASS 138.00 324429 2BEARGRASS 69.000 1 | 173 | 213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
206 | 324209 4BG PARKWAY 138.00 324263 4HURSTBORNE 138.00 1 | 266 | 266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
207 | 324210 4BAKER LANE 138.00 324262 4HIGBY MILL 138.00 1 | 187 | 237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
208 | 324210 4BAKER LANE 138.00 324334 4BROWN N 2-R138.00 1 | 208 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
209 | 324211 4BLACKWELL 138.00 324221 4BUTLER 138.00 1 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
210 | 324211 4BLACKWELL 138.00 324253 4GHENT 138.00 1 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
211 | 324212 4BLUE LICK 138.00 324285 4MUD LANE 138.00 1 | 271 | 329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
212 | 324212 4BLUE LICK 138.00 324443 2BLUE LICK 69.000 1 | 83 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
213 | 324213 4BONNIEVILLE138.00 324270 4LEBANON WES138.00 1 | 83 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
214 | 324213 4BONNIEVILLE138.00 324447 2BONNIE KU 69.000 1 | 33 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
215 | 324213 4BONNIEVILLE138.00 324800 4MERE TVA 138.00 1 | 121 | 121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
216 | 324214 4BRECKNRIDGE138.00 324243 4ETHEL 138.00 1 | 266 | 266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
217 | 324214 4BRECKNRIDGE138.00 324263 4HURSTBORNE 138.00 1 | 266 | 266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
218 | 324214 4BRECKNRIDGE138.00 324451 2BRECKNRIDGE69.000 1 | 112 | 129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
219 | 324215 4BRIDGPOR HE138.00 324237 4CANE RUN SW138.00 1 | 285 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220 | 324215 4BRIDGPOR HE138.00 324284 4MILL CREEK 138.00 1 | 347 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
221 | 324217 4BROWN PLANT138.00 324219 4BROWN T1 138.00 1 | 416 | 529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
222 | 324217 4BROWN PLANT138.00 324220 4BROWN T2 138.00 1 | 416 | 529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
223 | 324217 4BROWN PLANT138.00 324239 4DANVILE N T138.00 1 | 227 | 227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
224 | 324217 4BROWN PLANT138.00 324248 4FAWKES KU 138.00 1 | 166 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
225 | 324217 4BROWN PLANT138.00 324318 4WEST CLIFF 138.00 1 | 227 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
226 | 324217 4BROWN PLANT138.00 324318 4WEST CLIFF 138.00 2 | 227 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
227 | 324218 4BROWN CT 138.00 324219 4BROWN T1 138.00 1 | 454 | 580 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
228 | 324218 4BROWN CT 138.00 324220 4BROWN T2 138.00 1 | 454 | 580 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
229 | 324218 4BROWN CT 138.00 325957 4BROWN N 1 138.00 1 | 454 | 580 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
230 | 324219 4BROWN T1 138.00 325957 4BROWN N 1 138.00 1 | 454 | 580 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
231 | 324220 4BROWN T2 138.00 325956 4BROWN N 2 138.00 1 | 454 | 580 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
232 | 324221 4BUTLER 138.00 324225 4CARNTOWN TP138.00 1 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
233 | 324222 4CAMPGROUND 138.00 324237 4CANE RUN SW138.00 1 | 285 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
234 | 324222 4CAMPGROUND 138.00 324295 4PADDYS RUN 138.00 1 | 347 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
235 | 324223 4CANAL 138.00 324294 4PADDYS WEST138.00 1 | 200 | 254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
236 | 324223 4CANAL 138.00 324321 4WATERSIDE 138.00 1 | 200 | 208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
237 | 324223 4CANAL 138.00 324462 2CANAL 69.000 1 | 90 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
238 | 324225 4CARNTOWN TP138.00 324226 4CARNTOWN 138.00 1 | 136 | 171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
239 | 324225 4CARNTOWN TP138.00 324267 4KENTON 138.00 1 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
240 | 324226 4CARNTOWN 138.00 324463 2CARNTOWN 69.000 1 | 50 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
241 | 324227 4CARROLLTON 138.00 324274 4LOCKPORT 138.00 1 | 140 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
242 | 324227 4CARROLLTON 138.00 324466 2CARROLLTON 69.000 1 | 93 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
243 | 324227 4CARROLLTON 138.00 324466 2CARROLLTON 69.000 2 | 93 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
244 | 324227 4CARROLLTON 138.00 326512 4AIRGAS 138.00 1 | 208 | 208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
245 | 324228 4CENTERFIELD138.00 324281 4MIDDLETOWN 138.00 1 | 200 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
246 | 324228 4CENTERFIELD138.00 324469 2CENTERFIELD69.000 1 | 133 | 161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
247 | 324228 4CENTERFIELD138.00 326520 4TRIMBLE TR9138.00 1 | 200 | 254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
248 | 324229 4CLARK CO 138.00 324236 4RICHMND NO 138.00 1 | 136 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
249 | 324229 4CLARK CO 138.00 324310 4SPENCER RD 138.00 1 | 121 | 121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
250 | 324229 4CLARK CO 138.00 324472 2CLARK CO 69.000 1 | 93 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
251 | 324230 4CLAYS MILL 138.00 324262 4HIGBY MILL 138.00 1 | 187 | 237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
252 | 324230 4CLAYS MILL 138.00 325957 4BROWN N 1 138.00 1 | 208 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
253 | 324231 4CLOVERPORT 138.00 324256 4GR RVR STL 138.00 1 | 187 | 198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
254 | 324231 4CLOVERPORT 138.00 324260 4HARDINSBURG138.00 1 | 175 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
255 | 324231 4CLOVERPORT 138.00 325132 4GREENSOL TP138.00 1 | 134 | 134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
256 | 324232 4CANE RN 11A138.00 326574 4CR11 TAP 138.00 1 | 19 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
257 | 324236 4RICHMND NO 138.00 324248 4FAWKES KU 138.00 1 | 136 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
258 | 324237 4CANE RUN SW138.00 324295 4PADDYS RUN 138.00 1 | 281 | 329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
259 | 324237 4CANE RUN SW138.00 324488 2CANE RUN SW69.000 1 | 100 | 127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
260 | 324237 4CANE RUN SW138.00 324488 2CANE RUN SW69.000 2 | 100 | 127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
261 | 324237 4CANE RUN SW138.00 325096 4CANERN NGCC138.00 22 | 187 | 237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
262 | 324237 4CANE RUN SW138.00 325096 4CANERN NGCC138.00 24 | 208 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
263 | 324237 4CANE RUN SW138.00 325096 4CANERN NGCC138.00 25 | 227 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
264 | 324237 4CANE RUN SW138.00 326565 4INTRNTL TAP138.00 23 | 187 | 208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
265 | 324237 4CANE RUN SW138.00 326574 4CR11 TAP 138.00 21 | 187 | 237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
266 | 324238 4DANVILLE N 138.00 324239 4DANVILE N T138.00 1 | 166 | 166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
267 | 324238 4DANVILLE N 138.00 324495 2DANVILLE N 69.000 1 | 112 | 129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
268 | 324239 4DANVILE N T138.00 325121 4LOGAN TP 138.00 1 | 166 | 166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
269 | 324240 4DAY-WALT TP138.00 324242 4DOW CORN W 138.00 1 | 208 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
270 | 324240 4DAY-WALT TP138.00 324287 4NAS TAP 138.00 1 | 208 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
271 | 324241 4DIXIE 138.00 324295 4PADDYS RUN 138.00 1 | 191 | 302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
272 | 324242 4DOW CORN W 138.00 326512 4AIRGAS 138.00 1 | 208 | 208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
273 | 324243 4ETHEL 138.00 324518 2ETHEL 69.000 1 | 133 | 161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
274 | 324244 4ETOWN 138.00 324261 4HARDIN CO 138.00 1 | 208 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
275 | 324244 4ETOWN 138.00 324288 4NELSON CO 138.00 1 | 187 | 237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
276 | 324244 4ETOWN 138.00 324519 2ETOWN KU 69.000 1 | 136 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
277 | 324245 4FARMERS TAP138.00 324246 4FARMERS 138.00 1 | 134 | 134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
278 | 324245 4FARMERS TAP138.00 324307 4SHARKEY TAP138.00 1 | 166 | 166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
279 | 324245 4FARMERS TAP138.00 324310 4SPENCER RD 138.00 1 | 121 | 121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
280 | 324246 4FARMERS 138.00 324528 2FARMERS 69.000 1 | 61 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
281 | 324247 4FAWKES TAP 138.00 324248 4FAWKES KU 138.00 1 | 187 | 237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
282 | 324247 4FAWKES TAP 138.00 324276 4LAKE REBA T138.00 1 | 166 | 166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
283 | 324248 4FAWKES KU 138.00 324530 2FAWKES 69.000 1 | 120 | 154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
284 | 324248 4FAWKES KU 138.00 324530 2FAWKES 69.000 2 | 140 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
285 | 324249 4FERN VALLEY138.00 324257 4GRADE LANE 138.00 1 | 347 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
286 | 324249 4FERN VALLEY138.00 324292 4OKOLONA 138.00 1 | 266 | 287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
287 | 324249 4FERN VALLEY138.00 324322 4WATTERSON 138.00 1 | 200 | 208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
288 | 324249 4FERN VALLEY138.00 324532 2FERN VALLEY69.000 1 | 40 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
289 | 324249 4FERN VALLEY138.00 324532 2FERN VALLEY69.000 2 | 40 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
290 | 324250 4E FRANKFORT138.00 324306 4SHADRACK 138.00 1 | 171 | 171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
291 | 324250 4E FRANKFORT138.00 324315 4TYRONE 138.00 1 | 227 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
292 | 324250 4E FRANKFORT138.00 324319 4W FRANKFORT138.00 1 | 227 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
293 | 324250 4E FRANKFORT138.00 324535 2E FRANKFORT69.000 1 | 112 | 129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
294 | 324250 4E FRANKFORT138.00 324535 2E FRANKFORT69.000 2 | 112 | 129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
295 | 324251 4FLEMNB KU T138.00 324254 4GODDARD KU 138.00 1 | 134 | 169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
296 | 324251 4FLEMNB KU T138.00 324323 4WEDONIA 138.00 1 | 134 | 169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
297 | 324252 2SCHOLLS 69.000 324455 2BROMLEY 69.000 1 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
298 | 324253 4GHENT 138.00 324287 4NAS TAP 138.00 1 | 208 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
299 | 324253 4GHENT 138.00 324290 4OWEN CO TAP138.00 1 | 208 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
300 | 324253 4GHENT 138.00 324831 4WHITE SULPH138.00 1 | 187 | 208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
301 | 324254 4GODDARD KU 138.00 324302 4RODBURN 138.00 1 | 134 | 169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
302 | 324255 4GREEN RIVER138.00 324291 4OHIO COUNTY138.00 1 | 166 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
303 | 324255 4GREEN RIVER138.00 324550 2GREEN RIVER69.000 1 | 112 | 129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
304 | 324255 4GREEN RIVER138.00 324550 2GREEN RIVER69.000 2 | 135 | 143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
305 | 324255 4GREEN RIVER138.00 325015 4SMITH TAP 138.00 1 | 134 | 169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
306 | 324256 4GR RVR STL 138.00 324551 2GR RVR STL 69.000 1 | 90 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
307 | 324256 4GR RVR STL 138.00 325015 4SMITH TAP 138.00 1 | 134 | 169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
308 | 324258 4HAEFLING 138.00 324264 4IBM NORTHTP138.00 1 | 166 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
309 | 324258 4HAEFLING 138.00 324317 4VILEY ROAD 138.00 1 | 187 | 237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
310 | 324258 4HAEFLING 138.00 324335 4INNOVATION 138.00 1 | 140 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
311 | 324258 4HAEFLING 138.00 324558 2HAEFLING 69.000 1 | 120 | 143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
312 | 324258 4HAEFLING 138.00 325100 4W LEX R1 138.00 1 | 208 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
313 | 324259 4HANCOCK 138.00 324278 4MAGAZINE 138.00 1 | 266 | 266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
314 | 324259 4HANCOCK 138.00 324561 2HANCOCK 69.000 1 | 133 | 143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
315 | 324260 4HARDINSBURG138.00 325055 4RHUDES TP 138.00 1 | 208 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
316 | 324261 4HARDIN CO 138.00 324303 4ROGERSVILLE138.00 1 | 136 | 136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
317 | 324261 4HARDIN CO 138.00 324563 2HARDIN CO 69.000 1 | 185 | 213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
318 | 324261 4HARDIN CO 138.00 324563 2HARDIN CO 69.000 2 | 185 | 213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
319 | 324262 4HIGBY MILL 138.00 324269 4LANSDOWNE 138.00 1 | 140 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
320 | 324262 4HIGBY MILL 138.00 324333 4BROWN N 1-R138.00 1 | 208 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
321 | 324262 4HIGBY MILL 138.00 324568 2HIGBY 618 69.000 1 | 112 | 129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
322 | 324262 4HIGBY MILL 138.00 324569 2HIGBY 608 69.000 1 | 112 | 129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
323 | 324262 4HIGBY MILL 138.00 324569 2HIGBY 608 69.000 2 | 113 | 138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
324 | 324262 4HIGBY MILL 138.00 325089 4HIGBY MILL2138.00 Z1 | 285 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
325 | 324263 4HURSTBORNE 138.00 324297 4PLAINVIEW 138.00 1 | 266 | 266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
326 | 324264 4IBM NORTHTP138.00 324275 4LOUDON AVE 138.00 1 | 166 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
327 | 324264 4IBM NORTHTP138.00 326548 4IBM NORTH 138.00 1 | 166 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
328 | 324265 4JEFFRSONV T138.00 324289 4NORTHSIDE 138.00 1 | 347 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
329 | 324267 4KENTON 138.00 324323 4WEDONIA 138.00 1 | 134 | 169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
330 | 324267 4KENTON 138.00 324589 2KENTON 688 69.000 1 | 94 | 119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
331 | 324267 4KENTON 138.00 324882 2KENTON 698 69.000 1 | 33 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
332 | 324268 4KNOB CREEK 138.00 324284 4MILL CREEK 138.00 1 | 179 | 228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
333 | 324268 4KNOB CREEK 138.00 324300 4POND CREEK 138.00 1 | 179 | 179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
334 | 324269 4LANSDOWNE 138.00 324601 2LANSDOWNE 69.000 1 | 112 | 129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
335 | 324270 4LEBANON WES138.00 324271 4LEBANON 138.00 1 | 83 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
336 | 324271 4LEBANON 138.00 324606 2LEBANON 69.000 1 | 50 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
337 | 324271 4LEBANON 138.00 324606 2LEBANON 69.000 2 | 72 | 101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
338 | 324271 4LEBANON 138.00 325121 4LOGAN TP 138.00 1 | 166 | 166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
339 | 324272 4LEITCHFIELD138.00 324308 4SHREWSBURY 138.00 1 | 136 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
340 | 324272 4LEITCHFIELD138.00 324609 2LEITCHFIELD69.000 1 | 68 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
341 | 324273 4LAKE REBA 138.00 324612 2LAKE REBA 69.000 1 | 142 | 171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
342 | 324273 4LAKE REBA 138.00 326559 4BGAD TAP 138.00 Z1 | 166 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
343 | 324274 4LOCKPORT 138.00 324306 4SHADRACK 138.00 1 | 186 | 186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
344 | 324275 4LOUDON AVE 138.00 324617 2LOUDON 618 69.000 1 | 120 | 153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
345 | 324275 4LOUDON AVE 138.00 324618 2LOUDON 628 69.000 1 | 112 | 129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
346 | 324276 4LAKE REBA T138.00 326559 4BGAD TAP 138.00 1 | 136 | 171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
347 | 324277 4LYNDON SO 138.00 324281 4MIDDLETOWN 138.00 1 | 200 | 254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
348 | 324277 4LYNDON SO 138.00 324622 2LYNDON SO 69.000 1 | 140 | 143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
349 | 324278 4MAGAZINE 138.00 324321 4WATERSIDE 138.00 1 | 194 | 194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
350 | 324279 4MANSLICK 138.00 324284 4MILL CREEK 138.00 1 | 179 | 228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
351 | 324281 4MIDDLETOWN 138.00 324282 4MIDDLETWN-R138.00 1 | 203 | 259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
352 | 324281 4MIDDLETOWN 138.00 324364 4OLD HENRY 138.00 1 | 227 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
353 | 324281 4MIDDLETOWN 138.00 324637 2MIDDLETOWN 69.000 1 | 133 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
354 | 324281 4MIDDLETOWN 138.00 324637 2MIDDLETOWN 69.000 2 | 133 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
355 | 324281 4MIDDLETOWN 138.00 324637 2MIDDLETOWN 69.000 6 | 133 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
356 | 324281 4MIDDLETOWN 138.00 325042 4JEFERSONTWN138.00 1 | 347 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
357 | 324282 4MIDDLETWN-R138.00 324298 4PLAINVIEW T138.00 1 | 203 | 259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
358 | 324283 4MIDWAY 138.00 324320 4W LEXINGTON138.00 1 | 208 | 208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
359 | 324283 4MIDWAY 138.00 324831 4WHITE SULPH138.00 1 | 187 | 208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
360 | 324284 4MILL CREEK 138.00 324640 2MILL CREEK 69.000 7 | 40 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
361 | 324284 4MILL CREEK 138.00 324640 2MILL CREEK 69.000 8 | 50 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
362 | 324284 4MILL CREEK 138.00 325088 4MIL CK YARD138.00 1 | 203 | 203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
363 | 324285 4MUD LANE 138.00 324292 4OKOLONA 138.00 1 | 266 | 266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
364 | 324285 4MUD LANE 138.00 324651 2MUD LANE 69.000 1 | 120 | 138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
365 | 324286 4NAS 138.00 324287 4NAS TAP 138.00 1 | 208 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
366 | 324286 4NAS 138.00 324566 7NAS 222 345.00 1 | 281 | 329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
367 | 324289 4NORTHSIDE 138.00 325013 4CLIFTY TAP1138.00 1 | 120 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
368 | 324290 4OWEN CO TAP138.00 324305 4SCOTT CO 138.00 1 | 208 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
369 | 324291 4OHIO COUNTY138.00 324308 4SHREWSBURY 138.00 1 | 166 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
370 | 324291 4OHIO COUNTY138.00 324667 2OHIO COUNTY69.000 1 | 70 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
371 | 324294 4PADDYS WEST138.00 324295 4PADDYS RUN 138.00 1 | 454 | 580 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
372 | 324296 4PISGAH 138.00 324320 4W LEXINGTON138.00 1 | 208 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
373 | 324296 4PISGAH 138.00 324687 2PISGAH 69.000 1 | 112 | 129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
374 | 324296 4PISGAH 138.00 325857 4BROWN N TIE138.00 1 | 208 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
375 | 324297 4PLAINVIEW 138.00 324298 4PLAINVIEW T138.00 1 | 266 | 266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
376 | 324300 4POND CREEK 138.00 324311 4TIP TOP 138.00 1 | 136 | 171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
377 | 324301 4REYNOLDS 138.00 325089 4HIGBY MILL2138.00 1 | 203 | 203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
378 | 324302 4RODBURN 138.00 324307 4SHARKEY TAP138.00 1 | 136 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
379 | 324302 4RODBURN 138.00 324707 2RODBURN 69.000 1 | 90 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
380 | 324303 4ROGERSVILLE138.00 324708 2ROGERSVILLE69.000 1 | 93 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
381 | 324304 2VERSAILLE W69.000 324762 2VERSAIL W T69.000 1 | 23 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
382 | 324305 4SCOTT CO 138.00 324951 2SCOTT CO 69.000 1 | 93 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
383 | 324305 4SCOTT CO 138.00 324991 4ROGERS GAP 138.00 1 | 166 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
384 | 324307 4SHARKEY TAP138.00 326556 4N SHARKEY T138.00 1 | 183 | 202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
385 | 324308 4SHREWSBURY 138.00 324800 4MERE TVA 138.00 1 | 166 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
386 | 324310 4SPENCER RD 138.00 324733 2SPENCER RD 69.000 1 | 56 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
387 | 324310 4SPENCER RD 138.00 325009 2SPENCER A 69.000 1 | 33 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
388 | 324311 4TIP TOP 138.00 324976 2TIP TOP 1 69.000 3 | 33 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
389 | 324311 4TIP TOP 138.00 325132 4GREENSOL TP138.00 1 | 134 | 134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
390 | 324312 4TOYOTA N 138.00 324313 4TOYOTA S 138.00 1 | 104 | 131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
391 | 324312 4TOYOTA N 138.00 324991 4ROGERS GAP 138.00 1 | 166 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
392 | 324314 4TRIMBLE CO 138.00 326520 4TRIMBLE TR9138.00 Z1 | 316 | 359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
393 | 324315 4TYRONE 138.00 324755 2TYRONE 69.000 1 | 112 | 129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
394 | 324315 4TYRONE 138.00 325957 4BROWN N 1 138.00 1 | 166 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
395 | 324316 4VIRGINIA CI138.00 324759 2VIRGINIA CI69.000 1 | 120 | 138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
396 | 324317 4VILEY ROAD 138.00 325101 4W LEX R2 138.00 1 | 208 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
397 | 324318 4WEST CLIFF 138.00 324764 2WEST CLIFF 69.000 1 | 120 | 153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
398 | 324318 4WEST CLIFF 138.00 324764 2WEST CLIFF 69.000 2 | 120 | 153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
399 | 324318 4WEST CLIFF 138.00 324764 2WEST CLIFF 69.000 3 | 93 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
400 | 324319 4W FRANKFORT138.00 324765 2W FRANKFORT69.000 1 | 112 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
401 | 324320 4W LEXINGTON138.00 325089 4HIGBY MILL2138.00 1 | 208 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
402 | 324320 4W LEXINGTON138.00 325100 4W LEX R1 138.00 1 | 281 | 287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
403 | 324320 4W LEXINGTON138.00 325101 4W LEX R2 138.00 1 | 281 | 287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
404 | 324322 4WATTERSON 138.00 324771 2WATTERSON 69.000 1 | 100 | 127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
405 | 324322 4WATTERSON 138.00 324771 2WATTERSON 69.000 2 | 40 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
406 | 324322 4WATTERSON 138.00 325042 4JEFERSONTWN138.00 1 | 223 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
407 | 324328 4PARIS 138.00 324680 2PARIS KU 69.000 1 | 120 | 153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
408 | 324329 4COLLINS 138.00 324364 4OLD HENRY 138.00 1 | 200 | 254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
409 | 324329 4COLLINS 138.00 324481 2COLLINS 69.000 1 | 149 | 171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
410 | 324330 2WINCHES IND69.000 324783 2WINCHSTR KU69.000 1 | 45 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
411 | 324330 2WINCHES IND69.000 325063 2CORPORAT DR69.000 1 | 67 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
412 | 324331 2ASHLAND AVE69.000 324418 2ASHLND AV T69.000 1 | 33 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
413 | 324332 2LAKE SHORE 69.000 325059 2BRYANT RD T69.000 1 | 70 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
414 | 324333 4BROWN N 1-R138.00 325957 4BROWN N 1 138.00 1 | 281 | 329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
415 | 324334 4BROWN N 2-R138.00 325956 4BROWN N 2 138.00 1 | 227 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
416 | 324337 2MOUNT TABOR69.000 324650 2MT TBR T 69.000 1 | 19 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
417 | 324338 2SCOTT ST 4 69.000 324339 2SCOTT ST 1269.000 1 | 60 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
418 | 324338 2SCOTT ST 4 69.000 324952 2SCOTT ST TP69.000 1 | 102 | 129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
419 | 324340 2SPINDLETOP 69.000 324734 2SPINDLETP T69.000 1 | 19 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
420 | 324341 2WILMORE 69.000 324781 2WILMORE T 69.000 1 | 23 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
421 | 324344 2ATOKA 69.000 324421 2ATOKA TAP 69.000 1 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
422 | 324345 2BARDTWN IND69.000 324425 2BARDT IND T69.000 1 | 33 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
423 | 324346 2RICHMND E 69.000 324612 2LAKE REBA 69.000 1 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
424 | 324347 2BEATTY 649 69.000 325058 2BEATTY 614 69.000 1 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
425 | 324348 2BRODHEAD CI69.000 324808 2BRODHEAD KU69.000 1 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
426 | 324349 2CAMPBELVIL269.000 324479 2CAMPBELVL T69.000 1 | 23 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
427 | 324350 2CRAB ORCHAR69.000 324485 2CRAB ORCH T69.000 1 | 67 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
428 | 324351 2ETOWN 3 69.000 324354 2GATES RUBBR69.000 1 | 52 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
429 | 324351 2ETOWN 3 69.000 324519 2ETOWN KU 69.000 1 | 52 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
430 | 324352 2ETOWN IND 69.000 324563 2HARDIN CO 69.000 1 | 67 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
431 | 324353 2FLORDA TILE69.000 324863 2FLA TILE T169.000 1 | 18 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
432 | 324354 2GATES RUBBR69.000 326561 2ETOWN WEST 69.000 1 | 49 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
433 | 324355 2HARRDSBRG 469.000 325054 2HARRDSBRG N69.000 1 | 23 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
434 | 324356 2HARRDSBRG1269.000 325054 2HARRDSBRG N69.000 1 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
435 | 324357 2LANCASTER 169.000 324600 2LANCASTR KU69.000 1 | 23 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
436 | 324358 2M-V CLARKSN69.000 324914 2M-V CLARK T69.000 1 | 28 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
437 | 324359 2MT VERN 58969.000 324913 2MT VERNON 69.000 1 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
438 | 324360 2PINE HILL 69.000 324927 2PINE HILL T69.000 1 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
439 | 324361 2RADCLIFF KU69.000 324935 2RADCLF KU T69.000 1 | 41 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
440 | 324363 2SHELB CI KU69.000 324957 2SHELBY CI T69.000 1 | 28 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
441 | 324363 2SHELB CI KU69.000 326518 2SHELB CI EK69.000 1 | 20 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
442 | 324372 2BURNSIDE 69.000 324514 2ELIHU 69.000 1 | 21 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
443 | 324373 2CATRON CRK 69.000 324814 2CATRON CK T69.000 1 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
444 | 324374 2CROCKETT KU69.000 324376 2DEER BRANCH69.000 1 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
445 | 324374 2CROCKETT KU69.000 325083 2ALEX CK TAP69.000 1 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
446 | 324375 2DAYHOIT 69.000 324442 2BLEDSOE TAP69.000 1 | 28 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
447 | 324376 2DEER BRANCH69.000 324813 2CARY 69.000 1 | 23 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
448 | 324377 2GARDNER 69.000 325083 2ALEX CK TAP69.000 1 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
449 | 324378 2MIDDLBO780 69.000 324636 2MIDDLESBORO69.000 1 | 23 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
450 | 324380 2DANIEL BRAN69.000 324393 2ROSE HILL 69.000 1 | 18 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
451 | 324380 2DANIEL BRAN69.000 324945 2ROSE HILL T69.000 1 | 18 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
452 | 324381 2WILLAMSBURG69.000 325001 2WILLMBRG SW69.000 1 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
453 | 324382 2WILLMBRG SO69.000 325001 2WILLMBRG SW69.000 1 | 28 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
454 | 324384 2APPALACHIA 69.000 324549 2GORGE 69.000 1 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
455 | 324385 2BIG STONE G69.000 324549 2GORGE 69.000 1 | 36 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
456 | 324386 2DIXIANA 69.000 324388 2CRITICAL FK69.000 1 | 13 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
457 | 324387 2ADDINGTON 69.000 324392 2ROCKY FORK 69.000 1 | 18 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
458 | 324387 2ADDINGTON 69.000 325064 2LAUREL GROV69.000 1 | 18 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
459 | 324388 2CRITICAL FK69.000 325031 2LIPPS 69.000 1 | 18 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
460 | 324389 2DWINA 69.000 324851 2DWINA TAP 69.000 1 | 33 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
461 | 324390 2PENNINGTON 69.000 324391 2POOR VALLEY69.000 1 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
462 | 324391 2POOR VALLEY69.000 324689 2POCKET 69.000 1 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
463 | 324392 2ROCKY FORK 69.000 325031 2LIPPS 69.000 1 | 18 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
464 | 324394 2TOMS CREEK 69.000 324977 2TOMS CRK TP69.000 1 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
465 | 324395 2WISE 69.000 325005 2WISE TAP 69.000 1 | 39 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
466 | 324400 2WHAS TAP 69.000 324510 2EASTWOOD 69.000 1 | 94 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
467 | 324400 2WHAS TAP 69.000 324775 2WHAS 69.000 1 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
468 | 324400 2WHAS TAP 69.000 325022 2EASTWOOD W 69.000 1 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
469 | 324401 2FREYS HIL J69.000 324541 2FORD 69.000 1 | 113 | 133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
470 | 324401 2FREYS HIL J69.000 324545 2FREYS HILL 69.000 1 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
471 | 324401 2FREYS HIL J69.000 324785 2WORTHINGTON69.000 1 | 104 | 132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
472 | 324402 2FAIRMOUNT T69.000 324771 2WATTERSON 69.000 1 | 96 | 101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
473 | 324402 2FAIRMOUNT T69.000 324859 2FAIRMOUNT 169.000 1 | 100 | 101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
474 | 324403 2CRESTWOOD T69.000 324469 2CENTERFIELD69.000 1 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
475 | 324403 2CRESTWOOD T69.000 324487 2CRESTWOOD 69.000 1 | 100 | 127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
476 | 324403 2CRESTWOOD T69.000 324616 2LONG RUN 69.000 1 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
477 | 324404 2LYNDON TAP 69.000 324622 2LYNDON SO 69.000 1 | 135 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
478 | 324404 2LYNDON TAP 69.000 324623 2LYNDON 69.000 1 | 100 | 127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
479 | 324404 2LYNDON TAP 69.000 324750 2TAYLOR LG 69.000 1 | 90 | 114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
480 | 324405 2ADAMS 69.000 324500 2DELAPLAIN T69.000 1 | 52 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
481 | 324405 2ADAMS 69.000 324547 2GEORGETOWN 69.000 1 | 83 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
482 | 324405 2ADAMS 69.000 326989 2LONG LICK 69.000 1 | 52 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
483 | 324406 2AIKEN 69.000 324637 2MIDDLETOWN 69.000 1 | 173 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
484 | 324406 2AIKEN 69.000 324673 2OXMOOR 69.000 1 | 90 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
485 | 324406 2AIKEN 69.000 325022 2EASTWOOD W 69.000 1 | 100 | 127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
486 | 324407 2ALEXANDER 69.000 324755 2TYRONE 69.000 1 | 51 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
487 | 324407 2ALEXANDER 69.000 324955 2SHANNON RUN69.000 1 | 51 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
488 | 324408 2ALGONQUIN 69.000 324552 2GRADY 69.000 1 | 94 | 101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
489 | 324408 2ALGONQUIN 69.000 324625 2MAGAZINE 69.000 1 | 55 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
490 | 324408 2ALGONQUIN 69.000 324649 2MORRIS FORM69.000 1 | 56 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
491 | 324408 2ALGONQUIN 69.000 324719 2SEMINOLE 69.000 1 | 94 | 119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
492 | 324408 2ALGONQUIN 69.000 324739 2STEWART 69.000 1 | 94 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
493 | 324409 2AMERICAN AV69.000 324632 2UK MED CENT69.000 1 | 87 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
494 | 324409 2AMERICAN AV69.000 324683 2PICADOME 69.000 1 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
495 | 324409 2AMERICAN AV69.000 324772 2UK WEST 2 69.000 1 | 94 | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
496 | 324411 2ANDOVER TAP69.000 324440 2BLACK MOUNT69.000 1 | 39 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
497 | 324411 2ANDOVER TAP69.000 324583 2IMBODEN 69.000 1 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
498 | 324411 2ANDOVER TAP69.000 324670 2OSAKA EAST 69.000 1 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
499 | 324412 2ANDOVER 69.000 324670 2OSAKA EAST 69.000 1 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
500 | 324413 2AO SMITH TP69.000 324414 2AO SMITH 69.000 1 | 27 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
501 | 324413 2AO SMITH TP69.000 324461 2CAMARGO 69.000 1 | 51 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
502 | 324413 2AO SMITH TP69.000 324733 2SPENCER RD 69.000 1 | 51 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
503 | 324414 2AO SMITH 69.000 326531 2HINKSTON 69.000 1 | 54 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
504 | 324415 2APPOLO FUEL69.000 324593 2KU PARK 69.000 1 | 83 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
505 | 324415 2APPOLO FUEL69.000 324636 2MIDDLESBORO69.000 1 | 83 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
506 | 324416 2ARNOLD 69.000 324433 2BENHAM 69.000 1 | 32 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
507 | 324416 2ARNOLD 69.000 324490 2CUMBERLAND 69.000 1 | 36 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
508 | 324417 2ARTEMUS 69.000 324423 2BARBOURVILE69.000 1 | 68 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
509 | 324418 2ASHLND AV T69.000 324632 2UK MED CENT69.000 1 | 98 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
510 | 324418 2ASHLND AV T69.000 324934 2RACE STREET69.000 1 | 69 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
511 | 324419 2ASHBOT WEST69.000 325024 2ASHBOT SPRK69.000 1 | 94 | 119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
512 | 324421 2ATOKA TAP 69.000 324450 2BOYLE CO 69.000 1 | 70 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
513 | 324421 2ATOKA TAP 69.000 324495 2DANVILLE N 69.000 1 | 83 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
514 | 324422 2AVON T2 69.000 324508 2EASTLAND 69.000 1 | 38 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
515 | 324422 2AVON T2 69.000 324680 2PARIS KU 69.000 1 | 38 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
516 | 324422 2AVON T2 69.000 325081 2BRIAR HILL 69.000 1 | 18 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
517 | 324423 2BARBOURVILE69.000 324438 2BIMBLE 69.000 1 | 41 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
518 | 324424 2BARDTWN CTY69.000 324801 2BARTON 69.000 1 | 40 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
519 | 324424 2BARDTWN CTY69.000 326537 2WOODLAWN KU69.000 1 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
520 | 324425 2BARDT IND T69.000 324426 2BARDSTOWN 69.000 1 | 83 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
521 | 324426 2BARDSTOWN 69.000 324525 2FAIRFIELD 69.000 1 | 40 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
522 | 324426 2BARDSTOWN 69.000 326537 2WOODLAWN KU69.000 Z1 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
523 | 324427 2BARDWELL 69.000 324779 2WICKLIFFE 69.000 1 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
524 | 324427 2BARDWELL 69.000 324823 2CLINTON 58169.000 1 | 28 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
525 | 324428 2BARLOW 69.000 324778 2WICKLIFE CI69.000 1 | 67 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
526 | 324428 2BARLOW 69.000 324864 2FORRESTDALE69.000 1 | 67 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
527 | 324429 2BEARGRASS 69.000 324453 2BEARGRS PMP69.000 1 | 90 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
528 | 324429 2BEARGRASS 69.000 324475 2CLIFTON 69.000 1 | 89 | 89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
529 | 324429 2BEARGRASS 69.000 324624 2MADISON LGE69.000 1 | 90 | 114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
530 | 324429 2BEARGRASS 69.000 324710 2RVR CITY SH69.000 1 | 133 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
531 | 324430 2BEATTYVI KU69.000 325058 2BEATTY 614 69.000 1 | 70 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
532 | 324432 2BELT LINE 69.000 324558 2HAEFLING 69.000 1 | 121 | 121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
533 | 324432 2BELT LINE 69.000 324879 2IBM 998 69.000 1 | 135 | 173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
534 | 324433 2BENHAM 69.000 324621 2LYNCH 69.000 1 | 41 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
535 | 324434 2BEREA TAP 69.000 324435 2BEREA NORTH69.000 1 | 45 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
536 | 324434 2BEREA TAP 69.000 324612 2LAKE REBA 69.000 1 | 67 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
537 | 324434 2BEREA TAP 69.000 324668 2OKONITE 69.000 1 | 48 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
538 | 324435 2BEREA NORTH69.000 324805 2BEREA 2 69.000 1 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
539 | 324436 2BEREA EK TP69.000 324676 2PAINT LICK 69.000 1 | 40 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
540 | 324436 2BEREA EK TP69.000 324805 2BEREA 2 69.000 1 | 40 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
541 | 324437 2BEVIER KU 69.000 324745 2STRINGTOWN 69.000 1 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
542 | 324438 2BIMBLE 69.000 324515 2EMANUEL TAP69.000 1 | 75 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
543 | 324438 2BIMBLE 69.000 324573 2HINKLE 69.000 1 | 83 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
544 | 324439 2BISHOP 69.000 324518 2ETHEL 69.000 1 | 58 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
545 | 324439 2BISHOP 69.000 324532 2FERN VALLEY69.000 1 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
546 | 324440 2BLACK MOUNT69.000 324621 2LYNCH 69.000 1 | 39 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
547 | 324441 2BLACKWOOD 69.000 324503 2DORCHESTER 69.000 1 | 36 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
548 | 324441 2BLACKWOOD 69.000 324802 2BEAR BRANCH69.000 1 | 36 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
549 | 324442 2BLEDSOE TAP69.000 324497 2DAYHOIT TAP69.000 1 | 28 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
550 | 324442 2BLEDSOE TAP69.000 325008 2BLEDSOE 69.000 1 | 54 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
551 | 324443 2BLUE LICK 69.000 324789 2BLUE LCK TP69.000 1 | 83 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
552 | 324444 2BLUELICK EK69.000 324651 2MUD LANE 69.000 1 | 70 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
553 | 324444 2BLUELICK EK69.000 324788 2BROOKS EK T69.000 1 | 70 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
554 | 324445 2BONDS MILL 69.000 324620 2LAWRENCEBRG69.000 1 | 80 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
555 | 324445 2BONDS MILL 69.000 324732 2SOUTHVILLE 69.000 1 | 28 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
556 | 324445 2BONDS MILL 69.000 324863 2FLA TILE T169.000 1 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
557 | 324445 2BONDS MILL 69.000 325087 2CLAY LICK T69.000 1 | 67 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
558 | 324446 2BOND 69.000 324824 2CLINCH VALL69.000 1 | 57 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
559 | 324446 2BOND 69.000 324977 2TOMS CRK TP69.000 1 | 67 | 69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
560 | 324447 2BONNIE KU 69.000 324731 2SONORA TAP 69.000 1 | 67 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
561 | 324448 2BOONE AVE 69.000 324782 2WINCHEST SO69.000 1 | 113 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
562 | 324448 2BOONE AVE 69.000 325004 2WINCHES WTR69.000 1 | 113 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
563 | 324449 2BOONSBORO N69.000 325004 2WINCHES WTR69.000 1 | 113 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
564 | 324449 2BOONSBORO N69.000 325925 4BOONSBORO N138.00 1 | 120 | 153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
565 | 324450 2BOYLE CO 69.000 324494 2DANVILLE 1 69.000 1 | 52 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
566 | 324450 2BOYLE CO 69.000 324760 2VAKSDAHL AV69.000 1 | 67 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
567 | 324451 2BRECKNRIDGE69.000 324574 2HILLCREST 69.000 1 | 94 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
568 | 324451 2BRECKNRIDGE69.000 324673 2OXMOOR 69.000 1 | 90 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
569 | 324453 2BEARGRS PMP69.000 324475 2CLIFTON 69.000 1 | 90 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
570 | 324455 2BROMLEY 69.000 324966 2SPARTA KU 69.000 1 | 42 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
571 | 324456 2BRUSH CREEK69.000 324465 2CARPENTER T69.000 1 | 45 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
572 | 324456 2BRUSH CREEK69.000 324593 2KU PARK 69.000 1 | 42 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
573 | 324457 2BUCHANAN 69.000 324610 2LEX PLANT 69.000 1 | 68 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
574 | 324457 2BUCHANAN 69.000 324986 2W HIGH T2 69.000 1 | 68 | 86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
575 | 324458 2BUENA VISTA69.000 324501 2DIX DAM 69.000 1 | 83 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
576 | 324458 2BUENA VISTA69.000 324546 2GARRARD CT 69.000 1 | 83 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
577 | 324459 2BUSH TAP 69.000 324615 2LONDON 69.000 1 | 52 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
578 | 324459 2BUSH TAP 69.000 324626 2MANCHEST SO69.000 1 | 52 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
579 | 324459 2BUSH TAP 69.000 326533 2BUSH EKPC 69.000 1 | 54 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
580 | 324460 2CALLOWAY 69.000 324686 2PINEVILLE 69.000 1 | 83 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
581 | 324460 2CALLOWAY 69.000 324706 2ROCKY BRNCH69.000 1 | 67 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
582 | 324461 2CAMARGO 69.000 324912 2MT STERL KU69.000 1 | 51 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
583 | 324462 2CANAL 69.000 324499 2DEL PARK 69.000 1 | 83 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
584 | 324462 2CANAL 69.000 324624 2MADISON LGE69.000 1 | 94 | 117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
585 | 324462 2CANAL 69.000 324625 2MAGAZINE 69.000 1 | 91 | 91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
586 | 324462 2CANAL 69.000 324665 2OHIO FALL 169.000 1 | 70 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
587 | 324462 2CANAL 69.000 324666 2OHIO FALL 269.000 1 | 70 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
588 | 324464 2CARON 69.000 324615 2LONDON 69.000 1 | 53 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
589 | 324464 2CARON 69.000 324860 2FARISTON 69.000 1 | 57 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
590 | 324465 2CARPENTER T69.000 324784 2WOFFORD 69.000 1 | 67 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
591 | 324465 2CARPENTER T69.000 326535 2CARPENTER 69.000 1 | 23 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
592 | 324466 2CARROLLTON 69.000 324602 2LAWRENCE TP69.000 1 | 66 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
593 | 324466 2CARROLLTON 69.000 324634 2METAL+THERM69.000 1 | 52 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
594 | 324466 2CARROLLTON 69.000 324878 2HUNT BTM TP69.000 1 | 68 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
595 | 324467 2CAVE RUN TP69.000 324528 2FARMERS 69.000 1 | 28 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
596 | 324467 2CAVE RUN TP69.000 324714 2SALT LICK 69.000 1 | 28 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
597 | 324467 2CAVE RUN TP69.000 326538 2CAVE RUN 69.000 1 | 31 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
598 | 324468 2CENTRL CI S69.000 324572 2HILLSIDE 69.000 1 | 40 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
599 | 324468 2CENTRL CI S69.000 324817 2CENTRAL CIT69.000 1 | 40 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
600 | 324469 2CENTERFIELD69.000 324681 2PENAL FARM 69.000 1 | 49 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
601 | 324469 2CENTERFIELD69.000 324682 2PENAL TAP 69.000 1 | 83 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
602 | 324470 2CERRO-SALEM69.000 324486 2CRITTENDEN 69.000 1 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
603 | 324470 2CERRO-SALEM69.000 324948 2SALEM KU 69.000 1 | 28 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
604 | 324471 2CHRISTIAN 69.000 324777 2WHEATCROFT 69.000 1 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
605 | 324471 2CHRISTIAN 69.000 324822 2CLAY KU 69.000 1 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
606 | 324472 2CLARK CO 69.000 324540 2FOGG PIKE T69.000 1 | 67 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
607 | 324472 2CLARK CO 69.000 324749 2SYLVANIA 69.000 1 | 94 | 119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
608 | 324473 2CLAY LGE 69.000 324561 2HANCOCK 69.000 1 | 100 | 127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
609 | 324473 2CLAY LGE 69.000 324570 2HIGHLAND 69.000 1 | 100 | 127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
610 | 324473 2CLAY LGE 69.000 324624 2MADISON LGE69.000 1 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
611 | 324474 2CLAY VILG T69.000 324725 2SHELBYVIL E69.000 1 | 83 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
612 | 324474 2CLAY VILG T69.000 324765 2W FRANKFORT69.000 1 | 83 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
613 | 324475 2CLIFTON 69.000 324574 2HILLCREST 69.000 1 | 72 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
614 | 324476 2CMC TAP 69.000 324581 2HUGHES LANE69.000 1 | 67 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
615 | 324476 2CMC TAP 69.000 324680 2PARIS KU 69.000 1 | 67 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
616 | 324477 2CAMP BRECKN69.000 324502 2DIXON KU 69.000 1 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
617 | 324477 2CAMP BRECKN69.000 324645 2MORGANFIELD69.000 1 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
618 | 324478 2CAMPBELBURG69.000 324516 2EMINENCE KU69.000 1 | 49 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
619 | 324478 2CAMPBELBURG69.000 324828 2CAMPBBRG KU69.000 1 | 55 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
620 | 324479 2CAMPBELVL T69.000 324751 2TAYLOR CO 69.000 1 | 52 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
621 | 324479 2CAMPBELVL T69.000 324889 2LEBANON SO 69.000 1 | 52 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
622 | 324480 2CMPGND EK T69.000 324515 2EMANUEL TAP69.000 1 | 49 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
623 | 324480 2CMPGND EK T69.000 324615 2LONDON 69.000 1 | 32 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
624 | 324480 2CMPGND EK T69.000 326521 2CAMPGRND EK69.000 1 | 19 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
625 | 324481 2COLLINS 69.000 324487 2CRESTWOOD 69.000 1 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
626 | 324481 2COLLINS 69.000 324541 2FORD 69.000 1 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
627 | 324482 2CORBIN EAST69.000 324748 2SWEET HOLLO69.000 1 | 67 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
628 | 324482 2CORBIN EAST69.000 324832 2CORBIN 1 69.000 1 | 67 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
629 | 324484 2CORYDON 69.000 324571 2HIGHLAND MI69.000 1 | 67 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
630 | 324484 2CORYDON 69.000 324711 2SPEN CHEM T69.000 1 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
631 | 324484 2CORYDON 69.000 324754 2TUNNEL H KU69.000 1 | 27 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
632 | 324485 2CRAB ORCH T69.000 324600 2LANCASTR KU69.000 1 | 41 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
633 | 324485 2CRAB ORCH T69.000 324808 2BRODHEAD KU69.000 1 | 41 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
634 | 324486 2CRITTENDEN 69.000 324628 2MARION SO 69.000 1 | 57 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
635 | 324488 2CANE RUN SW69.000 324529 2FARNSLEY 69.000 1 | 94 | 94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
636 | 324488 2CANE RUN SW69.000 324724 2SHIVELY 69.000 1 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
637 | 324488 2CANE RUN SW69.000 324739 2STEWART 69.000 1 | 100 | 127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
638 | 324488 2CANE RUN SW69.000 324757 2UPR MIL CRK69.000 1 | 100 | 101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
639 | 324489 2CUMB FALL T69.000 324654 2MT VIC EK J69.000 1 | 67 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
640 | 324489 2CUMB FALL T69.000 324784 2WOFFORD 69.000 1 | 67 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
641 | 324489 2CUMB FALL T69.000 325034 2CUMBER FALL69.000 1 | 46 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
642 | 324490 2CUMBERLAND 69.000 324827 2CLOVERLICK 69.000 1 | 32 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
643 | 324491 2CYNTHIAN SO69.000 324837 2CYNTHIAN KU69.000 1 | 36 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
644 | 324491 2CYNTHIAN SO69.000 325085 2CYNTHI EK T69.000 1 | 39 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
645 | 324492 2CYNTHIAN SW69.000 324595 2KAWNEER 69.000 1 | 52 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
646 | 324493 2DAHLIA 69.000 324518 2ETHEL 69.000 1 | 100 | 124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
647 | 324493 2DAHLIA 69.000 324570 2HIGHLAND 69.000 1 | 96 | 101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
648 | 324494 2DANVILLE 1 69.000 324840 2DANVILLE E 69.000 1 | 67 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
649 | 324495 2DANVILLE N 69.000 324841 2DANVILLE W 69.000 1 | 67 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
650 | 324495 2DANVILLE N 69.000 326579 2HARRDSBRG 269.000 1 | 51 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
651 | 324496 2DARK HOLLOW69.000 324767 2WEST IRVINE69.000 1 | 52 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
652 | 324496 2DARK HOLLOW69.000 324880 2IRVINE 69.000 1 | 52 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
653 | 324497 2DAYHOIT TAP69.000 324564 2HARLAN WYE 69.000 1 | 52 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
654 | 324497 2DAYHOIT TAP69.000 324588 2KENTENIA 69.000 1 | 42 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
655 | 324498 2DAYS BRANCH69.000 324621 2LYNCH 69.000 1 | 52 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
656 | 324498 2DAYS BRANCH69.000 324876 2HOLMES MILL69.000 1 | 52 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
657 | 324499 2DEL PARK 69.000 324552 2GRADY 69.000 1 | 49 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
658 | 324500 2DELAPLAIN T69.000 324924 2OXFORD 69.000 1 | 39 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
659 | 324501 2DIX DAM 69.000 324764 2WEST CLIFF 69.000 1 | 120 | 153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
660 | 324501 2DIX DAM 69.000 324781 2WILMORE T 69.000 1 | 67 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
661 | 324502 2DIXON KU 69.000 324658 2NEBO 69.000 1 | 18 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
662 | 324503 2DORCHESTER 69.000 324517 2ESSERVILLE 69.000 1 | 67 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
663 | 324503 2DORCHESTER 69.000 324663 2NORTON EAST69.000 1 | 83 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
664 | 324503 2DORCHESTER 69.000 325064 2LAUREL GROV69.000 1 | 18 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
665 | 324504 2E BERNST KU69.000 324662 2N LONDON KU69.000 1 | 52 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
666 | 324504 2E BERNST KU69.000 324927 2PINE HILL T69.000 1 | 52 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
667 | 324505 2E DIAMOND 69.000 324506 2EARLINGTN N69.000 1 | 28 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
668 | 324505 2E DIAMOND 69.000 324947 2RUMSEY 69.000 1 | 67 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
669 | 324506 2EARLINGTN N69.000 324630 2MADSNV LP E69.000 1 | 83 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
670 | 324506 2EARLINGTN N69.000 324631 2MADSNV LP W69.000 1 | 104 | 132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
671 | 324506 2EARLINGTN N69.000 324769 2WALKER KU 69.000 1 | 94 | 119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
672 | 324506 2EARLINGTN N69.000 324954 2SENTRY TAP 69.000 1 | 67 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
673 | 324507 2EARLINGTON 69.000 324769 2WALKER KU 69.000 1 | 41 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
674 | 324507 2EARLINGTON 69.000 324850 2DOZIER H 69.000 1 | 41 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
675 | 324508 2EASTLAND 69.000 324617 2LOUDON 618 69.000 1 | 67 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
676 | 324509 2EASTVIEW 69.000 324914 2M-V CLARK T69.000 1 | 42 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
677 | 324510 2EASTWOOD 69.000 324729 2SIMPSONVILL69.000 1 | 83 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
678 | 324511 2ECHOLS 69.000 324584 2INDIAN HILL69.000 1 | 52 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
679 | 324511 2ECHOLS 69.000 324959 2SIMMONS 69.000 1 | 52 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
680 | 324512 2EDDYV PR TP69.000 324693 2PRINCETON 69.000 1 | 67 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
681 | 324513 2EDDYVILLE 69.000 324693 2PRINCETON 69.000 1 | 28 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
682 | 324513 2EDDYVILLE 69.000 324885 2KUTTAWA 69.000 1 | 18 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
683 | 324514 2ELIHU 69.000 324531 2FERGUSON SO69.000 1 | 104 | 132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
684 | 324514 2ELIHU 69.000 324654 2MT VIC EK J69.000 1 | 67 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
685 | 324514 2ELIHU 69.000 324962 2SOMERSET 1 69.000 1 | 67 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
686 | 324514 2ELIHU 69.000 324964 2SOMERSET 3 69.000 1 | 66 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
687 | 324515 2EMANUEL TAP69.000 326530 2EMANUEL 69.000 1 | 54 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
688 | 324516 2EMINENCE KU69.000 324585 2JERICHO 69.000 1 | 64 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
689 | 324516 2EMINENCE KU69.000 324727 2SHELBYVILLE69.000 1 | 52 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
690 | 324517 2ESSERVILLE 69.000 325005 2WISE TAP 69.000 1 | 67 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
691 | 324518 2ETHEL 69.000 324657 2NACHAND 69.000 1 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
692 | 324519 2ETOWN KU 69.000 324520 2ETOWN 2 TAP69.000 1 | 52 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
693 | 324519 2ETOWN KU 69.000 324521 2ETOWN 4 69.000 1 | 67 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
694 | 324519 2ETOWN KU 69.000 324563 2HARDIN CO 69.000 1 | 135 | 173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
695 | 324519 2ETOWN KU 69.000 324563 2HARDIN CO 69.000 2 | 135 | 173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
696 | 324520 2ETOWN 2 TAP69.000 326555 2RINEYVIL RD69.000 1 | 52 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
697 | 324521 2ETOWN 4 69.000 324575 2HODGENV KU 69.000 1 | 67 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
698 | 324522 2EVARTS TAP 69.000 324523 2EVARTS 69.000 1 | 36 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
699 | 324522 2EVARTS TAP 69.000 324692 2POWELL MTN 69.000 1 | 40 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
700 | 324522 2EVARTS TAP 69.000 324761 2VERDA 69.000 1 | 40 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
701 | 324523 2EVARTS 69.000 324798 2BAILEY CRK 69.000 1 | 40 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
702 | 324524 2EWINGTON 69.000 325009 2SPENCER A 69.000 1 | 45 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
703 | 324525 2FAIRFIELD 69.000 324974 2TAYLRV EK T69.000 1 | 40 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
704 | 324526 2FAIRMOUNT 269.000 324730 2SMYRNA 69.000 1 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
705 | 324527 2FARLEY KU 69.000 324704 2ROCKHOLD 69.000 1 | 40 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
706 | 324527 2FARLEY KU 69.000 324758 2US STEEL 69.000 1 | 113 | 133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
707 | 324528 2FARMERS 69.000 324647 2MOREHEAD W 69.000 1 | 44 | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
708 | 324529 2FARNSLEY 69.000 324675 2PADDYS RUN 69.000 1 | 94 | 94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
709 | 324529 2FARNSLEY 69.000 324724 2SHIVELY 69.000 1 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
710 | 324530 2FAWKES 69.000 324656 2N MADISON T69.000 1 | 49 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
711 | 324530 2FAWKES 69.000 324700 2RICHMND SO 69.000 1 | 94 | 119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
712 | 324530 2FAWKES 69.000 324701 2RICHMND 69.000 1 | 94 | 119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
713 | 324533 2FRANKFORT 169.000 324535 2E FRANKFORT69.000 1 | 49 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
714 | 324534 2FRANKFORT 269.000 324535 2E FRANKFORT69.000 1 | 66 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
715 | 324534 2FRANKFORT 269.000 324762 2VERSAIL W T69.000 1 | 51 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
716 | 324535 2E FRANKFORT69.000 326528 2BRIDGEPORT 69.000 1 | 113 | 143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
717 | 324536 2FINCHVILLE 69.000 324653 2M-V SIMPSON69.000 1 | 94 | 119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
718 | 324536 2FINCHVILLE 69.000 324718 2SHELBY CO T69.000 1 | 53 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
719 | 324536 2FINCHVILLE 69.000 324752 2TAYLORSV KU69.000 1 | 53 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
720 | 324537 2FLA TILE T269.000 324620 2LAWRENCEBRG69.000 1 | 67 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
721 | 324537 2FLA TILE T269.000 324755 2TYRONE 69.000 1 | 67 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
722 | 324538 2FLOYD 69.000 324561 2HANCOCK 69.000 1 | 65 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
723 | 324538 2FLOYD 69.000 324614 2LOCUST TAP 69.000 1 | 84 | 84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
724 | 324539 2FMC 69.000 324601 2LANSDOWNE 69.000 1 | 113 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
725 | 324539 2FMC 69.000 324613 2LK SHORE TP69.000 1 | 113 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
726 | 324540 2FOGG PIKE T69.000 324912 2MT STERL KU69.000 1 | 67 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
727 | 324541 2FORD 69.000 324637 2MIDDLETOWN 69.000 1 | 113 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
728 | 324542 2FORESTER CR69.000 324588 2KENTENIA 69.000 1 | 52 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
729 | 324542 2FORESTER CR69.000 324706 2ROCKY BRNCH69.000 1 | 52 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
730 | 324543 2FOUR MILE 69.000 324686 2PINEVILLE 69.000 1 | 32 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
731 | 324543 2FOUR MILE 69.000 324813 2CARY 69.000 1 | 40 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
732 | 324544 2FREDONIA QU69.000 324693 2PRINCETON 69.000 1 | 28 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
733 | 324544 2FREDONIA QU69.000 324865 2FREDONIA 69.000 1 | 45 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
734 | 324545 2FREYS HILL 69.000 324623 2LYNDON 69.000 1 | 100 | 127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
735 | 324546 2GARRARD CT 69.000 324600 2LANCASTR KU69.000 1 | 83 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
736 | 324547 2GEORGETOWN 69.000 324890 2LEMONS MILL69.000 1 | 75 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
737 | 324549 2GORGE 69.000 324583 2IMBODEN 69.000 1 | 68 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
738 | 324549 2GORGE 69.000 324894 2E STONE G T69.000 1 | 45 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
739 | 324550 2GREEN RIVER69.000 324652 2MUHLENBRG P69.000 1 | 53 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
740 | 324550 2GREEN RIVER69.000 324709 2RVR QUEEN T69.000 1 | 32 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
741 | 324550 2GREEN RIVER69.000 324723 2SHAVER CHAP69.000 1 | 49 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
742 | 324550 2GREEN RIVER69.000 325082 2ARMSTR BREC69.000 1 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
743 | 324550 2GREEN RIVER69.000 326513 2EQAL M BREC69.000 1 | 52 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
744 | 324551 2GR RVR STL 69.000 324786 2ZION 69.000 1 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
745 | 324551 2GR RVR STL 69.000 324947 2RUMSEY 69.000 1 | 28 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
746 | 324552 2GRADY 69.000 324675 2PADDYS RUN 69.000 1 | 94 | 101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
747 | 324553 2GRAHAMVILLE69.000 324864 2FORRESTDALE69.000 1 | 67 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
748 | 324554 2GRENSBRG KU69.000 324830 2CAMPBELV EK69.000 1 | 52 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
749 | 324555 2VA CTY REAC69.000 324716 2SANDY RIDGE69.000 1 | 67 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
750 | 324555 2VA CTY REAC69.000 324759 2VIRGINIA CI69.000 1 | 67 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
751 | 324556 2GREENV W TP69.000 324702 2RIVER QUEEN69.000 1 | 57 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
752 | 324556 2GREENV W TP69.000 324870 2GREENVILLE 69.000 1 | 40 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
753 | 324557 2GR RVR PLAZ69.000 324829 2CAMPBELVIL169.000 1 | 39 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
754 | 324557 2GR RVR PLAZ69.000 324830 2CAMPBELV EK69.000 1 | 47 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
755 | 324558 2HAEFLING 69.000 324734 2SPINDLETP T69.000 1 | 83 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
756 | 324558 2HAEFLING 69.000 324766 2W HIGH T1 69.000 1 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
757 | 324559 2HALEY 69.000 324797 2AVON T1 69.000 1 | 51 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
758 | 324559 2HALEY 69.000 326586 2HUME RD TAP69.000 1 | 51 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
759 | 324560 2HAMBLIN TAP69.000 324689 2POCKET 69.000 1 | 83 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
760 | 324560 2HAMBLIN TAP69.000 324815 2CAWOOD 69.000 1 | 70 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
761 | 324560 2HAMBLIN TAP69.000 325041 2STONE TVA 69.000 1 | 18 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
762 | 324562 2HARLAN KU 69.000 324564 2HARLAN WYE 69.000 1 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
763 | 324563 2HARDIN CO 69.000 324731 2SONORA TAP 69.000 1 | 67 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
764 | 324564 2HARLAN WYE 69.000 324956 2SHAWNEE GAS69.000 1 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
765 | 324565 7NAS TAP 345.00 324566 7NAS 222 345.00 1 | 956 | 956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
766 | 324567 2HIGBY MIL 269.000 324569 2HIGBY 608 69.000 1 | 83 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
767 | 324567 2HIGBY MIL 269.000 324780 2WIL DOWN T169.000 1 | 83 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
768 | 324568 2HIGBY 618 69.000 324569 2HIGBY 608 69.000 1 | 120 | 153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
769 | 324568 2HIGBY 618 69.000 324713 2SO ELKHORN 69.000 1 | 51 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
770 | 324568 2HIGBY 618 69.000 324742 2STONEWALL T69.000 1 | 94 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
771 | 324568 2HIGBY 618 69.000 325000 2WIL DOWN T269.000 1 | 67 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
772 | 324569 2HIGBY 608 69.000 324632 2UK MED CENT69.000 1 | 91 | 91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
773 | 324569 2HIGBY 608 69.000 324661 2NICHLSV 7 69.000 1 | 67 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
774 | 324571 2HIGHLAND MI69.000 324671 2OVERLAD S T69.000 1 | 57 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
775 | 324572 2HILLSIDE 69.000 324691 2POWDERLY 69.000 1 | 67 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
776 | 324573 2HINKLE 69.000 324741 2STINKIN CRK69.000 1 | 70 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
777 | 324576 2HOPEWELL 69.000 324748 2SWEET HOLLO69.000 1 | 67 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
778 | 324577 2HARDESTY A 69.000 324693 2PRINCETON 69.000 1 | 40 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
779 | 324577 2HARDESTY A 69.000 324769 2WALKER KU 69.000 1 | 40 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
780 | 324578 2HARDESTY B 69.000 324690 2DAWSON TAP 69.000 1 | 40 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
781 | 324578 2HARDESTY B 69.000 324769 2WALKER KU 69.000 1 | 40 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
782 | 324579 2HARMNY LAND69.000 324580 2HARRODS CRK69.000 1 | 38 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
783 | 324579 2HARMNY LAND69.000 324960 2SKYLIGHT 69.000 1 | 36 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
784 | 324580 2HARRODS CRK69.000 324750 2TAYLOR LG 69.000 1 | 100 | 127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
785 | 324580 2HARRODS CRK69.000 324785 2WORTHINGTON69.000 1 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
786 | 324581 2HUGHES LANE69.000 324586 2JOYLAND 69.000 1 | 53 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
787 | 324582 2IBM 69.000 324610 2LEX PLANT 69.000 1 | 94 | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
788 | 324582 2IBM 69.000 324879 2IBM 998 69.000 1 | 94 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
789 | 324583 2IMBODEN 69.000 324591 2KEOKEE TAP 69.000 1 | 67 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
790 | 324584 2INDIAN HILL69.000 324659 2NELSON 69.000 1 | 52 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
791 | 324585 2JERICHO 69.000 324598 2LA GRANGE E69.000 1 | 49 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
792 | 324586 2JOYLAND 69.000 324610 2LEX PLANT 69.000 1 | 67 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
793 | 324587 2KEN AMERICA69.000 324702 2RIVER QUEEN69.000 1 | 39 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
794 | 324587 2KEN AMERICA69.000 324709 2RVR QUEEN T69.000 1 | 52 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
795 | 324589 2KENTON 688 69.000 324722 2SHARON KU 69.000 1 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
796 | 324589 2KENTON 688 69.000 324899 2MAYSVILLE E69.000 1 | 23 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
797 | 324589 2KENTON 688 69.000 325019 2KENTON-6 69.000 1 | 67 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
798 | 324590 2KENWOOD 69.000 324719 2SEMINOLE 69.000 1 | 70 | 74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
799 | 324590 2KENWOOD 69.000 325023 2ASHBOT EAST69.000 1 | 94 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
800 | 324591 2KEOKEE TAP 69.000 324592 2KEOKEE TVA 69.000 1 | 113 | 136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
801 | 324592 2KEOKEE TVA 69.000 324689 2POCKET 69.000 1 | 67 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
802 | 324593 2KU PARK 69.000 324686 2PINEVILLE 69.000 1 | 113 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
803 | 324593 2KU PARK 69.000 324741 2STINKIN CRK69.000 1 | 68 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
804 | 324595 2KAWNEER 69.000 324837 2CYNTHIAN KU69.000 1 | 47 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
805 | 324597 2KY ST HOSP 69.000 324764 2WEST CLIFF 69.000 1 | 83 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
806 | 324597 2KY ST HOSP 69.000 324840 2DANVILLE E 69.000 1 | 83 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
807 | 324598 2LA GRANGE E69.000 324682 2PENAL TAP 69.000 1 | 67 | 69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
808 | 324599 2LANCASTER 269.000 324600 2LANCASTR KU69.000 1 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
809 | 324599 2LANCASTER 269.000 324971 2STANFORD NO69.000 1 | 45 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
810 | 324601 2LANSDOWNE 69.000 324650 2MT TBR T 69.000 1 | 120 | 153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
811 | 324601 2LANSDOWNE 69.000 324780 2WIL DOWN T169.000 1 | 67 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
812 | 324602 2LAWRENCE TP69.000 324828 2CAMPBBRG KU69.000 1 | 61 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
813 | 324602 2LAWRENCE TP69.000 324888 2LAWRENCE 69.000 1 | 26 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
814 | 324603 2LEBANON CIT69.000 324605 2LEBANON EK 69.000 1 | 52 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
815 | 324604 2LEBANON IND69.000 324606 2LEBANON 69.000 1 | 83 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
816 | 324604 2LEBANON IND69.000 325020 2LEBANON E 69.000 1 | 83 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
817 | 324605 2LEBANON EK 69.000 324889 2LEBANON SO 69.000 1 | 52 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
818 | 324606 2LEBANON 69.000 324736 2SPRINGFL KU69.000 1 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
819 | 324607 2LEITCHF CIT69.000 324608 2LEITCHF E 69.000 1 | 52 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
820 | 324607 2LEITCHF CIT69.000 324609 2LEITCHFIELD69.000 1 | 67 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
821 | 324608 2LEITCHF E 69.000 324992 2WARREN TIE 69.000 1 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
822 | 324609 2LEITCHFIELD69.000 324643 2MILL WOOD 69.000 1 | 52 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
823 | 324609 2LEITCHFIELD69.000 325040 2LEITCHF TVA69.000 1 | 68 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
824 | 324609 2LEITCHFIELD69.000 325040 2LEITCHF TVA69.000 2 | 68 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
825 | 324610 2LEX PLANT 69.000 324617 2LOUDON 618 69.000 1 | 120 | 134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
826 | 324610 2LEX PLANT 69.000 324674 2PROC & GAMB69.000 1 | 102 | 129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
827 | 324611 2LIBERTY RD 69.000 324618 2LOUDON 628 69.000 1 | 94 | 119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
828 | 324611 2LIBERTY RD 69.000 324891 2LEX WATER 69.000 1 | 113 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
829 | 324612 2LAKE REBA 69.000 324701 2RICHMND 69.000 1 | 52 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
830 | 324612 2LAKE REBA 69.000 324768 2WACO 69.000 1 | 52 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
831 | 324613 2LK SHORE TP69.000 324618 2LOUDON 628 69.000 1 | 94 | 119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
832 | 324613 2LK SHORE TP69.000 325059 2BRYANT RD T69.000 1 | 113 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
833 | 324614 2LOCUST TAP 69.000 324719 2SEMINOLE 69.000 1 | 94 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
834 | 324614 2LOCUST TAP 69.000 326545 2LOCUST LGE 69.000 1 | 58 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
835 | 324615 2LONDON 69.000 324688 2PITTSBRG KU69.000 1 | 104 | 132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
836 | 324616 2LONG RUN 69.000 324775 2WHAS 69.000 1 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
837 | 324617 2LOUDON 618 69.000 324618 2LOUDON 628 69.000 1 | 120 | 153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
838 | 324618 2LOUDON 628 69.000 326586 2HUME RD TAP69.000 1 | 67 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
839 | 324619 2LOWER MIL C69.000 324640 2MILL CREEK 69.000 1 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
840 | 324621 2LYNCH 69.000 326523 2ARKLAND JCT69.000 1 | 27 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
841 | 324622 2LYNDON SO 69.000 324637 2MIDDLETOWN 69.000 1 | 90 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
842 | 324622 2LYNDON SO 69.000 324673 2OXMOOR 69.000 1 | 100 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
843 | 324623 2LYNDON 69.000 324637 2MIDDLETOWN 69.000 1 | 90 | 114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
844 | 324626 2MANCHEST SO69.000 324627 2MANCHEST KU69.000 1 | 39 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
845 | 324628 2MARION SO 69.000 324629 2MARION KU 69.000 1 | 40 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
846 | 324629 2MARION KU 69.000 324904 2MEXICO KU 69.000 1 | 45 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
847 | 324630 2MADSNV LP E69.000 324862 2FIES CITY 69.000 1 | 55 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
848 | 324630 2MADSNV LP E69.000 324902 2MCCOY AVE 69.000 1 | 113 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
849 | 324631 2MADSNV LP W69.000 324658 2NEBO 69.000 1 | 53 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
850 | 324631 2MADSNV LP W69.000 324893 2MADSNV GE T69.000 1 | 104 | 132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
851 | 324633 2MELDRUM 69.000 324636 2MIDDLESBORO69.000 1 | 57 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
852 | 324633 2MELDRUM 69.000 324684 2PINEVIL 72269.000 1 | 67 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
853 | 324634 2METAL+THERM69.000 324849 2DOW CORNING69.000 1 | 52 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
854 | 324636 2MIDDLESBORO69.000 324874 2HARROGATE 69.000 1 | 23 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
855 | 324637 2MIDDLETOWN 69.000 324653 2M-V SIMPSON69.000 1 | 94 | 119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
856 | 324638 2MILL CRK KU69.000 324706 2ROCKY BRNCH69.000 1 | 28 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
857 | 324638 2MILL CRK KU69.000 324813 2CARY 69.000 1 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
858 | 324639 2MILLRSB624 69.000 324642 2MILLERSBURG69.000 1 | 94 | 119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
859 | 324639 2MILLRSB624 69.000 324812 2CARLISLE 69.000 1 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
860 | 324639 2MILLRSB624 69.000 325035 2BLUE SOL TP69.000 1 | 39 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
861 | 324641 2MILE LAN TP69.000 324751 2TAYLOR CO 69.000 1 | 52 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
862 | 324641 2MILE LAN TP69.000 324829 2CAMPBELVIL169.000 1 | 52 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
863 | 324641 2MILE LAN TP69.000 326970 2MILE LAN EK69.000 1 | 20 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
864 | 324642 2MILLERSBURG69.000 324677 2PARIS 12 69.000 1 | 21 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
865 | 324642 2MILLERSBURG69.000 324679 2PARIS 3 69.000 1 | 53 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
866 | 324642 2MILLERSBURG69.000 324717 2SARDIS TAP 69.000 1 | 70 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
867 | 324643 2MILL WOOD 69.000 324811 2CANEYVL JCT69.000 1 | 52 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
868 | 324644 2MORGANFLD 469.000 324645 2MORGANFIELD69.000 1 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
869 | 324644 2MORGANFLD 469.000 324776 2WHEATCROF T69.000 1 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
870 | 324645 2MORGANFIELD69.000 324671 2OVERLAD S T69.000 1 | 49 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
871 | 324645 2MORGANFIELD69.000 326546 2SUNOCO TAP 69.000 1 | 36 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
872 | 324645 2MORGANFIELD69.000 326572 2RIVRVW COAL69.000 1 | 48 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
873 | 324646 2MOREHEAD E 69.000 324707 2RODBURN 69.000 1 | 41 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
874 | 324646 2MOREHEAD E 69.000 324910 2MOREHEAD 69.000 1 | 38 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
875 | 324647 2MOREHEAD W 69.000 324910 2MOREHEAD 69.000 1 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
876 | 324648 2MORTONS GAP69.000 324664 2OAK HILL KU69.000 1 | 23 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
877 | 324648 2MORTONS GAP69.000 324769 2WALKER KU 69.000 1 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
878 | 324649 2MORRIS FORM69.000 324675 2PADDYS RUN 69.000 1 | 94 | 94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
879 | 324650 2MT TBR T 69.000 324891 2LEX WATER 69.000 1 | 70 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
880 | 324651 2MUD LANE 69.000 324730 2SMYRNA 69.000 1 | 90 | 114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
881 | 324652 2MUHLENBRG P69.000 324817 2CENTRAL CIT69.000 1 | 45 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
882 | 324655 2N CORBIN T 69.000 324748 2SWEET HOLLO69.000 1 | 67 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
883 | 324655 2N CORBIN T 69.000 324791 2AISIN 69.000 1 | 64 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
884 | 324655 2N CORBIN T 69.000 326542 2N CORBIN 69.000 1 | 36 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
885 | 324656 2N MADISON T69.000 324968 2SPEAR STA B69.000 1 | 49 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
886 | 324657 2NACHAND 69.000 324771 2WATTERSON 69.000 1 | 94 | 94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
887 | 324658 2NEBO 69.000 324774 2WEBCOAL 4 69.000 1 | 67 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
888 | 324658 2NEBO 69.000 324776 2WHEATCROF T69.000 1 | 28 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
889 | 324658 2NEBO 69.000 324931 2PROVIDNCE E69.000 1 | 36 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
890 | 324659 2NELSON 69.000 326513 2EQAL M BREC69.000 1 | 52 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
891 | 324660 2NEW HAVEN 69.000 324801 2BARTON 69.000 1 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
892 | 324661 2NICHLSV 7 69.000 324989 2W NICHSV T 69.000 1 | 67 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
893 | 324662 2N LONDON KU69.000 324688 2PITTSBRG KU69.000 1 | 52 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
894 | 324663 2NORTON EAST69.000 324826 2CLINCH V SW69.000 1 | 79 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
895 | 324667 2OHIO COUNTY69.000 324703 2RIVERVIEW 69.000 1 | 52 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
896 | 324667 2OHIO COUNTY69.000 324770 2WARREN 4 69.000 1 | 67 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
897 | 324668 2OKONITE 69.000 324936 2RICHMND IND69.000 1 | 49 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
898 | 324672 2OXFORD EK T69.000 324916 2NEWTOWN TAP69.000 1 | 28 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
899 | 324674 2PROC & GAMB69.000 324934 2RACE STREET69.000 1 | 102 | 129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
900 | 324677 2PARIS 12 69.000 324680 2PARIS KU 69.000 1 | 38 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
901 | 324678 2PARIS CITY 69.000 324679 2PARIS 3 69.000 1 | 45 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
902 | 324678 2PARIS CITY 69.000 324680 2PARIS KU 69.000 1 | 45 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
903 | 324681 2PENAL FARM 69.000 324960 2SKYLIGHT 69.000 1 | 38 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
904 | 324682 2PENAL TAP 69.000 324887 2LA GRANG PE69.000 1 | 49 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
905 | 324683 2PICADOME 69.000 324866 2GE LAMP 69.000 1 | 73 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
906 | 324684 2PINEVIL 72269.000 324686 2PINEVILLE 69.000 1 | 67 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
907 | 324687 2PISGAH 69.000 324694 2PARKR MIL T69.000 1 | 102 | 129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
908 | 324689 2POCKET 69.000 324738 2SAINT CHARL69.000 1 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
909 | 324689 2POCKET 69.000 324744 2STRAGHT CRK69.000 1 | 52 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
910 | 324690 2DAWSON TAP 69.000 324747 2SUNSET MINE69.000 1 | 40 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
911 | 324690 2DAWSON TAP 69.000 324843 2DAWSON IND 69.000 1 | 18 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
912 | 324691 2POWDERLY 69.000 324870 2GREENVILLE 69.000 1 | 67 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
913 | 324692 2POWELL MTN 69.000 324738 2SAINT CHARL69.000 1 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
914 | 324693 2PRINCETON 69.000 324747 2SUNSET MINE69.000 1 | 40 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
915 | 324694 2PARKR MIL T69.000 324884 2KUNKEL 69.000 1 | 67 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
916 | 324694 2PARKR MIL T69.000 324930 2PARKER MILL69.000 1 | 67 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
917 | 324695 2PARKER SEAL69.000 324749 2SYLVANIA 69.000 1 | 104 | 132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
918 | 324695 2PARKER SEAL69.000 324783 2WINCHSTR KU69.000 1 | 70 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
919 | 324696 2PUCKETT CRK69.000 324706 2ROCKY BRNCH69.000 1 | 32 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
920 | 324696 2PUCKETT CRK69.000 324792 2ALVA 69.000 1 | 32 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
921 | 324698 2RADCLIFF SO69.000 324708 2ROGERSVILLE69.000 1 | 45 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
922 | 324698 2RADCLIFF SO69.000 326555 2RINEYVIL RD69.000 1 | 52 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
923 | 324699 2RICE STA TP69.000 324768 2WACO 69.000 1 | 52 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
924 | 324699 2RICE STA TP69.000 326552 2SE COAL TP 69.000 1 | 45 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
925 | 324700 2RICHMND SO 69.000 324938 2RICHMND 3 69.000 1 | 67 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
926 | 324701 2RICHMND 69.000 324937 2RICHMND 2 69.000 1 | 67 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
927 | 324703 2RIVERVIEW 69.000 324959 2SIMMONS 69.000 1 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
928 | 324704 2ROCKHOLD 69.000 324784 2WOFFORD 69.000 1 | 45 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
929 | 324705 2ROCKWELL 69.000 324783 2WINCHSTR KU69.000 1 | 64 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
930 | 324705 2ROCKWELL 69.000 324855 2EKPC OFF TP69.000 1 | 49 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
931 | 324708 2ROGERSVILLE69.000 324944 2ROGERSV 60569.000 1 | 48 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932 | 324709 2RVR QUEEN T69.000 324981 2TEXAS GAS T69.000 1 | 32 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933 | 324710 2RVR CITY SH69.000 324750 2TAYLOR LG 69.000 1 | 118 | 118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934 | 324711 2SPEN CHEM T69.000 324790 2AIRLINE RD 69.000 1 | 28 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
935 | 324712 2SO PADUCAH 69.000 324825 2CLINTON KU 69.000 1 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936 | 324713 2SO ELKHORN 69.000 324955 2SHANNON RUN69.000 1 | 51 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937 | 324714 2SALT LICK 69.000 324733 2SPENCER RD 69.000 1 | 28 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938 | 324715 2SALVISA 69.000 324721 2SHAKERTOWN 69.000 1 | 67 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939 | 324715 2SALVISA 69.000 325087 2CLAY LICK T69.000 1 | 67 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
940 | 324716 2SANDY RIDGE69.000 324977 2TOMS CRK TP69.000 1 | 67 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
941 | 324717 2SARDIS TAP 69.000 326549 2SARDIS 69.000 1 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
942 | 324718 2SHELBY CO T69.000 324726 2SHELBYVIL S69.000 1 | 49 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
943 | 324719 2SEMINOLE 69.000 324724 2SHIVELY 69.000 1 | 94 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
944 | 324721 2SHAKERTOWN 69.000 324764 2WEST CLIFF 69.000 1 | 67 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
945 | 324723 2SHAVER CHAP69.000 325086 2KEN AMERI 269.000 1 | 61 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
946 | 324725 2SHELBYVIL E69.000 324727 2SHELBYVILLE69.000 1 | 83 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
947 | 324726 2SHELBYVIL S69.000 324727 2SHELBYVILLE69.000 1 | 67 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
948 | 324727 2SHELBYVILLE69.000 325102 2W SHELBY 69.000 1 | 67 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
949 | 324728 2SHUN PIKE 69.000 324781 2WILMORE T 69.000 1 | 67 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
950 | 324729 2SIMPSONVILL69.000 325102 2W SHELBY 69.000 1 | 67 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
951 | 324731 2SONORA TAP 69.000 326547 2SONORA 69.000 1 | 72 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
952 | 324734 2SPINDLETP T69.000 324848 2DONERAIL 69.000 1 | 83 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
953 | 324735 2SOUTH POINT69.000 324794 2ASHLND PIPE69.000 1 | 49 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
954 | 324735 2SOUTH POINT69.000 325000 2WIL DOWN T269.000 1 | 67 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
955 | 324737 2SOMERSET SO69.000 324969 2SMRST 615KU69.000 1 | 42 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
956 | 324740 2SOUTH PARK 69.000 324788 2BROOKS EK T69.000 1 | 100 | 127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
957 | 324740 2SOUTH PARK 69.000 325024 2ASHBOT SPRK69.000 1 | 120 | 143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
958 | 324742 2STONEWALL T69.000 324866 2GE LAMP 69.000 1 | 73 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
959 | 324742 2STONEWALL T69.000 324972 2STONEWALL 69.000 1 | 87 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
960 | 324743 2SAINT PAUL 69.000 324759 2VIRGINIA CI69.000 1 | 67 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
961 | 324743 2SAINT PAUL 69.000 324851 2DWINA TAP 69.000 1 | 67 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
962 | 324744 2STRAGHT CRK69.000 324876 2HOLMES MILL69.000 1 | 52 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
963 | 324746 2SUNOCO 69.000 326546 2SUNOCO TAP 69.000 1 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
964 | 324751 2TAYLOR CO 69.000 325921 5TAYLOR CO 161.00 1 | 90 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
965 | 324752 2TAYLORSV KU69.000 324974 2TAYLRV EK T69.000 1 | 45 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
966 | 324753 2TIP TOP 2 69.000 324807 2BRANDENBURG69.000 1 | 48 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
967 | 324754 2TUNNEL H KU69.000 324928 2POOLE 69.000 1 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
968 | 324755 2TYRONE 69.000 324762 2VERSAIL W T69.000 1 | 52 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969 | 324755 2TYRONE 69.000 324920 2NINEVAH TAP69.000 1 | 67 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
970 | 324755 2TYRONE 69.000 324985 2VSAIL BYPAS69.000 1 | 51 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
971 | 324756 2UK WEST 1 69.000 324772 2UK WEST 2 69.000 1 | 96 | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
972 | 324756 2UK WEST 1 69.000 324952 2SCOTT ST TP69.000 1 | 80 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
973 | 324757 2UPR MIL CRK69.000 324941 2RIVERPORT 69.000 1 | 63 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
974 | 324758 2US STEEL 69.000 324833 2CORBIN 2 69.000 1 | 113 | 133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
975 | 324760 2VAKSDAHL AV69.000 324838 2DANV IND TP69.000 1 | 67 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
976 | 324763 2VERSAILLES 69.000 324985 2VSAIL BYPAS69.000 1 | 51 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
977 | 324764 2WEST CLIFF 69.000 326578 2HARRDSBRG 169.000 1 | 83 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
978 | 324765 2W FRANKFORT69.000 326528 2BRIDGEPORT 69.000 1 | 113 | 143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
979 | 324765 2W FRANKFORT69.000 326973 2BRIDGPRT 1 69.000 1 | 54 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
980 | 324766 2W HIGH T1 69.000 324952 2SCOTT ST TP69.000 1 | 73 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
981 | 324766 2W HIGH T1 69.000 324988 2WEST HIGH 69.000 1 | 73 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
982 | 324767 2WEST IRVINE69.000 326552 2SE COAL TP 69.000 Z1 | 120 | 153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
983 | 324770 2WARREN 4 69.000 324946 2ROSINE JCT 69.000 1 | 67 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
984 | 324774 2WEBCOAL 4 69.000 324993 2WARRIOR CL 69.000 1 | 40 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
985 | 324776 2WHEATCROF T69.000 324777 2WHEATCROFT 69.000 1 | 36 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
986 | 324777 2WHEATCROFT 69.000 324973 2STURGIS 69.000 1 | 18 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
987 | 324778 2WICKLIFE CI69.000 324779 2WICKLIFFE 69.000 1 | 67 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
988 | 324780 2WIL DOWN T169.000 325002 2WILS DOWN 169.000 1 | 67 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
989 | 324782 2WINCHEST SO69.000 324783 2WINCHSTR KU69.000 1 | 104 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
990 | 324784 2WOFFORD 69.000 325001 2WILLMBRG SW69.000 1 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
991 | 324786 2ZION 69.000 324790 2AIRLINE RD 69.000 1 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
992 | 324787 2UNION UNDWR69.000 324990 2WAITSBORO 69.000 1 | 36 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
993 | 324788 2BROOKS EK T69.000 324809 2BROOKS EKPC69.000 1 | 58 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
994 | 324789 2BLUE LCK TP69.000 324806 2BEULAH EKPC69.000 1 | 58 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
995 | 324789 2BLUE LCK TP69.000 325021 2CONESTOGA 69.000 1 | 58 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
996 | 324791 2AISIN 69.000 324860 2FARISTON 69.000 1 | 67 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
997 | 324792 2ALVA 69.000 324819 2CHUNKLIC BR69.000 1 | 32 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
998 | 324794 2ASHLND PIPE69.000 324987 2W HICKMAN 69.000 1 | 67 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
999 | 324795 2ASHBYBRG PU69.000 324922 2ONTON 69.000 1 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1000 | 324796 2AVON 69.000 324797 2AVON T1 69.000 1 | 18 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1001 | 324797 2AVON T1 69.000 324855 2EKPC OFF TP69.000 1 | 51 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1002 | 324798 2BAILEY CRK 69.000 324875 2HIGHSPLINT 69.000 1 | 36 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1003 | 324799 2BARNHILL 69.000 324931 2PROVIDNCE E69.000 1 | 67 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1004 | 324799 2BARNHILL 69.000 324932 2PROVIDENCE 69.000 1 | 45 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1005 | 324802 2BEAR BRANCH69.000 324871 2HAMER 69.000 1 | 39 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1006 | 324803 2BEAR TRACK 69.000 324907 2MILLER CRK 69.000 1 | 47 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1007 | 324803 2BEAR TRACK 69.000 325058 2BEATTY 614 69.000 1 | 47 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1008 | 324804 2BEDFORD TAP69.000 324908 2MILTON 69.000 1 | 71 | 89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1009 | 324804 2BEDFORD TAP69.000 325033 2BEDFORD KU 69.000 1 | 54 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1010 | 324806 2BEULAH EKPC69.000 324925 2PLEAS GRV T69.000 1 | 58 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1011 | 324808 2BRODHEAD KU69.000 324913 2MT VERNON 69.000 1 | 52 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1012 | 324809 2BROOKS EKPC69.000 324958 2SHEPHRDSV T69.000 1 | 58 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1013 | 324810 2CALHOUN 69.000 324947 2RUMSEY 69.000 1 | 33 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1014 | 324811 2CANEYVL JCT69.000 324946 2ROSINE JCT 69.000 1 | 52 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1015 | 324814 2CATRON CK T69.000 324956 2SHAWNEE GAS69.000 1 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1016 | 324815 2CAWOOD 69.000 325007 2YANCY TAP 69.000 1 | 19 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1017 | 324816 2CEMETARY RD69.000 324970 2STANFORD KU69.000 1 | 21 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1018 | 324818 2CHAD TAP 69.000 324827 2CLOVERLICK 69.000 1 | 28 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1019 | 324818 2CHAD TAP 69.000 324978 2TOTZ 69.000 1 | 23 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1020 | 324819 2CHUNKLIC BR69.000 324945 2ROSE HILL T69.000 1 | 32 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1021 | 324820 2ISLAND MINE69.000 324850 2DOZIER H 69.000 1 | 41 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1022 | 324820 2ISLAND MINE69.000 324981 2TEXAS GAS T69.000 1 | 41 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1023 | 324821 2CLARKSON 69.000 324914 2M-V CLARK T69.000 1 | 47 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1024 | 324821 2CLARKSON 69.000 324992 2WARREN TIE 69.000 1 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1025 | 324822 2CLAY KU 69.000 324996 2DOTIKI TAP 69.000 1 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1026 | 324823 2CLINTON 58169.000 324825 2CLINTON KU 69.000 1 | 49 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1027 | 324824 2CLINCH VALL69.000 325005 2WISE TAP 69.000 1 | 67 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1028 | 324826 2CLINCH V SW69.000 324999 2WHTE OAK KU69.000 1 | 67 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1029 | 324832 2CORBIN 1 69.000 324833 2CORBIN 2 69.000 1 | 67 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1030 | 324836 2BENS BRANCH69.000 324853 2E STONE GAP69.000 1 | 40 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1031 | 324836 2BENS BRANCH69.000 324894 2E STONE G T69.000 1 | 40 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1032 | 324838 2DANV IND TP69.000 324957 2SHELBY CI T69.000 1 | 67 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1033 | 324839 2DANVILE IND69.000 324909 2MINR FARM T69.000 1 | 67 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1034 | 324841 2DANVILLE W 69.000 324909 2MINR FARM T69.000 1 | 67 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1035 | 324842 2DAVIS TAP 69.000 324967 2SPEAR STA A69.000 1 | 49 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1036 | 324842 2DAVIS TAP 69.000 324987 2W HICKMAN 69.000 1 | 49 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1037 | 324844 2DELAPLAIN 69.000 324943 2ROGERS GAP 69.000 1 | 67 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1038 | 324845 2DENHAM ST 69.000 324962 2SOMERSET 1 69.000 1 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1039 | 324845 2DENHAM ST 69.000 324963 2SOMERSET 2 69.000 1 | 45 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1040 | 324846 2DIAMOND 69.000 324932 2PROVIDENCE 69.000 1 | 28 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1041 | 324846 2DIAMOND 69.000 324996 2DOTIKI TAP 69.000 1 | 28 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1042 | 324847 2DODGE HILL 69.000 324973 2STURGIS 69.000 1 | 32 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1043 | 324847 2DODGE HILL 69.000 326546 2SUNOCO TAP 69.000 1 | 32 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1044 | 324848 2DONERAIL 69.000 324877 2HOOVER KU 69.000 1 | 68 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1045 | 324849 2DOW CORNING69.000 324867 2GHENT 69.000 1 | 47 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1046 | 324851 2DWINA TAP 69.000 324999 2WHTE OAK KU69.000 1 | 67 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1047 | 324852 2DYCUSBURG 69.000 324885 2KUTTAWA 69.000 1 | 27 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1048 | 324852 2DYCUSBURG 69.000 324949 2SALEM 673 69.000 1 | 27 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1049 | 324855 2EKPC OFF TP69.000 326541 2EKPC OFFICE69.000 1 | 29 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1050 | 324856 2ESTIL ST CO69.000 324880 2IRVINE 69.000 1 | 47 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1051 | 324856 2ESTIL ST CO69.000 324907 2MILLER CRK 69.000 1 | 47 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1052 | 324857 2ETOWN 2 69.000 324858 2ETOWN 5 69.000 1 | 42 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1053 | 324862 2FIES CITY 69.000 325086 2KEN AMERI 269.000 1 | 32 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1054 | 324863 2FLA TILE T169.000 324920 2NINEVAH TAP69.000 1 | 67 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1055 | 324865 2FREDONIA 69.000 324904 2MEXICO KU 69.000 1 | 45 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1056 | 324867 2GHENT 69.000 324911 2MARKLAND DM69.000 1 | 45 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1057 | 324871 2HAMER 69.000 324894 2E STONE G T69.000 1 | 47 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1058 | 324873 2HANSON JCT 69.000 324896 2MADSNV E 69.000 1 | 67 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1059 | 324875 2HIGHSPLINT 69.000 324942 2ROBBINS 69.000 1 | 28 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1060 | 324877 2HOOVER KU 69.000 324890 2LEMONS MILL69.000 1 | 68 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1061 | 324878 2HUNT BTM TP69.000 324908 2MILTON 69.000 1 | 71 | 89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1062 | 324881 2JACKS CREEK69.000 324942 2ROBBINS 69.000 1 | 28 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1063 | 324881 2JACKS CREEK69.000 324978 2TOTZ 69.000 1 | 23 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1064 | 324882 2KENTON 698 69.000 324901 2MAYSVILLE W69.000 1 | 28 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1065 | 324884 2KUNKEL 69.000 324979 2TRAFTON AVE69.000 1 | 67 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1066 | 324886 2KY RIVER 69.000 324967 2SPEAR STA A69.000 1 | 52 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1067 | 324886 2KY RIVER 69.000 324968 2SPEAR STA B69.000 1 | 67 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1068 | 324892 2LIGGETT 69.000 324945 2ROSE HILL T69.000 1 | 19 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1069 | 324892 2LIGGETT 69.000 325007 2YANCY TAP 69.000 1 | 19 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1070 | 324893 2MADSNV GE T69.000 324897 2MADSNV N 69.000 1 | 67 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1071 | 324893 2MADSNV GE T69.000 326587 2MADSNV W TP69.000 1 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1072 | 324895 2MADSNV HO 69.000 324897 2MADSNV N 69.000 1 | 67 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1073 | 324896 2MADSNV E 69.000 324902 2MCCOY AVE 69.000 1 | 67 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1074 | 324898 2MANITOU 69.000 324954 2SENTRY TAP 69.000 1 | 57 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1075 | 324898 2MANITOU 69.000 324993 2WARRIOR CL 69.000 1 | 67 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1076 | 324899 2MAYSVILLE E69.000 324900 2MAYSVILLE M69.000 1 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1077 | 324903 2MCKEE ROAD 69.000 324964 2SOMERSET 3 69.000 1 | 49 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1078 | 324903 2MCKEE ROAD 69.000 324965 2SOMERSET NO69.000 1 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1079 | 324909 2MINR FARM T69.000 325032 2MINOR FARM 69.000 1 | 67 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1080 | 324911 2MARKLAND DM69.000 324994 2WARSAW KU 69.000 1 | 45 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1081 | 324915 2MT WAS EK J69.000 325006 2W MT WSH EK69.000 1 | 38 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1082 | 324916 2NEWTOWN TAP69.000 324924 2OXFORD 69.000 1 | 23 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1083 | 324916 2NEWTOWN TAP69.000 325027 2NEWTOWN 69.000 1 | 23 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1084 | 324917 2NICHLSV 3 69.000 324918 2NICHLSV 4&569.000 1 | 67 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1085 | 324917 2NICHLSV 3 69.000 324980 2RJ CORMAN 69.000 1 | 67 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1086 | 324918 2NICHLSV 4&569.000 324919 2NICHLSV 6&869.000 1 | 67 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1087 | 324919 2NICHLSV 6&869.000 324989 2W NICHSV T 69.000 1 | 67 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1088 | 324920 2NINEVAH TAP69.000 326529 2NINEVAH 69.000 1 | 31 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1089 | 324921 2ARCH CHEM 69.000 324976 2TIP TOP 1 69.000 1 | 48 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1090 | 324922 2ONTON 69.000 326563 2ADVENT MINE69.000 1 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1091 | 324925 2PLEAS GRV T69.000 325006 2W MT WSH EK69.000 1 | 58 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1092 | 324928 2POOLE 69.000 324953 2SEBREE 69.000 1 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1093 | 324930 2PARKER MILL69.000 324972 2STONEWALL 69.000 1 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1094 | 324934 2RACE STREET69.000 324984 2VINE STREET69.000 1 | 69 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1095 | 324935 2RADCLF KU T69.000 324944 2ROGERSV 60569.000 1 | 36 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1096 | 324935 2RADCLF KU T69.000 324982 2VINE GRV KU69.000 1 | 32 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1097 | 324936 2RICHMND IND69.000 324940 2RICHMND J 69.000 1 | 57 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1098 | 324937 2RICHMND 2 69.000 324939 2RICHMND 4 69.000 1 | 67 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1099 | 324938 2RICHMND 3 69.000 324940 2RICHMND J 69.000 1 | 57 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1100 | 324941 2RIVERPORT 69.000 324975 2TERRY 69.000 1 | 63 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1101 | 324943 2ROGERS GAP 69.000 324951 2SCOTT CO 69.000 1 | 67 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1102 | 324948 2SALEM KU 69.000 324949 2SALEM 673 69.000 1 | 29 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1103 | 324950 2SCIENC HILL69.000 324965 2SOMERSET NO69.000 1 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1104 | 324951 2SCOTT CO 69.000 326989 2LONG LICK 69.000 1 | 52 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1105 | 324953 2SEBREE 69.000 326563 2ADVENT MINE69.000 1 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1106 | 324954 2SENTRY TAP 69.000 325762 2WARRIOR TAP69.000 1 | 7 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1107 | 324957 2SHELBY CI T69.000 324970 2STANFORD KU69.000 1 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1108 | 324958 2SHEPHRDSV T69.000 325043 2SHEPHERDSV 69.000 1 | 58 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1109 | 324959 2SIMMONS 69.000 326564 2LEW BREC 69.000 1 | 52 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1110 | 324961 2SOMERSET GE69.000 324963 2SOMERSET 2 69.000 1 | 40 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1111 | 324966 2SPARTA KU 69.000 324994 2WARSAW KU 69.000 1 | 42 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1112 | 324969 2SMRST 615KU69.000 324990 2WAITSBORO 69.000 1 | 42 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1113 | 324970 2STANFORD KU69.000 324971 2STANFORD NO69.000 1 | 39 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1114 | 324979 2TRAFTON AVE69.000 324986 2W HIGH T2 69.000 1 | 67 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1115 | 324981 2TEXAS GAS T69.000 325062 2TEXAS GAS 69.000 1 | 52 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1116 | 324984 2VINE STREET69.000 324988 2WEST HIGH 69.000 1 | 77 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1117 | 324994 2WARSAW KU 69.000 325025 2WARSAW EAST69.000 1 | 23 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1118 | 324996 2DOTIKI TAP 69.000 325010 2WEBCOAL 2 69.000 1 | 25 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1119 | 324997 2WEST CO 1 69.000 324998 2WEST CO 2 69.000 1 | 140 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1120 | 325000 2WIL DOWN T269.000 325003 2WILS DOWN 269.000 1 | 67 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1121 | 325002 2WILS DOWN 169.000 325003 2WILS DOWN 269.000 Z1 | 234 | 239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1122 | 325008 2BLEDSOE 69.000 325026 2PINE MOUNTN69.000 1 | 54 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1123 | 325010 2WEBCOAL 2 69.000 325011 2DOTIKI 69.000 1 | 52 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1124 | 325017 2CMWA 69.000 325018 2CLA 69.000 1 | 67 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1125 | 325018 2CLA 69.000 325061 2CMC 69.000 1 | 67 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1126 | 325023 2ASHBOT EAST69.000 325024 2ASHBOT SPRK69.000 1 | 94 | 119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1127 | 325028 5ASHWD SL TP161.00 325047 5ASHWOOD 161.00 1 | 180 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1128 | 325028 5ASHWD SL TP161.00 326589 5N PRN LIV R161.00 1 | 194 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1129 | 325035 2BLUE SOL TP69.000 325050 2BLUE SOLAR 69.000 1 | 74 | 74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1130 | 325035 2BLUE SOL TP69.000 325085 2CYNTHI EK T69.000 1 | 39 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1131 | 325041 2STONE TVA 69.000 325068 2HAMBLIN 69.000 1 | 18 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1132 | 325044 4INTRNTL 138.00 326565 4INTRNTL TAP138.00 1 | 208 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1133 | 325045 2TURTLE CRK 69.000 325092 2COAL GOOD 69.000 1 | 32 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1134 | 325055 4RHUDES TP 138.00 325116 4RHUDES CR 138.00 1 | 170 | 229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1135 | 325057 4KOSMOS CEME138.00 325088 4MIL CK YARD138.00 1 | 80 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1136 | 325059 2BRYANT RD T69.000 325060 2BRYANT ROAD69.000 1 | 70 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1137 | 325075 5KMPA COLEMN161.00 325077 5COLEMAN TAP161.00 Z1 | 176 | 176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1138 | 325077 5COLEMAN TAP161.00 325078 5PADUCAH PRI161.00 1 | 194 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1139 | 325078 5PADUCAH PRI161.00 326562 2PAD PRI 62469.000 1 | 93.3 | 93.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1140 | 325078 5PADUCAH PRI161.00 326596 2PAD PRI 61469.000 1 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1141 | 325079 5N PRINCETON161.00 326589 5N PRN LIV R161.00 1 | 251 | 251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1142 | 325079 5N PRINCETON161.00 326591 5W PRINCETON161.00 1 | 209 | 209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1143 | 325083 2ALEX CK TAP69.000 326544 2ALEX CREEK 69.000 1 | 54 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1144 | 325096 4CANERN NGCC138.00 326002 7CANERN NGCC345.00 1 | 450 | 518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1145 | 325096 4CANERN NGCC138.00 326565 4INTRNTL TAP138.00 23 | 208 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1146 | 325096 4CANERN NGCC138.00 326566 4CANE RUN 71138.00 71 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1147 | 325096 4CANERN NGCC138.00 326574 4CR11 TAP 138.00 21 | 208 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1148 | 325761 2WARRIOR PRP69.000 325762 2WARRIOR TAP69.000 1 | 7 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1149 | 325762 2WARRIOR TAP69.000 325767 2SENTRY 69.000 1 | 7 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1150 | 325857 4BROWN N TIE138.00 325956 4BROWN N 2 138.00 Z1 | 468 | 548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1151 | 325857 4BROWN N TIE138.00 325957 4BROWN N 1 138.00 Z1 | 717 | 717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1152 | 326001 7CANE RUN TP345.00 326002 7CANERN NGCC345.00 1 | 1123 | 1123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1153 | 326517 2OVEN FORK 69.000 326523 2ARKLAND JCT69.000 1 | 27 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1154 | 326523 2ARKLAND JCT69.000 326534 2ARKLAND 69.000 1 | 54 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1155 | 326524 2VAN METER 69.000 326527 2TREEHAVEN T69.000 1 | 36 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1156 | 326525 2TREEHAVEN 69.000 326527 2TREEHAVEN T69.000 1 | 54 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1157 | 326526 4N SHARKEY 138.00 326556 4N SHARKEY T138.00 1 | 183 | 202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1158 | 326527 2TREEHAVEN T69.000 326541 2EKPC OFFICE69.000 1 | 54 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1159 | 326528 2BRIDGEPORT 69.000 326974 2BRIDGPRT 2 69.000 1 | 54 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1160 | 326530 2EMANUEL 69.000 326539 2GIRDLER 69.000 1 | 54 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1161 | 326532 4SHARKEY 138.00 326556 4N SHARKEY T138.00 1 | 183 | 202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1162 | 326552 2SE COAL TP 69.000 326553 2SE COAL 69.000 1 | 7 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1163 | 326559 4BGAD TAP 138.00 326560 4BG ARMY DEP138.00 1 | 67 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1164 | 326562 2PAD PRI 62469.000 326596 2PAD PRI 61469.000 Z1 | 140 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1165 | 326571 2HUME RD 69.000 326586 2HUME RD TAP69.000 1 | 70 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1166 | 326578 2HARRDSBRG 169.000 326579 2HARRDSBRG 269.000 1 | 140 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1167 | 326578 2HARRDSBRG 169.000 326584 2CORNG7462_369.000 1 | 67 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1168 | 326579 2HARRDSBRG 269.000 326580 2CORNIG 825369.000 1 | 67 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1169 | 326582 2CORNG8251_269.000 326583 2CORNIG 746169.000 1 | 67 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1170 | 326583 2CORNIG 746169.000 326584 2CORNG7462_369.000 1 | 67 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1171 | 326591 5W PRINCETON161.00 326592 5E PRINCETON161.00 1 | 176 | 176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1172 | 326593 2GREENVIL N 69.000 326594 2GREENVL 12 69.000 1 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1173 | 339206 AE1-143 C 161.00 342769 5MARION CO 161.00 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1174 | 339206 AE1-143 C 161.00 939132 AE1-143 E 161.00 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1175 | 341002 2AIRPORT RD 69.000 341443 2ELLIO CO PT69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1176 | 341002 2AIRPORT RD 69.000 341752 2LEON 69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1177 | 341005 2ALBANY 69.000 342181 2S ALBANY 69.000 1 | 41 | 46 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1178 | 341005 2ALBANY 69.000 342283 2SNOW T 69.000 1 | 49 | 54 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1179 | 341005 2ALBANY 69.000 342397 2UPCHURCH T 69.000 1 | 49 | 54 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1180 | 341008 2ALCAN 69.000 342106 2PPG J 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1181 | 341008 2ALCAN 69.000 342430 2W BEREA 69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1182 | 341014 2ANNVILLE 69.000 341017 2ANNVILLE T 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1183 | 341017 2ANNVILLE T 69.000 341428 2EBERLE T 69.000 1 | 77 | 90 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1184 | 341017 2ANNVILLE T 69.000 342391 2TYNER 69.000 1 | 74 | 83 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1185 | 341020 2ARGENTUM 69.000 243725 05GRAYSB 69.000 1 | 42 | 42 | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1186 | 341020 2ARGENTUM 69.000 341782 2LOW GAP T 69.000 1 | 53 | 66 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1187 | 341020 2ARGENTUM 69.000 342538 4ARGENTUM 138.00 1 | 62 | 76 | 86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1188 | 341029 2ASAHI M W 69.000 341032 2ASAHI M W T69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1189 | 341032 2ASAHI M W T69.000 341379 2DAHL ROAD 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1190 | 341032 2ASAHI M W T69.000 342472 2WALNUT GROV69.000 1 | 55 | 57 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1191 | 341035 2BACON CRK 69.000 341038 2BACON CRK T69.000 1 | 91 | 101 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1192 | 341038 2BACON CRK T69.000 341755 2LIBER CH T 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1193 | 341038 2BACON CRK T69.000 342187 2S CORBIN 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1194 | 341041 2BAKER LN 69.000 341635 2HOLLOWAY 69.000 1 | 41 | 46 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1195 | 341041 2BAKER LN 69.000 341638 2HOLLOWAY J 69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1196 | 341041 2BAKER LN 69.000 342547 4BAKER LN 138.00 1 | 114 | 148 | 166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1197 | 341044 2BALLARD 69.000 341671 2HUNT FARM J69.000 1 | 41 | 46 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1198 | 341044 2BALLARD 69.000 342361 2TODDVILLE T69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1199 | 341047 2BALLTOWN 69.000 342424 2W BARDST J 69.000 1 | 35 | 39 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1200 | 341050 2BANK LCK 69.000 342295 2STANLY P J169.000 1 | 77 | 90 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1201 | 341053 2BARD SHOP 69.000 341056 2BARD SHOP T69.000 1 | 35 | 39 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1202 | 341056 2BARD SHOP T69.000 341407 2E BARDSTOWN69.000 1 | 77 | 90 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1203 | 341056 2BARD SHOP T69.000 342424 2W BARDST J 69.000 1 | 77 | 90 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1204 | 341059 2BARREN CO 69.000 341275 2CAVE CITY J69.000 1 | 77 | 90 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1205 | 341059 2BARREN CO 69.000 341542 2GOODNIGHT 69.000 1 | 77 | 90 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1206 | 341059 2BARREN CO 69.000 341651 2HORSECAVE J69.000 1 | 90 | 98 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1207 | 341059 2BARREN CO 69.000 342694 5BARREN CO 161.00 1 | 89 | 109 | 123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1208 | 341062 2BASS 69.000 341269 2CASEY CO 69.000 1 | 77 | 90 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1209 | 341065 2BEAM 69.000 341068 2BEAM T 69.000 1 | 77 | 90 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1210 | 341068 2BEAM T 69.000 341215 2BULLITT CO 69.000 1 | 114 | 124 | 133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1211 | 341068 2BEAM T 69.000 342253 2SHEPHEVIL J69.000 1 | 114 | 127 | 133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1212 | 341071 2BEATTYV 69.000 324430 2BEATTYVI KU69.000 1 | 94 | 119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1213 | 341071 2BEATTYV 69.000 341074 2BEATTYV D 69.000 1 | 73 | 76 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1214 | 341071 2BEATTYV 69.000 341077 2BEATTYV J 69.000 1 | 73 | 76 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1215 | 341071 2BEATTYV 69.000 342520 2ZACHARIAH 69.000 1 | 42 | 46 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1216 | 341074 2BEATTYV D 69.000 341992 2OAKDALE 69.000 1 | 42 | 46 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1217 | 341077 2BEATTYV J 69.000 341173 2BOONEVIL T 69.000 1 | 77 | 90 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1218 | 341080 2BECKTON 69.000 341149 2BON AYR 69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1219 | 341080 2BECKTON 69.000 342445 2W GLASGOW T69.000 1 | 77 | 90 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1220 | 341089 2BEKAERT 69.000 325102 2W SHELBY 69.000 1 | 89 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1221 | 341089 2BEKAERT 69.000 342500 2WIELAND 69.000 1 | 77 | 90 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1222 | 341092 2BELLVIEW 69.000 341095 2BELLVIEW T 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1223 | 341095 2BELLVIEW T 69.000 341164 2BOONE CO 69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1224 | 341095 2BELLVIEW T 69.000 341227 2BURLINGTN T69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1225 | 341098 2BEREAKU T 69.000 342433 2W BEREA J 69.000 1 | 49 | 54 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1226 | 341104 2BIG BONE 69.000 341107 2BIG BONE T 69.000 1 | 41 | 46 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1227 | 341107 2BIG BONE T 69.000 341164 2BOONE CO 69.000 1 | 53 | 66 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1228 | 341107 2BIG BONE T 69.000 341917 2MUNK 69.000 1 | 77 | 90 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1229 | 341110 2BIG CREEK 69.000 341113 2BIG CREEK T69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1230 | 341110 2BIG CREEK 69.000 341439 2ELK MT IP 69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1231 | 341113 2BIG CREEK T69.000 341464 2FALL ROCK 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1232 | 341113 2BIG CREEK T69.000 342001 2ONEIDA 69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1233 | 341114 2BIG HILL 69.000 341115 2BIG HILL T 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1234 | 341115 2BIG HILL T 69.000 342223 2SAND GAP T 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1235 | 341115 2BIG HILL T 69.000 342346 2THREE LINKS69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1236 | 341116 2BIG WOODS 69.000 341119 2BIG WOODS J69.000 1 | 57 | 63 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1237 | 341119 2BIG WOODS J69.000 341620 2HILDA 69.000 1 | 53 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1238 | 341119 2BIG WOODS J69.000 342088 2PLUMMR L T 69.000 1 | 53 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1239 | 341122 2BILL WELL T69.000 341125 2BILL WELLS 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1240 | 341122 2BILL WELL T69.000 341692 2JENNY WIL T69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1241 | 341122 2BILL WELL T69.000 341860 2MIDDL CRK T69.000 1 | 77 | 90 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1242 | 341131 2BLEVINS V T69.000 341134 2BLEVINS VAL69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1243 | 341131 2BLEVINS V T69.000 341644 2HOPE 69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1244 | 341131 2BLEVINS V T69.000 342112 2PRESTON T 69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1245 | 341137 2BLOOMFLD 69.000 341296 2CHAPLIN T 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1246 | 341137 2BLOOMFLD 69.000 341935 2N SPRINGFLD69.000 1 | 42 | 46 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1247 | 341140 2BLUE G PW 69.000 341143 2BLUE G PW T69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1248 | 341143 2BLUE G PW T69.000 342019 2OWENS IL J 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1249 | 341143 2BLUE G PW T69.000 342508 2WOODLAWN 69.000 1 | 41 | 46 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1250 | 341149 2BON AYR 69.000 341272 2CAVE CITY 69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1251 | 341152 2BONANZA 69.000 341155 2BONANZA T 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1252 | 341155 2BONANZA T 69.000 341803 2MAGOFFIN CO69.000 1 | 53 | 66 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1253 | 341155 2BONANZA T 69.000 341860 2MIDDL CRK T69.000 1 | 77 | 90 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1254 | 341158 2BONNIV DIST69.000 341161 2BONNIV EK 69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1255 | 341158 2BONNIV DIST69.000 341908 2MUNFVIL EK 69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1256 | 341161 2BONNIV EK 69.000 324213 4BONNIEVILLE138.00 1 | 89 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1257 | 341161 2BONNIV EK 69.000 342403 2UPTON T 69.000 1 | 49 | 54 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1258 | 341164 2BOONE CO 69.000 341167 2BOONE DIST 69.000 1 | 56 | 68 | 74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1259 | 341164 2BOONE CO 69.000 342388 2TURKEY FT J69.000 1 | 53 | 66 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1260 | 341164 2BOONE CO 69.000 342466 2W R SMOOT 69.000 1 | 53 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1261 | 341164 2BOONE CO 69.000 342559 4BOONE CO 138.00 1 | 90 | 108 | 117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1262 | 341170 2BOONEVIL 69.000 341173 2BOONEVIL T 69.000 1 | 41 | 46 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1263 | 341173 2BOONEVIL T 69.000 342196 2WHITE OAK 69.000 1 | 77 | 90 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1264 | 341179 2BOSTONKU 69.000 341746 2LEBANON J 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1265 | 341179 2BOSTONKU 69.000 342514 2WOOSLEY 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1266 | 341185 2BOWEN 69.000 341614 2HIGH ROCK 69.000 1 | 77 | 90 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1267 | 341185 2BOWEN 69.000 342100 2POWELL CO 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1268 | 341188 2BRACKEN CO 69.000 324463 2CARNTOWN 69.000 1 | 36 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1269 | 341188 2BRACKEN CO 69.000 324722 2SHARON KU 69.000 1 | 28 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1270 | 341188 2BRACKEN CO 69.000 341488 2FOUR OAKS T69.000 1 | 53 | 66 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1271 | 341188 2BRACKEN CO 69.000 341587 2GRIFFIN J 69.000 1 | 53 | 63 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1272 | 341194 2BRISTOW 69.000 342385 2TURKEY FT 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1273 | 341194 2BRISTOW 69.000 342388 2TURKEY FT J69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1274 | 341197 2BRODHEAD 69.000 341818 2MARETBURG T69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1275 | 341197 2BRODHEAD 69.000 342349 2THREE LNK J69.000 1 | 53 | 66 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1276 | 341200 2BROMLEYEK 69.000 341920 2MUNK J 69.000 1 | 77 | 90 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1277 | 341200 2BROMLEYEK 69.000 342010 2OWEN CO J1 69.000 1 | 77 | 90 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1278 | 341203 2BRONSTON 69.000 341206 2BRONSTON T 69.000 1 | 41 | 46 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1279 | 341206 2BRONSTON T 69.000 341347 2COOPER DIST69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1280 | 341206 2BRONSTON T 69.000 341392 2DENNY 69.000 1 | 41 | 46 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1281 | 341209 2BROUGTWN T 69.000 341210 2BROUGHT TWN69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1282 | 341209 2BROUGTWN T 69.000 341617 2HIGHLAND EK69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1283 | 341209 2BROUGTWN T 69.000 342367 2TOMM GOOC T69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1284 | 341212 2BUDD 69.000 341774 2LOGAN 2 T 69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1285 | 341212 2BUDD 69.000 342500 2WIELAND 69.000 1 | 77 | 90 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1286 | 341215 2BULLITT CO 69.000 341281 2CEDAR GR 69.000 1 | 114 | 127 | 133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1287 | 341215 2BULLITT CO 69.000 341389 2DEATSVILL T69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1288 | 341215 2BULLITT CO 69.000 342700 5BULLITT CO 161.00 1 | 144 | 166 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1289 | 341218 2BULLITTSVIL69.000 341227 2BURLINGTN T69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1290 | 341218 2BULLITTSVIL69.000 341605 2HEBRON 69.000 1 | 91 | 101 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1291 | 341224 2BURLINGTN 69.000 341227 2BURLINGTN T69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1292 | 341233 2CABIN HOLLW69.000 341974 2NORWOOD T 69.000 1 | 77 | 90 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1293 | 341233 2CABIN HOLLW69.000 342286 2SOMERSET 69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1294 | 341248 2CAMPTON 69.000 341608 2HELECHAW 69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1295 | 341248 2CAMPTON 69.000 342520 2ZACHARIAH 69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1296 | 341251 2CANE RIDG 69.000 341254 2CANE RIDG T69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1297 | 341254 2CANE RIDG T69.000 341872 2MILLB-CRL J69.000 1 | 69 | 80 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1298 | 341254 2CANE RIDG T69.000 342259 2SIDEVIEW 69.000 1 | 69 | 80 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1299 | 341260 2CARSON 69.000 342013 2OWEN CO J2 69.000 1 | 41 | 46 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1300 | 341263 2CARTER CTY 69.000 341266 2CARTER CY T69.000 1 | 77 | 90 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1301 | 341266 2CARTER CY T69.000 342034 2PACTOLUS T 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1302 | 341266 2CARTER CY T69.000 342475 2WARNOCK 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1303 | 341269 2CASEY CO 69.000 342064 2PEYTONS ST 69.000 1 | 77 | 90 | 97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1304 | 341269 2CASEY CO 69.000 342703 5CASEY CO 161.00 1 | 96 | 108 | 112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1305 | 341272 2CAVE CITY 69.000 341275 2CAVE CITY J69.000 1 | 41 | 46 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1306 | 341275 2CAVE CITY J69.000 342241 2SEYMOUR T 69.000 1 | 77 | 90 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1307 | 341281 2CEDAR GR 69.000 342082 2PLEAS GRV 69.000 1 | 42 | 46 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1308 | 341287 2CENT HARDIN69.000 341713 2KARGLE 69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1309 | 341287 2CENT HARDIN69.000 342307 2STEPHENSBRG69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1310 | 341287 2CENT HARDIN69.000 342568 4CENT HARDIN138.00 1 | 144 | 175 | 198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1311 | 341293 2CHAPLIN 69.000 341296 2CHAPLIN T 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1312 | 341296 2CHAPLIN T 69.000 342262 2SINAI 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1313 | 341299 2CHARTERS 69.000 341989 2OAK RIDGE T69.000 1 | 77 | 90 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1314 | 341299 2CHARTERS 69.000 342124 2RECTORVILLE69.000 1 | 41 | 46 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1315 | 341302 2CLAY CITY 69.000 341305 2CLAY CITY T69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1316 | 341305 2CLAY CITY T69.000 341593 2HARDWCRK T 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1317 | 341305 2CLAY CITY T69.000 341599 2HARGETT T 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1318 | 341308 2CLAY LCK 69.000 341314 2CLAY LCK SW69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1319 | 341311 2CLAY LCK J 69.000 341314 2CLAY LCK SW69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1320 | 341311 2CLAY LCK J 69.000 342184 2S ANDERSON 69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1321 | 341311 2CLAY LCK J 69.000 342406 2VAN ARSDELL69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1322 | 341317 2CLAY VILLAG69.000 324474 2CLAY VILG T69.000 1 | 73 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1323 | 341317 2CLAY VILLAG69.000 341390 2DEFOE TAP 69.000 1 | 23 | 25 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1324 | 341320 2COBURG 69.000 324830 2CAMPBELV EK69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1325 | 341320 2COBURG 69.000 341512 2GARLIN T 69.000 1 | 41 | 46 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1326 | 341323 2COBURG J 69.000 341335 2COLUMBIA 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1327 | 341323 2COBURG J 69.000 341512 2GARLIN T 69.000 1 | 41 | 46 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1328 | 341323 2COBURG J 69.000 342235 2SEWELTN J 69.000 1 | 53 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1329 | 341326 2COLEMANSVIL69.000 341488 2FOUR OAKS T69.000 1 | 77 | 90 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1330 | 341326 2COLEMANSVIL69.000 342133 2RENAKER 69.000 1 | 51 | 54 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1331 | 341329 2COLESBURG 69.000 341332 2COLESBURG J69.000 1 | 23 | 25 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1332 | 341332 2COLESBURG J69.000 341944 2NELSON CO 69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1333 | 341332 2COLESBURG J69.000 342155 2ROANOKE T 69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1334 | 341335 2COLUMBIA 69.000 341370 2COLUMB S KU69.000 1 | 77 | 90 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1335 | 341335 2COLUMBIA 69.000 342436 2W COLUMBI T69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1336 | 341338 2CONWAY 69.000 341341 2CONWAY T 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1337 | 341341 2CONWAY T 69.000 342346 2THREE LINKS69.000 1 | 77 | 90 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1338 | 341341 2CONWAY T 69.000 342349 2THREE LNK J69.000 1 | 53 | 66 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1339 | 341342 2CONTOWN T 69.000 341343 2CONTOWN 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1340 | 341342 2CONTOWN T 69.000 341761 2LIBERTY J 69.000 1 | 53 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1341 | 341342 2CONTOWN T 69.000 342067 2PHIL 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1342 | 341344 2COOPER 69.000 341347 2COOPER DIST69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1343 | 341344 2COOPER 69.000 342286 2SOMERSET 69.000 1 | 66 | 76 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1344 | 341344 2COOPER 69.000 342286 2SOMERSET 69.000 2 | 66 | 76 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1345 | 341344 2COOPER 69.000 342715 5COOPER1 161.00 1 | 134 | 152 | 166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1346 | 341350 2CRESTON 69.000 342067 2PHIL 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1347 | 341353 2CROCKETT 69.000 341356 2CROCKETT T 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1348 | 341356 2CROCKETT T 69.000 341653 2HOT MIX R T69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1349 | 341356 2CROCKETT T 69.000 342265 2SKAGGS 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1350 | 341359 2CROOKSVIL 69.000 341362 2CROOKSVIL T69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1351 | 341359 2CROOKSVIL 69.000 342288 2SPEEDWELL 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1352 | 341362 2CROOKSVIL T69.000 341406 2DUNCAN LN T69.000 1 | 89 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1353 | 341362 2CROOKSVIL T69.000 341611 2HICKORY PL 69.000 1 | 77 | 90 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1354 | 341366 2COLUMB KU 69.000 341370 2COLUMB S KU69.000 1 | 77 | 90 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1355 | 341377 2CYNTHIA TIE69.000 341602 2HEADQTRS 69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1356 | 341377 2CYNTHIA TIE69.000 342355 2THREE M T 69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1357 | 341379 2DAHL ROAD 69.000 342256 2SHOPVILLE 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1358 | 341380 2DALE 69.000 341959 2NEWBY 1 69.000 1 | 77 | 90 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1359 | 341380 2DALE 69.000 341962 2NEWBY 2 69.000 1 | 73 | 76 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1360 | 341380 2DALE 69.000 342574 4DALE 138.00 1 | 114 | 146 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1361 | 341381 2DAV LANE 69.000 341382 2DAV LANE T 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1362 | 341382 2DAV LANE T 69.000 341734 2LAUR C IP T69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1363 | 341382 2DAV LANE T 69.000 342451 2W LONDON 69.000 1 | 41 | 46 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1364 | 341383 2DAVIS 69.000 341467 2FAYETTE 69.000 1 | 66 | 76 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1365 | 341383 2DAVIS 69.000 341965 2NICHOLASVIL69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1366 | 341386 2DEATSVIL 69.000 341389 2DEATSVILL T69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1367 | 341389 2DEATSVILL T69.000 341707 2JOE TICH T 69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1368 | 341390 2DEFOE TAP 69.000 341391 2DEFOE 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1369 | 341390 2DEFOE TAP 69.000 341950 2NEW CASTLE 69.000 1 | 23 | 25 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1370 | 341392 2DENNY 69.000 341578 2GREGORY R T69.000 1 | 73 | 76 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1371 | 341392 2DENNY 69.000 342499 2WIBORG T 69.000 1 | 73 | 76 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1372 | 341392 2DENNY 69.000 342727 5DENNY 161.00 1 | 89 | 109 | 123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1373 | 341394 2PATRIOT PW 69.000 341479 2S BOUND RD 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1374 | 341394 2PATRIOT PW 69.000 342151 2RINEYVILLE 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1375 | 341394 2PATRIOT PW 69.000 342157 2ROGERSVIL J69.000 1 | 77 | 90 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1376 | 341394 2PATRIOT PW 69.000 342274 2SMITHRVIL T69.000 1 | 77 | 90 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1377 | 341398 2DOWNING 69.000 341605 2HEBRON 69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1378 | 341398 2DOWNING 69.000 341880 2MINEOLA PKE69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1379 | 341400 2DRAVO 69.000 342091 2PLUMVILLE 69.000 1 | 41 | 46 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1380 | 341401 2DURO 69.000 341842 2MBUSA T 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1381 | 341404 2DURO T 69.000 341842 2MBUSA T 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1382 | 341404 2DURO T 69.000 342295 2STANLY P J169.000 1 | 114 | 127 | 133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1383 | 341404 2DURO T 69.000 342388 2TURKEY FT J69.000 1 | 90 | 115 | 133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1384 | 341405 2DUNCANNO LN69.000 341406 2DUNCAN LN T69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1385 | 341406 2DUNCAN LN T69.000 324530 2FAWKES 69.000 1 | 114 | 127 | 133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1386 | 341407 2E BARDSTOWN69.000 324425 2BARDT IND T69.000 1 | 67 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1387 | 341407 2E BARDSTOWN69.000 342019 2OWENS IL J 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1388 | 341410 2E BERNSTADT69.000 341929 2N LONDON 69.000 1 | 41 | 46 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1389 | 341416 2E PINE KNOT69.000 342076 2PINE KNOT 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1390 | 341419 2E SOMERSE T69.000 341422 2E SOMERSET 69.000 1 | 41 | 46 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1391 | 341419 2E SOMERSE T69.000 341941 2NELSN VAL T69.000 1 | 41 | 46 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1392 | 341419 2E SOMERSE T69.000 341974 2NORWOOD T 69.000 1 | 41 | 46 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1393 | 341425 2EBERLE 69.000 341428 2EBERLE T 69.000 1 | 41 | 46 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1394 | 341428 2EBERLE T 69.000 341809 2MAPLESVIL T69.000 1 | 77 | 90 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1395 | 341431 2EDM-JBGAL J69.000 341434 2EDM-JBGAL T69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1396 | 341431 2EDM-JBGAL J69.000 341728 2KNOB LICK 69.000 1 | 41 | 46 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1397 | 341431 2EDM-JBGAL J69.000 342322 2SUMM SHADE 69.000 1 | 41 | 46 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1398 | 341434 2EDM-JBGAL T69.000 341437 2EDMON IND P69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1399 | 341434 2EDM-JBGAL T69.000 341680 2JB GALLOWAY69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1400 | 341443 2ELLIO CO PT69.000 341446 2ELLIOT CO P69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1401 | 341443 2ELLIO CO PT69.000 341953 2NEW FOUNDL 69.000 1 | 77 | 90 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1402 | 341449 2ELLIOTTVILL69.000 342163 2ROWAN CO 69.000 1 | 41 | 46 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1403 | 341455 2ETOWN EK1 69.000 341458 2ETOWN EK2 69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1404 | 341455 2ETOWN EK1 69.000 342274 2SMITHRVIL T69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1405 | 341455 2ETOWN EK1 69.000 342379 2TUNNEL H T 69.000 1 | 96 | 108 | 117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1406 | 341458 2ETOWN EK2 69.000 342340 2THARP T 69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1407 | 341461 2FALCON EK 69.000 243721 05FALCON 69.000 Z1 | 34 | 34 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1408 | 341461 2FALCON EK 69.000 341797 2MAGGARD 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1409 | 341461 2FALCON EK 69.000 342310 2SUBLETT 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1410 | 341464 2FALL ROCK 69.000 341569 2GREENBRIA T69.000 1 | 77 | 90 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1411 | 341464 2FALL ROCK 69.000 342391 2TYNER 69.000 1 | 66 | 69 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1412 | 341464 2FALL ROCK 69.000 342730 5FALL ROCK 161.00 1 | 96 | 117 | 132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1413 | 341467 2FAYETTE 69.000 342580 4FAYETTE 138.00 1 | 90 | 115 | 138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1414 | 341470 2FLOYD EK 69.000 341473 2FLOYD-SFL T69.000 1 | 77 | 90 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1415 | 341470 2FLOYD EK 69.000 342511 2WOODSTOCK 69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1416 | 341473 2FLOYD-SFL T69.000 342115 2PULASK CO 69.000 1 | 73 | 76 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1417 | 341473 2FLOYD-SFL T69.000 342193 2S FLOYD 69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1418 | 341476 2FOGG PIKE 69.000 341899 2MT STERLING69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1419 | 341476 2FOGG PIKE 69.000 342130 2REID VILLAG69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1420 | 341485 2FOUR OAKS 69.000 341488 2FOUR OAKS T69.000 1 | 31 | 34 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1421 | 341485 2FOUR OAKS 69.000 341550 2FALMOUTH KU69.000 1 | 31 | 34 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1422 | 341491 2FOX HOLLOW 69.000 341548 2GORIN PRK J69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1423 | 341491 2FOX HOLLOW 69.000 342037 2PARKWAY 1 69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1424 | 341491 2FOX HOLLOW 69.000 342043 2PARKWAY 2 T69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1425 | 341491 2FOX HOLLOW 69.000 342049 2PATTON RD J69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1426 | 341491 2FOX HOLLOW 69.000 342732 5FOX HOLLOW 161.00 1 | 144 | 175 | 192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1427 | 341494 2FREDRIKBG T69.000 341497 2FREDRIKBRG 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1428 | 341494 2FREDRIKBG T69.000 341935 2N SPRINGFLD69.000 1 | 41 | 46 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1429 | 341494 2FREDRIKBG T69.000 342508 2WOODLAWN 69.000 1 | 41 | 46 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1430 | 341500 2FRENCHBURG 69.000 341644 2HOPE 69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1431 | 341500 2FRENCHBURG 69.000 341824 2MARIBA T 69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1432 | 341503 2GAP OF RG T69.000 341506 2GAP OF RIDG69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1433 | 341503 2GAP OF RG T69.000 341578 2GREGORY R T69.000 1 | 91 | 101 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1434 | 341503 2GAP OF RG T69.000 341887 2MONTICELLO 69.000 1 | 77 | 90 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1435 | 341509 2GARLIN 69.000 341512 2GARLIN T 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1436 | 341515 2GARRARD CO 69.000 324600 2LANCASTR KU69.000 1 | 90 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1437 | 341515 2GARRARD CO 69.000 341732 2LANCASTER T69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1438 | 341515 2GARRARD CO 69.000 942410 AE2-254 TAP 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1439 | 341518 2GARRARD KU 69.000 341521 2GARRARDKU T69.000 1 | 37 | 43 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1440 | 341521 2GARRARDKU T69.000 341806 2MANCHESTER 69.000 1 | 23 | 25 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1441 | 341530 2GLASGO-CLEV69.000 342043 2PARKWAY 2 T69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1442 | 341530 2GLASGO-CLEV69.000 342445 2W GLASGOW T69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1443 | 341533 2GLENDALE 69.000 341632 2HODGENVILLE69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1444 | 341533 2GLENDALE 69.000 342307 2STEPHENSBRG69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1445 | 341536 2GODDARD 69.000 341623 2HILLSBORO 69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1446 | 341536 2GODDARD 69.000 341989 2OAK RIDGE T69.000 1 | 73 | 76 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1447 | 341536 2GODDARD 69.000 342088 2PLUMMR L T 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1448 | 341536 2GODDARD 69.000 342589 4GODDARD 138.00 1 | 96 | 117 | 132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1449 | 341539 2GOLDBUG 69.000 324784 2WOFFORD 69.000 1 | 70 | 72 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1450 | 341539 2GOLDBUG 69.000 341686 2JELLICO C T69.000 1 | 77 | 90 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1451 | 341542 2GOODNIGHT 69.000 341548 2GORIN PRK J69.000 1 | 107 | 125 | 137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1452 | 341551 2GRANTS LICK69.000 341587 2GRIFFIN J 69.000 1 | 53 | 66 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1453 | 341551 2GRANTS LICK69.000 342298 2STANLY P J269.000 1 | 77 | 90 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1454 | 341554 2GRAYSON J 69.000 243726 05GRAYSO 69.000 1 | 23 | 23 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1455 | 341554 2GRAYSON J 69.000 341752 2LEON 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1456 | 341554 2GRAYSON J 69.000 342034 2PACTOLUS T 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1457 | 341563 2GREEN CO 69.000 324554 2GRENSBRG KU69.000 1 | 52 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1458 | 341563 2GREEN CO 69.000 341575 2GREENSBURG 69.000 1 | 49 | 54 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1459 | 341563 2GREEN CO 69.000 342325 2SUMMERSVIL 69.000 1 | 35 | 39 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1460 | 341563 2GREEN CO 69.000 342733 5GREEN CO 161.00 1 | 89 | 108 | 117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1461 | 341569 2GREENBRIA T69.000 341572 2GREENBRIAR 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1462 | 341569 2GREENBRIA T69.000 341806 2MANCHESTER 69.000 1 | 77 | 90 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1463 | 341575 2GREENSBURG 69.000 341854 2MCKINNY T 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1464 | 341578 2GREGORY R T69.000 341581 2GREGORY RD 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1465 | 341584 2GRIFFIN 69.000 341587 2GRIFFIN J 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1466 | 341590 2HARDWCRK 69.000 341593 2HARDWCRK T 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1467 | 341593 2HARDWCRK T 69.000 342301 2STANTON 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1468 | 341596 2HARGETT 69.000 341599 2HARGETT T 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1469 | 341599 2HARGETT T 69.000 342370 2TRAPP 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1470 | 341602 2HEADQTRS 69.000 341872 2MILLB-CRL J69.000 1 | 73 | 76 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1471 | 341602 2HEADQTRS 69.000 342280 2SNOW HILL 69.000 1 | 73 | 76 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1472 | 341605 2HEBRON 69.000 251579 08HEBRON 69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1473 | 341605 2HEBRON 69.000 342595 4HEBRON 138.00 1 | 96 | 117 | 132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1474 | 341608 2HELECHAW 69.000 243812 05LEE C 69.000 Z1 | 52 | 52 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1475 | 341608 2HELECHAW 69.000 342313 2SUBLETT J 69.000 1 | 41 | 46 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1476 | 341611 2HICKORY PL 69.000 342103 2PPG 69.000 1 | 41 | 46 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1477 | 341614 2HIGH ROCK 69.000 342520 2ZACHARIAH 69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1478 | 341617 2HIGHLAND EK69.000 341896 2MT OLIVE J 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1479 | 341620 2HILDA 69.000 342163 2ROWAN CO 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1480 | 341623 2HILLSBORO 69.000 342052 2PEASTICKS 69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1481 | 341632 2HODGENVILLE69.000 324575 2HODGENV KU 69.000 1 | 53 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1482 | 341632 2HODGENVILLE69.000 324660 2NEW HAVEN 69.000 1 | 40 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1483 | 341632 2HODGENVILLE69.000 341800 2MAGNOLIA 69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1484 | 341632 2HODGENVILLE69.000 342316 2SULPHUR CRK69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1485 | 341638 2HOLLOWAY J 69.000 342199 2S JESSAM J 69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1486 | 341638 2HOLLOWAY J 69.000 342463 2W NICHVIL T69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1487 | 341641 2HOMESTEAD S69.000 341887 2MONTICELLO 69.000 1 | 16 | 22 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1488 | 341644 2HOPE 69.000 341683 2JEFFERSNVIL69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1489 | 341647 2HORSE CV KU69.000 341650 2HORSECAVE T69.000 1 | 67 | 72 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1490 | 341650 2HORSECAVE T69.000 341651 2HORSECAVE J69.000 Z1 | 77 | 90 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1491 | 341651 2HORSECAVE J69.000 341914 2MUNFVILKU T69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1492 | 341653 2HOT MIX R T69.000 341656 2HOT MIX RD 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1493 | 341653 2HOT MIX R T69.000 341890 2MORGAN CO 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1494 | 341659 2HT ADAMS 69.000 341662 2HT ADAMS T 69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1495 | 341662 2HT ADAMS T 69.000 341671 2HUNT FARM J69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1496 | 341662 2HT ADAMS T 69.000 341857 2MERCR IND 69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1497 | 341665 2HUNT 69.000 341701 2JK SMITH 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1498 | 341665 2HUNT 69.000 341869 2MILL HUNT T69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1499 | 341665 2HUNT 69.000 342596 4HUNT 138.00 1 | 96 | 117 | 132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1500 | 341671 2HUNT FARM J69.000 342061 2PERRYVILLE 69.000 1 | 41 | 46 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1501 | 341677 2INDEX 69.000 341890 2MORGAN CO 69.000 1 | 41 | 46 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1502 | 341683 2JEFFERSNVIL69.000 342100 2POWELL CO 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1503 | 341686 2JELLICO C T69.000 341689 2JELLICO CRK69.000 1 | 41 | 46 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1504 | 341686 2JELLICO C T69.000 342076 2PINE KNOT 69.000 1 | 71 | 74 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1505 | 341692 2JENNY WIL T69.000 341695 2JENNY WILEY69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1506 | 341692 2JENNY WIL T69.000 342343 2THELMA 69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1507 | 341701 2JK SMITH 69.000 342370 2TRAPP 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1508 | 341704 2JOE TICH 69.000 341707 2JOE TICH T 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1509 | 341707 2JOE TICH T 69.000 342427 2W BARDSTWN 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1510 | 341713 2KARGLE 69.000 324519 2ETOWN KU 69.000 1 | 89 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1511 | 341716 2KEAVY 69.000 341722 2KEAVY 2 T 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1512 | 341719 2KEAVY 1 T 69.000 341740 2LAUREL CO 69.000 1 | 77 | 90 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1513 | 341719 2KEAVY 1 T 69.000 342073 2PINE GRV T 69.000 1 | 77 | 90 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1514 | 341722 2KEAVY 2 T 69.000 341740 2LAUREL CO 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1515 | 341722 2KEAVY 2 T 69.000 342187 2S CORBIN 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1516 | 341725 2KEITH 69.000 342007 2OWEN CO 69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1517 | 341725 2KEITH 69.000 342058 2PENN 69.000 1 | 41 | 46 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1518 | 341728 2KNOB LICK 69.000 341854 2MCKINNY T 69.000 1 | 41 | 46 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1519 | 341731 2LANCASTER 69.000 341732 2LANCASTER T69.000 1 | 57 | 63 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1520 | 341732 2LANCASTER T69.000 341959 2NEWBY 1 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1521 | 341734 2LAUR C IP T69.000 341737 2LAUR CO IP 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1522 | 341734 2LAUR C IP T69.000 341929 2N LONDON 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1523 | 341740 2LAUREL CO 69.000 324576 2HOPEWELL 69.000 1 | 67 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1524 | 341740 2LAUREL CO 69.000 342754 5LAUREL CO 161.00 1 | 144 | 152 | 166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1525 | 341746 2LEBANON J 69.000 342253 2SHEPHEVIL J69.000 1 | 77 | 90 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1526 | 341749 2LEES LICK 69.000 342058 2PENN 69.000 1 | 36 | 40 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1527 | 341749 2LEES LICK 69.000 342133 2RENAKER 69.000 1 | 36 | 40 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1528 | 341752 2LEON 69.000 243737 05LEONKY 69.000 Z1 | 55 | 66 | 69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1529 | 341755 2LIBER CH T 69.000 324527 2FARLEY KU 69.000 1 | 66 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1530 | 341755 2LIBER CH T 69.000 341758 2LIBERT CHUR69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1531 | 341761 2LIBERTY J 69.000 341767 2LIBERTYKU T69.000 1 | 53 | 66 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1532 | 341761 2LIBERTY J 69.000 341896 2MT OLIVE J 69.000 1 | 53 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1533 | 341761 2LIBERTY J 69.000 342760 5LIBERTY J 161.00 1 | 89 | 109 | 123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1534 | 341764 2LIBERTY KU 69.000 341767 2LIBERTYKU T69.000 1 | 37 | 43 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1535 | 341767 2LIBERTYKU T69.000 342064 2PEYTONS ST 69.000 1 | 77 | 90 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1536 | 341772 2LOGAN 69.000 341774 2LOGAN 2 T 69.000 1 | 89 | 98 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1537 | 341774 2LOGAN 2 T 69.000 341775 2LOGAN TAP 69.000 1 | 89 | 98 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1538 | 341775 2LOGAN TAP 69.000 342247 2SHELBY CO 69.000 1 | 89 | 98 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1539 | 341776 2LORETTO 69.000 342208 2S SPRINGF T69.000 1 | 49 | 54 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1540 | 341776 2LORETTO 69.000 342316 2SULPHUR CRK69.000 1 | 41 | 46 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1541 | 341779 2LOW GAP 69.000 341782 2LOW GAP T 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1542 | 341782 2LOW GAP T 69.000 342475 2WARNOCK 69.000 1 | 77 | 90 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1543 | 341785 2LYMAN BW 69.000 341788 2LYMAN BW T 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1544 | 341788 2LYMAN BW T 69.000 342155 2ROANOKE T 69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1545 | 341788 2LYMAN BW T 69.000 342379 2TUNNEL H T 69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1546 | 341791 2MACKVIL KU 69.000 341794 2MACKVILKU T69.000 1 | 37 | 43 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1547 | 341794 2MACKVILKU T69.000 341935 2N SPRINGFLD69.000 1 | 53 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1548 | 341794 2MACKVILKU T69.000 342061 2PERRYVILLE 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1549 | 341797 2MAGGARD 69.000 342265 2SKAGGS 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1550 | 341800 2MAGNOLIA 69.000 342325 2SUMMERSVIL 69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1551 | 341803 2MAGOFFIN CO69.000 342310 2SUBLETT 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1552 | 341803 2MAGOFFIN CO69.000 342313 2SUBLETT J 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1553 | 341809 2MAPLESVIL T69.000 341812 2MAPLESVILLE69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1554 | 341809 2MAPLESVIL T69.000 341929 2N LONDON 69.000 1 | 114 | 140 | 146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1555 | 341815 2MARETBURG 69.000 341818 2MARETBURG T69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1556 | 341818 2MARETBURG T69.000 342472 2WALNUT GROV69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1557 | 341821 2MARIBA 69.000 341824 2MARIBA T 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1558 | 341824 2MARIBA T 69.000 341833 2MAYTOWN T 69.000 1 | 77 | 90 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1559 | 341827 2MARTIN CO 69.000 342343 2THELMA 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1560 | 341830 2MAYTOWN 69.000 341833 2MAYTOWN T 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1561 | 341833 2MAYTOWN T 69.000 341890 2MORGAN CO 69.000 1 | 58 | 68 | 74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1562 | 341836 2MAZIE 69.000 341953 2NEW FOUNDL 69.000 1 | 77 | 90 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1563 | 341836 2MAZIE 69.000 342265 2SKAGGS 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1564 | 341839 2MBUSA 69.000 341842 2MBUSA T 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1565 | 341845 2MCCREARY CO69.000 342139 2REVELO KU T69.000 1 | 73 | 76 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1566 | 341845 2MCCREARY CO69.000 342490 2WHITLEY CTY69.000 1 | 71 | 74 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1567 | 341845 2MCCREARY CO69.000 342778 5MCCREARY CO161.00 1 | 96 | 117 | 132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1568 | 341848 2MCKEE 69.000 342223 2SAND GAP T 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1569 | 341848 2MCKEE 69.000 342391 2TYNER 69.000 1 | 66 | 69 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1570 | 341851 2MCKINNEY 69.000 341854 2MCKINNY T 69.000 1 | 23 | 25 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1571 | 341857 2MERCR IND 69.000 342406 2VAN ARSDELL69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1572 | 341860 2MIDDL CRK T69.000 341863 2MIDDLE CRK 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1573 | 341869 2MILL HUNT T69.000 341875 2MILLER HUNT69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1574 | 341869 2MILL HUNT T69.000 342259 2SIDEVIEW 69.000 1 | 77 | 90 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1575 | 341872 2MILLB-CRL J69.000 341878 2MILLERSB EK69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1576 | 341887 2MONTICELLO 69.000 342268 2SLAT 69.000 1 | 77 | 90 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1577 | 341890 2MORGAN CO 69.000 246973 05MORGCO 69.000 Z1 | 69 | 69 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1578 | 341893 2MT OLIVE 69.000 341896 2MT OLIVE J 69.000 1 | 42 | 46 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1579 | 341908 2MUNFVIL EK 69.000 341914 2MUNFVILKU T69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1580 | 341911 2MUNFVIL KU 69.000 341914 2MUNFVILKU T69.000 1 | 37 | 43 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1581 | 341917 2MUNK 69.000 341998 2OAKLEY NOEL69.000 1 | 77 | 90 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1582 | 341920 2MUNK J 69.000 341998 2OAKLEY NOEL69.000 1 | 77 | 90 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1583 | 341920 2MUNK J 69.000 342502 2WILLIAMSTWN69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1584 | 341923 2MURPHYSVIL 69.000 324717 2SARDIS TAP 69.000 1 | 45 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1585 | 341923 2MURPHYSVIL 69.000 325019 2KENTON-6 69.000 1 | 53 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1586 | 341923 2MURPHYSVIL 69.000 342091 2PLUMVILLE 69.000 1 | 53 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1587 | 341923 2MURPHYSVIL 69.000 342280 2SNOW HILL 69.000 1 | 53 | 66 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1588 | 341929 2N LONDON 69.000 324662 2N LONDON KU69.000 1 | 73 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1589 | 341935 2N SPRINGFLD69.000 324736 2SPRINGFL KU69.000 1 | 49 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1590 | 341935 2N SPRINGFLD69.000 342208 2S SPRINGF T69.000 1 | 35 | 39 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1591 | 341938 2NANCY 69.000 342505 2WINDSOR 69.000 1 | 53 | 66 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1592 | 341938 2NANCY 69.000 342526 2ZOLLICOF T 69.000 1 | 77 | 90 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1593 | 341941 2NELSN VAL T69.000 341947 2NELSON VAL 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1594 | 341941 2NELSN VAL T69.000 341971 2NORWOOD 69.000 1 | 41 | 46 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1595 | 341944 2NELSON CO 69.000 324288 4NELSON CO 138.00 1 | 144 | 152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1596 | 341944 2NELSON CO 69.000 342424 2W BARDST J 69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1597 | 341944 2NELSON CO 69.000 342514 2WOOSLEY 69.000 1 | 77 | 90 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1598 | 341950 2NEW CASTLE 69.000 342007 2OWEN CO 69.000 1 | 77 | 90 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1599 | 341953 2NEW FOUNDL 69.000 342229 2SANDY HOOK 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1600 | 341962 2NEWBY 2 69.000 342361 2TODDVILLE T69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1601 | 341965 2NICHOLASVIL69.000 342199 2S JESSAM J 69.000 1 | 77 | 90 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1602 | 341971 2NORWOOD 69.000 342115 2PULASK CO 69.000 1 | 73 | 76 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1603 | 341974 2NORWOOD T 69.000 342256 2SHOPVILLE 69.000 1 | 77 | 90 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1604 | 341977 2OAK HILL 69.000 341983 2OAK HILL T 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1605 | 341980 2OAK HILL NO69.000 341983 2OAK HILL T 69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1606 | 341980 2OAK HILL NO69.000 342286 2SOMERSET 69.000 1 | 77 | 90 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1607 | 341983 2OAK HILL T 69.000 342469 2W SOMERSET 69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1608 | 341986 2OAK RIDGE 69.000 341989 2OAK RIDGE T69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1609 | 342000 5GAS 161.00 342703 5CASEY CO 161.00 1 | 148 | 153 | 158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1610 | 342000 5GAS 161.00 342760 5LIBERTY J 161.00 1 | 148 | 153 | 158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1611 | 342007 2OWEN CO 69.000 324455 2BROMLEY 69.000 1 | 49 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1612 | 342007 2OWEN CO 69.000 342008 4OWEN CO 138.00 1 | 139 | 152 | 166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1613 | 342007 2OWEN CO 69.000 342010 2OWEN CO J1 69.000 1 | 89 | 96 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1614 | 342007 2OWEN CO 69.000 342013 2OWEN CO J2 69.000 1 | 77 | 88 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1615 | 342008 4OWEN CO 138.00 324290 4OWEN CO TAP138.00 1 | 194 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1616 | 342016 2OWENS IL 69.000 342019 2OWENS IL J 69.000 1 | 41 | 46 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1617 | 342022 2OWINGSVIL T69.000 342025 2OWINGVIL KU69.000 1 | 37 | 43 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1618 | 342022 2OWINGSVIL T69.000 342052 2PEASTICKS 69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1619 | 342022 2OWINGSVIL T69.000 342112 2PRESTON T 69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1620 | 342031 2PACTOLUS 69.000 342034 2PACTOLUS T 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1621 | 342037 2PARKWAY 1 69.000 342040 2PARKWAY 2 69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1622 | 342049 2PATTON RD J69.000 342161 2ROSEVILLE T69.000 1 | 39 | 43 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1623 | 342049 2PATTON RD J69.000 342319 2SUMM SHAD J69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1624 | 342055 2PELFREY 69.000 243742 05CORYSS 69.000 1 | 35 | 39 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1625 | 342058 2PENN 69.000 324951 2SCOTT CO 69.000 1 | 52 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1626 | 342067 2PHIL 69.000 342505 2WINDSOR 69.000 1 | 53 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1627 | 342070 2PINE GROVE 69.000 342073 2PINE GRV T 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1628 | 342073 2PINE GRV T 69.000 342451 2W LONDON 69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1629 | 342076 2PINE KNOT 69.000 342139 2REVELO KU T69.000 1 | 77 | 90 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1630 | 342085 2PLUMMR L 69.000 342088 2PLUMMR L T 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1631 | 342091 2PLUMVILLE 69.000 342124 2RECTORVILLE69.000 1 | 53 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1632 | 342091 2PLUMVILLE 69.000 342634 4PLUMVILLE 138.00 1 | 134 | 152 | 166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1633 | 342097 2POWEL TAYL 69.000 342184 2S ANDERSON 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1634 | 342100 2POWELL CO 69.000 342301 2STANTON 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1635 | 342100 2POWELL CO 69.000 342637 4POWELL CO 138.00 1 | 96 | 117 | 132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1636 | 342103 2PPG 69.000 342106 2PPG J 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1637 | 342109 2PRESTON 69.000 342112 2PRESTON T 69.000 1 | 41 | 46 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1638 | 342115 2PULASK CO 69.000 342787 5PULASK CO 161.00 1 | 96 | 108 | 112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1639 | 342118 2RADCLIFF 69.000 342121 2T BROWN L T69.000 1 | 41 | 46 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1640 | 342121 2T BROWN L T69.000 342328 2T BROWN LOG69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1641 | 342121 2T BROWN L T69.000 342415 2VINE GROV J69.000 1 | 41 | 46 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1642 | 342127 2REDBUSH 69.000 342265 2SKAGGS 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1643 | 342127 2REDBUSH 69.000 342421 2VOLGA 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1644 | 342130 2REID VILLAG69.000 342259 2SIDEVIEW 69.000 1 | 41 | 46 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1645 | 342133 2RENAKER 69.000 324492 2CYNTHIAN SW69.000 1 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1646 | 342133 2RENAKER 69.000 342355 2THREE M T 69.000 1 | 53 | 66 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1647 | 342133 2RENAKER 69.000 342640 4RENAKER 138.00 1 | 80 | 98 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1648 | 342136 2REVELO KU 69.000 342139 2REVELO KU T69.000 1 | 37 | 43 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1649 | 342145 2RICHARDSON 69.000 342487 2WEBSTER RD 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1650 | 342154 2ROANOKE 69.000 342155 2ROANOKE T 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1651 | 342157 2ROGERSVIL J69.000 324708 2ROGERSVILLE69.000 1 | 114 | 127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1652 | 342157 2ROGERSVIL J69.000 342418 2VINE GROVE 69.000 1 | 63 | 70 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1653 | 342160 2ROSEVILLE 69.000 342161 2ROSEVILLE T69.000 1 | 53 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1654 | 342161 2ROSEVILLE T69.000 342334 2TEMPLE HILL69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1655 | 342163 2ROWAN CO 69.000 342649 4ROWAN CO 138.00 1 | 62 | 76 | 86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1656 | 342166 2RUSS SPEK T69.000 342169 2RUSS SPKU T69.000 1 | 77 | 90 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1657 | 342166 2RUSS SPEK T69.000 342172 2RUSS SPR EK69.000 1 | 35 | 39 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1658 | 342166 2RUSS SPEK T69.000 342235 2SEWELTN J 69.000 1 | 53 | 66 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1659 | 342169 2RUSS SPKU T69.000 342175 2RUSS SPR KU69.000 1 | 37 | 43 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1660 | 342169 2RUSS SPKU T69.000 342178 2RUSSEL CO 69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1661 | 342178 2RUSSEL CO 69.000 342232 2SEWELLTON 69.000 1 | 73 | 76 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1662 | 342178 2RUSSEL CO 69.000 342793 5RUSSEL CO 161.00 1 | 144 | 152 | 166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1663 | 342184 2S ANDERSON 69.000 324445 2BONDS MILL 69.000 1 | 89 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1664 | 342184 2S ANDERSON 69.000 324445 2BONDS MILL 69.000 2 | 83 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1665 | 342184 2S ANDERSON 69.000 342262 2SINAI 69.000 1 | 77 | 90 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1666 | 342186 2S BARDSTWN 69.000 342424 2W BARDST J 69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1667 | 342186 2S BARDSTWN 69.000 342427 2W BARDSTWN 69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1668 | 342196 2WHITE OAK 69.000 342391 2TYNER 69.000 1 | 66 | 69 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1669 | 342199 2S JESSAM J 69.000 342202 2S JESSAMINE69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1670 | 342208 2S SPRINGF T69.000 342211 2S SPRINGFLD69.000 1 | 35 | 39 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1671 | 342214 2SALEM EK 69.000 342217 2SALEM EK T 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1672 | 342217 2SALEM EK T 69.000 342481 2WEBB CR R T69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1673 | 342217 2SALEM EK T 69.000 342505 2WINDSOR 69.000 1 | 53 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1674 | 342218 2SALT LICK 138.00 247897 05SNAG FK SS138.00 Z1 | 99999 | 99999 | 99999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1675 | 342220 2SAND GAP 69.000 342223 2SAND GAP T 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1676 | 342232 2SEWELLTON 69.000 324787 2UNION UNDWR69.000 1 | 42 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1677 | 342235 2SEWELTN J 69.000 342481 2WEBB CR R T69.000 1 | 53 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1678 | 342238 2SEYMOUR 69.000 342241 2SEYMOUR T 69.000 1 | 114 | 127 | 133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1679 | 342247 2SHELBY CO 69.000 342248 2SHELBY TAP 69.000 1 | 89 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1680 | 342247 2SHELBY CO 69.000 342410 2VEECHDALE 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1681 | 342247 2SHELBY CO 69.000 342808 5SHELBY CO 161.00 1 | 96 | 117 | 132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1682 | 342248 2SHELBY TAP 69.000 324718 2SHELBY CO T69.000 1 | 89 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1683 | 342250 2SHEPHEVIL 69.000 342253 2SHEPHEVIL J69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1684 | 342265 2SKAGGS 69.000 342658 4SKAGGS 138.00 1 | 114 | 148 | 166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1685 | 342268 2SLAT 69.000 342478 2WAYNE CO 69.000 1 | 77 | 90 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1686 | 342271 2SMITHRSVIL 69.000 342274 2SMITHRVIL T69.000 1 | 41 | 46 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1687 | 342277 2SNOW 69.000 342283 2SNOW T 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1688 | 342283 2SNOW T 69.000 342322 2SUMM SHADE 69.000 1 | 77 | 84 | 86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1689 | 342286 2SOMERSET 69.000 342287 2SOMERSET KU69.000 1 | 90 | 115 | 129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1690 | 342287 2SOMERSET KU69.000 324531 2FERGUSON SO69.000 1 | 83 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1691 | 342287 2SOMERSET KU69.000 324737 2SOMERSET SO69.000 1 | 49 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1692 | 342292 2STANLEY PRK69.000 342295 2STANLY P J169.000 1 | 114 | 127 | 133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1693 | 342292 2STANLEY PRK69.000 342298 2STANLY P J269.000 1 | 103 | 108 | 117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1694 | 342292 2STANLEY PRK69.000 342667 4STANLEY PRK138.00 1 | 144 | 152 | 166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1695 | 342307 2STEPHENSBRG69.000 324509 2EASTVIEW 69.000 1 | 45 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1696 | 342307 2STEPHENSBRG69.000 342403 2UPTON T 69.000 1 | 35 | 39 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1697 | 342307 2STEPHENSBRG69.000 342412 2VERTREES 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1698 | 342319 2SUMM SHAD J69.000 342322 2SUMM SHADE 69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1699 | 342319 2SUMM SHAD J69.000 342334 2TEMPLE HILL69.000 1 | 49 | 54 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1700 | 342322 2SUMM SHADE 69.000 342436 2W COLUMBI T69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1701 | 342322 2SUMM SHADE 69.000 342814 5SUMM SHADE 161.00 1 | 114 | 148 | 166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1702 | 342337 2THARP 69.000 342340 2THARP T 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1703 | 342340 2THARP T 69.000 324519 2ETOWN KU 69.000 1 | 103 | 132 | 137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1704 | 342343 2THELMA 69.000 246971 05THELM2 69.000 1 | 71 | 71 | 74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1705 | 342343 2THELMA 69.000 342421 2VOLGA 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1706 | 342349 2THREE LNK J69.000 342433 2W BEREA J 69.000 1 | 53 | 66 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1707 | 342352 2THREE M 69.000 342355 2THREE M T 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1708 | 342358 2TODDVILLE 69.000 342361 2TODDVILLE T69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1709 | 342364 2TOMM GOOC 69.000 342367 2TOMM GOOC T69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1710 | 342367 2TOMM GOOC T69.000 942410 AE2-254 TAP 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1711 | 342379 2TUNNEL H T 69.000 342382 2TUNNEL HILL69.000 1 | 49 | 54 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1712 | 342385 2TURKEY FT 69.000 342487 2WEBSTER RD 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1713 | 342391 2TYNER 69.000 342820 5TYNER 161.00 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1714 | 342394 2UPCHURCH 69.000 342397 2UPCHURCH T 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1715 | 342397 2UPCHURCH T 69.000 342532 2ZULA J NO 69.000 1 | 49 | 54 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1716 | 342400 2UPTON 69.000 342403 2UPTON T 69.000 1 | 31 | 34 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1717 | 342415 2VINE GROV J69.000 342418 2VINE GROVE 69.000 1 | 41 | 46 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1718 | 342430 2W BEREA 69.000 342433 2W BEREA J 69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1719 | 342430 2W BEREA 69.000 342691 4W BEREA 138.00 1 | 114 | 148 | 166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1720 | 342436 2W COLUMBI T69.000 342439 2W COLUMBIA 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1721 | 342442 2W GLASGOW 69.000 342445 2W GLASGOW T69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1722 | 342454 2W M SMITH 69.000 251315 08EKSMTH 69.000 1 | 106 | 132 | 132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1723 | 342460 2W NICHVIL 69.000 342463 2W NICHVIL T69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1724 | 342469 2W SOMERSET 69.000 342526 2ZOLLICOF T 69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1725 | 342472 2WALNUT GROV69.000 342511 2WOODSTOCK 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1726 | 342478 2WAYNE CO 69.000 342532 2ZULA J NO 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1727 | 342478 2WAYNE CO 69.000 342535 2ZULA T 69.000 1 | 49 | 54 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1728 | 342478 2WAYNE CO 69.000 342823 5WAYNE CO 161.00 1 | 127 | 131 | 135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1729 | 342481 2WEBB CR R T69.000 342484 2WEBB CR RDS69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1730 | 342487 2WEBSTER RD 69.000 250148 08EKPWEB 138.00 1 | 96 | 117 | 132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1731 | 342490 2WHITLEY CTY69.000 342493 2WHITLY C KU69.000 1 | 37 | 43 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1732 | 342490 2WHITLEY CTY69.000 342499 2WIBORG T 69.000 1 | 58 | 68 | 74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1733 | 342496 2WIBORG 69.000 342499 2WIBORG T 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1734 | 342523 2ZOLLICOF 69.000 342526 2ZOLLICOF T 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1735 | 342529 2ZULA 69.000 342535 2ZULA T 69.000 1 | 35 | 39 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1736 | 342538 4ARGENTUM 138.00 243688 05S.PORT MTR138.00 1 | 170 | 170 | 176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1737 | 342538 4ARGENTUM 138.00 342616 4LOVE HYDRO 138.00 1 | 100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1738 | 342541 4AVON 138.00 342544 4AVON-R 138.00 1 | 223 | 223 | 223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1739 | 342541 4AVON 138.00 342556 4BECKNERV T 138.00 1 | 436 | 450 | 463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1740 | 342541 4AVON 138.00 342580 4FAYETTE 138.00 1 | 229 | 252 | 259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1741 | 342541 4AVON 138.00 342631 4PARIS T 138.00 1 | 197 | 220 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1742 | 342541 4AVON 138.00 342829 7AVON 345.00 1 | 432 | 526 | 594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1743 | 342544 4AVON-R 138.00 324275 4LOUDON AVE 138.00 1 | 203 | 203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1744 | 342547 4BAKER LN 138.00 324210 4BAKER LANE 138.00 1 | 178 | 197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1745 | 342550 4BAVARIAN LF138.00 342559 4BOONE CO 138.00 1 | 197 | 220 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1746 | 342550 4BAVARIAN LF138.00 342640 4RENAKER 138.00 1 | 167 | 179 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1747 | 342553 4BECKNERV 138.00 342556 4BECKNERV T 138.00 1 | 178 | 197 | 206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1748 | 342556 4BECKNERV T 138.00 342565 4BOONESBOR T138.00 1 | 436 | 450 | 463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1749 | 342559 4BOONE CO 138.00 250054 08LONGBR 138.00 1 | 254 | 284 | 297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1750 | 342559 4BOONE CO 138.00 342646 4RICHWOOD T 138.00 1 | 229 | 255 | 267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1751 | 342559 4BOONE CO 138.00 342673 4STERLNG T 138.00 1 | 229 | 255 | 267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1752 | 342565 4BOONESBOR T138.00 325925 4BOONSBORO N138.00 1 | 166 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1753 | 342565 4BOONESBOR T138.00 342574 4DALE 138.00 1 | 229 | 296 | 358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1754 | 342568 4CENT HARDIN138.00 324047 4BLACKBRANCH138.00 1 | 227 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1755 | 342568 4CENT HARDIN138.00 324261 4HARDIN CO 138.00 1 | 208 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1756 | 342571 4CRANSTON 138.00 342589 4GODDARD 138.00 1 | 229 | 255 | 267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1757 | 342571 4CRANSTON 138.00 342649 4ROWAN CO 138.00 1 | 229 | 255 | 267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1758 | 342574 4DALE 138.00 342596 4HUNT 138.00 1 | 229 | 296 | 358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1759 | 342574 4DALE 138.00 342676 4THREE FK T 138.00 1 | 183 | 203 | 212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1760 | 342577 4FAWKES EK 138.00 324247 4FAWKES TAP 138.00 1 | 229 | 284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1761 | 342577 4FAWKES EK 138.00 324248 4FAWKES KU 138.00 1 | 229 | 296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1762 | 342577 4FAWKES EK 138.00 342607 4JK SMITH 138.00 1 | 229 | 284 | 297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1763 | 342577 4FAWKES EK 138.00 342676 4THREE FK T 138.00 1 | 183 | 203 | 212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1764 | 342577 4FAWKES EK 138.00 342691 4W BEREA 138.00 1 | 229 | 255 | 267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1765 | 342583 4FLEMINGSBRG138.00 342589 4GODDARD 138.00 1 | 184 | 206 | 226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1766 | 342583 4FLEMINGSBRG138.00 342664 4SPURLOCK 138.00 1 | 229 | 255 | 267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1767 | 342586 4GALLATIN CO138.00 324253 4GHENT 138.00 1 | 229 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1768 | 342586 4GALLATIN CO138.00 342587 1GALLATIN CO34.500 1 | 43 | 50 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1769 | 342586 4GALLATIN CO138.00 342673 4STERLNG T 138.00 1 | 229 | 255 | 267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1770 | 342589 4GODDARD 138.00 342634 4PLUMVILLE 138.00 1 | 167 | 186 | 204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1771 | 342595 4HEBRON 138.00 250152 08HEBRNG 138.00 1 | 229 | 255 | 267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1772 | 342596 4HUNT 138.00 342607 4JK SMITH 138.00 1 | 297 | 354 | 374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1773 | 342598 4INLAND C T 138.00 342664 4SPURLOCK 138.00 1 | 229 | 255 | 267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1774 | 342601 4JACKSNVIL 138.00 342604 4JACKSNVIL T138.00 1 | 183 | 203 | 212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1775 | 342604 4JACKSNVIL T138.00 342631 4PARIS T 138.00 1 | 197 | 220 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1776 | 342604 4JACKSNVIL T138.00 342640 4RENAKER 138.00 1 | 197 | 215 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1777 | 342607 4JK SMITH 138.00 342610 4JK SMITH 21138.00 1 | 432 | 522 | 522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1778 | 342607 4JK SMITH 138.00 342613 4JK SMITH 22138.00 1 | 432 | 522 | 522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1779 | 342607 4JK SMITH 138.00 342637 4POWELL CO 138.00 1 | 254 | 284 | 297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1780 | 342607 4JK SMITH 138.00 342688 4UNION CTY T138.00 1 | 297 | 364 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1781 | 342610 4JK SMITH 21138.00 342832 7JK SMITH 345.00 1 | 432 | 522 | 571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1782 | 342613 4JK SMITH 22138.00 342832 7JK SMITH 345.00 1 | 432 | 522 | 571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1783 | 342622 4MAYSVIL I T138.00 342625 4MAYSVIL IND138.00 1 | 183 | 203 | 212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1784 | 342622 4MAYSVIL I T138.00 342634 4PLUMVILLE 138.00 1 | 229 | 291 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1785 | 342622 4MAYSVIL I T138.00 342664 4SPURLOCK 138.00 1 | 229 | 291 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1786 | 342631 4PARIS T 138.00 324328 4PARIS 138.00 1 | 208 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1787 | 342637 4POWELL CO 138.00 342784 5POWELL CO 161.00 1 | 144 | 175 | 198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1788 | 342640 4RENAKER 138.00 342664 4SPURLOCK 138.00 1 | 196 | 213 | 227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1789 | 342643 4RICHWOOD 138.00 342646 4RICHWOOD T 138.00 1 | 178 | 197 | 206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1790 | 342646 4RICHWOOD T 138.00 342667 4STANLEY PRK138.00 1 | 229 | 255 | 267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1791 | 342649 4ROWAN CO 138.00 324302 4RODBURN 138.00 1 | 143 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1792 | 342649 4ROWAN CO 138.00 342658 4SKAGGS 138.00 1 | 229 | 255 | 264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1793 | 342661 4SPUR-KENT-R138.00 324267 4KENTON 138.00 1 | 240 | 291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1794 | 342661 4SPUR-KENT-R138.00 342664 4SPURLOCK 138.00 1 | 259 | 291 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1795 | 342664 4SPURLOCK 138.00 342667 4STANLEY PRK138.00 1 | 229 | 255 | 267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1796 | 342664 4SPURLOCK 138.00 342838 7SPURLOCK 345.00 1 | 432 | 522 | 571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1797 | 342664 4SPURLOCK 138.00 342838 7SPURLOCK 345.00 2 | 288 | 351 | 396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1798 | 342664 4SPURLOCK 138.00 342838 7SPURLOCK 345.00 3 | 361 | 468 | 528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1799 | 342670 4STERLING 138.00 342673 4STERLNG T 138.00 1 | 183 | 203 | 212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1800 | 342676 4THREE FK T 138.00 342679 4THREE FORKS138.00 1 | 229 | 255 | 267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1801 | 342685 4UNION CITY 138.00 342688 4UNION CTY T138.00 1 | 254 | 284 | 297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1802 | 342688 4UNION CTY T138.00 324276 4LAKE REBA T138.00 1 | 240 | 306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1803 | 342694 5BARREN CO 161.00 342814 5SUMM SHADE 161.00 1 | 153 | 157 | 162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1804 | 342697 5BEATTYV J 161.00 324138 5DELVINTA 161.00 1 | 219 | 223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1805 | 342697 5BEATTYV J 161.00 324430 2BEATTYVI KU69.000 1 | 84 | 84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1806 | 342697 5BEATTYV J 161.00 342780 5MILL CRK T 161.00 1 | 226 | 233 | 284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1807 | 342700 5BULLITT CO 161.00 326975 5CEDAR GRV 161.00 1 | 219 | 277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1808 | 342700 5BULLITT CO 161.00 326998 5BULLITT TAP161.00 1 | 267 | 298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1809 | 342700 5BULLITT CO 161.00 342819 5TAYLORSV T 161.00 1 | 268 | 331 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1810 | 342703 5CASEY CO 161.00 342769 5MARION CO 161.00 1 | 148 | 153 | 158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1811 | 342715 5COOPER1 161.00 342718 5COOPER2 161.00 1 | 468 | 501 | 669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1812 | 342715 5COOPER1 161.00 342790 5PULASK CO J161.00 1 | 267 | 298 | 312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1813 | 342715 5COOPER1 161.00 342799 5S OAKHILL 161.00 1 | 267 | 298 | 312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1814 | 342718 5COOPER2 161.00 324141 5ELIHU 161.00 1 | 219 | 277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1815 | 342718 5COOPER2 161.00 342727 5DENNY 161.00 1 | 186 | 210 | 231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1816 | 342718 5COOPER2 161.00 342757 5LAUREL DAM 161.00 1 | 267 | 298 | 312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1817 | 342721 5DARWIN TH 161.00 342724 5DARWIN TH T161.00 1 | 207 | 230 | 241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1818 | 342724 5DARWIN TH T161.00 342766 5LITTLE MT T161.00 1 | 297 | 331 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1819 | 342724 5DARWIN TH T161.00 342808 5SHELBY CO 161.00 1 | 243 | 271 | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1820 | 342730 5FALL ROCK 161.00 342820 5TYNER 161.00 1 | 234 | 250 | 273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1821 | 342732 5FOX HOLLOW 161.00 361603 5E GLASGOW T161.00 1 | 267 | 298 | 299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1822 | 342733 5GREEN CO 161.00 342814 5SUMM SHADE 161.00 1 | 267 | 298 | 312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1823 | 342733 5GREEN CO 161.00 342817 5TAYLOR CO J161.00 1 | 267 | 298 | 312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1824 | 342736 5GREEN HAL T161.00 324138 5DELVINTA 161.00 1 | 219 | 251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1825 | 342736 5GREEN HAL T161.00 342739 5GREEN HALL 161.00 1 | 207 | 230 | 241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1826 | 342736 5GREEN HAL T161.00 342820 5TYNER 161.00 1 | 230 | 250 | 268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1827 | 342742 5JABEZ 161.00 342745 5JABEZ T 161.00 1 | 207 | 230 | 241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1828 | 342745 5JABEZ T 161.00 342751 5JAMESTOWN T161.00 1 | 267 | 298 | 312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1829 | 342745 5JABEZ T 161.00 342799 5S OAKHILL 161.00 1 | 267 | 298 | 312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1830 | 342748 5JAMESTOWN 161.00 342751 5JAMESTOWN T161.00 1 | 207 | 230 | 241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1831 | 342751 5JAMESTOWN T161.00 342796 5RUSSEL CO J161.00 1 | 218 | 238 | 256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1832 | 342754 5LAUREL CO 161.00 342757 5LAUREL DAM 161.00 1 | 174 | 200 | 222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1833 | 342754 5LAUREL CO 161.00 342781 5PITTSBURG 161.00 1 | 174 | 200 | 222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1834 | 342760 5LIBERTY J 161.00 342790 5PULASK CO J161.00 1 | 230 | 256 | 268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1835 | 342763 5LITTLE MT 161.00 342766 5LITTLE MT T161.00 1 | 207 | 230 | 241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1836 | 342766 5LITTLE MT T161.00 342819 5TAYLORSV T 161.00 1 | 268 | 331 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1837 | 342769 5MARION CO 161.00 342770 4MARION CO 138.00 1 | 192 | 234 | 264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1838 | 342769 5MARION CO 161.00 342775 5MARION IP T161.00 1 | 186 | 210 | 231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1839 | 342770 4MARION CO 138.00 324271 4LEBANON 138.00 1 | 187 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1840 | 342772 5MARION IP 161.00 342797 5S MARION IT161.00 1 | 207 | 230 | 241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1841 | 342775 5MARION IP T161.00 342797 5S MARION IT161.00 1 | 207 | 230 | 241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1842 | 342775 5MARION IP T161.00 342805 5SALOMA T 161.00 1 | 186 | 210 | 231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1843 | 342778 5MCCREARY CO161.00 360473 5JELLICO TN 161.00 1 | 181 | 181 | 181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1844 | 342778 5MCCREARY CO161.00 360486 5WAYNE CO KY161.00 1 | 181 | 181 | 181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1845 | 342778 5MCCREARY CO161.00 361579 5WINFIELD TN161.00 1 | 226 | 226 | 249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1846 | 342779 5MILLER CRK 161.00 342780 5MILL CRK T 161.00 1 | 267 | 298 | 312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1847 | 342780 5MILL CRK T 161.00 342784 5POWELL CO 161.00 1 | 226 | 233 | 284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1848 | 342781 5PITTSBURG 161.00 324688 2PITTSBRG KU69.000 1 | 112 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1849 | 342781 5PITTSBURG 161.00 342820 5TYNER 161.00 1 | 234 | 250 | 312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1850 | 342787 5PULASK CO 161.00 342790 5PULASK CO J161.00 1 | 163 | 168 | 173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1851 | 342793 5RUSSEL CO 161.00 342796 5RUSSEL CO J161.00 1 | 210 | 240 | 247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1852 | 342796 5RUSSEL CO J161.00 360448 5WOLF CRK HP161.00 1 | 267 | 298 | 312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1853 | 342797 5S MARION IT161.00 342798 5S MARION IP161.00 1 | 207 | 230 | 241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1854 | 342802 5SALOMA 161.00 342805 5SALOMA T 161.00 1 | 207 | 230 | 241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1855 | 342805 5SALOMA T 161.00 342817 5TAYLOR CO J161.00 1 | 267 | 298 | 312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1856 | 342814 5SUMM SHADE 161.00 360334 5SUMMER SHAD161.00 1 | 267 | 289 | 312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1857 | 342814 5SUMM SHADE 161.00 361788 5SUM SHAD TP161.00 1 | 396 | 420 | 420 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1858 | 342817 5TAYLOR CO J161.00 325921 5TAYLOR CO 161.00 1 | 159 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1859 | 342818 5TAYLORSVILL161.00 342819 5TAYLORSV T 161.00 1 | 267 | 298 | 312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1860 | 342823 5WAYNE CO 161.00 360486 5WAYNE CO KY161.00 1 | 127 | 131 | 135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1861 | 342829 7AVON 345.00 342835 7N CLARK 345.00 1 | 910 | 938 | 966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1862 | 342832 7JK SMITH 345.00 342835 7N CLARK 345.00 1 | 1274 | 1421 | 1488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1863 | 342832 7JK SMITH 345.00 342841 7W GARRARDEK345.00 1 | 1260 | 1403 | 1458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1864 | 342835 7N CLARK 345.00 342838 7SPURLOCK 345.00 1 | 1056 | 1151 | 1238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1865 | 342838 7SPURLOCK 345.00 249581 08MELDAL 345.00 1 | 1274 | 1421 | 1488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1866 | 342838 7SPURLOCK 345.00 253077 09STUART 345.00 1 | 1240 | 1532 | 1792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1867 | 342841 7W GARRARDEK345.00 325074 7W GARRARDKU345.00 Z1 | 1169 | 1370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1868 | 342844 8SOUTHGEN 500.00 384157 8MILLER8 500.00 1 | 9999 | 9999 | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1869 | 342847 9NORTHGEN 765.00 243205 05COOK 765.00 1 | 9999 | 9999 | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1870 | 942410 AE2-254 TAP 69.000 942411 AE2-254 C O169.000 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1871 | 942411 AE2-254 C O169.000 942412 AE2-254 E O169.000 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Monitored Buses
MON# | BUS | RECORD | TYPE | MIN/DROP | MAX/RISE
1 | 339206 AE1-143 C 161.00 | EKPC' | RANGE | 0.94 | 1.05
2 | 341002 2AIRPORT RD 69.000 | EKPC' | RANGE | 0.94 | 1.05
3 | 341005 2ALBANY 69.000 | EKPC' | RANGE | 0.94 | 1.05
4 | 341008 2ALCAN 69.000 | EKPC' | RANGE | 0.94 | 1.05
5 | 341014 2ANNVILLE 69.000 | EKPC' | RANGE | 0.94 | 1.05
6 | 341017 2ANNVILLE T 69.000 | EKPC' | RANGE | 0.94 | 1.05
7 | 341020 2ARGENTUM 69.000 | EKPC' | RANGE | 0.94 | 1.05
8 | 341029 2ASAHI M W 69.000 | EKPC' | RANGE | 0.94 | 1.05
9 | 341032 2ASAHI M W T69.000 | EKPC' | RANGE | 0.94 | 1.05
10 | 341035 2BACON CRK 69.000 | EKPC' | RANGE | 0.94 | 1.05
11 | 341038 2BACON CRK T69.000 | EKPC' | RANGE | 0.94 | 1.05
12 | 341041 2BAKER LN 69.000 | EKPC' | RANGE | 0.94 | 1.05
13 | 341044 2BALLARD 69.000 | EKPC' | RANGE | 0.94 | 1.05
14 | 341047 2BALLTOWN 69.000 | EKPC' | RANGE | 0.94 | 1.05
15 | 341050 2BANK LCK 69.000 | EKPC' | RANGE | 0.94 | 1.05
16 | 341053 2BARD SHOP 69.000 | EKPC' | RANGE | 0.94 | 1.05
17 | 341056 2BARD SHOP T69.000 | EKPC' | RANGE | 0.94 | 1.05
18 | 341059 2BARREN CO 69.000 | EKPC' | RANGE | 0.94 | 1.05
19 | 341062 2BASS 69.000 | EKPC' | RANGE | 0.94 | 1.05
20 | 341065 2BEAM 69.000 | EKPC' | RANGE | 0.94 | 1.05
21 | 341068 2BEAM T 69.000 | EKPC' | RANGE | 0.94 | 1.05
22 | 341071 2BEATTYV 69.000 | EKPC' | RANGE | 0.94 | 1.05
23 | 341074 2BEATTYV D 69.000 | EKPC' | RANGE | 0.94 | 1.05
24 | 341077 2BEATTYV J 69.000 | EKPC' | RANGE | 0.94 | 1.05
25 | 341080 2BECKTON 69.000 | EKPC' | RANGE | 0.94 | 1.05
26 | 341089 2BEKAERT 69.000 | EKPC' | RANGE | 0.94 | 1.05
27 | 341092 2BELLVIEW 69.000 | EKPC' | RANGE | 0.94 | 1.05
28 | 341095 2BELLVIEW T 69.000 | EKPC' | RANGE | 0.94 | 1.05
29 | 341098 2BEREAKU T 69.000 | EKPC' | RANGE | 0.94 | 1.05
30 | 341104 2BIG BONE 69.000 | EKPC' | RANGE | 0.94 | 1.05
31 | 341107 2BIG BONE T 69.000 | EKPC' | RANGE | 0.94 | 1.05
32 | 341110 2BIG CREEK 69.000 | EKPC' | RANGE | 0.94 | 1.05
33 | 341113 2BIG CREEK T69.000 | EKPC' | RANGE | 0.94 | 1.05
34 | 341114 2BIG HILL 69.000 | EKPC' | RANGE | 0.94 | 1.05
35 | 341115 2BIG HILL T 69.000 | EKPC' | RANGE | 0.94 | 1.05
36 | 341116 2BIG WOODS 69.000 | EKPC' | RANGE | 0.94 | 1.05
37 | 341119 2BIG WOODS J69.000 | EKPC' | RANGE | 0.94 | 1.05
38 | 341122 2BILL WELL T69.000 | EKPC' | RANGE | 0.94 | 1.05
39 | 341125 2BILL WELLS 69.000 | EKPC' | RANGE | 0.94 | 1.05
40 | 341131 2BLEVINS V T69.000 | EKPC' | RANGE | 0.94 | 1.05
41 | 341134 2BLEVINS VAL69.000 | EKPC' | RANGE | 0.94 | 1.05
42 | 341137 2BLOOMFLD 69.000 | EKPC' | RANGE | 0.94 | 1.05
43 | 341140 2BLUE G PW 69.000 | EKPC' | RANGE | 0.94 | 1.05
44 | 341143 2BLUE G PW T69.000 | EKPC' | RANGE | 0.94 | 1.05
45 | 341149 2BON AYR 69.000 | EKPC' | RANGE | 0.94 | 1.05
46 | 341152 2BONANZA 69.000 | EKPC' | RANGE | 0.94 | 1.05
47 | 341155 2BONANZA T 69.000 | EKPC' | RANGE | 0.94 | 1.05
48 | 341158 2BONNIV DIST69.000 | EKPC' | RANGE | 0.94 | 1.05
49 | 341161 2BONNIV EK 69.000 | EKPC' | RANGE | 0.94 | 1.05
50 | 341164 2BOONE CO 69.000 | EKPC' | RANGE | 0.94 | 1.05
51 | 341167 2BOONE DIST 69.000 | EKPC' | RANGE | 0.94 | 1.05
52 | 341170 2BOONEVIL 69.000 | EKPC' | RANGE | 0.94 | 1.05
53 | 341173 2BOONEVIL T 69.000 | EKPC' | RANGE | 0.94 | 1.05
54 | 341179 2BOSTONKU 69.000 | EKPC' | RANGE | 0.94 | 1.05
55 | 341185 2BOWEN 69.000 | EKPC' | RANGE | 0.94 | 1.05
56 | 341188 2BRACKEN CO 69.000 | EKPC' | RANGE | 0.94 | 1.05
57 | 341194 2BRISTOW 69.000 | EKPC' | RANGE | 0.94 | 1.05
58 | 341197 2BRODHEAD 69.000 | EKPC' | RANGE | 0.94 | 1.05
59 | 341200 2BROMLEYEK 69.000 | EKPC' | RANGE | 0.94 | 1.05
60 | 341203 2BRONSTON 69.000 | EKPC' | RANGE | 0.94 | 1.05
61 | 341206 2BRONSTON T 69.000 | EKPC' | RANGE | 0.94 | 1.05
62 | 341209 2BROUGTWN T 69.000 | EKPC' | RANGE | 0.94 | 1.05
63 | 341210 2BROUGHT TWN69.000 | EKPC' | RANGE | 0.94 | 1.05
64 | 341212 2BUDD 69.000 | EKPC' | RANGE | 0.94 | 1.05
65 | 341215 2BULLITT CO 69.000 | EKPC' | RANGE | 0.94 | 1.05
66 | 341218 2BULLITTSVIL69.000 | EKPC' | RANGE | 0.94 | 1.05
67 | 341224 2BURLINGTN 69.000 | EKPC' | RANGE | 0.94 | 1.05
68 | 341227 2BURLINGTN T69.000 | EKPC' | RANGE | 0.94 | 1.05
69 | 341233 2CABIN HOLLW69.000 | EKPC' | RANGE | 0.94 | 1.05
70 | 341248 2CAMPTON 69.000 | EKPC' | RANGE | 0.94 | 1.05
71 | 341251 2CANE RIDG 69.000 | EKPC' | RANGE | 0.94 | 1.05
72 | 341254 2CANE RIDG T69.000 | EKPC' | RANGE | 0.94 | 1.05
73 | 341260 2CARSON 69.000 | EKPC' | RANGE | 0.94 | 1.05
74 | 341263 2CARTER CTY 69.000 | EKPC' | RANGE | 0.94 | 1.05
75 | 341266 2CARTER CY T69.000 | EKPC' | RANGE | 0.94 | 1.05
76 | 341269 2CASEY CO 69.000 | EKPC' | RANGE | 0.94 | 1.05
77 | 341272 2CAVE CITY 69.000 | EKPC' | RANGE | 0.94 | 1.05
78 | 341275 2CAVE CITY J69.000 | EKPC' | RANGE | 0.94 | 1.05
79 | 341281 2CEDAR GR 69.000 | EKPC' | RANGE | 0.94 | 1.05
80 | 341287 2CENT HARDIN69.000 | EKPC' | RANGE | 0.94 | 1.05
81 | 341293 2CHAPLIN 69.000 | EKPC' | RANGE | 0.94 | 1.05
82 | 341296 2CHAPLIN T 69.000 | EKPC' | RANGE | 0.94 | 1.05
83 | 341299 2CHARTERS 69.000 | EKPC' | RANGE | 0.94 | 1.05
84 | 341302 2CLAY CITY 69.000 | EKPC' | RANGE | 0.94 | 1.05
85 | 341305 2CLAY CITY T69.000 | EKPC' | RANGE | 0.94 | 1.05
86 | 341308 2CLAY LCK 69.000 | EKPC' | RANGE | 0.94 | 1.05
87 | 341311 2CLAY LCK J 69.000 | EKPC' | RANGE | 0.94 | 1.05
88 | 341314 2CLAY LCK SW69.000 | EKPC' | RANGE | 0.94 | 1.05
89 | 341317 2CLAY VILLAG69.000 | EKPC' | RANGE | 0.94 | 1.05
90 | 341320 2COBURG 69.000 | EKPC' | RANGE | 0.94 | 1.05
91 | 341323 2COBURG J 69.000 | EKPC' | RANGE | 0.94 | 1.05
92 | 341326 2COLEMANSVIL69.000 | EKPC' | RANGE | 0.94 | 1.05
93 | 341329 2COLESBURG 69.000 | EKPC' | RANGE | 0.94 | 1.05
94 | 341332 2COLESBURG J69.000 | EKPC' | RANGE | 0.94 | 1.05
95 | 341335 2COLUMBIA 69.000 | EKPC' | RANGE | 0.94 | 1.05
96 | 341338 2CONWAY 69.000 | EKPC' | RANGE | 0.94 | 1.05
97 | 341341 2CONWAY T 69.000 | EKPC' | RANGE | 0.94 | 1.05
98 | 341342 2CONTOWN T 69.000 | EKPC' | RANGE | 0.94 | 1.05
99 | 341343 2CONTOWN 69.000 | EKPC' | RANGE | 0.94 | 1.05
100 | 341344 2COOPER 69.000 | EKPC' | RANGE | 0.94 | 1.05
101 | 341347 2COOPER DIST69.000 | EKPC' | RANGE | 0.94 | 1.05
102 | 341350 2CRESTON 69.000 | EKPC' | RANGE | 0.94 | 1.05
103 | 341353 2CROCKETT 69.000 | EKPC' | RANGE | 0.94 | 1.05
104 | 341356 2CROCKETT T 69.000 | EKPC' | RANGE | 0.94 | 1.05
105 | 341359 2CROOKSVIL 69.000 | EKPC' | RANGE | 0.94 | 1.05
106 | 341362 2CROOKSVIL T69.000 | EKPC' | RANGE | 0.94 | 1.05
107 | 341366 2COLUMB KU 69.000 | EKPC' | RANGE | 0.94 | 1.05
108 | 341370 2COLUMB S KU69.000 | EKPC' | RANGE | 0.94 | 1.05
109 | 341377 2CYNTHIA TIE69.000 | EKPC' | RANGE | 0.94 | 1.05
110 | 341379 2DAHL ROAD 69.000 | EKPC' | RANGE | 0.94 | 1.05
111 | 341380 2DALE 69.000 | EKPC' | RANGE | 0.94 | 1.05
112 | 341381 2DAV LANE 69.000 | EKPC' | RANGE | 0.94 | 1.05
113 | 341382 2DAV LANE T 69.000 | EKPC' | RANGE | 0.94 | 1.05
114 | 341383 2DAVIS 69.000 | EKPC' | RANGE | 0.94 | 1.05
115 | 341386 2DEATSVIL 69.000 | EKPC' | RANGE | 0.94 | 1.05
116 | 341389 2DEATSVILL T69.000 | EKPC' | RANGE | 0.94 | 1.05
117 | 341390 2DEFOE TAP 69.000 | EKPC' | RANGE | 0.94 | 1.05
118 | 341391 2DEFOE 69.000 | EKPC' | RANGE | 0.94 | 1.05
119 | 341392 2DENNY 69.000 | EKPC' | RANGE | 0.94 | 1.05
120 | 341394 2PATRIOT PW 69.000 | EKPC' | RANGE | 0.94 | 1.05
121 | 341398 2DOWNING 69.000 | EKPC' | RANGE | 0.94 | 1.05
122 | 341400 2DRAVO 69.000 | EKPC' | RANGE | 0.94 | 1.05
123 | 341401 2DURO 69.000 | EKPC' | RANGE | 0.94 | 1.05
124 | 341404 2DURO T 69.000 | EKPC' | RANGE | 0.94 | 1.05
125 | 341405 2DUNCANNO LN69.000 | EKPC' | RANGE | 0.94 | 1.05
126 | 341406 2DUNCAN LN T69.000 | EKPC' | RANGE | 0.94 | 1.05
127 | 341407 2E BARDSTOWN69.000 | EKPC' | RANGE | 0.94 | 1.05
128 | 341410 2E BERNSTADT69.000 | EKPC' | RANGE | 0.94 | 1.05
129 | 341416 2E PINE KNOT69.000 | EKPC' | RANGE | 0.94 | 1.05
130 | 341419 2E SOMERSE T69.000 | EKPC' | RANGE | 0.94 | 1.05
131 | 341422 2E SOMERSET 69.000 | EKPC' | RANGE | 0.94 | 1.05
132 | 341425 2EBERLE 69.000 | EKPC' | RANGE | 0.94 | 1.05
133 | 341428 2EBERLE T 69.000 | EKPC' | RANGE | 0.94 | 1.05
134 | 341431 2EDM-JBGAL J69.000 | EKPC' | RANGE | 0.94 | 1.05
135 | 341434 2EDM-JBGAL T69.000 | EKPC' | RANGE | 0.94 | 1.05
136 | 341437 2EDMON IND P69.000 | EKPC' | RANGE | 0.94 | 1.05
137 | 341439 2ELK MT IP 69.000 | EKPC' | RANGE | 0.94 | 1.05
138 | 341443 2ELLIO CO PT69.000 | EKPC' | RANGE | 0.94 | 1.05
139 | 341446 2ELLIOT CO P69.000 | EKPC' | RANGE | 0.94 | 1.05
140 | 341449 2ELLIOTTVILL69.000 | EKPC' | RANGE | 0.94 | 1.05
141 | 341455 2ETOWN EK1 69.000 | EKPC' | RANGE | 0.94 | 1.05
142 | 341458 2ETOWN EK2 69.000 | EKPC' | RANGE | 0.94 | 1.05
143 | 341461 2FALCON EK 69.000 | EKPC' | RANGE | 0.94 | 1.05
144 | 341464 2FALL ROCK 69.000 | EKPC' | RANGE | 0.94 | 1.05
145 | 341467 2FAYETTE 69.000 | EKPC' | RANGE | 0.94 | 1.05
146 | 341470 2FLOYD EK 69.000 | EKPC' | RANGE | 0.94 | 1.05
147 | 341473 2FLOYD-SFL T69.000 | EKPC' | RANGE | 0.94 | 1.05
148 | 341476 2FOGG PIKE 69.000 | EKPC' | RANGE | 0.94 | 1.05
149 | 341479 2S BOUND RD 69.000 | EKPC' | RANGE | 0.94 | 1.05
150 | 341485 2FOUR OAKS 69.000 | EKPC' | RANGE | 0.94 | 1.05
151 | 341488 2FOUR OAKS T69.000 | EKPC' | RANGE | 0.94 | 1.05
152 | 341491 2FOX HOLLOW 69.000 | EKPC' | RANGE | 0.94 | 1.05
153 | 341494 2FREDRIKBG T69.000 | EKPC' | RANGE | 0.94 | 1.05
154 | 341497 2FREDRIKBRG 69.000 | EKPC' | RANGE | 0.94 | 1.05
155 | 341500 2FRENCHBURG 69.000 | EKPC' | RANGE | 0.94 | 1.05
156 | 341503 2GAP OF RG T69.000 | EKPC' | RANGE | 0.94 | 1.05
157 | 341506 2GAP OF RIDG69.000 | EKPC' | RANGE | 0.94 | 1.05
158 | 341509 2GARLIN 69.000 | EKPC' | RANGE | 0.94 | 1.05
159 | 341512 2GARLIN T 69.000 | EKPC' | RANGE | 0.94 | 1.05
160 | 341515 2GARRARD CO 69.000 | EKPC' | RANGE | 0.94 | 1.05
161 | 341518 2GARRARD KU 69.000 | EKPC' | RANGE | 0.94 | 1.05
162 | 341521 2GARRARDKU T69.000 | EKPC' | RANGE | 0.94 | 1.05
163 | 341530 2GLASGO-CLEV69.000 | EKPC' | RANGE | 0.94 | 1.05
164 | 341533 2GLENDALE 69.000 | EKPC' | RANGE | 0.94 | 1.05
165 | 341536 2GODDARD 69.000 | EKPC' | RANGE | 0.94 | 1.05
166 | 341539 2GOLDBUG 69.000 | EKPC' | RANGE | 0.94 | 1.05
167 | 341542 2GOODNIGHT 69.000 | EKPC' | RANGE | 0.94 | 1.05
168 | 341548 2GORIN PRK J69.000 | EKPC' | RANGE | 0.94 | 1.05
169 | 341550 2FALMOUTH KU69.000 | EKPC' | RANGE | 0.94 | 1.05
170 | 341551 2GRANTS LICK69.000 | EKPC' | RANGE | 0.94 | 1.05
171 | 341554 2GRAYSON J 69.000 | EKPC' | RANGE | 0.94 | 1.05
172 | 341563 2GREEN CO 69.000 | EKPC' | RANGE | 0.94 | 1.05
173 | 341569 2GREENBRIA T69.000 | EKPC' | RANGE | 0.94 | 1.05
174 | 341572 2GREENBRIAR 69.000 | EKPC' | RANGE | 0.94 | 1.05
175 | 341575 2GREENSBURG 69.000 | EKPC' | RANGE | 0.94 | 1.05
176 | 341578 2GREGORY R T69.000 | EKPC' | RANGE | 0.94 | 1.05
177 | 341581 2GREGORY RD 69.000 | EKPC' | RANGE | 0.94 | 1.05
178 | 341584 2GRIFFIN 69.000 | EKPC' | RANGE | 0.94 | 1.05
179 | 341587 2GRIFFIN J 69.000 | EKPC' | RANGE | 0.94 | 1.05
180 | 341590 2HARDWCRK 69.000 | EKPC' | RANGE | 0.94 | 1.05
181 | 341593 2HARDWCRK T 69.000 | EKPC' | RANGE | 0.94 | 1.05
182 | 341596 2HARGETT 69.000 | EKPC' | RANGE | 0.94 | 1.05
183 | 341599 2HARGETT T 69.000 | EKPC' | RANGE | 0.94 | 1.05
184 | 341602 2HEADQTRS 69.000 | EKPC' | RANGE | 0.94 | 1.05
185 | 341605 2HEBRON 69.000 | EKPC' | RANGE | 0.94 | 1.05
186 | 341608 2HELECHAW 69.000 | EKPC' | RANGE | 0.94 | 1.05
187 | 341611 2HICKORY PL 69.000 | EKPC' | RANGE | 0.94 | 1.05
188 | 341614 2HIGH ROCK 69.000 | EKPC' | RANGE | 0.94 | 1.05
189 | 341617 2HIGHLAND EK69.000 | EKPC' | RANGE | 0.94 | 1.05
190 | 341620 2HILDA 69.000 | EKPC' | RANGE | 0.94 | 1.05
191 | 341623 2HILLSBORO 69.000 | EKPC' | RANGE | 0.94 | 1.05
192 | 341632 2HODGENVILLE69.000 | EKPC' | RANGE | 0.94 | 1.05
193 | 341635 2HOLLOWAY 69.000 | EKPC' | RANGE | 0.94 | 1.05
194 | 341638 2HOLLOWAY J 69.000 | EKPC' | RANGE | 0.94 | 1.05
195 | 341641 2HOMESTEAD S69.000 | EKPC' | RANGE | 0.94 | 1.05
196 | 341644 2HOPE 69.000 | EKPC' | RANGE | 0.94 | 1.05
197 | 341647 2HORSE CV KU69.000 | EKPC' | RANGE | 0.94 | 1.05
198 | 341650 2HORSECAVE T69.000 | EKPC' | RANGE | 0.94 | 1.05
199 | 341651 2HORSECAVE J69.000 | EKPC' | RANGE | 0.94 | 1.05
200 | 341653 2HOT MIX R T69.000 | EKPC' | RANGE | 0.94 | 1.05
201 | 341656 2HOT MIX RD 69.000 | EKPC' | RANGE | 0.94 | 1.05
202 | 341659 2HT ADAMS 69.000 | EKPC' | RANGE | 0.94 | 1.05
203 | 341662 2HT ADAMS T 69.000 | EKPC' | RANGE | 0.94 | 1.05
204 | 341665 2HUNT 69.000 | EKPC' | RANGE | 0.94 | 1.05
205 | 341671 2HUNT FARM J69.000 | EKPC' | RANGE | 0.94 | 1.05
206 | 341677 2INDEX 69.000 | EKPC' | RANGE | 0.94 | 1.05
207 | 341680 2JB GALLOWAY69.000 | EKPC' | RANGE | 0.94 | 1.05
208 | 341683 2JEFFERSNVIL69.000 | EKPC' | RANGE | 0.94 | 1.05
209 | 341686 2JELLICO C T69.000 | EKPC' | RANGE | 0.94 | 1.05
210 | 341689 2JELLICO CRK69.000 | EKPC' | RANGE | 0.94 | 1.05
211 | 341692 2JENNY WIL T69.000 | EKPC' | RANGE | 0.94 | 1.05
212 | 341695 2JENNY WILEY69.000 | EKPC' | RANGE | 0.94 | 1.05
213 | 341701 2JK SMITH 69.000 | EKPC' | RANGE | 0.94 | 1.05
214 | 341704 2JOE TICH 69.000 | EKPC' | RANGE | 0.94 | 1.05
215 | 341707 2JOE TICH T 69.000 | EKPC' | RANGE | 0.94 | 1.05
216 | 341713 2KARGLE 69.000 | EKPC' | RANGE | 0.94 | 1.05
217 | 341716 2KEAVY 69.000 | EKPC' | RANGE | 0.94 | 1.05
218 | 341719 2KEAVY 1 T 69.000 | EKPC' | RANGE | 0.94 | 1.05
219 | 341722 2KEAVY 2 T 69.000 | EKPC' | RANGE | 0.94 | 1.05
220 | 341725 2KEITH 69.000 | EKPC' | RANGE | 0.94 | 1.05
221 | 341728 2KNOB LICK 69.000 | EKPC' | RANGE | 0.94 | 1.05
222 | 341731 2LANCASTER 69.000 | EKPC' | RANGE | 0.94 | 1.05
223 | 341732 2LANCASTER T69.000 | EKPC' | RANGE | 0.94 | 1.05
224 | 341734 2LAUR C IP T69.000 | EKPC' | RANGE | 0.94 | 1.05
225 | 341737 2LAUR CO IP 69.000 | EKPC' | RANGE | 0.94 | 1.05
226 | 341740 2LAUREL CO 69.000 | EKPC' | RANGE | 0.94 | 1.05
227 | 341746 2LEBANON J 69.000 | EKPC' | RANGE | 0.94 | 1.05
228 | 341749 2LEES LICK 69.000 | EKPC' | RANGE | 0.94 | 1.05
229 | 341752 2LEON 69.000 | EKPC' | RANGE | 0.94 | 1.05
230 | 341755 2LIBER CH T 69.000 | EKPC' | RANGE | 0.94 | 1.05
231 | 341758 2LIBERT CHUR69.000 | EKPC' | RANGE | 0.94 | 1.05
232 | 341761 2LIBERTY J 69.000 | EKPC' | RANGE | 0.94 | 1.05
233 | 341764 2LIBERTY KU 69.000 | EKPC' | RANGE | 0.94 | 1.05
234 | 341767 2LIBERTYKU T69.000 | EKPC' | RANGE | 0.94 | 1.05
235 | 341772 2LOGAN 69.000 | EKPC' | RANGE | 0.94 | 1.05
236 | 341774 2LOGAN 2 T 69.000 | EKPC' | RANGE | 0.94 | 1.05
237 | 341775 2LOGAN TAP 69.000 | EKPC' | RANGE | 0.94 | 1.05
238 | 341776 2LORETTO 69.000 | EKPC' | RANGE | 0.94 | 1.05
239 | 341779 2LOW GAP 69.000 | EKPC' | RANGE | 0.94 | 1.05
240 | 341782 2LOW GAP T 69.000 | EKPC' | RANGE | 0.94 | 1.05
241 | 341785 2LYMAN BW 69.000 | EKPC' | RANGE | 0.94 | 1.05
242 | 341788 2LYMAN BW T 69.000 | EKPC' | RANGE | 0.94 | 1.05
243 | 341791 2MACKVIL KU 69.000 | EKPC' | RANGE | 0.94 | 1.05
244 | 341794 2MACKVILKU T69.000 | EKPC' | RANGE | 0.94 | 1.05
245 | 341797 2MAGGARD 69.000 | EKPC' | RANGE | 0.94 | 1.05
246 | 341800 2MAGNOLIA 69.000 | EKPC' | RANGE | 0.94 | 1.05
247 | 341803 2MAGOFFIN CO69.000 | EKPC' | RANGE | 0.94 | 1.05
248 | 341806 2MANCHESTER 69.000 | EKPC' | RANGE | 0.94 | 1.05
249 | 341809 2MAPLESVIL T69.000 | EKPC' | RANGE | 0.94 | 1.05
250 | 341812 2MAPLESVILLE69.000 | EKPC' | RANGE | 0.94 | 1.05
251 | 341815 2MARETBURG 69.000 | EKPC' | RANGE | 0.94 | 1.05
252 | 341818 2MARETBURG T69.000 | EKPC' | RANGE | 0.94 | 1.05
253 | 341821 2MARIBA 69.000 | EKPC' | RANGE | 0.94 | 1.05
254 | 341824 2MARIBA T 69.000 | EKPC' | RANGE | 0.94 | 1.05
255 | 341827 2MARTIN CO 69.000 | EKPC' | RANGE | 0.94 | 1.05
256 | 341830 2MAYTOWN 69.000 | EKPC' | RANGE | 0.94 | 1.05
257 | 341833 2MAYTOWN T 69.000 | EKPC' | RANGE | 0.94 | 1.05
258 | 341836 2MAZIE 69.000 | EKPC' | RANGE | 0.94 | 1.05
259 | 341839 2MBUSA 69.000 | EKPC' | RANGE | 0.94 | 1.05
260 | 341842 2MBUSA T 69.000 | EKPC' | RANGE | 0.94 | 1.05
261 | 341845 2MCCREARY CO69.000 | EKPC' | RANGE | 0.94 | 1.05
262 | 341848 2MCKEE 69.000 | EKPC' | RANGE | 0.94 | 1.05
263 | 341851 2MCKINNEY 69.000 | EKPC' | RANGE | 0.94 | 1.05
264 | 341854 2MCKINNY T 69.000 | EKPC' | RANGE | 0.94 | 1.05
265 | 341857 2MERCR IND 69.000 | EKPC' | RANGE | 0.94 | 1.05
266 | 341860 2MIDDL CRK T69.000 | EKPC' | RANGE | 0.94 | 1.05
267 | 341863 2MIDDLE CRK 69.000 | EKPC' | RANGE | 0.94 | 1.05
268 | 341869 2MILL HUNT T69.000 | EKPC' | RANGE | 0.94 | 1.05
269 | 341872 2MILLB-CRL J69.000 | EKPC' | RANGE | 0.94 | 1.05
270 | 341875 2MILLER HUNT69.000 | EKPC' | RANGE | 0.94 | 1.05
271 | 341878 2MILLERSB EK69.000 | EKPC' | RANGE | 0.94 | 1.05
272 | 341880 2MINEOLA PKE69.000 | EKPC' | RANGE | 0.94 | 1.05
273 | 341887 2MONTICELLO 69.000 | EKPC' | RANGE | 0.94 | 1.05
274 | 341890 2MORGAN CO 69.000 | EKPC' | RANGE | 0.94 | 1.05
275 | 341893 2MT OLIVE 69.000 | EKPC' | RANGE | 0.94 | 1.05
276 | 341896 2MT OLIVE J 69.000 | EKPC' | RANGE | 0.94 | 1.05
277 | 341899 2MT STERLING69.000 | EKPC' | RANGE | 0.94 | 1.05
278 | 341908 2MUNFVIL EK 69.000 | EKPC' | RANGE | 0.94 | 1.05
279 | 341911 2MUNFVIL KU 69.000 | EKPC' | RANGE | 0.94 | 1.05
280 | 341914 2MUNFVILKU T69.000 | EKPC' | RANGE | 0.94 | 1.05
281 | 341917 2MUNK 69.000 | EKPC' | RANGE | 0.94 | 1.05
282 | 341920 2MUNK J 69.000 | EKPC' | RANGE | 0.94 | 1.05
283 | 341923 2MURPHYSVIL 69.000 | EKPC' | RANGE | 0.94 | 1.05
284 | 341929 2N LONDON 69.000 | EKPC' | RANGE | 0.94 | 1.05
285 | 341935 2N SPRINGFLD69.000 | EKPC' | RANGE | 0.94 | 1.05
286 | 341938 2NANCY 69.000 | EKPC' | RANGE | 0.94 | 1.05
287 | 341941 2NELSN VAL T69.000 | EKPC' | RANGE | 0.94 | 1.05
288 | 341944 2NELSON CO 69.000 | EKPC' | RANGE | 0.94 | 1.05
289 | 341947 2NELSON VAL 69.000 | EKPC' | RANGE | 0.94 | 1.05
290 | 341950 2NEW CASTLE 69.000 | EKPC' | RANGE | 0.94 | 1.05
291 | 341953 2NEW FOUNDL 69.000 | EKPC' | RANGE | 0.94 | 1.05
292 | 341959 2NEWBY 1 69.000 | EKPC' | RANGE | 0.94 | 1.05
293 | 341962 2NEWBY 2 69.000 | EKPC' | RANGE | 0.94 | 1.05
294 | 341965 2NICHOLASVIL69.000 | EKPC' | RANGE | 0.94 | 1.05
295 | 341971 2NORWOOD 69.000 | EKPC' | RANGE | 0.94 | 1.05
296 | 341974 2NORWOOD T 69.000 | EKPC' | RANGE | 0.94 | 1.05
297 | 341977 2OAK HILL 69.000 | EKPC' | RANGE | 0.94 | 1.05
298 | 341980 2OAK HILL NO69.000 | EKPC' | RANGE | 0.94 | 1.05
299 | 341983 2OAK HILL T 69.000 | EKPC' | RANGE | 0.94 | 1.05
300 | 341986 2OAK RIDGE 69.000 | EKPC' | RANGE | 0.94 | 1.05
301 | 341989 2OAK RIDGE T69.000 | EKPC' | RANGE | 0.94 | 1.05
302 | 341992 2OAKDALE 69.000 | EKPC' | RANGE | 0.94 | 1.05
303 | 341998 2OAKLEY NOEL69.000 | EKPC' | RANGE | 0.94 | 1.05
304 | 342000 5GAS 161.00 | EKPC' | RANGE | 0.94 | 1.05
305 | 342001 2ONEIDA 69.000 | EKPC' | RANGE | 0.94 | 1.05
306 | 342007 2OWEN CO 69.000 | EKPC' | RANGE | 0.94 | 1.05
307 | 342008 4OWEN CO 138.00 | EKPC' | RANGE | 0.94 | 1.05
308 | 342010 2OWEN CO J1 69.000 | EKPC' | RANGE | 0.94 | 1.05
309 | 342013 2OWEN CO J2 69.000 | EKPC' | RANGE | 0.94 | 1.05
310 | 342016 2OWENS IL 69.000 | EKPC' | RANGE | 0.94 | 1.05
311 | 342019 2OWENS IL J 69.000 | EKPC' | RANGE | 0.94 | 1.05
312 | 342022 2OWINGSVIL T69.000 | EKPC' | RANGE | 0.94 | 1.05
313 | 342025 2OWINGVIL KU69.000 | EKPC' | RANGE | 0.94 | 1.05
314 | 342031 2PACTOLUS 69.000 | EKPC' | RANGE | 0.94 | 1.05
315 | 342034 2PACTOLUS T 69.000 | EKPC' | RANGE | 0.94 | 1.05
316 | 342037 2PARKWAY 1 69.000 | EKPC' | RANGE | 0.94 | 1.05
317 | 342040 2PARKWAY 2 69.000 | EKPC' | RANGE | 0.94 | 1.05
318 | 342043 2PARKWAY 2 T69.000 | EKPC' | RANGE | 0.94 | 1.05
319 | 342049 2PATTON RD J69.000 | EKPC' | RANGE | 0.94 | 1.05
320 | 342052 2PEASTICKS 69.000 | EKPC' | RANGE | 0.94 | 1.05
321 | 342055 2PELFREY 69.000 | EKPC' | RANGE | 0.94 | 1.05
322 | 342058 2PENN 69.000 | EKPC' | RANGE | 0.94 | 1.05
323 | 342061 2PERRYVILLE 69.000 | EKPC' | RANGE | 0.94 | 1.05
324 | 342064 2PEYTONS ST 69.000 | EKPC' | RANGE | 0.94 | 1.05
325 | 342067 2PHIL 69.000 | EKPC' | RANGE | 0.94 | 1.05
326 | 342070 2PINE GROVE 69.000 | EKPC' | RANGE | 0.94 | 1.05
327 | 342073 2PINE GRV T 69.000 | EKPC' | RANGE | 0.94 | 1.05
328 | 342076 2PINE KNOT 69.000 | EKPC' | RANGE | 0.94 | 1.05
329 | 342082 2PLEAS GRV 69.000 | EKPC' | RANGE | 0.94 | 1.05
330 | 342085 2PLUMMR L 69.000 | EKPC' | RANGE | 0.94 | 1.05
331 | 342088 2PLUMMR L T 69.000 | EKPC' | RANGE | 0.94 | 1.05
332 | 342091 2PLUMVILLE 69.000 | EKPC' | RANGE | 0.94 | 1.05
333 | 342097 2POWEL TAYL 69.000 | EKPC' | RANGE | 0.94 | 1.05
334 | 342100 2POWELL CO 69.000 | EKPC' | RANGE | 0.94 | 1.05
335 | 342103 2PPG 69.000 | EKPC' | RANGE | 0.94 | 1.05
336 | 342106 2PPG J 69.000 | EKPC' | RANGE | 0.94 | 1.05
337 | 342109 2PRESTON 69.000 | EKPC' | RANGE | 0.94 | 1.05
338 | 342112 2PRESTON T 69.000 | EKPC' | RANGE | 0.94 | 1.05
339 | 342115 2PULASK CO 69.000 | EKPC' | RANGE | 0.94 | 1.05
340 | 342118 2RADCLIFF 69.000 | EKPC' | RANGE | 0.94 | 1.05
341 | 342121 2T BROWN L T69.000 | EKPC' | RANGE | 0.94 | 1.05
342 | 342124 2RECTORVILLE69.000 | EKPC' | RANGE | 0.94 | 1.05
343 | 342127 2REDBUSH 69.000 | EKPC' | RANGE | 0.94 | 1.05
344 | 342130 2REID VILLAG69.000 | EKPC' | RANGE | 0.94 | 1.05
345 | 342133 2RENAKER 69.000 | EKPC' | RANGE | 0.94 | 1.05
346 | 342136 2REVELO KU 69.000 | EKPC' | RANGE | 0.94 | 1.05
347 | 342139 2REVELO KU T69.000 | EKPC' | RANGE | 0.94 | 1.05
348 | 342145 2RICHARDSON 69.000 | EKPC' | RANGE | 0.94 | 1.05
349 | 342151 2RINEYVILLE 69.000 | EKPC' | RANGE | 0.94 | 1.05
350 | 342154 2ROANOKE 69.000 | EKPC' | RANGE | 0.94 | 1.05
351 | 342155 2ROANOKE T 69.000 | EKPC' | RANGE | 0.94 | 1.05
352 | 342157 2ROGERSVIL J69.000 | EKPC' | RANGE | 0.94 | 1.05
353 | 342160 2ROSEVILLE 69.000 | EKPC' | RANGE | 0.94 | 1.05
354 | 342161 2ROSEVILLE T69.000 | EKPC' | RANGE | 0.94 | 1.05
355 | 342163 2ROWAN CO 69.000 | EKPC' | RANGE | 0.94 | 1.05
356 | 342166 2RUSS SPEK T69.000 | EKPC' | RANGE | 0.94 | 1.05
357 | 342169 2RUSS SPKU T69.000 | EKPC' | RANGE | 0.94 | 1.05
358 | 342172 2RUSS SPR EK69.000 | EKPC' | RANGE | 0.94 | 1.05
359 | 342175 2RUSS SPR KU69.000 | EKPC' | RANGE | 0.94 | 1.05
360 | 342178 2RUSSEL CO 69.000 | EKPC' | RANGE | 0.94 | 1.05
361 | 342181 2S ALBANY 69.000 | EKPC' | RANGE | 0.94 | 1.05
362 | 342184 2S ANDERSON 69.000 | EKPC' | RANGE | 0.94 | 1.05
363 | 342186 2S BARDSTWN 69.000 | EKPC' | RANGE | 0.94 | 1.05
364 | 342187 2S CORBIN 69.000 | EKPC' | RANGE | 0.94 | 1.05
365 | 342193 2S FLOYD 69.000 | EKPC' | RANGE | 0.94 | 1.05
366 | 342196 2WHITE OAK 69.000 | EKPC' | RANGE | 0.94 | 1.05
367 | 342199 2S JESSAM J 69.000 | EKPC' | RANGE | 0.94 | 1.05
368 | 342202 2S JESSAMINE69.000 | EKPC' | RANGE | 0.94 | 1.05
369 | 342208 2S SPRINGF T69.000 | EKPC' | RANGE | 0.94 | 1.05
370 | 342211 2S SPRINGFLD69.000 | EKPC' | RANGE | 0.94 | 1.05
371 | 342214 2SALEM EK 69.000 | EKPC' | RANGE | 0.94 | 1.05
372 | 342217 2SALEM EK T 69.000 | EKPC' | RANGE | 0.94 | 1.05
373 | 342218 2SALT LICK 138.00 | EKPC' | RANGE | 0.94 | 1.05
374 | 342220 2SAND GAP 69.000 | EKPC' | RANGE | 0.94 | 1.05
375 | 342223 2SAND GAP T 69.000 | EKPC' | RANGE | 0.94 | 1.05
376 | 342229 2SANDY HOOK 69.000 | EKPC' | RANGE | 0.94 | 1.05
377 | 342232 2SEWELLTON 69.000 | EKPC' | RANGE | 0.94 | 1.05
378 | 342235 2SEWELTN J 69.000 | EKPC' | RANGE | 0.94 | 1.05
379 | 342238 2SEYMOUR 69.000 | EKPC' | RANGE | 0.94 | 1.05
380 | 342241 2SEYMOUR T 69.000 | EKPC' | RANGE | 0.94 | 1.05
381 | 342247 2SHELBY CO 69.000 | EKPC' | RANGE | 0.94 | 1.05
382 | 342248 2SHELBY TAP 69.000 | EKPC' | RANGE | 0.94 | 1.05
383 | 342250 2SHEPHEVIL 69.000 | EKPC' | RANGE | 0.94 | 1.05
384 | 342253 2SHEPHEVIL J69.000 | EKPC' | RANGE | 0.94 | 1.05
385 | 342256 2SHOPVILLE 69.000 | EKPC' | RANGE | 0.94 | 1.05
386 | 342259 2SIDEVIEW 69.000 | EKPC' | RANGE | 0.94 | 1.05
387 | 342262 2SINAI 69.000 | EKPC' | RANGE | 0.94 | 1.05
388 | 342265 2SKAGGS 69.000 | EKPC' | RANGE | 0.94 | 1.05
389 | 342268 2SLAT 69.000 | EKPC' | RANGE | 0.94 | 1.05
390 | 342271 2SMITHRSVIL 69.000 | EKPC' | RANGE | 0.94 | 1.05
391 | 342274 2SMITHRVIL T69.000 | EKPC' | RANGE | 0.94 | 1.05
392 | 342277 2SNOW 69.000 | EKPC' | RANGE | 0.94 | 1.05
393 | 342280 2SNOW HILL 69.000 | EKPC' | RANGE | 0.94 | 1.05
394 | 342283 2SNOW T 69.000 | EKPC' | RANGE | 0.94 | 1.05
395 | 342286 2SOMERSET 69.000 | EKPC' | RANGE | 0.94 | 1.05
396 | 342287 2SOMERSET KU69.000 | EKPC' | RANGE | 0.94 | 1.05
397 | 342288 2SPEEDWELL 69.000 | EKPC' | RANGE | 0.94 | 1.05
398 | 342292 2STANLEY PRK69.000 | EKPC' | RANGE | 0.94 | 1.05
399 | 342295 2STANLY P J169.000 | EKPC' | RANGE | 0.94 | 1.05
400 | 342298 2STANLY P J269.000 | EKPC' | RANGE | 0.94 | 1.05
401 | 342301 2STANTON 69.000 | EKPC' | RANGE | 0.94 | 1.05
402 | 342307 2STEPHENSBRG69.000 | EKPC' | RANGE | 0.94 | 1.05
403 | 342310 2SUBLETT 69.000 | EKPC' | RANGE | 0.94 | 1.05
404 | 342313 2SUBLETT J 69.000 | EKPC' | RANGE | 0.94 | 1.05
405 | 342316 2SULPHUR CRK69.000 | EKPC' | RANGE | 0.94 | 1.05
406 | 342319 2SUMM SHAD J69.000 | EKPC' | RANGE | 0.94 | 1.05
407 | 342322 2SUMM SHADE 69.000 | EKPC' | RANGE | 0.94 | 1.05
408 | 342325 2SUMMERSVIL 69.000 | EKPC' | RANGE | 0.94 | 1.05
409 | 342328 2T BROWN LOG69.000 | EKPC' | RANGE | 0.94 | 1.05
410 | 342334 2TEMPLE HILL69.000 | EKPC' | RANGE | 0.94 | 1.05
411 | 342337 2THARP 69.000 | EKPC' | RANGE | 0.94 | 1.05
412 | 342340 2THARP T 69.000 | EKPC' | RANGE | 0.94 | 1.05
413 | 342343 2THELMA 69.000 | EKPC' | RANGE | 0.94 | 1.05
414 | 342346 2THREE LINKS69.000 | EKPC' | RANGE | 0.94 | 1.05
415 | 342349 2THREE LNK J69.000 | EKPC' | RANGE | 0.94 | 1.05
416 | 342352 2THREE M 69.000 | EKPC' | RANGE | 0.94 | 1.05
417 | 342355 2THREE M T 69.000 | EKPC' | RANGE | 0.94 | 1.05
418 | 342358 2TODDVILLE 69.000 | EKPC' | RANGE | 0.94 | 1.05
419 | 342361 2TODDVILLE T69.000 | EKPC' | RANGE | 0.94 | 1.05
420 | 342364 2TOMM GOOC 69.000 | EKPC' | RANGE | 0.94 | 1.05
421 | 342367 2TOMM GOOC T69.000 | EKPC' | RANGE | 0.94 | 1.05
422 | 342370 2TRAPP 69.000 | EKPC' | RANGE | 0.94 | 1.05
423 | 342379 2TUNNEL H T 69.000 | EKPC' | RANGE | 0.94 | 1.05
424 | 342382 2TUNNEL HILL69.000 | EKPC' | RANGE | 0.94 | 1.05
425 | 342385 2TURKEY FT 69.000 | EKPC' | RANGE | 0.94 | 1.05
426 | 342388 2TURKEY FT J69.000 | EKPC' | RANGE | 0.94 | 1.05
427 | 342391 2TYNER 69.000 | EKPC' | RANGE | 0.94 | 1.05
428 | 342394 2UPCHURCH 69.000 | EKPC' | RANGE | 0.94 | 1.05
429 | 342397 2UPCHURCH T 69.000 | EKPC' | RANGE | 0.94 | 1.05
430 | 342400 2UPTON 69.000 | EKPC' | RANGE | 0.94 | 1.05
431 | 342403 2UPTON T 69.000 | EKPC' | RANGE | 0.94 | 1.05
432 | 342406 2VAN ARSDELL69.000 | EKPC' | RANGE | 0.94 | 1.05
433 | 342410 2VEECHDALE 69.000 | EKPC' | RANGE | 0.94 | 1.05
434 | 342412 2VERTREES 69.000 | EKPC' | RANGE | 0.94 | 1.05
435 | 342415 2VINE GROV J69.000 | EKPC' | RANGE | 0.94 | 1.05
436 | 342418 2VINE GROVE 69.000 | EKPC' | RANGE | 0.94 | 1.05
437 | 342421 2VOLGA 69.000 | EKPC' | RANGE | 0.94 | 1.05
438 | 342424 2W BARDST J 69.000 | EKPC' | RANGE | 0.94 | 1.05
439 | 342427 2W BARDSTWN 69.000 | EKPC' | RANGE | 0.94 | 1.05
440 | 342430 2W BEREA 69.000 | EKPC' | RANGE | 0.94 | 1.05
441 | 342433 2W BEREA J 69.000 | EKPC' | RANGE | 0.94 | 1.05
442 | 342436 2W COLUMBI T69.000 | EKPC' | RANGE | 0.94 | 1.05
443 | 342439 2W COLUMBIA 69.000 | EKPC' | RANGE | 0.94 | 1.05
444 | 342442 2W GLASGOW 69.000 | EKPC' | RANGE | 0.94 | 1.05
445 | 342445 2W GLASGOW T69.000 | EKPC' | RANGE | 0.94 | 1.05
446 | 342451 2W LONDON 69.000 | EKPC' | RANGE | 0.94 | 1.05
447 | 342454 2W M SMITH 69.000 | EKPC' | RANGE | 0.94 | 1.05
448 | 342460 2W NICHVIL 69.000 | EKPC' | RANGE | 0.94 | 1.05
449 | 342463 2W NICHVIL T69.000 | EKPC' | RANGE | 0.94 | 1.05
450 | 342466 2W R SMOOT 69.000 | EKPC' | RANGE | 0.94 | 1.05
451 | 342469 2W SOMERSET 69.000 | EKPC' | RANGE | 0.94 | 1.05
452 | 342472 2WALNUT GROV69.000 | EKPC' | RANGE | 0.94 | 1.05
453 | 342475 2WARNOCK 69.000 | EKPC' | RANGE | 0.94 | 1.05
454 | 342478 2WAYNE CO 69.000 | EKPC' | RANGE | 0.94 | 1.05
455 | 342481 2WEBB CR R T69.000 | EKPC' | RANGE | 0.94 | 1.05
456 | 342484 2WEBB CR RDS69.000 | EKPC' | RANGE | 0.94 | 1.05
457 | 342487 2WEBSTER RD 69.000 | EKPC' | RANGE | 0.94 | 1.05
458 | 342490 2WHITLEY CTY69.000 | EKPC' | RANGE | 0.94 | 1.05
459 | 342493 2WHITLY C KU69.000 | EKPC' | RANGE | 0.94 | 1.05
460 | 342496 2WIBORG 69.000 | EKPC' | RANGE | 0.94 | 1.05
461 | 342499 2WIBORG T 69.000 | EKPC' | RANGE | 0.94 | 1.05
462 | 342500 2WIELAND 69.000 | EKPC' | RANGE | 0.94 | 1.05
463 | 342502 2WILLIAMSTWN69.000 | EKPC' | RANGE | 0.94 | 1.05
464 | 342505 2WINDSOR 69.000 | EKPC' | RANGE | 0.94 | 1.05
465 | 342508 2WOODLAWN 69.000 | EKPC' | RANGE | 0.94 | 1.05
466 | 342511 2WOODSTOCK 69.000 | EKPC' | RANGE | 0.94 | 1.05
467 | 342514 2WOOSLEY 69.000 | EKPC' | RANGE | 0.94 | 1.05
468 | 342520 2ZACHARIAH 69.000 | EKPC' | RANGE | 0.94 | 1.05
469 | 342523 2ZOLLICOF 69.000 | EKPC' | RANGE | 0.94 | 1.05
470 | 342526 2ZOLLICOF T 69.000 | EKPC' | RANGE | 0.94 | 1.05
471 | 342529 2ZULA 69.000 | EKPC' | RANGE | 0.94 | 1.05
472 | 342532 2ZULA J NO 69.000 | EKPC' | RANGE | 0.94 | 1.05
473 | 342535 2ZULA T 69.000 | EKPC' | RANGE | 0.94 | 1.05
474 | 342538 4ARGENTUM 138.00 | EKPC' | RANGE | 0.94 | 1.05
475 | 342541 4AVON 138.00 | EKPC' | RANGE | 0.94 | 1.05
476 | 342544 4AVON-R 138.00 | EKPC' | RANGE | 0.94 | 1.05
477 | 342547 4BAKER LN 138.00 | EKPC' | RANGE | 0.94 | 1.05
478 | 342550 4BAVARIAN LF138.00 | EKPC' | RANGE | 0.94 | 1.05
479 | 342553 4BECKNERV 138.00 | EKPC' | RANGE | 0.94 | 1.05
480 | 342556 4BECKNERV T 138.00 | EKPC' | RANGE | 0.94 | 1.05
481 | 342559 4BOONE CO 138.00 | EKPC' | RANGE | 0.94 | 1.05
482 | 342565 4BOONESBOR T138.00 | EKPC' | RANGE | 0.94 | 1.05
483 | 342568 4CENT HARDIN138.00 | EKPC' | RANGE | 0.94 | 1.05
484 | 342571 4CRANSTON 138.00 | EKPC' | RANGE | 0.94 | 1.05
485 | 342574 4DALE 138.00 | EKPC' | RANGE | 0.94 | 1.05
486 | 342577 4FAWKES EK 138.00 | EKPC' | RANGE | 0.94 | 1.05
487 | 342580 4FAYETTE 138.00 | EKPC' | RANGE | 0.94 | 1.05
488 | 342583 4FLEMINGSBRG138.00 | EKPC' | RANGE | 0.94 | 1.05
489 | 342586 4GALLATIN CO138.00 | EKPC' | RANGE | 0.94 | 1.05
490 | 342587 1GALLATIN CO34.500 | EKPC' | RANGE | 0.94 | 1.05
491 | 342589 4GODDARD 138.00 | EKPC' | RANGE | 0.94 | 1.05
492 | 342595 4HEBRON 138.00 | EKPC' | RANGE | 0.94 | 1.05
493 | 342596 4HUNT 138.00 | EKPC' | RANGE | 0.94 | 1.05
494 | 342598 4INLAND C T 138.00 | EKPC' | RANGE | 0.94 | 1.05
495 | 342601 4JACKSNVIL 138.00 | EKPC' | RANGE | 0.94 | 1.05
496 | 342604 4JACKSNVIL T138.00 | EKPC' | RANGE | 0.94 | 1.05
497 | 342607 4JK SMITH 138.00 | EKPC' | RANGE | 0.94 | 1.05
498 | 342610 4JK SMITH 21138.00 | EKPC' | RANGE | 0.94 | 1.05
499 | 342613 4JK SMITH 22138.00 | EKPC' | RANGE | 0.94 | 1.05
500 | 342616 4LOVE HYDRO 138.00 | EKPC' | RANGE | 0.94 | 1.05
501 | 342622 4MAYSVIL I T138.00 | EKPC' | RANGE | 0.94 | 1.05
502 | 342625 4MAYSVIL IND138.00 | EKPC' | RANGE | 0.94 | 1.05
503 | 342631 4PARIS T 138.00 | EKPC' | RANGE | 0.94 | 1.05
504 | 342634 4PLUMVILLE 138.00 | EKPC' | RANGE | 0.94 | 1.05
505 | 342637 4POWELL CO 138.00 | EKPC' | RANGE | 0.94 | 1.05
506 | 342640 4RENAKER 138.00 | EKPC' | RANGE | 0.94 | 1.05
507 | 342643 4RICHWOOD 138.00 | EKPC' | RANGE | 0.94 | 1.05
508 | 342646 4RICHWOOD T 138.00 | EKPC' | RANGE | 0.94 | 1.05
509 | 342649 4ROWAN CO 138.00 | EKPC' | RANGE | 0.94 | 1.05
510 | 342658 4SKAGGS 138.00 | EKPC' | RANGE | 0.94 | 1.05
511 | 342661 4SPUR-KENT-R138.00 | EKPC' | RANGE | 0.94 | 1.05
512 | 342664 4SPURLOCK 138.00 | EKPC' | RANGE | 0.94 | 1.05
513 | 342667 4STANLEY PRK138.00 | EKPC' | RANGE | 0.94 | 1.05
514 | 342670 4STERLING 138.00 | EKPC' | RANGE | 0.94 | 1.05
515 | 342673 4STERLNG T 138.00 | EKPC' | RANGE | 0.94 | 1.05
516 | 342676 4THREE FK T 138.00 | EKPC' | RANGE | 0.94 | 1.05
517 | 342679 4THREE FORKS138.00 | EKPC' | RANGE | 0.94 | 1.05
518 | 342685 4UNION CITY 138.00 | EKPC' | RANGE | 0.94 | 1.05
519 | 342688 4UNION CTY T138.00 | EKPC' | RANGE | 0.94 | 1.05
520 | 342691 4W BEREA 138.00 | EKPC' | RANGE | 0.94 | 1.05
521 | 342694 5BARREN CO 161.00 | EKPC' | RANGE | 0.94 | 1.05
522 | 342697 5BEATTYV J 161.00 | EKPC' | RANGE | 0.94 | 1.05
523 | 342700 5BULLITT CO 161.00 | EKPC' | RANGE | 0.94 | 1.05
524 | 342703 5CASEY CO 161.00 | EKPC' | RANGE | 0.94 | 1.05
525 | 342715 5COOPER1 161.00 | EKPC' | RANGE | 0.94 | 1.05
526 | 342718 5COOPER2 161.00 | EKPC' | RANGE | 0.94 | 1.05
527 | 342721 5DARWIN TH 161.00 | EKPC' | RANGE | 0.94 | 1.05
528 | 342724 5DARWIN TH T161.00 | EKPC' | RANGE | 0.94 | 1.05
529 | 342727 5DENNY 161.00 | EKPC' | RANGE | 0.94 | 1.05
530 | 342730 5FALL ROCK 161.00 | EKPC' | RANGE | 0.94 | 1.05
531 | 342732 5FOX HOLLOW 161.00 | EKPC' | RANGE | 0.94 | 1.05
532 | 342733 5GREEN CO 161.00 | EKPC' | RANGE | 0.94 | 1.05
533 | 342736 5GREEN HAL T161.00 | EKPC' | RANGE | 0.94 | 1.05
534 | 342739 5GREEN HALL 161.00 | EKPC' | RANGE | 0.94 | 1.05
535 | 342742 5JABEZ 161.00 | EKPC' | RANGE | 0.94 | 1.05
536 | 342745 5JABEZ T 161.00 | EKPC' | RANGE | 0.94 | 1.05
537 | 342748 5JAMESTOWN 161.00 | EKPC' | RANGE | 0.94 | 1.05
538 | 342751 5JAMESTOWN T161.00 | EKPC' | RANGE | 0.94 | 1.05
539 | 342754 5LAUREL CO 161.00 | EKPC' | RANGE | 0.94 | 1.05
540 | 342757 5LAUREL DAM 161.00 | EKPC' | RANGE | 0.94 | 1.05
541 | 342760 5LIBERTY J 161.00 | EKPC' | RANGE | 0.94 | 1.05
542 | 342763 5LITTLE MT 161.00 | EKPC' | RANGE | 0.94 | 1.05
543 | 342766 5LITTLE MT T161.00 | EKPC' | RANGE | 0.94 | 1.05
544 | 342769 5MARION CO 161.00 | EKPC' | RANGE | 0.94 | 1.05
545 | 342770 4MARION CO 138.00 | EKPC' | RANGE | 0.94 | 1.05
546 | 342772 5MARION IP 161.00 | EKPC' | RANGE | 0.94 | 1.05
547 | 342775 5MARION IP T161.00 | EKPC' | RANGE | 0.94 | 1.05
548 | 342778 5MCCREARY CO161.00 | EKPC' | RANGE | 0.94 | 1.05
549 | 342779 5MILLER CRK 161.00 | EKPC' | RANGE | 0.94 | 1.05
550 | 342780 5MILL CRK T 161.00 | EKPC' | RANGE | 0.94 | 1.05
551 | 342781 5PITTSBURG 161.00 | EKPC' | RANGE | 0.94 | 1.05
552 | 342784 5POWELL CO 161.00 | EKPC' | RANGE | 0.94 | 1.05
553 | 342787 5PULASK CO 161.00 | EKPC' | RANGE | 0.94 | 1.05
554 | 342790 5PULASK CO J161.00 | EKPC' | RANGE | 0.94 | 1.05
555 | 342793 5RUSSEL CO 161.00 | EKPC' | RANGE | 0.94 | 1.05
556 | 342796 5RUSSEL CO J161.00 | EKPC' | RANGE | 0.94 | 1.05
557 | 342797 5S MARION IT161.00 | EKPC' | RANGE | 0.94 | 1.05
558 | 342798 5S MARION IP161.00 | EKPC' | RANGE | 0.94 | 1.05
559 | 342799 5S OAKHILL 161.00 | EKPC' | RANGE | 0.94 | 1.05
560 | 342802 5SALOMA 161.00 | EKPC' | RANGE | 0.94 | 1.05
561 | 342805 5SALOMA T 161.00 | EKPC' | RANGE | 0.94 | 1.05
562 | 342808 5SHELBY CO 161.00 | EKPC' | RANGE | 0.94 | 1.05
563 | 342814 5SUMM SHADE 161.00 | EKPC' | RANGE | 0.94 | 1.05
564 | 342817 5TAYLOR CO J161.00 | EKPC' | RANGE | 0.94 | 1.05
565 | 342818 5TAYLORSVILL161.00 | EKPC' | RANGE | 0.94 | 1.05
566 | 342819 5TAYLORSV T 161.00 | EKPC' | RANGE | 0.94 | 1.05
567 | 342820 5TYNER 161.00 | EKPC' | RANGE | 0.94 | 1.05
568 | 342823 5WAYNE CO 161.00 | EKPC' | RANGE | 0.94 | 1.05
569 | 342829 7AVON 345.00 | EKPC' | RANGE | 0.94 | 1.05
570 | 342832 7JK SMITH 345.00 | EKPC' | RANGE | 0.94 | 1.05
571 | 342835 7N CLARK 345.00 | EKPC' | RANGE | 0.94 | 1.05
572 | 342838 7SPURLOCK 345.00 | EKPC' | RANGE | 0.94 | 1.05
573 | 342841 7W GARRARDEK345.00 | EKPC' | RANGE | 0.94 | 1.05
574 | 342844 8SOUTHGEN 500.00 | EKPC' | RANGE | 0.94 | 1.05
575 | 342847 9NORTHGEN 765.00 | EKPC' | RANGE | 0.94 | 1.05
576 | 939132 AE1-143 E 161.00 | EKPC' | RANGE | 0.94 | 1.05
577 | 942410 AE2-254 TAP 69.000 | EKPC' | RANGE | 0.94 | 1.05
578 | 942411 AE2-254 C O169.000 | EKPC' | RANGE | 0.94 | 1.05
579 | 942412 AE2-254 E O169.000 | EKPC' | RANGE | 0.94 | 1.05
580 | 324170 1KNOB CRK 34.500 | EKPC_EXT' | RANGE | 0.94 | 1.05
581 | 324010 7TRIMBL REAC345.00 | LGEE' | RANGE | 0.94 | 1.06
582 | 324021 7BLUEGRASS12345.00 | LGEE' | RANGE | 0.94 | 1.06
583 | 324022 7BLUEGRASS 3345.00 | LGEE' | RANGE | 0.94 | 1.06
584 | 324029 7TRIMBLE CTA345.00 | LGEE' | RANGE | 0.94 | 1.06
585 | 324030 7TRIMBLE CTB345.00 | LGEE' | RANGE | 0.94 | 1.06
586 | 324047 4BLACKBRANCH138.00 | LGEE' | RANGE | 0.94 | 1.06
587 | 324048 2PARKWY MINE69.000 | LGEE' | RANGE | 0.94 | 1.06
588 | 324049 2OXFORD COAL69.000 | LGEE' | RANGE | 0.94 | 1.06
589 | 324050 2JONESVILLE 69.000 | LGEE' | RANGE | 0.94 | 1.06
590 | 324051 4MATANZAS 138.00 | LGEE' | RANGE | 0.94 | 1.06
591 | 324058 2BEAVER DAM 69.000 | LGEE' | RANGE | 0.94 | 1.06
592 | 324059 2BEAVER DM N69.000 | LGEE' | RANGE | 0.94 | 1.06
593 | 324061 2BORG-WARNER69.000 | LGEE' | RANGE | 0.94 | 1.06
594 | 324065 2DAWSON 764 69.000 | LGEE' | RANGE | 0.94 | 1.06
595 | 324067 2EDDYV PRIS 69.000 | LGEE' | RANGE | 0.94 | 1.06
596 | 324068 2E CAMPBELVL69.000 | LGEE' | RANGE | 0.94 | 1.06
597 | 324069 2PAYNES ML 69.000 | LGEE' | RANGE | 0.94 | 1.06
598 | 324075 2GRAHAM 69.000 | LGEE' | RANGE | 0.94 | 1.06
599 | 324077 2GREENVILE W69.000 | LGEE' | RANGE | 0.94 | 1.06
600 | 324079 2HANSON 69.000 | LGEE' | RANGE | 0.94 | 1.06
601 | 324080 2HARTFORD 69.000 | LGEE' | RANGE | 0.94 | 1.06
602 | 324081 2MADSNV GE 69.000 | LGEE' | RANGE | 0.94 | 1.06
603 | 324082 2PARIS 4 69.000 | LGEE' | RANGE | 0.94 | 1.06
604 | 324083 2MADSNV W 69.000 | LGEE' | RANGE | 0.94 | 1.06
605 | 324085 2MARION 4 69.000 | LGEE' | RANGE | 0.94 | 1.06
606 | 324086 2MORGANF IND69.000 | LGEE' | RANGE | 0.94 | 1.06
607 | 324087 2MT VERN SO 69.000 | LGEE' | RANGE | 0.94 | 1.06
608 | 324090 2OVERLAND NO69.000 | LGEE' | RANGE | 0.94 | 1.06
609 | 324091 2OVERLAND SO69.000 | LGEE' | RANGE | 0.94 | 1.06
610 | 324092 2PEABODY RVR69.000 | LGEE' | RANGE | 0.94 | 1.06
611 | 324093 2SPEN CHEMIC69.000 | LGEE' | RANGE | 0.94 | 1.06
612 | 324094 2TURTLE CK T69.000 | LGEE' | RANGE | 0.94 | 1.06
613 | 324095 2UNIONTOWN 69.000 | LGEE' | RANGE | 0.94 | 1.06
614 | 324096 2PEA WSH TAP69.000 | LGEE' | RANGE | 0.94 | 1.06
615 | 324097 2PEAB WASH 69.000 | LGEE' | RANGE | 0.94 | 1.06
616 | 324098 2WEST VACO 69.000 | LGEE' | RANGE | 0.94 | 1.06
617 | 324100 7ALCALDE 345.00 | LGEE' | RANGE | 0.94 | 1.06
618 | 324101 7BLUE LICK 345.00 | LGEE' | RANGE | 0.94 | 1.06
619 | 324102 7BROWN NORTH345.00 | LGEE' | RANGE | 0.94 | 1.06
620 | 324103 7BUCKNER 345.00 | LGEE' | RANGE | 0.94 | 1.06
621 | 324104 7DAVIESS 345.00 | LGEE' | RANGE | 0.94 | 1.06
622 | 324105 7GHENT 345.00 | LGEE' | RANGE | 0.94 | 1.06
623 | 324106 7HARDIN CO 345.00 | LGEE' | RANGE | 0.94 | 1.06
624 | 324107 7MIDDLETOWN 345.00 | LGEE' | RANGE | 0.94 | 1.06
625 | 324108 7MILL CREEK 345.00 | LGEE' | RANGE | 0.94 | 1.06
626 | 324109 7NAS 345.00 | LGEE' | RANGE | 0.94 | 1.06
627 | 324110 7NORTHSIDE 345.00 | LGEE' | RANGE | 0.94 | 1.06
628 | 324111 7PADDYS WEST345.00 | LGEE' | RANGE | 0.94 | 1.06
629 | 324112 7PINEVILLE 345.00 | LGEE' | RANGE | 0.94 | 1.06
630 | 324114 7TRIMBLE CO 345.00 | LGEE' | RANGE | 0.94 | 1.06
631 | 324115 7W FRANKFORT345.00 | LGEE' | RANGE | 0.94 | 1.06
632 | 324116 7W LEXINGTON345.00 | LGEE' | RANGE | 0.94 | 1.06
633 | 324124 2CENTRTOWN S69.000 | LGEE' | RANGE | 0.94 | 1.06
634 | 324130 5ALCALDE 161.00 | LGEE' | RANGE | 0.94 | 1.06
635 | 324131 5ARNOLD 161.00 | LGEE' | RANGE | 0.94 | 1.06
636 | 324132 5ARTEMUS TAP161.00 | LGEE' | RANGE | 0.94 | 1.06
637 | 324133 5ARTEMUS 161.00 | LGEE' | RANGE | 0.94 | 1.06
638 | 324134 5BLUE LICK 161.00 | LGEE' | RANGE | 0.94 | 1.06
639 | 324135 5CORYDON TAP161.00 | LGEE' | RANGE | 0.94 | 1.06
640 | 324136 5CORYDON 161.00 | LGEE' | RANGE | 0.94 | 1.06
641 | 324137 5CRITTENDEN 161.00 | LGEE' | RANGE | 0.94 | 1.06
642 | 324138 5DELVINTA 161.00 | LGEE' | RANGE | 0.94 | 1.06
643 | 324139 5DORCHESTER 161.00 | LGEE' | RANGE | 0.94 | 1.06
644 | 324140 5EARLINGTN N161.00 | LGEE' | RANGE | 0.94 | 1.06
645 | 324141 5ELIHU 161.00 | LGEE' | RANGE | 0.94 | 1.06
646 | 324143 5FARLEY 161.00 | LGEE' | RANGE | 0.94 | 1.06
647 | 324144 5GREEN RIVER161.00 | LGEE' | RANGE | 0.94 | 1.06
648 | 324145 5GRAHAMVILLE161.00 | LGEE' | RANGE | 0.94 | 1.06
649 | 324146 5HARLAN WYE 161.00 | LGEE' | RANGE | 0.94 | 1.06
650 | 324147 5HOWARDS BR 161.00 | LGEE' | RANGE | 0.94 | 1.06
651 | 324148 5WOOTON TAP 161.00 | LGEE' | RANGE | 0.94 | 1.06
652 | 324149 5IMBODEN 161.00 | LGEE' | RANGE | 0.94 | 1.06
653 | 324150 5LEBANON JCT161.00 | LGEE' | RANGE | 0.94 | 1.06
654 | 324151 5LIVNGSTN CO161.00 | LGEE' | RANGE | 0.94 | 1.06
655 | 324152 5LAKE REBA T161.00 | LGEE' | RANGE | 0.94 | 1.06
656 | 324153 5MORGANFIELD161.00 | LGEE' | RANGE | 0.94 | 1.06
657 | 324154 5PADDYS RUN 161.00 | LGEE' | RANGE | 0.94 | 1.06
658 | 324155 5PINEVILLE 1161.00 | LGEE' | RANGE | 0.94 | 1.06
659 | 324156 5PINEVILE SW161.00 | LGEE' | RANGE | 0.94 | 1.06
660 | 324157 5POCKET N 161.00 | LGEE' | RANGE | 0.94 | 1.06
661 | 324158 5POCKET 161.00 | LGEE' | RANGE | 0.94 | 1.06
662 | 324159 5RIVER QUEEN161.00 | LGEE' | RANGE | 0.94 | 1.06
663 | 324160 5RIVER QN T 161.00 | LGEE' | RANGE | 0.94 | 1.06
664 | 324161 5S PADUCAH 161.00 | LGEE' | RANGE | 0.94 | 1.06
665 | 324163 5WEST IRVINE161.00 | LGEE' | RANGE | 0.94 | 1.06
666 | 324164 5WALKER 161.00 | LGEE' | RANGE | 0.94 | 1.06
667 | 324165 5W IRVINE T 161.00 | LGEE' | RANGE | 0.94 | 1.06
668 | 324166 5WICKLIFFE 161.00 | LGEE' | RANGE | 0.94 | 1.06
669 | 324167 5PINEVILLE 2161.00 | LGEE' | RANGE | 0.94 | 1.06
670 | 324171 5GRAHMVILE 1161.00 | LGEE' | RANGE | 0.94 | 1.06
671 | 324172 5GRAHMVILE 2161.00 | LGEE' | RANGE | 0.94 | 1.06
672 | 324173 5MATANZAS 161.00 | LGEE' | RANGE | 0.94 | 1.06
673 | 324191 2LEBANON E T69.000 | LGEE' | RANGE | 0.94 | 1.06
674 | 324192 4DAYTON-WALT138.00 | LGEE' | RANGE | 0.94 | 1.06
675 | 324193 4FLEMINGB KU138.00 | LGEE' | RANGE | 0.94 | 1.06
676 | 324195 2AUGUSTA 69.000 | LGEE' | RANGE | 0.94 | 1.06
677 | 324196 2BOONESB PRK69.000 | LGEE' | RANGE | 0.94 | 1.06
678 | 324197 2DETROIT HAR69.000 | LGEE' | RANGE | 0.94 | 1.06
679 | 324198 2HUNT BOTTOM69.000 | LGEE' | RANGE | 0.94 | 1.06
680 | 324199 2OWENTON 69.000 | LGEE' | RANGE | 0.94 | 1.06
681 | 324200 4PLSUR RDG T138.00 | LGEE' | RANGE | 0.94 | 1.06
682 | 324201 4ADAMS 138.00 | LGEE' | RANGE | 0.94 | 1.06
683 | 324202 4ALGONQUIN 138.00 | LGEE' | RANGE | 0.94 | 1.06
684 | 324203 4AMERICAN AV138.00 | LGEE' | RANGE | 0.94 | 1.06
685 | 324204 4APPLIANC PK138.00 | LGEE' | RANGE | 0.94 | 1.06
686 | 324205 4ASHBOTTOM 138.00 | LGEE' | RANGE | 0.94 | 1.06
687 | 324206 4ASHBY 138.00 | LGEE' | RANGE | 0.94 | 1.06
688 | 324207 4BARDSTOWN 138.00 | LGEE' | RANGE | 0.94 | 1.06
689 | 324208 4BEARGRASS 138.00 | LGEE' | RANGE | 0.94 | 1.06
690 | 324209 4BG PARKWAY 138.00 | LGEE' | RANGE | 0.94 | 1.06
691 | 324210 4BAKER LANE 138.00 | LGEE' | RANGE | 0.94 | 1.06
692 | 324211 4BLACKWELL 138.00 | LGEE' | RANGE | 0.94 | 1.06
693 | 324212 4BLUE LICK 138.00 | LGEE' | RANGE | 0.94 | 1.06
694 | 324213 4BONNIEVILLE138.00 | LGEE' | RANGE | 0.94 | 1.06
695 | 324214 4BRECKNRIDGE138.00 | LGEE' | RANGE | 0.94 | 1.06
696 | 324215 4BRIDGPOR HE138.00 | LGEE' | RANGE | 0.94 | 1.06
697 | 324217 4BROWN PLANT138.00 | LGEE' | RANGE | 0.94 | 1.06
698 | 324218 4BROWN CT 138.00 | LGEE' | RANGE | 0.94 | 1.06
699 | 324219 4BROWN T1 138.00 | LGEE' | RANGE | 0.94 | 1.06
700 | 324220 4BROWN T2 138.00 | LGEE' | RANGE | 0.94 | 1.06
701 | 324221 4BUTLER 138.00 | LGEE' | RANGE | 0.94 | 1.06
702 | 324222 4CAMPGROUND 138.00 | LGEE' | RANGE | 0.94 | 1.06
703 | 324223 4CANAL 138.00 | LGEE' | RANGE | 0.94 | 1.06
704 | 324224 2RED HOUSE 69.000 | LGEE' | RANGE | 0.94 | 1.06
705 | 324225 4CARNTOWN TP138.00 | LGEE' | RANGE | 0.94 | 1.06
706 | 324226 4CARNTOWN 138.00 | LGEE' | RANGE | 0.94 | 1.06
707 | 324227 4CARROLLTON 138.00 | LGEE' | RANGE | 0.94 | 1.06
708 | 324228 4CENTERFIELD138.00 | LGEE' | RANGE | 0.94 | 1.06
709 | 324229 4CLARK CO 138.00 | LGEE' | RANGE | 0.94 | 1.06
710 | 324230 4CLAYS MILL 138.00 | LGEE' | RANGE | 0.94 | 1.06
711 | 324231 4CLOVERPORT 138.00 | LGEE' | RANGE | 0.94 | 1.06
712 | 324232 4CANE RN 11A138.00 | LGEE' | RANGE | 0.94 | 1.06
713 | 324236 4RICHMND NO 138.00 | LGEE' | RANGE | 0.94 | 1.06
714 | 324237 4CANE RUN SW138.00 | LGEE' | RANGE | 0.94 | 1.06
715 | 324238 4DANVILLE N 138.00 | LGEE' | RANGE | 0.94 | 1.06
716 | 324239 4DANVILE N T138.00 | LGEE' | RANGE | 0.94 | 1.06
717 | 324240 4DAY-WALT TP138.00 | LGEE' | RANGE | 0.94 | 1.06
718 | 324241 4DIXIE 138.00 | LGEE' | RANGE | 0.94 | 1.06
719 | 324242 4DOW CORN W 138.00 | LGEE' | RANGE | 0.94 | 1.06
720 | 324243 4ETHEL 138.00 | LGEE' | RANGE | 0.94 | 1.06
721 | 324244 4ETOWN 138.00 | LGEE' | RANGE | 0.94 | 1.06
722 | 324245 4FARMERS TAP138.00 | LGEE' | RANGE | 0.94 | 1.06
723 | 324246 4FARMERS 138.00 | LGEE' | RANGE | 0.94 | 1.06
724 | 324247 4FAWKES TAP 138.00 | LGEE' | RANGE | 0.94 | 1.06
725 | 324248 4FAWKES KU 138.00 | LGEE' | RANGE | 0.94 | 1.06
726 | 324249 4FERN VALLEY138.00 | LGEE' | RANGE | 0.94 | 1.06
727 | 324250 4E FRANKFORT138.00 | LGEE' | RANGE | 0.94 | 1.06
728 | 324251 4FLEMNB KU T138.00 | LGEE' | RANGE | 0.94 | 1.06
729 | 324252 2SCHOLLS 69.000 | LGEE' | RANGE | 0.94 | 1.06
730 | 324253 4GHENT 138.00 | LGEE' | RANGE | 0.94 | 1.06
731 | 324254 4GODDARD KU 138.00 | LGEE' | RANGE | 0.94 | 1.06
732 | 324255 4GREEN RIVER138.00 | LGEE' | RANGE | 0.94 | 1.06
733 | 324256 4GR RVR STL 138.00 | LGEE' | RANGE | 0.94 | 1.06
734 | 324257 4GRADE LANE 138.00 | LGEE' | RANGE | 0.94 | 1.06
735 | 324258 4HAEFLING 138.00 | LGEE' | RANGE | 0.94 | 1.06
736 | 324259 4HANCOCK 138.00 | LGEE' | RANGE | 0.94 | 1.06
737 | 324260 4HARDINSBURG138.00 | LGEE' | RANGE | 0.94 | 1.06
738 | 324261 4HARDIN CO 138.00 | LGEE' | RANGE | 0.94 | 1.06
739 | 324262 4HIGBY MILL 138.00 | LGEE' | RANGE | 0.94 | 1.06
740 | 324263 4HURSTBORNE 138.00 | LGEE' | RANGE | 0.94 | 1.06
741 | 324264 4IBM NORTHTP138.00 | LGEE' | RANGE | 0.94 | 1.06
742 | 324265 4JEFFRSONV T138.00 | LGEE' | RANGE | 0.94 | 1.06
743 | 324267 4KENTON 138.00 | LGEE' | RANGE | 0.94 | 1.06
744 | 324268 4KNOB CREEK 138.00 | LGEE' | RANGE | 0.94 | 1.06
745 | 324269 4LANSDOWNE 138.00 | LGEE' | RANGE | 0.94 | 1.06
746 | 324270 4LEBANON WES138.00 | LGEE' | RANGE | 0.94 | 1.06
747 | 324271 4LEBANON 138.00 | LGEE' | RANGE | 0.94 | 1.06
748 | 324272 4LEITCHFIELD138.00 | LGEE' | RANGE | 0.94 | 1.06
749 | 324273 4LAKE REBA 138.00 | LGEE' | RANGE | 0.94 | 1.06
750 | 324274 4LOCKPORT 138.00 | LGEE' | RANGE | 0.94 | 1.06
751 | 324275 4LOUDON AVE 138.00 | LGEE' | RANGE | 0.94 | 1.06
752 | 324276 4LAKE REBA T138.00 | LGEE' | RANGE | 0.94 | 1.06
753 | 324277 4LYNDON SO 138.00 | LGEE' | RANGE | 0.94 | 1.06
754 | 324278 4MAGAZINE 138.00 | LGEE' | RANGE | 0.94 | 1.06
755 | 324279 4MANSLICK 138.00 | LGEE' | RANGE | 0.94 | 1.06
756 | 324281 4MIDDLETOWN 138.00 | LGEE' | RANGE | 0.94 | 1.06
757 | 324282 4MIDDLETWN-R138.00 | LGEE' | RANGE | 0.94 | 1.06
758 | 324283 4MIDWAY 138.00 | LGEE' | RANGE | 0.94 | 1.06
759 | 324284 4MILL CREEK 138.00 | LGEE' | RANGE | 0.94 | 1.06
760 | 324285 4MUD LANE 138.00 | LGEE' | RANGE | 0.94 | 1.06
761 | 324286 4NAS 138.00 | LGEE' | RANGE | 0.94 | 1.06
762 | 324287 4NAS TAP 138.00 | LGEE' | RANGE | 0.94 | 1.06
763 | 324288 4NELSON CO 138.00 | LGEE' | RANGE | 0.94 | 1.06
764 | 324289 4NORTHSIDE 138.00 | LGEE' | RANGE | 0.94 | 1.06
765 | 324290 4OWEN CO TAP138.00 | LGEE' | RANGE | 0.94 | 1.06
766 | 324291 4OHIO COUNTY138.00 | LGEE' | RANGE | 0.94 | 1.06
767 | 324292 4OKOLONA 138.00 | LGEE' | RANGE | 0.94 | 1.06
768 | 324294 4PADDYS WEST138.00 | LGEE' | RANGE | 0.94 | 1.06
769 | 324295 4PADDYS RUN 138.00 | LGEE' | RANGE | 0.94 | 1.06
770 | 324296 4PISGAH 138.00 | LGEE' | RANGE | 0.94 | 1.06
771 | 324297 4PLAINVIEW 138.00 | LGEE' | RANGE | 0.94 | 1.06
772 | 324298 4PLAINVIEW T138.00 | LGEE' | RANGE | 0.94 | 1.06
773 | 324299 4PLEASUR RDG138.00 | LGEE' | RANGE | 0.94 | 1.06
774 | 324300 4POND CREEK 138.00 | LGEE' | RANGE | 0.94 | 1.06
775 | 324301 4REYNOLDS 138.00 | LGEE' | RANGE | 0.94 | 1.06
776 | 324302 4RODBURN 138.00 | LGEE' | RANGE | 0.94 | 1.06
777 | 324303 4ROGERSVILLE138.00 | LGEE' | RANGE | 0.94 | 1.06
778 | 324304 2VERSAILLE W69.000 | LGEE' | RANGE | 0.94 | 1.06
779 | 324305 4SCOTT CO 138.00 | LGEE' | RANGE | 0.94 | 1.06
780 | 324306 4SHADRACK 138.00 | LGEE' | RANGE | 0.94 | 1.06
781 | 324307 4SHARKEY TAP138.00 | LGEE' | RANGE | 0.94 | 1.06
782 | 324308 4SHREWSBURY 138.00 | LGEE' | RANGE | 0.94 | 1.06
783 | 324310 4SPENCER RD 138.00 | LGEE' | RANGE | 0.94 | 1.06
784 | 324311 4TIP TOP 138.00 | LGEE' | RANGE | 0.94 | 1.06
785 | 324312 4TOYOTA N 138.00 | LGEE' | RANGE | 0.94 | 1.06
786 | 324313 4TOYOTA S 138.00 | LGEE' | RANGE | 0.94 | 1.06
787 | 324314 4TRIMBLE CO 138.00 | LGEE' | RANGE | 0.94 | 1.06
788 | 324315 4TYRONE 138.00 | LGEE' | RANGE | 0.94 | 1.06
789 | 324316 4VIRGINIA CI138.00 | LGEE' | RANGE | 0.94 | 1.06
790 | 324317 4VILEY ROAD 138.00 | LGEE' | RANGE | 0.94 | 1.06
791 | 324318 4WEST CLIFF 138.00 | LGEE' | RANGE | 0.94 | 1.06
792 | 324319 4W FRANKFORT138.00 | LGEE' | RANGE | 0.94 | 1.06
793 | 324320 4W LEXINGTON138.00 | LGEE' | RANGE | 0.94 | 1.06
794 | 324321 4WATERSIDE 138.00 | LGEE' | RANGE | 0.94 | 1.06
795 | 324322 4WATTERSON 138.00 | LGEE' | RANGE | 0.94 | 1.06
796 | 324323 4WEDONIA 138.00 | LGEE' | RANGE | 0.94 | 1.06
797 | 324328 4PARIS 138.00 | LGEE' | RANGE | 0.94 | 1.06
798 | 324329 4COLLINS 138.00 | LGEE' | RANGE | 0.94 | 1.06
799 | 324330 2WINCHES IND69.000 | LGEE' | RANGE | 0.94 | 1.06
800 | 324331 2ASHLAND AVE69.000 | LGEE' | RANGE | 0.94 | 1.06
801 | 324332 2LAKE SHORE 69.000 | LGEE' | RANGE | 0.94 | 1.06
802 | 324333 4BROWN N 1-R138.00 | LGEE' | RANGE | 0.94 | 1.06
803 | 324334 4BROWN N 2-R138.00 | LGEE' | RANGE | 0.94 | 1.06
804 | 324335 4INNOVATION 138.00 | LGEE' | RANGE | 0.94 | 1.06
805 | 324337 2MOUNT TABOR69.000 | LGEE' | RANGE | 0.94 | 1.06
806 | 324338 2SCOTT ST 4 69.000 | LGEE' | RANGE | 0.94 | 1.06
807 | 324339 2SCOTT ST 1269.000 | LGEE' | RANGE | 0.94 | 1.06
808 | 324340 2SPINDLETOP 69.000 | LGEE' | RANGE | 0.94 | 1.06
809 | 324341 2WILMORE 69.000 | LGEE' | RANGE | 0.94 | 1.06
810 | 324344 2ATOKA 69.000 | LGEE' | RANGE | 0.94 | 1.06
811 | 324345 2BARDTWN IND69.000 | LGEE' | RANGE | 0.94 | 1.06
812 | 324346 2RICHMND E 69.000 | LGEE' | RANGE | 0.94 | 1.06
813 | 324347 2BEATTY 649 69.000 | LGEE' | RANGE | 0.94 | 1.06
814 | 324348 2BRODHEAD CI69.000 | LGEE' | RANGE | 0.94 | 1.06
815 | 324349 2CAMPBELVIL269.000 | LGEE' | RANGE | 0.94 | 1.06
816 | 324350 2CRAB ORCHAR69.000 | LGEE' | RANGE | 0.94 | 1.06
817 | 324351 2ETOWN 3 69.000 | LGEE' | RANGE | 0.94 | 1.06
818 | 324352 2ETOWN IND 69.000 | LGEE' | RANGE | 0.94 | 1.06
819 | 324353 2FLORDA TILE69.000 | LGEE' | RANGE | 0.94 | 1.06
820 | 324354 2GATES RUBBR69.000 | LGEE' | RANGE | 0.94 | 1.06
821 | 324355 2HARRDSBRG 469.000 | LGEE' | RANGE | 0.94 | 1.06
822 | 324356 2HARRDSBRG1269.000 | LGEE' | RANGE | 0.94 | 1.06
823 | 324357 2LANCASTER 169.000 | LGEE' | RANGE | 0.94 | 1.06
824 | 324358 2M-V CLARKSN69.000 | LGEE' | RANGE | 0.94 | 1.06
825 | 324359 2MT VERN 58969.000 | LGEE' | RANGE | 0.94 | 1.06
826 | 324360 2PINE HILL 69.000 | LGEE' | RANGE | 0.94 | 1.06
827 | 324361 2RADCLIFF KU69.000 | LGEE' | RANGE | 0.94 | 1.06
828 | 324362 2RIO 69.000 | LGEE' | RANGE | 0.94 | 1.06
829 | 324363 2SHELB CI KU69.000 | LGEE' | RANGE | 0.94 | 1.06
830 | 324364 4OLD HENRY 138.00 | LGEE' | RANGE | 0.94 | 1.06
831 | 324372 2BURNSIDE 69.000 | LGEE' | RANGE | 0.94 | 1.06
832 | 324373 2CATRON CRK 69.000 | LGEE' | RANGE | 0.94 | 1.06
833 | 324374 2CROCKETT KU69.000 | LGEE' | RANGE | 0.94 | 1.06
834 | 324375 2DAYHOIT 69.000 | LGEE' | RANGE | 0.94 | 1.06
835 | 324376 2DEER BRANCH69.000 | LGEE' | RANGE | 0.94 | 1.06
836 | 324377 2GARDNER 69.000 | LGEE' | RANGE | 0.94 | 1.06
837 | 324378 2MIDDLBO780 69.000 | LGEE' | RANGE | 0.94 | 1.06
838 | 324380 2DANIEL BRAN69.000 | LGEE' | RANGE | 0.94 | 1.06
839 | 324381 2WILLAMSBURG69.000 | LGEE' | RANGE | 0.94 | 1.06
840 | 324382 2WILLMBRG SO69.000 | LGEE' | RANGE | 0.94 | 1.06
841 | 324384 2APPALACHIA 69.000 | LGEE' | RANGE | 0.94 | 1.06
842 | 324385 2BIG STONE G69.000 | LGEE' | RANGE | 0.94 | 1.06
843 | 324386 2DIXIANA 69.000 | LGEE' | RANGE | 0.94 | 1.06
844 | 324387 2ADDINGTON 69.000 | LGEE' | RANGE | 0.94 | 1.06
845 | 324388 2CRITICAL FK69.000 | LGEE' | RANGE | 0.94 | 1.06
846 | 324389 2DWINA 69.000 | LGEE' | RANGE | 0.94 | 1.06
847 | 324390 2PENNINGTON 69.000 | LGEE' | RANGE | 0.94 | 1.06
848 | 324391 2POOR VALLEY69.000 | LGEE' | RANGE | 0.94 | 1.06
849 | 324392 2ROCKY FORK 69.000 | LGEE' | RANGE | 0.94 | 1.06
850 | 324393 2ROSE HILL 69.000 | LGEE' | RANGE | 0.94 | 1.06
851 | 324394 2TOMS CREEK 69.000 | LGEE' | RANGE | 0.94 | 1.06
852 | 324395 2WISE 69.000 | LGEE' | RANGE | 0.94 | 1.06
853 | 324400 2WHAS TAP 69.000 | LGEE' | RANGE | 0.94 | 1.06
854 | 324401 2FREYS HIL J69.000 | LGEE' | RANGE | 0.94 | 1.06
855 | 324402 2FAIRMOUNT T69.000 | LGEE' | RANGE | 0.94 | 1.06
856 | 324403 2CRESTWOOD T69.000 | LGEE' | RANGE | 0.94 | 1.06
857 | 324404 2LYNDON TAP 69.000 | LGEE' | RANGE | 0.94 | 1.06
858 | 324405 2ADAMS 69.000 | LGEE' | RANGE | 0.94 | 1.06
859 | 324406 2AIKEN 69.000 | LGEE' | RANGE | 0.94 | 1.06
860 | 324407 2ALEXANDER 69.000 | LGEE' | RANGE | 0.94 | 1.06
861 | 324408 2ALGONQUIN 69.000 | LGEE' | RANGE | 0.94 | 1.06
862 | 324409 2AMERICAN AV69.000 | LGEE' | RANGE | 0.94 | 1.06
863 | 324411 2ANDOVER TAP69.000 | LGEE' | RANGE | 0.94 | 1.06
864 | 324412 2ANDOVER 69.000 | LGEE' | RANGE | 0.94 | 1.06
865 | 324413 2AO SMITH TP69.000 | LGEE' | RANGE | 0.94 | 1.06
866 | 324414 2AO SMITH 69.000 | LGEE' | RANGE | 0.94 | 1.06
867 | 324415 2APPOLO FUEL69.000 | LGEE' | RANGE | 0.94 | 1.06
868 | 324416 2ARNOLD 69.000 | LGEE' | RANGE | 0.94 | 1.06
869 | 324417 2ARTEMUS 69.000 | LGEE' | RANGE | 0.94 | 1.06
870 | 324418 2ASHLND AV T69.000 | LGEE' | RANGE | 0.94 | 1.06
871 | 324419 2ASHBOT WEST69.000 | LGEE' | RANGE | 0.94 | 1.06
872 | 324421 2ATOKA TAP 69.000 | LGEE' | RANGE | 0.94 | 1.06
873 | 324422 2AVON T2 69.000 | LGEE' | RANGE | 0.94 | 1.06
874 | 324423 2BARBOURVILE69.000 | LGEE' | RANGE | 0.94 | 1.06
875 | 324424 2BARDTWN CTY69.000 | LGEE' | RANGE | 0.94 | 1.06
876 | 324425 2BARDT IND T69.000 | LGEE' | RANGE | 0.94 | 1.06
877 | 324426 2BARDSTOWN 69.000 | LGEE' | RANGE | 0.94 | 1.06
878 | 324427 2BARDWELL 69.000 | LGEE' | RANGE | 0.94 | 1.06
879 | 324428 2BARLOW 69.000 | LGEE' | RANGE | 0.94 | 1.06
880 | 324429 2BEARGRASS 69.000 | LGEE' | RANGE | 0.94 | 1.06
881 | 324430 2BEATTYVI KU69.000 | LGEE' | RANGE | 0.94 | 1.06
882 | 324432 2BELT LINE 69.000 | LGEE' | RANGE | 0.94 | 1.06
883 | 324433 2BENHAM 69.000 | LGEE' | RANGE | 0.94 | 1.06
884 | 324434 2BEREA TAP 69.000 | LGEE' | RANGE | 0.94 | 1.06
885 | 324435 2BEREA NORTH69.000 | LGEE' | RANGE | 0.94 | 1.06
886 | 324436 2BEREA EK TP69.000 | LGEE' | RANGE | 0.94 | 1.06
887 | 324437 2BEVIER KU 69.000 | LGEE' | RANGE | 0.94 | 1.06
888 | 324438 2BIMBLE 69.000 | LGEE' | RANGE | 0.94 | 1.06
889 | 324439 2BISHOP 69.000 | LGEE' | RANGE | 0.94 | 1.06
890 | 324440 2BLACK MOUNT69.000 | LGEE' | RANGE | 0.94 | 1.06
891 | 324441 2BLACKWOOD 69.000 | LGEE' | RANGE | 0.94 | 1.06
892 | 324442 2BLEDSOE TAP69.000 | LGEE' | RANGE | 0.94 | 1.06
893 | 324443 2BLUE LICK 69.000 | LGEE' | RANGE | 0.94 | 1.06
894 | 324444 2BLUELICK EK69.000 | LGEE' | RANGE | 0.94 | 1.06
895 | 324445 2BONDS MILL 69.000 | LGEE' | RANGE | 0.94 | 1.06
896 | 324446 2BOND 69.000 | LGEE' | RANGE | 0.94 | 1.06
897 | 324447 2BONNIE KU 69.000 | LGEE' | RANGE | 0.94 | 1.06
898 | 324448 2BOONE AVE 69.000 | LGEE' | RANGE | 0.94 | 1.06
899 | 324449 2BOONSBORO N69.000 | LGEE' | RANGE | 0.94 | 1.06
900 | 324450 2BOYLE CO 69.000 | LGEE' | RANGE | 0.94 | 1.06
901 | 324451 2BRECKNRIDGE69.000 | LGEE' | RANGE | 0.94 | 1.06
902 | 324453 2BEARGRS PMP69.000 | LGEE' | RANGE | 0.94 | 1.06
903 | 324455 2BROMLEY 69.000 | LGEE' | RANGE | 0.94 | 1.06
904 | 324456 2BRUSH CREEK69.000 | LGEE' | RANGE | 0.94 | 1.06
905 | 324457 2BUCHANAN 69.000 | LGEE' | RANGE | 0.94 | 1.06
906 | 324458 2BUENA VISTA69.000 | LGEE' | RANGE | 0.94 | 1.06
907 | 324459 2BUSH TAP 69.000 | LGEE' | RANGE | 0.94 | 1.06
908 | 324460 2CALLOWAY 69.000 | LGEE' | RANGE | 0.94 | 1.06
909 | 324461 2CAMARGO 69.000 | LGEE' | RANGE | 0.94 | 1.06
910 | 324462 2CANAL 69.000 | LGEE' | RANGE | 0.94 | 1.06
911 | 324463 2CARNTOWN 69.000 | LGEE' | RANGE | 0.94 | 1.06
912 | 324464 2CARON 69.000 | LGEE' | RANGE | 0.94 | 1.06
913 | 324465 2CARPENTER T69.000 | LGEE' | RANGE | 0.94 | 1.06
914 | 324466 2CARROLLTON 69.000 | LGEE' | RANGE | 0.94 | 1.06
915 | 324467 2CAVE RUN TP69.000 | LGEE' | RANGE | 0.94 | 1.06
916 | 324468 2CENTRL CI S69.000 | LGEE' | RANGE | 0.94 | 1.06
917 | 324469 2CENTERFIELD69.000 | LGEE' | RANGE | 0.94 | 1.06
918 | 324470 2CERRO-SALEM69.000 | LGEE' | RANGE | 0.94 | 1.06
919 | 324471 2CHRISTIAN 69.000 | LGEE' | RANGE | 0.94 | 1.06
920 | 324472 2CLARK CO 69.000 | LGEE' | RANGE | 0.94 | 1.06
921 | 324473 2CLAY LGE 69.000 | LGEE' | RANGE | 0.94 | 1.06
922 | 324474 2CLAY VILG T69.000 | LGEE' | RANGE | 0.94 | 1.06
923 | 324475 2CLIFTON 69.000 | LGEE' | RANGE | 0.94 | 1.06
924 | 324476 2CMC TAP 69.000 | LGEE' | RANGE | 0.94 | 1.06
925 | 324477 2CAMP BRECKN69.000 | LGEE' | RANGE | 0.94 | 1.06
926 | 324478 2CAMPBELBURG69.000 | LGEE' | RANGE | 0.94 | 1.06
927 | 324479 2CAMPBELVL T69.000 | LGEE' | RANGE | 0.94 | 1.06
928 | 324480 2CMPGND EK T69.000 | LGEE' | RANGE | 0.94 | 1.06
929 | 324481 2COLLINS 69.000 | LGEE' | RANGE | 0.94 | 1.06
930 | 324482 2CORBIN EAST69.000 | LGEE' | RANGE | 0.94 | 1.06
931 | 324484 2CORYDON 69.000 | LGEE' | RANGE | 0.94 | 1.06
932 | 324485 2CRAB ORCH T69.000 | LGEE' | RANGE | 0.94 | 1.06
933 | 324486 2CRITTENDEN 69.000 | LGEE' | RANGE | 0.94 | 1.06
934 | 324487 2CRESTWOOD 69.000 | LGEE' | RANGE | 0.94 | 1.06
935 | 324488 2CANE RUN SW69.000 | LGEE' | RANGE | 0.94 | 1.06
936 | 324489 2CUMB FALL T69.000 | LGEE' | RANGE | 0.94 | 1.06
937 | 324490 2CUMBERLAND 69.000 | LGEE' | RANGE | 0.94 | 1.06
938 | 324491 2CYNTHIAN SO69.000 | LGEE' | RANGE | 0.94 | 1.06
939 | 324492 2CYNTHIAN SW69.000 | LGEE' | RANGE | 0.94 | 1.06
940 | 324493 2DAHLIA 69.000 | LGEE' | RANGE | 0.94 | 1.06
941 | 324494 2DANVILLE 1 69.000 | LGEE' | RANGE | 0.94 | 1.06
942 | 324495 2DANVILLE N 69.000 | LGEE' | RANGE | 0.94 | 1.06
943 | 324496 2DARK HOLLOW69.000 | LGEE' | RANGE | 0.94 | 1.06
944 | 324497 2DAYHOIT TAP69.000 | LGEE' | RANGE | 0.94 | 1.06
945 | 324498 2DAYS BRANCH69.000 | LGEE' | RANGE | 0.94 | 1.06
946 | 324499 2DEL PARK 69.000 | LGEE' | RANGE | 0.94 | 1.06
947 | 324500 2DELAPLAIN T69.000 | LGEE' | RANGE | 0.94 | 1.06
948 | 324501 2DIX DAM 69.000 | LGEE' | RANGE | 0.94 | 1.06
949 | 324502 2DIXON KU 69.000 | LGEE' | RANGE | 0.94 | 1.06
950 | 324503 2DORCHESTER 69.000 | LGEE' | RANGE | 0.94 | 1.06
951 | 324504 2E BERNST KU69.000 | LGEE' | RANGE | 0.94 | 1.06
952 | 324505 2E DIAMOND 69.000 | LGEE' | RANGE | 0.94 | 1.06
953 | 324506 2EARLINGTN N69.000 | LGEE' | RANGE | 0.94 | 1.06
954 | 324507 2EARLINGTON 69.000 | LGEE' | RANGE | 0.94 | 1.06
955 | 324508 2EASTLAND 69.000 | LGEE' | RANGE | 0.94 | 1.06
956 | 324509 2EASTVIEW 69.000 | LGEE' | RANGE | 0.94 | 1.06
957 | 324510 2EASTWOOD 69.000 | LGEE' | RANGE | 0.94 | 1.06
958 | 324511 2ECHOLS 69.000 | LGEE' | RANGE | 0.94 | 1.06
959 | 324512 2EDDYV PR TP69.000 | LGEE' | RANGE | 0.94 | 1.06
960 | 324513 2EDDYVILLE 69.000 | LGEE' | RANGE | 0.94 | 1.06
961 | 324514 2ELIHU 69.000 | LGEE' | RANGE | 0.94 | 1.06
962 | 324515 2EMANUEL TAP69.000 | LGEE' | RANGE | 0.94 | 1.06
963 | 324516 2EMINENCE KU69.000 | LGEE' | RANGE | 0.94 | 1.06
964 | 324517 2ESSERVILLE 69.000 | LGEE' | RANGE | 0.94 | 1.06
965 | 324518 2ETHEL 69.000 | LGEE' | RANGE | 0.94 | 1.06
966 | 324519 2ETOWN KU 69.000 | LGEE' | RANGE | 0.94 | 1.06
967 | 324520 2ETOWN 2 TAP69.000 | LGEE' | RANGE | 0.94 | 1.06
968 | 324521 2ETOWN 4 69.000 | LGEE' | RANGE | 0.94 | 1.06
969 | 324522 2EVARTS TAP 69.000 | LGEE' | RANGE | 0.94 | 1.06
970 | 324523 2EVARTS 69.000 | LGEE' | RANGE | 0.94 | 1.06
971 | 324524 2EWINGTON 69.000 | LGEE' | RANGE | 0.94 | 1.06
972 | 324525 2FAIRFIELD 69.000 | LGEE' | RANGE | 0.94 | 1.06
973 | 324526 2FAIRMOUNT 269.000 | LGEE' | RANGE | 0.94 | 1.06
974 | 324527 2FARLEY KU 69.000 | LGEE' | RANGE | 0.94 | 1.06
975 | 324528 2FARMERS 69.000 | LGEE' | RANGE | 0.94 | 1.06
976 | 324529 2FARNSLEY 69.000 | LGEE' | RANGE | 0.94 | 1.06
977 | 324530 2FAWKES 69.000 | LGEE' | RANGE | 0.94 | 1.06
978 | 324531 2FERGUSON SO69.000 | LGEE' | RANGE | 0.94 | 1.06
979 | 324532 2FERN VALLEY69.000 | LGEE' | RANGE | 0.94 | 1.06
980 | 324533 2FRANKFORT 169.000 | LGEE' | RANGE | 0.94 | 1.06
981 | 324534 2FRANKFORT 269.000 | LGEE' | RANGE | 0.94 | 1.06
982 | 324535 2E FRANKFORT69.000 | LGEE' | RANGE | 0.94 | 1.06
983 | 324536 2FINCHVILLE 69.000 | LGEE' | RANGE | 0.94 | 1.06
984 | 324537 2FLA TILE T269.000 | LGEE' | RANGE | 0.94 | 1.06
985 | 324538 2FLOYD 69.000 | LGEE' | RANGE | 0.94 | 1.06
986 | 324539 2FMC 69.000 | LGEE' | RANGE | 0.94 | 1.06
987 | 324540 2FOGG PIKE T69.000 | LGEE' | RANGE | 0.94 | 1.06
988 | 324541 2FORD 69.000 | LGEE' | RANGE | 0.94 | 1.06
989 | 324542 2FORESTER CR69.000 | LGEE' | RANGE | 0.94 | 1.06
990 | 324543 2FOUR MILE 69.000 | LGEE' | RANGE | 0.94 | 1.06
991 | 324544 2FREDONIA QU69.000 | LGEE' | RANGE | 0.94 | 1.06
992 | 324545 2FREYS HILL 69.000 | LGEE' | RANGE | 0.94 | 1.06
993 | 324546 2GARRARD CT 69.000 | LGEE' | RANGE | 0.94 | 1.06
994 | 324547 2GEORGETOWN 69.000 | LGEE' | RANGE | 0.94 | 1.06
995 | 324549 2GORGE 69.000 | LGEE' | RANGE | 0.94 | 1.06
996 | 324550 2GREEN RIVER69.000 | LGEE' | RANGE | 0.94 | 1.06
997 | 324551 2GR RVR STL 69.000 | LGEE' | RANGE | 0.94 | 1.06
998 | 324552 2GRADY 69.000 | LGEE' | RANGE | 0.94 | 1.06
999 | 324553 2GRAHAMVILLE69.000 | LGEE' | RANGE | 0.94 | 1.06
1000 | 324554 2GRENSBRG KU69.000 | LGEE' | RANGE | 0.94 | 1.06
1001 | 324555 2VA CTY REAC69.000 | LGEE' | RANGE | 0.94 | 1.06
1002 | 324556 2GREENV W TP69.000 | LGEE' | RANGE | 0.94 | 1.06
1003 | 324557 2GR RVR PLAZ69.000 | LGEE' | RANGE | 0.94 | 1.06
1004 | 324558 2HAEFLING 69.000 | LGEE' | RANGE | 0.94 | 1.06
1005 | 324559 2HALEY 69.000 | LGEE' | RANGE | 0.94 | 1.06
1006 | 324560 2HAMBLIN TAP69.000 | LGEE' | RANGE | 0.94 | 1.06
1007 | 324561 2HANCOCK 69.000 | LGEE' | RANGE | 0.94 | 1.06
1008 | 324562 2HARLAN KU 69.000 | LGEE' | RANGE | 0.94 | 1.06
1009 | 324563 2HARDIN CO 69.000 | LGEE' | RANGE | 0.94 | 1.06
1010 | 324564 2HARLAN WYE 69.000 | LGEE' | RANGE | 0.94 | 1.06
1011 | 324565 7NAS TAP 345.00 | LGEE' | RANGE | 0.94 | 1.06
1012 | 324566 7NAS 222 345.00 | LGEE' | RANGE | 0.94 | 1.06
1013 | 324567 2HIGBY MIL 269.000 | LGEE' | RANGE | 0.94 | 1.06
1014 | 324568 2HIGBY 618 69.000 | LGEE' | RANGE | 0.94 | 1.06
1015 | 324569 2HIGBY 608 69.000 | LGEE' | RANGE | 0.94 | 1.06
1016 | 324570 2HIGHLAND 69.000 | LGEE' | RANGE | 0.94 | 1.06
1017 | 324571 2HIGHLAND MI69.000 | LGEE' | RANGE | 0.94 | 1.06
1018 | 324572 2HILLSIDE 69.000 | LGEE' | RANGE | 0.94 | 1.06
1019 | 324573 2HINKLE 69.000 | LGEE' | RANGE | 0.94 | 1.06
1020 | 324574 2HILLCREST 69.000 | LGEE' | RANGE | 0.94 | 1.06
1021 | 324575 2HODGENV KU 69.000 | LGEE' | RANGE | 0.94 | 1.06
1022 | 324576 2HOPEWELL 69.000 | LGEE' | RANGE | 0.94 | 1.06
1023 | 324577 2HARDESTY A 69.000 | LGEE' | RANGE | 0.94 | 1.06
1024 | 324578 2HARDESTY B 69.000 | LGEE' | RANGE | 0.94 | 1.06
1025 | 324579 2HARMNY LAND69.000 | LGEE' | RANGE | 0.94 | 1.06
1026 | 324580 2HARRODS CRK69.000 | LGEE' | RANGE | 0.94 | 1.06
1027 | 324581 2HUGHES LANE69.000 | LGEE' | RANGE | 0.94 | 1.06
1028 | 324582 2IBM 69.000 | LGEE' | RANGE | 0.94 | 1.06
1029 | 324583 2IMBODEN 69.000 | LGEE' | RANGE | 0.94 | 1.06
1030 | 324584 2INDIAN HILL69.000 | LGEE' | RANGE | 0.94 | 1.06
1031 | 324585 2JERICHO 69.000 | LGEE' | RANGE | 0.94 | 1.06
1032 | 324586 2JOYLAND 69.000 | LGEE' | RANGE | 0.94 | 1.06
1033 | 324587 2KEN AMERICA69.000 | LGEE' | RANGE | 0.94 | 1.06
1034 | 324588 2KENTENIA 69.000 | LGEE' | RANGE | 0.94 | 1.06
1035 | 324589 2KENTON 688 69.000 | LGEE' | RANGE | 0.94 | 1.06
1036 | 324590 2KENWOOD 69.000 | LGEE' | RANGE | 0.94 | 1.06
1037 | 324591 2KEOKEE TAP 69.000 | LGEE' | RANGE | 0.94 | 1.06
1038 | 324592 2KEOKEE TVA 69.000 | LGEE' | RANGE | 0.94 | 1.06
1039 | 324593 2KU PARK 69.000 | LGEE' | RANGE | 0.94 | 1.06
1040 | 324595 2KAWNEER 69.000 | LGEE' | RANGE | 0.94 | 1.06
1041 | 324597 2KY ST HOSP 69.000 | LGEE' | RANGE | 0.94 | 1.06
1042 | 324598 2LA GRANGE E69.000 | LGEE' | RANGE | 0.94 | 1.06
1043 | 324599 2LANCASTER 269.000 | LGEE' | RANGE | 0.94 | 1.06
1044 | 324600 2LANCASTR KU69.000 | LGEE' | RANGE | 0.94 | 1.06
1045 | 324601 2LANSDOWNE 69.000 | LGEE' | RANGE | 0.94 | 1.06
1046 | 324602 2LAWRENCE TP69.000 | LGEE' | RANGE | 0.94 | 1.06
1047 | 324603 2LEBANON CIT69.000 | LGEE' | RANGE | 0.94 | 1.06
1048 | 324604 2LEBANON IND69.000 | LGEE' | RANGE | 0.94 | 1.06
1049 | 324605 2LEBANON EK 69.000 | LGEE' | RANGE | 0.94 | 1.06
1050 | 324606 2LEBANON 69.000 | LGEE' | RANGE | 0.94 | 1.06
1051 | 324607 2LEITCHF CIT69.000 | LGEE' | RANGE | 0.94 | 1.06
1052 | 324608 2LEITCHF E 69.000 | LGEE' | RANGE | 0.94 | 1.06
1053 | 324609 2LEITCHFIELD69.000 | LGEE' | RANGE | 0.94 | 1.06
1054 | 324610 2LEX PLANT 69.000 | LGEE' | RANGE | 0.94 | 1.06
1055 | 324611 2LIBERTY RD 69.000 | LGEE' | RANGE | 0.94 | 1.06
1056 | 324612 2LAKE REBA 69.000 | LGEE' | RANGE | 0.94 | 1.06
1057 | 324613 2LK SHORE TP69.000 | LGEE' | RANGE | 0.94 | 1.06
1058 | 324614 2LOCUST TAP 69.000 | LGEE' | RANGE | 0.94 | 1.06
1059 | 324615 2LONDON 69.000 | LGEE' | RANGE | 0.94 | 1.06
1060 | 324616 2LONG RUN 69.000 | LGEE' | RANGE | 0.94 | 1.06
1061 | 324617 2LOUDON 618 69.000 | LGEE' | RANGE | 0.94 | 1.06
1062 | 324618 2LOUDON 628 69.000 | LGEE' | RANGE | 0.94 | 1.06
1063 | 324619 2LOWER MIL C69.000 | LGEE' | RANGE | 0.94 | 1.06
1064 | 324620 2LAWRENCEBRG69.000 | LGEE' | RANGE | 0.94 | 1.06
1065 | 324621 2LYNCH 69.000 | LGEE' | RANGE | 0.94 | 1.06
1066 | 324622 2LYNDON SO 69.000 | LGEE' | RANGE | 0.94 | 1.06
1067 | 324623 2LYNDON 69.000 | LGEE' | RANGE | 0.94 | 1.06
1068 | 324624 2MADISON LGE69.000 | LGEE' | RANGE | 0.94 | 1.06
1069 | 324625 2MAGAZINE 69.000 | LGEE' | RANGE | 0.94 | 1.06
1070 | 324626 2MANCHEST SO69.000 | LGEE' | RANGE | 0.94 | 1.06
1071 | 324627 2MANCHEST KU69.000 | LGEE' | RANGE | 0.94 | 1.06
1072 | 324628 2MARION SO 69.000 | LGEE' | RANGE | 0.94 | 1.06
1073 | 324629 2MARION KU 69.000 | LGEE' | RANGE | 0.94 | 1.06
1074 | 324630 2MADSNV LP E69.000 | LGEE' | RANGE | 0.94 | 1.06
1075 | 324631 2MADSNV LP W69.000 | LGEE' | RANGE | 0.94 | 1.06
1076 | 324632 2UK MED CENT69.000 | LGEE' | RANGE | 0.94 | 1.06
1077 | 324633 2MELDRUM 69.000 | LGEE' | RANGE | 0.94 | 1.06
1078 | 324634 2METAL+THERM69.000 | LGEE' | RANGE | 0.94 | 1.06
1079 | 324636 2MIDDLESBORO69.000 | LGEE' | RANGE | 0.94 | 1.06
1080 | 324637 2MIDDLETOWN 69.000 | LGEE' | RANGE | 0.94 | 1.06
1081 | 324638 2MILL CRK KU69.000 | LGEE' | RANGE | 0.94 | 1.06
1082 | 324639 2MILLRSB624 69.000 | LGEE' | RANGE | 0.94 | 1.06
1083 | 324640 2MILL CREEK 69.000 | LGEE' | RANGE | 0.94 | 1.06
1084 | 324641 2MILE LAN TP69.000 | LGEE' | RANGE | 0.94 | 1.06
1085 | 324642 2MILLERSBURG69.000 | LGEE' | RANGE | 0.94 | 1.06
1086 | 324643 2MILL WOOD 69.000 | LGEE' | RANGE | 0.94 | 1.06
1087 | 324644 2MORGANFLD 469.000 | LGEE' | RANGE | 0.94 | 1.06
1088 | 324645 2MORGANFIELD69.000 | LGEE' | RANGE | 0.94 | 1.06
1089 | 324646 2MOREHEAD E 69.000 | LGEE' | RANGE | 0.94 | 1.06
1090 | 324647 2MOREHEAD W 69.000 | LGEE' | RANGE | 0.94 | 1.06
1091 | 324648 2MORTONS GAP69.000 | LGEE' | RANGE | 0.94 | 1.06
1092 | 324649 2MORRIS FORM69.000 | LGEE' | RANGE | 0.94 | 1.06
1093 | 324650 2MT TBR T 69.000 | LGEE' | RANGE | 0.94 | 1.06
1094 | 324651 2MUD LANE 69.000 | LGEE' | RANGE | 0.94 | 1.06
1095 | 324652 2MUHLENBRG P69.000 | LGEE' | RANGE | 0.94 | 1.06
1096 | 324653 2M-V SIMPSON69.000 | LGEE' | RANGE | 0.94 | 1.06
1097 | 324654 2MT VIC EK J69.000 | LGEE' | RANGE | 0.94 | 1.06
1098 | 324655 2N CORBIN T 69.000 | LGEE' | RANGE | 0.94 | 1.06
1099 | 324656 2N MADISON T69.000 | LGEE' | RANGE | 0.94 | 1.06
1100 | 324657 2NACHAND 69.000 | LGEE' | RANGE | 0.94 | 1.06
1101 | 324658 2NEBO 69.000 | LGEE' | RANGE | 0.94 | 1.06
1102 | 324659 2NELSON 69.000 | LGEE' | RANGE | 0.94 | 1.06
1103 | 324660 2NEW HAVEN 69.000 | LGEE' | RANGE | 0.94 | 1.06
1104 | 324661 2NICHLSV 7 69.000 | LGEE' | RANGE | 0.94 | 1.06
1105 | 324662 2N LONDON KU69.000 | LGEE' | RANGE | 0.94 | 1.06
1106 | 324663 2NORTON EAST69.000 | LGEE' | RANGE | 0.94 | 1.06
1107 | 324664 2OAK HILL KU69.000 | LGEE' | RANGE | 0.94 | 1.06
1108 | 324665 2OHIO FALL 169.000 | LGEE' | RANGE | 0.94 | 1.06
1109 | 324666 2OHIO FALL 269.000 | LGEE' | RANGE | 0.94 | 1.06
1110 | 324667 2OHIO COUNTY69.000 | LGEE' | RANGE | 0.94 | 1.06
1111 | 324668 2OKONITE 69.000 | LGEE' | RANGE | 0.94 | 1.06
1112 | 324670 2OSAKA EAST 69.000 | LGEE' | RANGE | 0.94 | 1.06
1113 | 324671 2OVERLAD S T69.000 | LGEE' | RANGE | 0.94 | 1.06
1114 | 324672 2OXFORD EK T69.000 | LGEE' | RANGE | 0.94 | 1.06
1115 | 324673 2OXMOOR 69.000 | LGEE' | RANGE | 0.94 | 1.06
1116 | 324674 2PROC & GAMB69.000 | LGEE' | RANGE | 0.94 | 1.06
1117 | 324675 2PADDYS RUN 69.000 | LGEE' | RANGE | 0.94 | 1.06
1118 | 324676 2PAINT LICK 69.000 | LGEE' | RANGE | 0.94 | 1.06
1119 | 324677 2PARIS 12 69.000 | LGEE' | RANGE | 0.94 | 1.06
1120 | 324678 2PARIS CITY 69.000 | LGEE' | RANGE | 0.94 | 1.06
1121 | 324679 2PARIS 3 69.000 | LGEE' | RANGE | 0.94 | 1.06
1122 | 324680 2PARIS KU 69.000 | LGEE' | RANGE | 0.94 | 1.06
1123 | 324681 2PENAL FARM 69.000 | LGEE' | RANGE | 0.94 | 1.06
1124 | 324682 2PENAL TAP 69.000 | LGEE' | RANGE | 0.94 | 1.06
1125 | 324683 2PICADOME 69.000 | LGEE' | RANGE | 0.94 | 1.06
1126 | 324684 2PINEVIL 72269.000 | LGEE' | RANGE | 0.94 | 1.06
1127 | 324686 2PINEVILLE 69.000 | LGEE' | RANGE | 0.94 | 1.06
1128 | 324687 2PISGAH 69.000 | LGEE' | RANGE | 0.94 | 1.06
1129 | 324688 2PITTSBRG KU69.000 | LGEE' | RANGE | 0.94 | 1.06
1130 | 324689 2POCKET 69.000 | LGEE' | RANGE | 0.94 | 1.06
1131 | 324690 2DAWSON TAP 69.000 | LGEE' | RANGE | 0.94 | 1.06
1132 | 324691 2POWDERLY 69.000 | LGEE' | RANGE | 0.94 | 1.06
1133 | 324692 2POWELL MTN 69.000 | LGEE' | RANGE | 0.94 | 1.06
1134 | 324693 2PRINCETON 69.000 | LGEE' | RANGE | 0.94 | 1.06
1135 | 324694 2PARKR MIL T69.000 | LGEE' | RANGE | 0.94 | 1.06
1136 | 324695 2PARKER SEAL69.000 | LGEE' | RANGE | 0.94 | 1.06
1137 | 324696 2PUCKETT CRK69.000 | LGEE' | RANGE | 0.94 | 1.06
1138 | 324698 2RADCLIFF SO69.000 | LGEE' | RANGE | 0.94 | 1.06
1139 | 324699 2RICE STA TP69.000 | LGEE' | RANGE | 0.94 | 1.06
1140 | 324700 2RICHMND SO 69.000 | LGEE' | RANGE | 0.94 | 1.06
1141 | 324701 2RICHMND 69.000 | LGEE' | RANGE | 0.94 | 1.06
1142 | 324702 2RIVER QUEEN69.000 | LGEE' | RANGE | 0.94 | 1.06
1143 | 324703 2RIVERVIEW 69.000 | LGEE' | RANGE | 0.94 | 1.06
1144 | 324704 2ROCKHOLD 69.000 | LGEE' | RANGE | 0.94 | 1.06
1145 | 324705 2ROCKWELL 69.000 | LGEE' | RANGE | 0.94 | 1.06
1146 | 324706 2ROCKY BRNCH69.000 | LGEE' | RANGE | 0.94 | 1.06
1147 | 324707 2RODBURN 69.000 | LGEE' | RANGE | 0.94 | 1.06
1148 | 324708 2ROGERSVILLE69.000 | LGEE' | RANGE | 0.94 | 1.06
1149 | 324709 2RVR QUEEN T69.000 | LGEE' | RANGE | 0.94 | 1.06
1150 | 324710 2RVR CITY SH69.000 | LGEE' | RANGE | 0.94 | 1.06
1151 | 324711 2SPEN CHEM T69.000 | LGEE' | RANGE | 0.94 | 1.06
1152 | 324712 2SO PADUCAH 69.000 | LGEE' | RANGE | 0.94 | 1.06
1153 | 324713 2SO ELKHORN 69.000 | LGEE' | RANGE | 0.94 | 1.06
1154 | 324714 2SALT LICK 69.000 | LGEE' | RANGE | 0.94 | 1.06
1155 | 324715 2SALVISA 69.000 | LGEE' | RANGE | 0.94 | 1.06
1156 | 324716 2SANDY RIDGE69.000 | LGEE' | RANGE | 0.94 | 1.06
1157 | 324717 2SARDIS TAP 69.000 | LGEE' | RANGE | 0.94 | 1.06
1158 | 324718 2SHELBY CO T69.000 | LGEE' | RANGE | 0.94 | 1.06
1159 | 324719 2SEMINOLE 69.000 | LGEE' | RANGE | 0.94 | 1.06
1160 | 324721 2SHAKERTOWN 69.000 | LGEE' | RANGE | 0.94 | 1.06
1161 | 324722 2SHARON KU 69.000 | LGEE' | RANGE | 0.94 | 1.06
1162 | 324723 2SHAVER CHAP69.000 | LGEE' | RANGE | 0.94 | 1.06
1163 | 324724 2SHIVELY 69.000 | LGEE' | RANGE | 0.94 | 1.06
1164 | 324725 2SHELBYVIL E69.000 | LGEE' | RANGE | 0.94 | 1.06
1165 | 324726 2SHELBYVIL S69.000 | LGEE' | RANGE | 0.94 | 1.06
1166 | 324727 2SHELBYVILLE69.000 | LGEE' | RANGE | 0.94 | 1.06
1167 | 324728 2SHUN PIKE 69.000 | LGEE' | RANGE | 0.94 | 1.06
1168 | 324729 2SIMPSONVILL69.000 | LGEE' | RANGE | 0.94 | 1.06
1169 | 324730 2SMYRNA 69.000 | LGEE' | RANGE | 0.94 | 1.06
1170 | 324731 2SONORA TAP 69.000 | LGEE' | RANGE | 0.94 | 1.06
1171 | 324732 2SOUTHVILLE 69.000 | LGEE' | RANGE | 0.94 | 1.06
1172 | 324733 2SPENCER RD 69.000 | LGEE' | RANGE | 0.94 | 1.06
1173 | 324734 2SPINDLETP T69.000 | LGEE' | RANGE | 0.94 | 1.06
1174 | 324735 2SOUTH POINT69.000 | LGEE' | RANGE | 0.94 | 1.06
1175 | 324736 2SPRINGFL KU69.000 | LGEE' | RANGE | 0.94 | 1.06
1176 | 324737 2SOMERSET SO69.000 | LGEE' | RANGE | 0.94 | 1.06
1177 | 324738 2SAINT CHARL69.000 | LGEE' | RANGE | 0.94 | 1.06
1178 | 324739 2STEWART 69.000 | LGEE' | RANGE | 0.94 | 1.06
1179 | 324740 2SOUTH PARK 69.000 | LGEE' | RANGE | 0.94 | 1.06
1180 | 324741 2STINKIN CRK69.000 | LGEE' | RANGE | 0.94 | 1.06
1181 | 324742 2STONEWALL T69.000 | LGEE' | RANGE | 0.94 | 1.06
1182 | 324743 2SAINT PAUL 69.000 | LGEE' | RANGE | 0.94 | 1.06
1183 | 324744 2STRAGHT CRK69.000 | LGEE' | RANGE | 0.94 | 1.06
1184 | 324745 2STRINGTOWN 69.000 | LGEE' | RANGE | 0.94 | 1.06
1185 | 324746 2SUNOCO 69.000 | LGEE' | RANGE | 0.94 | 1.06
1186 | 324747 2SUNSET MINE69.000 | LGEE' | RANGE | 0.94 | 1.06
1187 | 324748 2SWEET HOLLO69.000 | LGEE' | RANGE | 0.94 | 1.06
1188 | 324749 2SYLVANIA 69.000 | LGEE' | RANGE | 0.94 | 1.06
1189 | 324750 2TAYLOR LG 69.000 | LGEE' | RANGE | 0.94 | 1.06
1190 | 324751 2TAYLOR CO 69.000 | LGEE' | RANGE | 0.94 | 1.06
1191 | 324752 2TAYLORSV KU69.000 | LGEE' | RANGE | 0.94 | 1.06
1192 | 324753 2TIP TOP 2 69.000 | LGEE' | RANGE | 0.94 | 1.06
1193 | 324754 2TUNNEL H KU69.000 | LGEE' | RANGE | 0.94 | 1.06
1194 | 324755 2TYRONE 69.000 | LGEE' | RANGE | 0.94 | 1.06
1195 | 324756 2UK WEST 1 69.000 | LGEE' | RANGE | 0.94 | 1.06
1196 | 324757 2UPR MIL CRK69.000 | LGEE' | RANGE | 0.94 | 1.06
1197 | 324758 2US STEEL 69.000 | LGEE' | RANGE | 0.94 | 1.06
1198 | 324759 2VIRGINIA CI69.000 | LGEE' | RANGE | 0.94 | 1.06
1199 | 324760 2VAKSDAHL AV69.000 | LGEE' | RANGE | 0.94 | 1.06
1200 | 324761 2VERDA 69.000 | LGEE' | RANGE | 0.94 | 1.06
1201 | 324762 2VERSAIL W T69.000 | LGEE' | RANGE | 0.94 | 1.06
1202 | 324763 2VERSAILLES 69.000 | LGEE' | RANGE | 0.94 | 1.06
1203 | 324764 2WEST CLIFF 69.000 | LGEE' | RANGE | 0.94 | 1.06
1204 | 324765 2W FRANKFORT69.000 | LGEE' | RANGE | 0.94 | 1.06
1205 | 324766 2W HIGH T1 69.000 | LGEE' | RANGE | 0.94 | 1.06
1206 | 324767 2WEST IRVINE69.000 | LGEE' | RANGE | 0.94 | 1.06
1207 | 324768 2WACO 69.000 | LGEE' | RANGE | 0.94 | 1.06
1208 | 324769 2WALKER KU 69.000 | LGEE' | RANGE | 0.94 | 1.06
1209 | 324770 2WARREN 4 69.000 | LGEE' | RANGE | 0.94 | 1.06
1210 | 324771 2WATTERSON 69.000 | LGEE' | RANGE | 0.94 | 1.06
1211 | 324772 2UK WEST 2 69.000 | LGEE' | RANGE | 0.94 | 1.06
1212 | 324774 2WEBCOAL 4 69.000 | LGEE' | RANGE | 0.94 | 1.06
1213 | 324775 2WHAS 69.000 | LGEE' | RANGE | 0.94 | 1.06
1214 | 324776 2WHEATCROF T69.000 | LGEE' | RANGE | 0.94 | 1.06
1215 | 324777 2WHEATCROFT 69.000 | LGEE' | RANGE | 0.94 | 1.06
1216 | 324778 2WICKLIFE CI69.000 | LGEE' | RANGE | 0.94 | 1.06
1217 | 324779 2WICKLIFFE 69.000 | LGEE' | RANGE | 0.94 | 1.06
1218 | 324780 2WIL DOWN T169.000 | LGEE' | RANGE | 0.94 | 1.06
1219 | 324781 2WILMORE T 69.000 | LGEE' | RANGE | 0.94 | 1.06
1220 | 324782 2WINCHEST SO69.000 | LGEE' | RANGE | 0.94 | 1.06
1221 | 324783 2WINCHSTR KU69.000 | LGEE' | RANGE | 0.94 | 1.06
1222 | 324784 2WOFFORD 69.000 | LGEE' | RANGE | 0.94 | 1.06
1223 | 324785 2WORTHINGTON69.000 | LGEE' | RANGE | 0.94 | 1.06
1224 | 324786 2ZION 69.000 | LGEE' | RANGE | 0.94 | 1.06
1225 | 324787 2UNION UNDWR69.000 | LGEE' | RANGE | 0.94 | 1.06
1226 | 324788 2BROOKS EK T69.000 | LGEE' | RANGE | 0.94 | 1.06
1227 | 324789 2BLUE LCK TP69.000 | LGEE' | RANGE | 0.94 | 1.06
1228 | 324790 2AIRLINE RD 69.000 | LGEE' | RANGE | 0.94 | 1.06
1229 | 324791 2AISIN 69.000 | LGEE' | RANGE | 0.94 | 1.06
1230 | 324792 2ALVA 69.000 | LGEE' | RANGE | 0.94 | 1.06
1231 | 324794 2ASHLND PIPE69.000 | LGEE' | RANGE | 0.94 | 1.06
1232 | 324795 2ASHBYBRG PU69.000 | LGEE' | RANGE | 0.94 | 1.06
1233 | 324796 2AVON 69.000 | LGEE' | RANGE | 0.94 | 1.06
1234 | 324797 2AVON T1 69.000 | LGEE' | RANGE | 0.94 | 1.06
1235 | 324798 2BAILEY CRK 69.000 | LGEE' | RANGE | 0.94 | 1.06
1236 | 324799 2BARNHILL 69.000 | LGEE' | RANGE | 0.94 | 1.06
1237 | 324800 4MERE TVA 138.00 | LGEE' | RANGE | 0.94 | 1.06
1238 | 324801 2BARTON 69.000 | LGEE' | RANGE | 0.94 | 1.06
1239 | 324802 2BEAR BRANCH69.000 | LGEE' | RANGE | 0.94 | 1.06
1240 | 324803 2BEAR TRACK 69.000 | LGEE' | RANGE | 0.94 | 1.06
1241 | 324804 2BEDFORD TAP69.000 | LGEE' | RANGE | 0.94 | 1.06
1242 | 324805 2BEREA 2 69.000 | LGEE' | RANGE | 0.94 | 1.06
1243 | 324806 2BEULAH EKPC69.000 | LGEE' | RANGE | 0.94 | 1.06
1244 | 324807 2BRANDENBURG69.000 | LGEE' | RANGE | 0.94 | 1.06
1245 | 324808 2BRODHEAD KU69.000 | LGEE' | RANGE | 0.94 | 1.06
1246 | 324809 2BROOKS EKPC69.000 | LGEE' | RANGE | 0.94 | 1.06
1247 | 324810 2CALHOUN 69.000 | LGEE' | RANGE | 0.94 | 1.06
1248 | 324811 2CANEYVL JCT69.000 | LGEE' | RANGE | 0.94 | 1.06
1249 | 324812 2CARLISLE 69.000 | LGEE' | RANGE | 0.94 | 1.06
1250 | 324813 2CARY 69.000 | LGEE' | RANGE | 0.94 | 1.06
1251 | 324814 2CATRON CK T69.000 | LGEE' | RANGE | 0.94 | 1.06
1252 | 324815 2CAWOOD 69.000 | LGEE' | RANGE | 0.94 | 1.06
1253 | 324816 2CEMETARY RD69.000 | LGEE' | RANGE | 0.94 | 1.06
1254 | 324817 2CENTRAL CIT69.000 | LGEE' | RANGE | 0.94 | 1.06
1255 | 324818 2CHAD TAP 69.000 | LGEE' | RANGE | 0.94 | 1.06
1256 | 324819 2CHUNKLIC BR69.000 | LGEE' | RANGE | 0.94 | 1.06
1257 | 324820 2ISLAND MINE69.000 | LGEE' | RANGE | 0.94 | 1.06
1258 | 324821 2CLARKSON 69.000 | LGEE' | RANGE | 0.94 | 1.06
1259 | 324822 2CLAY KU 69.000 | LGEE' | RANGE | 0.94 | 1.06
1260 | 324823 2CLINTON 58169.000 | LGEE' | RANGE | 0.94 | 1.06
1261 | 324824 2CLINCH VALL69.000 | LGEE' | RANGE | 0.94 | 1.06
1262 | 324825 2CLINTON KU 69.000 | LGEE' | RANGE | 0.94 | 1.06
1263 | 324826 2CLINCH V SW69.000 | LGEE' | RANGE | 0.94 | 1.06
1264 | 324827 2CLOVERLICK 69.000 | LGEE' | RANGE | 0.94 | 1.06
1265 | 324828 2CAMPBBRG KU69.000 | LGEE' | RANGE | 0.94 | 1.06
1266 | 324829 2CAMPBELVIL169.000 | LGEE' | RANGE | 0.94 | 1.06
1267 | 324830 2CAMPBELV EK69.000 | LGEE' | RANGE | 0.94 | 1.06
1268 | 324831 4WHITE SULPH138.00 | LGEE' | RANGE | 0.94 | 1.06
1269 | 324832 2CORBIN 1 69.000 | LGEE' | RANGE | 0.94 | 1.06
1270 | 324833 2CORBIN 2 69.000 | LGEE' | RANGE | 0.94 | 1.06
1271 | 324836 2BENS BRANCH69.000 | LGEE' | RANGE | 0.94 | 1.06
1272 | 324837 2CYNTHIAN KU69.000 | LGEE' | RANGE | 0.94 | 1.06
1273 | 324838 2DANV IND TP69.000 | LGEE' | RANGE | 0.94 | 1.06
1274 | 324839 2DANVILE IND69.000 | LGEE' | RANGE | 0.94 | 1.06
1275 | 324840 2DANVILLE E 69.000 | LGEE' | RANGE | 0.94 | 1.06
1276 | 324841 2DANVILLE W 69.000 | LGEE' | RANGE | 0.94 | 1.06
1277 | 324842 2DAVIS TAP 69.000 | LGEE' | RANGE | 0.94 | 1.06
1278 | 324843 2DAWSON IND 69.000 | LGEE' | RANGE | 0.94 | 1.06
1279 | 324844 2DELAPLAIN 69.000 | LGEE' | RANGE | 0.94 | 1.06
1280 | 324845 2DENHAM ST 69.000 | LGEE' | RANGE | 0.94 | 1.06
1281 | 324846 2DIAMOND 69.000 | LGEE' | RANGE | 0.94 | 1.06
1282 | 324847 2DODGE HILL 69.000 | LGEE' | RANGE | 0.94 | 1.06
1283 | 324848 2DONERAIL 69.000 | LGEE' | RANGE | 0.94 | 1.06
1284 | 324849 2DOW CORNING69.000 | LGEE' | RANGE | 0.94 | 1.06
1285 | 324850 2DOZIER H 69.000 | LGEE' | RANGE | 0.94 | 1.06
1286 | 324851 2DWINA TAP 69.000 | LGEE' | RANGE | 0.94 | 1.06
1287 | 324852 2DYCUSBURG 69.000 | LGEE' | RANGE | 0.94 | 1.06
1288 | 324853 2E STONE GAP69.000 | LGEE' | RANGE | 0.94 | 1.06
1289 | 324855 2EKPC OFF TP69.000 | LGEE' | RANGE | 0.94 | 1.06
1290 | 324856 2ESTIL ST CO69.000 | LGEE' | RANGE | 0.94 | 1.06
1291 | 324857 2ETOWN 2 69.000 | LGEE' | RANGE | 0.94 | 1.06
1292 | 324858 2ETOWN 5 69.000 | LGEE' | RANGE | 0.94 | 1.06
1293 | 324859 2FAIRMOUNT 169.000 | LGEE' | RANGE | 0.94 | 1.06
1294 | 324860 2FARISTON 69.000 | LGEE' | RANGE | 0.94 | 1.06
1295 | 324862 2FIES CITY 69.000 | LGEE' | RANGE | 0.94 | 1.06
1296 | 324863 2FLA TILE T169.000 | LGEE' | RANGE | 0.94 | 1.06
1297 | 324864 2FORRESTDALE69.000 | LGEE' | RANGE | 0.94 | 1.06
1298 | 324865 2FREDONIA 69.000 | LGEE' | RANGE | 0.94 | 1.06
1299 | 324866 2GE LAMP 69.000 | LGEE' | RANGE | 0.94 | 1.06
1300 | 324867 2GHENT 69.000 | LGEE' | RANGE | 0.94 | 1.06
1301 | 324870 2GREENVILLE 69.000 | LGEE' | RANGE | 0.94 | 1.06
1302 | 324871 2HAMER 69.000 | LGEE' | RANGE | 0.94 | 1.06
1303 | 324873 2HANSON JCT 69.000 | LGEE' | RANGE | 0.94 | 1.06
1304 | 324874 2HARROGATE 69.000 | LGEE' | RANGE | 0.94 | 1.06
1305 | 324875 2HIGHSPLINT 69.000 | LGEE' | RANGE | 0.94 | 1.06
1306 | 324876 2HOLMES MILL69.000 | LGEE' | RANGE | 0.94 | 1.06
1307 | 324877 2HOOVER KU 69.000 | LGEE' | RANGE | 0.94 | 1.06
1308 | 324878 2HUNT BTM TP69.000 | LGEE' | RANGE | 0.94 | 1.06
1309 | 324879 2IBM 998 69.000 | LGEE' | RANGE | 0.94 | 1.06
1310 | 324880 2IRVINE 69.000 | LGEE' | RANGE | 0.94 | 1.06
1311 | 324881 2JACKS CREEK69.000 | LGEE' | RANGE | 0.94 | 1.06
1312 | 324882 2KENTON 698 69.000 | LGEE' | RANGE | 0.94 | 1.06
1313 | 324884 2KUNKEL 69.000 | LGEE' | RANGE | 0.94 | 1.06
1314 | 324885 2KUTTAWA 69.000 | LGEE' | RANGE | 0.94 | 1.06
1315 | 324886 2KY RIVER 69.000 | LGEE' | RANGE | 0.94 | 1.06
1316 | 324887 2LA GRANG PE69.000 | LGEE' | RANGE | 0.94 | 1.06
1317 | 324888 2LAWRENCE 69.000 | LGEE' | RANGE | 0.94 | 1.06
1318 | 324889 2LEBANON SO 69.000 | LGEE' | RANGE | 0.94 | 1.06
1319 | 324890 2LEMONS MILL69.000 | LGEE' | RANGE | 0.94 | 1.06
1320 | 324891 2LEX WATER 69.000 | LGEE' | RANGE | 0.94 | 1.06
1321 | 324892 2LIGGETT 69.000 | LGEE' | RANGE | 0.94 | 1.06
1322 | 324893 2MADSNV GE T69.000 | LGEE' | RANGE | 0.94 | 1.06
1323 | 324894 2E STONE G T69.000 | LGEE' | RANGE | 0.94 | 1.06
1324 | 324895 2MADSNV HO 69.000 | LGEE' | RANGE | 0.94 | 1.06
1325 | 324896 2MADSNV E 69.000 | LGEE' | RANGE | 0.94 | 1.06
1326 | 324897 2MADSNV N 69.000 | LGEE' | RANGE | 0.94 | 1.06
1327 | 324898 2MANITOU 69.000 | LGEE' | RANGE | 0.94 | 1.06
1328 | 324899 2MAYSVILLE E69.000 | LGEE' | RANGE | 0.94 | 1.06
1329 | 324900 2MAYSVILLE M69.000 | LGEE' | RANGE | 0.94 | 1.06
1330 | 324901 2MAYSVILLE W69.000 | LGEE' | RANGE | 0.94 | 1.06
1331 | 324902 2MCCOY AVE 69.000 | LGEE' | RANGE | 0.94 | 1.06
1332 | 324903 2MCKEE ROAD 69.000 | LGEE' | RANGE | 0.94 | 1.06
1333 | 324904 2MEXICO KU 69.000 | LGEE' | RANGE | 0.94 | 1.06
1334 | 324907 2MILLER CRK 69.000 | LGEE' | RANGE | 0.94 | 1.06
1335 | 324908 2MILTON 69.000 | LGEE' | RANGE | 0.94 | 1.06
1336 | 324909 2MINR FARM T69.000 | LGEE' | RANGE | 0.94 | 1.06
1337 | 324910 2MOREHEAD 69.000 | LGEE' | RANGE | 0.94 | 1.06
1338 | 324911 2MARKLAND DM69.000 | LGEE' | RANGE | 0.94 | 1.06
1339 | 324912 2MT STERL KU69.000 | LGEE' | RANGE | 0.94 | 1.06
1340 | 324913 2MT VERNON 69.000 | LGEE' | RANGE | 0.94 | 1.06
1341 | 324914 2M-V CLARK T69.000 | LGEE' | RANGE | 0.94 | 1.06
1342 | 324915 2MT WAS EK J69.000 | LGEE' | RANGE | 0.94 | 1.06
1343 | 324916 2NEWTOWN TAP69.000 | LGEE' | RANGE | 0.94 | 1.06
1344 | 324917 2NICHLSV 3 69.000 | LGEE' | RANGE | 0.94 | 1.06
1345 | 324918 2NICHLSV 4&569.000 | LGEE' | RANGE | 0.94 | 1.06
1346 | 324919 2NICHLSV 6&869.000 | LGEE' | RANGE | 0.94 | 1.06
1347 | 324920 2NINEVAH TAP69.000 | LGEE' | RANGE | 0.94 | 1.06
1348 | 324921 2ARCH CHEM 69.000 | LGEE' | RANGE | 0.94 | 1.06
1349 | 324922 2ONTON 69.000 | LGEE' | RANGE | 0.94 | 1.06
1350 | 324924 2OXFORD 69.000 | LGEE' | RANGE | 0.94 | 1.06
1351 | 324925 2PLEAS GRV T69.000 | LGEE' | RANGE | 0.94 | 1.06
1352 | 324927 2PINE HILL T69.000 | LGEE' | RANGE | 0.94 | 1.06
1353 | 324928 2POOLE 69.000 | LGEE' | RANGE | 0.94 | 1.06
1354 | 324930 2PARKER MILL69.000 | LGEE' | RANGE | 0.94 | 1.06
1355 | 324931 2PROVIDNCE E69.000 | LGEE' | RANGE | 0.94 | 1.06
1356 | 324932 2PROVIDENCE 69.000 | LGEE' | RANGE | 0.94 | 1.06
1357 | 324934 2RACE STREET69.000 | LGEE' | RANGE | 0.94 | 1.06
1358 | 324935 2RADCLF KU T69.000 | LGEE' | RANGE | 0.94 | 1.06
1359 | 324936 2RICHMND IND69.000 | LGEE' | RANGE | 0.94 | 1.06
1360 | 324937 2RICHMND 2 69.000 | LGEE' | RANGE | 0.94 | 1.06
1361 | 324938 2RICHMND 3 69.000 | LGEE' | RANGE | 0.94 | 1.06
1362 | 324939 2RICHMND 4 69.000 | LGEE' | RANGE | 0.94 | 1.06
1363 | 324940 2RICHMND J 69.000 | LGEE' | RANGE | 0.94 | 1.06
1364 | 324941 2RIVERPORT 69.000 | LGEE' | RANGE | 0.94 | 1.06
1365 | 324942 2ROBBINS 69.000 | LGEE' | RANGE | 0.94 | 1.06
1366 | 324943 2ROGERS GAP 69.000 | LGEE' | RANGE | 0.94 | 1.06
1367 | 324944 2ROGERSV 60569.000 | LGEE' | RANGE | 0.94 | 1.06
1368 | 324945 2ROSE HILL T69.000 | LGEE' | RANGE | 0.94 | 1.06
1369 | 324946 2ROSINE JCT 69.000 | LGEE' | RANGE | 0.94 | 1.06
1370 | 324947 2RUMSEY 69.000 | LGEE' | RANGE | 0.94 | 1.06
1371 | 324948 2SALEM KU 69.000 | LGEE' | RANGE | 0.94 | 1.06
1372 | 324949 2SALEM 673 69.000 | LGEE' | RANGE | 0.94 | 1.06
1373 | 324950 2SCIENC HILL69.000 | LGEE' | RANGE | 0.94 | 1.06
1374 | 324951 2SCOTT CO 69.000 | LGEE' | RANGE | 0.94 | 1.06
1375 | 324952 2SCOTT ST TP69.000 | LGEE' | RANGE | 0.94 | 1.06
1376 | 324953 2SEBREE 69.000 | LGEE' | RANGE | 0.94 | 1.06
1377 | 324954 2SENTRY TAP 69.000 | LGEE' | RANGE | 0.94 | 1.06
1378 | 324955 2SHANNON RUN69.000 | LGEE' | RANGE | 0.94 | 1.06
1379 | 324956 2SHAWNEE GAS69.000 | LGEE' | RANGE | 0.94 | 1.06
1380 | 324957 2SHELBY CI T69.000 | LGEE' | RANGE | 0.94 | 1.06
1381 | 324958 2SHEPHRDSV T69.000 | LGEE' | RANGE | 0.94 | 1.06
1382 | 324959 2SIMMONS 69.000 | LGEE' | RANGE | 0.94 | 1.06
1383 | 324960 2SKYLIGHT 69.000 | LGEE' | RANGE | 0.94 | 1.06
1384 | 324961 2SOMERSET GE69.000 | LGEE' | RANGE | 0.94 | 1.06
1385 | 324962 2SOMERSET 1 69.000 | LGEE' | RANGE | 0.94 | 1.06
1386 | 324963 2SOMERSET 2 69.000 | LGEE' | RANGE | 0.94 | 1.06
1387 | 324964 2SOMERSET 3 69.000 | LGEE' | RANGE | 0.94 | 1.06
1388 | 324965 2SOMERSET NO69.000 | LGEE' | RANGE | 0.94 | 1.06
1389 | 324966 2SPARTA KU 69.000 | LGEE' | RANGE | 0.94 | 1.06
1390 | 324967 2SPEAR STA A69.000 | LGEE' | RANGE | 0.94 | 1.06
1391 | 324968 2SPEAR STA B69.000 | LGEE' | RANGE | 0.94 | 1.06
1392 | 324969 2SMRST 615KU69.000 | LGEE' | RANGE | 0.94 | 1.06
1393 | 324970 2STANFORD KU69.000 | LGEE' | RANGE | 0.94 | 1.06
1394 | 324971 2STANFORD NO69.000 | LGEE' | RANGE | 0.94 | 1.06
1395 | 324972 2STONEWALL 69.000 | LGEE' | RANGE | 0.94 | 1.06
1396 | 324973 2STURGIS 69.000 | LGEE' | RANGE | 0.94 | 1.06
1397 | 324974 2TAYLRV EK T69.000 | LGEE' | RANGE | 0.94 | 1.06
1398 | 324975 2TERRY 69.000 | LGEE' | RANGE | 0.94 | 1.06
1399 | 324976 2TIP TOP 1 69.000 | LGEE' | RANGE | 0.94 | 1.06
1400 | 324977 2TOMS CRK TP69.000 | LGEE' | RANGE | 0.94 | 1.06
1401 | 324978 2TOTZ 69.000 | LGEE' | RANGE | 0.94 | 1.06
1402 | 324979 2TRAFTON AVE69.000 | LGEE' | RANGE | 0.94 | 1.06
1403 | 324980 2RJ CORMAN 69.000 | LGEE' | RANGE | 0.94 | 1.06
1404 | 324981 2TEXAS GAS T69.000 | LGEE' | RANGE | 0.94 | 1.06
1405 | 324982 2VINE GRV KU69.000 | LGEE' | RANGE | 0.94 | 1.06
1406 | 324984 2VINE STREET69.000 | LGEE' | RANGE | 0.94 | 1.06
1407 | 324985 2VSAIL BYPAS69.000 | LGEE' | RANGE | 0.94 | 1.06
1408 | 324986 2W HIGH T2 69.000 | LGEE' | RANGE | 0.94 | 1.06
1409 | 324987 2W HICKMAN 69.000 | LGEE' | RANGE | 0.94 | 1.06
1410 | 324988 2WEST HIGH 69.000 | LGEE' | RANGE | 0.94 | 1.06
1411 | 324989 2W NICHSV T 69.000 | LGEE' | RANGE | 0.94 | 1.06
1412 | 324990 2WAITSBORO 69.000 | LGEE' | RANGE | 0.94 | 1.06
1413 | 324991 4ROGERS GAP 138.00 | LGEE' | RANGE | 0.94 | 1.06
1414 | 324992 2WARREN TIE 69.000 | LGEE' | RANGE | 0.94 | 1.06
1415 | 324993 2WARRIOR CL 69.000 | LGEE' | RANGE | 0.94 | 1.06
1416 | 324994 2WARSAW KU 69.000 | LGEE' | RANGE | 0.94 | 1.06
1417 | 324995 2WAYNESBURG 69.000 | LGEE' | RANGE | 0.94 | 1.06
1418 | 324996 2DOTIKI TAP 69.000 | LGEE' | RANGE | 0.94 | 1.06
1419 | 324997 2WEST CO 1 69.000 | LGEE' | RANGE | 0.94 | 1.06
1420 | 324998 2WEST CO 2 69.000 | LGEE' | RANGE | 0.94 | 1.06
1421 | 324999 2WHTE OAK KU69.000 | LGEE' | RANGE | 0.94 | 1.06
1422 | 325000 2WIL DOWN T269.000 | LGEE' | RANGE | 0.94 | 1.06
1423 | 325001 2WILLMBRG SW69.000 | LGEE' | RANGE | 0.94 | 1.06
1424 | 325002 2WILS DOWN 169.000 | LGEE' | RANGE | 0.94 | 1.06
1425 | 325003 2WILS DOWN 269.000 | LGEE' | RANGE | 0.94 | 1.06
1426 | 325004 2WINCHES WTR69.000 | LGEE' | RANGE | 0.94 | 1.06
1427 | 325005 2WISE TAP 69.000 | LGEE' | RANGE | 0.94 | 1.06
1428 | 325006 2W MT WSH EK69.000 | LGEE' | RANGE | 0.94 | 1.06
1429 | 325007 2YANCY TAP 69.000 | LGEE' | RANGE | 0.94 | 1.06
1430 | 325008 2BLEDSOE 69.000 | LGEE' | RANGE | 0.94 | 1.06
1431 | 325009 2SPENCER A 69.000 | LGEE' | RANGE | 0.94 | 1.06
1432 | 325010 2WEBCOAL 2 69.000 | LGEE' | RANGE | 0.94 | 1.06
1433 | 325011 2DOTIKI 69.000 | LGEE' | RANGE | 0.94 | 1.06
1434 | 325013 4CLIFTY TAP1138.00 | LGEE' | RANGE | 0.94 | 1.06
1435 | 325014 4CLIFTY TAP2138.00 | LGEE' | RANGE | 0.94 | 1.06
1436 | 325015 4SMITH TAP 138.00 | LGEE' | RANGE | 0.94 | 1.06
1437 | 325017 2CMWA 69.000 | LGEE' | RANGE | 0.94 | 1.06
1438 | 325018 2CLA 69.000 | LGEE' | RANGE | 0.94 | 1.06
1439 | 325019 2KENTON-6 69.000 | LGEE' | RANGE | 0.94 | 1.06
1440 | 325020 2LEBANON E 69.000 | LGEE' | RANGE | 0.94 | 1.06
1441 | 325021 2CONESTOGA 69.000 | LGEE' | RANGE | 0.94 | 1.06
1442 | 325022 2EASTWOOD W 69.000 | LGEE' | RANGE | 0.94 | 1.06
1443 | 325023 2ASHBOT EAST69.000 | LGEE' | RANGE | 0.94 | 1.06
1444 | 325024 2ASHBOT SPRK69.000 | LGEE' | RANGE | 0.94 | 1.06
1445 | 325025 2WARSAW EAST69.000 | LGEE' | RANGE | 0.94 | 1.06
1446 | 325026 2PINE MOUNTN69.000 | LGEE' | RANGE | 0.94 | 1.06
1447 | 325027 2NEWTOWN 69.000 | LGEE' | RANGE | 0.94 | 1.06
1448 | 325028 5ASHWD SL TP161.00 | LGEE' | RANGE | 0.94 | 1.06
1449 | 325031 2LIPPS 69.000 | LGEE' | RANGE | 0.94 | 1.06
1450 | 325032 2MINOR FARM 69.000 | LGEE' | RANGE | 0.94 | 1.06
1451 | 325033 2BEDFORD KU 69.000 | LGEE' | RANGE | 0.94 | 1.06
1452 | 325034 2CUMBER FALL69.000 | LGEE' | RANGE | 0.94 | 1.06
1453 | 325035 2BLUE SOL TP69.000 | LGEE' | RANGE | 0.94 | 1.06
1454 | 325040 2LEITCHF TVA69.000 | LGEE' | RANGE | 0.94 | 1.06
1455 | 325041 2STONE TVA 69.000 | LGEE' | RANGE | 0.94 | 1.06
1456 | 325042 4JEFERSONTWN138.00 | LGEE' | RANGE | 0.94 | 1.06
1457 | 325043 2SHEPHERDSV 69.000 | LGEE' | RANGE | 0.94 | 1.06
1458 | 325044 4INTRNTL 138.00 | LGEE' | RANGE | 0.94 | 1.06
1459 | 325045 2TURTLE CRK 69.000 | LGEE' | RANGE | 0.94 | 1.06
1460 | 325047 5ASHWOOD 161.00 | LGEE' | RANGE | 0.94 | 1.06
1461 | 325050 2BLUE SOLAR 69.000 | LGEE' | RANGE | 0.94 | 1.06
1462 | 325054 2HARRDSBRG N69.000 | LGEE' | RANGE | 0.94 | 1.06
1463 | 325055 4RHUDES TP 138.00 | LGEE' | RANGE | 0.94 | 1.06
1464 | 325057 4KOSMOS CEME138.00 | LGEE' | RANGE | 0.94 | 1.06
1465 | 325058 2BEATTY 614 69.000 | LGEE' | RANGE | 0.94 | 1.06
1466 | 325059 2BRYANT RD T69.000 | LGEE' | RANGE | 0.94 | 1.06
1467 | 325060 2BRYANT ROAD69.000 | LGEE' | RANGE | 0.94 | 1.06
1468 | 325061 2CMC 69.000 | LGEE' | RANGE | 0.94 | 1.06
1469 | 325062 2TEXAS GAS 69.000 | LGEE' | RANGE | 0.94 | 1.06
1470 | 325063 2CORPORAT DR69.000 | LGEE' | RANGE | 0.94 | 1.06
1471 | 325064 2LAUREL GROV69.000 | LGEE' | RANGE | 0.94 | 1.06
1472 | 325068 2HAMBLIN 69.000 | LGEE' | RANGE | 0.94 | 1.06
1473 | 325069 5SONG SP TP 161.00 | LGEE' | RANGE | 0.94 | 1.06
1474 | 325073 7REDMON RD 345.00 | LGEE' | RANGE | 0.94 | 1.06
1475 | 325074 7W GARRARDKU345.00 | LGEE' | RANGE | 0.94 | 1.06
1476 | 325075 5KMPA COLEMN161.00 | LGEE' | RANGE | 0.94 | 1.06
1477 | 325077 5COLEMAN TAP161.00 | LGEE' | RANGE | 0.94 | 1.06
1478 | 325078 5PADUCAH PRI161.00 | LGEE' | RANGE | 0.94 | 1.06
1479 | 325079 5N PRINCETON161.00 | LGEE' | RANGE | 0.94 | 1.06
1480 | 325081 2BRIAR HILL 69.000 | LGEE' | RANGE | 0.94 | 1.06
1481 | 325082 2ARMSTR BREC69.000 | LGEE' | RANGE | 0.94 | 1.06
1482 | 325083 2ALEX CK TAP69.000 | LGEE' | RANGE | 0.94 | 1.06
1483 | 325084 2FLOYD EKP T69.000 | LGEE' | RANGE | 0.94 | 1.06
1484 | 325085 2CYNTHI EK T69.000 | LGEE' | RANGE | 0.94 | 1.06
1485 | 325086 2KEN AMERI 269.000 | LGEE' | RANGE | 0.94 | 1.06
1486 | 325087 2CLAY LICK T69.000 | LGEE' | RANGE | 0.94 | 1.06
1487 | 325088 4MIL CK YARD138.00 | LGEE' | RANGE | 0.94 | 1.06
1488 | 325089 4HIGBY MILL2138.00 | LGEE' | RANGE | 0.94 | 1.06
1489 | 325092 2COAL GOOD 69.000 | LGEE' | RANGE | 0.94 | 1.06
1490 | 325096 4CANERN NGCC138.00 | LGEE' | RANGE | 0.94 | 1.06
1491 | 325100 4W LEX R1 138.00 | LGEE' | RANGE | 0.94 | 1.06
1492 | 325101 4W LEX R2 138.00 | LGEE' | RANGE | 0.94 | 1.06
1493 | 325102 2W SHELBY 69.000 | LGEE' | RANGE | 0.94 | 1.06
1494 | 325116 4RHUDES CR 138.00 | LGEE' | RANGE | 0.94 | 1.06
1495 | 325121 4LOGAN TP 138.00 | LGEE' | RANGE | 0.94 | 1.06
1496 | 325132 4GREENSOL TP138.00 | LGEE' | RANGE | 0.94 | 1.06
1497 | 325761 2WARRIOR PRP69.000 | LGEE' | RANGE | 0.94 | 1.06
1498 | 325762 2WARRIOR TAP69.000 | LGEE' | RANGE | 0.94 | 1.06
1499 | 325767 2SENTRY 69.000 | LGEE' | RANGE | 0.94 | 1.06
1500 | 325857 4BROWN N TIE138.00 | LGEE' | RANGE | 0.94 | 1.06
1501 | 325921 5TAYLOR CO 161.00 | LGEE' | RANGE | 0.94 | 1.06
1502 | 325925 4BOONSBORO N138.00 | LGEE' | RANGE | 0.94 | 1.06
1503 | 325956 4BROWN N 2 138.00 | LGEE' | RANGE | 0.94 | 1.06
1504 | 325957 4BROWN N 1 138.00 | LGEE' | RANGE | 0.94 | 1.06
1505 | 326001 7CANE RUN TP345.00 | LGEE' | RANGE | 0.94 | 1.06
1506 | 326002 7CANERN NGCC345.00 | LGEE' | RANGE | 0.94 | 1.06
1507 | 326512 4AIRGAS 138.00 | LGEE' | RANGE | 0.94 | 1.06
1508 | 326513 2EQAL M BREC69.000 | LGEE' | RANGE | 0.94 | 1.06
1509 | 326517 2OVEN FORK 69.000 | LGEE' | RANGE | 0.94 | 1.06
1510 | 326518 2SHELB CI EK69.000 | LGEE' | RANGE | 0.94 | 1.06
1511 | 326520 4TRIMBLE TR9138.00 | LGEE' | RANGE | 0.94 | 1.06
1512 | 326521 2CAMPGRND EK69.000 | LGEE' | RANGE | 0.94 | 1.06
1513 | 326523 2ARKLAND JCT69.000 | LGEE' | RANGE | 0.94 | 1.06
1514 | 326524 2VAN METER 69.000 | LGEE' | RANGE | 0.94 | 1.06
1515 | 326525 2TREEHAVEN 69.000 | LGEE' | RANGE | 0.94 | 1.06
1516 | 326526 4N SHARKEY 138.00 | LGEE' | RANGE | 0.94 | 1.06
1517 | 326527 2TREEHAVEN T69.000 | LGEE' | RANGE | 0.94 | 1.06
1518 | 326528 2BRIDGEPORT 69.000 | LGEE' | RANGE | 0.94 | 1.06
1519 | 326529 2NINEVAH 69.000 | LGEE' | RANGE | 0.94 | 1.06
1520 | 326530 2EMANUEL 69.000 | LGEE' | RANGE | 0.94 | 1.06
1521 | 326531 2HINKSTON 69.000 | LGEE' | RANGE | 0.94 | 1.06
1522 | 326532 4SHARKEY 138.00 | LGEE' | RANGE | 0.94 | 1.06
1523 | 326533 2BUSH EKPC 69.000 | LGEE' | RANGE | 0.94 | 1.06
1524 | 326534 2ARKLAND 69.000 | LGEE' | RANGE | 0.94 | 1.06
1525 | 326535 2CARPENTER 69.000 | LGEE' | RANGE | 0.94 | 1.06
1526 | 326536 7GALLATIN 345.00 | LGEE' | RANGE | 0.94 | 1.06
1527 | 326537 2WOODLAWN KU69.000 | LGEE' | RANGE | 0.94 | 1.06
1528 | 326538 2CAVE RUN 69.000 | LGEE' | RANGE | 0.94 | 1.06
1529 | 326539 2GIRDLER 69.000 | LGEE' | RANGE | 0.94 | 1.06
1530 | 326541 2EKPC OFFICE69.000 | LGEE' | RANGE | 0.94 | 1.06
1531 | 326542 2N CORBIN 69.000 | LGEE' | RANGE | 0.94 | 1.06
1532 | 326544 2ALEX CREEK 69.000 | LGEE' | RANGE | 0.94 | 1.06
1533 | 326545 2LOCUST LGE 69.000 | LGEE' | RANGE | 0.94 | 1.06
1534 | 326546 2SUNOCO TAP 69.000 | LGEE' | RANGE | 0.94 | 1.06
1535 | 326547 2SONORA 69.000 | LGEE' | RANGE | 0.94 | 1.06
1536 | 326548 4IBM NORTH 138.00 | LGEE' | RANGE | 0.94 | 1.06
1537 | 326549 2SARDIS 69.000 | LGEE' | RANGE | 0.94 | 1.06
1538 | 326552 2SE COAL TP 69.000 | LGEE' | RANGE | 0.94 | 1.06
1539 | 326553 2SE COAL 69.000 | LGEE' | RANGE | 0.94 | 1.06
1540 | 326555 2RINEYVIL RD69.000 | LGEE' | RANGE | 0.94 | 1.06
1541 | 326556 4N SHARKEY T138.00 | LGEE' | RANGE | 0.94 | 1.06
1542 | 326559 4BGAD TAP 138.00 | LGEE' | RANGE | 0.94 | 1.06
1543 | 326560 4BG ARMY DEP138.00 | LGEE' | RANGE | 0.94 | 1.06
1544 | 326561 2ETOWN WEST 69.000 | LGEE' | RANGE | 0.94 | 1.06
1545 | 326562 2PAD PRI 62469.000 | LGEE' | RANGE | 0.94 | 1.06
1546 | 326563 2ADVENT MINE69.000 | LGEE' | RANGE | 0.94 | 1.06
1547 | 326564 2LEW BREC 69.000 | LGEE' | RANGE | 0.94 | 1.06
1548 | 326565 4INTRNTL TAP138.00 | LGEE' | RANGE | 0.94 | 1.06
1549 | 326566 4CANE RUN 71138.00 | LGEE' | RANGE | 0.94 | 1.06
1550 | 326567 4CANE RUN 72138.00 | LGEE' | RANGE | 0.94 | 1.06
1551 | 326568 4CANE RUN 7S138.00 | LGEE' | RANGE | 0.94 | 1.06
1552 | 326569 7KENZIG ROAD345.00 | LGEE' | RANGE | 0.94 | 1.06
1553 | 326571 2HUME RD 69.000 | LGEE' | RANGE | 0.94 | 1.06
1554 | 326572 2RIVRVW COAL69.000 | LGEE' | RANGE | 0.94 | 1.06
1555 | 326574 4CR11 TAP 138.00 | LGEE' | RANGE | 0.94 | 1.06
1556 | 326578 2HARRDSBRG 169.000 | LGEE' | RANGE | 0.94 | 1.06
1557 | 326579 2HARRDSBRG 269.000 | LGEE' | RANGE | 0.94 | 1.06
1558 | 326580 2CORNIG 825369.000 | LGEE' | RANGE | 0.94 | 1.06
1559 | 326582 2CORNG8251_269.000 | LGEE' | RANGE | 0.94 | 1.06
1560 | 326583 2CORNIG 746169.000 | LGEE' | RANGE | 0.94 | 1.06
1561 | 326584 2CORNG7462_369.000 | LGEE' | RANGE | 0.94 | 1.06
1562 | 326586 2HUME RD TAP69.000 | LGEE' | RANGE | 0.94 | 1.06
1563 | 326587 2MADSNV W TP69.000 | LGEE' | RANGE | 0.94 | 1.06
1564 | 326589 5N PRN LIV R161.00 | LGEE' | RANGE | 0.94 | 1.06
1565 | 326591 5W PRINCETON161.00 | LGEE' | RANGE | 0.94 | 1.06
1566 | 326592 5E PRINCETON161.00 | LGEE' | RANGE | 0.94 | 1.06
1567 | 326593 2GREENVIL N 69.000 | LGEE' | RANGE | 0.94 | 1.06
1568 | 326594 2GREENVL 12 69.000 | LGEE' | RANGE | 0.94 | 1.06
1569 | 326596 2PAD PRI 61469.000 | LGEE' | RANGE | 0.94 | 1.06
1570 | 326970 2MILE LAN EK69.000 | LGEE' | RANGE | 0.94 | 1.06
1571 | 326973 2BRIDGPRT 1 69.000 | LGEE' | RANGE | 0.94 | 1.06
1572 | 326974 2BRIDGPRT 2 69.000 | LGEE' | RANGE | 0.94 | 1.06
1573 | 326975 5CEDAR GRV 161.00 | LGEE' | RANGE | 0.94 | 1.06
1574 | 326989 2LONG LICK 69.000 | LGEE' | RANGE | 0.94 | 1.06
1575 | 326998 5BULLITT TAP161.00 | LGEE' | RANGE | 0.94 | 1.06
ACCC Contingency Labels
Note 1: Contingency labels appended with '+T' have 'Tripping' solutions.
Note 2: Contingency labels appended with '+CA' have 'Corrective Action' solutions.
BASE CASE, SINGLE OPN LIN 1 339206-342769(1), SINGLE OPN LIN 2 339206-939132(1), SINGLE OPN LIN 3 341002-341443(1), SINGLE OPN LIN 4 341002-341752(1), SINGLE OPN LIN 5 341005-342181(1), SINGLE OPN LIN 6 341005-342283(1),
SINGLE OPN LIN 7 341005-342397(1), SINGLE OPN LIN 8 341008-342106(1), SINGLE OPN LIN 9 341008-342430(1), SINGLE OPN LIN 10 341014-341017(1), SINGLE OPN LIN 11 341017-341428(1), SINGLE OPN LIN 12 341017-342391(1), SINGLE OPN LIN 13 341020-341782(1),
SINGLE OPN LIN 14 341020-342538(1), SINGLE OPN LIN 15 341029-341032(1), SINGLE OPN LIN 16 341032-341379(1), SINGLE OPN LIN 17 341032-342472(1), SINGLE OPN LIN 18 341035-341038(1), SINGLE OPN LIN 19 341038-341755(1), SINGLE OPN LIN 20 341038-342187(1),
SINGLE OPN LIN 21 341041-341635(1), SINGLE OPN LIN 22 341041-341638(1), SINGLE OPN LIN 23 341041-342547(1), SINGLE OPN LIN 24 341044-341671(1), SINGLE OPN LIN 25 341044-342361(1), SINGLE OPN LIN 26 341047-342424(1), SINGLE OPN LIN 27 341050-342295(1),
SINGLE OPN LIN 28 341053-341056(1), SINGLE OPN LIN 29 341056-341407(1), SINGLE OPN LIN 30 341056-342424(1), SINGLE OPN LIN 31 341059-341275(1), SINGLE OPN LIN 32 341059-341542(1), SINGLE OPN LIN 33 341059-341651(1), SINGLE OPN LIN 34 341059-342694(1),
SINGLE OPN LIN 35 341062-341269(1), SINGLE OPN LIN 36 341065-341068(1), SINGLE OPN LIN 37 341068-341215(1), SINGLE OPN LIN 38 341068-342253(1), SINGLE OPN LIN 39 341071-341074(1), SINGLE OPN LIN 40 341071-341077(1), SINGLE OPN LIN 41 341071-342520(1),
SINGLE OPN LIN 42 341074-341992(1), SINGLE OPN LIN 43 341077-341173(1), SINGLE OPN LIN 44 341080-341149(1), SINGLE OPN LIN 45 341080-342445(1), SINGLE OPN LIN 46 341089-342500(1), SINGLE OPN LIN 47 341092-341095(1), SINGLE OPN LIN 48 341095-341164(1),
SINGLE OPN LIN 49 341095-341227(1), SINGLE OPN LIN 50 341098-342433(1), SINGLE OPN LIN 51 341104-341107(1), SINGLE OPN LIN 52 341107-341164(1), SINGLE OPN LIN 53 341107-341917(1), SINGLE OPN LIN 54 341110-341113(1), SINGLE OPN LIN 55 341110-341439(1),
SINGLE OPN LIN 56 341113-341464(1), SINGLE OPN LIN 57 341113-342001(1), SINGLE OPN LIN 58 341114-341115(1), SINGLE OPN LIN 59 341115-342223(1), SINGLE OPN LIN 60 341115-342346(1), SINGLE OPN LIN 61 341116-341119(1), SINGLE OPN LIN 62 341119-341620(1),
SINGLE OPN LIN 63 341119-342088(1), SINGLE OPN LIN 64 341122-341125(1), SINGLE OPN LIN 65 341122-341692(1), SINGLE OPN LIN 66 341122-341860(1), SINGLE OPN LIN 67 341131-341134(1), SINGLE OPN LIN 68 341131-341644(1), SINGLE OPN LIN 69 341131-342112(1),
SINGLE OPN LIN 70 341137-341296(1), SINGLE OPN LIN 71 341137-341935(1), SINGLE OPN LIN 72 341140-341143(1), SINGLE OPN LIN 73 341143-342019(1), SINGLE OPN LIN 74 341143-342508(1), SINGLE OPN LIN 75 341149-341272(1), SINGLE OPN LIN 76 341152-341155(1),
SINGLE OPN LIN 77 341155-341803(1), SINGLE OPN LIN 78 341155-341860(1), SINGLE OPN LIN 79 341158-341161(1), SINGLE OPN LIN 80 341158-341908(1), SINGLE OPN LIN 81 341161-342403(1), SINGLE OPN LIN 82 341164-341167(1), SINGLE OPN LIN 83 341164-342388(1),
SINGLE OPN LIN 84 341164-342466(1), SINGLE OPN LIN 85 341164-342559(1), SINGLE OPN LIN 86 341170-341173(1), SINGLE OPN LIN 87 341173-342196(1), SINGLE OPN LIN 88 341179-341746(1), SINGLE OPN LIN 89 341179-342514(1), SINGLE OPN LIN 90 341185-341614(1),
SINGLE OPN LIN 91 341185-342100(1), SINGLE OPN LIN 92 341188-341488(1), SINGLE OPN LIN 93 341188-341587(1), SINGLE OPN LIN 94 341194-342385(1), SINGLE OPN LIN 95 341194-342388(1), SINGLE OPN LIN 96 341197-341818(1), SINGLE OPN LIN 97 341197-342349(1),
SINGLE OPN LIN 98 341200-341920(1), SINGLE OPN LIN 99 341200-342010(1), SINGLE OPN LIN 100 341203-341206(1), SINGLE OPN LIN 101 341206-341347(1), SINGLE OPN LIN 102 341206-341392(1), SINGLE OPN LIN 103 341209-341210(1), SINGLE OPN LIN 104 341209-341617(1),
SINGLE OPN LIN 105 341209-342367(1), SINGLE OPN LIN 106 341212-341774(1), SINGLE OPN LIN 107 341212-342500(1), SINGLE OPN LIN 108 341215-341281(1), SINGLE OPN LIN 109 341215-341389(1), SINGLE OPN LIN 110 341215-342700(1), SINGLE OPN LIN 111 341218-341227(1),
SINGLE OPN LIN 112 341218-341605(1), SINGLE OPN LIN 113 341224-341227(1), SINGLE OPN LIN 114 341233-341974(1), SINGLE OPN LIN 115 341233-342286(1), SINGLE OPN LIN 116 341248-341608(1), SINGLE OPN LIN 117 341248-342520(1), SINGLE OPN LIN 118 341251-341254(1),
SINGLE OPN LIN 119 341254-341872(1), SINGLE OPN LIN 120 341254-342259(1), SINGLE OPN LIN 121 341260-342013(1), SINGLE OPN LIN 122 341263-341266(1), SINGLE OPN LIN 123 341266-342034(1), SINGLE OPN LIN 124 341266-342475(1), SINGLE OPN LIN 125 341269-342064(1),
SINGLE OPN LIN 126 341269-342703(1), SINGLE OPN LIN 127 341272-341275(1), SINGLE OPN LIN 128 341275-342241(1), SINGLE OPN LIN 129 341281-342082(1), SINGLE OPN LIN 130 341287-341713(1), SINGLE OPN LIN 131 341287-342307(1), SINGLE OPN LIN 132 341287-342568(1),
SINGLE OPN LIN 133 341293-341296(1), SINGLE OPN LIN 134 341296-342262(1), SINGLE OPN LIN 135 341299-341989(1), SINGLE OPN LIN 136 341299-342124(1), SINGLE OPN LIN 137 341302-341305(1), SINGLE OPN LIN 138 341305-341593(1), SINGLE OPN LIN 139 341305-341599(1),
SINGLE OPN LIN 140 341308-341314(1), SINGLE OPN LIN 141 341311-341314(1), SINGLE OPN LIN 142 341311-342184(1), SINGLE OPN LIN 143 341311-342406(1), SINGLE OPN LIN 144 341317-341390(1), SINGLE OPN LIN 145 341320-341512(1), SINGLE OPN LIN 146 341323-341335(1),
SINGLE OPN LIN 147 341323-341512(1), SINGLE OPN LIN 148 341323-342235(1), SINGLE OPN LIN 149 341326-341488(1), SINGLE OPN LIN 150 341326-342133(1), SINGLE OPN LIN 151 341329-341332(1), SINGLE OPN LIN 152 341332-341944(1), SINGLE OPN LIN 153 341332-342155(1),
SINGLE OPN LIN 154 341335-341370(1), SINGLE OPN LIN 155 341335-342436(1), SINGLE OPN LIN 156 341338-341341(1), SINGLE OPN LIN 157 341341-342346(1), SINGLE OPN LIN 158 341341-342349(1), SINGLE OPN LIN 159 341342-341343(1), SINGLE OPN LIN 160 341342-341761(1),
SINGLE OPN LIN 161 341342-342067(1), SINGLE OPN LIN 162 341344-341347(1), SINGLE OPN LIN 163 341344-342286(1), SINGLE OPN LIN 164 341344-342286(2), SINGLE OPN LIN 165 341344-342715(1), SINGLE OPN LIN 166 341350-342067(1), SINGLE OPN LIN 167 341353-341356(1),
SINGLE OPN LIN 168 341356-341653(1), SINGLE OPN LIN 169 341356-342265(1), SINGLE OPN LIN 170 341359-341362(1), SINGLE OPN LIN 171 341359-342288(1), SINGLE OPN LIN 172 341362-341406(1), SINGLE OPN LIN 173 341362-341611(1), SINGLE OPN LIN 174 341366-341370(1),
SINGLE OPN LIN 175 341377-341602(1), SINGLE OPN LIN 176 341377-342355(1), SINGLE OPN LIN 177 341379-342256(1), SINGLE OPN LIN 178 341380-341959(1), SINGLE OPN LIN 179 341380-341962(1), SINGLE OPN LIN 180 341380-342574(1), SINGLE OPN LIN 181 341381-341382(1),
SINGLE OPN LIN 182 341382-341734(1), SINGLE OPN LIN 183 341382-342451(1), SINGLE OPN LIN 184 341383-341467(1), SINGLE OPN LIN 185 341383-341965(1), SINGLE OPN LIN 186 341386-341389(1), SINGLE OPN LIN 187 341389-341707(1), SINGLE OPN LIN 188 341390-341391(1),
SINGLE OPN LIN 189 341390-341950(1), SINGLE OPN LIN 190 341392-341578(1), SINGLE OPN LIN 191 341392-342499(1), SINGLE OPN LIN 192 341392-342727(1), SINGLE OPN LIN 193 341394-341479(1), SINGLE OPN LIN 194 341394-342151(1), SINGLE OPN LIN 195 341394-342157(1),
SINGLE OPN LIN 196 341394-342274(1), SINGLE OPN LIN 197 341398-341605(1), SINGLE OPN LIN 198 341398-341880(1), SINGLE OPN LIN 199 341400-342091(1), SINGLE OPN LIN 200 341401-341842(1), SINGLE OPN LIN 201 341404-341842(1), SINGLE OPN LIN 202 341404-342295(1),
SINGLE OPN LIN 203 341404-342388(1), SINGLE OPN LIN 204 341405-341406(1), SINGLE OPN LIN 205 341407-342019(1), SINGLE OPN LIN 206 341410-341929(1), SINGLE OPN LIN 207 341416-342076(1), SINGLE OPN LIN 208 341419-341422(1), SINGLE OPN LIN 209 341419-341941(1),
SINGLE OPN LIN 210 341419-341974(1), SINGLE OPN LIN 211 341425-341428(1), SINGLE OPN LIN 212 341428-341809(1), SINGLE OPN LIN 213 341431-341434(1), SINGLE OPN LIN 214 341431-341728(1), SINGLE OPN LIN 215 341431-342322(1), SINGLE OPN LIN 216 341434-341437(1),
SINGLE OPN LIN 217 341434-341680(1), SINGLE OPN LIN 218 341443-341446(1), SINGLE OPN LIN 219 341443-341953(1), SINGLE OPN LIN 220 341449-342163(1), SINGLE OPN LIN 221 341455-341458(1), SINGLE OPN LIN 222 341455-342274(1), SINGLE OPN LIN 223 341455-342379(1),
SINGLE OPN LIN 224 341458-342340(1), SINGLE OPN LIN 225 341461-341797(1), SINGLE OPN LIN 226 341461-342310(1), SINGLE OPN LIN 227 341464-341569(1), SINGLE OPN LIN 228 341464-342391(1), SINGLE OPN LIN 229 341464-342730(1), SINGLE OPN LIN 230 341467-342580(1),
SINGLE OPN LIN 231 341470-341473(1), SINGLE OPN LIN 232 341470-342511(1), SINGLE OPN LIN 233 341473-342115(1), SINGLE OPN LIN 234 341473-342193(1), SINGLE OPN LIN 235 341476-341899(1), SINGLE OPN LIN 236 341476-342130(1), SINGLE OPN LIN 237 341485-341488(1),
SINGLE OPN LIN 238 341485-341550(1), SINGLE OPN LIN 239 341491-341548(1), SINGLE OPN LIN 240 341491-342037(1), SINGLE OPN LIN 241 341491-342043(1), SINGLE OPN LIN 242 341491-342049(1), SINGLE OPN LIN 243 341491-342732(1), SINGLE OPN LIN 244 341494-341497(1),
SINGLE OPN LIN 245 341494-341935(1), SINGLE OPN LIN 246 341494-342508(1), SINGLE OPN LIN 247 341500-341644(1), SINGLE OPN LIN 248 341500-341824(1), SINGLE OPN LIN 249 341503-341506(1), SINGLE OPN LIN 250 341503-341578(1), SINGLE OPN LIN 251 341503-341887(1),
SINGLE OPN LIN 252 341509-341512(1), SINGLE OPN LIN 253 341515-341732(1), SINGLE OPN LIN 254 341515-942410(1), SINGLE OPN LIN 255 341518-341521(1), SINGLE OPN LIN 256 341521-341806(1), SINGLE OPN LIN 257 341530-342043(1), SINGLE OPN LIN 258 341530-342445(1),
SINGLE OPN LIN 259 341533-341632(1), SINGLE OPN LIN 260 341533-342307(1), SINGLE OPN LIN 261 341536-341623(1), SINGLE OPN LIN 262 341536-341989(1), SINGLE OPN LIN 263 341536-342088(1), SINGLE OPN LIN 264 341536-342589(1), SINGLE OPN LIN 265 341539-341686(1),
SINGLE OPN LIN 266 341542-341548(1), SINGLE OPN LIN 267 341551-341587(1), SINGLE OPN LIN 268 341551-342298(1), SINGLE OPN LIN 269 341554-341752(1), SINGLE OPN LIN 270 341554-342034(1), SINGLE OPN LIN 271 341563-341575(1), SINGLE OPN LIN 272 341563-342325(1),
SINGLE OPN LIN 273 341563-342733(1), SINGLE OPN LIN 274 341569-341572(1), SINGLE OPN LIN 275 341569-341806(1), SINGLE OPN LIN 276 341575-341854(1), SINGLE OPN LIN 277 341578-341581(1), SINGLE OPN LIN 278 341584-341587(1), SINGLE OPN LIN 279 341590-341593(1),
SINGLE OPN LIN 280 341593-342301(1), SINGLE OPN LIN 281 341596-341599(1), SINGLE OPN LIN 282 341599-342370(1), SINGLE OPN LIN 283 341602-341872(1), SINGLE OPN LIN 284 341602-342280(1), SINGLE OPN LIN 285 341605-342595(1), SINGLE OPN LIN 286 341608-342313(1),
SINGLE OPN LIN 287 341611-342103(1), SINGLE OPN LIN 288 341614-342520(1), SINGLE OPN LIN 289 341617-341896(1), SINGLE OPN LIN 290 341620-342163(1), SINGLE OPN LIN 291 341623-342052(1), SINGLE OPN LIN 292 341632-341800(1), SINGLE OPN LIN 293 341632-342316(1),
SINGLE OPN LIN 294 341638-342199(1), SINGLE OPN LIN 295 341638-342463(1), SINGLE OPN LIN 296 341641-341887(1), SINGLE OPN LIN 297 341644-341683(1), SINGLE OPN LIN 298 341647-341650(1), SINGLE OPN LIN 299 341650-341651(Z1), SINGLE OPN LIN 300 341651-341914(1),
SINGLE OPN LIN 301 341653-341656(1), SINGLE OPN LIN 302 341653-341890(1), SINGLE OPN LIN 303 341659-341662(1), SINGLE OPN LIN 304 341662-341671(1), SINGLE OPN LIN 305 341662-341857(1), SINGLE OPN LIN 306 341665-341701(1), SINGLE OPN LIN 307 341665-341869(1),
SINGLE OPN LIN 308 341665-342596(1), SINGLE OPN LIN 309 341671-342061(1), SINGLE OPN LIN 310 341677-341890(1), SINGLE OPN LIN 311 341683-342100(1), SINGLE OPN LIN 312 341686-341689(1), SINGLE OPN LIN 313 341686-342076(1), SINGLE OPN LIN 314 341692-341695(1),
SINGLE OPN LIN 315 341692-342343(1), SINGLE OPN LIN 316 341701-342370(1), SINGLE OPN LIN 317 341704-341707(1), SINGLE OPN LIN 318 341707-342427(1), SINGLE OPN LIN 319 341716-341722(1), SINGLE OPN LIN 320 341719-341740(1), SINGLE OPN LIN 321 341719-342073(1),
SINGLE OPN LIN 322 341722-341740(1), SINGLE OPN LIN 323 341722-342187(1), SINGLE OPN LIN 324 341725-342007(1), SINGLE OPN LIN 325 341725-342058(1), SINGLE OPN LIN 326 341728-341854(1), SINGLE OPN LIN 327 341731-341732(1), SINGLE OPN LIN 328 341732-341959(1),
SINGLE OPN LIN 329 341734-341737(1), SINGLE OPN LIN 330 341734-341929(1), SINGLE OPN LIN 331 341740-342754(1), SINGLE OPN LIN 332 341746-342253(1), SINGLE OPN LIN 333 341749-342058(1), SINGLE OPN LIN 334 341749-342133(1), SINGLE OPN LIN 335 341755-341758(1),
SINGLE OPN LIN 336 341761-341767(1), SINGLE OPN LIN 337 341761-341896(1), SINGLE OPN LIN 338 341761-342760(1), SINGLE OPN LIN 339 341764-341767(1), SINGLE OPN LIN 340 341767-342064(1), SINGLE OPN LIN 341 341772-341774(1), SINGLE OPN LIN 342 341774-341775(1),
SINGLE OPN LIN 343 341775-342247(1), SINGLE OPN LIN 344 341776-342208(1), SINGLE OPN LIN 345 341776-342316(1), SINGLE OPN LIN 346 341779-341782(1), SINGLE OPN LIN 347 341782-342475(1), SINGLE OPN LIN 348 341785-341788(1), SINGLE OPN LIN 349 341788-342155(1),
SINGLE OPN LIN 350 341788-342379(1), SINGLE OPN LIN 351 341791-341794(1), SINGLE OPN LIN 352 341794-341935(1), SINGLE OPN LIN 353 341794-342061(1), SINGLE OPN LIN 354 341797-342265(1), SINGLE OPN LIN 355 341800-342325(1), SINGLE OPN LIN 356 341803-342310(1),
SINGLE OPN LIN 357 341803-342313(1), SINGLE OPN LIN 358 341809-341812(1), SINGLE OPN LIN 359 341809-341929(1), SINGLE OPN LIN 360 341815-341818(1), SINGLE OPN LIN 361 341818-342472(1), SINGLE OPN LIN 362 341821-341824(1), SINGLE OPN LIN 363 341824-341833(1),
SINGLE OPN LIN 364 341827-342343(1), SINGLE OPN LIN 365 341830-341833(1), SINGLE OPN LIN 366 341833-341890(1), SINGLE OPN LIN 367 341836-341953(1), SINGLE OPN LIN 368 341836-342265(1), SINGLE OPN LIN 369 341839-341842(1), SINGLE OPN LIN 370 341845-342139(1),
SINGLE OPN LIN 371 341845-342490(1), SINGLE OPN LIN 372 341845-342778(1), SINGLE OPN LIN 373 341848-342223(1), SINGLE OPN LIN 374 341848-342391(1), SINGLE OPN LIN 375 341851-341854(1), SINGLE OPN LIN 376 341857-342406(1), SINGLE OPN LIN 377 341860-341863(1),
SINGLE OPN LIN 378 341869-341875(1), SINGLE OPN LIN 379 341869-342259(1), SINGLE OPN LIN 380 341872-341878(1), SINGLE OPN LIN 381 341887-342268(1), SINGLE OPN LIN 382 341893-341896(1), SINGLE OPN LIN 383 341908-341914(1), SINGLE OPN LIN 384 341911-341914(1),
SINGLE OPN LIN 385 341917-341998(1), SINGLE OPN LIN 386 341920-341998(1), SINGLE OPN LIN 387 341920-342502(1), SINGLE OPN LIN 388 341923-342091(1), SINGLE OPN LIN 389 341923-342280(1), SINGLE OPN LIN 390 341935-342208(1), SINGLE OPN LIN 391 341938-342505(1),
SINGLE OPN LIN 392 341938-342526(1), SINGLE OPN LIN 393 341941-341947(1), SINGLE OPN LIN 394 341941-341971(1), SINGLE OPN LIN 395 341944-342424(1), SINGLE OPN LIN 396 341944-342514(1), SINGLE OPN LIN 397 341950-342007(1), SINGLE OPN LIN 398 341953-342229(1),
SINGLE OPN LIN 399 341962-342361(1), SINGLE OPN LIN 400 341965-342199(1), SINGLE OPN LIN 401 341971-342115(1), SINGLE OPN LIN 402 341974-342256(1), SINGLE OPN LIN 403 341977-341983(1), SINGLE OPN LIN 404 341980-341983(1), SINGLE OPN LIN 405 341980-342286(1),
SINGLE OPN LIN 406 341983-342469(1), SINGLE OPN LIN 407 341986-341989(1), SINGLE OPN LIN 408 342000-342703(1), SINGLE OPN LIN 409 342000-342760(1), SINGLE OPN LIN 410 342007-342008(1), SINGLE OPN LIN 411 342007-342010(1), SINGLE OPN LIN 412 342007-342013(1),
SINGLE OPN LIN 413 342016-342019(1), SINGLE OPN LIN 414 342022-342025(1), SINGLE OPN LIN 415 342022-342052(1), SINGLE OPN LIN 416 342022-342112(1), SINGLE OPN LIN 417 342031-342034(1), SINGLE OPN LIN 418 342037-342040(1), SINGLE OPN LIN 419 342049-342161(1),
SINGLE OPN LIN 420 342049-342319(1), SINGLE OPN LIN 421 342067-342505(1), SINGLE OPN LIN 422 342070-342073(1), SINGLE OPN LIN 423 342073-342451(1), SINGLE OPN LIN 424 342076-342139(1), SINGLE OPN LIN 425 342085-342088(1), SINGLE OPN LIN 426 342091-342124(1),
SINGLE OPN LIN 427 342091-342634(1), SINGLE OPN LIN 428 342097-342184(1), SINGLE OPN LIN 429 342100-342301(1), SINGLE OPN LIN 430 342100-342637(1), SINGLE OPN LIN 431 342103-342106(1), SINGLE OPN LIN 432 342109-342112(1), SINGLE OPN LIN 433 342115-342787(1),
SINGLE OPN LIN 434 342118-342121(1), SINGLE OPN LIN 435 342121-342328(1), SINGLE OPN LIN 436 342121-342415(1), SINGLE OPN LIN 437 342127-342265(1), SINGLE OPN LIN 438 342127-342421(1), SINGLE OPN LIN 439 342130-342259(1), SINGLE OPN LIN 440 342133-342355(1),
SINGLE OPN LIN 441 342133-342640(1), SINGLE OPN LIN 442 342136-342139(1), SINGLE OPN LIN 443 342145-342487(1), SINGLE OPN LIN 444 342154-342155(1), SINGLE OPN LIN 445 342157-342418(1), SINGLE OPN LIN 446 342160-342161(1), SINGLE OPN LIN 447 342161-342334(1),
SINGLE OPN LIN 448 342163-342649(1), SINGLE OPN LIN 449 342166-342169(1), SINGLE OPN LIN 450 342166-342172(1), SINGLE OPN LIN 451 342166-342235(1), SINGLE OPN LIN 452 342169-342175(1), SINGLE OPN LIN 453 342169-342178(1), SINGLE OPN LIN 454 342178-342232(1),
SINGLE OPN LIN 455 342178-342793(1), SINGLE OPN LIN 456 342184-342262(1), SINGLE OPN LIN 457 342186-342424(1), SINGLE OPN LIN 458 342186-342427(1), SINGLE OPN LIN 459 342196-342391(1), SINGLE OPN LIN 460 342199-342202(1), SINGLE OPN LIN 461 342208-342211(1),
SINGLE OPN LIN 462 342214-342217(1), SINGLE OPN LIN 463 342217-342481(1), SINGLE OPN LIN 464 342217-342505(1), SINGLE OPN LIN 465 342220-342223(1), SINGLE OPN LIN 466 342235-342481(1), SINGLE OPN LIN 467 342238-342241(1), SINGLE OPN LIN 468 342247-342248(1),
SINGLE OPN LIN 469 342247-342410(1), SINGLE OPN LIN 470 342247-342808(1), SINGLE OPN LIN 471 342250-342253(1), SINGLE OPN LIN 472 342265-342658(1), SINGLE OPN LIN 473 342268-342478(1), SINGLE OPN LIN 474 342271-342274(1), SINGLE OPN LIN 475 342277-342283(1),
SINGLE OPN LIN 476 342283-342322(1), SINGLE OPN LIN 477 342286-342287(1), SINGLE OPN LIN 478 342292-342295(1), SINGLE OPN LIN 479 342292-342298(1), SINGLE OPN LIN 480 342292-342667(1), SINGLE OPN LIN 481 342307-342403(1), SINGLE OPN LIN 482 342307-342412(1),
SINGLE OPN LIN 483 342319-342322(1), SINGLE OPN LIN 484 342319-342334(1), SINGLE OPN LIN 485 342322-342436(1), SINGLE OPN LIN 486 342322-342814(1), SINGLE OPN LIN 487 342337-342340(1), SINGLE OPN LIN 488 342343-342421(1), SINGLE OPN LIN 489 342349-342433(1),
SINGLE OPN LIN 490 342352-342355(1), SINGLE OPN LIN 491 342358-342361(1), SINGLE OPN LIN 492 342364-342367(1), SINGLE OPN LIN 493 342367-942410(1), SINGLE OPN LIN 494 342379-342382(1), SINGLE OPN LIN 495 342385-342487(1), SINGLE OPN LIN 496 342391-342820(1),
SINGLE OPN LIN 497 342394-342397(1), SINGLE OPN LIN 498 342397-342532(1), SINGLE OPN LIN 499 342400-342403(1), SINGLE OPN LIN 500 342415-342418(1), SINGLE OPN LIN 501 342430-342433(1), SINGLE OPN LIN 502 342430-342691(1), SINGLE OPN LIN 503 342436-342439(1),
SINGLE OPN LIN 504 342442-342445(1), SINGLE OPN LIN 505 342460-342463(1), SINGLE OPN LIN 506 342469-342526(1), SINGLE OPN LIN 507 342472-342511(1), SINGLE OPN LIN 508 342478-342532(1), SINGLE OPN LIN 509 342478-342535(1), SINGLE OPN LIN 510 342478-342823(1),
SINGLE OPN LIN 511 342481-342484(1), SINGLE OPN LIN 512 342490-342493(1), SINGLE OPN LIN 513 342490-342499(1), SINGLE OPN LIN 514 342496-342499(1), SINGLE OPN LIN 515 342523-342526(1), SINGLE OPN LIN 516 342529-342535(1), SINGLE OPN LIN 517 342538-342616(1),
SINGLE OPN LIN 518 342541-342544(1), SINGLE OPN LIN 519 342541-342556(1), SINGLE OPN LIN 520 342541-342580(1), SINGLE OPN LIN 521 342541-342631(1), SINGLE OPN LIN 522 342541-342829(1), SINGLE OPN LIN 523 342550-342559(1), SINGLE OPN LIN 524 342550-342640(1),
SINGLE OPN LIN 525 342553-342556(1), SINGLE OPN LIN 526 342556-342565(1), SINGLE OPN LIN 527 342559-342646(1), SINGLE OPN LIN 528 342559-342673(1), SINGLE OPN LIN 529 342565-342574(1), SINGLE OPN LIN 530 342571-342589(1), SINGLE OPN LIN 531 342571-342649(1),
SINGLE OPN LIN 532 342574-342596(1), SINGLE OPN LIN 533 342574-342676(1), SINGLE OPN LIN 534 342577-342607(1), SINGLE OPN LIN 535 342577-342676(1), SINGLE OPN LIN 536 342577-342691(1), SINGLE OPN LIN 537 342583-342589(1), SINGLE OPN LIN 538 342583-342664(1),
SINGLE OPN LIN 539 342586-342587(1), SINGLE OPN LIN 540 342586-342673(1), SINGLE OPN LIN 541 342589-342634(1), SINGLE OPN LIN 542 342596-342607(1), SINGLE OPN LIN 543 342598-342664(1), SINGLE OPN LIN 544 342601-342604(1), SINGLE OPN LIN 545 342604-342631(1),
SINGLE OPN LIN 546 342604-342640(1), SINGLE OPN LIN 547 342607-342610(1), SINGLE OPN LIN 548 342607-342613(1), SINGLE OPN LIN 549 342607-342637(1), SINGLE OPN LIN 550 342607-342688(1), SINGLE OPN LIN 551 342610-342832(1), SINGLE OPN LIN 552 342613-342832(1),
SINGLE OPN LIN 553 342622-342625(1), SINGLE OPN LIN 554 342622-342634(1), SINGLE OPN LIN 555 342622-342664(1), SINGLE OPN LIN 556 342637-342784(1), SINGLE OPN LIN 557 342640-342664(1), SINGLE OPN LIN 558 342643-342646(1), SINGLE OPN LIN 559 342646-342667(1),
SINGLE OPN LIN 560 342649-342658(1), SINGLE OPN LIN 561 342661-342664(1), SINGLE OPN LIN 562 342664-342667(1), SINGLE OPN LIN 563 342664-342838(1), SINGLE OPN LIN 564 342664-342838(2), SINGLE OPN LIN 565 342664-342838(3), SINGLE OPN LIN 566 342670-342673(1),
SINGLE OPN LIN 567 342676-342679(1), SINGLE OPN LIN 568 342685-342688(1), SINGLE OPN LIN 569 342694-342814(1), SINGLE OPN LIN 570 342697-342780(1), SINGLE OPN LIN 571 342700-342819(1), SINGLE OPN LIN 572 342703-342769(1), SINGLE OPN LIN 573 342715-342718(1),
SINGLE OPN LIN 574 342715-342790(1), SINGLE OPN LIN 575 342715-342799(1), SINGLE OPN LIN 576 342718-342727(1), SINGLE OPN LIN 577 342718-342757(1), SINGLE OPN LIN 578 342721-342724(1), SINGLE OPN LIN 579 342724-342766(1), SINGLE OPN LIN 580 342724-342808(1),
SINGLE OPN LIN 581 342730-342820(1), SINGLE OPN LIN 582 342733-342814(1), SINGLE OPN LIN 583 342733-342817(1), SINGLE OPN LIN 584 342736-342739(1), SINGLE OPN LIN 585 342736-342820(1), SINGLE OPN LIN 586 342742-342745(1), SINGLE OPN LIN 587 342745-342751(1),
SINGLE OPN LIN 588 342745-342799(1), SINGLE OPN LIN 589 342748-342751(1), SINGLE OPN LIN 590 342751-342796(1), SINGLE OPN LIN 591 342754-342757(1), SINGLE OPN LIN 592 342754-342781(1), SINGLE OPN LIN 593 342760-342790(1), SINGLE OPN LIN 594 342763-342766(1),
SINGLE OPN LIN 595 342766-342819(1), SINGLE OPN LIN 596 342769-342770(1), SINGLE OPN LIN 597 342769-342775(1), SINGLE OPN LIN 598 342772-342797(1), SINGLE OPN LIN 599 342775-342797(1), SINGLE OPN LIN 600 342775-342805(1), SINGLE OPN LIN 601 342779-342780(1),
SINGLE OPN LIN 602 342780-342784(1), SINGLE OPN LIN 603 342781-342820(1), SINGLE OPN LIN 604 342787-342790(1), SINGLE OPN LIN 605 342793-342796(1), SINGLE OPN LIN 606 342797-342798(1), SINGLE OPN LIN 607 342802-342805(1), SINGLE OPN LIN 608 342805-342817(1),
SINGLE OPN LIN 609 342818-342819(1), SINGLE OPN LIN 610 342829-342835(1), SINGLE OPN LIN 611 342832-342835(1), SINGLE OPN LIN 612 342832-342841(1), SINGLE OPN LIN 613 342835-342838(1), SINGLE OPN LIN 614 942410-942411(1), SINGLE OPN LIN 615 942411-942412(1),
SINGLE OPN TIE 616 341020-243725(1), SINGLE OPN TIE 617 341071-324430(1), SINGLE OPN TIE 618 341089-325102(1), SINGLE OPN TIE 619 341161-324213(1), SINGLE OPN TIE 620 341188-324463(1), SINGLE OPN TIE 621 341188-324722(1), SINGLE OPN TIE 622 341317-324474(1),
SINGLE OPN TIE 623 341320-324830(1), SINGLE OPN TIE 624 341406-324530(1), SINGLE OPN TIE 625 341407-324425(1), SINGLE OPN TIE 626 341461-243721(Z1), SINGLE OPN TIE 627 341515-324600(1), SINGLE OPN TIE 628 341539-324784(1), SINGLE OPN TIE 629 341554-243726(1),
SINGLE OPN TIE 630 341563-324554(1), SINGLE OPN TIE 631 341605-251579(1), SINGLE OPN TIE 632 341608-243812(Z1), SINGLE OPN TIE 633 341632-324575(1), SINGLE OPN TIE 634 341632-324660(1), SINGLE OPN TIE 635 341713-324519(1), SINGLE OPN TIE 636 341740-324576(1),
SINGLE OPN TIE 637 341752-243737(Z1), SINGLE OPN TIE 638 341755-324527(1), SINGLE OPN TIE 639 341890-246973(Z1), SINGLE OPN TIE 640 341923-324717(1), SINGLE OPN TIE 641 341923-325019(1), SINGLE OPN TIE 642 341929-324662(1), SINGLE OPN TIE 643 341935-324736(1),
SINGLE OPN TIE 644 341944-324288(1), SINGLE OPN TIE 645 342007-324455(1), SINGLE OPN TIE 646 342008-324290(1), SINGLE OPN TIE 647 342055-243742(1), SINGLE OPN TIE 648 342058-324951(1), SINGLE OPN TIE 649 342133-324492(1), SINGLE OPN TIE 650 342157-324708(1),
SINGLE OPN TIE 651 342184-324445(1), SINGLE OPN TIE 652 342184-324445(2), SINGLE OPN TIE 653 342218-247897(Z1), SINGLE OPN TIE 654 342232-324787(1), SINGLE OPN TIE 655 342248-324718(1), SINGLE OPN TIE 656 342287-324531(1), SINGLE OPN TIE 657 342287-324737(1),
SINGLE OPN TIE 658 342307-324509(1), SINGLE OPN TIE 659 342340-324519(1), SINGLE OPN TIE 660 342343-246971(1), SINGLE OPN TIE 661 342454-251315(1), SINGLE OPN TIE 662 342487-250148(1), SINGLE OPN TIE 663 342538-243688(1), SINGLE OPN TIE 664 342544-324275(1),
SINGLE OPN TIE 665 342547-324210(1), SINGLE OPN TIE 666 342559-250054(1), SINGLE OPN TIE 667 342565-325925(1), SINGLE OPN TIE 668 342568-324047(1), SINGLE OPN TIE 669 342568-324261(1), SINGLE OPN TIE 670 342577-324247(1), SINGLE OPN TIE 671 342577-324248(1),
SINGLE OPN TIE 672 342586-324253(1), SINGLE OPN TIE 673 342595-250152(1), SINGLE OPN TIE 674 342607-342918(1), SINGLE OPN TIE 675 342607-342921(1), SINGLE OPN TIE 676 342607-342924(1), SINGLE OPN TIE 677 342607-342927(1), SINGLE OPN TIE 678 342607-342930(1),
SINGLE OPN TIE 679 342607-342933(1), SINGLE OPN TIE 680 342607-342936(1), SINGLE OPN TIE 681 342616-342948(1), SINGLE OPN TIE 682 342631-324328(1), SINGLE OPN TIE 683 342649-324302(1), SINGLE OPN TIE 684 342661-324267(1), SINGLE OPN TIE 685 342664-342957(1),
SINGLE OPN TIE 686 342688-324276(1), SINGLE OPN TIE 687 342697-324138(1), SINGLE OPN TIE 688 342697-324430(1), SINGLE OPN TIE 689 342700-326975(1), SINGLE OPN TIE 690 342700-326998(1), SINGLE OPN TIE 691 342718-324141(1), SINGLE OPN TIE 692 342732-361603(1),
SINGLE OPN TIE 693 342736-324138(1), SINGLE OPN TIE 694 342757-342945(1), SINGLE OPN TIE 695 342770-324271(1), SINGLE OPN TIE 696 342778-360473(1), SINGLE OPN TIE 697 342778-360486(1), SINGLE OPN TIE 698 342778-361579(1), SINGLE OPN TIE 699 342781-324688(1),
SINGLE OPN TIE 700 342796-360448(1), SINGLE OPN TIE 701 342814-360334(1), SINGLE OPN TIE 702 342814-361788(1), SINGLE OPN TIE 703 342817-325921(1), SINGLE OPN TIE 704 342823-360486(1), SINGLE OPN TIE 705 342832-342939-342942(1), SINGLE OPN TIE 706 342838-249581(1),
SINGLE OPN TIE 707 342838-253077(1), SINGLE OPN TIE 708 342838-342960(1), SINGLE OPN TIE 709 342838-342963(1), SINGLE OPN TIE 710 342838-342966(1), SINGLE OPN TIE 711 342841-325074(Z1), SINGLE OPN TIE 712 342844-384157(1), SINGLE OPN TIE 713 342847-243205(1),
BARREN CO - HORSECAVE 69 SS, CAVE CITY J-SEYMOUR T 69 SS, CAVE CITY - CAVE CITY JCT 69 SS, FOX HOLLOW - PARKWAY1 69 SS, WAYNE CO - ZULA TAP 69 SS, KU GARRARD T-MANCHESTER 69 SS, GREEN BRIAR T-MANCHESTER 69 SS,
FALL ROCK-GREEN BRIAR T 69 SS, BIG CREEK - BIG CREEK TAP 69 SS, FALL ROCK - BIG CREEK TAP 69 SS, BIG CREEK - ELK MT 69 SS, CLAY LICK JCT - S ANDERSON 69 SS, CLAY LICK J-CLAY LICK SW 69 SS, OWEN CO - OWEN CO JCT 2 69 SS,
OWEN CO JCT 1 - BROMLEY EK 69 SS, BROMLEY EK - MUNK JCT 69 SS, MUNK JCT - WILLIAMSTOWN 69 SS, RENAKER - THREE M 69 SS, KU W FRANKFORT BRDGPT1 69 SS, BRIDGEPORT J-BRDGPT2 69 SS, STANLEY PARKER - BANK LICK 69 SS,
BEATTYVILLE-BEATTYVLLE D SS, BEATTYVILLE DIST - OAKDALE 69 SS, SHELBY CO BUS SS, EKPC_P1-2_OWEN-PENN69, EKPC_P1-2_PENN-RENAKER69, EKPC_P1-2_BOONE-HEBRON69, EKPC_P1-2_BOON-OWN-REN69,
EKPC_P1-2_T FTJ-WEB RD69, EKPC_P1-2_TFTJ- ST PRK69, EKPC_P1-2_ST PRK-BRAK 69, EKPC_P1-2_OWN-CARSON 69, EKPC_P1-2_OWN-CLY VILL69, EKPC_P1-2_BRAK- REN 69, EKPC_P1-2_BRAK- KU KEN69,
EKPC_P1-2_PLUM-GODDARD69, EKPC_P1-2_MURPH - HQ 69, EKPC_P1-2_MURPH-MILLBG69, EKPC_P1-2_MURPH-KU KEN69, EKPC_P1-2_ARGEN - LEON69, EKPC_P1-2_LEON-SKAGGS 69, EKPC_P1-2_FIN-SHL-SHBV69,
EKPC_P1-2_SHL-BUD-BKRT69, EKPC_P1-2_REN - HQ 69, EKPC_P1-2_GODD - HOPE 69, EKPC_P1-2_GODD - ROW 69, EKPC_P1-2_BULL-W BARDJ69, EKPC_P1-2_BULL - NELS 69, EKPC_P1-2_N SPR -S AND69,
EKPC_P1-2_HNTFMJ-S AND69, EKPC_P1-2_BKR LN-FAY 69, EKPC_P1-2_HQ-HUNT 69, EKPC_P1-2_HUNT-POWELL 69, EKPC_P1-2_DALE-HTFRMJ69, EKPC_P1-2_DALE-GARRD 69, EKPC_P1-2_HOPE - POW 69,
EKPC_P1-2_HOPE - MORG 69, EKPC_P1-2_MORG-SKAGGS69, EKPC_P1-2_SKAGGS-FALC69, EKPC_P1-2_SKAGGS-THELM69, EKPC_P1-2_C HAR-KU ETN69, EKPC_P1-2_STEPH-HODG 69, EKPC_P1-2_STEPH-BONN 69,
EKPC_P1-2_ETOWN-KU ETN69, EKPC_P1-2_ETWN-ROG-RAD69, EKPC_P1-2_ETOWN-NELSN 69, EKPC_P1-2_W BARDJ-EBRD69, EKPC_P1-2_HODG-GREEN 69, EKPC_P1-2_HODG-N SPR 69, EKPC_P1-2_E BARD-N SPR69,
EKPC_P1-2_E BRD-KU BRD69, EKPC_P1-2_HNTFMJ-N SPR69, EKPC_P1-2_W BER-THRLJ 69, EKPC_P1-2_W BER-KU FAW69, EKPC_P1-2_POW - ZACH 69, EKPC_P1-2_ZACH-HELECH69, EKPC_P1-2_BETYV - OAK 69,
EKPC_P1-2_BETYV - TYN 69, EKPC_P1-2_HELECH-MAG 69, EKPC_P1-2_FALC - MAG 69, EKPC_P1-2_MAG - THELM 69, EKPC_P1-2_BONN - BARR 69, EKPC_P1-2_GREEN-SUM SH69, EKPC_P1-2_CASEY-LIB J69,
EKPC_P1-2_LIB J-GARR69, EKPC_P1-2_LIB J-WIND 69, EKPC_P1-2_PUL-WAL-SSET69, EKPC_P1-2_PUL - WOODSTOCK 69, EKPC_P1-2_THREELJ- WAL69, EKPC_P1-2_TYN - N LON 69, EKPC_P1-2_FALL R-GARR69,
EKPC_P1-2_FALL R-GOOS 69, EKPC_P1-2_BARR- FOX H 69, EKPC_P1-2_FOX H-SUMMSH69, EKPC_P1-2_SUMMSH-SEWJ 69, EKPC_P1-2_SUMMSH-WAYNE69, EKPC_P1-2_WAYNE-ZULA 69, EKPC_P1-2_SEWJ - RUSS 69,
EKPC_P1-2_SEWJ - WIND 69, EKPC_P1-2_RUSS-KU SSET69, EKPC_P1-2_WIND - SSET 69, EKPC_P1-2_SSET-KU ELI 69, EKPC_P1-2_COOP-DENNY 69, EKPC_P1-2_LAUR-KU FAR69, EKPC_P1-2_LAUR-KU SWTH69,
EKPC_P1-2_WAYNE-DENNY69, EKPC_P1-2_DENNY-MCCRRY69, EKPC_P1-2_MCCRY-KUWOFF69, EKPC_P1-2_CLYV-SHL-FRK69, EKPC_P1-2_BULL- PLENTG69, EKPC_P1-2_AEPMORG- MOR69, EKPC_P1-2_AEPMORG-INDX69,
EKPC_P1-2_HODG-KU BARD69, EKPC_P1-2_HODG-KU ETWN69, EKPC_P1-2_N SPR-KU LEB69, EKPC_P1-2_BAR-BON-FHOL69, EKPC_P1-2_FHOL-PARK69, EKPC_P1-2_GREEN-KUTAY69, EKPC_P1-2_NLON-KU NLON69,
EKPC_P1-2_DK HEB-HEB 138, EKPC_P1-2_BOONE-BUFF138, EKPC_P1-2_BOONE-STANP138, EKPC_P1-2_BOONE-GALL138, EKPC_P1-2_BOONE-REN 138, EKPC_P1-2_OWEN 138/69, EKPC_P1-2_SPUR-KUKEN 138,
EKPC_P1-2_SPUR-PLUM 138, EKPC_P1-2_SPUR-GODD 138, EKPC_P1-2_GODD - ROW138, EKPC_P1-2_AVN-PAR-REN138, EKPC_P1-2_AVN-BBN-DLE138, EKPC_P1-2_AVON-FAY 138, EKPC_P1-2_AVON-LOUD 138,
EKPC_P1-2_DALE-JKSMIT138, EKPC_P1-2_DALE-FAWK 138, EKPC_P1-2_FAW-W BER 138, EKPC_P1-2_JKS 345/138 1, EKPC_P1-2_JKS 345/138 2, EKPC_P1-2_JKSMTH-REBA138, EKPC_P1-2_ROW-SKAG138,
EKPC_P1-2_CHARD-HRDBG138, EKPC_P1-2_COP-RUS-WLF161, EKPC_P1-2_COOP-DEN161, EKPC_P1-2_COP-LIBJ-PU161, EKPC_P1-2_LIB-CAS-GAS-MAR161, EKPC_P1-2_MCCR-WAYNE161, EKPC_P1-2_LAUR-PIT-TY161,
EKPC_P1-2_TYN-DELV161, EKPC_P1-2_TYN-FALLR161, EKPC_P1-2_GRE-TAY-MAR161, EKPC_P1-2_BARR-SUMSH161, EKPC_P1-2_BULL-SUMSH161, EKPC_P1-2_BULL-BLUE L161, EKPC_P1-2_BULL-SHEL161,
EKPC_P1-2_POW-BTV-DEL161, TVA SS-GLASGOW & LAFAYETTE 161, EK-TVA SSHD & SSHD 161 XFMR, EKPC_P1-2_AVON-NCLA345, SINGLE OPN LIN 714 324010-324114(1), SINGLE OPN LIN 715 324021-324103(Z1), SINGLE OPN LIN 716 324022-324103(Z1),
SINGLE OPN LIN 717 324029-324030(1), SINGLE OPN LIN 718 324029-324114(1), SINGLE OPN LIN 719 324030-324114(1), SINGLE OPN LIN 720 324047-325055(1), SINGLE OPN LIN 721 324048-324437(1), SINGLE OPN LIN 722 324048-324584(1), SINGLE OPN LIN 723 324049-324572(1),
SINGLE OPN LIN 724 324049-324745(1), SINGLE OPN LIN 725 324050-324362(1), SINGLE OPN LIN 726 324050-324447(1), SINGLE OPN LIN 727 324051-324173(1), SINGLE OPN LIN 728 324051-324173(2), SINGLE OPN LIN 729 324051-324255(1), SINGLE OPN LIN 730 324051-324291(1),
SINGLE OPN LIN 731 324058-324059(1), SINGLE OPN LIN 732 324058-324667(1), SINGLE OPN LIN 733 324059-324080(1), SINGLE OPN LIN 734 324061-324079(1), SINGLE OPN LIN 735 324061-324873(1), SINGLE OPN LIN 736 324065-324843(1), SINGLE OPN LIN 737 324067-324512(1),
SINGLE OPN LIN 738 324068-324349(1), SINGLE OPN LIN 739 324069-324687(1), SINGLE OPN LIN 740 324069-324763(1), SINGLE OPN LIN 741 324075-324702(1), SINGLE OPN LIN 742 324077-326594(1), SINGLE OPN LIN 743 324081-326587(1), SINGLE OPN LIN 744 324082-324197(1),
SINGLE OPN LIN 745 324082-324476(1), SINGLE OPN LIN 746 324082-325061(1), SINGLE OPN LIN 747 324083-326587(1), SINGLE OPN LIN 748 324085-324629(1), SINGLE OPN LIN 749 324086-324096(1), SINGLE OPN LIN 750 324086-324671(1), SINGLE OPN LIN 751 324087-324913(1),
SINGLE OPN LIN 752 324087-324927(1), SINGLE OPN LIN 753 324090-324095(1), SINGLE OPN LIN 754 324091-324096(1), SINGLE OPN LIN 755 324092-324702(1), SINGLE OPN LIN 756 324093-324711(1), SINGLE OPN LIN 757 324094-324562(1), SINGLE OPN LIN 758 324094-324761(1),
SINGLE OPN LIN 759 324094-325045(1), SINGLE OPN LIN 760 324095-326572(1), SINGLE OPN LIN 761 324096-324097(1), SINGLE OPN LIN 762 324098-324779(1), SINGLE OPN LIN 763 324100-324102(1), SINGLE OPN LIN 764 324100-324112(1), SINGLE OPN LIN 765 324100-324130(1),
SINGLE OPN LIN 766 324101-324107(1), SINGLE OPN LIN 767 324101-324108(1), SINGLE OPN LIN 768 324101-324134(1), SINGLE OPN LIN 769 324101-324212(1), SINGLE OPN LIN 770 324102-324106(1), SINGLE OPN LIN 771 324102-324116(1), SINGLE OPN LIN 772 324102-325074(1),
SINGLE OPN LIN 773 324102-325956(1), SINGLE OPN LIN 774 324102-325957(2), SINGLE OPN LIN 775 324103-324107(1), SINGLE OPN LIN 776 324103-324114(1), SINGLE OPN LIN 777 324104-324106(1), SINGLE OPN LIN 778 324105-324115(1), SINGLE OPN LIN 779 324105-324116(1),
SINGLE OPN LIN 780 324105-324253(1), SINGLE OPN LIN 781 324105-324253(2), SINGLE OPN LIN 782 324105-326536(1), SINGLE OPN LIN 783 324106-324261(1), SINGLE OPN LIN 784 324106-324261(2), SINGLE OPN LIN 785 324106-325073(1), SINGLE OPN LIN 786 324107-324108(1),
SINGLE OPN LIN 787 324107-324114(1), SINGLE OPN LIN 788 324107-324281(3), SINGLE OPN LIN 789 324107-324281(4), SINGLE OPN LIN 790 324107-324281(5), SINGLE OPN LIN 791 324107-324281(7), SINGLE OPN LIN 792 324108-325073(1), SINGLE OPN LIN 793 324108-326001(1),
SINGLE OPN LIN 794 324109-324565(1), SINGLE OPN LIN 795 324110-324289(1), SINGLE OPN LIN 796 324110-326569(1), SINGLE OPN LIN 797 324111-324294(1), SINGLE OPN LIN 798 324111-326001(1), SINGLE OPN LIN 799 324111-326569(1), SINGLE OPN LIN 800 324112-324167(1),
SINGLE OPN LIN 801 324112-325074(1), SINGLE OPN LIN 802 324114-324314(5), SINGLE OPN LIN 803 324114-324314(6), SINGLE OPN LIN 804 324115-324319(1), SINGLE OPN LIN 805 324116-324320(1), SINGLE OPN LIN 806 324124-326564(1), SINGLE OPN LIN 807 324130-324141(1),
SINGLE OPN LIN 808 324130-324143(1), SINGLE OPN LIN 809 324131-324139(1), SINGLE OPN LIN 810 324131-324146(1), SINGLE OPN LIN 811 324131-324148(1), SINGLE OPN LIN 812 324131-324416(1), SINGLE OPN LIN 813 324132-324133(1), SINGLE OPN LIN 814 324132-324143(1),
SINGLE OPN LIN 815 324132-324156(1), SINGLE OPN LIN 816 324133-324417(1), SINGLE OPN LIN 817 324134-326975(1), SINGLE OPN LIN 818 324135-324136(1), SINGLE OPN LIN 819 324135-324144(1), SINGLE OPN LIN 820 324135-324153(1), SINGLE OPN LIN 821 324136-324484(1),
SINGLE OPN LIN 822 324137-324151(1), SINGLE OPN LIN 823 324137-324153(1), SINGLE OPN LIN 824 324137-324486(1), SINGLE OPN LIN 825 324138-324148(1), SINGLE OPN LIN 826 324138-324165(1), SINGLE OPN LIN 827 324139-324149(1), SINGLE OPN LIN 828 324139-324503(1),
SINGLE OPN LIN 829 324139-324503(2), SINGLE OPN LIN 830 324140-324160(1), SINGLE OPN LIN 831 324140-324164(1), SINGLE OPN LIN 832 324140-324506(1), SINGLE OPN LIN 833 324140-325079(1), SINGLE OPN LIN 834 324141-324514(1), SINGLE OPN LIN 835 324141-324514(2),
SINGLE OPN LIN 836 324143-324527(1), SINGLE OPN LIN 837 324144-324160(1), SINGLE OPN LIN 838 324144-324255(1), SINGLE OPN LIN 839 324144-324255(2), SINGLE OPN LIN 840 324144-324255(3), SINGLE OPN LIN 841 324145-324171(1), SINGLE OPN LIN 842 324145-324172(1),
SINGLE OPN LIN 843 324145-324553(1), SINGLE OPN LIN 844 324145-325069(1), SINGLE OPN LIN 845 324145-325077(1), SINGLE OPN LIN 846 324146-324147(1), SINGLE OPN LIN 847 324146-324155(1), SINGLE OPN LIN 848 324146-324157(1), SINGLE OPN LIN 849 324146-324564(1),
SINGLE OPN LIN 850 324147-324155(1), SINGLE OPN LIN 851 324149-324157(1), SINGLE OPN LIN 852 324149-324583(1), SINGLE OPN LIN 853 324150-324154(1), SINGLE OPN LIN 854 324151-324161(1), SINGLE OPN LIN 855 324151-325028(1), SINGLE OPN LIN 856 324152-324165(1),
SINGLE OPN LIN 857 324152-324276(1), SINGLE OPN LIN 858 324153-324645(1), SINGLE OPN LIN 859 324155-324156(1), SINGLE OPN LIN 860 324155-324167(Z1), SINGLE OPN LIN 861 324155-324686(1), SINGLE OPN LIN 862 324157-324158(1), SINGLE OPN LIN 863 324158-324689(1),
SINGLE OPN LIN 864 324159-324160(1), SINGLE OPN LIN 865 324159-324702(1), SINGLE OPN LIN 866 324161-324712(1), SINGLE OPN LIN 867 324161-325078(1), SINGLE OPN LIN 868 324163-324165(1), SINGLE OPN LIN 869 324163-324767(1), SINGLE OPN LIN 870 324164-324769(1),
SINGLE OPN LIN 871 324166-324779(1), SINGLE OPN LIN 872 324166-325069(1), SINGLE OPN LIN 873 324167-324686(2), SINGLE OPN LIN 874 324191-324603(1), SINGLE OPN LIN 875 324191-324606(1), SINGLE OPN LIN 876 324192-324240(1), SINGLE OPN LIN 877 324193-324251(1),
SINGLE OPN LIN 878 324195-324722(1), SINGLE OPN LIN 879 324196-324224(1), SINGLE OPN LIN 880 324196-324449(1), SINGLE OPN LIN 881 324198-324878(1), SINGLE OPN LIN 882 324199-324252(1), SINGLE OPN LIN 883 324200-324205(1), SINGLE OPN LIN 884 324200-324237(1),
SINGLE OPN LIN 885 324200-324299(1), SINGLE OPN LIN 886 324201-324305(1), SINGLE OPN LIN 887 324201-324313(1), SINGLE OPN LIN 888 324201-324315(1), SINGLE OPN LIN 889 324201-324335(1), SINGLE OPN LIN 890 324201-324405(1), SINGLE OPN LIN 891 324201-324405(2),
SINGLE OPN LIN 892 324202-324241(1), SINGLE OPN LIN 893 324202-324408(1), SINGLE OPN LIN 894 324203-324258(1), SINGLE OPN LIN 895 324203-324301(1), SINGLE OPN LIN 896 324203-324409(1), SINGLE OPN LIN 897 324204-324205(1), SINGLE OPN LIN 898 324204-324243(1),
SINGLE OPN LIN 899 324204-324281(1), SINGLE OPN LIN 900 324205-324237(1), SINGLE OPN LIN 901 324205-324257(1), SINGLE OPN LIN 902 324205-324279(1), SINGLE OPN LIN 903 324205-324419(1), SINGLE OPN LIN 904 324205-325023(2), SINGLE OPN LIN 905 324206-324284(1),
SINGLE OPN LIN 906 324206-324299(1), SINGLE OPN LIN 907 324207-324218(1), SINGLE OPN LIN 908 324207-324288(1), SINGLE OPN LIN 909 324207-324426(1), SINGLE OPN LIN 910 324208-324265(1), SINGLE OPN LIN 911 324208-324277(1), SINGLE OPN LIN 912 324208-324289(1),
SINGLE OPN LIN 913 324208-324298(1), SINGLE OPN LIN 914 324208-324321(1), SINGLE OPN LIN 915 324208-324321(2), SINGLE OPN LIN 916 324208-324429(1), SINGLE OPN LIN 917 324209-324263(1), SINGLE OPN LIN 918 324210-324262(1), SINGLE OPN LIN 919 324210-324334(1),
SINGLE OPN LIN 920 324211-324221(1), SINGLE OPN LIN 921 324211-324253(1), SINGLE OPN LIN 922 324212-324285(1), SINGLE OPN LIN 923 324213-324270(1), SINGLE OPN LIN 924 324213-324447(1), SINGLE OPN LIN 925 324213-324800(1), SINGLE OPN LIN 926 324214-324243(1),
SINGLE OPN LIN 927 324214-324263(1), SINGLE OPN LIN 928 324214-324451(1), SINGLE OPN LIN 929 324215-324237(1), SINGLE OPN LIN 930 324215-324284(1), SINGLE OPN LIN 931 324217-324219(1), SINGLE OPN LIN 932 324217-324220(1), SINGLE OPN LIN 933 324217-324239(1),
SINGLE OPN LIN 934 324217-324248(1), SINGLE OPN LIN 935 324218-324219(1), SINGLE OPN LIN 936 324218-324220(1), SINGLE OPN LIN 937 324218-325957(1), SINGLE OPN LIN 938 324219-325957(1), SINGLE OPN LIN 939 324220-325956(1), SINGLE OPN LIN 940 324221-324225(1),
SINGLE OPN LIN 941 324222-324237(1), SINGLE OPN LIN 942 324222-324295(1), SINGLE OPN LIN 943 324223-324294(1), SINGLE OPN LIN 944 324223-324321(1), SINGLE OPN LIN 945 324223-324462(1), SINGLE OPN LIN 946 324225-324226(1), SINGLE OPN LIN 947 324225-324267(1),
SINGLE OPN LIN 948 324226-324463(1), SINGLE OPN LIN 949 324227-324274(1), SINGLE OPN LIN 950 324227-324466(1), SINGLE OPN LIN 951 324227-324466(2), SINGLE OPN LIN 952 324227-326512(1), SINGLE OPN LIN 953 324228-324281(1), SINGLE OPN LIN 954 324228-324469(1),
SINGLE OPN LIN 955 324228-326520(1), SINGLE OPN LIN 956 324229-324236(1), SINGLE OPN LIN 957 324229-324310(1), SINGLE OPN LIN 958 324229-324472(1), SINGLE OPN LIN 959 324230-324262(1), SINGLE OPN LIN 960 324230-325957(1), SINGLE OPN LIN 961 324231-324256(1),
SINGLE OPN LIN 962 324231-324260(1), SINGLE OPN LIN 963 324231-325132(1), SINGLE OPN LIN 964 324232-326574(1), SINGLE OPN LIN 965 324236-324248(1), SINGLE OPN LIN 966 324237-324295(1), SINGLE OPN LIN 967 324237-324488(1), SINGLE OPN LIN 968 324237-324488(2),
SINGLE OPN LIN 969 324237-325096(22), SINGLE OPN LIN 970 324237-325096(24), SINGLE OPN LIN 971 324237-325096(25), SINGLE OPN LIN 972 324237-326565(23), SINGLE OPN LIN 973 324237-326574(21), SINGLE OPN LIN 974 324238-324239(1), SINGLE OPN LIN 975 324238-324495(1),
SINGLE OPN LIN 976 324239-325121(1), SINGLE OPN LIN 977 324240-324242(1), SINGLE OPN LIN 978 324240-324287(1), SINGLE OPN LIN 979 324241-324295(1), SINGLE OPN LIN 980 324242-326512(1), SINGLE OPN LIN 981 324243-324518(1), SINGLE OPN LIN 982 324244-324261(1),
SINGLE OPN LIN 983 324244-324288(1), SINGLE OPN LIN 984 324244-324519(1), SINGLE OPN LIN 985 324245-324246(1), SINGLE OPN LIN 986 324245-324307(1), SINGLE OPN LIN 987 324245-324310(1), SINGLE OPN LIN 988 324246-324528(1), SINGLE OPN LIN 989 324247-324248(1),
SINGLE OPN LIN 990 324247-324276(1), SINGLE OPN LIN 991 324248-324530(1), SINGLE OPN LIN 992 324248-324530(2), SINGLE OPN LIN 993 324249-324257(1), SINGLE OPN LIN 994 324249-324292(1), SINGLE OPN LIN 995 324249-324322(1), SINGLE OPN LIN 996 324249-324532(1),
SINGLE OPN LIN 997 324249-324532(2), SINGLE OPN LIN 998 324250-324306(1), SINGLE OPN LIN 999 324250-324315(1), SINGLE OPN LIN 1000 324250-324535(1), SINGLE OPN LIN 1001 324250-324535(2), SINGLE OPN LIN 1002 324251-324254(1), SINGLE OPN LIN 1003 324251-324323(1),
SINGLE OPN LIN 1004 324252-324455(1), SINGLE OPN LIN 1005 324253-324287(1), SINGLE OPN LIN 1006 324253-324290(1), SINGLE OPN LIN 1007 324253-324831(1), SINGLE OPN LIN 1008 324254-324302(1), SINGLE OPN LIN 1009 324255-324291(1), SINGLE OPN LIN 1010 324255-324550(1),
SINGLE OPN LIN 1011 324255-324550(2), SINGLE OPN LIN 1012 324255-325015(1), SINGLE OPN LIN 1013 324256-324551(1), SINGLE OPN LIN 1014 324256-325015(1), SINGLE OPN LIN 1015 324258-324264(1), SINGLE OPN LIN 1016 324258-324317(1), SINGLE OPN LIN 1017 324258-324335(1),
SINGLE OPN LIN 1018 324258-324558(1), SINGLE OPN LIN 1019 324258-325100(1), SINGLE OPN LIN 1020 324259-324278(1), SINGLE OPN LIN 1021 324259-324561(1), SINGLE OPN LIN 1022 324260-325055(1), SINGLE OPN LIN 1023 324261-324303(1), SINGLE OPN LIN 1024 324261-324563(1),
SINGLE OPN LIN 1025 324261-324563(2), SINGLE OPN LIN 1026 324262-324269(1), SINGLE OPN LIN 1027 324262-324333(1), SINGLE OPN LIN 1028 324262-324568(1), SINGLE OPN LIN 1029 324262-324569(1), SINGLE OPN LIN 1030 324262-324569(2), SINGLE OPN LIN 1031 324262-325089(Z1),
SINGLE OPN LIN 1032 324263-324297(1), SINGLE OPN LIN 1033 324264-324275(1), SINGLE OPN LIN 1034 324264-326548(1), SINGLE OPN LIN 1035 324265-324289(1), SINGLE OPN LIN 1036 324267-324323(1), SINGLE OPN LIN 1037 324267-324589(1), SINGLE OPN LIN 1038 324267-324882(1),
SINGLE OPN LIN 1039 324268-324284(1), SINGLE OPN LIN 1040 324268-324300(1), SINGLE OPN LIN 1041 324269-324601(1), SINGLE OPN LIN 1042 324270-324271(1), SINGLE OPN LIN 1043 324271-324606(1), SINGLE OPN LIN 1044 324271-324606(2), SINGLE OPN LIN 1045 324271-325121(1),
SINGLE OPN LIN 1046 324272-324308(1), SINGLE OPN LIN 1047 324272-324609(1), SINGLE OPN LIN 1048 324273-326559(Z1), SINGLE OPN LIN 1049 324274-324306(1), SINGLE OPN LIN 1050 324275-324618(1), SINGLE OPN LIN 1051 324276-326559(1), SINGLE OPN LIN 1052 324277-324281(1),
SINGLE OPN LIN 1053 324277-324622(1), SINGLE OPN LIN 1054 324278-324321(1), SINGLE OPN LIN 1055 324279-324284(1), SINGLE OPN LIN 1056 324281-324282(1), SINGLE OPN LIN 1057 324281-324364(1), SINGLE OPN LIN 1058 324281-324637(1), SINGLE OPN LIN 1059 324281-324637(2),
SINGLE OPN LIN 1060 324281-324637(6), SINGLE OPN LIN 1061 324281-325042(1), SINGLE OPN LIN 1062 324282-324298(1), SINGLE OPN LIN 1063 324283-324320(1), SINGLE OPN LIN 1064 324283-324831(1), SINGLE OPN LIN 1065 324284-324640(7), SINGLE OPN LIN 1066 324284-324640(8),
SINGLE OPN LIN 1067 324284-325088(1), SINGLE OPN LIN 1068 324285-324292(1), SINGLE OPN LIN 1069 324285-324651(1), SINGLE OPN LIN 1070 324286-324287(1), SINGLE OPN LIN 1071 324289-325013(1), SINGLE OPN LIN 1072 324290-324305(1), SINGLE OPN LIN 1073 324291-324667(1),
SINGLE OPN LIN 1074 324294-324295(1), SINGLE OPN LIN 1075 324296-324320(1), SINGLE OPN LIN 1076 324296-324687(1), SINGLE OPN LIN 1077 324296-325857(1), SINGLE OPN LIN 1078 324297-324298(1), SINGLE OPN LIN 1079 324300-324311(1), SINGLE OPN LIN 1080 324301-325089(1),
SINGLE OPN LIN 1081 324302-324307(1), SINGLE OPN LIN 1082 324303-324708(1), SINGLE OPN LIN 1083 324304-324762(1), SINGLE OPN LIN 1084 324305-324951(1), SINGLE OPN LIN 1085 324305-324991(1), SINGLE OPN LIN 1086 324307-326556(1), SINGLE OPN LIN 1087 324310-324733(1),
SINGLE OPN LIN 1088 324310-325009(1), SINGLE OPN LIN 1089 324311-324976(3), SINGLE OPN LIN 1090 324311-325132(1), SINGLE OPN LIN 1091 324312-324313(1), SINGLE OPN LIN 1092 324312-324991(1), SINGLE OPN LIN 1093 324314-326520(Z1), SINGLE OPN LIN 1094 324315-324755(1),
SINGLE OPN LIN 1095 324315-325957(1), SINGLE OPN LIN 1096 324316-324759(1), SINGLE OPN LIN 1097 324317-325101(1), SINGLE OPN LIN 1098 324318-324764(1), SINGLE OPN LIN 1099 324318-324764(2), SINGLE OPN LIN 1100 324319-324765(1), SINGLE OPN LIN 1101 324320-325089(1),
SINGLE OPN LIN 1102 324320-325100(1), SINGLE OPN LIN 1103 324320-325101(1), SINGLE OPN LIN 1104 324322-324771(1), SINGLE OPN LIN 1105 324322-324771(2), SINGLE OPN LIN 1106 324322-325042(1), SINGLE OPN LIN 1107 324328-324680(1), SINGLE OPN LIN 1108 324329-324364(1),
SINGLE OPN LIN 1109 324329-324481(1), SINGLE OPN LIN 1110 324330-324783(1), SINGLE OPN LIN 1111 324330-325063(1), SINGLE OPN LIN 1112 324331-324418(1), SINGLE OPN LIN 1113 324332-325059(1), SINGLE OPN LIN 1114 324333-325957(1), SINGLE OPN LIN 1115 324334-325956(1),
SINGLE OPN LIN 1116 324337-324650(1), SINGLE OPN LIN 1117 324338-324339(1), SINGLE OPN LIN 1118 324338-324952(1), SINGLE OPN LIN 1119 324340-324734(1), SINGLE OPN LIN 1120 324341-324781(1), SINGLE OPN LIN 1121 324344-324421(1), SINGLE OPN LIN 1122 324345-324425(1),
SINGLE OPN LIN 1123 324346-324612(1), SINGLE OPN LIN 1124 324347-325058(1), SINGLE OPN LIN 1125 324348-324808(1), SINGLE OPN LIN 1126 324349-324479(1), SINGLE OPN LIN 1127 324350-324485(1), SINGLE OPN LIN 1128 324351-324354(1), SINGLE OPN LIN 1129 324351-324519(1),
SINGLE OPN LIN 1130 324352-324563(1), SINGLE OPN LIN 1131 324353-324863(1), SINGLE OPN LIN 1132 324354-326561(1), SINGLE OPN LIN 1133 324355-325054(1), SINGLE OPN LIN 1134 324355-326578(1), SINGLE OPN LIN 1135 324356-325054(1), SINGLE OPN LIN 1136 324357-324600(1),
SINGLE OPN LIN 1137 324358-324914(1), SINGLE OPN LIN 1138 324359-324913(1), SINGLE OPN LIN 1139 324360-324927(1), SINGLE OPN LIN 1140 324361-324935(1), SINGLE OPN LIN 1141 324363-324957(1), SINGLE OPN LIN 1142 324363-326518(1), SINGLE OPN LIN 1143 324372-324514(1),
SINGLE OPN LIN 1144 324373-324814(1), SINGLE OPN LIN 1145 324374-324376(1), SINGLE OPN LIN 1146 324374-325083(1), SINGLE OPN LIN 1147 324375-324442(1), SINGLE OPN LIN 1148 324376-324813(1), SINGLE OPN LIN 1149 324377-325083(1), SINGLE OPN LIN 1150 324378-324636(1),
SINGLE OPN LIN 1151 324380-324393(1), SINGLE OPN LIN 1152 324380-324945(1), SINGLE OPN LIN 1153 324381-325001(1), SINGLE OPN LIN 1154 324382-325001(1), SINGLE OPN LIN 1155 324384-324549(1), SINGLE OPN LIN 1156 324385-324549(1), SINGLE OPN LIN 1157 324386-324388(1),
SINGLE OPN LIN 1158 324387-324392(1), SINGLE OPN LIN 1159 324387-325064(1), SINGLE OPN LIN 1160 324388-325031(1), SINGLE OPN LIN 1161 324389-324851(1), SINGLE OPN LIN 1162 324390-324391(1), SINGLE OPN LIN 1163 324391-324689(1), SINGLE OPN LIN 1164 324392-325031(1),
SINGLE OPN LIN 1165 324394-324977(1), SINGLE OPN LIN 1166 324395-325005(1), SINGLE OPN LIN 1167 324400-324510(1), SINGLE OPN LIN 1168 324400-324775(1), SINGLE OPN LIN 1169 324400-325022(1), SINGLE OPN LIN 1170 324401-324541(1), SINGLE OPN LIN 1171 324401-324545(1),
SINGLE OPN LIN 1172 324401-324785(1), SINGLE OPN LIN 1173 324402-324859(1), SINGLE OPN LIN 1174 324403-324469(1), SINGLE OPN LIN 1175 324403-324487(1), SINGLE OPN LIN 1176 324403-324616(1), SINGLE OPN LIN 1177 324404-324622(1), SINGLE OPN LIN 1178 324404-324623(1),
SINGLE OPN LIN 1179 324404-324750(1), SINGLE OPN LIN 1180 324405-324547(1), SINGLE OPN LIN 1181 324405-326989(1), SINGLE OPN LIN 1182 324406-324637(1), SINGLE OPN LIN 1183 324406-324673(1), SINGLE OPN LIN 1184 324406-325022(1), SINGLE OPN LIN 1185 324407-324755(1),
SINGLE OPN LIN 1186 324407-324955(1), SINGLE OPN LIN 1187 324408-324552(1), SINGLE OPN LIN 1188 324408-324625(1), SINGLE OPN LIN 1189 324408-324649(1), SINGLE OPN LIN 1190 324408-324719(1), SINGLE OPN LIN 1191 324408-324739(1), SINGLE OPN LIN 1192 324409-324632(1),
SINGLE OPN LIN 1193 324409-324683(1), SINGLE OPN LIN 1194 324409-324772(1), SINGLE OPN LIN 1195 324411-324440(1), SINGLE OPN LIN 1196 324411-324583(1), SINGLE OPN LIN 1197 324411-324670(1), SINGLE OPN LIN 1198 324412-324670(1), SINGLE OPN LIN 1199 324413-324414(1),
SINGLE OPN LIN 1200 324413-324461(1), SINGLE OPN LIN 1201 324413-324733(1), SINGLE OPN LIN 1202 324414-326531(1), SINGLE OPN LIN 1203 324415-324593(1), SINGLE OPN LIN 1204 324415-324636(1), SINGLE OPN LIN 1205 324416-324433(1), SINGLE OPN LIN 1206 324416-324490(1),
SINGLE OPN LIN 1207 324417-324423(1), SINGLE OPN LIN 1208 324418-324632(1), SINGLE OPN LIN 1209 324418-324934(1), SINGLE OPN LIN 1210 324419-325024(1), SINGLE OPN LIN 1211 324421-324450(1), SINGLE OPN LIN 1212 324421-324495(1), SINGLE OPN LIN 1213 324422-324508(1),
SINGLE OPN LIN 1214 324422-324680(1), SINGLE OPN LIN 1215 324422-325081(1), SINGLE OPN LIN 1216 324423-324438(1), SINGLE OPN LIN 1217 324424-324801(1), SINGLE OPN LIN 1218 324424-326537(1), SINGLE OPN LIN 1219 324425-324426(1), SINGLE OPN LIN 1220 324426-324525(1),
SINGLE OPN LIN 1221 324426-326537(Z1), SINGLE OPN LIN 1222 324427-324779(1), SINGLE OPN LIN 1223 324427-324823(1), SINGLE OPN LIN 1224 324428-324778(1), SINGLE OPN LIN 1225 324428-324864(1), SINGLE OPN LIN 1226 324429-324453(1), SINGLE OPN LIN 1227 324429-324475(1),
SINGLE OPN LIN 1228 324429-324624(1), SINGLE OPN LIN 1229 324429-324710(1), SINGLE OPN LIN 1230 324430-325058(1), SINGLE OPN LIN 1231 324432-324558(1), SINGLE OPN LIN 1232 324432-324879(1), SINGLE OPN LIN 1233 324433-324621(1), SINGLE OPN LIN 1234 324434-324435(1),
SINGLE OPN LIN 1235 324434-324668(1), SINGLE OPN LIN 1236 324435-324805(1), SINGLE OPN LIN 1237 324436-324676(1), SINGLE OPN LIN 1238 324436-324805(1), SINGLE OPN LIN 1239 324437-324745(1), SINGLE OPN LIN 1240 324438-324515(1), SINGLE OPN LIN 1241 324438-324573(1),
SINGLE OPN LIN 1242 324439-324518(1), SINGLE OPN LIN 1243 324439-324532(1), SINGLE OPN LIN 1244 324440-324621(1), SINGLE OPN LIN 1245 324441-324503(1), SINGLE OPN LIN 1246 324441-324802(1), SINGLE OPN LIN 1247 324442-324497(1), SINGLE OPN LIN 1248 324442-325008(1),
SINGLE OPN LIN 1249 324443-324789(1), SINGLE OPN LIN 1250 324444-324651(1), SINGLE OPN LIN 1251 324444-324788(1), SINGLE OPN LIN 1252 324445-324620(1), SINGLE OPN LIN 1253 324445-324732(1), SINGLE OPN LIN 1254 324445-324863(1), SINGLE OPN LIN 1255 324445-325087(1),
SINGLE OPN LIN 1256 324446-324824(1), SINGLE OPN LIN 1257 324446-324977(1), SINGLE OPN LIN 1258 324447-324731(1), SINGLE OPN LIN 1259 324448-324782(1), SINGLE OPN LIN 1260 324448-325004(1), SINGLE OPN LIN 1261 324449-325004(1), SINGLE OPN LIN 1262 324449-325925(1),
SINGLE OPN LIN 1263 324450-324494(1), SINGLE OPN LIN 1264 324451-324574(1), SINGLE OPN LIN 1265 324451-324673(1), SINGLE OPN LIN 1266 324453-324475(1), SINGLE OPN LIN 1267 324455-324966(1), SINGLE OPN LIN 1268 324456-324465(1), SINGLE OPN LIN 1269 324456-324593(1),
SINGLE OPN LIN 1270 324457-324610(1), SINGLE OPN LIN 1271 324457-324986(1), SINGLE OPN LIN 1272 324458-324501(1), SINGLE OPN LIN 1273 324458-324546(1), SINGLE OPN LIN 1274 324459-324626(1), SINGLE OPN LIN 1275 324459-326533(1), SINGLE OPN LIN 1276 324460-324686(1),
SINGLE OPN LIN 1277 324460-324706(1), SINGLE OPN LIN 1278 324461-324912(1), SINGLE OPN LIN 1279 324462-324499(1), SINGLE OPN LIN 1280 324462-324624(1), SINGLE OPN LIN 1281 324462-324625(1), SINGLE OPN LIN 1282 324462-324665(1), SINGLE OPN LIN 1283 324462-324666(1),
SINGLE OPN LIN 1284 324464-324615(1), SINGLE OPN LIN 1285 324464-324860(1), SINGLE OPN LIN 1286 324465-324784(1), SINGLE OPN LIN 1287 324465-326535(1), SINGLE OPN LIN 1288 324466-324602(1), SINGLE OPN LIN 1289 324466-324634(1), SINGLE OPN LIN 1290 324467-324528(1),
SINGLE OPN LIN 1291 324467-324714(1), SINGLE OPN LIN 1292 324467-326538(1), SINGLE OPN LIN 1293 324468-324572(1), SINGLE OPN LIN 1294 324468-324817(1), SINGLE OPN LIN 1295 324469-324681(1), SINGLE OPN LIN 1296 324469-324682(1), SINGLE OPN LIN 1297 324470-324486(1),
SINGLE OPN LIN 1298 324470-324948(1), SINGLE OPN LIN 1299 324471-324777(1), SINGLE OPN LIN 1300 324471-324822(1), SINGLE OPN LIN 1301 324472-324540(1), SINGLE OPN LIN 1302 324472-324749(1), SINGLE OPN LIN 1303 324473-324561(1), SINGLE OPN LIN 1304 324473-324570(1),
SINGLE OPN LIN 1305 324473-324624(1), SINGLE OPN LIN 1306 324474-324725(1), SINGLE OPN LIN 1307 324474-324765(1), SINGLE OPN LIN 1308 324475-324574(1), SINGLE OPN LIN 1309 324476-324581(1), SINGLE OPN LIN 1310 324476-324680(1), SINGLE OPN LIN 1311 324477-324502(1),
SINGLE OPN LIN 1312 324477-324645(1), SINGLE OPN LIN 1313 324478-324516(1), SINGLE OPN LIN 1314 324478-324828(1), SINGLE OPN LIN 1315 324479-324751(1), SINGLE OPN LIN 1316 324479-324889(1), SINGLE OPN LIN 1317 324480-324515(1), SINGLE OPN LIN 1318 324480-324615(1),
SINGLE OPN LIN 1319 324480-326521(1), SINGLE OPN LIN 1320 324481-324487(1), SINGLE OPN LIN 1321 324481-324541(1), SINGLE OPN LIN 1322 324482-324748(1), SINGLE OPN LIN 1323 324482-324832(1), SINGLE OPN LIN 1324 324484-324571(1), SINGLE OPN LIN 1325 324484-324711(1),
SINGLE OPN LIN 1326 324485-324600(1), SINGLE OPN LIN 1327 324485-324808(1), SINGLE OPN LIN 1328 324486-324628(1), SINGLE OPN LIN 1329 324488-324529(1), SINGLE OPN LIN 1330 324488-324724(1), SINGLE OPN LIN 1331 324488-324739(1), SINGLE OPN LIN 1332 324489-324654(1),
SINGLE OPN LIN 1333 324489-324784(1), SINGLE OPN LIN 1334 324489-325034(1), SINGLE OPN LIN 1335 324490-324827(1), SINGLE OPN LIN 1336 324491-324837(1), SINGLE OPN LIN 1337 324491-325085(1), SINGLE OPN LIN 1338 324492-324595(1), SINGLE OPN LIN 1339 324493-324518(1),
SINGLE OPN LIN 1340 324493-324570(1), SINGLE OPN LIN 1341 324494-324840(1), SINGLE OPN LIN 1342 324495-326579(1), SINGLE OPN LIN 1343 324496-324767(1), SINGLE OPN LIN 1344 324496-324880(1), SINGLE OPN LIN 1345 324497-324564(1), SINGLE OPN LIN 1346 324497-324588(1),
SINGLE OPN LIN 1347 324498-324621(1), SINGLE OPN LIN 1348 324498-324876(1), SINGLE OPN LIN 1349 324499-324552(1), SINGLE OPN LIN 1350 324500-324924(1), SINGLE OPN LIN 1351 324501-324764(1), SINGLE OPN LIN 1352 324502-324658(1), SINGLE OPN LIN 1353 324503-325064(1),
SINGLE OPN LIN 1354 324504-324662(1), SINGLE OPN LIN 1355 324504-324927(1), SINGLE OPN LIN 1356 324505-324506(1), SINGLE OPN LIN 1357 324505-324947(1), SINGLE OPN LIN 1358 324506-324769(1), SINGLE OPN LIN 1359 324506-324954(1), SINGLE OPN LIN 1360 324507-324769(1),
SINGLE OPN LIN 1361 324507-324850(1), SINGLE OPN LIN 1362 324508-324617(1), SINGLE OPN LIN 1363 324509-324914(1), SINGLE OPN LIN 1364 324510-324729(1), SINGLE OPN LIN 1365 324511-324584(1), SINGLE OPN LIN 1366 324511-324959(1), SINGLE OPN LIN 1367 324512-324693(1),
SINGLE OPN LIN 1368 324513-324693(1), SINGLE OPN LIN 1369 324513-324885(1), SINGLE OPN LIN 1370 324514-324531(1), SINGLE OPN LIN 1371 324514-324654(1), SINGLE OPN LIN 1372 324514-324962(1), SINGLE OPN LIN 1373 324515-326530(1), SINGLE OPN LIN 1374 324516-324585(1),
SINGLE OPN LIN 1375 324516-324727(1), SINGLE OPN LIN 1376 324517-325005(1), SINGLE OPN LIN 1377 324518-324657(1), SINGLE OPN LIN 1378 324519-324520(1), SINGLE OPN LIN 1379 324519-324521(1), SINGLE OPN LIN 1380 324519-324563(1), SINGLE OPN LIN 1381 324519-324563(2),
SINGLE OPN LIN 1382 324520-326555(1), SINGLE OPN LIN 1383 324521-324575(1), SINGLE OPN LIN 1384 324522-324523(1), SINGLE OPN LIN 1385 324522-324692(1), SINGLE OPN LIN 1386 324522-324761(1), SINGLE OPN LIN 1387 324523-324798(1), SINGLE OPN LIN 1388 324524-325009(1),
SINGLE OPN LIN 1389 324525-324974(1), SINGLE OPN LIN 1390 324526-324730(1), SINGLE OPN LIN 1391 324527-324704(1), SINGLE OPN LIN 1392 324527-324758(1), SINGLE OPN LIN 1393 324528-324647(1), SINGLE OPN LIN 1394 324529-324675(1), SINGLE OPN LIN 1395 324529-324724(1),
SINGLE OPN LIN 1396 324530-324701(1), SINGLE OPN LIN 1397 324533-324535(1), SINGLE OPN LIN 1398 324534-324535(1), SINGLE OPN LIN 1399 324534-324762(1), SINGLE OPN LIN 1400 324535-326528(1), SINGLE OPN LIN 1401 324536-324653(1), SINGLE OPN LIN 1402 324536-324718(1),
SINGLE OPN LIN 1403 324536-324752(1), SINGLE OPN LIN 1404 324537-324620(1), SINGLE OPN LIN 1405 324537-324755(1), SINGLE OPN LIN 1406 324538-324561(1), SINGLE OPN LIN 1407 324538-324614(1), SINGLE OPN LIN 1408 324539-324601(1), SINGLE OPN LIN 1409 324539-324613(1),
SINGLE OPN LIN 1410 324540-324912(1), SINGLE OPN LIN 1411 324541-324637(1), SINGLE OPN LIN 1412 324542-324588(1), SINGLE OPN LIN 1413 324542-324706(1), SINGLE OPN LIN 1414 324543-324686(1), SINGLE OPN LIN 1415 324543-324813(1), SINGLE OPN LIN 1416 324544-324693(1),
SINGLE OPN LIN 1417 324544-324865(1), SINGLE OPN LIN 1418 324545-324623(1), SINGLE OPN LIN 1419 324546-324600(1), SINGLE OPN LIN 1420 324547-324890(1), SINGLE OPN LIN 1421 324549-324583(1), SINGLE OPN LIN 1422 324549-324894(1), SINGLE OPN LIN 1423 324550-324652(1),
SINGLE OPN LIN 1424 324550-324709(1), SINGLE OPN LIN 1425 324550-324723(1), SINGLE OPN LIN 1426 324550-325082(1), SINGLE OPN LIN 1427 324550-326513(1), SINGLE OPN LIN 1428 324551-324786(1), SINGLE OPN LIN 1429 324551-324947(1), SINGLE OPN LIN 1430 324552-324675(1),
SINGLE OPN LIN 1431 324553-324864(1), SINGLE OPN LIN 1432 324554-324830(1), SINGLE OPN LIN 1433 324555-324716(1), SINGLE OPN LIN 1434 324555-324759(1), SINGLE OPN LIN 1435 324556-324702(1), SINGLE OPN LIN 1436 324556-324870(1), SINGLE OPN LIN 1437 324556-326593(1),
SINGLE OPN LIN 1438 324557-324829(1), SINGLE OPN LIN 1439 324557-324830(1), SINGLE OPN LIN 1440 324558-324734(1), SINGLE OPN LIN 1441 324558-324766(1), SINGLE OPN LIN 1442 324559-324797(1), SINGLE OPN LIN 1443 324559-326586(1), SINGLE OPN LIN 1444 324560-324689(1),
SINGLE OPN LIN 1445 324560-324815(1), SINGLE OPN LIN 1446 324560-325041(1), SINGLE OPN LIN 1447 324562-324564(1), SINGLE OPN LIN 1448 324563-324731(1), SINGLE OPN LIN 1449 324565-324566(1), SINGLE OPN LIN 1450 324567-324780(1), SINGLE OPN LIN 1451 324568-324569(1),
SINGLE OPN LIN 1452 324568-324713(1), SINGLE OPN LIN 1453 324568-324742(1), SINGLE OPN LIN 1454 324569-324632(1), SINGLE OPN LIN 1455 324571-324671(1), SINGLE OPN LIN 1456 324572-324691(1), SINGLE OPN LIN 1457 324573-324741(1), SINGLE OPN LIN 1458 324576-324748(1),
SINGLE OPN LIN 1459 324577-324693(1), SINGLE OPN LIN 1460 324577-324769(1), SINGLE OPN LIN 1461 324578-324690(1), SINGLE OPN LIN 1462 324578-324769(1), SINGLE OPN LIN 1463 324579-324580(1), SINGLE OPN LIN 1464 324579-324960(1), SINGLE OPN LIN 1465 324580-324750(1),
SINGLE OPN LIN 1466 324580-324785(1), SINGLE OPN LIN 1467 324581-324586(1), SINGLE OPN LIN 1468 324582-324610(1), SINGLE OPN LIN 1469 324582-324879(1), SINGLE OPN LIN 1470 324583-324591(1), SINGLE OPN LIN 1471 324584-324659(1), SINGLE OPN LIN 1472 324585-324598(1),
SINGLE OPN LIN 1473 324586-324610(1), SINGLE OPN LIN 1474 324587-324702(1), SINGLE OPN LIN 1475 324587-324709(1), SINGLE OPN LIN 1476 324589-324722(1), SINGLE OPN LIN 1477 324589-324899(1), SINGLE OPN LIN 1478 324589-325019(1), SINGLE OPN LIN 1479 324590-324719(1),
SINGLE OPN LIN 1480 324590-325023(1), SINGLE OPN LIN 1481 324591-324592(1), SINGLE OPN LIN 1482 324592-324689(1), SINGLE OPN LIN 1483 324593-324686(1), SINGLE OPN LIN 1484 324593-324741(1), SINGLE OPN LIN 1485 324595-324837(1), SINGLE OPN LIN 1486 324597-324764(1),
SINGLE OPN LIN 1487 324597-324840(1), SINGLE OPN LIN 1488 324598-324682(1), SINGLE OPN LIN 1489 324599-324600(1), SINGLE OPN LIN 1490 324599-324971(1), SINGLE OPN LIN 1491 324601-324650(1), SINGLE OPN LIN 1492 324601-324780(1), SINGLE OPN LIN 1493 324602-324828(1),
SINGLE OPN LIN 1494 324602-324888(1), SINGLE OPN LIN 1495 324603-324605(1), SINGLE OPN LIN 1496 324604-324606(1), SINGLE OPN LIN 1497 324604-325020(1), SINGLE OPN LIN 1498 324605-324889(1), SINGLE OPN LIN 1499 324606-324736(1), SINGLE OPN LIN 1500 324607-324608(1),
SINGLE OPN LIN 1501 324607-324609(1), SINGLE OPN LIN 1502 324608-324992(1), SINGLE OPN LIN 1503 324609-324643(1), SINGLE OPN LIN 1504 324609-325040(1), SINGLE OPN LIN 1505 324609-325040(2), SINGLE OPN LIN 1506 324610-324617(1), SINGLE OPN LIN 1507 324610-324674(1),
SINGLE OPN LIN 1508 324611-324618(1), SINGLE OPN LIN 1509 324611-324891(1), SINGLE OPN LIN 1510 324612-324701(1), SINGLE OPN LIN 1511 324612-324768(1), SINGLE OPN LIN 1512 324613-324618(1), SINGLE OPN LIN 1513 324613-325059(1), SINGLE OPN LIN 1514 324614-324719(1),
SINGLE OPN LIN 1515 324614-326545(1), SINGLE OPN LIN 1516 324615-324688(1), SINGLE OPN LIN 1517 324616-324775(1), SINGLE OPN LIN 1518 324617-324618(1), SINGLE OPN LIN 1519 324618-326586(1), SINGLE OPN LIN 1520 324619-324998(1), SINGLE OPN LIN 1521 324621-326523(1),
SINGLE OPN LIN 1522 324622-324637(1), SINGLE OPN LIN 1523 324622-324673(1), SINGLE OPN LIN 1524 324623-324637(1), SINGLE OPN LIN 1525 324626-324627(1), SINGLE OPN LIN 1526 324628-324629(1), SINGLE OPN LIN 1527 324629-324904(1), SINGLE OPN LIN 1528 324630-324862(1),
SINGLE OPN LIN 1529 324631-324658(1), SINGLE OPN LIN 1530 324633-324636(1), SINGLE OPN LIN 1531 324633-324684(1), SINGLE OPN LIN 1532 324634-324849(1), SINGLE OPN LIN 1533 324636-324874(1), SINGLE OPN LIN 1534 324637-324653(1), SINGLE OPN LIN 1535 324638-324706(1),
SINGLE OPN LIN 1536 324638-324813(1), SINGLE OPN LIN 1537 324639-324642(1), SINGLE OPN LIN 1538 324639-324812(1), SINGLE OPN LIN 1539 324639-325035(1), SINGLE OPN LIN 1540 324641-324751(1), SINGLE OPN LIN 1541 324641-324829(1), SINGLE OPN LIN 1542 324641-326970(1),
SINGLE OPN LIN 1543 324642-324677(1), SINGLE OPN LIN 1544 324642-324679(1), SINGLE OPN LIN 1545 324642-324717(1), SINGLE OPN LIN 1546 324643-324811(1), SINGLE OPN LIN 1547 324644-324645(1), SINGLE OPN LIN 1548 324644-324776(1), SINGLE OPN LIN 1549 324645-324671(1),
SINGLE OPN LIN 1550 324645-326546(1), SINGLE OPN LIN 1551 324645-326572(1), SINGLE OPN LIN 1552 324646-324707(1), SINGLE OPN LIN 1553 324646-324910(1), SINGLE OPN LIN 1554 324647-324910(1), SINGLE OPN LIN 1555 324648-324664(1), SINGLE OPN LIN 1556 324648-324769(1),
SINGLE OPN LIN 1557 324649-324675(1), SINGLE OPN LIN 1558 324650-324891(1), SINGLE OPN LIN 1559 324652-324817(1), SINGLE OPN LIN 1560 324655-324748(1), SINGLE OPN LIN 1561 324655-324791(1), SINGLE OPN LIN 1562 324655-326542(1), SINGLE OPN LIN 1563 324656-324968(1),
SINGLE OPN LIN 1564 324657-324771(1), SINGLE OPN LIN 1565 324658-324774(1), SINGLE OPN LIN 1566 324658-324776(1), SINGLE OPN LIN 1567 324658-324931(1), SINGLE OPN LIN 1568 324659-326513(1), SINGLE OPN LIN 1569 324660-324801(1), SINGLE OPN LIN 1570 324661-324989(1),
SINGLE OPN LIN 1571 324662-324688(1), SINGLE OPN LIN 1572 324663-324826(1), SINGLE OPN LIN 1573 324667-324703(1), SINGLE OPN LIN 1574 324667-324770(1), SINGLE OPN LIN 1575 324668-324936(1), SINGLE OPN LIN 1576 324672-324916(1), SINGLE OPN LIN 1577 324674-324934(1),
SINGLE OPN LIN 1578 324677-324680(1), SINGLE OPN LIN 1579 324678-324679(1), SINGLE OPN LIN 1580 324678-324680(1), SINGLE OPN LIN 1581 324681-324960(1), SINGLE OPN LIN 1582 324682-324887(1), SINGLE OPN LIN 1583 324683-324866(1), SINGLE OPN LIN 1584 324684-324686(1),
SINGLE OPN LIN 1585 324687-324694(1), SINGLE OPN LIN 1586 324689-324738(1), SINGLE OPN LIN 1587 324689-324744(1), SINGLE OPN LIN 1588 324690-324747(1), SINGLE OPN LIN 1589 324690-324843(1), SINGLE OPN LIN 1590 324691-324870(1), SINGLE OPN LIN 1591 324692-324738(1),
SINGLE OPN LIN 1592 324693-324747(1), SINGLE OPN LIN 1593 324694-324884(1), SINGLE OPN LIN 1594 324694-324930(1), SINGLE OPN LIN 1595 324695-324749(1), SINGLE OPN LIN 1596 324695-324783(1), SINGLE OPN LIN 1597 324696-324706(1), SINGLE OPN LIN 1598 324696-324792(1),
SINGLE OPN LIN 1599 324698-324708(1), SINGLE OPN LIN 1600 324698-326555(1), SINGLE OPN LIN 1601 324699-324768(1), SINGLE OPN LIN 1602 324699-326552(1), SINGLE OPN LIN 1603 324700-324938(1), SINGLE OPN LIN 1604 324703-324959(1), SINGLE OPN LIN 1605 324704-324784(1),
SINGLE OPN LIN 1606 324705-324783(1), SINGLE OPN LIN 1607 324705-324855(1), SINGLE OPN LIN 1608 324708-324944(1), SINGLE OPN LIN 1609 324709-324981(1), SINGLE OPN LIN 1610 324710-324750(1), SINGLE OPN LIN 1611 324711-324790(1), SINGLE OPN LIN 1612 324712-324825(1),
SINGLE OPN LIN 1613 324713-324955(1), SINGLE OPN LIN 1614 324714-324733(1), SINGLE OPN LIN 1615 324715-324721(1), SINGLE OPN LIN 1616 324715-325087(1), SINGLE OPN LIN 1617 324716-324977(1), SINGLE OPN LIN 1618 324717-326549(1), SINGLE OPN LIN 1619 324718-324726(1),
SINGLE OPN LIN 1620 324719-324724(1), SINGLE OPN LIN 1621 324721-324764(1), SINGLE OPN LIN 1622 324723-325086(1), SINGLE OPN LIN 1623 324725-324727(1), SINGLE OPN LIN 1624 324726-324727(1), SINGLE OPN LIN 1625 324727-325102(1), SINGLE OPN LIN 1626 324728-324781(1),
SINGLE OPN LIN 1627 324729-325102(1), SINGLE OPN LIN 1628 324731-326547(1), SINGLE OPN LIN 1629 324734-324848(1), SINGLE OPN LIN 1630 324735-324794(1), SINGLE OPN LIN 1631 324737-324969(1), SINGLE OPN LIN 1632 324740-324788(1), SINGLE OPN LIN 1633 324740-325024(1),
SINGLE OPN LIN 1634 324742-324866(1), SINGLE OPN LIN 1635 324742-324972(1), SINGLE OPN LIN 1636 324743-324759(1), SINGLE OPN LIN 1637 324743-324851(1), SINGLE OPN LIN 1638 324744-324876(1), SINGLE OPN LIN 1639 324746-326546(1), SINGLE OPN LIN 1640 324751-325921(1),
SINGLE OPN LIN 1641 324752-324974(1), SINGLE OPN LIN 1642 324754-324928(1), SINGLE OPN LIN 1643 324755-324762(1), SINGLE OPN LIN 1644 324755-324920(1), SINGLE OPN LIN 1645 324755-324985(1), SINGLE OPN LIN 1646 324756-324772(1), SINGLE OPN LIN 1647 324756-324952(1),
SINGLE OPN LIN 1648 324757-324941(1), SINGLE OPN LIN 1649 324758-324833(1), SINGLE OPN LIN 1650 324760-324838(1), SINGLE OPN LIN 1651 324763-324985(1), SINGLE OPN LIN 1652 324764-326578(1), SINGLE OPN LIN 1653 324765-326528(1), SINGLE OPN LIN 1654 324765-326973(1),
SINGLE OPN LIN 1655 324766-324952(1), SINGLE OPN LIN 1656 324767-326552(Z1), SINGLE OPN LIN 1657 324770-324946(1), SINGLE OPN LIN 1658 324774-324993(1), SINGLE OPN LIN 1659 324776-324777(1), SINGLE OPN LIN 1660 324777-324973(1), SINGLE OPN LIN 1661 324778-324779(1),
SINGLE OPN LIN 1662 324782-324783(1), SINGLE OPN LIN 1663 324784-325001(1), SINGLE OPN LIN 1664 324786-324790(1), SINGLE OPN LIN 1665 324787-324990(1), SINGLE OPN LIN 1666 324788-324809(1), SINGLE OPN LIN 1667 324789-324806(1), SINGLE OPN LIN 1668 324789-325021(1),
SINGLE OPN LIN 1669 324791-324860(1), SINGLE OPN LIN 1670 324792-324819(1), SINGLE OPN LIN 1671 324794-324987(1), SINGLE OPN LIN 1672 324795-324922(1), SINGLE OPN LIN 1673 324797-324855(1), SINGLE OPN LIN 1674 324798-324875(1), SINGLE OPN LIN 1675 324799-324931(1),
SINGLE OPN LIN 1676 324799-324932(1), SINGLE OPN LIN 1677 324802-324871(1), SINGLE OPN LIN 1678 324803-324907(1), SINGLE OPN LIN 1679 324803-325058(1), SINGLE OPN LIN 1680 324804-324908(1), SINGLE OPN LIN 1681 324804-325033(1), SINGLE OPN LIN 1682 324806-324925(1),
SINGLE OPN LIN 1683 324808-324913(1), SINGLE OPN LIN 1684 324809-324958(1), SINGLE OPN LIN 1685 324810-324947(1), SINGLE OPN LIN 1686 324811-324946(1), SINGLE OPN LIN 1687 324814-324956(1), SINGLE OPN LIN 1688 324815-325007(1), SINGLE OPN LIN 1689 324816-324970(1),
SINGLE OPN LIN 1690 324818-324827(1), SINGLE OPN LIN 1691 324818-324978(1), SINGLE OPN LIN 1692 324819-324945(1), SINGLE OPN LIN 1693 324820-324850(1), SINGLE OPN LIN 1694 324820-324981(1), SINGLE OPN LIN 1695 324821-324914(1), SINGLE OPN LIN 1696 324821-324992(1),
SINGLE OPN LIN 1697 324822-324996(1), SINGLE OPN LIN 1698 324823-324825(1), SINGLE OPN LIN 1699 324824-325005(1), SINGLE OPN LIN 1700 324826-324999(1), SINGLE OPN LIN 1701 324832-324833(1), SINGLE OPN LIN 1702 324836-324853(1), SINGLE OPN LIN 1703 324836-324894(1),
SINGLE OPN LIN 1704 324838-324957(1), SINGLE OPN LIN 1705 324839-324909(1), SINGLE OPN LIN 1706 324841-324909(1), SINGLE OPN LIN 1707 324842-324967(1), SINGLE OPN LIN 1708 324842-324987(1), SINGLE OPN LIN 1709 324844-324943(1), SINGLE OPN LIN 1710 324845-324962(1),
SINGLE OPN LIN 1711 324845-324963(1), SINGLE OPN LIN 1712 324846-324932(1), SINGLE OPN LIN 1713 324846-324996(1), SINGLE OPN LIN 1714 324847-324973(1), SINGLE OPN LIN 1715 324847-326546(1), SINGLE OPN LIN 1716 324848-324877(1), SINGLE OPN LIN 1717 324849-324867(1),
SINGLE OPN LIN 1718 324851-324999(1), SINGLE OPN LIN 1719 324852-324885(1), SINGLE OPN LIN 1720 324852-324949(1), SINGLE OPN LIN 1721 324855-326541(1), SINGLE OPN LIN 1722 324856-324880(1), SINGLE OPN LIN 1723 324856-324907(1), SINGLE OPN LIN 1724 324857-324858(1),
SINGLE OPN LIN 1725 324862-325086(1), SINGLE OPN LIN 1726 324863-324920(1), SINGLE OPN LIN 1727 324865-324904(1), SINGLE OPN LIN 1728 324867-324911(1), SINGLE OPN LIN 1729 324871-324894(1), SINGLE OPN LIN 1730 324873-324896(1), SINGLE OPN LIN 1731 324875-324942(1),
SINGLE OPN LIN 1732 324877-324890(1), SINGLE OPN LIN 1733 324878-324908(1), SINGLE OPN LIN 1734 324881-324942(1), SINGLE OPN LIN 1735 324881-324978(1), SINGLE OPN LIN 1736 324884-324979(1), SINGLE OPN LIN 1737 324886-324967(1), SINGLE OPN LIN 1738 324886-324968(1),
SINGLE OPN LIN 1739 324892-324945(1), SINGLE OPN LIN 1740 324892-325007(1), SINGLE OPN LIN 1741 324893-324897(1), SINGLE OPN LIN 1742 324893-326587(1), SINGLE OPN LIN 1743 324895-324897(1), SINGLE OPN LIN 1744 324896-324902(1), SINGLE OPN LIN 1745 324898-324954(1),
SINGLE OPN LIN 1746 324898-324993(1), SINGLE OPN LIN 1747 324899-324900(1), SINGLE OPN LIN 1748 324903-324964(1), SINGLE OPN LIN 1749 324903-324965(1), SINGLE OPN LIN 1750 324909-325032(1), SINGLE OPN LIN 1751 324911-324994(1), SINGLE OPN LIN 1752 324915-325006(1),
SINGLE OPN LIN 1753 324916-324924(1), SINGLE OPN LIN 1754 324916-325027(1), SINGLE OPN LIN 1755 324917-324918(1), SINGLE OPN LIN 1756 324917-324980(1), SINGLE OPN LIN 1757 324918-324919(1), SINGLE OPN LIN 1758 324919-324989(1), SINGLE OPN LIN 1759 324920-326529(1),
SINGLE OPN LIN 1760 324922-326563(1), SINGLE OPN LIN 1761 324925-325006(1), SINGLE OPN LIN 1762 324928-324953(1), SINGLE OPN LIN 1763 324930-324972(1), SINGLE OPN LIN 1764 324934-324984(1), SINGLE OPN LIN 1765 324935-324944(1), SINGLE OPN LIN 1766 324935-324982(1),
SINGLE OPN LIN 1767 324936-324940(1), SINGLE OPN LIN 1768 324937-324939(1), SINGLE OPN LIN 1769 324938-324940(1), SINGLE OPN LIN 1770 324941-324975(1), SINGLE OPN LIN 1771 324948-324949(1), SINGLE OPN LIN 1772 324950-325084(1), SINGLE OPN LIN 1773 324951-326989(1),
SINGLE OPN LIN 1774 324953-326563(1), SINGLE OPN LIN 1775 324954-325762(1), SINGLE OPN LIN 1776 324957-324970(1), SINGLE OPN LIN 1777 324958-325043(1), SINGLE OPN LIN 1778 324959-326564(1), SINGLE OPN LIN 1779 324961-324963(1), SINGLE OPN LIN 1780 324966-324994(1),
SINGLE OPN LIN 1781 324969-324990(1), SINGLE OPN LIN 1782 324970-324971(1), SINGLE OPN LIN 1783 324975-324997(1), SINGLE OPN LIN 1784 324979-324986(1), SINGLE OPN LIN 1785 324981-325062(1), SINGLE OPN LIN 1786 324984-324988(1), SINGLE OPN LIN 1787 324994-325025(1),
SINGLE OPN LIN 1788 324995-325084(1), SINGLE OPN LIN 1789 324996-325010(1), SINGLE OPN LIN 1790 324997-324998(1), SINGLE OPN LIN 1791 325002-325003(Z1), SINGLE OPN LIN 1792 325008-325026(1), SINGLE OPN LIN 1793 325010-325011(1), SINGLE OPN LIN 1794 325017-325018(1),
SINGLE OPN LIN 1795 325018-325061(1), SINGLE OPN LIN 1796 325023-325024(1), SINGLE OPN LIN 1797 325028-325047(1), SINGLE OPN LIN 1798 325028-326589(1), SINGLE OPN LIN 1799 325035-325050(1), SINGLE OPN LIN 1800 325035-325085(1), SINGLE OPN LIN 1801 325041-325068(1),
SINGLE OPN LIN 1802 325044-326565(1), SINGLE OPN LIN 1803 325045-325092(1), SINGLE OPN LIN 1804 325055-325116(1), SINGLE OPN LIN 1805 325057-325088(1), SINGLE OPN LIN 1806 325059-325060(1), SINGLE OPN LIN 1807 325075-325077(Z1), SINGLE OPN LIN 1808 325077-325078(1),
SINGLE OPN LIN 1809 325078-326562(1), SINGLE OPN LIN 1810 325078-326596(1), SINGLE OPN LIN 1811 325079-326589(1), SINGLE OPN LIN 1812 325079-326591(1), SINGLE OPN LIN 1813 325083-326544(1), SINGLE OPN LIN 1814 325096-326002(1), SINGLE OPN LIN 1815 325096-326565(23),
SINGLE OPN LIN 1816 325096-326566(71), SINGLE OPN LIN 1817 325096-326567(72), SINGLE OPN LIN 1818 325096-326568(7S), SINGLE OPN LIN 1819 325096-326574(21), SINGLE OPN LIN 1820 325761-325762(1), SINGLE OPN LIN 1821 325762-325767(1), SINGLE OPN LIN 1822 325857-325956(Z1),
SINGLE OPN LIN 1823 325857-325957(Z1), SINGLE OPN LIN 1824 326001-326002(1), SINGLE OPN LIN 1825 326517-326523(1), SINGLE OPN LIN 1826 326523-326534(1), SINGLE OPN LIN 1827 326524-326527(1), SINGLE OPN LIN 1828 326525-326527(1), SINGLE OPN LIN 1829 326526-326556(1),
SINGLE OPN LIN 1830 326527-326541(1), SINGLE OPN LIN 1831 326528-326974(1), SINGLE OPN LIN 1832 326530-326539(1), SINGLE OPN LIN 1833 326532-326556(1), SINGLE OPN LIN 1834 326552-326553(1), SINGLE OPN LIN 1835 326559-326560(1), SINGLE OPN LIN 1836 326562-326596(Z1),
SINGLE OPN LIN 1837 326571-326586(1), SINGLE OPN LIN 1838 326578-326579(1), SINGLE OPN LIN 1839 326578-326584(1), SINGLE OPN LIN 1840 326579-326580(1), SINGLE OPN LIN 1841 326582-326583(1), SINGLE OPN LIN 1842 326583-326584(1), SINGLE OPN LIN 1843 326591-326592(1),
SINGLE OPN LIN 1844 326593-326594(1), SINGLE OPN TIE 1845 324010-248000(1), SINGLE OPN TIE 1846 324021-324044(1), SINGLE OPN TIE 1847 324021-324045(1), SINGLE OPN TIE 1848 324022-324046(1), SINGLE OPN TIE 1850 324104-324113(1), SINGLE OPN TIE 1851 324104-340561(1),
SINGLE OPN TIE 1852 324104-340563(1), SINGLE OPN TIE 1853 324105-249501(1), SINGLE OPN TIE 1854 324105-249532(1), SINGLE OPN TIE 1855 324108-324284-326550(5), SINGLE OPN TIE 1856 324108-324284-326551(6), SINGLE OPN TIE 1857 324112-324072(1), SINGLE OPN TIE 1858 324114-249520(1),
SINGLE OPN TIE 1859 324114-249532(1), SINGLE OPN TIE 1863 324144-340553(1), SINGLE OPN TIE 1864 324148-243668(1), SINGLE OPN TIE 1865 324150-360334(1), SINGLE OPN TIE 1866 324151-360125(1), SINGLE OPN TIE 1867 324151-360127(1), SINGLE OPN TIE 1868 324156-360452(1),
SINGLE OPN TIE 1869 324157-324073(1), SINGLE OPN TIE 1870 324171-351003(1), SINGLE OPN TIE 1871 324172-351002(1), SINGLE OPN TIE 1872 324173-340553(1), SINGLE OPN TIE 1873 324173-340624(1), SINGLE OPN TIE 1875 324211-251561(1), SINGLE OPN TIE 1877 324217-325012(1),
SINGLE OPN TIE 1878 324227-248009(1), SINGLE OPN TIE 1879 324231-253623(1), SINGLE OPN TIE 1880 324231-340615(1), SINGLE OPN TIE 1881 324232-324399(1), SINGLE OPN TIE 1884 324253-249723(1), SINGLE OPN TIE 1886 324256-324309(1), SINGLE OPN TIE 1887 324260-340615(1),
SINGLE OPN TIE 1889 324265-249763(1), SINGLE OPN TIE 1890 324267-247508(1), SINGLE OPN TIE 1892 324268-324170(1), SINGLE OPN TIE 1899 324289-249789(1), SINGLE OPN TIE 1901 324294-249730(1), SINGLE OPN TIE 1902 324295-324431(4A), SINGLE OPN TIE 1903 324295-324596(5),
SINGLE OPN TIE 1904 324295-324675-324635(3), SINGLE OPN TIE 1906 324311-324366(1), SINGLE OPN TIE 1907 324311-324753-326511(2), SINGLE OPN TIE 1908 324316-242605(1), SINGLE OPN TIE 1910 324405-326500(1), SINGLE OPN TIE 1911 324412-326501(1), SINGLE OPN TIE 1915 324437-324063(1),
SINGLE OPN TIE 1918 324446-324397(1), SINGLE OPN TIE 1923 324503-324398(1), SINGLE OPN TIE 1924 324503-326504(1), SINGLE OPN TIE 1925 324507-324123(1), SINGLE OPN TIE 1927 324512-362916(1), SINGLE OPN TIE 1933 324533-326505(1), SINGLE OPN TIE 1934 324550-324128(1),
SINGLE OPN TIE 1935 324551-324669(1), SINGLE OPN TIE 1937 324574-324043(1), SINGLE OPN TIE 1940 324578-324142(1), SINGLE OPN TIE 1941 324583-324168(1), SINGLE OPN TIE 1945 324664-326507(1), SINGLE OPN TIE 1948 324689-324184(1), SINGLE OPN TIE 1949 324693-326509(1),
SINGLE OPN TIE 1950 324707-243740(Z1), SINGLE OPN TIE 1952 324712-362116(1), SINGLE OPN TIE 1959 324764-324368(1), SINGLE OPN TIE 1962 324803-324057(1), SINGLE OPN TIE 1964 324947-324190(1), SINGLE OPN TIE 1965 324948-324883(1), SINGLE OPN TIE 1967 325013-248009(1),
SINGLE OPN TIE 1968 325014-248009(1), SINGLE OPN TIE 1969 325014-250057(1), SINGLE OPN TIE 1970 325015-324309(1), SINGLE OPN TIE 1972 325047-325046(1), SINGLE OPN TIE 1973 325073-340651(1), SINGLE OPN TIE 1976 325116-325117(1), SINGLE OPN TIE 1979 326569-248830(1),
SINGLE OPN TIE 1980 326569-249520(1), SINGLE OPN TIE 1981 326596-324697(1), SINGLE OPN TIE 1982 326596-324933(1), SINGLE OPN TIE 1985 326998-361788(1), MERE SWS, B-69-51, B-69-446,
B-69-65, B-69-63, B-69-66, B-69-53, B-69-36, B-69-49, B-69-37,
B-69-11, B-69-50, B-69-316A, B-69-9, SW-1000, B-69-47, B-69-48,
B-69-52, B-69-56, B-69-57, B-69-58, B-69-60, B-69-61, B-69-62,
B-69-318, B-69-319, B-69-67, B-69-693, B-69-69, B-69-72, B-69-74,
B-69-76, B-69-77, B-69-73, B-69-10, B-345-449, B-138-123, B-69-322,
B-69-324, B-69-79, B-69-80, B-69-325, B-69-327, B-138-115, B-69-448,
B-161-131, B-69-334, B-69-335, B-138-447, B-69-330, B-69-332, B-69-337,
B-69-338, B-69-450, B-500-97, B-69-339, B-69-340, BB-2000, BB-1366,
BB-1452, BB-1386, BB-1456, BB-1280, BB-1479, BB-1317, BB-1225,
BB-1373, BB-1073, BB-1493, BB-1494, BB-1495, BB-1395, BB-1318,
BB-1352, BB-1405, BB-1301, BB-1387, BB-1443, BB-1335, BB-1298,
BB-1369, BB-1297, BB-1288, BB-1468, BB-1315, BB-1482, BB-1368,
BB-1312, BB-1313, BB-1319, BB-1323, BB-1325, BB-1407, BB-1356,
BB-1316, BB-1370, BB-1349, BB-1320, BB-1434, BB-1285, BB-1401,
MORG-WHT-NEB, BB-1302, BB-1400, BB-1344, BB-1473, BB-1420, BB-1306,
BB-1307, BB-1415, BB-1342, BB-1287, BB-1491, BB-1303, BB-1374,
BB-1367, BB-1339, BB-1308, BB-1338, BB-1404, BB-1442, BB-1513,
BB-1408, BB-1286, BB-1365, BB-1486, BB-1322, BB-1379, BB-1391,
BB-1403, BB-1390, BB-1425, BB-1436, BB-1321, BB-1343, BB-1300,
BB-1294, BB-1327, BB-1336, BB-1446, BB-1514, BB-1345, BB-1361,
BB-3000, BB-1337, BB-1432, BB-1461, BB-1353, BB-1457, B-69-41,
BB-1299, BB-1428, BB-1428A, B-69-40, BB-1464, BB-1410, BB-1326,
BB-1406, B-69-42, BB-1399, BB-1346, B-69-78, BB-1332, BB-1402,
BB-1398, BB-1453, BB-1274, BB-1277, BB-1289, BB-1328, BB-1272,
B-69-45, BB-1512, BB-1470, BB-1430, BB-1450, BB-1424, BB-1393,
BB-1392, BB-1375, B-69-136, B-69-137, B-69-140, B-69-141, BB-1364,
BB-1355, BB-1354, BB-1270, BB-1271, BB-1275, PRIN-KYD-PAD, B-69-46,
P1-1000, P1-1001, B-69-25, BB-1164, BB-1097, B-138-114, B-138-119,
B-138-113, B-138-118, BB-1179, BB-1192, BB-1201, BB-1203, BB-1240,
B-138-122, BB-1143, BB-1049, B-138-111, B-161-125, B-138-21, BB-1133,
B-161-126, BB-1063, B-161-24, B-161-23, B-161-124, BB-1509, B-138-112,
BB-1239, BB-1216, BB-1019, B-138-97, B-161-108, BB-1057, B-161-106,
B-161-128, B-69-18, B-69-19, B-138-28, BB-1228, BB-1229, BB-1066,
BB-1026, B-345-475, BB-1139, B-138-130, B-138-12, B-69-13, B-69-15,
B-69-20, B-69-26, B-69-29, B-69-30, B-69-31, BB-1205, BB-1187,
BB-1136, BB-1112, BB-1098, BB-1075, BB-1062, BB-1060, BB-1061,
B-69-135, B-69-132, B-138-120, B-138-121, B-138-109, BB-1226, BB-1001,
B-345-100, B-161-107, B-138-110, B-138-117, B-161-84, B-138-116, B-345-101,
B-345-102, B-69-133, BB-1074, BB-1132, BB-1218, BB-2021, BB-1245B,
B-69-35, B-69-32, B-69-33, P1-1002, P1-2-1004, P1-2-1005, SINGLE OPN LIN 1986 242691-243088(1),
SINGLE OPN LIN 1987 242927-242938(1), SINGLE OPN LIN 1988 242938-243034(2), SINGLE OPN LIN 1989 242938-243034(3), SINGLE OPN LIN 1990 242938-246888(1), SINGLE OPN LIN 1991 242982-243047(1), SINGLE OPN LIN 1992 242988-242992(1), SINGLE OPN LIN 1993 242988-243042(1),
SINGLE OPN LIN 1994 243013-243069(1), SINGLE OPN LIN 1995 243019-243102(1), SINGLE OPN LIN 1996 243042-243047(1), SINGLE OPN LIN 1997 243042-243069(1), SINGLE OPN LIN 1998 243042-243173(5), SINGLE OPN LIN 1999 243047-243087(1), SINGLE OPN LIN 2000 243047-243819(1),
SINGLE OPN LIN 2001 243069-246782(1), SINGLE OPN LIN 2002 243088-243184(2), SINGLE OPN LIN 2003 243167-243171(1), SINGLE OPN LIN 2004 243167-243178(1), SINGLE OPN LIN 2005 243167-243725(1), SINGLE OPN LIN 2006 243171-243183(1), SINGLE OPN LIN 2007 243173-243181(1),
SINGLE OPN LIN 2008 243173-243597(1), SINGLE OPN LIN 2009 243173-246916(1), SINGLE OPN LIN 2010 243173-246917(1), SINGLE OPN LIN 2011 243176-243178(1), SINGLE OPN LIN 2012 243178-247476(1), SINGLE OPN LIN 2013 243181-243183(1), SINGLE OPN LIN 2014 243618-247072(1),
SINGLE OPN LIN 2015 243656-243808(1), SINGLE OPN LIN 2016 243657-243808(1), SINGLE OPN LIN 2017 243663-243702(1), SINGLE OPN LIN 2018 243663-243750(1), SINGLE OPN LIN 2019 243663-243811(1), SINGLE OPN LIN 2020 243678-243679(1), SINGLE OPN LIN 2021 243679-243702(1),
SINGLE OPN LIN 2022 243684-243702(1), SINGLE OPN LIN 2023 243684-243804(1), SINGLE OPN LIN 2024 243684-244008(1), SINGLE OPN LIN 2025 243688-244686(Z1), SINGLE OPN LIN 2026 243702-246971(1), SINGLE OPN LIN 2027 243712-243716(1), SINGLE OPN LIN 2028 243714-243727(1),
SINGLE OPN LIN 2029 243716-243732(1), SINGLE OPN LIN 2030 243716-243743(1), SINGLE OPN LIN 2031 243724-243737(1), SINGLE OPN LIN 2032 243724-243742(1), SINGLE OPN LIN 2033 243727-243734(1), SINGLE OPN LIN 2034 243728-243740(1), SINGLE OPN LIN 2035 243728-243741(1),
SINGLE OPN LIN 2036 243732-243737(1), SINGLE OPN LIN 2037 243733-243812(1), SINGLE OPN LIN 2039 243734-243812(1), SINGLE OPN LIN 2041 243741-243742(1), SINGLE OPN LIN 2042 243750-244632(1), SINGLE OPN LIN 2043 243758-243759(1), SINGLE OPN LIN 2044 243808-244592(1),
SINGLE OPN LIN 2045 243808-244616(1), SINGLE OPN LIN 2046 244632-246970(1), SINGLE OPN LIN 2047 246970-246971(1), SINGLE OPN TIE 2048 242691-242835(1), SINGLE OPN TIE 2049 242691-244720(1), SINGLE OPN TIE 2050 242918-244965(EQ), SINGLE OPN TIE 2051 242918-245615(4),
SINGLE OPN TIE 2052 242927-242924(1), SINGLE OPN TIE 2053 242938-248005(1), SINGLE OPN TIE 2054 242938-248005(2), SINGLE OPN TIE 2055 242938-248013(1), SINGLE OPN TIE 2056 242938-253077(1), SINGLE OPN TIE 2057 242982-243815(2), SINGLE OPN TIE 2058 242992-243124(1),
SINGLE OPN TIE 2059 242992-243968(1), SINGLE OPN TIE 2060 243013-242698(1), SINGLE OPN TIE 2061 243013-242807(1), SINGLE OPN TIE 2062 243013-243611(1), SINGLE OPN TIE 2063 243013-243766(ZC), SINGLE OPN TIE 2064 243013-243766(ZD), SINGLE OPN TIE 2065 243013-244949(1),
SINGLE OPN TIE 2066 243013-244949(2), SINGLE OPN TIE 2067 243013-246324(Z1), SINGLE OPN TIE 2068 243019-242787(1), SINGLE OPN TIE 2069 243019-246911(1), SINGLE OPN TIE 2070 243019-246946(1), SINGLE OPN TIE 2071 243019-249995(1), SINGLE OPN TIE 2072 243034-243501(1),
SINGLE OPN TIE 2073 243034-243544(2), SINGLE OPN TIE 2074 243034-245632(1), SINGLE OPN TIE 2075 243042-245948(Z1), SINGLE OPN TIE 2076 243042-245949(Z1), SINGLE OPN TIE 2077 243064-242929(2), SINGLE OPN TIE 2078 243064-242999(1), SINGLE OPN TIE 2079 243064-243193(1),
SINGLE OPN TIE 2080 243064-243675(1), SINGLE OPN TIE 2081 243064-245615(1), SINGLE OPN TIE 2082 243064-245664(1), SINGLE OPN TIE 2083 243064-290186(2), SINGLE OPN TIE 2084 243087-243140(1), SINGLE OPN TIE 2085 243088-245615(Z1), SINGLE OPN TIE 2086 243088-245948(1),
SINGLE OPN TIE 2087 243102-244942(Z1), SINGLE OPN TIE 2088 243102-245948(1), SINGLE OPN TIE 2089 243171-290138(1), SINGLE OPN TIE 2090 243173-246850(1), SINGLE OPN TIE 2091 243176-243164(1), SINGLE OPN TIE 2092 243176-243827(1), SINGLE OPN TIE 2093 243176-247033(1),
SINGLE OPN TIE 2094 243184-244719(1), SINGLE OPN TIE 2095 243184-244968(1), SINGLE OPN TIE 2096 243184-244968(2), SINGLE OPN TIE 2097 243453-243454(1), SINGLE OPN TIE 2098 243453-243469(3), SINGLE OPN TIE 2099 243453-243469(4), SINGLE OPN TIE 2100 243453-244022(1),
SINGLE OPN TIE 2101 243453-245769(1), SINGLE OPN TIE 2102 243453-253248(1), SINGLE OPN TIE 2103 243597-246741(1), SINGLE OPN TIE 2104 243618-253076(1), SINGLE OPN TIE 2105 243656-243671(1), SINGLE OPN TIE 2106 243657-243708(1), SINGLE OPN TIE 2107 243657-244688(1),
SINGLE OPN TIE 2108 243678-243669(SR), SINGLE OPN TIE 2109 243688-245949(1), SINGLE OPN TIE 2111 243712-244727(1), SINGLE OPN TIE 2112 243714-243710(1), SINGLE OPN TIE 2119 243743-244670(1), SINGLE OPN TIE 2120 243759-243753(1), SINGLE OPN TIE 2121 243759-243754(1),
SINGLE OPN TIE 2122 243759-247415(1), SINGLE OPN TIE 2123 243804-244575(1), SINGLE OPN TIE 2124 243811-243756(1), SINGLE OPN TIE 2126 243819-243822(1), SINGLE OPN TIE 2127 243819-243826(1), SINGLE OPN TIE 2128 244008-242915(Z1), SINGLE OPN TIE 2129 244592-244599(1),
SINGLE OPN TIE 2130 244616-244626(1), SINGLE OPN TIE 2131 246782-247061(1), SINGLE OPN TIE 2132 246782-247062(1), SINGLE OPN TIE 2133 246888-243454(1), SINGLE OPN TIE 2134 246888-246889(1), SINGLE OPN TIE 2135 246916-243815(1), SINGLE OPN TIE 2136 246917-243815(1),
SINGLE OPN TIE 2139 247072-246790(1), SINGLE OPN TIE 2140 247072-247073(1), SINGLE OPN LIN 2141 249564-249991(1), SINGLE OPN LIN 2142 249564-249991(46), SINGLE OPN LIN 2143 249566-249570(1), SINGLE OPN LIN 2144 249566-249578(1), SINGLE OPN LIN 2145 249566-249582(1),
SINGLE OPN LIN 2146 249567-249575(1), SINGLE OPN LIN 2147 249567-250057(10), SINGLE OPN LIN 2148 249567-250057(9), SINGLE OPN LIN 2149 249570-249575(1), SINGLE OPN LIN 2150 249570-249577(1), SINGLE OPN LIN 2151 249570-250082(1), SINGLE OPN LIN 2152 249570-250083(1),
SINGLE OPN LIN 2153 249571-249573(1), SINGLE OPN LIN 2154 249571-249575(1), SINGLE OPN LIN 2155 249573-249577(1), SINGLE OPN LIN 2156 249573-250097(1), SINGLE OPN LIN 2157 249577-249580(Z1), SINGLE OPN LIN 2158 249577-249581(1), SINGLE OPN LIN 2159 249578-250136(1),
SINGLE OPN LIN 2160 249580-251968(1H), SINGLE OPN LIN 2161 249580-251969(1L), SINGLE OPN LIN 2162 249581-250145(1), SINGLE OPN LIN 2163 249990-250021(1), SINGLE OPN LIN 2164 249991-250028(1), SINGLE OPN LIN 2165 249991-250077(1), SINGLE OPN LIN 2166 249991-250148(1),
SINGLE OPN LIN 2167 249991-251279(2), SINGLE OPN LIN 2168 249999-250007(1), SINGLE OPN LIN 2169 249999-250044(1), SINGLE OPN LIN 2170 250016-250057(1), SINGLE OPN LIN 2171 250044-250152(Z1), SINGLE OPN LIN 2172 250045-250151(Z1), SINGLE OPN LIN 2173 250054-250077(1),
SINGLE OPN LIN 2174 250057-250058(1), SINGLE OPN LIN 2175 250057-250060(1), SINGLE OPN LIN 2176 250057-250070(1), SINGLE OPN LIN 2177 250057-250131(1), SINGLE OPN LIN 2178 250057-250151(1), SINGLE OPN LIN 2179 250058-251378(1), SINGLE OPN LIN 2180 250136-250141(1),
SINGLE OPN LIN 2181 250145-250154(1), SINGLE OPN LIN 2182 250151-250152(Z1), SINGLE OPN LIN 2183 250154-251970(T1), SINGLE OPN LIN 2184 250154-251971(T2), SINGLE OPN LIN 2185 250154-251972(T3), SINGLE OPN LIN 2186 251276-251469(1), SINGLE OPN LIN 2187 251291-251301(1),
SINGLE OPN LIN 2188 251291-251315(1), SINGLE OPN LIN 2189 251301-251310(1), SINGLE OPN LIN 2190 251314-251315(1), SINGLE OPN LIN 2191 251314-251467(1), SINGLE OPN LIN 2192 251367-251368(Z1), SINGLE OPN LIN 2193 251367-251467(1), SINGLE OPN LIN 2194 251378-251406(1),
SINGLE OPN LIN 2195 251378-251469(1), SINGLE OPN LIN 2196 251378-251579(1), SINGLE OPN LIN 2197 251467-251579(1), SINGLE OPN LIN 2198 251468-251469(1), SINGLE OPN TIE 2199 249564-248002(1), SINGLE OPN TIE 2200 249564-248013(1), SINGLE OPN TIE 2201 249566-248013(1),
SINGLE OPN TIE 2202 249566-250029(1), SINGLE OPN TIE 2203 249566-253006(1), SINGLE OPN TIE 2204 249566-253079(1), SINGLE OPN TIE 2205 249567-243233(1), SINGLE OPN TIE 2206 249567-249576(1), SINGLE OPN TIE 2207 249567-251950(7), SINGLE OPN TIE 2208 249567-251951(8),
SINGLE OPN TIE 2209 249567-253090(1), SINGLE OPN TIE 2210 249571-250092(1), SINGLE OPN TIE 2211 249571-250093(1), SINGLE OPN TIE 2212 249575-249565(1), SINGLE OPN TIE 2213 249575-250117(1), SINGLE OPN TIE 2214 249575-250118(1), SINGLE OPN TIE 2215 249578-253077(1),
SINGLE OPN TIE 2217 249582-249574(1), SINGLE OPN TIE 2218 249582-249583(1), SINGLE OPN TIE 2219 249582-250162(1), SINGLE OPN TIE 2220 249990-253076(1), SINGLE OPN TIE 2221 249990-251277-251792(1), SINGLE OPN TIE 2222 249991-251278(1), SINGLE OPN TIE 2223 249991-251278-252039(1),
SINGLE OPN TIE 2224 250007-250014(1), SINGLE OPN TIE 2225 250007-250124(1), SINGLE OPN TIE 2226 250016-250061(1), SINGLE OPN TIE 2227 250016-251311(1), SINGLE OPN TIE 2228 250016-251312(1), SINGLE OPN TIE 2229 250016-251793(1), SINGLE OPN TIE 2230 250021-250020(Z1),
SINGLE OPN TIE 2231 250028-250027(Z1), SINGLE OPN TIE 2233 250057-249736(1), SINGLE OPN TIE 2235 250058-251960-251961(18), SINGLE OPN TIE 2236 250060-250048(1), SINGLE OPN TIE 2237 250070-250032(1), SINGLE OPN TIE 2238 250082-249985(1), SINGLE OPN TIE 2239 250082-250050(1),
SINGLE OPN TIE 2240 250082-250067(1), SINGLE OPN TIE 2241 250082-250096(1), SINGLE OPN TIE 2242 250082-250157(1), SINGLE OPN TIE 2243 250082-251428-251798(1), SINGLE OPN TIE 2244 250083-250013(1), SINGLE OPN TIE 2245 250083-250065(1), SINGLE OPN TIE 2246 250083-250160(1),
SINGLE OPN TIE 2247 250083-251429(1), SINGLE OPN TIE 2248 250083-251798(1), SINGLE OPN TIE 2249 250083-252045(5), SINGLE OPN TIE 2250 250083-251428-252045(1), SINGLE OPN TIE 2251 250097-249988(1), SINGLE OPN TIE 2252 250097-250042(1), SINGLE OPN TIE 2253 250097-250052(1),
SINGLE OPN TIE 2254 250097-250053(1), SINGLE OPN TIE 2255 250131-250032(1), SINGLE OPN TIE 2256 250131-250068(1), SINGLE OPN TIE 2257 250131-250155(1), SINGLE OPN TIE 2258 250131-251826(1), SINGLE OPN TIE 2259 250136-250166(Z1), SINGLE OPN TIE 2260 250141-250020(1),
SINGLE OPN TIE 2261 250148-250043(1), SINGLE OPN TIE 2264 251279-251527(1), SINGLE OPN TIE 2265 251279-251543(1), SINGLE OPN TIE 2266 251310-251284(1), SINGLE OPN TIE 2268 251368-251373(1), SINGLE OPN TIE 2269 251405-251449(1), SINGLE OPN TIE 2270 251468-251414(1),
SINGLE OPN LIN 2272 360112-360450(1), SINGLE OPN LIN 2273 360145-360473(1), SINGLE OPN LIN 2274 360145-361771(1), SINGLE OPN LIN 2275 360333-361113(1), SINGLE OPN LIN 2276 360334-360354(1), SINGLE OPN LIN 2277 360334-360448(1), SINGLE OPN LIN 2278 360334-361064(1),
SINGLE OPN LIN 2279 360334-361788(1), SINGLE OPN LIN 2280 360338-361139(1), SINGLE OPN LIN 2281 360342-362499(1), SINGLE OPN LIN 2282 360354-361139(1), SINGLE OPN LIN 2283 360354-361265(1), SINGLE OPN LIN 2284 360354-361558(1), SINGLE OPN LIN 2285 360445-360450(1),
SINGLE OPN LIN 2286 360448-360486(1), SINGLE OPN LIN 2287 360448-361618(1), SINGLE OPN LIN 2288 360448-361666(1), SINGLE OPN LIN 2289 360448-364620(1), SINGLE OPN LIN 2290 360448-364621(2), SINGLE OPN LIN 2291 360448-364622(3), SINGLE OPN LIN 2292 360450-361580(1),
SINGLE OPN LIN 2293 360450-361618(1), SINGLE OPN LIN 2294 360454-361771(1), SINGLE OPN LIN 2295 360509-361246(1), SINGLE OPN LIN 2296 361064-361246(1), SINGLE OPN LIN 2297 361064-361666(1), SINGLE OPN LIN 2298 361113-361735(1), SINGLE OPN LIN 2299 361114-361735(1),
SINGLE OPN LIN 2300 361117-361246(1), SINGLE OPN LIN 2301 361265-361266(1), SINGLE OPN LIN 2302 361267-361558(1), SINGLE OPN LIN 2303 361558-361559(1), SINGLE OPN LIN 2304 361579-361580(1), SINGLE OPN LIN 2305 361603-361604(1), SINGLE OPN LIN 2306 361618-361619(1),
SINGLE OPN LIN 2307 361666-361667(1), SINGLE OPN LIN 2308 362058-362059(1), SINGLE OPN LIN 2309 362058-362061(1), SINGLE OPN LIN 2310 362058-363060(1), SINGLE OPN LIN 2311 362059-362060(1), SINGLE OPN LIN 2312 362060-362061(1), SINGLE OPN LIN 2313 362061-364614(1),
SINGLE OPN LIN 2314 362061-364615(2), SINGLE OPN LIN 2315 362061-364616(3), SINGLE OPN TIE 2316 360112-361287(1), SINGLE OPN TIE 2319 360334-360607(1), SINGLE OPN TIE 2320 360334-362060-362483(2), SINGLE OPN TIE 2321 360338-361553(1), SINGLE OPN TIE 2322 360338-361621(1),
SINGLE OPN TIE 2323 360342-361617(1), SINGLE OPN TIE 2324 360342-361731(1), SINGLE OPN TIE 2325 360352-360349(2), SINGLE OPN TIE 2326 360352-360382(1), SINGLE OPN TIE 2327 360352-360773(1), SINGLE OPN TIE 2328 360352-361128(1), SINGLE OPN TIE 2329 360352-361714(1),
SINGLE OPN TIE 2330 360352-361827(1), SINGLE OPN TIE 2331 360352-364121(1), SINGLE OPN TIE 2332 360352-364122(2), SINGLE OPN TIE 2333 360352-364221-364222(T1), SINGLE OPN TIE 2334 360352-364223-364224(T2), SINGLE OPN TIE 2335 360445-361542(1), SINGLE OPN TIE 2337 360454-361330(1),
SINGLE OPN TIE 2341 361113-360607(1), SINGLE OPN TIE 2342 361114-360332(1), SINGLE OPN TIE 2343 361114-360335(1), SINGLE OPN TIE 2344 361265-361827(1), SINGLE OPN TIE 2345 361267-360530(1), SINGLE OPN TIE 2348 361603-360607(1), SINGLE OPN LIN 2352 253006-253027(1),
SINGLE OPN LIN 2353 253013-253014(1), SINGLE OPN LIN 2354 253013-253014(2), SINGLE OPN LIN 2355 253013-253094(1), SINGLE OPN LIN 2356 253013-253094(2), SINGLE OPN LIN 2357 253014-253027(1), SINGLE OPN LIN 2358 253026-253027(1), SINGLE OPN LIN 2359 253026-253027(2),
SINGLE OPN LIN 2360 253027-253079(1), SINGLE OPN LIN 2361 253076-253077(1), SINGLE OPN LIN 2362 253077-253100(1), SINGLE OPN LIN 2363 253099-253100(1), SINGLE OPN LIN 2364 253099-253181(1), SINGLE OPN TIE 2366 253006-253005(1), SINGLE OPN TIE 2367 253006-253005(2),
SINGLE OPN TIE 2368 253006-253047(1), SINGLE OPN TIE 2369 253014-253310(1), SINGLE OPN TIE 2370 253026-238623(1), SINGLE OPN TIE 2371 253026-253002(1), SINGLE OPN TIE 2372 253026-253040(1), SINGLE OPN TIE 2373 253026-253062(1), SINGLE OPN TIE 2374 253026-253083(1),
SINGLE OPN TIE 2375 253026-253107(1), SINGLE OPN TIE 2376 253027-253248(1), SINGLE OPN TIE 2381 253077-253310(1), SINGLE OPN TIE 2382 253077-253352(1), SINGLE OPN TIE 2385 253079-253078(1), SINGLE OPN TIE 2386 253079-253078(2), SINGLE OPN TIE 2387 253094-253043(1),
SINGLE OPN TIE 2388 253094-253115(1), SINGLE OPN TIE 2389 253094-253131(1), SINGLE OPN TIE 2390 253094-253237(1), SINGLE OPN TIE 2391 253099-253322(1), SINGLE OPN TIE 2392 253099-253330(1), SINGLE OPN TIE 2393 253099-253335(1), SINGLE OPN TIE 2394 253099-253340(1),
SINGLE OPN TIE 2395 253100-245769(1), SINGLE OPN TIE 2396 253181-253201(1), SINGLE OPN LIN 2397 248005-248013(1), SINGLE OPN TIE 2398 248005-242528(1), SINGLE OPN TIE 2401 248005-248027-248026(1), SINGLE OPN TIE 2402 248005-248029-248028(1), SINGLE OPN TIE 2403 248005-248031-248030(1),
SINGLE OPN TIE 2404 248005-248033-248032(1), SINGLE OPN TIE 2405 248005-248035-248034(1), SINGLE OPN TIE 2406 248009-248008(SR), SINGLE OPN TIE 2411 248013-248000(1), SINGLE OPN TIE 2412 248013-248000(2), SINGLE OPN TIE 2413 248013-248001(1), SINGLE OPN TIE 2416 248013-250086(17),
SINGLE OPN TIE 2417 248013-250143(18), SINGLE OPN TIE 2418 249736-249754(1)

## Load Shed
LOAD BUS |  |  | CONTINGENCY | LOAD SHED(MW)
|  |  | BASE CASE | -
|  |  | SINGLE OPN LIN 1 339206-342769(1) | -
|  |  | SINGLE OPN LIN 2 339206-939132(1) | -
|  |  | SINGLE OPN LIN 3 341002-341443(1) | -
|  |  | SINGLE OPN LIN 4 341002-341752(1) | -
342181 | 2S ALBANY | 69 | SINGLE OPN LIN 5 341005-342181(1) | 7.995
|  |  | SINGLE OPN LIN 6 341005-342283(1) | -
|  |  | SINGLE OPN LIN 7 341005-342397(1) | -
|  |  | SINGLE OPN LIN 8 341008-342106(1) | -
|  |  | SINGLE OPN LIN 9 341008-342430(1) | -
341014 | 2ANNVILLE | 69 | SINGLE OPN LIN 10 341014-341017(1) | 4.3545
|  |  | SINGLE OPN LIN 11 341017-341428(1) | -
|  |  | SINGLE OPN LIN 12 341017-342391(1) | -
|  |  | SINGLE OPN LIN 13 341020-341782(1) | -
|  |  | SINGLE OPN LIN 14 341020-342538(1) | -
341029 | 2ASAHI M W | 69 | SINGLE OPN LIN 15 341029-341032(1) | 11.9039
|  |  | SINGLE OPN LIN 16 341032-341379(1) | -
|  |  | SINGLE OPN LIN 17 341032-342472(1) | -
341035 | 2BACON CRK | 69 | SINGLE OPN LIN 18 341035-341038(1) | 4.3674
|  |  | SINGLE OPN LIN 19 341038-341755(1) | -
|  |  | SINGLE OPN LIN 20 341038-342187(1) | -
341635 | 2HOLLOWAY | 69 | SINGLE OPN LIN 21 341041-341635(1) | 10.8215
|  |  | SINGLE OPN LIN 22 341041-341638(1) | -
|  |  | SINGLE OPN LIN 23 341041-342547(1) | -
|  |  | SINGLE OPN LIN 24 341044-341671(1) | -
|  |  | SINGLE OPN LIN 25 341044-342361(1) | -
341047 | 2BALLTOWN | 69 | SINGLE OPN LIN 26 341047-342424(1) | 11.9528
341050 | 2BANK LCK | 69 | SINGLE OPN LIN 27 341050-342295(1) | 13.3486
341053 | 2BARD SHOP | 69 | SINGLE OPN LIN 28 341053-341056(1) | 11.0844
|  |  | SINGLE OPN LIN 29 341056-341407(1) | -
|  |  | SINGLE OPN LIN 30 341056-342424(1) | -
|  |  | SINGLE OPN LIN 31 341059-341275(1) | -
|  |  | SINGLE OPN LIN 32 341059-341542(1) | -
|  |  | SINGLE OPN LIN 33 341059-341651(1) | -
|  |  | SINGLE OPN LIN 34 341059-342694(1) | -
341062 | 2BASS | 69 | SINGLE OPN LIN 35 341062-341269(1) | 4.6051
341065 | 2BEAM | 69 | SINGLE OPN LIN 36 341065-341068(1) | 8.1995
|  |  | SINGLE OPN LIN 37 341068-341215(1) | -
|  |  | SINGLE OPN LIN 38 341068-342253(1) | -
341074 | 2BEATTYV D | 69 | SINGLE OPN LIN 39 341071-341074(1) | 7.6723
341992 | 2OAKDALE | 69 | SINGLE OPN LIN 39 341071-341074(1) | 5.3401
|  |  | SINGLE OPN LIN 40 341071-341077(1) | -
|  |  | SINGLE OPN LIN 41 341071-342520(1) | -
341992 | 2OAKDALE | 69 | SINGLE OPN LIN 42 341074-341992(1) | 5.3401
|  |  | SINGLE OPN LIN 43 341077-341173(1) | -
|  |  | SINGLE OPN LIN 44 341080-341149(1) | -
|  |  | SINGLE OPN LIN 45 341080-342445(1) | -
|  |  | SINGLE OPN LIN 46 341089-342500(1) | -
341092 | 2BELLVIEW | 69 | SINGLE OPN LIN 47 341092-341095(1) | 5.1645
|  |  | SINGLE OPN LIN 48 341095-341164(1) | -
|  |  | SINGLE OPN LIN 49 341095-341227(1) | -
|  |  | SINGLE OPN LIN 50 341098-342433(1) | -
341104 | 2BIG BONE | 69 | SINGLE OPN LIN 51 341104-341107(1) | 3.3535
|  |  | SINGLE OPN LIN 52 341107-341164(1) | -
|  |  | SINGLE OPN LIN 53 341107-341917(1) | -
341110 | 2BIG CREEK | 69 | SINGLE OPN LIN 54 341110-341113(1) | 4.7334
341439 | 2ELK MT IP | 69 | SINGLE OPN LIN 54 341110-341113(1) | 4.7318
341439 | 2ELK MT IP | 69 | SINGLE OPN LIN 55 341110-341439(1) | 4.7318
341110 | 2BIG CREEK | 69 | SINGLE OPN LIN 56 341113-341464(1) | 4.7334
341439 | 2ELK MT IP | 69 | SINGLE OPN LIN 56 341113-341464(1) | 4.7318
342001 | 2ONEIDA | 69 | SINGLE OPN LIN 56 341113-341464(1) | 2.365
342001 | 2ONEIDA | 69 | SINGLE OPN LIN 57 341113-342001(1) | 2.365
341114 | 2BIG HILL | 69 | SINGLE OPN LIN 58 341114-341115(1) | 5.202
|  |  | SINGLE OPN LIN 59 341115-342223(1) | -
|  |  | SINGLE OPN LIN 60 341115-342346(1) | -
341116 | 2BIG WOODS | 69 | SINGLE OPN LIN 61 341116-341119(1) | 5.4642
|  |  | SINGLE OPN LIN 62 341119-341620(1) | -
|  |  | SINGLE OPN LIN 63 341119-342088(1) | -
341125 | 2BILL WELLS | 69 | SINGLE OPN LIN 64 341122-341125(1) | 7.6338
|  |  | SINGLE OPN LIN 65 341122-341692(1) | -
|  |  | SINGLE OPN LIN 66 341122-341860(1) | -
341134 | 2BLEVINS VAL | 69 | SINGLE OPN LIN 67 341131-341134(1) | 2.7272
|  |  | SINGLE OPN LIN 69 341131-342112(1) | -
|  |  | SINGLE OPN LIN 70 341137-341296(1) | -
|  |  | SINGLE OPN LIN 71 341137-341935(1) | -
341140 | 2BLUE G PW | 69 | SINGLE OPN LIN 72 341140-341143(1) | 11.2397
|  |  | SINGLE OPN LIN 73 341143-342019(1) | -
|  |  | SINGLE OPN LIN 74 341143-342508(1) | -
|  |  | SINGLE OPN LIN 75 341149-341272(1) | -
341152 | 2BONANZA | 69 | SINGLE OPN LIN 76 341152-341155(1) | 4.0496
|  |  | SINGLE OPN LIN 77 341155-341803(1) | -
|  |  | SINGLE OPN LIN 78 341155-341860(1) | -
|  |  | SINGLE OPN LIN 79 341158-341161(1) | -
|  |  | SINGLE OPN LIN 80 341158-341908(1) | -
|  |  | SINGLE OPN LIN 81 341161-342403(1) | -
341167 | 2BOONE DIST | 69 | SINGLE OPN LIN 82 341164-341167(1) | 12.5148
|  |  | SINGLE OPN LIN 83 341164-342388(1) | -
342466 | 2W R SMOOT | 69 | SINGLE OPN LIN 84 341164-342466(1) | 23.4435
|  |  | SINGLE OPN LIN 85 341164-342559(1) | -
341170 | 2BOONEVIL | 69 | SINGLE OPN LIN 86 341170-341173(1) | 4.449
|  |  | SINGLE OPN LIN 87 341173-342196(1) | -
|  |  | SINGLE OPN LIN 88 341179-341746(1) | -
|  |  | SINGLE OPN LIN 89 341179-342514(1) | -
|  |  | SINGLE OPN LIN 90 341185-341614(1) | -
|  |  | SINGLE OPN LIN 91 341185-342100(1) | -
|  |  | SINGLE OPN LIN 92 341188-341488(1) | -
|  |  | SINGLE OPN LIN 93 341188-341587(1) | -
|  |  | SINGLE OPN LIN 94 341194-342385(1) | -
|  |  | SINGLE OPN LIN 95 341194-342388(1) | -
|  |  | SINGLE OPN LIN 96 341197-341818(1) | -
|  |  | SINGLE OPN LIN 97 341197-342349(1) | -
|  |  | SINGLE OPN LIN 98 341200-341920(1) | -
|  |  | SINGLE OPN LIN 99 341200-342010(1) | -
341203 | 2BRONSTON | 69 | SINGLE OPN LIN 100 341203-341206(1) | 13.1724
|  |  | SINGLE OPN LIN 101 341206-341347(1) | -
|  |  | SINGLE OPN LIN 102 341206-341392(1) | -
341210 | 2BROUGHT TWN | 69 | SINGLE OPN LIN 103 341209-341210(1) | 4.4578
|  |  | SINGLE OPN LIN 104 341209-341617(1) | -
|  |  | SINGLE OPN LIN 105 341209-342367(1) | -
|  |  | SINGLE OPN LIN 106 341212-341774(1) | -
|  |  | SINGLE OPN LIN 107 341212-342500(1) | -
341281 | 2CEDAR GR | 69 | SINGLE OPN LIN 108 341215-341281(1) | 8.5817
342082 | 2PLEAS GRV | 69 | SINGLE OPN LIN 108 341215-341281(1) | 26.1472
|  |  | SINGLE OPN LIN 109 341215-341389(1) | -
|  |  | SINGLE OPN LIN 110 341215-342700(1) | -
|  |  | SINGLE OPN LIN 111 341218-341227(1) | -
|  |  | SINGLE OPN LIN 112 341218-341605(1) | -
341224 | 2BURLINGTN | 69 | SINGLE OPN LIN 113 341224-341227(1) | 8.1595
|  |  | SINGLE OPN LIN 114 341233-341974(1) | -
|  |  | SINGLE OPN LIN 115 341233-342286(1) | -
|  |  | SINGLE OPN LIN 116 341248-341608(1) | -
|  |  | SINGLE OPN LIN 117 341248-342520(1) | -
341251 | 2CANE RIDG | 69 | SINGLE OPN LIN 118 341251-341254(1) | 0.37481
|  |  | SINGLE OPN LIN 119 341254-341872(1) | -
|  |  | SINGLE OPN LIN 120 341254-342259(1) | -
341260 | 2CARSON | 69 | SINGLE OPN LIN 121 341260-342013(1) | 5.8918
341263 | 2CARTER CTY | 69 | SINGLE OPN LIN 122 341263-341266(1) | 3.7198
|  |  | SINGLE OPN LIN 123 341266-342034(1) | -
|  |  | SINGLE OPN LIN 124 341266-342475(1) | -
|  |  | SINGLE OPN LIN 125 341269-342064(1) | -
|  |  | SINGLE OPN LIN 126 341269-342703(1) | -
|  |  | SINGLE OPN LIN 127 341272-341275(1) | -
342238 | 2SEYMOUR | 69 | SINGLE OPN LIN 128 341275-342241(1) | 3.7942
342082 | 2PLEAS GRV | 69 | SINGLE OPN LIN 129 341281-342082(1) | 26.1472
|  |  | SINGLE OPN LIN 130 341287-341713(1) | -
|  |  | SINGLE OPN LIN 131 341287-342307(1) | -
|  |  | SINGLE OPN LIN 132 341287-342568(1) | -
341293 | 2CHAPLIN | 69 | SINGLE OPN LIN 133 341293-341296(1) | 1.4053
|  |  | SINGLE OPN LIN 134 341296-342262(1) | -
|  |  | SINGLE OPN LIN 135 341299-341989(1) | -
|  |  | SINGLE OPN LIN 136 341299-342124(1) | -
341302 | 2CLAY CITY | 69 | SINGLE OPN LIN 137 341302-341305(1) | 8.5542
|  |  | SINGLE OPN LIN 138 341305-341593(1) | -
|  |  | SINGLE OPN LIN 139 341305-341599(1) | -
341308 | 2CLAY LCK | 69 | SINGLE OPN LIN 140 341308-341314(1) | 6.1845
341308 | 2CLAY LCK | 69 | SINGLE OPN LIN 141 341311-341314(1) | 6.1845
|  |  | SINGLE OPN LIN 142 341311-342184(1) | -
|  |  | SINGLE OPN LIN 143 341311-342406(1) | -
|  |  | SINGLE OPN LIN 144 341317-341390(1) | -
|  |  | SINGLE OPN LIN 145 341320-341512(1) | -
|  |  | SINGLE OPN LIN 146 341323-341335(1) | -
|  |  | SINGLE OPN LIN 147 341323-341512(1) | -
|  |  | SINGLE OPN LIN 148 341323-342235(1) | -
|  |  | SINGLE OPN LIN 149 341326-341488(1) | -
|  |  | SINGLE OPN LIN 150 341326-342133(1) | -
341329 | 2COLESBURG | 69 | SINGLE OPN LIN 151 341329-341332(1) | 2.9494
|  |  | SINGLE OPN LIN 152 341332-341944(1) | -
|  |  | SINGLE OPN LIN 153 341332-342155(1) | -
341366 | 2COLUMB KU | 69 | SINGLE OPN LIN 154 341335-341370(1) | 6.29
341370 | 2COLUMB S KU | 69 | SINGLE OPN LIN 154 341335-341370(1) | 4.41
|  |  | SINGLE OPN LIN 155 341335-342436(1) | -
341338 | 2CONWAY | 69 | SINGLE OPN LIN 156 341338-341341(1) | 4.2596
|  |  | SINGLE OPN LIN 157 341341-342346(1) | -
|  |  | SINGLE OPN LIN 158 341341-342349(1) | -
341343 | 2CONTOWN | 69 | SINGLE OPN LIN 159 341342-341343(1) | 2.2548
|  |  | SINGLE OPN LIN 160 341342-341761(1) | -
|  |  | SINGLE OPN LIN 161 341342-342067(1) | -
|  |  | SINGLE OPN LIN 162 341344-341347(1) | -
|  |  | SINGLE OPN LIN 163 341344-342286(1) | -
|  |  | SINGLE OPN LIN 164 341344-342286(2) | -
|  |  | SINGLE OPN LIN 165 341344-342715(1) | -
341350 | 2CRESTON | 69 | SINGLE OPN LIN 166 341350-342067(1) | 5.7798
341353 | 2CROCKETT | 69 | SINGLE OPN LIN 167 341353-341356(1) | 3.3314
|  |  | SINGLE OPN LIN 168 341356-341653(1) | -
|  |  | SINGLE OPN LIN 169 341356-342265(1) | -
341359 | 2CROOKSVIL | 69 | SINGLE OPN LIN 170 341359-341362(1) | 5.895
342288 | 2SPEEDWELL | 69 | SINGLE OPN LIN 170 341359-341362(1) | 1.3
342288 | 2SPEEDWELL | 69 | SINGLE OPN LIN 171 341359-342288(1) | 1.3
|  |  | SINGLE OPN LIN 172 341362-341406(1) | -
|  |  | SINGLE OPN LIN 173 341362-341611(1) | -
341366 | 2COLUMB KU | 69 | SINGLE OPN LIN 174 341366-341370(1) | 6.29
|  |  | SINGLE OPN LIN 175 341377-341602(1) | -
|  |  | SINGLE OPN LIN 176 341377-342355(1) | -
|  |  | SINGLE OPN LIN 177 341379-342256(1) | -
|  |  | SINGLE OPN LIN 178 341380-341959(1) | -
|  |  | SINGLE OPN LIN 179 341380-341962(1) | -
|  |  | SINGLE OPN LIN 180 341380-342574(1) | -
341381 | 2DAV LANE | 69 | SINGLE OPN LIN 181 341381-341382(1) | 14
|  |  | SINGLE OPN LIN 182 341382-341734(1) | -
|  |  | SINGLE OPN LIN 183 341382-342451(1) | -
|  |  | SINGLE OPN LIN 184 341383-341467(1) | -
|  |  | SINGLE OPN LIN 185 341383-341965(1) | -
341386 | 2DEATSVIL | 69 | SINGLE OPN LIN 186 341386-341389(1) | 7.9864
|  |  | SINGLE OPN LIN 187 341389-341707(1) | -
341391 | 2DEFOE | 69 | SINGLE OPN LIN 188 341390-341391(1) | 4.021
|  |  | SINGLE OPN LIN 189 341390-341950(1) | -
|  |  | SINGLE OPN LIN 190 341392-341578(1) | -
|  |  | SINGLE OPN LIN 191 341392-342499(1) | -
|  |  | SINGLE OPN LIN 192 341392-342727(1) | -
341479 | 2S BOUND RD | 69 | SINGLE OPN LIN 193 341394-341479(1) | 6.5271
342151 | 2RINEYVILLE | 69 | SINGLE OPN LIN 194 341394-342151(1) | 5.6071
|  |  | SINGLE OPN LIN 195 341394-342157(1) | -
|  |  | SINGLE OPN LIN 196 341394-342274(1) | -
341398 | 2DOWNING | 69 | SINGLE OPN LIN 197 341398-341605(1) | 11.3406
341880 | 2MINEOLA PKE | 69 | SINGLE OPN LIN 197 341398-341605(1) | 12.222
341880 | 2MINEOLA PKE | 69 | SINGLE OPN LIN 198 341398-341880(1) | 12.222
341400 | 2DRAVO | 69 | SINGLE OPN LIN 199 341400-342091(1) | 2.641
341401 | 2DURO | 69 | SINGLE OPN LIN 200 341401-341842(1) | 8.9714
341401 | 2DURO | 69 | SINGLE OPN LIN 201 341404-341842(1) | 8.9714
341839 | 2MBUSA | 69 | SINGLE OPN LIN 201 341404-341842(1) | 14.5365
|  |  | SINGLE OPN LIN 202 341404-342295(1) | -
|  |  | SINGLE OPN LIN 203 341404-342388(1) | -
341405 | 2DUNCANNO LN | 69 | SINGLE OPN LIN 204 341405-341406(1) | 3.7451
|  |  | SINGLE OPN LIN 205 341407-342019(1) | -
341410 | 2E BERNSTADT | 69 | SINGLE OPN LIN 206 341410-341929(1) | 6.944
341416 | 2E PINE KNOT | 69 | SINGLE OPN LIN 207 341416-342076(1) | 4.2639
341422 | 2E SOMERSET | 69 | SINGLE OPN LIN 208 341419-341422(1) | 8.3699
|  |  | SINGLE OPN LIN 209 341419-341941(1) | -
|  |  | SINGLE OPN LIN 210 341419-341974(1) | -
341425 | 2EBERLE | 69 | SINGLE OPN LIN 211 341425-341428(1) | 4.738
|  |  | SINGLE OPN LIN 212 341428-341809(1) | -
341437 | 2EDMON IND P | 69 | SINGLE OPN LIN 213 341431-341434(1) | 1.5349
341680 | 2JB GALLOWAY | 69 | SINGLE OPN LIN 213 341431-341434(1) | 7.4175
|  |  | SINGLE OPN LIN 214 341431-341728(1) | -
|  |  | SINGLE OPN LIN 215 341431-342322(1) | -
341437 | 2EDMON IND P | 69 | SINGLE OPN LIN 216 341434-341437(1) | 1.5349
341680 | 2JB GALLOWAY | 69 | SINGLE OPN LIN 217 341434-341680(1) | 7.4175
341446 | 2ELLIOT CO P | 69 | SINGLE OPN LIN 218 341443-341446(1) | 10.6457
|  |  | SINGLE OPN LIN 219 341443-341953(1) | -
341449 | 2ELLIOTTVILL | 69 | SINGLE OPN LIN 220 341449-342163(1) | 6.2363
|  |  | SINGLE OPN LIN 221 341455-341458(1) | -
|  |  | SINGLE OPN LIN 222 341455-342274(1) | -
|  |  | SINGLE OPN LIN 223 341455-342379(1) | -
|  |  | SINGLE OPN LIN 224 341458-342340(1) | -
|  |  | SINGLE OPN LIN 225 341461-341797(1) | -
|  |  | SINGLE OPN LIN 226 341461-342310(1) | -
341572 | 2GREENBRIAR | 69 | SINGLE OPN LIN 227 341464-341569(1) | 7.3931
|  |  | SINGLE OPN LIN 228 341464-342391(1) | -
|  |  | SINGLE OPN LIN 229 341464-342730(1) | -
|  |  | SINGLE OPN LIN 230 341467-342580(1) | -
|  |  | SINGLE OPN LIN 231 341470-341473(1) | -
|  |  | SINGLE OPN LIN 232 341470-342511(1) | -
|  |  | SINGLE OPN LIN 233 341473-342115(1) | -
342193 | 2S FLOYD | 69 | SINGLE OPN LIN 234 341473-342193(1) | 7.0517
341899 | 2MT STERLING | 69 | SINGLE OPN LIN 235 341476-341899(1) | 4.504
341899 | 2MT STERLING | 69 | SINGLE OPN LIN 236 341476-342130(1) | 4.504
341485 | 2FOUR OAKS | 69 | SINGLE OPN LIN 237 341485-341488(1) | 6.5608
341550 | 2FALMOUTH KU | 69 | SINGLE OPN LIN 237 341485-341488(1) | 4.56
341550 | 2FALMOUTH KU | 69 | SINGLE OPN LIN 238 341485-341550(1) | 4.56
|  |  | SINGLE OPN LIN 239 341491-341548(1) | -
342037 | 2PARKWAY 1 | 69 | SINGLE OPN LIN 240 341491-342037(1) | 9.3281
342040 | 2PARKWAY 2 | 69 | SINGLE OPN LIN 240 341491-342037(1) | 3.3429
|  |  | SINGLE OPN LIN 241 341491-342043(1) | -
|  |  | SINGLE OPN LIN 242 341491-342049(1) | -
|  |  | SINGLE OPN LIN 243 341491-342732(1) | -
341497 | 2FREDRIKBRG | 69 | SINGLE OPN LIN 244 341494-341497(1) | 4.135
|  |  | SINGLE OPN LIN 245 341494-341935(1) | -
|  |  | SINGLE OPN LIN 246 341494-342508(1) | -
|  |  | SINGLE OPN LIN 247 341500-341644(1) | -
|  |  | SINGLE OPN LIN 248 341500-341824(1) | -
341506 | 2GAP OF RIDG | 69 | SINGLE OPN LIN 249 341503-341506(1) | 9.8439
|  |  | SINGLE OPN LIN 250 341503-341578(1) | -
|  |  | SINGLE OPN LIN 251 341503-341887(1) | -
341509 | 2GARLIN | 69 | SINGLE OPN LIN 252 341509-341512(1) | 5.8713
|  |  | SINGLE OPN LIN 253 341515-341732(1) | -
|  |  | SINGLE OPN LIN 254 341515-942410(1) | -
|  |  | SINGLE OPN LIN 255 341518-341521(1) | -
|  |  | SINGLE OPN LIN 256 341521-341806(1) | -
|  |  | SINGLE OPN LIN 257 341530-342043(1) | -
|  |  | SINGLE OPN LIN 258 341530-342445(1) | -
|  |  | SINGLE OPN LIN 259 341533-341632(1) | -
|  |  | SINGLE OPN LIN 260 341533-342307(1) | -
|  |  | SINGLE OPN LIN 261 341536-341623(1) | -
|  |  | SINGLE OPN LIN 262 341536-341989(1) | -
|  |  | SINGLE OPN LIN 263 341536-342088(1) | -
|  |  | SINGLE OPN LIN 264 341536-342589(1) | -
|  |  | SINGLE OPN LIN 265 341539-341686(1) | -
|  |  | SINGLE OPN LIN 266 341542-341548(1) | -
|  |  | SINGLE OPN LIN 267 341551-341587(1) | -
|  |  | SINGLE OPN LIN 268 341551-342298(1) | -
|  |  | SINGLE OPN LIN 269 341554-341752(1) | -
|  |  | SINGLE OPN LIN 270 341554-342034(1) | -
|  |  | SINGLE OPN LIN 271 341563-341575(1) | -
|  |  | SINGLE OPN LIN 272 341563-342325(1) | -
|  |  | SINGLE OPN LIN 273 341563-342733(1) | -
341572 | 2GREENBRIAR | 69 | SINGLE OPN LIN 274 341569-341572(1) | 7.3931
|  |  | SINGLE OPN LIN 275 341569-341806(1) | -
|  |  | SINGLE OPN LIN 276 341575-341854(1) | -
341581 | 2GREGORY RD | 69 | SINGLE OPN LIN 277 341578-341581(1) | 1.8519
341584 | 2GRIFFIN | 69 | SINGLE OPN LIN 278 341584-341587(1) | 7.6275
341590 | 2HARDWCRK | 69 | SINGLE OPN LIN 279 341590-341593(1) | 1.8746
|  |  | SINGLE OPN LIN 280 341593-342301(1) | -
341596 | 2HARGETT | 69 | SINGLE OPN LIN 281 341596-341599(1) | 3.9751
|  |  | SINGLE OPN LIN 282 341599-342370(1) | -
|  |  | SINGLE OPN LIN 283 341602-341872(1) | -
|  |  | SINGLE OPN LIN 284 341602-342280(1) | -
|  |  | SINGLE OPN LIN 285 341605-342595(1) | -
|  |  | SINGLE OPN LIN 286 341608-342313(1) | -
|  |  | SINGLE OPN LIN 287 341611-342103(1) | -
|  |  | SINGLE OPN LIN 288 341614-342520(1) | -
|  |  | SINGLE OPN LIN 289 341617-341896(1) | -
|  |  | SINGLE OPN LIN 290 341620-342163(1) | -
|  |  | SINGLE OPN LIN 291 341623-342052(1) | -
|  |  | SINGLE OPN LIN 292 341632-341800(1) | -
|  |  | SINGLE OPN LIN 293 341632-342316(1) | -
|  |  | SINGLE OPN LIN 294 341638-342199(1) | -
342460 | 2W NICHVIL | 69 | SINGLE OPN LIN 295 341638-342463(1) | 23.1559
341641 | 2HOMESTEAD S | 69 | SINGLE OPN LIN 296 341641-341887(1) | 14.1787
|  |  | SINGLE OPN LIN 297 341644-341683(1) | -
341647 | 2HORSE CV KU | 69 | SINGLE OPN LIN 298 341647-341650(1) | 46.06
341647 | 2HORSE CV KU | 69 | SINGLE OPN LIN 299 341650-341651(Z1) | 46.06
|  |  | SINGLE OPN LIN 300 341651-341914(1) | -
341656 | 2HOT MIX RD | 69 | SINGLE OPN LIN 301 341653-341656(1) | 5.3326
|  |  | SINGLE OPN LIN 302 341653-341890(1) | -
341659 | 2HT ADAMS | 69 | SINGLE OPN LIN 303 341659-341662(1) | 6.0761
|  |  | SINGLE OPN LIN 304 341662-341671(1) | -
|  |  | SINGLE OPN LIN 306 341665-341701(1) | -
|  |  | SINGLE OPN LIN 307 341665-341869(1) | -
|  |  | SINGLE OPN LIN 308 341665-342596(1) | -
|  |  | SINGLE OPN LIN 309 341671-342061(1) | -
341677 | 2INDEX | 69 | SINGLE OPN LIN 310 341677-341890(1) | 6.9677
|  |  | SINGLE OPN LIN 311 341683-342100(1) | -
341689 | 2JELLICO CRK | 69 | SINGLE OPN LIN 312 341686-341689(1) | 1.9129
|  |  | SINGLE OPN LIN 313 341686-342076(1) | -
341695 | 2JENNY WILEY | 69 | SINGLE OPN LIN 314 341692-341695(1) | 5.4657
|  |  | SINGLE OPN LIN 315 341692-342343(1) | -
|  |  | SINGLE OPN LIN 316 341701-342370(1) | -
341704 | 2JOE TICH | 69 | SINGLE OPN LIN 317 341704-341707(1) | 7.9884
|  |  | SINGLE OPN LIN 318 341707-342427(1) | -
341716 | 2KEAVY | 69 | SINGLE OPN LIN 319 341716-341722(1) | 10.7978
|  |  | SINGLE OPN LIN 320 341719-341740(1) | -
|  |  | SINGLE OPN LIN 321 341719-342073(1) | -
|  |  | SINGLE OPN LIN 322 341722-341740(1) | -
|  |  | SINGLE OPN LIN 323 341722-342187(1) | -
|  |  | SINGLE OPN LIN 324 341725-342007(1) | -
|  |  | SINGLE OPN LIN 325 341725-342058(1) | -
|  |  | SINGLE OPN LIN 326 341728-341854(1) | -
341731 | 2LANCASTER | 69 | SINGLE OPN LIN 327 341731-341732(1) | 5.5024
|  |  | SINGLE OPN LIN 328 341732-341959(1) | -
341737 | 2LAUR CO IP | 69 | SINGLE OPN LIN 329 341734-341737(1) | 9.26
|  |  | SINGLE OPN LIN 330 341734-341929(1) | -
|  |  | SINGLE OPN LIN 331 341740-342754(1) | -
|  |  | SINGLE OPN LIN 332 341746-342253(1) | -
|  |  | SINGLE OPN LIN 333 341749-342058(1) | -
|  |  | SINGLE OPN LIN 334 341749-342133(1) | -
341758 | 2LIBERT CHUR | 69 | SINGLE OPN LIN 335 341755-341758(1) | 4.8231
|  |  | SINGLE OPN LIN 336 341761-341767(1) | -
|  |  | SINGLE OPN LIN 337 341761-341896(1) | -
|  |  | SINGLE OPN LIN 338 341761-342760(1) | -
341764 | 2LIBERTY KU | 69 | SINGLE OPN LIN 339 341764-341767(1) | 7.68
|  |  | SINGLE OPN LIN 340 341767-342064(1) | -
341772 | 2LOGAN | 69 | SINGLE OPN LIN 341 341772-341774(1) | 13.452
|  |  | SINGLE OPN LIN 342 341774-341775(1) | -
|  |  | SINGLE OPN LIN 343 341775-342247(1) | -
|  |  | SINGLE OPN LIN 344 341776-342208(1) | -
|  |  | SINGLE OPN LIN 345 341776-342316(1) | -
341779 | 2LOW GAP | 69 | SINGLE OPN LIN 346 341779-341782(1) | 4.1103
|  |  | SINGLE OPN LIN 347 341782-342475(1) | -
341785 | 2LYMAN BW | 69 | SINGLE OPN LIN 348 341785-341788(1) | 7.0814
|  |  | SINGLE OPN LIN 349 341788-342155(1) | -
|  |  | SINGLE OPN LIN 350 341788-342379(1) | -
341791 | 2MACKVIL KU | 69 | SINGLE OPN LIN 351 341791-341794(1) | 0.45
|  |  | SINGLE OPN LIN 352 341794-341935(1) | -
|  |  | SINGLE OPN LIN 353 341794-342061(1) | -
|  |  | SINGLE OPN LIN 354 341797-342265(1) | -
|  |  | SINGLE OPN LIN 355 341800-342325(1) | -
|  |  | SINGLE OPN LIN 356 341803-342310(1) | -
|  |  | SINGLE OPN LIN 357 341803-342313(1) | -
341812 | 2MAPLESVILLE | 69 | SINGLE OPN LIN 358 341809-341812(1) | 5.784
|  |  | SINGLE OPN LIN 359 341809-341929(1) | -
341815 | 2MARETBURG | 69 | SINGLE OPN LIN 360 341815-341818(1) | 6.4511
|  |  | SINGLE OPN LIN 361 341818-342472(1) | -
341821 | 2MARIBA | 69 | SINGLE OPN LIN 362 341821-341824(1) | 4.525
|  |  | SINGLE OPN LIN 363 341824-341833(1) | -
341827 | 2MARTIN CO | 69 | SINGLE OPN LIN 364 341827-342343(1) | 4.7105
341830 | 2MAYTOWN | 69 | SINGLE OPN LIN 365 341830-341833(1) | 3.9033
|  |  | SINGLE OPN LIN 366 341833-341890(1) | -
|  |  | SINGLE OPN LIN 367 341836-341953(1) | -
|  |  | SINGLE OPN LIN 368 341836-342265(1) | -
341839 | 2MBUSA | 69 | SINGLE OPN LIN 369 341839-341842(1) | 14.5365
|  |  | SINGLE OPN LIN 371 341845-342490(1) | -
|  |  | SINGLE OPN LIN 372 341845-342778(1) | -
|  |  | SINGLE OPN LIN 373 341848-342223(1) | -
|  |  | SINGLE OPN LIN 374 341848-342391(1) | -
341851 | 2MCKINNEY | 69 | SINGLE OPN LIN 375 341851-341854(1) | 4.4445
|  |  | SINGLE OPN LIN 376 341857-342406(1) | -
341863 | 2MIDDLE CRK | 69 | SINGLE OPN LIN 377 341860-341863(1) | 5.746
341875 | 2MILLER HUNT | 69 | SINGLE OPN LIN 378 341869-341875(1) | 2.2498
|  |  | SINGLE OPN LIN 379 341869-342259(1) | -
341878 | 2MILLERSB EK | 69 | SINGLE OPN LIN 380 341872-341878(1) | 3.855
|  |  | SINGLE OPN LIN 381 341887-342268(1) | -
341893 | 2MT OLIVE | 69 | SINGLE OPN LIN 382 341893-341896(1) | 4.6349
|  |  | SINGLE OPN LIN 383 341908-341914(1) | -
341911 | 2MUNFVIL KU | 69 | SINGLE OPN LIN 384 341911-341914(1) | 6.11
|  |  | SINGLE OPN LIN 385 341917-341998(1) | -
|  |  | SINGLE OPN LIN 386 341920-341998(1) | -
342502 | 2WILLIAMSTWN | 69 | SINGLE OPN LIN 387 341920-342502(1) | 12.2435
|  |  | SINGLE OPN LIN 388 341923-342091(1) | -
|  |  | SINGLE OPN LIN 389 341923-342280(1) | -
|  |  | SINGLE OPN LIN 390 341935-342208(1) | -
|  |  | SINGLE OPN LIN 391 341938-342505(1) | -
|  |  | SINGLE OPN LIN 392 341938-342526(1) | -
341947 | 2NELSON VAL | 69 | SINGLE OPN LIN 393 341941-341947(1) | 5.5639
|  |  | SINGLE OPN LIN 394 341941-341971(1) | -
|  |  | SINGLE OPN LIN 395 341944-342424(1) | -
|  |  | SINGLE OPN LIN 396 341944-342514(1) | -
|  |  | SINGLE OPN LIN 397 341950-342007(1) | -
342229 | 2SANDY HOOK | 69 | SINGLE OPN LIN 398 341953-342229(1) | 3.5476
|  |  | SINGLE OPN LIN 399 341962-342361(1) | -
|  |  | SINGLE OPN LIN 400 341965-342199(1) | -
|  |  | SINGLE OPN LIN 401 341971-342115(1) | -
|  |  | SINGLE OPN LIN 402 341974-342256(1) | -
341977 | 2OAK HILL | 69 | SINGLE OPN LIN 403 341977-341983(1) | 6.5887
|  |  | SINGLE OPN LIN 404 341980-341983(1) | -
|  |  | SINGLE OPN LIN 405 341980-342286(1) | -
|  |  | SINGLE OPN LIN 406 341983-342469(1) | -
341986 | 2OAK RIDGE | 69 | SINGLE OPN LIN 407 341986-341989(1) | 4.6709
|  |  | SINGLE OPN LIN 408 342000-342703(1) | -
|  |  | SINGLE OPN LIN 409 342000-342760(1) | -
|  |  | SINGLE OPN LIN 410 342007-342008(1) | -
|  |  | SINGLE OPN LIN 411 342007-342010(1) | -
341260 | 2CARSON | 69 | SINGLE OPN LIN 412 342007-342013(1) | 5.8918
342016 | 2OWENS IL | 69 | SINGLE OPN LIN 413 342016-342019(1) | 7.503
342025 | 2OWINGVIL KU | 69 | SINGLE OPN LIN 414 342022-342025(1) | 9.53
|  |  | SINGLE OPN LIN 415 342022-342052(1) | -
|  |  | SINGLE OPN LIN 416 342022-342112(1) | -
342031 | 2PACTOLUS | 69 | SINGLE OPN LIN 417 342031-342034(1) | 8.8816
342040 | 2PARKWAY 2 | 69 | SINGLE OPN LIN 418 342037-342040(1) | 3.3429
|  |  | SINGLE OPN LIN 419 342049-342161(1) | -
|  |  | SINGLE OPN LIN 420 342049-342319(1) | -
|  |  | SINGLE OPN LIN 421 342067-342505(1) | -
342070 | 2PINE GROVE | 69 | SINGLE OPN LIN 422 342070-342073(1) | 9.8481
|  |  | SINGLE OPN LIN 423 342073-342451(1) | -
342085 | 2PLUMMR L | 69 | SINGLE OPN LIN 425 342085-342088(1) | 4.0531
|  |  | SINGLE OPN LIN 426 342091-342124(1) | -
|  |  | SINGLE OPN LIN 427 342091-342634(1) | -
342097 | 2POWEL TAYL | 69 | SINGLE OPN LIN 428 342097-342184(1) | 5.6222
|  |  | SINGLE OPN LIN 429 342100-342301(1) | -
|  |  | SINGLE OPN LIN 430 342100-342637(1) | -
|  |  | SINGLE OPN LIN 431 342103-342106(1) | -
342109 | 2PRESTON | 69 | SINGLE OPN LIN 432 342109-342112(1) | 1.5083
|  |  | SINGLE OPN LIN 433 342115-342787(1) | -
342118 | 2RADCLIFF | 69 | SINGLE OPN LIN 434 342118-342121(1) | 7.6513
342328 | 2T BROWN LOG | 69 | SINGLE OPN LIN 435 342121-342328(1) | 7.5424
342118 | 2RADCLIFF | 69 | SINGLE OPN LIN 436 342121-342415(1) | 7.6513
342328 | 2T BROWN LOG | 69 | SINGLE OPN LIN 436 342121-342415(1) | 7.5424
|  |  | SINGLE OPN LIN 437 342127-342265(1) | -
|  |  | SINGLE OPN LIN 438 342127-342421(1) | -
341899 | 2MT STERLING | 69 | SINGLE OPN LIN 439 342130-342259(1) | 4.504
342130 | 2REID VILLAG | 69 | SINGLE OPN LIN 439 342130-342259(1) | 3.2944
|  |  | SINGLE OPN LIN 441 342133-342640(1) | -
342136 | 2REVELO KU | 69 | SINGLE OPN LIN 442 342136-342139(1) | 1.8
342145 | 2RICHARDSON | 69 | SINGLE OPN LIN 443 342145-342487(1) | 13.5187
342154 | 2ROANOKE | 69 | SINGLE OPN LIN 444 342154-342155(1) | 3.4896
342118 | 2RADCLIFF | 69 | SINGLE OPN LIN 445 342157-342418(1) | 7.6513
342328 | 2T BROWN LOG | 69 | SINGLE OPN LIN 445 342157-342418(1) | 7.5424
342418 | 2VINE GROVE | 69 | SINGLE OPN LIN 445 342157-342418(1) | 8.2029
342160 | 2ROSEVILLE | 69 | SINGLE OPN LIN 446 342160-342161(1) | 7.0525
|  |  | SINGLE OPN LIN 447 342161-342334(1) | -
|  |  | SINGLE OPN LIN 448 342163-342649(1) | -
|  |  | SINGLE OPN LIN 449 342166-342169(1) | -
342172 | 2RUSS SPR EK | 69 | SINGLE OPN LIN 450 342166-342172(1) | 11.0494
|  |  | SINGLE OPN LIN 451 342166-342235(1) | -
342175 | 2RUSS SPR KU | 69 | SINGLE OPN LIN 452 342169-342175(1) | 6.4
|  |  | SINGLE OPN LIN 453 342169-342178(1) | -
|  |  | SINGLE OPN LIN 454 342178-342232(1) | -
|  |  | SINGLE OPN LIN 455 342178-342793(1) | -
|  |  | SINGLE OPN LIN 456 342184-342262(1) | -
|  |  | SINGLE OPN LIN 457 342186-342424(1) | -
|  |  | SINGLE OPN LIN 458 342186-342427(1) | -
|  |  | SINGLE OPN LIN 459 342196-342391(1) | -
342202 | 2S JESSAMINE | 69 | SINGLE OPN LIN 460 342199-342202(1) | 14.9115
342211 | 2S SPRINGFLD | 69 | SINGLE OPN LIN 461 342208-342211(1) | 4.6495
342214 | 2SALEM EK | 69 | SINGLE OPN LIN 462 342214-342217(1) | 10.2212
|  |  | SINGLE OPN LIN 463 342217-342481(1) | -
|  |  | SINGLE OPN LIN 464 342217-342505(1) | -
342220 | 2SAND GAP | 69 | SINGLE OPN LIN 465 342220-342223(1) | 2.7435
|  |  | SINGLE OPN LIN 466 342235-342481(1) | -
342238 | 2SEYMOUR | 69 | SINGLE OPN LIN 467 342238-342241(1) | 3.7942
|  |  | SINGLE OPN LIN 468 342247-342248(1) | -
342410 | 2VEECHDALE | 69 | SINGLE OPN LIN 469 342247-342410(1) | 5.1171
|  |  | SINGLE OPN LIN 470 342247-342808(1) | -
342250 | 2SHEPHEVIL | 69 | SINGLE OPN LIN 471 342250-342253(1) | 20.8315
|  |  | SINGLE OPN LIN 472 342265-342658(1) | -
|  |  | SINGLE OPN LIN 473 342268-342478(1) | -
342271 | 2SMITHRSVIL | 69 | SINGLE OPN LIN 474 342271-342274(1) | 13.9816
342277 | 2SNOW | 69 | SINGLE OPN LIN 475 342277-342283(1) | 9.8435
|  |  | SINGLE OPN LIN 476 342283-342322(1) | -
|  |  | SINGLE OPN LIN 477 342286-342287(1) | -
|  |  | SINGLE OPN LIN 478 342292-342295(1) | -
|  |  | SINGLE OPN LIN 479 342292-342298(1) | -
|  |  | SINGLE OPN LIN 480 342292-342667(1) | -
|  |  | SINGLE OPN LIN 481 342307-342403(1) | -
342412 | 2VERTREES | 69 | SINGLE OPN LIN 482 342307-342412(1) | 5.8907
|  |  | SINGLE OPN LIN 483 342319-342322(1) | -
|  |  | SINGLE OPN LIN 484 342319-342334(1) | -
|  |  | SINGLE OPN LIN 485 342322-342436(1) | -
|  |  | SINGLE OPN LIN 486 342322-342814(1) | -
342337 | 2THARP | 69 | SINGLE OPN LIN 487 342337-342340(1) | 10.0175
|  |  | SINGLE OPN LIN 488 342343-342421(1) | -
|  |  | SINGLE OPN LIN 489 342349-342433(1) | -
342352 | 2THREE M | 69 | SINGLE OPN LIN 490 342352-342355(1) | 19.4904
342358 | 2TODDVILLE | 69 | SINGLE OPN LIN 491 342358-342361(1) | 4.2681
342364 | 2TOMM GOOC | 69 | SINGLE OPN LIN 492 342364-342367(1) | 14.7257
|  |  | SINGLE OPN LIN 493 342367-942410(1) | -
342382 | 2TUNNEL HILL | 69 | SINGLE OPN LIN 494 342379-342382(1) | 16.3905
|  |  | SINGLE OPN LIN 495 342385-342487(1) | -
|  |  | SINGLE OPN LIN 496 342391-342820(1) | -
342394 | 2UPCHURCH | 69 | SINGLE OPN LIN 497 342394-342397(1) | 8.1682
|  |  | SINGLE OPN LIN 498 342397-342532(1) | -
342400 | 2UPTON | 69 | SINGLE OPN LIN 499 342400-342403(1) | 3.4103
342118 | 2RADCLIFF | 69 | SINGLE OPN LIN 500 342415-342418(1) | 7.6513
342328 | 2T BROWN LOG | 69 | SINGLE OPN LIN 500 342415-342418(1) | 7.5424
|  |  | SINGLE OPN LIN 501 342430-342433(1) | -
|  |  | SINGLE OPN LIN 502 342430-342691(1) | -
342439 | 2W COLUMBIA | 69 | SINGLE OPN LIN 503 342436-342439(1) | 5.8725
342442 | 2W GLASGOW | 69 | SINGLE OPN LIN 504 342442-342445(1) | 12.7509
342460 | 2W NICHVIL | 69 | SINGLE OPN LIN 505 342460-342463(1) | 23.1559
|  |  | SINGLE OPN LIN 506 342469-342526(1) | -
|  |  | SINGLE OPN LIN 507 342472-342511(1) | -
|  |  | SINGLE OPN LIN 508 342478-342532(1) | -
342529 | 2ZULA | 69 | SINGLE OPN LIN 509 342478-342535(1) | 8.451
|  |  | SINGLE OPN LIN 510 342478-342823(1) | -
342484 | 2WEBB CR RDS | 69 | SINGLE OPN LIN 511 342481-342484(1) | 5.4721
342493 | 2WHITLY C KU | 69 | SINGLE OPN LIN 512 342490-342493(1) | 3.81
|  |  | SINGLE OPN LIN 513 342490-342499(1) | -
342496 | 2WIBORG | 69 | SINGLE OPN LIN 514 342496-342499(1) | 8.0737
342523 | 2ZOLLICOF | 69 | SINGLE OPN LIN 515 342523-342526(1) | 3.8925
342529 | 2ZULA | 69 | SINGLE OPN LIN 516 342529-342535(1) | 8.451
|  |  | SINGLE OPN LIN 517 342538-342616(1) | -
|  |  | SINGLE OPN LIN 518 342541-342544(1) | -
|  |  | SINGLE OPN LIN 519 342541-342556(1) | -
|  |  | SINGLE OPN LIN 520 342541-342580(1) | -
|  |  | SINGLE OPN LIN 521 342541-342631(1) | -
|  |  | SINGLE OPN LIN 522 342541-342829(1) | -
|  |  | SINGLE OPN LIN 523 342550-342559(1) | -
|  |  | SINGLE OPN LIN 524 342550-342640(1) | -
342553 | 4BECKNERV | 138 | SINGLE OPN LIN 525 342553-342556(1) | 1.593
|  |  | SINGLE OPN LIN 526 342556-342565(1) | -
|  |  | SINGLE OPN LIN 527 342559-342646(1) | -
|  |  | SINGLE OPN LIN 528 342559-342673(1) | -
|  |  | SINGLE OPN LIN 529 342565-342574(1) | -
|  |  | SINGLE OPN LIN 530 342571-342589(1) | -
|  |  | SINGLE OPN LIN 531 342571-342649(1) | -
|  |  | SINGLE OPN LIN 532 342574-342596(1) | -
|  |  | SINGLE OPN LIN 533 342574-342676(1) | -
|  |  | SINGLE OPN LIN 534 342577-342607(1) | -
|  |  | SINGLE OPN LIN 535 342577-342676(1) | -
|  |  | SINGLE OPN LIN 536 342577-342691(1) | -
|  |  | SINGLE OPN LIN 537 342583-342589(1) | -
|  |  | SINGLE OPN LIN 538 342583-342664(1) | -
342587 | 1GALLATIN CO | 34.5 | SINGLE OPN LIN 539 342586-342587(1) | 23.73
|  |  | SINGLE OPN LIN 540 342586-342673(1) | -
|  |  | SINGLE OPN LIN 541 342589-342634(1) | -
|  |  | SINGLE OPN LIN 542 342596-342607(1) | -
342598 | 4INLAND C T | 138 | SINGLE OPN LIN 543 342598-342664(1) | 31.2332
342601 | 4JACKSNVIL | 138 | SINGLE OPN LIN 544 342601-342604(1) | 3.3691
|  |  | SINGLE OPN LIN 545 342604-342631(1) | -
|  |  | SINGLE OPN LIN 546 342604-342640(1) | -
|  |  | SINGLE OPN LIN 547 342607-342610(1) | -
|  |  | SINGLE OPN LIN 548 342607-342613(1) | -
|  |  | SINGLE OPN LIN 549 342607-342637(1) | -
|  |  | SINGLE OPN LIN 550 342607-342688(1) | -
|  |  | SINGLE OPN LIN 551 342610-342832(1) | -
|  |  | SINGLE OPN LIN 552 342613-342832(1) | -
342625 | 4MAYSVIL IND | 138 | SINGLE OPN LIN 553 342622-342625(1) | 8.0269
|  |  | SINGLE OPN LIN 554 342622-342634(1) | -
|  |  | SINGLE OPN LIN 555 342622-342664(1) | -
|  |  | SINGLE OPN LIN 556 342637-342784(1) | -
|  |  | SINGLE OPN LIN 557 342640-342664(1) | -
342643 | 4RICHWOOD | 138 | SINGLE OPN LIN 558 342643-342646(1) | 11.3427
|  |  | SINGLE OPN LIN 559 342646-342667(1) | -
|  |  | SINGLE OPN LIN 560 342649-342658(1) | -
|  |  | SINGLE OPN LIN 561 342661-342664(1) | -
|  |  | SINGLE OPN LIN 562 342664-342667(1) | -
|  |  | SINGLE OPN LIN 563 342664-342838(1) | -
|  |  | SINGLE OPN LIN 564 342664-342838(2) | -
|  |  | SINGLE OPN LIN 565 342664-342838(3) | -
342670 | 4STERLING | 138 | SINGLE OPN LIN 566 342670-342673(1) | 6.9793
342679 | 4THREE FORKS | 138 | SINGLE OPN LIN 567 342676-342679(1) | 3.0944
342685 | 4UNION CITY | 138 | SINGLE OPN LIN 568 342685-342688(1) | 6.4748
|  |  | SINGLE OPN LIN 569 342694-342814(1) | -
|  |  | SINGLE OPN LIN 570 342697-342780(1) | -
|  |  | SINGLE OPN LIN 571 342700-342819(1) | -
|  |  | SINGLE OPN LIN 572 342703-342769(1) | -
|  |  | SINGLE OPN LIN 573 342715-342718(1) | -
|  |  | SINGLE OPN LIN 574 342715-342790(1) | -
|  |  | SINGLE OPN LIN 575 342715-342799(1) | -
|  |  | SINGLE OPN LIN 576 342718-342727(1) | -
|  |  | SINGLE OPN LIN 577 342718-342757(1) | -
342721 | 5DARWIN TH | 161 | SINGLE OPN LIN 578 342721-342724(1) | 15.3905
|  |  | SINGLE OPN LIN 579 342724-342766(1) | -
|  |  | SINGLE OPN LIN 580 342724-342808(1) | -
|  |  | SINGLE OPN LIN 581 342730-342820(1) | -
|  |  | SINGLE OPN LIN 582 342733-342814(1) | -
|  |  | SINGLE OPN LIN 583 342733-342817(1) | -
342739 | 5GREEN HALL | 161 | SINGLE OPN LIN 584 342736-342739(1) | 2.6482
|  |  | SINGLE OPN LIN 585 342736-342820(1) | -
342742 | 5JABEZ | 161 | SINGLE OPN LIN 586 342742-342745(1) | 4.1686
|  |  | SINGLE OPN LIN 587 342745-342751(1) | -
|  |  | SINGLE OPN LIN 588 342745-342799(1) | -
342748 | 5JAMESTOWN | 161 | SINGLE OPN LIN 589 342748-342751(1) | 6.8602
|  |  | SINGLE OPN LIN 590 342751-342796(1) | -
|  |  | SINGLE OPN LIN 591 342754-342757(1) | -
|  |  | SINGLE OPN LIN 592 342754-342781(1) | -
|  |  | SINGLE OPN LIN 593 342760-342790(1) | -
342763 | 5LITTLE MT | 161 | SINGLE OPN LIN 594 342763-342766(1) | 5.1178
|  |  | SINGLE OPN LIN 595 342766-342819(1) | -
|  |  | SINGLE OPN LIN 596 342769-342770(1) | -
|  |  | SINGLE OPN LIN 597 342769-342775(1) | -
342772 | 5MARION IP | 161 | SINGLE OPN LIN 598 342772-342797(1) | 7.3059
342772 | 5MARION IP | 161 | SINGLE OPN LIN 599 342775-342797(1) | 7.3059
342798 | 5S MARION IP | 161 | SINGLE OPN LIN 599 342775-342797(1) | 30.4021
|  |  | SINGLE OPN LIN 600 342775-342805(1) | -
342779 | 5MILLER CRK | 161 | SINGLE OPN LIN 601 342779-342780(1) | 3.1325
|  |  | SINGLE OPN LIN 602 342780-342784(1) | -
|  |  | SINGLE OPN LIN 603 342781-342820(1) | -
|  |  | SINGLE OPN LIN 604 342787-342790(1) | -
|  |  | SINGLE OPN LIN 605 342793-342796(1) | -
342798 | 5S MARION IP | 161 | SINGLE OPN LIN 606 342797-342798(1) | 30.4021
342802 | 5SALOMA | 161 | SINGLE OPN LIN 607 342802-342805(1) | 12.0099
|  |  | SINGLE OPN LIN 608 342805-342817(1) | -
342818 | 5TAYLORSVILL | 161 | SINGLE OPN LIN 609 342818-342819(1) | 10.0637
|  |  | SINGLE OPN LIN 610 342829-342835(1) | -
|  |  | SINGLE OPN LIN 611 342832-342835(1) | -
|  |  | SINGLE OPN LIN 612 342832-342841(1) | -
|  |  | SINGLE OPN LIN 613 342835-342838(1) | -
|  |  | SINGLE OPN LIN 614 942410-942411(1) | -
|  |  | SINGLE OPN LIN 615 942411-942412(1) | -
|  |  | SINGLE OPN TIE 616 341020-243725(1) | -
|  |  | SINGLE OPN TIE 617 341071-324430(1) | -
|  |  | SINGLE OPN TIE 618 341089-325102(1) | -
|  |  | SINGLE OPN TIE 619 341161-324213(1) | -
|  |  | SINGLE OPN TIE 620 341188-324463(1) | -
|  |  | SINGLE OPN TIE 621 341188-324722(1) | -
|  |  | SINGLE OPN TIE 622 341317-324474(1) | -
|  |  | SINGLE OPN TIE 623 341320-324830(1) | -
|  |  | SINGLE OPN TIE 624 341406-324530(1) | -
|  |  | SINGLE OPN TIE 625 341407-324425(1) | -
243721 | 05FALCON | 69 | SINGLE OPN TIE 626 341461-243721(Z1) | 10.79
|  |  | SINGLE OPN TIE 627 341515-324600(1) | -
|  |  | SINGLE OPN TIE 628 341539-324784(1) | -
243726 | 05GRAYSO | 69 | SINGLE OPN TIE 629 341554-243726(1) | 9.905
|  |  | SINGLE OPN TIE 630 341563-324554(1) | -
|  |  | SINGLE OPN TIE 631 341605-251579(1) | -
|  |  | SINGLE OPN TIE 632 341608-243812(Z1) | -
|  |  | SINGLE OPN TIE 633 341632-324575(1) | -
|  |  | SINGLE OPN TIE 634 341632-324660(1) | -
|  |  | SINGLE OPN TIE 635 341713-324519(1) | -
|  |  | SINGLE OPN TIE 636 341740-324576(1) | -
|  |  | SINGLE OPN TIE 637 341752-243737(Z1) | -
|  |  | SINGLE OPN TIE 638 341755-324527(1) | -
|  |  | SINGLE OPN TIE 639 341890-246973(Z1) | -
|  |  | SINGLE OPN TIE 640 341923-324717(1) | -
|  |  | SINGLE OPN TIE 641 341923-325019(1) | -
|  |  | SINGLE OPN TIE 642 341929-324662(1) | -
|  |  | SINGLE OPN TIE 643 341935-324736(1) | -
|  |  | SINGLE OPN TIE 644 341944-324288(1) | -
|  |  | SINGLE OPN TIE 645 342007-324455(1) | -
|  |  | SINGLE OPN TIE 646 342008-324290(1) | -
342055 | 2PELFREY | 69 | SINGLE OPN TIE 647 342055-243742(1) | 3.5497
|  |  | SINGLE OPN TIE 648 342058-324951(1) | -
|  |  | SINGLE OPN TIE 649 342133-324492(1) | -
|  |  | SINGLE OPN TIE 650 342157-324708(1) | -
|  |  | SINGLE OPN TIE 651 342184-324445(1) | -
|  |  | SINGLE OPN TIE 652 342184-324445(2) | -
342218 | 2SALT LICK | 138 | SINGLE OPN TIE 653 342218-247897(Z1) | 4.2393
|  |  | SINGLE OPN TIE 654 342232-324787(1) | -
|  |  | SINGLE OPN TIE 655 342248-324718(1) | -
|  |  | SINGLE OPN TIE 656 342287-324531(1) | -
|  |  | SINGLE OPN TIE 657 342287-324737(1) | -
|  |  | SINGLE OPN TIE 658 342307-324509(1) | -
|  |  | SINGLE OPN TIE 659 342340-324519(1) | -
|  |  | SINGLE OPN TIE 660 342343-246971(1) | -
342454 | 2W M SMITH | 69 | SINGLE OPN TIE 661 342454-251315(1) | 3.651
|  |  | SINGLE OPN TIE 662 342487-250148(1) | -
|  |  | SINGLE OPN TIE 663 342538-243688(1) | -
|  |  | SINGLE OPN TIE 664 342544-324275(1) | -
|  |  | SINGLE OPN TIE 665 342547-324210(1) | -
|  |  | SINGLE OPN TIE 666 342559-250054(1) | -
|  |  | SINGLE OPN TIE 667 342565-325925(1) | -
|  |  | SINGLE OPN TIE 668 342568-324047(1) | -
|  |  | SINGLE OPN TIE 669 342568-324261(1) | -
|  |  | SINGLE OPN TIE 670 342577-324247(1) | -
|  |  | SINGLE OPN TIE 671 342577-324248(1) | -
|  |  | SINGLE OPN TIE 672 342586-324253(1) | -
|  |  | SINGLE OPN TIE 673 342595-250152(1) | -
|  |  | SINGLE OPN TIE 674 342607-342918(1) | -
|  |  | SINGLE OPN TIE 675 342607-342921(1) | -
|  |  | SINGLE OPN TIE 676 342607-342924(1) | -
|  |  | SINGLE OPN TIE 677 342607-342927(1) | -
|  |  | SINGLE OPN TIE 678 342607-342930(1) | -
|  |  | SINGLE OPN TIE 679 342607-342933(1) | -
|  |  | SINGLE OPN TIE 680 342607-342936(1) | -
|  |  | SINGLE OPN TIE 681 342616-342948(1) | -
|  |  | SINGLE OPN TIE 682 342631-324328(1) | -
|  |  | SINGLE OPN TIE 683 342649-324302(1) | -
|  |  | SINGLE OPN TIE 684 342661-324267(1) | -
342957 | 1SPURLK1G | 22 | SINGLE OPN TIE 685 342664-342957(1) | 44
|  |  | SINGLE OPN TIE 686 342688-324276(1) | -
|  |  | SINGLE OPN TIE 687 342697-324138(1) | -
|  |  | SINGLE OPN TIE 688 342697-324430(1) | -
|  |  | SINGLE OPN TIE 689 342700-326975(1) | -
|  |  | SINGLE OPN TIE 690 342700-326998(1) | -
|  |  | SINGLE OPN TIE 691 342718-324141(1) | -
|  |  | SINGLE OPN TIE 692 342732-361603(1) | -
|  |  | SINGLE OPN TIE 693 342736-324138(1) | -
|  |  | SINGLE OPN TIE 694 342757-342945(1) | -
|  |  | SINGLE OPN TIE 695 342770-324271(1) | -
|  |  | SINGLE OPN TIE 696 342778-360473(1) | -
|  |  | SINGLE OPN TIE 697 342778-360486(1) | -
|  |  | SINGLE OPN TIE 698 342778-361579(1) | -
|  |  | SINGLE OPN TIE 699 342781-324688(1) | -
|  |  | SINGLE OPN TIE 700 342796-360448(1) | -
|  |  | SINGLE OPN TIE 701 342814-360334(1) | -
|  |  | SINGLE OPN TIE 702 342814-361788(1) | -
|  |  | SINGLE OPN TIE 703 342817-325921(1) | -
|  |  | SINGLE OPN TIE 704 342823-360486(1) | -
342939 | 1JKCT 9G | 13.8 | SINGLE OPN TIE 705 342832-342939-342942(1) | 2.5
342942 | 1JKCT 10G | 13.8 | SINGLE OPN TIE 705 342832-342939-342942(1) | 3.5
|  |  | SINGLE OPN TIE 706 342838-249581(1) | -
|  |  | SINGLE OPN TIE 707 342838-253077(1) | -
342960 | 1SPURLK2G | 22 | SINGLE OPN TIE 708 342838-342960(1) | 45
342963 | 1SPURLK3G | 18 | SINGLE OPN TIE 709 342838-342963(1) | 20
342966 | 1SPURLK4G | 18 | SINGLE OPN TIE 710 342838-342966(1) | 38
|  |  | SINGLE OPN TIE 711 342841-325074(Z1) | -
|  |  | SINGLE OPN TIE 712 342844-384157(1) | -
|  |  | SINGLE OPN TIE 713 342847-243205(1) | -
|  |  | BARREN CO - HORSECAVE 69 SS | -
|  |  | CAVE CITY J-SEYMOUR T 69 SS | -
|  |  | CAVE CITY - CAVE CITY JCT 69 SS | -
|  |  | FOX HOLLOW - PARKWAY1 69 SS | -
|  |  | WAYNE CO - ZULA TAP 69 SS | -
|  |  | KU GARRARD T-MANCHESTER 69 SS | -
|  |  | GREEN BRIAR T-MANCHESTER 69 SS | -
|  |  | FALL ROCK-GREEN BRIAR T 69 SS | -
|  |  | BIG CREEK - BIG CREEK TAP 69 SS | -
|  |  | FALL ROCK - BIG CREEK TAP 69 SS | -
|  |  | BIG CREEK - ELK MT 69 SS | -
|  |  | CLAY LICK JCT - S ANDERSON 69 SS | -
|  |  | CLAY LICK J-CLAY LICK SW 69 SS | -
|  |  | OWEN CO - OWEN CO JCT 2 69 SS | -
|  |  | OWEN CO JCT 1 - BROMLEY EK 69 SS | -
|  |  | BROMLEY EK - MUNK JCT 69 SS | -
|  |  | MUNK JCT - WILLIAMSTOWN 69 SS | -
|  |  | RENAKER - THREE M 69 SS | -
|  |  | KU W FRANKFORT BRDGPT1 69 SS | -
|  |  | BRIDGEPORT J-BRDGPT2 69 SS | -
|  |  | STANLEY PARKER - BANK LICK 69 SS | -
|  |  | BEATTYVILLE-BEATTYVLLE D SS | -
|  |  | BEATTYVILLE DIST - OAKDALE 69 SS | -
342410 | 2VEECHDALE | 69 | SHELBY CO BUS SS | 5.1171
341725 | 2KEITH | 69 | EKPC_P1-2_OWEN-PENN69 | 8.2574
341749 | 2LEES LICK | 69 | EKPC_P1-2_PENN-RENAKER69 | 6.1828
341092 | 2BELLVIEW | 69 | EKPC_P1-2_BOONE-HEBRON69 | 5.1645
341167 | 2BOONE DIST | 69 | EKPC_P1-2_BOONE-HEBRON69 | 12.5148
341218 | 2BULLITTSVIL | 69 | EKPC_P1-2_BOONE-HEBRON69 | 10.2665
341224 | 2BURLINGTN | 69 | EKPC_P1-2_BOONE-HEBRON69 | 8.1595
341104 | 2BIG BONE | 69 | EKPC_P1-2_BOON-OWN-REN69 | 3.3535
341200 | 2BROMLEYEK | 69 | EKPC_P1-2_BOON-OWN-REN69 | 5.8016
341917 | 2MUNK | 69 | EKPC_P1-2_BOON-OWN-REN69 | 9.4431
341998 | 2OAKLEY NOEL | 69 | EKPC_P1-2_BOON-OWN-REN69 | 8.8938
342502 | 2WILLIAMSTWN | 69 | EKPC_P1-2_BOON-OWN-REN69 | 12.2435
341194 | 2BRISTOW | 69 | EKPC_P1-2_T FTJ-WEB RD69 | 12.7881
342385 | 2TURKEY FT | 69 | EKPC_P1-2_T FTJ-WEB RD69 | 11.9861
341050 | 2BANK LCK | 69 | EKPC_P1-2_TFTJ- ST PRK69 | 13.3486
341401 | 2DURO | 69 | EKPC_P1-2_TFTJ- ST PRK69 | 8.9714
341839 | 2MBUSA | 69 | EKPC_P1-2_TFTJ- ST PRK69 | 14.5365
341551 | 2GRANTS LICK | 69 | EKPC_P1-2_ST PRK-BRAK 69 | 20.8619
341584 | 2GRIFFIN | 69 | EKPC_P1-2_ST PRK-BRAK 69 | 7.6275
341260 | 2CARSON | 69 | EKPC_P1-2_OWN-CARSON 69 | 5.8918
341391 | 2DEFOE | 69 | EKPC_P1-2_OWN-CLY VILL69 | 4.021
341950 | 2NEW CASTLE | 69 | EKPC_P1-2_OWN-CLY VILL69 | 5.3063
341326 | 2COLEMANSVIL | 69 | EKPC_P1-2_BRAK- REN 69 | 7.7829
341485 | 2FOUR OAKS | 69 | EKPC_P1-2_BRAK- REN 69 | 6.5608
341550 | 2FALMOUTH KU | 69 | EKPC_P1-2_BRAK- REN 69 | 4.56
324195 | 2AUGUSTA | 69 | EKPC_P1-2_BRAK- KU KEN69 | 7
324722 | 2SHARON KU | 69 | EKPC_P1-2_BRAK- KU KEN69 | 6.28
341299 | 2CHARTERS | 69 | EKPC_P1-2_PLUM-GODDARD69 | 9.5341
341986 | 2OAK RIDGE | 69 | EKPC_P1-2_PLUM-GODDARD69 | 4.6709
342124 | 2RECTORVILLE | 69 | EKPC_P1-2_PLUM-GODDARD69 | 7.1568
342280 | 2SNOW HILL | 69 | EKPC_P1-2_MURPH - HQ 69 | 4.4062
326549 | 2SARDIS | 69 | EKPC_P1-2_MURPH-MILLBG69 | 1.36
325019 | 2KENTON-6 | 69 | EKPC_P1-2_MURPH-KU KEN69 | 8.38
243726 | 05GRAYSO | 69 | EKPC_P1-2_ARGEN - LEON69 | 9.905
341263 | 2CARTER CTY | 69 | EKPC_P1-2_ARGEN - LEON69 | 3.7198
341779 | 2LOW GAP | 69 | EKPC_P1-2_ARGEN - LEON69 | 4.1103
342031 | 2PACTOLUS | 69 | EKPC_P1-2_ARGEN - LEON69 | 8.8816
342475 | 2WARNOCK | 69 | EKPC_P1-2_ARGEN - LEON69 | 4.7497
341002 | 2AIRPORT RD | 69 | EKPC_P1-2_LEON-SKAGGS 69 | 3.6398
341446 | 2ELLIOT CO P | 69 | EKPC_P1-2_LEON-SKAGGS 69 | 10.6457
341836 | 2MAZIE | 69 | EKPC_P1-2_LEON-SKAGGS 69 | 3.0777
341953 | 2NEW FOUNDL | 69 | EKPC_P1-2_LEON-SKAGGS 69 | 3.626
342229 | 2SANDY HOOK | 69 | EKPC_P1-2_LEON-SKAGGS 69 | 3.5476
324726 | 2SHELBYVIL S | 69 | EKPC_P1-2_FIN-SHL-SHBV69 | 21.57
341212 | 2BUDD | 69 | EKPC_P1-2_SHL-BUD-BKRT69 | 5.6735
341772 | 2LOGAN | 69 | EKPC_P1-2_SHL-BUD-BKRT69 | 13.452
342500 | 2WIELAND | 69 | EKPC_P1-2_SHL-BUD-BKRT69 | 40
342352 | 2THREE M | 69 | EKPC_P1-2_REN - HQ 69 | 19.4904
341134 | 2BLEVINS VAL | 69 | EKPC_P1-2_GODD - HOPE 69 | 2.7272
341623 | 2HILLSBORO | 69 | EKPC_P1-2_GODD - HOPE 69 | 5.1989
342025 | 2OWINGVIL KU | 69 | EKPC_P1-2_GODD - HOPE 69 | 9.53
342052 | 2PEASTICKS | 69 | EKPC_P1-2_GODD - HOPE 69 | 6.9679
342109 | 2PRESTON | 69 | EKPC_P1-2_GODD - HOPE 69 | 1.5083
341116 | 2BIG WOODS | 69 | EKPC_P1-2_GODD - ROW 69 | 5.4642
341620 | 2HILDA | 69 | EKPC_P1-2_GODD - ROW 69 | 18.8682
342085 | 2PLUMMR L | 69 | EKPC_P1-2_GODD - ROW 69 | 4.0531
341386 | 2DEATSVIL | 69 | EKPC_P1-2_BULL-W BARDJ69 | 7.9864
341704 | 2JOE TICH | 69 | EKPC_P1-2_BULL-W BARDJ69 | 7.9884
342186 | 2S BARDSTWN | 69 | EKPC_P1-2_BULL-W BARDJ69 | 6.5963
342427 | 2W BARDSTWN | 69 | EKPC_P1-2_BULL-W BARDJ69 | 8.1787
341065 | 2BEAM | 69 | EKPC_P1-2_BULL - NELS 69 | 8.1995
341746 | 2LEBANON J | 69 | EKPC_P1-2_BULL - NELS 69 | 6.1184
342250 | 2SHEPHEVIL | 69 | EKPC_P1-2_BULL - NELS 69 | 20.8315
342514 | 2WOOSLEY | 69 | EKPC_P1-2_BULL - NELS 69 | 3.4626
341137 | 2BLOOMFLD | 69 | EKPC_P1-2_N SPR -S AND69 | 7.5908
341293 | 2CHAPLIN | 69 | EKPC_P1-2_N SPR -S AND69 | 1.4053
342262 | 2SINAI | 69 | EKPC_P1-2_N SPR -S AND69 | 7.5123
341308 | 2CLAY LCK | 69 | EKPC_P1-2_HNTFMJ-S AND69 | 6.1845
341659 | 2HT ADAMS | 69 | EKPC_P1-2_HNTFMJ-S AND69 | 6.0761
341857 | 2MERCR IND | 69 | EKPC_P1-2_HNTFMJ-S AND69 | 5.1464
342406 | 2VAN ARSDELL | 69 | EKPC_P1-2_HNTFMJ-S AND69 | 8.2474
341383 | 2DAVIS | 69 | EKPC_P1-2_BKR LN-FAY 69 | 5.2467
341965 | 2NICHOLASVIL | 69 | EKPC_P1-2_BKR LN-FAY 69 | 7.6909
342202 | 2S JESSAMINE | 69 | EKPC_P1-2_BKR LN-FAY 69 | 14.9115
342460 | 2W NICHVIL | 69 | EKPC_P1-2_BKR LN-FAY 69 | 23.1559
341251 | 2CANE RIDG | 69 | EKPC_P1-2_HQ-HUNT 69 | 0.37481
341875 | 2MILLER HUNT | 69 | EKPC_P1-2_HQ-HUNT 69 | 2.2498
341878 | 2MILLERSB EK | 69 | EKPC_P1-2_HQ-HUNT 69 | 3.855
341899 | 2MT STERLING | 69 | EKPC_P1-2_HQ-HUNT 69 | 4.504
342130 | 2REID VILLAG | 69 | EKPC_P1-2_HQ-HUNT 69 | 3.2944
342259 | 2SIDEVIEW | 69 | EKPC_P1-2_HQ-HUNT 69 | 4.7849
341302 | 2CLAY CITY | 69 | EKPC_P1-2_HUNT-POWELL 69 | 8.5542
341590 | 2HARDWCRK | 69 | EKPC_P1-2_HUNT-POWELL 69 | 1.8746
341596 | 2HARGETT | 69 | EKPC_P1-2_HUNT-POWELL 69 | 3.9751
342301 | 2STANTON | 69 | EKPC_P1-2_HUNT-POWELL 69 | 12.2052
342370 | 2TRAPP | 69 | EKPC_P1-2_HUNT-POWELL 69 | 2.3494
341044 | 2BALLARD | 69 | EKPC_P1-2_DALE-HTFRMJ69 | 5.0309
342358 | 2TODDVILLE | 69 | EKPC_P1-2_DALE-HTFRMJ69 | 4.2681
341731 | 2LANCASTER | 69 | EKPC_P1-2_DALE-GARRD 69 | 5.5024
341959 | 2NEWBY 1 | 69 | EKPC_P1-2_DALE-GARRD 69 | 7.6911
341683 | 2JEFFERSNVIL | 69 | EKPC_P1-2_HOPE - POW 69 | 4.5971
341500 | 2FRENCHBURG | 69 | EKPC_P1-2_HOPE - MORG 69 | 6.1971
341821 | 2MARIBA | 69 | EKPC_P1-2_HOPE - MORG 69 | 4.525
341830 | 2MAYTOWN | 69 | EKPC_P1-2_HOPE - MORG 69 | 3.9033
341353 | 2CROCKETT | 69 | EKPC_P1-2_MORG-SKAGGS69 | 3.3314
341656 | 2HOT MIX RD | 69 | EKPC_P1-2_MORG-SKAGGS69 | 5.3326
341797 | 2MAGGARD | 69 | EKPC_P1-2_SKAGGS-FALC69 | 3.9024
342127 | 2REDBUSH | 69 | EKPC_P1-2_SKAGGS-THELM69 | 1.6023
342421 | 2VOLGA | 69 | EKPC_P1-2_SKAGGS-THELM69 | 8.0118
341713 | 2KARGLE | 69 | EKPC_P1-2_C HAR-KU ETN69 | 18.7858
341533 | 2GLENDALE | 69 | EKPC_P1-2_STEPH-HODG 69 | 5.9756
342400 | 2UPTON | 69 | EKPC_P1-2_STEPH-BONN 69 | 3.4103
341458 | 2ETOWN EK2 | 69 | EKPC_P1-2_ETOWN-KU ETN69 | 9.3887
342337 | 2THARP | 69 | EKPC_P1-2_ETOWN-KU ETN69 | 10.0175
341479 | 2S BOUND RD | 69 | EKPC_P1-2_ETWN-ROG-RAD69 | 6.5271
342118 | 2RADCLIFF | 69 | EKPC_P1-2_ETWN-ROG-RAD69 | 7.6513
342151 | 2RINEYVILLE | 69 | EKPC_P1-2_ETWN-ROG-RAD69 | 5.6071
342271 | 2SMITHRSVIL | 69 | EKPC_P1-2_ETWN-ROG-RAD69 | 13.9816
342328 | 2T BROWN LOG | 69 | EKPC_P1-2_ETWN-ROG-RAD69 | 7.5424
342418 | 2VINE GROVE | 69 | EKPC_P1-2_ETWN-ROG-RAD69 | 8.2029
341329 | 2COLESBURG | 69 | EKPC_P1-2_ETOWN-NELSN 69 | 2.9494
341785 | 2LYMAN BW | 69 | EKPC_P1-2_ETOWN-NELSN 69 | 7.0814
342154 | 2ROANOKE | 69 | EKPC_P1-2_ETOWN-NELSN 69 | 3.4896
342382 | 2TUNNEL HILL | 69 | EKPC_P1-2_ETOWN-NELSN 69 | 16.3905
341053 | 2BARD SHOP | 69 | EKPC_P1-2_W BARDJ-EBRD69 | 11.0844
341800 | 2MAGNOLIA | 69 | EKPC_P1-2_HODG-GREEN 69 | 6.0678
342325 | 2SUMMERSVIL | 69 | EKPC_P1-2_HODG-GREEN 69 | 6.8647
341776 | 2LORETTO | 69 | EKPC_P1-2_HODG-N SPR 69 | 6.9275
342211 | 2S SPRINGFLD | 69 | EKPC_P1-2_HODG-N SPR 69 | 4.6495
342316 | 2SULPHUR CRK | 69 | EKPC_P1-2_HODG-N SPR 69 | 5.3135
341140 | 2BLUE G PW | 69 | EKPC_P1-2_E BARD-N SPR69 | 11.2397
341497 | 2FREDRIKBRG | 69 | EKPC_P1-2_E BARD-N SPR69 | 4.135
342016 | 2OWENS IL | 69 | EKPC_P1-2_E BARD-N SPR69 | 7.503
324345 | 2BARDTWN IND | 69 | EKPC_P1-2_E BRD-KU BRD69 | 17.37
341791 | 2MACKVIL KU | 69 | EKPC_P1-2_HNTFMJ-N SPR69 | 0.45
342061 | 2PERRYVILLE | 69 | EKPC_P1-2_HNTFMJ-N SPR69 | 7.8964
|  |  | EKPC_P1-2_W BER-THRLJ 69 | -
341008 | 2ALCAN | 69 | EKPC_P1-2_W BER-KU FAW69 | 30.1274
341359 | 2CROOKSVIL | 69 | EKPC_P1-2_W BER-KU FAW69 | 5.895
341405 | 2DUNCANNO LN | 69 | EKPC_P1-2_W BER-KU FAW69 | 3.7451
341611 | 2HICKORY PL | 69 | EKPC_P1-2_W BER-KU FAW69 | 12.443
342103 | 2PPG | 69 | EKPC_P1-2_W BER-KU FAW69 | 4.3099
342288 | 2SPEEDWELL | 69 | EKPC_P1-2_W BER-KU FAW69 | 1.3
341185 | 2BOWEN | 69 | EKPC_P1-2_POW - ZACH 69 | 3.6713
341614 | 2HIGH ROCK | 69 | EKPC_P1-2_POW - ZACH 69 | 0.47094
341248 | 2CAMPTON | 69 | EKPC_P1-2_ZACH-HELECH69 | 7.9277
341074 | 2BEATTYV D | 69 | EKPC_P1-2_BETYV - OAK 69 | 7.6723
341992 | 2OAKDALE | 69 | EKPC_P1-2_BETYV - OAK 69 | 5.3401
341170 | 2BOONEVIL | 69 | EKPC_P1-2_BETYV - TYN 69 | 4.449
342196 | 2WHITE OAK | 69 | EKPC_P1-2_BETYV - TYN 69 | 7.9782
|  |  | EKPC_P1-2_HELECH-MAG 69 | -
342310 | 2SUBLETT | 69 | EKPC_P1-2_FALC - MAG 69 | 6.8625
341125 | 2BILL WELLS | 69 | EKPC_P1-2_MAG - THELM 69 | 7.6338
341152 | 2BONANZA | 69 | EKPC_P1-2_MAG - THELM 69 | 4.0496
341695 | 2JENNY WILEY | 69 | EKPC_P1-2_MAG - THELM 69 | 5.4657
341863 | 2MIDDLE CRK | 69 | EKPC_P1-2_MAG - THELM 69 | 5.746
341158 | 2BONNIV DIST | 69 | EKPC_P1-2_BONN - BARR 69 | 3.0767
341647 | 2HORSE CV KU | 69 | EKPC_P1-2_BONN - BARR 69 | 46.06
341908 | 2MUNFVIL EK | 69 | EKPC_P1-2_BONN - BARR 69 | 9.2259
341911 | 2MUNFVIL KU | 69 | EKPC_P1-2_BONN - BARR 69 | 6.11
341437 | 2EDMON IND P | 69 | EKPC_P1-2_GREEN-SUM SH69 | 1.5349
341575 | 2GREENSBURG | 69 | EKPC_P1-2_GREEN-SUM SH69 | 5.9623
341680 | 2JB GALLOWAY | 69 | EKPC_P1-2_GREEN-SUM SH69 | 7.4175
341728 | 2KNOB LICK | 69 | EKPC_P1-2_GREEN-SUM SH69 | 5.6051
341851 | 2MCKINNEY | 69 | EKPC_P1-2_GREEN-SUM SH69 | 4.4445
341764 | 2LIBERTY KU | 69 | EKPC_P1-2_CASEY-LIB J69 | 7.68
342064 | 2PEYTONS ST | 69 | EKPC_P1-2_CASEY-LIB J69 | 6.0717
341210 | 2BROUGHT TWN | 69 | EKPC_P1-2_LIB J-GARR69 | 4.4578
341617 | 2HIGHLAND EK | 69 | EKPC_P1-2_LIB J-GARR69 | 5.9777
341893 | 2MT OLIVE | 69 | EKPC_P1-2_LIB J-GARR69 | 4.6349
342364 | 2TOMM GOOC | 69 | EKPC_P1-2_LIB J-GARR69 | 14.7257
341343 | 2CONTOWN | 69 | EKPC_P1-2_LIB J-WIND 69 | 2.2548
341350 | 2CRESTON | 69 | EKPC_P1-2_LIB J-WIND 69 | 5.7798
342067 | 2PHIL | 69 | EKPC_P1-2_LIB J-WIND 69 | 5.7813
341029 | 2ASAHI M W | 69 | EKPC_P1-2_PUL-WAL-SSET69 | 11.9039
341233 | 2CABIN HOLLW | 69 | EKPC_P1-2_PUL-WAL-SSET69 | 8.7275
341379 | 2DAHL ROAD | 69 | EKPC_P1-2_PUL-WAL-SSET69 | 12
341422 | 2E SOMERSET | 69 | EKPC_P1-2_PUL-WAL-SSET69 | 8.3699
341947 | 2NELSON VAL | 69 | EKPC_P1-2_PUL-WAL-SSET69 | 5.5639
341971 | 2NORWOOD | 69 | EKPC_P1-2_PUL-WAL-SSET69 | 8.5638
342256 | 2SHOPVILLE | 69 | EKPC_P1-2_PUL-WAL-SSET69 | 7.7057
341470 | 2FLOYD EK | 69 | EKPC_P1-2_PUL - WOODSTOCK 69 | 5.8408
342193 | 2S FLOYD | 69 | EKPC_P1-2_PUL - WOODSTOCK 69 | 7.0517
341197 | 2BRODHEAD | 69 | EKPC_P1-2_THREELJ- WAL69 | 7.5934
341815 | 2MARETBURG | 69 | EKPC_P1-2_THREELJ- WAL69 | 6.4511
341014 | 2ANNVILLE | 69 | EKPC_P1-2_TYN - N LON 69 | 4.3545
341425 | 2EBERLE | 69 | EKPC_P1-2_TYN - N LON 69 | 4.738
341812 | 2MAPLESVILLE | 69 | EKPC_P1-2_TYN - N LON 69 | 5.784
341572 | 2GREENBRIAR | 69 | EKPC_P1-2_FALL R-GARR69 | 7.3931
341110 | 2BIG CREEK | 69 | EKPC_P1-2_FALL R-GOOS 69 | 4.7334
341439 | 2ELK MT IP | 69 | EKPC_P1-2_FALL R-GOOS 69 | 4.7318
342001 | 2ONEIDA | 69 | EKPC_P1-2_FALL R-GOOS 69 | 2.365
341542 | 2GOODNIGHT | 69 | EKPC_P1-2_BARR- FOX H 69 | 9.2502
342160 | 2ROSEVILLE | 69 | EKPC_P1-2_FOX H-SUMMSH69 | 7.0525
342334 | 2TEMPLE HILL | 69 | EKPC_P1-2_FOX H-SUMMSH69 | 7.0546
341335 | 2COLUMBIA | 69 | EKPC_P1-2_SUMMSH-SEWJ 69 | 6.5135
341366 | 2COLUMB KU | 69 | EKPC_P1-2_SUMMSH-SEWJ 69 | 6.29
341370 | 2COLUMB S KU | 69 | EKPC_P1-2_SUMMSH-SEWJ 69 | 4.41
341509 | 2GARLIN | 69 | EKPC_P1-2_SUMMSH-SEWJ 69 | 5.8713
342439 | 2W COLUMBIA | 69 | EKPC_P1-2_SUMMSH-SEWJ 69 | 5.8725
341005 | 2ALBANY | 69 | EKPC_P1-2_SUMMSH-WAYNE69 | 8.5373
342181 | 2S ALBANY | 69 | EKPC_P1-2_SUMMSH-WAYNE69 | 7.995
342277 | 2SNOW | 69 | EKPC_P1-2_SUMMSH-WAYNE69 | 9.8435
342394 | 2UPCHURCH | 69 | EKPC_P1-2_SUMMSH-WAYNE69 | 8.1682
342529 | 2ZULA | 69 | EKPC_P1-2_WAYNE-ZULA 69 | 8.451
342172 | 2RUSS SPR EK | 69 | EKPC_P1-2_SEWJ - RUSS 69 | 11.0494
342175 | 2RUSS SPR KU | 69 | EKPC_P1-2_SEWJ - RUSS 69 | 6.4
342214 | 2SALEM EK | 69 | EKPC_P1-2_SEWJ - WIND 69 | 10.2212
342484 | 2WEBB CR RDS | 69 | EKPC_P1-2_SEWJ - WIND 69 | 5.4721
324737 | 2SOMERSET SO | 69 | EKPC_P1-2_RUSS-KU SSET69 | 7.33
324787 | 2UNION UNDWR | 69 | EKPC_P1-2_RUSS-KU SSET69 | 12.44
324990 | 2WAITSBORO | 69 | EKPC_P1-2_RUSS-KU SSET69 | 8.02
342232 | 2SEWELLTON | 69 | EKPC_P1-2_RUSS-KU SSET69 | 5.5615
341938 | 2NANCY | 69 | EKPC_P1-2_WIND - SSET 69 | 6.3159
341977 | 2OAK HILL | 69 | EKPC_P1-2_WIND - SSET 69 | 6.5887
342469 | 2W SOMERSET | 69 | EKPC_P1-2_WIND - SSET 69 | 7.984
342523 | 2ZOLLICOF | 69 | EKPC_P1-2_WIND - SSET 69 | 3.8925
324531 | 2FERGUSON SO | 69 | EKPC_P1-2_SSET-KU ELI 69 | 5.58
341203 | 2BRONSTON | 69 | EKPC_P1-2_COOP-DENNY 69 | 13.1724
341035 | 2BACON CRK | 69 | EKPC_P1-2_LAUR-KU FAR69 | 4.3674
341716 | 2KEAVY | 69 | EKPC_P1-2_LAUR-KU FAR69 | 10.7978
341758 | 2LIBERT CHUR | 69 | EKPC_P1-2_LAUR-KU FAR69 | 4.8231
342187 | 2S CORBIN | 69 | EKPC_P1-2_LAUR-KU FAR69 | 9.1367
324576 | 2HOPEWELL | 69 | EKPC_P1-2_LAUR-KU SWTH69 | 12.82
341506 | 2GAP OF RIDG | 69 | EKPC_P1-2_WAYNE-DENNY69 | 9.8439
341581 | 2GREGORY RD | 69 | EKPC_P1-2_WAYNE-DENNY69 | 1.8519
341641 | 2HOMESTEAD S | 69 | EKPC_P1-2_WAYNE-DENNY69 | 14.1787
341887 | 2MONTICELLO | 69 | EKPC_P1-2_WAYNE-DENNY69 | 7.6051
342268 | 2SLAT | 69 | EKPC_P1-2_WAYNE-DENNY69 | 8.7197
342490 | 2WHITLEY CTY | 69 | EKPC_P1-2_DENNY-MCCRRY69 | 6.1217
342493 | 2WHITLY C KU | 69 | EKPC_P1-2_DENNY-MCCRRY69 | 3.81
342496 | 2WIBORG | 69 | EKPC_P1-2_DENNY-MCCRRY69 | 8.0737
341416 | 2E PINE KNOT | 69 | EKPC_P1-2_MCCRY-KUWOFF69 | 4.2639
341539 | 2GOLDBUG | 69 | EKPC_P1-2_MCCRY-KUWOFF69 | 8.1097
341689 | 2JELLICO CRK | 69 | EKPC_P1-2_MCCRY-KUWOFF69 | 1.9129
342076 | 2PINE KNOT | 69 | EKPC_P1-2_MCCRY-KUWOFF69 | 6.4931
342136 | 2REVELO KU | 69 | EKPC_P1-2_MCCRY-KUWOFF69 | 1.8
324725 | 2SHELBYVIL E | 69 | EKPC_P1-2_CLYV-SHL-FRK69 | 21.53
341281 | 2CEDAR GR | 69 | EKPC_P1-2_BULL- PLENTG69 | 8.5817
342082 | 2PLEAS GRV | 69 | EKPC_P1-2_BULL- PLENTG69 | 26.1472
|  |  | EKPC_P1-2_AEPMORG- MOR69 | -
|  |  | EKPC_P1-2_AEPMORG-INDX69 | -
324424 | 2BARDTWN CTY | 69 | EKPC_P1-2_HODG-KU BARD69 | 9.42
324660 | 2NEW HAVEN | 69 | EKPC_P1-2_HODG-KU BARD69 | 3.33
324801 | 2BARTON | 69 | EKPC_P1-2_HODG-KU BARD69 | 6.46
326537 | 2WOODLAWN KU | 69 | EKPC_P1-2_HODG-KU BARD69 | 5.15
324521 | 2ETOWN 4 | 69 | EKPC_P1-2_HODG-KU ETWN69 | 13.48
324575 | 2HODGENV KU | 69 | EKPC_P1-2_HODG-KU ETWN69 | 10.02
324736 | 2SPRINGFL KU | 69 | EKPC_P1-2_N SPR-KU LEB69 | 13.78
341080 | 2BECKTON | 69 | EKPC_P1-2_BAR-BON-FHOL69 | 8.3189
341149 | 2BON AYR | 69 | EKPC_P1-2_BAR-BON-FHOL69 | 3.8843
341272 | 2CAVE CITY | 69 | EKPC_P1-2_BAR-BON-FHOL69 | 7.5201
342238 | 2SEYMOUR | 69 | EKPC_P1-2_BAR-BON-FHOL69 | 3.7942
342442 | 2W GLASGOW | 69 | EKPC_P1-2_BAR-BON-FHOL69 | 12.7509
342037 | 2PARKWAY 1 | 69 | EKPC_P1-2_FHOL-PARK69 | 9.3281
342040 | 2PARKWAY 2 | 69 | EKPC_P1-2_FHOL-PARK69 | 3.3429
324554 | 2GRENSBRG KU | 69 | EKPC_P1-2_GREEN-KUTAY69 | 4.57
324557 | 2GR RVR PLAZ | 69 | EKPC_P1-2_GREEN-KUTAY69 | 7.3221
324829 | 2CAMPBELVIL1 | 69 | EKPC_P1-2_GREEN-KUTAY69 | 12.53
326970 | 2MILE LAN EK | 69 | EKPC_P1-2_GREEN-KUTAY69 | 9.7611
341410 | 2E BERNSTADT | 69 | EKPC_P1-2_NLON-KU NLON69 | 6.944
342595 | 4HEBRON | 138 | EKPC_P1-2_DK HEB-HEB 138 | 16.4491
250054 | 08LONGBR | 138 | EKPC_P1-2_BOONE-BUFF138 | 20.26
250077 | 08MTZION | 138 | EKPC_P1-2_BOONE-BUFF138 | 13.028
342643 | 4RICHWOOD | 138 | EKPC_P1-2_BOONE-STANP138 | 11.3427
342670 | 4STERLING | 138 | EKPC_P1-2_BOONE-GALL138 | 6.9793
342550 | 4BAVARIAN LF | 138 | EKPC_P1-2_BOONE-REN 138 | 5.0733
|  |  | EKPC_P1-2_OWEN 138/69 | -
|  |  | EKPC_P1-2_SPUR-KUKEN 138 | -
342625 | 4MAYSVIL IND | 138 | EKPC_P1-2_SPUR-PLUM 138 | 8.0269
342583 | 4FLEMINGSBRG | 138 | EKPC_P1-2_SPUR-GODD 138 | 10.4135
342571 | 4CRANSTON | 138 | EKPC_P1-2_GODD - ROW138 | 25.3272
342601 | 4JACKSNVIL | 138 | EKPC_P1-2_AVN-PAR-REN138 | 3.3691
342553 | 4BECKNERV | 138 | EKPC_P1-2_AVN-BBN-DLE138 | 1.593
|  |  | EKPC_P1-2_AVON-FAY 138 | -
|  |  | EKPC_P1-2_AVON-LOUD 138 | -
|  |  | EKPC_P1-2_DALE-JKSMIT138 | -
342679 | 4THREE FORKS | 138 | EKPC_P1-2_DALE-FAWK 138 | 3.0944
|  |  | EKPC_P1-2_FAW-W BER 138 | -
|  |  | EKPC_P1-2_JKS 345/138 1 | -
|  |  | EKPC_P1-2_JKS 345/138 2 | -
342685 | 4UNION CITY | 138 | EKPC_P1-2_JKSMTH-REBA138 | 6.4748
|  |  | EKPC_P1-2_ROW-SKAG138 | -
324047 | 4BLACKBRANCH | 138 | EKPC_P1-2_CHARD-HRDBG138 | 13.06
325130 | 1RHUDES GEN | 0.6 | EKPC_P1-2_CHARD-HRDBG138 | 0.16
342742 | 5JABEZ | 161 | EKPC_P1-2_COP-RUS-WLF161 | 4.1686
342748 | 5JAMESTOWN | 161 | EKPC_P1-2_COP-RUS-WLF161 | 6.8602
342799 | 5S OAKHILL | 161 | EKPC_P1-2_COP-RUS-WLF161 | 10.6696
|  |  | EKPC_P1-2_COOP-DEN161 | -
|  |  | EKPC_P1-2_COP-LIBJ-PU161 | -
|  |  | EKPC_P1-2_LIB-CAS-GAS-MAR161 | -
|  |  | EKPC_P1-2_MCCR-WAYNE161 | -
|  |  | EKPC_P1-2_LAUR-PIT-TY161 | -
342739 | 5GREEN HALL | 161 | EKPC_P1-2_TYN-DELV161 | 2.6482
|  |  | EKPC_P1-2_TYN-FALLR161 | -
342772 | 5MARION IP | 161 | EKPC_P1-2_GRE-TAY-MAR161 | 7.3059
342798 | 5S MARION IP | 161 | EKPC_P1-2_GRE-TAY-MAR161 | 30.4021
342802 | 5SALOMA | 161 | EKPC_P1-2_GRE-TAY-MAR161 | 12.0099
|  |  | EKPC_P1-2_BARR-SUMSH161 | -
|  |  | EKPC_P1-2_BULL-SUMSH161 | -
326975 | 5CEDAR GRV | 161 | EKPC_P1-2_BULL-BLUE L161 | 23.384
342721 | 5DARWIN TH | 161 | EKPC_P1-2_BULL-SHEL161 | 15.3905
342763 | 5LITTLE MT | 161 | EKPC_P1-2_BULL-SHEL161 | 5.1178
342818 | 5TAYLORSVILL | 161 | EKPC_P1-2_BULL-SHEL161 | 10.0637
342779 | 5MILLER CRK | 161 | EKPC_P1-2_POW-BTV-DEL161 | 3.1325
|  |  | TVA SS-GLASGOW & LAFAYETTE 161 | -
|  |  | EK-TVA SSHD & SSHD 161 XFMR | -
|  |  | EKPC_P1-2_AVON-NCLA345 | -
|  |  | SINGLE OPN LIN 714 324010-324114(1) | -
324044 | 1BLUEGRASS 1 | 18 | SINGLE OPN LIN 715 324021-324103(Z1) | 0.6333
324045 | 1BLUEGRASS 2 | 18 | SINGLE OPN LIN 715 324021-324103(Z1) | 1.4333
324046 | 1BLUEGRASS 3 | 18 | SINGLE OPN LIN 716 324022-324103(Z1) | 0.6333
|  |  | SINGLE OPN LIN 717 324029-324030(1) | -
|  |  | SINGLE OPN LIN 718 324029-324114(1) | -
|  |  | SINGLE OPN LIN 719 324030-324114(1) | -
|  |  | SINGLE OPN LIN 720 324047-325055(1) | -
|  |  | SINGLE OPN LIN 721 324048-324437(1) | -
|  |  | SINGLE OPN LIN 722 324048-324584(1) | -
|  |  | SINGLE OPN LIN 723 324049-324572(1) | -
|  |  | SINGLE OPN LIN 724 324049-324745(1) | -
324362 | 2RIO | 69 | SINGLE OPN LIN 725 324050-324362(1) | 1.59
324050 | 2JONESVILLE | 69 | SINGLE OPN LIN 726 324050-324447(1) | 4.5173
324362 | 2RIO | 69 | SINGLE OPN LIN 726 324050-324447(1) | 1.59
|  |  | SINGLE OPN LIN 727 324051-324173(1) | -
|  |  | SINGLE OPN LIN 728 324051-324173(2) | -
|  |  | SINGLE OPN LIN 729 324051-324255(1) | -
|  |  | SINGLE OPN LIN 730 324051-324291(1) | -
324059 | 2BEAVER DM N | 69 | SINGLE OPN LIN 731 324058-324059(1) | 4.6
324080 | 2HARTFORD | 69 | SINGLE OPN LIN 731 324058-324059(1) | 6.07
324058 | 2BEAVER DAM | 69 | SINGLE OPN LIN 732 324058-324667(1) | 6.09
324059 | 2BEAVER DM N | 69 | SINGLE OPN LIN 732 324058-324667(1) | 4.6
324080 | 2HARTFORD | 69 | SINGLE OPN LIN 732 324058-324667(1) | 6.07
324080 | 2HARTFORD | 69 | SINGLE OPN LIN 733 324059-324080(1) | 6.07
324079 | 2HANSON | 69 | SINGLE OPN LIN 734 324061-324079(1) | 9.89
324061 | 2BORG-WARNER | 69 | SINGLE OPN LIN 735 324061-324873(1) | 8.5
324079 | 2HANSON | 69 | SINGLE OPN LIN 735 324061-324873(1) | 9.89
324065 | 2DAWSON 764 | 69 | SINGLE OPN LIN 736 324065-324843(1) | 3.55
324067 | 2EDDYV PRIS | 69 | SINGLE OPN LIN 737 324067-324512(1) | 3.61
324068 | 2E CAMPBELVL | 69 | SINGLE OPN LIN 738 324068-324349(1) | 7.2306
|  |  | SINGLE OPN LIN 739 324069-324687(1) | -
|  |  | SINGLE OPN LIN 740 324069-324763(1) | -
324075 | 2GRAHAM | 69 | SINGLE OPN LIN 741 324075-324702(1) | 3.7
324077 | 2GREENVILE W | 69 | SINGLE OPN LIN 742 324077-326594(1) | 1.98
324081 | 2MADSNV GE | 69 | SINGLE OPN LIN 743 324081-326587(1) | 5.41
324197 | 2DETROIT HAR | 69 | SINGLE OPN LIN 744 324082-324197(1) | 10.92
324082 | 2PARIS 4 | 69 | SINGLE OPN LIN 745 324082-324476(1) | 1.08
324197 | 2DETROIT HAR | 69 | SINGLE OPN LIN 745 324082-324476(1) | 10.92
325018 | 2CLA | 69 | SINGLE OPN LIN 745 324082-324476(1) | 6.31
325061 | 2CMC | 69 | SINGLE OPN LIN 745 324082-324476(1) | 4.08
325017 | 2CMWA | 69 | SINGLE OPN LIN 745 324082-324476(1) | 7.49
325018 | 2CLA | 69 | SINGLE OPN LIN 746 324082-325061(1) | 6.31
325061 | 2CMC | 69 | SINGLE OPN LIN 746 324082-325061(1) | 4.08
325017 | 2CMWA | 69 | SINGLE OPN LIN 746 324082-325061(1) | 7.49
324083 | 2MADSNV W | 69 | SINGLE OPN LIN 747 324083-326587(1) | 17.4
324085 | 2MARION 4 | 69 | SINGLE OPN LIN 748 324085-324629(1) | 3.35
324097 | 2PEAB WASH | 69 | SINGLE OPN LIN 749 324086-324096(1) | 0.2
324086 | 2MORGANF IND | 69 | SINGLE OPN LIN 750 324086-324671(1) | 4.67
324097 | 2PEAB WASH | 69 | SINGLE OPN LIN 750 324086-324671(1) | 0.2
|  |  | SINGLE OPN LIN 751 324087-324913(1) | -
|  |  | SINGLE OPN LIN 752 324087-324927(1) | -
|  |  | SINGLE OPN LIN 753 324090-324095(1) | -
|  |  | SINGLE OPN LIN 754 324091-324096(1) | -
|  |  | SINGLE OPN LIN 755 324092-324702(1) | -
324093 | 2SPEN CHEMIC | 69 | SINGLE OPN LIN 756 324093-324711(1) | 5.83
|  |  | SINGLE OPN LIN 757 324094-324562(1) | -
|  |  | SINGLE OPN LIN 758 324094-324761(1) | -
325045 | 2TURTLE CRK | 69 | SINGLE OPN LIN 759 324094-325045(1) | 0.25
325092 | 2COAL GOOD | 69 | SINGLE OPN LIN 759 324094-325045(1) | 2.45
324095 | 2UNIONTOWN | 69 | SINGLE OPN LIN 760 324095-326572(1) | 2.32
324097 | 2PEAB WASH | 69 | SINGLE OPN LIN 761 324096-324097(1) | 0.2
324098 | 2WEST VACO | 69 | SINGLE OPN LIN 762 324098-324779(1) | 34.42
|  |  | SINGLE OPN LIN 763 324100-324102(1) | -
|  |  | SINGLE OPN LIN 764 324100-324112(1) | -
|  |  | SINGLE OPN LIN 765 324100-324130(1) | -
|  |  | SINGLE OPN LIN 766 324101-324107(1) | -
|  |  | SINGLE OPN LIN 767 324101-324108(1) | -
|  |  | SINGLE OPN LIN 768 324101-324134(1) | -
|  |  | SINGLE OPN LIN 769 324101-324212(1) | -
|  |  | SINGLE OPN LIN 770 324102-324106(1) | -
|  |  | SINGLE OPN LIN 771 324102-324116(1) | -
|  |  | SINGLE OPN LIN 772 324102-325074(1) | -
|  |  | SINGLE OPN LIN 773 324102-325956(1) | -
|  |  | SINGLE OPN LIN 774 324102-325957(2) | -
|  |  | SINGLE OPN LIN 775 324103-324107(1) | -
|  |  | SINGLE OPN LIN 776 324103-324114(1) | -
|  |  | SINGLE OPN LIN 777 324104-324106(1) | -
|  |  | SINGLE OPN LIN 778 324105-324115(1) | -
|  |  | SINGLE OPN LIN 779 324105-324116(1) | -
|  |  | SINGLE OPN LIN 780 324105-324253(1) | -
|  |  | SINGLE OPN LIN 781 324105-324253(2) | -
326536 | 7GALLATIN | 345 | SINGLE OPN LIN 782 324105-326536(1) | 362.97
|  |  | SINGLE OPN LIN 783 324106-324261(1) | -
|  |  | SINGLE OPN LIN 784 324106-324261(2) | -
|  |  | SINGLE OPN LIN 785 324106-325073(1) | -
|  |  | SINGLE OPN LIN 786 324107-324108(1) | -
|  |  | SINGLE OPN LIN 787 324107-324114(1) | -
|  |  | SINGLE OPN LIN 788 324107-324281(3) | -
|  |  | SINGLE OPN LIN 789 324107-324281(4) | -
|  |  | SINGLE OPN LIN 790 324107-324281(5) | -
|  |  | SINGLE OPN LIN 791 324107-324281(7) | -
|  |  | SINGLE OPN LIN 792 324108-325073(1) | -
|  |  | SINGLE OPN LIN 793 324108-326001(1) | -
324109 | 7NAS | 345 | SINGLE OPN LIN 794 324109-324565(1) | 106.67
|  |  | SINGLE OPN LIN 795 324110-324289(1) | -
|  |  | SINGLE OPN LIN 796 324110-326569(1) | -
|  |  | SINGLE OPN LIN 797 324111-324294(1) | -
|  |  | SINGLE OPN LIN 798 324111-326001(1) | -
|  |  | SINGLE OPN LIN 799 324111-326569(1) | -
|  |  | SINGLE OPN LIN 800 324112-324167(1) | -
|  |  | SINGLE OPN LIN 801 324112-325074(1) | -
|  |  | SINGLE OPN LIN 802 324114-324314(5) | -
|  |  | SINGLE OPN LIN 803 324114-324314(6) | -
|  |  | SINGLE OPN LIN 804 324115-324319(1) | -
|  |  | SINGLE OPN LIN 805 324116-324320(1) | -
324124 | 2CENTRTOWN S | 69 | SINGLE OPN LIN 806 324124-326564(1) | 0.95
|  |  | SINGLE OPN LIN 807 324130-324141(1) | -
|  |  | SINGLE OPN LIN 808 324130-324143(1) | -
|  |  | SINGLE OPN LIN 809 324131-324139(1) | -
|  |  | SINGLE OPN LIN 810 324131-324146(1) | -
|  |  | SINGLE OPN LIN 811 324131-324148(1) | -
|  |  | SINGLE OPN LIN 812 324131-324416(1) | -
|  |  | SINGLE OPN LIN 813 324132-324133(1) | -
|  |  | SINGLE OPN LIN 814 324132-324143(1) | -
|  |  | SINGLE OPN LIN 815 324132-324156(1) | -
|  |  | SINGLE OPN LIN 816 324133-324417(1) | -
|  |  | SINGLE OPN LIN 817 324134-326975(1) | -
|  |  | SINGLE OPN LIN 818 324135-324136(1) | -
|  |  | SINGLE OPN LIN 819 324135-324144(1) | -
|  |  | SINGLE OPN LIN 820 324135-324153(1) | -
|  |  | SINGLE OPN LIN 821 324136-324484(1) | -
|  |  | SINGLE OPN LIN 822 324137-324151(1) | -
|  |  | SINGLE OPN LIN 823 324137-324153(1) | -
|  |  | SINGLE OPN LIN 824 324137-324486(1) | -
|  |  | SINGLE OPN LIN 825 324138-324148(1) | -
|  |  | SINGLE OPN LIN 826 324138-324165(1) | -
|  |  | SINGLE OPN LIN 827 324139-324149(1) | -
|  |  | SINGLE OPN LIN 828 324139-324503(1) | -
|  |  | SINGLE OPN LIN 829 324139-324503(2) | -
|  |  | SINGLE OPN LIN 830 324140-324160(1) | -
|  |  | SINGLE OPN LIN 831 324140-324164(1) | -
|  |  | SINGLE OPN LIN 832 324140-324506(1) | -
|  |  | SINGLE OPN LIN 833 324140-325079(1) | -
|  |  | SINGLE OPN LIN 834 324141-324514(1) | -
|  |  | SINGLE OPN LIN 835 324141-324514(2) | -
|  |  | SINGLE OPN LIN 836 324143-324527(1) | -
|  |  | SINGLE OPN LIN 837 324144-324160(1) | -
|  |  | SINGLE OPN LIN 838 324144-324255(1) | -
|  |  | SINGLE OPN LIN 839 324144-324255(2) | -
|  |  | SINGLE OPN LIN 840 324144-324255(3) | -
|  |  | SINGLE OPN LIN 841 324145-324171(1) | -
|  |  | SINGLE OPN LIN 842 324145-324172(1) | -
|  |  | SINGLE OPN LIN 843 324145-324553(1) | -
|  |  | SINGLE OPN LIN 844 324145-325069(1) | -
|  |  | SINGLE OPN LIN 845 324145-325077(1) | -
|  |  | SINGLE OPN LIN 846 324146-324147(1) | -
|  |  | SINGLE OPN LIN 847 324146-324155(1) | -
|  |  | SINGLE OPN LIN 848 324146-324157(1) | -
|  |  | SINGLE OPN LIN 849 324146-324564(1) | -
|  |  | SINGLE OPN LIN 850 324147-324155(1) | -
|  |  | SINGLE OPN LIN 851 324149-324157(1) | -
|  |  | SINGLE OPN LIN 852 324149-324583(1) | -
|  |  | SINGLE OPN LIN 853 324150-324154(1) | -
|  |  | SINGLE OPN LIN 854 324151-324161(1) | -
|  |  | SINGLE OPN LIN 855 324151-325028(1) | -
|  |  | SINGLE OPN LIN 856 324152-324165(1) | -
|  |  | SINGLE OPN LIN 857 324152-324276(1) | -
|  |  | SINGLE OPN LIN 858 324153-324645(1) | -
|  |  | SINGLE OPN LIN 859 324155-324156(1) | -
|  |  | SINGLE OPN LIN 860 324155-324167(Z1) | -
|  |  | SINGLE OPN LIN 861 324155-324686(1) | -
|  |  | SINGLE OPN LIN 862 324157-324158(1) | -
|  |  | SINGLE OPN LIN 863 324158-324689(1) | -
|  |  | SINGLE OPN LIN 864 324159-324160(1) | -
|  |  | SINGLE OPN LIN 865 324159-324702(1) | -
|  |  | SINGLE OPN LIN 866 324161-324712(1) | -
|  |  | SINGLE OPN LIN 867 324161-325078(1) | -
|  |  | SINGLE OPN LIN 868 324163-324165(1) | -
|  |  | SINGLE OPN LIN 869 324163-324767(1) | -
|  |  | SINGLE OPN LIN 870 324164-324769(1) | -
|  |  | SINGLE OPN LIN 871 324166-324779(1) | -
|  |  | SINGLE OPN LIN 872 324166-325069(1) | -
|  |  | SINGLE OPN LIN 873 324167-324686(2) | -
|  |  | SINGLE OPN LIN 874 324191-324603(1) | -
|  |  | SINGLE OPN LIN 875 324191-324606(1) | -
324192 | 4DAYTON-WALT | 138 | SINGLE OPN LIN 876 324192-324240(1) | 3.5
324193 | 4FLEMINGB KU | 138 | SINGLE OPN LIN 877 324193-324251(1) | 4.82
324195 | 2AUGUSTA | 69 | SINGLE OPN LIN 878 324195-324722(1) | 7
324224 | 2RED HOUSE | 69 | SINGLE OPN LIN 879 324196-324224(1) | 4.24
324196 | 2BOONESB PRK | 69 | SINGLE OPN LIN 880 324196-324449(1) | 3.09
324224 | 2RED HOUSE | 69 | SINGLE OPN LIN 880 324196-324449(1) | 4.24
324198 | 2HUNT BOTTOM | 69 | SINGLE OPN LIN 881 324198-324878(1) | 2.19
324199 | 2OWENTON | 69 | SINGLE OPN LIN 882 324199-324252(1) | 2.89
|  |  | SINGLE OPN LIN 883 324200-324205(1) | -
|  |  | SINGLE OPN LIN 884 324200-324237(1) | -
|  |  | SINGLE OPN LIN 885 324200-324299(1) | -
|  |  | SINGLE OPN LIN 886 324201-324305(1) | -
|  |  | SINGLE OPN LIN 887 324201-324313(1) | -
|  |  | SINGLE OPN LIN 888 324201-324315(1) | -
|  |  | SINGLE OPN LIN 889 324201-324335(1) | -
|  |  | SINGLE OPN LIN 890 324201-324405(1) | -
|  |  | SINGLE OPN LIN 891 324201-324405(2) | -
|  |  | SINGLE OPN LIN 892 324202-324241(1) | -
|  |  | SINGLE OPN LIN 893 324202-324408(1) | -
|  |  | SINGLE OPN LIN 894 324203-324258(1) | -
|  |  | SINGLE OPN LIN 895 324203-324301(1) | -
|  |  | SINGLE OPN LIN 896 324203-324409(1) | -
|  |  | SINGLE OPN LIN 897 324204-324205(1) | -
|  |  | SINGLE OPN LIN 898 324204-324243(1) | -
|  |  | SINGLE OPN LIN 899 324204-324281(1) | -
|  |  | SINGLE OPN LIN 900 324205-324237(1) | -
|  |  | SINGLE OPN LIN 901 324205-324257(1) | -
|  |  | SINGLE OPN LIN 902 324205-324279(1) | -
|  |  | SINGLE OPN LIN 903 324205-324419(1) | -
|  |  | SINGLE OPN LIN 904 324205-325023(2) | -
|  |  | SINGLE OPN LIN 905 324206-324284(1) | -
|  |  | SINGLE OPN LIN 906 324206-324299(1) | -
|  |  | SINGLE OPN LIN 907 324207-324218(1) | -
|  |  | SINGLE OPN LIN 908 324207-324288(1) | -
|  |  | SINGLE OPN LIN 909 324207-324426(1) | -
|  |  | SINGLE OPN LIN 910 324208-324265(1) | -
|  |  | SINGLE OPN LIN 911 324208-324277(1) | -
|  |  | SINGLE OPN LIN 912 324208-324289(1) | -
|  |  | SINGLE OPN LIN 913 324208-324298(1) | -
|  |  | SINGLE OPN LIN 914 324208-324321(1) | -
|  |  | SINGLE OPN LIN 915 324208-324321(2) | -
|  |  | SINGLE OPN LIN 916 324208-324429(1) | -
324209 | 4BG PARKWAY | 138 | SINGLE OPN LIN 917 324209-324263(1) | 48.37
|  |  | SINGLE OPN LIN 918 324210-324262(1) | -
|  |  | SINGLE OPN LIN 919 324210-324334(1) | -
|  |  | SINGLE OPN LIN 920 324211-324221(1) | -
|  |  | SINGLE OPN LIN 921 324211-324253(1) | -
|  |  | SINGLE OPN LIN 922 324212-324285(1) | -
|  |  | SINGLE OPN LIN 923 324213-324270(1) | -
|  |  | SINGLE OPN LIN 924 324213-324447(1) | -
|  |  | SINGLE OPN LIN 925 324213-324800(1) | -
|  |  | SINGLE OPN LIN 926 324214-324243(1) | -
|  |  | SINGLE OPN LIN 927 324214-324263(1) | -
|  |  | SINGLE OPN LIN 928 324214-324451(1) | -
|  |  | SINGLE OPN LIN 929 324215-324237(1) | -
|  |  | SINGLE OPN LIN 930 324215-324284(1) | -
|  |  | SINGLE OPN LIN 931 324217-324219(1) | -
|  |  | SINGLE OPN LIN 932 324217-324220(1) | -
|  |  | SINGLE OPN LIN 933 324217-324239(1) | -
|  |  | SINGLE OPN LIN 934 324217-324248(1) | -
|  |  | SINGLE OPN LIN 935 324218-324219(1) | -
|  |  | SINGLE OPN LIN 936 324218-324220(1) | -
|  |  | SINGLE OPN LIN 937 324218-325957(1) | -
|  |  | SINGLE OPN LIN 938 324219-325957(1) | -
|  |  | SINGLE OPN LIN 939 324220-325956(1) | -
|  |  | SINGLE OPN LIN 940 324221-324225(1) | -
|  |  | SINGLE OPN LIN 941 324222-324237(1) | -
|  |  | SINGLE OPN LIN 942 324222-324295(1) | -
|  |  | SINGLE OPN LIN 943 324223-324294(1) | -
|  |  | SINGLE OPN LIN 944 324223-324321(1) | -
|  |  | SINGLE OPN LIN 945 324223-324462(1) | -
|  |  | SINGLE OPN LIN 946 324225-324226(1) | -
|  |  | SINGLE OPN LIN 947 324225-324267(1) | -
|  |  | SINGLE OPN LIN 948 324226-324463(1) | -
|  |  | SINGLE OPN LIN 949 324227-324274(1) | -
|  |  | SINGLE OPN LIN 950 324227-324466(1) | -
|  |  | SINGLE OPN LIN 951 324227-324466(2) | -
|  |  | SINGLE OPN LIN 952 324227-326512(1) | -
|  |  | SINGLE OPN LIN 953 324228-324281(1) | -
|  |  | SINGLE OPN LIN 954 324228-324469(1) | -
|  |  | SINGLE OPN LIN 955 324228-326520(1) | -
|  |  | SINGLE OPN LIN 956 324229-324236(1) | -
|  |  | SINGLE OPN LIN 957 324229-324310(1) | -
|  |  | SINGLE OPN LIN 958 324229-324472(1) | -
|  |  | SINGLE OPN LIN 959 324230-324262(1) | -
|  |  | SINGLE OPN LIN 960 324230-325957(1) | -
|  |  | SINGLE OPN LIN 961 324231-324256(1) | -
|  |  | SINGLE OPN LIN 962 324231-324260(1) | -
|  |  | SINGLE OPN LIN 963 324231-325132(1) | -
324399 | 1CANERN11 | 14 | SINGLE OPN LIN 964 324232-326574(1) | 5.4
|  |  | SINGLE OPN LIN 965 324236-324248(1) | -
|  |  | SINGLE OPN LIN 966 324237-324295(1) | -
|  |  | SINGLE OPN LIN 967 324237-324488(1) | -
|  |  | SINGLE OPN LIN 968 324237-324488(2) | -
|  |  | SINGLE OPN LIN 969 324237-325096(22) | -
|  |  | SINGLE OPN LIN 970 324237-325096(24) | -
|  |  | SINGLE OPN LIN 971 324237-325096(25) | -
|  |  | SINGLE OPN LIN 972 324237-326565(23) | -
|  |  | SINGLE OPN LIN 973 324237-326574(21) | -
|  |  | SINGLE OPN LIN 974 324238-324239(1) | -
|  |  | SINGLE OPN LIN 975 324238-324495(1) | -
|  |  | SINGLE OPN LIN 976 324239-325121(1) | -
|  |  | SINGLE OPN LIN 977 324240-324242(1) | -
|  |  | SINGLE OPN LIN 978 324240-324287(1) | -
|  |  | SINGLE OPN LIN 979 324241-324295(1) | -
|  |  | SINGLE OPN LIN 980 324242-326512(1) | -
|  |  | SINGLE OPN LIN 981 324243-324518(1) | -
|  |  | SINGLE OPN LIN 982 324244-324261(1) | -
|  |  | SINGLE OPN LIN 983 324244-324288(1) | -
|  |  | SINGLE OPN LIN 984 324244-324519(1) | -
|  |  | SINGLE OPN LIN 985 324245-324246(1) | -
|  |  | SINGLE OPN LIN 986 324245-324307(1) | -
|  |  | SINGLE OPN LIN 987 324245-324310(1) | -
|  |  | SINGLE OPN LIN 988 324246-324528(1) | -
|  |  | SINGLE OPN LIN 989 324247-324248(1) | -
|  |  | SINGLE OPN LIN 990 324247-324276(1) | -
|  |  | SINGLE OPN LIN 991 324248-324530(1) | -
|  |  | SINGLE OPN LIN 992 324248-324530(2) | -
|  |  | SINGLE OPN LIN 993 324249-324257(1) | -
|  |  | SINGLE OPN LIN 994 324249-324292(1) | -
|  |  | SINGLE OPN LIN 995 324249-324322(1) | -
|  |  | SINGLE OPN LIN 996 324249-324532(1) | -
|  |  | SINGLE OPN LIN 997 324249-324532(2) | -
|  |  | SINGLE OPN LIN 998 324250-324306(1) | -
|  |  | SINGLE OPN LIN 999 324250-324315(1) | -
|  |  | SINGLE OPN LIN 1000 324250-324535(1) | -
|  |  | SINGLE OPN LIN 1001 324250-324535(2) | -
|  |  | SINGLE OPN LIN 1002 324251-324254(1) | -
|  |  | SINGLE OPN LIN 1003 324251-324323(1) | -
324199 | 2OWENTON | 69 | SINGLE OPN LIN 1004 324252-324455(1) | 2.89
324252 | 2SCHOLLS | 69 | SINGLE OPN LIN 1004 324252-324455(1) | 1.08
|  |  | SINGLE OPN LIN 1005 324253-324287(1) | -
|  |  | SINGLE OPN LIN 1006 324253-324290(1) | -
|  |  | SINGLE OPN LIN 1007 324253-324831(1) | -
|  |  | SINGLE OPN LIN 1008 324254-324302(1) | -
|  |  | SINGLE OPN LIN 1009 324255-324291(1) | -
|  |  | SINGLE OPN LIN 1010 324255-324550(1) | -
|  |  | SINGLE OPN LIN 1011 324255-324550(2) | -
|  |  | SINGLE OPN LIN 1012 324255-325015(1) | -
|  |  | SINGLE OPN LIN 1013 324256-324551(1) | -
|  |  | SINGLE OPN LIN 1014 324256-325015(1) | -
|  |  | SINGLE OPN LIN 1015 324258-324264(1) | -
|  |  | SINGLE OPN LIN 1016 324258-324317(1) | -
|  |  | SINGLE OPN LIN 1017 324258-324335(1) | -
|  |  | SINGLE OPN LIN 1018 324258-324558(1) | -
|  |  | SINGLE OPN LIN 1019 324258-325100(1) | -
|  |  | SINGLE OPN LIN 1020 324259-324278(1) | -
|  |  | SINGLE OPN LIN 1021 324259-324561(1) | -
|  |  | SINGLE OPN LIN 1022 324260-325055(1) | -
|  |  | SINGLE OPN LIN 1023 324261-324303(1) | -
|  |  | SINGLE OPN LIN 1024 324261-324563(1) | -
|  |  | SINGLE OPN LIN 1025 324261-324563(2) | -
|  |  | SINGLE OPN LIN 1026 324262-324269(1) | -
|  |  | SINGLE OPN LIN 1027 324262-324333(1) | -
|  |  | SINGLE OPN LIN 1028 324262-324568(1) | -
|  |  | SINGLE OPN LIN 1029 324262-324569(1) | -
|  |  | SINGLE OPN LIN 1030 324262-324569(2) | -
|  |  | SINGLE OPN LIN 1031 324262-325089(Z1) | -
|  |  | SINGLE OPN LIN 1032 324263-324297(1) | -
|  |  | SINGLE OPN LIN 1033 324264-324275(1) | -
326548 | 4IBM NORTH | 138 | SINGLE OPN LIN 1034 324264-326548(1) | 2.67
|  |  | SINGLE OPN LIN 1035 324265-324289(1) | -
|  |  | SINGLE OPN LIN 1036 324267-324323(1) | -
|  |  | SINGLE OPN LIN 1037 324267-324589(1) | -
324901 | 2MAYSVILLE W | 69 | SINGLE OPN LIN 1038 324267-324882(1) | 3.7
|  |  | SINGLE OPN LIN 1039 324268-324284(1) | -
|  |  | SINGLE OPN LIN 1040 324268-324300(1) | -
|  |  | SINGLE OPN LIN 1041 324269-324601(1) | -
|  |  | SINGLE OPN LIN 1042 324270-324271(1) | -
|  |  | SINGLE OPN LIN 1043 324271-324606(1) | -
|  |  | SINGLE OPN LIN 1044 324271-324606(2) | -
|  |  | SINGLE OPN LIN 1045 324271-325121(1) | -
|  |  | SINGLE OPN LIN 1046 324272-324308(1) | -
|  |  | SINGLE OPN LIN 1047 324272-324609(1) | -
|  |  | SINGLE OPN LIN 1048 324273-326559(Z1) | -
|  |  | SINGLE OPN LIN 1049 324274-324306(1) | -
|  |  | SINGLE OPN LIN 1050 324275-324618(1) | -
|  |  | SINGLE OPN LIN 1051 324276-326559(1) | -
|  |  | SINGLE OPN LIN 1052 324277-324281(1) | -
|  |  | SINGLE OPN LIN 1053 324277-324622(1) | -
|  |  | SINGLE OPN LIN 1054 324278-324321(1) | -
|  |  | SINGLE OPN LIN 1055 324279-324284(1) | -
|  |  | SINGLE OPN LIN 1056 324281-324282(1) | -
|  |  | SINGLE OPN LIN 1057 324281-324364(1) | -
|  |  | SINGLE OPN LIN 1058 324281-324637(1) | -
|  |  | SINGLE OPN LIN 1059 324281-324637(2) | -
|  |  | SINGLE OPN LIN 1060 324281-324637(6) | -
|  |  | SINGLE OPN LIN 1061 324281-325042(1) | -
|  |  | SINGLE OPN LIN 1062 324282-324298(1) | -
|  |  | SINGLE OPN LIN 1063 324283-324320(1) | -
|  |  | SINGLE OPN LIN 1064 324283-324831(1) | -
|  |  | SINGLE OPN LIN 1065 324284-324640(7) | -
|  |  | SINGLE OPN LIN 1066 324284-324640(8) | -
325057 | 4KOSMOS CEME | 138 | SINGLE OPN LIN 1067 324284-325088(1) | 27.23
|  |  | SINGLE OPN LIN 1068 324285-324292(1) | -
|  |  | SINGLE OPN LIN 1069 324285-324651(1) | -
|  |  | SINGLE OPN LIN 1070 324286-324287(1) | -
|  |  | SINGLE OPN LIN 1071 324289-325013(1) | -
|  |  | SINGLE OPN LIN 1072 324290-324305(1) | -
|  |  | SINGLE OPN LIN 1073 324291-324667(1) | -
|  |  | SINGLE OPN LIN 1074 324294-324295(1) | -
|  |  | SINGLE OPN LIN 1075 324296-324320(1) | -
|  |  | SINGLE OPN LIN 1076 324296-324687(1) | -
|  |  | SINGLE OPN LIN 1077 324296-325857(1) | -
|  |  | SINGLE OPN LIN 1078 324297-324298(1) | -
|  |  | SINGLE OPN LIN 1079 324300-324311(1) | -
|  |  | SINGLE OPN LIN 1080 324301-325089(1) | -
|  |  | SINGLE OPN LIN 1081 324302-324307(1) | -
|  |  | SINGLE OPN LIN 1082 324303-324708(1) | -
324304 | 2VERSAILLE W | 69 | SINGLE OPN LIN 1083 324304-324762(1) | 11.32
|  |  | SINGLE OPN LIN 1084 324305-324951(1) | -
|  |  | SINGLE OPN LIN 1085 324305-324991(1) | -
326526 | 4N SHARKEY | 138 | SINGLE OPN LIN 1086 324307-326556(1) | 1.2322
326532 | 4SHARKEY | 138 | SINGLE OPN LIN 1086 324307-326556(1) | 8.4668
|  |  | SINGLE OPN LIN 1087 324310-324733(1) | -
324524 | 2EWINGTON | 69 | SINGLE OPN LIN 1088 324310-325009(1) | 20.32
324921 | 2ARCH CHEM | 69 | SINGLE OPN LIN 1089 324311-324976(3) | 6.49
|  |  | SINGLE OPN LIN 1090 324311-325132(1) | -
|  |  | SINGLE OPN LIN 1091 324312-324313(1) | -
|  |  | SINGLE OPN LIN 1092 324312-324991(1) | -
|  |  | SINGLE OPN LIN 1093 324314-326520(Z1) | -
|  |  | SINGLE OPN LIN 1094 324315-324755(1) | -
|  |  | SINGLE OPN LIN 1095 324315-325957(1) | -
|  |  | SINGLE OPN LIN 1096 324316-324759(1) | -
|  |  | SINGLE OPN LIN 1097 324317-325101(1) | -
|  |  | SINGLE OPN LIN 1098 324318-324764(1) | -
|  |  | SINGLE OPN LIN 1099 324318-324764(2) | -
|  |  | SINGLE OPN LIN 1100 324319-324765(1) | -
|  |  | SINGLE OPN LIN 1101 324320-325089(1) | -
|  |  | SINGLE OPN LIN 1102 324320-325100(1) | -
|  |  | SINGLE OPN LIN 1103 324320-325101(1) | -
|  |  | SINGLE OPN LIN 1104 324322-324771(1) | -
|  |  | SINGLE OPN LIN 1105 324322-324771(2) | -
|  |  | SINGLE OPN LIN 1106 324322-325042(1) | -
|  |  | SINGLE OPN LIN 1107 324328-324680(1) | -
|  |  | SINGLE OPN LIN 1108 324329-324364(1) | -
|  |  | SINGLE OPN LIN 1109 324329-324481(1) | -
324330 | 2WINCHES IND | 69 | SINGLE OPN LIN 1110 324330-324783(1) | 11.23
325063 | 2CORPORAT DR | 69 | SINGLE OPN LIN 1110 324330-324783(1) | 21.31
325063 | 2CORPORAT DR | 69 | SINGLE OPN LIN 1111 324330-325063(1) | 21.31
324331 | 2ASHLAND AVE | 69 | SINGLE OPN LIN 1112 324331-324418(1) | 14.14
324332 | 2LAKE SHORE | 69 | SINGLE OPN LIN 1113 324332-325059(1) | 25.39
|  |  | SINGLE OPN LIN 1114 324333-325957(1) | -
|  |  | SINGLE OPN LIN 1115 324334-325956(1) | -
324337 | 2MOUNT TABOR | 69 | SINGLE OPN LIN 1116 324337-324650(1) | 0.99
324339 | 2SCOTT ST 12 | 69 | SINGLE OPN LIN 1117 324338-324339(1) | 13.4
324338 | 2SCOTT ST 4 | 69 | SINGLE OPN LIN 1118 324338-324952(1) | 4.24
324339 | 2SCOTT ST 12 | 69 | SINGLE OPN LIN 1118 324338-324952(1) | 13.4
324340 | 2SPINDLETOP | 69 | SINGLE OPN LIN 1119 324340-324734(1) | 1.54
324341 | 2WILMORE | 69 | SINGLE OPN LIN 1120 324341-324781(1) | 10.1
324344 | 2ATOKA | 69 | SINGLE OPN LIN 1121 324344-324421(1) | 3.33
324345 | 2BARDTWN IND | 69 | SINGLE OPN LIN 1122 324345-324425(1) | 17.37
324346 | 2RICHMND E | 69 | SINGLE OPN LIN 1123 324346-324612(1) | 11.03
324347 | 2BEATTY 649 | 69 | SINGLE OPN LIN 1124 324347-325058(1) | 2.56
324348 | 2BRODHEAD CI | 69 | SINGLE OPN LIN 1125 324348-324808(1) | 2.14
324068 | 2E CAMPBELVL | 69 | SINGLE OPN LIN 1126 324349-324479(1) | 7.2306
324349 | 2CAMPBELVIL2 | 69 | SINGLE OPN LIN 1126 324349-324479(1) | 7.53
324350 | 2CRAB ORCHAR | 69 | SINGLE OPN LIN 1127 324350-324485(1) | 1.41
324354 | 2GATES RUBBR | 69 | SINGLE OPN LIN 1128 324351-324354(1) | 0.18
326561 | 2ETOWN WEST | 69 | SINGLE OPN LIN 1128 324351-324354(1) | 14.78
324351 | 2ETOWN 3 | 69 | SINGLE OPN LIN 1129 324351-324519(1) | 6.22
324354 | 2GATES RUBBR | 69 | SINGLE OPN LIN 1129 324351-324519(1) | 0.18
326561 | 2ETOWN WEST | 69 | SINGLE OPN LIN 1129 324351-324519(1) | 14.78
324352 | 2ETOWN IND | 69 | SINGLE OPN LIN 1130 324352-324563(1) | 11.79
324353 | 2FLORDA TILE | 69 | SINGLE OPN LIN 1131 324353-324863(1) | 11.99
326561 | 2ETOWN WEST | 69 | SINGLE OPN LIN 1132 324354-326561(1) | 14.78
324356 | 2HARRDSBRG12 | 69 | SINGLE OPN LIN 1133 324355-325054(1) | 7.67
325054 | 2HARRDSBRG N | 69 | SINGLE OPN LIN 1133 324355-325054(1) | 8.3
324355 | 2HARRDSBRG 4 | 69 | SINGLE OPN LIN 1134 324355-326578(1) | 2.1
324356 | 2HARRDSBRG12 | 69 | SINGLE OPN LIN 1134 324355-326578(1) | 7.67
325054 | 2HARRDSBRG N | 69 | SINGLE OPN LIN 1134 324355-326578(1) | 8.3
324356 | 2HARRDSBRG12 | 69 | SINGLE OPN LIN 1135 324356-325054(1) | 7.67
324357 | 2LANCASTER 1 | 69 | SINGLE OPN LIN 1136 324357-324600(1) | 5.49
324358 | 2M-V CLARKSN | 69 | SINGLE OPN LIN 1137 324358-324914(1) | 2.49
324359 | 2MT VERN 589 | 69 | SINGLE OPN LIN 1138 324359-324913(1) | 4.26
324360 | 2PINE HILL | 69 | SINGLE OPN LIN 1139 324360-324927(1) | 1.07
324361 | 2RADCLIFF KU | 69 | SINGLE OPN LIN 1140 324361-324935(1) | 7.78
324363 | 2SHELB CI KU | 69 | SINGLE OPN LIN 1141 324363-324957(1) | 4.35
326518 | 2SHELB CI EK | 69 | SINGLE OPN LIN 1141 324363-324957(1) | 13.6767
326518 | 2SHELB CI EK | 69 | SINGLE OPN LIN 1142 324363-326518(1) | 13.6767
324372 | 2BURNSIDE | 69 | SINGLE OPN LIN 1143 324372-324514(1) | 5.59
324373 | 2CATRON CRK | 69 | SINGLE OPN LIN 1144 324373-324814(1) | 1.04
324374 | 2CROCKETT KU | 69 | SINGLE OPN LIN 1145 324374-324376(1) | 1.37
324377 | 2GARDNER | 69 | SINGLE OPN LIN 1145 324374-324376(1) | 0.27
326544 | 2ALEX CREEK | 69 | SINGLE OPN LIN 1145 324374-324376(1) | 1.3637
324377 | 2GARDNER | 69 | SINGLE OPN LIN 1146 324374-325083(1) | 0.27
326544 | 2ALEX CREEK | 69 | SINGLE OPN LIN 1146 324374-325083(1) | 1.3637
324375 | 2DAYHOIT | 69 | SINGLE OPN LIN 1147 324375-324442(1) | 2.59
324374 | 2CROCKETT KU | 69 | SINGLE OPN LIN 1148 324376-324813(1) | 1.37
324376 | 2DEER BRANCH | 69 | SINGLE OPN LIN 1148 324376-324813(1) | 0.57
324377 | 2GARDNER | 69 | SINGLE OPN LIN 1148 324376-324813(1) | 0.27
326544 | 2ALEX CREEK | 69 | SINGLE OPN LIN 1148 324376-324813(1) | 1.3637
324377 | 2GARDNER | 69 | SINGLE OPN LIN 1149 324377-325083(1) | 0.27
324378 | 2MIDDLBO780 | 69 | SINGLE OPN LIN 1150 324378-324636(1) | 10.53
324393 | 2ROSE HILL | 69 | SINGLE OPN LIN 1151 324380-324393(1) | 3.59
324380 | 2DANIEL BRAN | 69 | SINGLE OPN LIN 1152 324380-324945(1) | 0.49
324393 | 2ROSE HILL | 69 | SINGLE OPN LIN 1152 324380-324945(1) | 3.59
324381 | 2WILLAMSBURG | 69 | SINGLE OPN LIN 1153 324381-325001(1) | 2.98
324382 | 2WILLMBRG SO | 69 | SINGLE OPN LIN 1154 324382-325001(1) | 13.08
324384 | 2APPALACHIA | 69 | SINGLE OPN LIN 1155 324384-324549(1) | 2.5
324385 | 2BIG STONE G | 69 | SINGLE OPN LIN 1156 324385-324549(1) | 12.29
324386 | 2DIXIANA | 69 | SINGLE OPN LIN 1157 324386-324388(1) | 4.13
324386 | 2DIXIANA | 69 | SINGLE OPN LIN 1158 324387-324392(1) | 4.13
324392 | 2ROCKY FORK | 69 | SINGLE OPN LIN 1158 324387-324392(1) | 0.15
325031 | 2LIPPS | 69 | SINGLE OPN LIN 1158 324387-324392(1) | 0.29
324386 | 2DIXIANA | 69 | SINGLE OPN LIN 1159 324387-325064(1) | 4.13
324387 | 2ADDINGTON | 69 | SINGLE OPN LIN 1159 324387-325064(1) | 0.74
324392 | 2ROCKY FORK | 69 | SINGLE OPN LIN 1159 324387-325064(1) | 0.15
325031 | 2LIPPS | 69 | SINGLE OPN LIN 1159 324387-325064(1) | 0.29
324386 | 2DIXIANA | 69 | SINGLE OPN LIN 1160 324388-325031(1) | 4.13
324389 | 2DWINA | 69 | SINGLE OPN LIN 1161 324389-324851(1) | 0.8
324390 | 2PENNINGTON | 69 | SINGLE OPN LIN 1162 324390-324391(1) | 0.97
324390 | 2PENNINGTON | 69 | SINGLE OPN LIN 1163 324391-324689(1) | 0.97
324391 | 2POOR VALLEY | 69 | SINGLE OPN LIN 1163 324391-324689(1) | 5.18
324386 | 2DIXIANA | 69 | SINGLE OPN LIN 1164 324392-325031(1) | 4.13
325031 | 2LIPPS | 69 | SINGLE OPN LIN 1164 324392-325031(1) | 0.29
324394 | 2TOMS CREEK | 69 | SINGLE OPN LIN 1165 324394-324977(1) | 5.62
324395 | 2WISE | 69 | SINGLE OPN LIN 1166 324395-325005(1) | 6.07
|  |  | SINGLE OPN LIN 1167 324400-324510(1) | -
|  |  | SINGLE OPN LIN 1168 324400-324775(1) | -
|  |  | SINGLE OPN LIN 1169 324400-325022(1) | -
|  |  | SINGLE OPN LIN 1170 324401-324541(1) | -
|  |  | SINGLE OPN LIN 1171 324401-324545(1) | -
|  |  | SINGLE OPN LIN 1172 324401-324785(1) | -
324859 | 2FAIRMOUNT 1 | 69 | SINGLE OPN LIN 1173 324402-324859(1) | 21.19
|  |  | SINGLE OPN LIN 1174 324403-324469(1) | -
|  |  | SINGLE OPN LIN 1175 324403-324487(1) | -
|  |  | SINGLE OPN LIN 1176 324403-324616(1) | -
|  |  | SINGLE OPN LIN 1177 324404-324622(1) | -
|  |  | SINGLE OPN LIN 1178 324404-324623(1) | -
|  |  | SINGLE OPN LIN 1179 324404-324750(1) | -
|  |  | SINGLE OPN LIN 1180 324405-324547(1) | -
|  |  | SINGLE OPN LIN 1181 324405-326989(1) | -
|  |  | SINGLE OPN LIN 1182 324406-324637(1) | -
|  |  | SINGLE OPN LIN 1183 324406-324673(1) | -
|  |  | SINGLE OPN LIN 1184 324406-325022(1) | -
|  |  | SINGLE OPN LIN 1185 324407-324755(1) | -
|  |  | SINGLE OPN LIN 1186 324407-324955(1) | -
|  |  | SINGLE OPN LIN 1187 324408-324552(1) | -
|  |  | SINGLE OPN LIN 1188 324408-324625(1) | -
|  |  | SINGLE OPN LIN 1189 324408-324649(1) | -
|  |  | SINGLE OPN LIN 1190 324408-324719(1) | -
|  |  | SINGLE OPN LIN 1191 324408-324739(1) | -
|  |  | SINGLE OPN LIN 1192 324409-324632(1) | -
|  |  | SINGLE OPN LIN 1193 324409-324683(1) | -
|  |  | SINGLE OPN LIN 1194 324409-324772(1) | -
|  |  | SINGLE OPN LIN 1195 324411-324440(1) | -
|  |  | SINGLE OPN LIN 1196 324411-324583(1) | -
324369 | 1WENTZ | 34.5 | SINGLE OPN LIN 1197 324411-324670(1) | 3.87
324670 | 2OSAKA EAST | 69 | SINGLE OPN LIN 1197 324411-324670(1) | 0.46
324369 | 1WENTZ | 34.5 | SINGLE OPN LIN 1198 324412-324670(1) | 3.87
324414 | 2AO SMITH | 69 | SINGLE OPN LIN 1199 324413-324414(1) | 8.26
326531 | 2HINKSTON | 69 | SINGLE OPN LIN 1199 324413-324414(1) | 3.5628
|  |  | SINGLE OPN LIN 1200 324413-324461(1) | -
|  |  | SINGLE OPN LIN 1201 324413-324733(1) | -
326531 | 2HINKSTON | 69 | SINGLE OPN LIN 1202 324414-326531(1) | 3.5628
|  |  | SINGLE OPN LIN 1203 324415-324593(1) | -
|  |  | SINGLE OPN LIN 1204 324415-324636(1) | -
|  |  | SINGLE OPN LIN 1205 324416-324433(1) | -
|  |  | SINGLE OPN LIN 1206 324416-324490(1) | -
|  |  | SINGLE OPN LIN 1207 324417-324423(1) | -
|  |  | SINGLE OPN LIN 1208 324418-324632(1) | -
|  |  | SINGLE OPN LIN 1209 324418-324934(1) | -
|  |  | SINGLE OPN LIN 1210 324419-325024(1) | -
|  |  | SINGLE OPN LIN 1211 324421-324450(1) | -
|  |  | SINGLE OPN LIN 1212 324421-324495(1) | -
|  |  | SINGLE OPN LIN 1213 324422-324508(1) | -
|  |  | SINGLE OPN LIN 1214 324422-324680(1) | -
325081 | 2BRIAR HILL | 69 | SINGLE OPN LIN 1215 324422-325081(1) | 4.05
|  |  | SINGLE OPN LIN 1216 324423-324438(1) | -
|  |  | SINGLE OPN LIN 1217 324424-324801(1) | -
|  |  | SINGLE OPN LIN 1218 324424-326537(1) | -
|  |  | SINGLE OPN LIN 1219 324425-324426(1) | -
|  |  | SINGLE OPN LIN 1220 324426-324525(1) | -
|  |  | SINGLE OPN LIN 1221 324426-326537(Z1) | -
|  |  | SINGLE OPN LIN 1222 324427-324779(1) | -
|  |  | SINGLE OPN LIN 1223 324427-324823(1) | -
|  |  | SINGLE OPN LIN 1224 324428-324778(1) | -
|  |  | SINGLE OPN LIN 1225 324428-324864(1) | -
|  |  | SINGLE OPN LIN 1226 324429-324453(1) | -
|  |  | SINGLE OPN LIN 1227 324429-324475(1) | -
|  |  | SINGLE OPN LIN 1228 324429-324624(1) | -
|  |  | SINGLE OPN LIN 1229 324429-324710(1) | -
|  |  | SINGLE OPN LIN 1230 324430-325058(1) | -
|  |  | SINGLE OPN LIN 1231 324432-324558(1) | -
|  |  | SINGLE OPN LIN 1232 324432-324879(1) | -
|  |  | SINGLE OPN LIN 1233 324433-324621(1) | -
324435 | 2BEREA NORTH | 69 | SINGLE OPN LIN 1234 324434-324435(1) | 11.01
324676 | 2PAINT LICK | 69 | SINGLE OPN LIN 1234 324434-324435(1) | 1.03
324805 | 2BEREA 2 | 69 | SINGLE OPN LIN 1234 324434-324435(1) | 11.66
|  |  | SINGLE OPN LIN 1235 324434-324668(1) | -
324676 | 2PAINT LICK | 69 | SINGLE OPN LIN 1236 324435-324805(1) | 1.03
324805 | 2BEREA 2 | 69 | SINGLE OPN LIN 1236 324435-324805(1) | 11.66
324676 | 2PAINT LICK | 69 | SINGLE OPN LIN 1237 324436-324676(1) | 1.03
324676 | 2PAINT LICK | 69 | SINGLE OPN LIN 1238 324436-324805(1) | 1.03
|  |  | SINGLE OPN LIN 1239 324437-324745(1) | -
|  |  | SINGLE OPN LIN 1240 324438-324515(1) | -
|  |  | SINGLE OPN LIN 1241 324438-324573(1) | -
|  |  | SINGLE OPN LIN 1242 324439-324518(1) | -
|  |  | SINGLE OPN LIN 1243 324439-324532(1) | -
|  |  | SINGLE OPN LIN 1244 324440-324621(1) | -
|  |  | SINGLE OPN LIN 1245 324441-324503(1) | -
|  |  | SINGLE OPN LIN 1246 324441-324802(1) | -
324375 | 2DAYHOIT | 69 | SINGLE OPN LIN 1247 324442-324497(1) | 2.59
325008 | 2BLEDSOE | 69 | SINGLE OPN LIN 1247 324442-324497(1) | 2.5456
325026 | 2PINE MOUNTN | 69 | SINGLE OPN LIN 1247 324442-324497(1) | 2.4546
325008 | 2BLEDSOE | 69 | SINGLE OPN LIN 1248 324442-325008(1) | 2.5456
325026 | 2PINE MOUNTN | 69 | SINGLE OPN LIN 1248 324442-325008(1) | 2.4546
324806 | 2BEULAH EKPC | 69 | SINGLE OPN LIN 1249 324443-324789(1) | 10.5644
324915 | 2MT WAS EK J | 69 | SINGLE OPN LIN 1249 324443-324789(1) | 23.6017
325006 | 2W MT WSH EK | 69 | SINGLE OPN LIN 1249 324443-324789(1) | 13.7413
325021 | 2CONESTOGA | 69 | SINGLE OPN LIN 1249 324443-324789(1) | 12.55
|  |  | SINGLE OPN LIN 1250 324444-324651(1) | -
|  |  | SINGLE OPN LIN 1251 324444-324788(1) | -
|  |  | SINGLE OPN LIN 1252 324445-324620(1) | -
324732 | 2SOUTHVILLE | 69 | SINGLE OPN LIN 1253 324445-324732(1) | 8.7902
|  |  | SINGLE OPN LIN 1254 324445-324863(1) | -
|  |  | SINGLE OPN LIN 1255 324445-325087(1) | -
|  |  | SINGLE OPN LIN 1256 324446-324824(1) | -
|  |  | SINGLE OPN LIN 1257 324446-324977(1) | -
|  |  | SINGLE OPN LIN 1258 324447-324731(1) | -
|  |  | SINGLE OPN LIN 1259 324448-324782(1) | -
|  |  | SINGLE OPN LIN 1260 324448-325004(1) | -
|  |  | SINGLE OPN LIN 1261 324449-325004(1) | -
|  |  | SINGLE OPN LIN 1262 324449-325925(1) | -
|  |  | SINGLE OPN LIN 1263 324450-324494(1) | -
|  |  | SINGLE OPN LIN 1264 324451-324574(1) | -
|  |  | SINGLE OPN LIN 1265 324451-324673(1) | -
|  |  | SINGLE OPN LIN 1266 324453-324475(1) | -
|  |  | SINGLE OPN LIN 1267 324455-324966(1) | -
|  |  | SINGLE OPN LIN 1268 324456-324465(1) | -
|  |  | SINGLE OPN LIN 1269 324456-324593(1) | -
|  |  | SINGLE OPN LIN 1270 324457-324610(1) | -
|  |  | SINGLE OPN LIN 1271 324457-324986(1) | -
|  |  | SINGLE OPN LIN 1272 324458-324501(1) | -
|  |  | SINGLE OPN LIN 1273 324458-324546(1) | -
324626 | 2MANCHEST SO | 69 | SINGLE OPN LIN 1274 324459-324626(1) | 4.76
324627 | 2MANCHEST KU | 69 | SINGLE OPN LIN 1274 324459-324626(1) | 3.54
326533 | 2BUSH EKPC | 69 | SINGLE OPN LIN 1275 324459-326533(1) | 5.967
|  |  | SINGLE OPN LIN 1276 324460-324686(1) | -
|  |  | SINGLE OPN LIN 1277 324460-324706(1) | -
|  |  | SINGLE OPN LIN 1278 324461-324912(1) | -
|  |  | SINGLE OPN LIN 1279 324462-324499(1) | -
|  |  | SINGLE OPN LIN 1280 324462-324624(1) | -
|  |  | SINGLE OPN LIN 1281 324462-324625(1) | -
|  |  | SINGLE OPN LIN 1282 324462-324665(1) | -
|  |  | SINGLE OPN LIN 1283 324462-324666(1) | -
|  |  | SINGLE OPN LIN 1284 324464-324615(1) | -
|  |  | SINGLE OPN LIN 1285 324464-324860(1) | -
|  |  | SINGLE OPN LIN 1286 324465-324784(1) | -
326535 | 2CARPENTER | 69 | SINGLE OPN LIN 1287 324465-326535(1) | 11.7579
|  |  | SINGLE OPN LIN 1288 324466-324602(1) | -
|  |  | SINGLE OPN LIN 1289 324466-324634(1) | -
|  |  | SINGLE OPN LIN 1290 324467-324528(1) | -
|  |  | SINGLE OPN LIN 1291 324467-324714(1) | -
326538 | 2CAVE RUN | 69 | SINGLE OPN LIN 1292 324467-326538(1) | 1.4141
|  |  | SINGLE OPN LIN 1293 324468-324572(1) | -
|  |  | SINGLE OPN LIN 1294 324468-324817(1) | -
|  |  | SINGLE OPN LIN 1295 324469-324681(1) | -
|  |  | SINGLE OPN LIN 1296 324469-324682(1) | -
|  |  | SINGLE OPN LIN 1297 324470-324486(1) | -
|  |  | SINGLE OPN LIN 1298 324470-324948(1) | -
|  |  | SINGLE OPN LIN 1299 324471-324777(1) | -
|  |  | SINGLE OPN LIN 1300 324471-324822(1) | -
|  |  | SINGLE OPN LIN 1301 324472-324540(1) | -
|  |  | SINGLE OPN LIN 1302 324472-324749(1) | -
|  |  | SINGLE OPN LIN 1303 324473-324561(1) | -
|  |  | SINGLE OPN LIN 1304 324473-324570(1) | -
|  |  | SINGLE OPN LIN 1305 324473-324624(1) | -
|  |  | SINGLE OPN LIN 1306 324474-324725(1) | -
|  |  | SINGLE OPN LIN 1307 324474-324765(1) | -
|  |  | SINGLE OPN LIN 1308 324475-324574(1) | -
|  |  | SINGLE OPN LIN 1309 324476-324581(1) | -
|  |  | SINGLE OPN LIN 1310 324476-324680(1) | -
|  |  | SINGLE OPN LIN 1311 324477-324502(1) | -
|  |  | SINGLE OPN LIN 1312 324477-324645(1) | -
|  |  | SINGLE OPN LIN 1313 324478-324516(1) | -
|  |  | SINGLE OPN LIN 1314 324478-324828(1) | -
|  |  | SINGLE OPN LIN 1315 324479-324751(1) | -
|  |  | SINGLE OPN LIN 1316 324479-324889(1) | -
|  |  | SINGLE OPN LIN 1317 324480-324515(1) | -
|  |  | SINGLE OPN LIN 1318 324480-324615(1) | -
326521 | 2CAMPGRND EK | 69 | SINGLE OPN LIN 1319 324480-326521(1) | 10.5141
|  |  | SINGLE OPN LIN 1320 324481-324487(1) | -
|  |  | SINGLE OPN LIN 1321 324481-324541(1) | -
|  |  | SINGLE OPN LIN 1322 324482-324748(1) | -
|  |  | SINGLE OPN LIN 1323 324482-324832(1) | -
|  |  | SINGLE OPN LIN 1324 324484-324571(1) | -
|  |  | SINGLE OPN LIN 1325 324484-324711(1) | -
|  |  | SINGLE OPN LIN 1326 324485-324600(1) | -
|  |  | SINGLE OPN LIN 1327 324485-324808(1) | -
|  |  | SINGLE OPN LIN 1328 324486-324628(1) | -
|  |  | SINGLE OPN LIN 1329 324488-324529(1) | -
|  |  | SINGLE OPN LIN 1330 324488-324724(1) | -
|  |  | SINGLE OPN LIN 1331 324488-324739(1) | -
|  |  | SINGLE OPN LIN 1332 324489-324654(1) | -
|  |  | SINGLE OPN LIN 1333 324489-324784(1) | -
325034 | 2CUMBER FALL | 69 | SINGLE OPN LIN 1334 324489-325034(1) | 8.1243
|  |  | SINGLE OPN LIN 1335 324490-324827(1) | -
|  |  | SINGLE OPN LIN 1336 324491-324837(1) | -
|  |  | SINGLE OPN LIN 1337 324491-325085(1) | -
|  |  | SINGLE OPN LIN 1338 324492-324595(1) | -
|  |  | SINGLE OPN LIN 1339 324493-324518(1) | -
|  |  | SINGLE OPN LIN 1340 324493-324570(1) | -
|  |  | SINGLE OPN LIN 1341 324494-324840(1) | -
|  |  | SINGLE OPN LIN 1342 324495-326579(1) | -
|  |  | SINGLE OPN LIN 1343 324496-324767(1) | -
|  |  | SINGLE OPN LIN 1344 324496-324880(1) | -
|  |  | SINGLE OPN LIN 1345 324497-324564(1) | -
|  |  | SINGLE OPN LIN 1346 324497-324588(1) | -
|  |  | SINGLE OPN LIN 1347 324498-324621(1) | -
|  |  | SINGLE OPN LIN 1348 324498-324876(1) | -
|  |  | SINGLE OPN LIN 1349 324499-324552(1) | -
324672 | 2OXFORD EK T | 69 | SINGLE OPN LIN 1350 324500-324924(1) | 5.9966
324924 | 2OXFORD | 69 | SINGLE OPN LIN 1350 324500-324924(1) | 15.68
325027 | 2NEWTOWN | 69 | SINGLE OPN LIN 1350 324500-324924(1) | 5.78
|  |  | SINGLE OPN LIN 1351 324501-324764(1) | -
|  |  | SINGLE OPN LIN 1352 324502-324658(1) | -
324386 | 2DIXIANA | 69 | SINGLE OPN LIN 1353 324503-325064(1) | 4.13
324387 | 2ADDINGTON | 69 | SINGLE OPN LIN 1353 324503-325064(1) | 0.74
324392 | 2ROCKY FORK | 69 | SINGLE OPN LIN 1353 324503-325064(1) | 0.15
325031 | 2LIPPS | 69 | SINGLE OPN LIN 1353 324503-325064(1) | 0.29
325064 | 2LAUREL GROV | 69 | SINGLE OPN LIN 1353 324503-325064(1) | 0.25
|  |  | SINGLE OPN LIN 1354 324504-324662(1) | -
|  |  | SINGLE OPN LIN 1355 324504-324927(1) | -
|  |  | SINGLE OPN LIN 1356 324505-324506(1) | -
|  |  | SINGLE OPN LIN 1357 324505-324947(1) | -
|  |  | SINGLE OPN LIN 1358 324506-324769(1) | -
|  |  | SINGLE OPN LIN 1359 324506-324954(1) | -
|  |  | SINGLE OPN LIN 1360 324507-324769(1) | -
|  |  | SINGLE OPN LIN 1361 324507-324850(1) | -
|  |  | SINGLE OPN LIN 1362 324508-324617(1) | -
|  |  | SINGLE OPN LIN 1363 324509-324914(1) | -
|  |  | SINGLE OPN LIN 1364 324510-324729(1) | -
|  |  | SINGLE OPN LIN 1365 324511-324584(1) | -
|  |  | SINGLE OPN LIN 1366 324511-324959(1) | -
|  |  | SINGLE OPN LIN 1367 324512-324693(1) | -
|  |  | SINGLE OPN LIN 1368 324513-324693(1) | -
|  |  | SINGLE OPN LIN 1369 324513-324885(1) | -
|  |  | SINGLE OPN LIN 1370 324514-324531(1) | -
|  |  | SINGLE OPN LIN 1371 324514-324654(1) | -
324845 | 2DENHAM ST | 69 | SINGLE OPN LIN 1372 324514-324962(1) | 8.04
324961 | 2SOMERSET GE | 69 | SINGLE OPN LIN 1372 324514-324962(1) | 0.18
324962 | 2SOMERSET 1 | 69 | SINGLE OPN LIN 1372 324514-324962(1) | 2.95
324963 | 2SOMERSET 2 | 69 | SINGLE OPN LIN 1372 324514-324962(1) | 3.38
326530 | 2EMANUEL | 69 | SINGLE OPN LIN 1373 324515-326530(1) | 9.7548
326539 | 2GIRDLER | 69 | SINGLE OPN LIN 1373 324515-326530(1) | 4.6408
|  |  | SINGLE OPN LIN 1374 324516-324585(1) | -
|  |  | SINGLE OPN LIN 1375 324516-324727(1) | -
|  |  | SINGLE OPN LIN 1376 324517-325005(1) | -
|  |  | SINGLE OPN LIN 1377 324518-324657(1) | -
|  |  | SINGLE OPN LIN 1378 324519-324520(1) | -
|  |  | SINGLE OPN LIN 1379 324519-324521(1) | -
|  |  | SINGLE OPN LIN 1380 324519-324563(1) | -
|  |  | SINGLE OPN LIN 1381 324519-324563(2) | -
|  |  | SINGLE OPN LIN 1382 324520-326555(1) | -
|  |  | SINGLE OPN LIN 1383 324521-324575(1) | -
|  |  | SINGLE OPN LIN 1384 324522-324523(1) | -
|  |  | SINGLE OPN LIN 1385 324522-324692(1) | -
|  |  | SINGLE OPN LIN 1386 324522-324761(1) | -
|  |  | SINGLE OPN LIN 1387 324523-324798(1) | -
324524 | 2EWINGTON | 69 | SINGLE OPN LIN 1388 324524-325009(1) | 20.32
|  |  | SINGLE OPN LIN 1389 324525-324974(1) | -
324526 | 2FAIRMOUNT 2 | 69 | SINGLE OPN LIN 1390 324526-324730(1) | 23.62
|  |  | SINGLE OPN LIN 1391 324527-324704(1) | -
|  |  | SINGLE OPN LIN 1392 324527-324758(1) | -
|  |  | SINGLE OPN LIN 1393 324528-324647(1) | -
|  |  | SINGLE OPN LIN 1394 324529-324675(1) | -
|  |  | SINGLE OPN LIN 1395 324529-324724(1) | -
|  |  | SINGLE OPN LIN 1396 324530-324701(1) | -
324126 | 1FORK ELK | 34.5 | SINGLE OPN LIN 1397 324533-324535(1) | 7.75
324343 | 1STMP GRD | 34.5 | SINGLE OPN LIN 1397 324533-324535(1) | 5.55
324396 | 1WOODLAKE | 34.5 | SINGLE OPN LIN 1397 324533-324535(1) | 1.18
|  |  | SINGLE OPN LIN 1398 324534-324535(1) | -
|  |  | SINGLE OPN LIN 1399 324534-324762(1) | -
|  |  | SINGLE OPN LIN 1400 324535-326528(1) | -
|  |  | SINGLE OPN LIN 1401 324536-324653(1) | -
|  |  | SINGLE OPN LIN 1402 324536-324718(1) | -
|  |  | SINGLE OPN LIN 1403 324536-324752(1) | -
|  |  | SINGLE OPN LIN 1404 324537-324620(1) | -
|  |  | SINGLE OPN LIN 1405 324537-324755(1) | -
|  |  | SINGLE OPN LIN 1406 324538-324561(1) | -
|  |  | SINGLE OPN LIN 1407 324538-324614(1) | -
|  |  | SINGLE OPN LIN 1408 324539-324601(1) | -
|  |  | SINGLE OPN LIN 1409 324539-324613(1) | -
|  |  | SINGLE OPN LIN 1410 324540-324912(1) | -
|  |  | SINGLE OPN LIN 1411 324541-324637(1) | -
|  |  | SINGLE OPN LIN 1412 324542-324588(1) | -
|  |  | SINGLE OPN LIN 1413 324542-324706(1) | -
|  |  | SINGLE OPN LIN 1414 324543-324686(1) | -
|  |  | SINGLE OPN LIN 1415 324543-324813(1) | -
|  |  | SINGLE OPN LIN 1416 324544-324693(1) | -
|  |  | SINGLE OPN LIN 1417 324544-324865(1) | -
|  |  | SINGLE OPN LIN 1418 324545-324623(1) | -
|  |  | SINGLE OPN LIN 1419 324546-324600(1) | -
|  |  | SINGLE OPN LIN 1420 324547-324890(1) | -
|  |  | SINGLE OPN LIN 1421 324549-324583(1) | -
|  |  | SINGLE OPN LIN 1422 324549-324894(1) | -
|  |  | SINGLE OPN LIN 1423 324550-324652(1) | -
|  |  | SINGLE OPN LIN 1424 324550-324709(1) | -
|  |  | SINGLE OPN LIN 1425 324550-324723(1) | -
325082 | 2ARMSTR BREC | 69 | SINGLE OPN LIN 1426 324550-325082(1) | 3.51
|  |  | SINGLE OPN LIN 1427 324550-326513(1) | -
|  |  | SINGLE OPN LIN 1428 324551-324786(1) | -
|  |  | SINGLE OPN LIN 1429 324551-324947(1) | -
|  |  | SINGLE OPN LIN 1430 324552-324675(1) | -
|  |  | SINGLE OPN LIN 1431 324553-324864(1) | -
|  |  | SINGLE OPN LIN 1432 324554-324830(1) | -
|  |  | SINGLE OPN LIN 1433 324555-324716(1) | -
|  |  | SINGLE OPN LIN 1434 324555-324759(1) | -
|  |  | SINGLE OPN LIN 1435 324556-324702(1) | -
|  |  | SINGLE OPN LIN 1436 324556-324870(1) | -
324077 | 2GREENVILE W | 69 | SINGLE OPN LIN 1437 324556-326593(1) | 1.98
326593 | 2GREENVIL N | 69 | SINGLE OPN LIN 1437 324556-326593(1) | 8.46
326594 | 2GREENVL 12 | 69 | SINGLE OPN LIN 1437 324556-326593(1) | 5.87
|  |  | SINGLE OPN LIN 1438 324557-324829(1) | -
|  |  | SINGLE OPN LIN 1439 324557-324830(1) | -
|  |  | SINGLE OPN LIN 1440 324558-324734(1) | -
|  |  | SINGLE OPN LIN 1441 324558-324766(1) | -
|  |  | SINGLE OPN LIN 1442 324559-324797(1) | -
|  |  | SINGLE OPN LIN 1443 324559-326586(1) | -
|  |  | SINGLE OPN LIN 1444 324560-324689(1) | -
|  |  | SINGLE OPN LIN 1445 324560-324815(1) | -
325068 | 2HAMBLIN | 69 | SINGLE OPN LIN 1446 324560-325041(1) | 6.81
|  |  | SINGLE OPN LIN 1447 324562-324564(1) | -
|  |  | SINGLE OPN LIN 1448 324563-324731(1) | -
|  |  | SINGLE OPN LIN 1449 324565-324566(1) | -
|  |  | SINGLE OPN LIN 1450 324567-324780(1) | -
|  |  | SINGLE OPN LIN 1451 324568-324569(1) | -
|  |  | SINGLE OPN LIN 1452 324568-324713(1) | -
|  |  | SINGLE OPN LIN 1453 324568-324742(1) | -
|  |  | SINGLE OPN LIN 1454 324569-324632(1) | -
|  |  | SINGLE OPN LIN 1455 324571-324671(1) | -
|  |  | SINGLE OPN LIN 1456 324572-324691(1) | -
|  |  | SINGLE OPN LIN 1457 324573-324741(1) | -
|  |  | SINGLE OPN LIN 1458 324576-324748(1) | -
|  |  | SINGLE OPN LIN 1459 324577-324693(1) | -
|  |  | SINGLE OPN LIN 1460 324577-324769(1) | -
|  |  | SINGLE OPN LIN 1461 324578-324690(1) | -
|  |  | SINGLE OPN LIN 1462 324578-324769(1) | -
|  |  | SINGLE OPN LIN 1463 324579-324580(1) | -
|  |  | SINGLE OPN LIN 1464 324579-324960(1) | -
|  |  | SINGLE OPN LIN 1465 324580-324750(1) | -
|  |  | SINGLE OPN LIN 1466 324580-324785(1) | -
|  |  | SINGLE OPN LIN 1467 324581-324586(1) | -
|  |  | SINGLE OPN LIN 1468 324582-324610(1) | -
|  |  | SINGLE OPN LIN 1469 324582-324879(1) | -
|  |  | SINGLE OPN LIN 1470 324583-324591(1) | -
|  |  | SINGLE OPN LIN 1471 324584-324659(1) | -
|  |  | SINGLE OPN LIN 1472 324585-324598(1) | -
|  |  | SINGLE OPN LIN 1473 324586-324610(1) | -
|  |  | SINGLE OPN LIN 1474 324587-324702(1) | -
|  |  | SINGLE OPN LIN 1475 324587-324709(1) | -
|  |  | SINGLE OPN LIN 1476 324589-324722(1) | -
324899 | 2MAYSVILLE E | 69 | SINGLE OPN LIN 1477 324589-324899(1) | 3.24
324900 | 2MAYSVILLE M | 69 | SINGLE OPN LIN 1477 324589-324899(1) | 3.56
|  |  | SINGLE OPN LIN 1478 324589-325019(1) | -
|  |  | SINGLE OPN LIN 1479 324590-324719(1) | -
|  |  | SINGLE OPN LIN 1480 324590-325023(1) | -
|  |  | SINGLE OPN LIN 1481 324591-324592(1) | -
|  |  | SINGLE OPN LIN 1482 324592-324689(1) | -
|  |  | SINGLE OPN LIN 1483 324593-324686(1) | -
|  |  | SINGLE OPN LIN 1484 324593-324741(1) | -
|  |  | SINGLE OPN LIN 1485 324595-324837(1) | -
|  |  | SINGLE OPN LIN 1486 324597-324764(1) | -
|  |  | SINGLE OPN LIN 1487 324597-324840(1) | -
|  |  | SINGLE OPN LIN 1488 324598-324682(1) | -
|  |  | SINGLE OPN LIN 1489 324599-324600(1) | -
|  |  | SINGLE OPN LIN 1490 324599-324971(1) | -
|  |  | SINGLE OPN LIN 1491 324601-324650(1) | -
|  |  | SINGLE OPN LIN 1492 324601-324780(1) | -
|  |  | SINGLE OPN LIN 1493 324602-324828(1) | -
324888 | 2LAWRENCE | 69 | SINGLE OPN LIN 1494 324602-324888(1) | 0.32
|  |  | SINGLE OPN LIN 1495 324603-324605(1) | -
324604 | 2LEBANON IND | 69 | SINGLE OPN LIN 1496 324604-324606(1) | 2.44
325020 | 2LEBANON E | 69 | SINGLE OPN LIN 1496 324604-324606(1) | 14.02
325020 | 2LEBANON E | 69 | SINGLE OPN LIN 1497 324604-325020(1) | 14.02
|  |  | SINGLE OPN LIN 1498 324605-324889(1) | -
|  |  | SINGLE OPN LIN 1499 324606-324736(1) | -
|  |  | SINGLE OPN LIN 1500 324607-324608(1) | -
|  |  | SINGLE OPN LIN 1501 324607-324609(1) | -
|  |  | SINGLE OPN LIN 1502 324608-324992(1) | -
|  |  | SINGLE OPN LIN 1503 324609-324643(1) | -
|  |  | SINGLE OPN LIN 1504 324609-325040(1) | -
|  |  | SINGLE OPN LIN 1505 324609-325040(2) | -
|  |  | SINGLE OPN LIN 1506 324610-324617(1) | -
|  |  | SINGLE OPN LIN 1507 324610-324674(1) | -
|  |  | SINGLE OPN LIN 1508 324611-324618(1) | -
|  |  | SINGLE OPN LIN 1509 324611-324891(1) | -
|  |  | SINGLE OPN LIN 1510 324612-324701(1) | -
|  |  | SINGLE OPN LIN 1511 324612-324768(1) | -
|  |  | SINGLE OPN LIN 1512 324613-324618(1) | -
324332 | 2LAKE SHORE | 69 | SINGLE OPN LIN 1513 324613-325059(1) | 25.39
325060 | 2BRYANT ROAD | 69 | SINGLE OPN LIN 1513 324613-325059(1) | 41.17
|  |  | SINGLE OPN LIN 1514 324614-324719(1) | -
326545 | 2LOCUST LGE | 69 | SINGLE OPN LIN 1515 324614-326545(1) | 20.82
|  |  | SINGLE OPN LIN 1516 324615-324688(1) | -
|  |  | SINGLE OPN LIN 1517 324616-324775(1) | -
|  |  | SINGLE OPN LIN 1518 324617-324618(1) | -
|  |  | SINGLE OPN LIN 1519 324618-326586(1) | -
|  |  | SINGLE OPN LIN 1520 324619-324998(1) | -
326517 | 2OVEN FORK | 69 | SINGLE OPN LIN 1521 324621-326523(1) | 14.3636
326534 | 2ARKLAND | 69 | SINGLE OPN LIN 1521 324621-326523(1) | 0.45468
|  |  | SINGLE OPN LIN 1522 324622-324637(1) | -
|  |  | SINGLE OPN LIN 1523 324622-324673(1) | -
|  |  | SINGLE OPN LIN 1524 324623-324637(1) | -
324627 | 2MANCHEST KU | 69 | SINGLE OPN LIN 1525 324626-324627(1) | 3.54
|  |  | SINGLE OPN LIN 1526 324628-324629(1) | -
|  |  | SINGLE OPN LIN 1527 324629-324904(1) | -
|  |  | SINGLE OPN LIN 1528 324630-324862(1) | -
|  |  | SINGLE OPN LIN 1529 324631-324658(1) | -
|  |  | SINGLE OPN LIN 1530 324633-324636(1) | -
|  |  | SINGLE OPN LIN 1531 324633-324684(1) | -
|  |  | SINGLE OPN LIN 1532 324634-324849(1) | -
324874 | 2HARROGATE | 69 | SINGLE OPN LIN 1533 324636-324874(1) | 2.06
|  |  | SINGLE OPN LIN 1534 324637-324653(1) | -
|  |  | SINGLE OPN LIN 1535 324638-324706(1) | -
|  |  | SINGLE OPN LIN 1536 324638-324813(1) | -
|  |  | SINGLE OPN LIN 1537 324639-324642(1) | -
324812 | 2CARLISLE | 69 | SINGLE OPN LIN 1538 324639-324812(1) | 6.61
|  |  | SINGLE OPN LIN 1539 324639-325035(1) | -
|  |  | SINGLE OPN LIN 1540 324641-324751(1) | -
|  |  | SINGLE OPN LIN 1541 324641-324829(1) | -
326970 | 2MILE LAN EK | 69 | SINGLE OPN LIN 1542 324641-326970(1) | 9.7611
|  |  | SINGLE OPN LIN 1543 324642-324677(1) | -
|  |  | SINGLE OPN LIN 1544 324642-324679(1) | -
|  |  | SINGLE OPN LIN 1545 324642-324717(1) | -
|  |  | SINGLE OPN LIN 1546 324643-324811(1) | -
|  |  | SINGLE OPN LIN 1547 324644-324645(1) | -
|  |  | SINGLE OPN LIN 1548 324644-324776(1) | -
|  |  | SINGLE OPN LIN 1549 324645-324671(1) | -
|  |  | SINGLE OPN LIN 1550 324645-326546(1) | -
324095 | 2UNIONTOWN | 69 | SINGLE OPN LIN 1551 324645-326572(1) | 2.32
326572 | 2RIVRVW COAL | 69 | SINGLE OPN LIN 1551 324645-326572(1) | 30.67
|  |  | SINGLE OPN LIN 1552 324646-324707(1) | -
|  |  | SINGLE OPN LIN 1553 324646-324910(1) | -
|  |  | SINGLE OPN LIN 1554 324647-324910(1) | -
324118 | 1CROFTON | 34.5 | SINGLE OPN LIN 1555 324648-324664(1) | 2.3
324181 | 1NORTNVL | 34.5 | SINGLE OPN LIN 1555 324648-324664(1) | 4.1
324371 | 1WHIT PLN | 34.5 | SINGLE OPN LIN 1555 324648-324664(1) | 2.74
326506 | 1MANNIN | 34.5 | SINGLE OPN LIN 1555 324648-324664(1) | 0.64
324118 | 1CROFTON | 34.5 | SINGLE OPN LIN 1556 324648-324769(1) | 2.3
324181 | 1NORTNVL | 34.5 | SINGLE OPN LIN 1556 324648-324769(1) | 4.1
324371 | 1WHIT PLN | 34.5 | SINGLE OPN LIN 1556 324648-324769(1) | 2.74
324648 | 2MORTONS GAP | 69 | SINGLE OPN LIN 1556 324648-324769(1) | 2.29
326506 | 1MANNIN | 34.5 | SINGLE OPN LIN 1556 324648-324769(1) | 0.64
|  |  | SINGLE OPN LIN 1557 324649-324675(1) | -
|  |  | SINGLE OPN LIN 1558 324650-324891(1) | -
|  |  | SINGLE OPN LIN 1559 324652-324817(1) | -
|  |  | SINGLE OPN LIN 1560 324655-324748(1) | -
|  |  | SINGLE OPN LIN 1561 324655-324791(1) | -
326542 | 2N CORBIN | 69 | SINGLE OPN LIN 1562 324655-326542(1) | 6.1092
|  |  | SINGLE OPN LIN 1563 324656-324968(1) | -
|  |  | SINGLE OPN LIN 1564 324657-324771(1) | -
|  |  | SINGLE OPN LIN 1565 324658-324774(1) | -
|  |  | SINGLE OPN LIN 1566 324658-324776(1) | -
|  |  | SINGLE OPN LIN 1567 324658-324931(1) | -
|  |  | SINGLE OPN LIN 1568 324659-326513(1) | -
|  |  | SINGLE OPN LIN 1569 324660-324801(1) | -
324917 | 2NICHLSV 3 | 69 | SINGLE OPN LIN 1570 324661-324989(1) | 5.05
324918 | 2NICHLSV 4&5 | 69 | SINGLE OPN LIN 1570 324661-324989(1) | 11.34
324919 | 2NICHLSV 6&8 | 69 | SINGLE OPN LIN 1570 324661-324989(1) | 7.4
|  |  | SINGLE OPN LIN 1571 324662-324688(1) | -
|  |  | SINGLE OPN LIN 1572 324663-324826(1) | -
|  |  | SINGLE OPN LIN 1573 324667-324703(1) | -
|  |  | SINGLE OPN LIN 1574 324667-324770(1) | -
|  |  | SINGLE OPN LIN 1575 324668-324936(1) | -
324672 | 2OXFORD EK T | 69 | SINGLE OPN LIN 1576 324672-324916(1) | 5.9966
|  |  | SINGLE OPN LIN 1577 324674-324934(1) | -
|  |  | SINGLE OPN LIN 1578 324677-324680(1) | -
|  |  | SINGLE OPN LIN 1579 324678-324679(1) | -
|  |  | SINGLE OPN LIN 1580 324678-324680(1) | -
|  |  | SINGLE OPN LIN 1581 324681-324960(1) | -
324887 | 2LA GRANG PE | 69 | SINGLE OPN LIN 1582 324682-324887(1) | 9.59
|  |  | SINGLE OPN LIN 1583 324683-324866(1) | -
|  |  | SINGLE OPN LIN 1584 324684-324686(1) | -
|  |  | SINGLE OPN LIN 1585 324687-324694(1) | -
|  |  | SINGLE OPN LIN 1586 324689-324738(1) | -
|  |  | SINGLE OPN LIN 1587 324689-324744(1) | -
|  |  | SINGLE OPN LIN 1588 324690-324747(1) | -
324065 | 2DAWSON 764 | 69 | SINGLE OPN LIN 1589 324690-324843(1) | 3.55
324843 | 2DAWSON IND | 69 | SINGLE OPN LIN 1589 324690-324843(1) | 2.02
|  |  | SINGLE OPN LIN 1590 324691-324870(1) | -
|  |  | SINGLE OPN LIN 1591 324692-324738(1) | -
|  |  | SINGLE OPN LIN 1592 324693-324747(1) | -
|  |  | SINGLE OPN LIN 1593 324694-324884(1) | -
|  |  | SINGLE OPN LIN 1594 324694-324930(1) | -
|  |  | SINGLE OPN LIN 1595 324695-324749(1) | -
|  |  | SINGLE OPN LIN 1596 324695-324783(1) | -
|  |  | SINGLE OPN LIN 1597 324696-324706(1) | -
|  |  | SINGLE OPN LIN 1598 324696-324792(1) | -
|  |  | SINGLE OPN LIN 1599 324698-324708(1) | -
|  |  | SINGLE OPN LIN 1600 324698-326555(1) | -
|  |  | SINGLE OPN LIN 1601 324699-324768(1) | -
|  |  | SINGLE OPN LIN 1602 324699-326552(1) | -
|  |  | SINGLE OPN LIN 1603 324700-324938(1) | -
|  |  | SINGLE OPN LIN 1604 324703-324959(1) | -
|  |  | SINGLE OPN LIN 1605 324704-324784(1) | -
|  |  | SINGLE OPN LIN 1606 324705-324783(1) | -
|  |  | SINGLE OPN LIN 1607 324705-324855(1) | -
324361 | 2RADCLIFF KU | 69 | SINGLE OPN LIN 1608 324708-324944(1) | 7.78
324944 | 2ROGERSV 605 | 69 | SINGLE OPN LIN 1608 324708-324944(1) | 7.93
324982 | 2VINE GRV KU | 69 | SINGLE OPN LIN 1608 324708-324944(1) | 3.61
|  |  | SINGLE OPN LIN 1609 324709-324981(1) | -
|  |  | SINGLE OPN LIN 1610 324710-324750(1) | -
|  |  | SINGLE OPN LIN 1611 324711-324790(1) | -
|  |  | SINGLE OPN LIN 1612 324712-324825(1) | -
|  |  | SINGLE OPN LIN 1613 324713-324955(1) | -
|  |  | SINGLE OPN LIN 1614 324714-324733(1) | -
|  |  | SINGLE OPN LIN 1615 324715-324721(1) | -
|  |  | SINGLE OPN LIN 1616 324715-325087(1) | -
|  |  | SINGLE OPN LIN 1617 324716-324977(1) | -
326549 | 2SARDIS | 69 | SINGLE OPN LIN 1618 324717-326549(1) | 1.36
|  |  | SINGLE OPN LIN 1619 324718-324726(1) | -
|  |  | SINGLE OPN LIN 1620 324719-324724(1) | -
|  |  | SINGLE OPN LIN 1621 324721-324764(1) | -
|  |  | SINGLE OPN LIN 1622 324723-325086(1) | -
|  |  | SINGLE OPN LIN 1623 324725-324727(1) | -
|  |  | SINGLE OPN LIN 1624 324726-324727(1) | -
|  |  | SINGLE OPN LIN 1625 324727-325102(1) | -
324728 | 2SHUN PIKE | 69 | SINGLE OPN LIN 1626 324728-324781(1) | 8.09
|  |  | SINGLE OPN LIN 1627 324729-325102(1) | -
326547 | 2SONORA | 69 | SINGLE OPN LIN 1628 324731-326547(1) | 4.15
|  |  | SINGLE OPN LIN 1629 324734-324848(1) | -
|  |  | SINGLE OPN LIN 1630 324735-324794(1) | -
|  |  | SINGLE OPN LIN 1631 324737-324969(1) | -
|  |  | SINGLE OPN LIN 1632 324740-324788(1) | -
|  |  | SINGLE OPN LIN 1633 324740-325024(1) | -
|  |  | SINGLE OPN LIN 1634 324742-324866(1) | -
|  |  | SINGLE OPN LIN 1635 324742-324972(1) | -
|  |  | SINGLE OPN LIN 1636 324743-324759(1) | -
|  |  | SINGLE OPN LIN 1637 324743-324851(1) | -
|  |  | SINGLE OPN LIN 1638 324744-324876(1) | -
324746 | 2SUNOCO | 69 | SINGLE OPN LIN 1639 324746-326546(1) | 1.51
|  |  | SINGLE OPN LIN 1640 324751-325921(1) | -
|  |  | SINGLE OPN LIN 1641 324752-324974(1) | -
324795 | 2ASHBYBRG PU | 69 | SINGLE OPN LIN 1642 324754-324928(1) | 0.57
324922 | 2ONTON | 69 | SINGLE OPN LIN 1642 324754-324928(1) | 1.12
324928 | 2POOLE | 69 | SINGLE OPN LIN 1642 324754-324928(1) | 0.64
324953 | 2SEBREE | 69 | SINGLE OPN LIN 1642 324754-324928(1) | 2.72
|  |  | SINGLE OPN LIN 1643 324755-324762(1) | -
|  |  | SINGLE OPN LIN 1644 324755-324920(1) | -
|  |  | SINGLE OPN LIN 1645 324755-324985(1) | -
|  |  | SINGLE OPN LIN 1646 324756-324772(1) | -
|  |  | SINGLE OPN LIN 1647 324756-324952(1) | -
|  |  | SINGLE OPN LIN 1648 324757-324941(1) | -
|  |  | SINGLE OPN LIN 1649 324758-324833(1) | -
|  |  | SINGLE OPN LIN 1650 324760-324838(1) | -
|  |  | SINGLE OPN LIN 1651 324763-324985(1) | -
|  |  | SINGLE OPN LIN 1652 324764-326578(1) | -
|  |  | SINGLE OPN LIN 1653 324765-326528(1) | -
326973 | 2BRIDGPRT 1 | 69 | SINGLE OPN LIN 1654 324765-326973(1) | 8.5298
|  |  | SINGLE OPN LIN 1655 324766-324952(1) | -
|  |  | SINGLE OPN LIN 1656 324767-326552(Z1) | -
|  |  | SINGLE OPN LIN 1657 324770-324946(1) | -
|  |  | SINGLE OPN LIN 1658 324774-324993(1) | -
|  |  | SINGLE OPN LIN 1659 324776-324777(1) | -
|  |  | SINGLE OPN LIN 1660 324777-324973(1) | -
|  |  | SINGLE OPN LIN 1661 324778-324779(1) | -
|  |  | SINGLE OPN LIN 1662 324782-324783(1) | -
324381 | 2WILLAMSBURG | 69 | SINGLE OPN LIN 1663 324784-325001(1) | 2.98
324382 | 2WILLMBRG SO | 69 | SINGLE OPN LIN 1663 324784-325001(1) | 13.08
|  |  | SINGLE OPN LIN 1664 324786-324790(1) | -
|  |  | SINGLE OPN LIN 1665 324787-324990(1) | -
324809 | 2BROOKS EKPC | 69 | SINGLE OPN LIN 1666 324788-324809(1) | 24.5121
325043 | 2SHEPHERDSV | 69 | SINGLE OPN LIN 1666 324788-324809(1) | 8.36
324806 | 2BEULAH EKPC | 69 | SINGLE OPN LIN 1667 324789-324806(1) | 10.5644
324915 | 2MT WAS EK J | 69 | SINGLE OPN LIN 1667 324789-324806(1) | 23.6017
325006 | 2W MT WSH EK | 69 | SINGLE OPN LIN 1667 324789-324806(1) | 13.7413
325021 | 2CONESTOGA | 69 | SINGLE OPN LIN 1668 324789-325021(1) | 12.55
|  |  | SINGLE OPN LIN 1669 324791-324860(1) | -
|  |  | SINGLE OPN LIN 1670 324792-324819(1) | -
|  |  | SINGLE OPN LIN 1671 324794-324987(1) | -
324795 | 2ASHBYBRG PU | 69 | SINGLE OPN LIN 1672 324795-324922(1) | 0.57
|  |  | SINGLE OPN LIN 1673 324797-324855(1) | -
|  |  | SINGLE OPN LIN 1674 324798-324875(1) | -
|  |  | SINGLE OPN LIN 1675 324799-324931(1) | -
|  |  | SINGLE OPN LIN 1676 324799-324932(1) | -
|  |  | SINGLE OPN LIN 1677 324802-324871(1) | -
|  |  | SINGLE OPN LIN 1678 324803-324907(1) | -
|  |  | SINGLE OPN LIN 1679 324803-325058(1) | -
324804 | 2BEDFORD TAP | 69 | SINGLE OPN LIN 1680 324804-324908(1) | 7.1395
325033 | 2BEDFORD KU | 69 | SINGLE OPN LIN 1680 324804-324908(1) | 2.55
325033 | 2BEDFORD KU | 69 | SINGLE OPN LIN 1681 324804-325033(1) | 2.55
324915 | 2MT WAS EK J | 69 | SINGLE OPN LIN 1682 324806-324925(1) | 23.6017
325006 | 2W MT WSH EK | 69 | SINGLE OPN LIN 1682 324806-324925(1) | 13.7413
|  |  | SINGLE OPN LIN 1683 324808-324913(1) | -
325043 | 2SHEPHERDSV | 69 | SINGLE OPN LIN 1684 324809-324958(1) | 8.36
324810 | 2CALHOUN | 69 | SINGLE OPN LIN 1685 324810-324947(1) | 2.53
|  |  | SINGLE OPN LIN 1686 324811-324946(1) | -
324373 | 2CATRON CRK | 69 | SINGLE OPN LIN 1687 324814-324956(1) | 1.04
|  |  | SINGLE OPN LIN 1688 324815-325007(1) | -
324816 | 2CEMETARY RD | 69 | SINGLE OPN LIN 1689 324816-324970(1) | 3.2549
|  |  | SINGLE OPN LIN 1690 324818-324827(1) | -
|  |  | SINGLE OPN LIN 1691 324818-324978(1) | -
|  |  | SINGLE OPN LIN 1692 324819-324945(1) | -
|  |  | SINGLE OPN LIN 1693 324820-324850(1) | -
|  |  | SINGLE OPN LIN 1694 324820-324981(1) | -
|  |  | SINGLE OPN LIN 1695 324821-324914(1) | -
|  |  | SINGLE OPN LIN 1696 324821-324992(1) | -
|  |  | SINGLE OPN LIN 1697 324822-324996(1) | -
|  |  | SINGLE OPN LIN 1698 324823-324825(1) | -
|  |  | SINGLE OPN LIN 1699 324824-325005(1) | -
|  |  | SINGLE OPN LIN 1700 324826-324999(1) | -
|  |  | SINGLE OPN LIN 1701 324832-324833(1) | -
324853 | 2E STONE GAP | 69 | SINGLE OPN LIN 1702 324836-324853(1) | 6.55
324853 | 2E STONE GAP | 69 | SINGLE OPN LIN 1703 324836-324894(1) | 6.55
|  |  | SINGLE OPN LIN 1704 324838-324957(1) | -
324839 | 2DANVILE IND | 69 | SINGLE OPN LIN 1705 324839-324909(1) | 20.27
324839 | 2DANVILE IND | 69 | SINGLE OPN LIN 1706 324841-324909(1) | 20.27
325032 | 2MINOR FARM | 69 | SINGLE OPN LIN 1706 324841-324909(1) | 6.09
|  |  | SINGLE OPN LIN 1707 324842-324967(1) | -
|  |  | SINGLE OPN LIN 1708 324842-324987(1) | -
324844 | 2DELAPLAIN | 69 | SINGLE OPN LIN 1709 324844-324943(1) | 22.92
324845 | 2DENHAM ST | 69 | SINGLE OPN LIN 1710 324845-324962(1) | 8.04
324961 | 2SOMERSET GE | 69 | SINGLE OPN LIN 1710 324845-324962(1) | 0.18
324963 | 2SOMERSET 2 | 69 | SINGLE OPN LIN 1710 324845-324962(1) | 3.38
324961 | 2SOMERSET GE | 69 | SINGLE OPN LIN 1711 324845-324963(1) | 0.18
324963 | 2SOMERSET 2 | 69 | SINGLE OPN LIN 1711 324845-324963(1) | 3.38
|  |  | SINGLE OPN LIN 1712 324846-324932(1) | -
|  |  | SINGLE OPN LIN 1713 324846-324996(1) | -
|  |  | SINGLE OPN LIN 1714 324847-324973(1) | -
|  |  | SINGLE OPN LIN 1715 324847-326546(1) | -
|  |  | SINGLE OPN LIN 1716 324848-324877(1) | -
|  |  | SINGLE OPN LIN 1717 324849-324867(1) | -
|  |  | SINGLE OPN LIN 1718 324851-324999(1) | -
|  |  | SINGLE OPN LIN 1719 324852-324885(1) | -
|  |  | SINGLE OPN LIN 1720 324852-324949(1) | -
326524 | 2VAN METER | 69 | SINGLE OPN LIN 1721 324855-326541(1) | 2.3496
326525 | 2TREEHAVEN | 69 | SINGLE OPN LIN 1721 324855-326541(1) | 1.8784
326541 | 2EKPC OFFICE | 69 | SINGLE OPN LIN 1721 324855-326541(1) | 0.782
|  |  | SINGLE OPN LIN 1722 324856-324880(1) | -
|  |  | SINGLE OPN LIN 1723 324856-324907(1) | -
324857 | 2ETOWN 2 | 69 | SINGLE OPN LIN 1724 324857-324858(1) | 33.95
|  |  | SINGLE OPN LIN 1725 324862-325086(1) | -
|  |  | SINGLE OPN LIN 1726 324863-324920(1) | -
|  |  | SINGLE OPN LIN 1727 324865-324904(1) | -
|  |  | SINGLE OPN LIN 1728 324867-324911(1) | -
|  |  | SINGLE OPN LIN 1729 324871-324894(1) | -
324061 | 2BORG-WARNER | 69 | SINGLE OPN LIN 1730 324873-324896(1) | 8.5
324079 | 2HANSON | 69 | SINGLE OPN LIN 1730 324873-324896(1) | 9.89
|  |  | SINGLE OPN LIN 1731 324875-324942(1) | -
|  |  | SINGLE OPN LIN 1732 324877-324890(1) | -
324804 | 2BEDFORD TAP | 69 | SINGLE OPN LIN 1733 324878-324908(1) | 7.1395
324908 | 2MILTON | 69 | SINGLE OPN LIN 1733 324878-324908(1) | 5.671
325033 | 2BEDFORD KU | 69 | SINGLE OPN LIN 1733 324878-324908(1) | 2.55
|  |  | SINGLE OPN LIN 1734 324881-324942(1) | -
|  |  | SINGLE OPN LIN 1735 324881-324978(1) | -
|  |  | SINGLE OPN LIN 1736 324884-324979(1) | -
|  |  | SINGLE OPN LIN 1737 324886-324967(1) | -
|  |  | SINGLE OPN LIN 1738 324886-324968(1) | -
|  |  | SINGLE OPN LIN 1739 324892-324945(1) | -
|  |  | SINGLE OPN LIN 1740 324892-325007(1) | -
324895 | 2MADSNV HO | 69 | SINGLE OPN LIN 1741 324893-324897(1) | 9.41
324897 | 2MADSNV N | 69 | SINGLE OPN LIN 1741 324893-324897(1) | 13.19
324081 | 2MADSNV GE | 69 | SINGLE OPN LIN 1742 324893-326587(1) | 5.41
324083 | 2MADSNV W | 69 | SINGLE OPN LIN 1742 324893-326587(1) | 17.4
324895 | 2MADSNV HO | 69 | SINGLE OPN LIN 1743 324895-324897(1) | 9.41
324061 | 2BORG-WARNER | 69 | SINGLE OPN LIN 1744 324896-324902(1) | 8.5
324079 | 2HANSON | 69 | SINGLE OPN LIN 1744 324896-324902(1) | 9.89
324896 | 2MADSNV E | 69 | SINGLE OPN LIN 1744 324896-324902(1) | 8.39
|  |  | SINGLE OPN LIN 1745 324898-324954(1) | -
|  |  | SINGLE OPN LIN 1746 324898-324993(1) | -
324900 | 2MAYSVILLE M | 69 | SINGLE OPN LIN 1747 324899-324900(1) | 3.56
324903 | 2MCKEE ROAD | 69 | SINGLE OPN LIN 1748 324903-324964(1) | 9.44
324950 | 2SCIENC HILL | 69 | SINGLE OPN LIN 1748 324903-324964(1) | 2.22
324995 | 2WAYNESBURG | 69 | SINGLE OPN LIN 1748 324903-324964(1) | 2.37
324950 | 2SCIENC HILL | 69 | SINGLE OPN LIN 1749 324903-324965(1) | 2.22
324995 | 2WAYNESBURG | 69 | SINGLE OPN LIN 1749 324903-324965(1) | 2.37
325032 | 2MINOR FARM | 69 | SINGLE OPN LIN 1750 324909-325032(1) | 6.09
|  |  | SINGLE OPN LIN 1751 324911-324994(1) | -
324915 | 2MT WAS EK J | 69 | SINGLE OPN LIN 1752 324915-325006(1) | 23.6017
324672 | 2OXFORD EK T | 69 | SINGLE OPN LIN 1753 324916-324924(1) | 5.9966
325027 | 2NEWTOWN | 69 | SINGLE OPN LIN 1753 324916-324924(1) | 5.78
325027 | 2NEWTOWN | 69 | SINGLE OPN LIN 1754 324916-325027(1) | 5.78
324917 | 2NICHLSV 3 | 69 | SINGLE OPN LIN 1755 324917-324918(1) | 5.05
|  |  | SINGLE OPN LIN 1756 324917-324980(1) | -
324917 | 2NICHLSV 3 | 69 | SINGLE OPN LIN 1757 324918-324919(1) | 5.05
324918 | 2NICHLSV 4&5 | 69 | SINGLE OPN LIN 1757 324918-324919(1) | 11.34
324917 | 2NICHLSV 3 | 69 | SINGLE OPN LIN 1758 324919-324989(1) | 5.05
324918 | 2NICHLSV 4&5 | 69 | SINGLE OPN LIN 1758 324919-324989(1) | 11.34
324919 | 2NICHLSV 6&8 | 69 | SINGLE OPN LIN 1758 324919-324989(1) | 7.4
326529 | 2NINEVAH | 69 | SINGLE OPN LIN 1759 324920-326529(1) | 6.3826
324795 | 2ASHBYBRG PU | 69 | SINGLE OPN LIN 1760 324922-326563(1) | 0.57
324922 | 2ONTON | 69 | SINGLE OPN LIN 1760 324922-326563(1) | 1.12
324915 | 2MT WAS EK J | 69 | SINGLE OPN LIN 1761 324925-325006(1) | 23.6017
325006 | 2W MT WSH EK | 69 | SINGLE OPN LIN 1761 324925-325006(1) | 13.7413
324795 | 2ASHBYBRG PU | 69 | SINGLE OPN LIN 1762 324928-324953(1) | 0.57
324922 | 2ONTON | 69 | SINGLE OPN LIN 1762 324928-324953(1) | 1.12
324953 | 2SEBREE | 69 | SINGLE OPN LIN 1762 324928-324953(1) | 2.72
|  |  | SINGLE OPN LIN 1763 324930-324972(1) | -
|  |  | SINGLE OPN LIN 1764 324934-324984(1) | -
324361 | 2RADCLIFF KU | 69 | SINGLE OPN LIN 1765 324935-324944(1) | 7.78
324982 | 2VINE GRV KU | 69 | SINGLE OPN LIN 1765 324935-324944(1) | 3.61
324982 | 2VINE GRV KU | 69 | SINGLE OPN LIN 1766 324935-324982(1) | 3.61
|  |  | SINGLE OPN LIN 1767 324936-324940(1) | -
324939 | 2RICHMND 4 | 69 | SINGLE OPN LIN 1768 324937-324939(1) | 6.79
|  |  | SINGLE OPN LIN 1769 324938-324940(1) | -
|  |  | SINGLE OPN LIN 1770 324941-324975(1) | -
|  |  | SINGLE OPN LIN 1771 324948-324949(1) | -
324995 | 2WAYNESBURG | 69 | SINGLE OPN LIN 1772 324950-325084(1) | 2.37
|  |  | SINGLE OPN LIN 1773 324951-326989(1) | -
324795 | 2ASHBYBRG PU | 69 | SINGLE OPN LIN 1774 324953-326563(1) | 0.57
324922 | 2ONTON | 69 | SINGLE OPN LIN 1774 324953-326563(1) | 1.12
325761 | 2WARRIOR PRP | 69 | SINGLE OPN LIN 1775 324954-325762(1) | 6.24
325767 | 2SENTRY | 69 | SINGLE OPN LIN 1775 324954-325762(1) | 0.21
|  |  | SINGLE OPN LIN 1776 324957-324970(1) | -
325043 | 2SHEPHERDSV | 69 | SINGLE OPN LIN 1777 324958-325043(1) | 8.36
324124 | 2CENTRTOWN S | 69 | SINGLE OPN LIN 1778 324959-326564(1) | 0.95
326564 | 2LEW BREC | 69 | SINGLE OPN LIN 1778 324959-326564(1) | 0.14
324961 | 2SOMERSET GE | 69 | SINGLE OPN LIN 1779 324961-324963(1) | 0.18
|  |  | SINGLE OPN LIN 1780 324966-324994(1) | -
|  |  | SINGLE OPN LIN 1781 324969-324990(1) | -
|  |  | SINGLE OPN LIN 1782 324970-324971(1) | -
|  |  | SINGLE OPN LIN 1783 324975-324997(1) | -
|  |  | SINGLE OPN LIN 1784 324979-324986(1) | -
325062 | 2TEXAS GAS | 69 | SINGLE OPN LIN 1785 324981-325062(1) | 2.64
|  |  | SINGLE OPN LIN 1786 324984-324988(1) | -
325025 | 2WARSAW EAST | 69 | SINGLE OPN LIN 1787 324994-325025(1) | 2.05
324995 | 2WAYNESBURG | 69 | SINGLE OPN LIN 1788 324995-325084(1) | 2.37
325010 | 2WEBCOAL 2 | 69 | SINGLE OPN LIN 1789 324996-325010(1) | 0.62
|  |  | SINGLE OPN LIN 1790 324997-324998(1) | -
|  |  | SINGLE OPN LIN 1791 325002-325003(Z1) | -
325026 | 2PINE MOUNTN | 69 | SINGLE OPN LIN 1792 325008-325026(1) | 2.4546
|  |  | SINGLE OPN LIN 1793 325010-325011(1) | -
325017 | 2CMWA | 69 | SINGLE OPN LIN 1794 325017-325018(1) | 7.49
325018 | 2CLA | 69 | SINGLE OPN LIN 1795 325018-325061(1) | 6.31
325017 | 2CMWA | 69 | SINGLE OPN LIN 1795 325018-325061(1) | 7.49
|  |  | SINGLE OPN LIN 1796 325023-325024(1) | -
325037 | 1ASHWOOD INV | 34.5 | SINGLE OPN LIN 1797 325028-325047(1) | 1.4
|  |  | SINGLE OPN LIN 1798 325028-326589(1) | -
|  |  | SINGLE OPN LIN 1799 325035-325050(1) | -
|  |  | SINGLE OPN LIN 1800 325035-325085(1) | -
325068 | 2HAMBLIN | 69 | SINGLE OPN LIN 1801 325041-325068(1) | 6.81
325044 | 4INTRNTL | 138 | SINGLE OPN LIN 1802 325044-326565(1) | 30.17
325092 | 2COAL GOOD | 69 | SINGLE OPN LIN 1803 325045-325092(1) | 2.45
325130 | 1RHUDES GEN | 0.6 | SINGLE OPN LIN 1804 325055-325116(1) | 0.16
325057 | 4KOSMOS CEME | 138 | SINGLE OPN LIN 1805 325057-325088(1) | 27.23
325060 | 2BRYANT ROAD | 69 | SINGLE OPN LIN 1806 325059-325060(1) | 41.17
325075 | 5KMPA COLEMN | 161 | SINGLE OPN LIN 1807 325075-325077(Z1) | 66.99
|  |  | SINGLE OPN LIN 1808 325077-325078(1) | -
|  |  | SINGLE OPN LIN 1809 325078-326562(1) | -
|  |  | SINGLE OPN LIN 1810 325078-326596(1) | -
|  |  | SINGLE OPN LIN 1811 325079-326589(1) | -
326591 | 5W PRINCETON | 161 | SINGLE OPN LIN 1812 325079-326591(1) | 14.5
326592 | 5E PRINCETON | 161 | SINGLE OPN LIN 1812 325079-326591(1) | 10.7
326544 | 2ALEX CREEK | 69 | SINGLE OPN LIN 1813 325083-326544(1) | 1.3637
|  |  | SINGLE OPN LIN 1814 325096-326002(1) | -
|  |  | SINGLE OPN LIN 1815 325096-326565(23) | -
325093 | 1CANERUN7CT1 | 18 | SINGLE OPN LIN 1816 325096-326566(71) | 7.5
325094 | 1CANERUN7CT2 | 18 | SINGLE OPN LIN 1817 325096-326567(72) | 6
|  |  | SINGLE OPN LIN 1818 325096-326568(7S) | -
|  |  | SINGLE OPN LIN 1819 325096-326574(21) | -
325761 | 2WARRIOR PRP | 69 | SINGLE OPN LIN 1820 325761-325762(1) | 6.24
325767 | 2SENTRY | 69 | SINGLE OPN LIN 1821 325762-325767(1) | 0.21
|  |  | SINGLE OPN LIN 1822 325857-325956(Z1) | -
|  |  | SINGLE OPN LIN 1823 325857-325957(Z1) | -
|  |  | SINGLE OPN LIN 1824 326001-326002(1) | -
326517 | 2OVEN FORK | 69 | SINGLE OPN LIN 1825 326517-326523(1) | 14.3636
326534 | 2ARKLAND | 69 | SINGLE OPN LIN 1826 326523-326534(1) | 0.45468
326524 | 2VAN METER | 69 | SINGLE OPN LIN 1827 326524-326527(1) | 2.3496
326525 | 2TREEHAVEN | 69 | SINGLE OPN LIN 1828 326525-326527(1) | 1.8784
326526 | 4N SHARKEY | 138 | SINGLE OPN LIN 1829 326526-326556(1) | 1.2322
326524 | 2VAN METER | 69 | SINGLE OPN LIN 1830 326527-326541(1) | 2.3496
326525 | 2TREEHAVEN | 69 | SINGLE OPN LIN 1830 326527-326541(1) | 1.8784
326974 | 2BRIDGPRT 2 | 69 | SINGLE OPN LIN 1831 326528-326974(1) | 5.8078
326539 | 2GIRDLER | 69 | SINGLE OPN LIN 1832 326530-326539(1) | 4.6408
326532 | 4SHARKEY | 138 | SINGLE OPN LIN 1833 326532-326556(1) | 8.4668
326553 | 2SE COAL | 69 | SINGLE OPN LIN 1834 326552-326553(1) | 0.11
326560 | 4BG ARMY DEP | 138 | SINGLE OPN LIN 1835 326559-326560(1) | 4.8
|  |  | SINGLE OPN LIN 1836 326562-326596(Z1) | -
326571 | 2HUME RD | 69 | SINGLE OPN LIN 1837 326571-326586(1) | 15.02
|  |  | SINGLE OPN LIN 1838 326578-326579(1) | -
326582 | 2CORNG8251_2 | 69 | SINGLE OPN LIN 1839 326578-326584(1) | 3.01
326584 | 2CORNG7462_3 | 69 | SINGLE OPN LIN 1839 326578-326584(1) | 0.73
326580 | 2CORNIG 8253 | 69 | SINGLE OPN LIN 1840 326579-326580(1) | 4.51
326582 | 2CORNG8251_2 | 69 | SINGLE OPN LIN 1841 326582-326583(1) | 3.01
326582 | 2CORNG8251_2 | 69 | SINGLE OPN LIN 1842 326583-326584(1) | 3.01
326592 | 5E PRINCETON | 161 | SINGLE OPN LIN 1843 326591-326592(1) | 10.7
324077 | 2GREENVILE W | 69 | SINGLE OPN LIN 1844 326593-326594(1) | 1.98
326594 | 2GREENVL 12 | 69 | SINGLE OPN LIN 1844 326593-326594(1) | 5.87
|  |  | SINGLE OPN TIE 1845 324010-248000(1) | -
324044 | 1BLUEGRASS 1 | 18 | SINGLE OPN TIE 1846 324021-324044(1) | 0.6333
324045 | 1BLUEGRASS 2 | 18 | SINGLE OPN TIE 1847 324021-324045(1) | 1.4333
324046 | 1BLUEGRASS 3 | 18 | SINGLE OPN TIE 1848 324022-324046(1) | 0.6333
|  |  | SINGLE OPN TIE 1850 324104-324113(1) | -
|  |  | SINGLE OPN TIE 1851 324104-340561(1) | -
|  |  | SINGLE OPN TIE 1852 324104-340563(1) | -
|  |  | SINGLE OPN TIE 1853 324105-249501(1) | -
|  |  | SINGLE OPN TIE 1854 324105-249532(1) | -
|  |  | SINGLE OPN TIE 1855 324108-324284-326550(5) | -
|  |  | SINGLE OPN TIE 1856 324108-324284-326551(6) | -
|  |  | SINGLE OPN TIE 1857 324112-324072(1) | -
|  |  | SINGLE OPN TIE 1858 324114-249520(1) | -
|  |  | SINGLE OPN TIE 1859 324114-249532(1) | -
|  |  | SINGLE OPN TIE 1863 324144-340553(1) | -
|  |  | SINGLE OPN TIE 1864 324148-243668(1) | -
|  |  | SINGLE OPN TIE 1865 324150-360334(1) | -
|  |  | SINGLE OPN TIE 1866 324151-360125(1) | -
|  |  | SINGLE OPN TIE 1867 324151-360127(1) | -
|  |  | SINGLE OPN TIE 1868 324156-360452(1) | -
|  |  | SINGLE OPN TIE 1869 324157-324073(1) | -
|  |  | SINGLE OPN TIE 1870 324171-351003(1) | -
|  |  | SINGLE OPN TIE 1871 324172-351002(1) | -
|  |  | SINGLE OPN TIE 1872 324173-340553(1) | -
|  |  | SINGLE OPN TIE 1873 324173-340624(1) | -
|  |  | SINGLE OPN TIE 1875 324211-251561(1) | -
|  |  | SINGLE OPN TIE 1877 324217-325012(1) | -
|  |  | SINGLE OPN TIE 1878 324227-248009(1) | -
|  |  | SINGLE OPN TIE 1879 324231-253623(1) | -
|  |  | SINGLE OPN TIE 1880 324231-340615(1) | -
324399 | 1CANERN11 | 14 | SINGLE OPN TIE 1881 324232-324399(1) | 5.4
|  |  | SINGLE OPN TIE 1884 324253-249723(1) | -
|  |  | SINGLE OPN TIE 1886 324256-324309(1) | -
|  |  | SINGLE OPN TIE 1887 324260-340615(1) | -
|  |  | SINGLE OPN TIE 1889 324265-249763(1) | -
|  |  | SINGLE OPN TIE 1890 324267-247508(1) | -
324170 | 1KNOB CRK | 34.5 | SINGLE OPN TIE 1892 324268-324170(1) | 15.4897
|  |  | SINGLE OPN TIE 1899 324289-249789(1) | -
|  |  | SINGLE OPN TIE 1901 324294-249730(1) | -
|  |  | SINGLE OPN TIE 1902 324295-324431(4A) | -
|  |  | SINGLE OPN TIE 1903 324295-324596(5) | -
|  |  | SINGLE OPN TIE 1904 324295-324675-324635(3) | -
324366 | 1TIPTOP 1 | 34.5 | SINGLE OPN TIE 1906 324311-324366(1) | 7.84
324807 | 2BRANDENBURG | 69 | SINGLE OPN TIE 1907 324311-324753-326511(2) | 4.97
326511 | 1TIPTOP | 34.5 | SINGLE OPN TIE 1907 324311-324753-326511(2) | 11.22
|  |  | SINGLE OPN TIE 1908 324316-242605(1) | -
|  |  | SINGLE OPN TIE 1910 324405-326500(1) | -
324369 | 1WENTZ | 34.5 | SINGLE OPN TIE 1911 324412-326501(1) | 3.87
324060 | 1BEECH CR | 34.5 | SINGLE OPN TIE 1915 324437-324063(1) | 1.09
324062 | 1BEECHMNT | 34.5 | SINGLE OPN TIE 1915 324437-324063(1) | 2.57
324122 | 1DRAKESBO | 34.5 | SINGLE OPN TIE 1915 324437-324063(1) | 2.14
324188 | 1REED MIN | 34.5 | SINGLE OPN TIE 1915 324437-324063(1) | 0.48
324397 | 1BOND | 23 | SINGLE OPN TIE 1918 324446-324397(1) | 3.82
324398 | 1DORCHEST | 23 | SINGLE OPN TIE 1923 324503-324398(1) | 3.75
324185 | 1POTCAMP | 34.5 | SINGLE OPN TIE 1924 324503-326504(1) | 0.11
324189 | 1ROARG FK | 34.5 | SINGLE OPN TIE 1924 324503-326504(1) | 0.11
324119 | 1CROSSRD | 34.5 | SINGLE OPN TIE 1925 324507-324123(1) | 0.31
324121 | 1DANL BOONE | 34.5 | SINGLE OPN TIE 1925 324507-324123(1) | 0.46
324327 | 1ST CHARL | 34.5 | SINGLE OPN TIE 1925 324507-324123(1) | 2.79
|  |  | SINGLE OPN TIE 1927 324512-362916(1) | -
324126 | 1FORK ELK | 34.5 | SINGLE OPN TIE 1933 324533-326505(1) | 7.75
324343 | 1STMP GRD | 34.5 | SINGLE OPN TIE 1933 324533-326505(1) | 5.55
324396 | 1WOODLAKE | 34.5 | SINGLE OPN TIE 1933 324533-326505(1) | 1.18
324169 | 1ISLAND | 34.5 | SINGLE OPN TIE 1934 324550-324128(1) | 1.64
324174 | 1LIVERMOR | 34.5 | SINGLE OPN TIE 1934 324550-324128(1) | 2.78
324183 | 1PERDUE | 34.5 | SINGLE OPN TIE 1934 324550-324128(1) | 1.67
|  |  | SINGLE OPN TIE 1935 324551-324669(1) | -
|  |  | SINGLE OPN TIE 1937 324574-324043(1) | -
324182 | 1OUTWOOD | 34.5 | SINGLE OPN TIE 1940 324578-324142(1) | 0.35
324720 | 1SIXTHVEIN | 34.5 | SINGLE OPN TIE 1940 324578-324142(1) | 2.56
324125 | 1EXETER | 34.5 | SINGLE OPN TIE 1941 324583-324168(1) | 0.29
324176 | 1OSAKA MINE | 34.5 | SINGLE OPN TIE 1941 324583-324168(1) | 0.33
324118 | 1CROFTON | 34.5 | SINGLE OPN TIE 1945 324664-326507(1) | 2.3
324181 | 1NORTNVL | 34.5 | SINGLE OPN TIE 1945 324664-326507(1) | 4.1
324371 | 1WHIT PLN | 34.5 | SINGLE OPN TIE 1945 324664-326507(1) | 2.74
326506 | 1MANNIN | 34.5 | SINGLE OPN TIE 1945 324664-326507(1) | 0.64
324084 | 1CALVIN | 34.5 | SINGLE OPN TIE 1948 324689-324184(1) | 0.12
324184 | 1POCKET | 34.5 | SINGLE OPN TIE 1948 324689-324184(1) | 0.23
324099 | 1CEDAR BL | 34.5 | SINGLE OPN TIE 1949 324693-326509(1) | 1.33
326502 | 1CLAXTON | 34.5 | SINGLE OPN TIE 1949 324693-326509(1) | 0.53
326503 | 1DAWSON | 34.5 | SINGLE OPN TIE 1949 324693-326509(1) | 2
|  |  | SINGLE OPN TIE 1950 324707-243740(Z1) | -
|  |  | SINGLE OPN TIE 1952 324712-362116(1) | -
324162 | 1HI BRIDG | 34.5 | SINGLE OPN TIE 1959 324764-324368(1) | 0.42
324383 | 1YEL RK N | 34.5 | SINGLE OPN TIE 1962 324803-324057(1) | 0.18
|  |  | SINGLE OPN TIE 1964 324947-324190(1) | -
324883 | 1SALEM | 34.5 | SINGLE OPN TIE 1965 324948-324883(1) | 2.22
|  |  | SINGLE OPN TIE 1967 325013-248009(1) | -
|  |  | SINGLE OPN TIE 1968 325014-248009(1) | -
|  |  | SINGLE OPN TIE 1969 325014-250057(1) | -
|  |  | SINGLE OPN TIE 1970 325015-324309(1) | -
325037 | 1ASHWOOD INV | 34.5 | SINGLE OPN TIE 1972 325047-325046(1) | 1.4
|  |  | SINGLE OPN TIE 1973 325073-340651(1) | -
325130 | 1RHUDES GEN | 0.6 | SINGLE OPN TIE 1976 325116-325117(1) | 0.16
|  |  | SINGLE OPN TIE 1979 326569-248830(1) | -
|  |  | SINGLE OPN TIE 1980 326569-249520(1) | -
324697 | 1KMPA PAD2 | 13.8 | SINGLE OPN TIE 1981 326596-324697(1) | 1.144
324933 | 1KMPA PAD1 | 13.8 | SINGLE OPN TIE 1982 326596-324933(1) | 1.144
|  |  | SINGLE OPN TIE 1985 326998-361788(1) | -
|  |  | MERE SWS | -
|  |  | B-69-51 | -
|  |  | B-69-446 | -
|  |  | B-69-65 | -
|  |  | B-69-63 | -
|  |  | B-69-66 | -
|  |  | B-69-53 | -
|  |  | B-69-36 | -
|  |  | B-69-49 | -
|  |  | B-69-37 | -
|  |  | B-69-11 | -
|  |  | B-69-50 | -
|  |  | B-69-316A | -
|  |  | B-69-9 | -
|  |  | SW-1000 | -
|  |  | B-69-47 | -
|  |  | B-69-48 | -
|  |  | B-69-52 | -
|  |  | B-69-56 | -
|  |  | B-69-57 | -
324950 | 2SCIENC HILL | 69 | B-69-58 | 2.22
324995 | 2WAYNESBURG | 69 | B-69-58 | 2.37
|  |  | B-69-60 | -
|  |  | B-69-61 | -
|  |  | B-69-62 | -
|  |  | B-69-318 | -
|  |  | B-69-319 | -
|  |  | B-69-67 | -
324901 | 2MAYSVILLE W | 69 | B-69-693 | 3.7
|  |  | B-69-69 | -
|  |  | B-69-72 | -
|  |  | B-69-74 | -
|  |  | B-69-76 | -
|  |  | B-69-77 | -
|  |  | B-69-73 | -
|  |  | B-69-10 | -
324109 | 7NAS | 345 | B-345-449 | 106.67
|  |  | B-138-123 | -
|  |  | B-69-322 | -
|  |  | B-69-324 | -
|  |  | B-69-79 | -
|  |  | B-69-80 | -
|  |  | B-69-325 | -
326560 | 4BG ARMY DEP | 138 | B-69-327 | 4.8
|  |  | B-138-115 | -
|  |  | B-69-448 | -
|  |  | B-161-131 | -
|  |  | B-69-334 | -
|  |  | B-69-335 | -
326526 | 4N SHARKEY | 138 | B-138-447 | 1.2322
326532 | 4SHARKEY | 138 | B-138-447 | 8.4668
326526 | 4N SHARKEY | 138 | B-69-330 | 1.2322
326532 | 4SHARKEY | 138 | B-69-330 | 8.4668
|  |  | B-69-332 | -
|  |  | B-69-337 | -
|  |  | B-69-338 | -
|  |  | B-69-450 | -
|  |  | B-500-97 | -
|  |  | B-69-339 | -
|  |  | B-69-340 | -
324236 | 4RICHMND NO | 138 | BB-2000 | 8.1
324199 | 2OWENTON | 69 | BB-1366 | 2.89
324252 | 2SCHOLLS | 69 | BB-1366 | 1.08
324455 | 2BROMLEY | 69 | BB-1366 | 2.38
324966 | 2SPARTA KU | 69 | BB-1366 | 1.43
324994 | 2WARSAW KU | 69 | BB-1366 | 2.81
325025 | 2WARSAW EAST | 69 | BB-1366 | 2.05
324634 | 2METAL+THERM | 69 | BB-1452 | 5.02
324849 | 2DOW CORNING | 69 | BB-1452 | 3.43
324867 | 2GHENT | 69 | BB-1452 | 1.5
324911 | 2MARKLAND DM | 69 | BB-1452 | 0.17
324478 | 2CAMPBELBURG | 69 | BB-1386 | 9.6211
324828 | 2CAMPBBRG KU | 69 | BB-1386 | 2.58
324888 | 2LAWRENCE | 69 | BB-1386 | 0.32
324304 | 2VERSAILLE W | 69 | BB-1456 | 11.32
324340 | 2SPINDLETOP | 69 | BB-1280 | 1.54
324547 | 2GEORGETOWN | 69 | BB-1280 | 12.19
324848 | 2DONERAIL | 69 | BB-1280 | 6.82
324877 | 2HOOVER KU | 69 | BB-1280 | 23.82
324890 | 2LEMONS MILL | 69 | BB-1280 | 27.33
324763 | 2VERSAILLES | 69 | BB-1479 | 4.06
324985 | 2VSAIL BYPAS | 69 | BB-1479 | 28.71
324195 | 2AUGUSTA | 69 | BB-1317 | 7
324722 | 2SHARON KU | 69 | BB-1317 | 6.28
324297 | 4PLAINVIEW | 138 | BB-1225 | 29.5
324491 | 2CYNTHIAN SO | 69 | BB-1373 | 3.41
324595 | 2KAWNEER | 69 | BB-1373 | 3.76
324812 | 2CARLISLE | 69 | BB-1373 | 6.61
324837 | 2CYNTHIAN KU | 69 | BB-1373 | 9.9
|  |  | BB-1073 | -
324677 | 2PARIS 12 | 69 | BB-1493 | 12.9696
324678 | 2PARIS CITY | 69 | BB-1494 | 4.4
324679 | 2PARIS 3 | 69 | BB-1494 | 4.69
326549 | 2SARDIS | 69 | BB-1495 | 1.36
324082 | 2PARIS 4 | 69 | BB-1395 | 1.08
324197 | 2DETROIT HAR | 69 | BB-1395 | 10.92
324581 | 2HUGHES LANE | 69 | BB-1395 | 3.82
324586 | 2JOYLAND | 69 | BB-1395 | 19.24
325018 | 2CLA | 69 | BB-1395 | 6.31
325061 | 2CMC | 69 | BB-1395 | 4.08
325017 | 2CMWA | 69 | BB-1395 | 7.49
324559 | 2HALEY | 69 | BB-1318 | 5.78
324705 | 2ROCKWELL | 69 | BB-1318 | 15.24
326524 | 2VAN METER | 69 | BB-1318 | 2.3496
326525 | 2TREEHAVEN | 69 | BB-1318 | 1.8784
326541 | 2EKPC OFFICE | 69 | BB-1318 | 0.782
326571 | 2HUME RD | 69 | BB-1318 | 15.02
324448 | 2BOONE AVE | 69 | BB-1352 | 13.7
324782 | 2WINCHEST SO | 69 | BB-1352 | 2.5
325004 | 2WINCHES WTR | 69 | BB-1352 | 6.96
324330 | 2WINCHES IND | 69 | BB-1405 | 11.23
325063 | 2CORPORAT DR | 69 | BB-1405 | 21.31
324414 | 2AO SMITH | 69 | BB-1301 | 8.26
324461 | 2CAMARGO | 69 | BB-1301 | 17.74
324912 | 2MT STERL KU | 69 | BB-1301 | 10.56
326531 | 2HINKSTON | 69 | BB-1301 | 3.5628
324714 | 2SALT LICK | 69 | BB-1387 | 2.39
326538 | 2CAVE RUN | 69 | BB-1387 | 1.4141
324646 | 2MOREHEAD E | 69 | BB-1443 | 5.51
324647 | 2MOREHEAD W | 69 | BB-1443 | 5.62
324910 | 2MOREHEAD | 69 | BB-1443 | 9.76
324432 | 2BELT LINE | 69 | BB-1335 | 11.23
324582 | 2IBM | 69 | BB-1335 | 26.59
324879 | 2IBM 998 | 69 | BB-1335 | 4.32
324338 | 2SCOTT ST 4 | 69 | BB-1298 | 4.24
324339 | 2SCOTT ST 12 | 69 | BB-1298 | 13.4
324756 | 2UK WEST 1 | 69 | BB-1298 | 7.68
324772 | 2UK WEST 2 | 69 | BB-1298 | 9.41
324988 | 2WEST HIGH | 69 | BB-1298 | 20.62
324457 | 2BUCHANAN | 69 | BB-1369 | 3.81
324884 | 2KUNKEL | 69 | BB-1369 | 2.3
324979 | 2TRAFTON AVE | 69 | BB-1369 | 18.12
324683 | 2PICADOME | 69 | BB-1297 | 27.61
324866 | 2GE LAMP | 69 | BB-1297 | 9.6
324972 | 2STONEWALL | 69 | BB-1297 | 29.11
324407 | 2ALEXANDER | 69 | BB-1288 | 6.66
324713 | 2SO ELKHORN | 69 | BB-1288 | 14.1598
324955 | 2SHANNON RUN | 69 | BB-1288 | 8.27
325002 | 2WILS DOWN 1 | 69 | BB-1468 | 13.9
324656 | 2N MADISON T | 69 | BB-1315 | 6.6544
324735 | 2SOUTH POINT | 69 | BB-1315 | 5.7155
324794 | 2ASHLND PIPE | 69 | BB-1315 | 10.91
324886 | 2KY RIVER | 69 | BB-1315 | 7.49
324987 | 2W HICKMAN | 69 | BB-1315 | 17.39
325003 | 2WILS DOWN 2 | 69 | BB-1315 | 11.82
324337 | 2MOUNT TABOR | 69 | BB-1482 | 0.99
324611 | 2LIBERTY RD | 69 | BB-1482 | 24.46
324891 | 2LEX WATER | 69 | BB-1482 | 25.37
324332 | 2LAKE SHORE | 69 | BB-1368 | 25.39
324539 | 2FMC | 69 | BB-1368 | 16.18
325060 | 2BRYANT ROAD | 69 | BB-1368 | 41.17
324674 | 2PROC & GAMB | 69 | BB-1312 | 8.89
324331 | 2ASHLAND AVE | 69 | BB-1313 | 14.14
324984 | 2VINE STREET | 69 | BB-1313 | 11.23
324508 | 2EASTLAND | 69 | BB-1319 | 7.2
325081 | 2BRIAR HILL | 69 | BB-1319 | 4.05
324427 | 2BARDWELL | 69 | BB-1323 | 4.02
324823 | 2CLINTON 581 | 69 | BB-1323 | 4.2
324428 | 2BARLOW | 69 | BB-1325 | 4.78
324778 | 2WICKLIFE CI | 69 | BB-1325 | 2.45
324864 | 2FORRESTDALE | 69 | BB-1325 | 5.82
324085 | 2MARION 4 | 69 | BB-1407 | 3.35
324544 | 2FREDONIA QU | 69 | BB-1407 | 2.2
324628 | 2MARION SO | 69 | BB-1407 | 7.03
324865 | 2FREDONIA | 69 | BB-1407 | 2.15
324904 | 2MEXICO KU | 69 | BB-1407 | 0.62
324363 | 2SHELB CI KU | 69 | BB-1356 | 4.35
324599 | 2LANCASTER 2 | 69 | BB-1356 | 2.75
324760 | 2VAKSDAHL AV | 69 | BB-1356 | 3.64
324816 | 2CEMETARY RD | 69 | BB-1356 | 3.2549
324970 | 2STANFORD KU | 69 | BB-1356 | 5.87
324971 | 2STANFORD NO | 69 | BB-1356 | 6.56
326518 | 2SHELB CI EK | 69 | BB-1356 | 13.6767
324344 | 2ATOKA | 69 | BB-1316 | 3.33
324458 | 2BUENA VISTA | 69 | BB-1370 | 7.24
324546 | 2GARRARD CT | 69 | BB-1370 | 0.47
326547 | 2SONORA | 69 | BB-1349 | 4.15
324424 | 2BARDTWN CTY | 69 | BB-1320 | 9.42
324660 | 2NEW HAVEN | 69 | BB-1320 | 3.33
324801 | 2BARTON | 69 | BB-1320 | 6.46
326537 | 2WOODLAWN KU | 69 | BB-1320 | 5.15
324521 | 2ETOWN 4 | 69 | BB-1434 | 13.48
324575 | 2HODGENV KU | 69 | BB-1434 | 10.02
324093 | 2SPEN CHEMIC | 69 | BB-1285 | 5.83
324786 | 2ZION | 69 | BB-1285 | 3.17
324790 | 2AIRLINE RD | 69 | BB-1285 | 3.57
324477 | 2CAMP BRECKN | 69 | BB-1401 | 4.33
324502 | 2DIXON KU | 69 | BB-1401 | 2.3
324644 | 2MORGANFLD 4 | 69 | MORG-WHT-NEB | 3.6
324384 | 2APPALACHIA | 69 | BB-1302 | 2.5
324385 | 2BIG STONE G | 69 | BB-1302 | 12.29
324802 | 2BEAR BRANCH | 69 | BB-1302 | 1.89
324853 | 2E STONE GAP | 69 | BB-1302 | 6.55
324871 | 2HAMER | 69 | BB-1302 | 1.07
324389 | 2DWINA | 69 | BB-1400 | 0.8
324663 | 2NORTON EAST | 69 | BB-1400 | 4.53
324999 | 2WHTE OAK KU | 69 | BB-1400 | 0.53
324394 | 2TOMS CREEK | 69 | BB-1344 | 5.62
324716 | 2SANDY RIDGE | 69 | BB-1344 | 1.6
324591 | 2KEOKEE TAP | 69 | BB-1473 | 0.28
324592 | 2KEOKEE TVA | 69 | BB-1473 | 0.93
324498 | 2DAYS BRANCH | 69 | BB-1420 | 3.15
324744 | 2STRAGHT CRK | 69 | BB-1420 | 1.46
324876 | 2HOLMES MILL | 69 | BB-1420 | 0.45
324433 | 2BENHAM | 69 | BB-1306 | 0.99
324490 | 2CUMBERLAND | 69 | BB-1307 | 2.53
324798 | 2BAILEY CRK | 69 | BB-1307 | 0.8
324818 | 2CHAD TAP | 69 | BB-1307 | 12.5994
324827 | 2CLOVERLICK | 69 | BB-1307 | 2.01
324875 | 2HIGHSPLINT | 69 | BB-1307 | 1.46
324942 | 2ROBBINS | 69 | BB-1307 | 1.24
324978 | 2TOTZ | 69 | BB-1307 | 0.84
324562 | 2HARLAN KU | 69 | BB-1415 | 5.21
324738 | 2SAINT CHARL | 69 | BB-1415 | 0.74
324761 | 2VERDA | 69 | BB-1415 | 2.34
325045 | 2TURTLE CRK | 69 | BB-1415 | 0.25
325092 | 2COAL GOOD | 69 | BB-1415 | 2.45
324375 | 2DAYHOIT | 69 | BB-1342 | 2.59
324588 | 2KENTENIA | 69 | BB-1342 | 3.31
325008 | 2BLEDSOE | 69 | BB-1342 | 2.5456
325026 | 2PINE MOUNTN | 69 | BB-1342 | 2.4546
324374 | 2CROCKETT KU | 69 | BB-1287 | 1.37
324376 | 2DEER BRANCH | 69 | BB-1287 | 0.57
324377 | 2GARDNER | 69 | BB-1287 | 0.27
324543 | 2FOUR MILE | 69 | BB-1287 | 0.43
324638 | 2MILL CRK KU | 69 | BB-1287 | 3.27
324813 | 2CARY | 69 | BB-1287 | 0.55
326544 | 2ALEX CREEK | 69 | BB-1287 | 1.3637
324633 | 2MELDRUM | 69 | BB-1491 | 3.36
324684 | 2PINEVIL 722 | 69 | BB-1491 | 9
324415 | 2APPOLO FUEL | 69 | BB-1303 | 0.11
324460 | 2CALLOWAY | 69 | BB-1374 | 4.32
324456 | 2BRUSH CREEK | 69 | BB-1367 | 0.15
326535 | 2CARPENTER | 69 | BB-1367 | 11.7579
324573 | 2HINKLE | 69 | BB-1339 | 4.8232
324741 | 2STINKIN CRK | 69 | BB-1339 | 3.34
324423 | 2BARBOURVILE | 69 | BB-1308 | 19.37
326521 | 2CAMPGRND EK | 69 | BB-1338 | 10.5141
326530 | 2EMANUEL | 69 | BB-1338 | 9.7548
326539 | 2GIRDLER | 69 | BB-1338 | 4.6408
324482 | 2CORBIN EAST | 69 | BB-1404 | 11.65
324758 | 2US STEEL | 69 | BB-1404 | 9.04
324832 | 2CORBIN 1 | 69 | BB-1404 | 5.32
324833 | 2CORBIN 2 | 69 | BB-1404 | 13.56
324704 | 2ROCKHOLD | 69 | BB-1442 | 5.3769
341035 | 2BACON CRK | 69 | BB-1513 | 4.3674
341716 | 2KEAVY | 69 | BB-1513 | 10.7978
341758 | 2LIBERT CHUR | 69 | BB-1513 | 4.8231
342187 | 2S CORBIN | 69 | BB-1513 | 9.1367
324654 | 2MT VIC EK J | 69 | BB-1408 | 1.4839
325034 | 2CUMBER FALL | 69 | BB-1408 | 8.1243
324464 | 2CARON | 69 | BB-1286 | 10.9
324791 | 2AISIN | 69 | BB-1286 | 12.56
324860 | 2FARISTON | 69 | BB-1286 | 5.12
326542 | 2N CORBIN | 69 | BB-1286 | 6.1092
324360 | 2PINE HILL | 69 | BB-1365 | 1.07
324504 | 2E BERNST KU | 69 | BB-1365 | 4.67
324699 | 2RICE STA TP | 69 | BB-1486 | 7.1044
324768 | 2WACO | 69 | BB-1486 | 4.5
326553 | 2SE COAL | 69 | BB-1486 | 0.11
324525 | 2FAIRFIELD | 69 | BB-1322 | 4.17
324752 | 2TAYLORSV KU | 69 | BB-1322 | 6.63
324643 | 2MILL WOOD | 69 | BB-1379 | 2.01
324811 | 2CANEYVL JCT | 69 | BB-1379 | 5.96
324946 | 2ROSINE JCT | 69 | BB-1379 | 6.24
324585 | 2JERICHO | 69 | BB-1391 | 9.3411
324598 | 2LA GRANGE E | 69 | BB-1391 | 25.61
324887 | 2LA GRANG PE | 69 | BB-1391 | 9.59
324068 | 2E CAMPBELVL | 69 | BB-1403 | 7.2306
324349 | 2CAMPBELVIL2 | 69 | BB-1403 | 7.53
324603 | 2LEBANON CIT | 69 | BB-1403 | 6.21
324604 | 2LEBANON IND | 69 | BB-1403 | 2.44
324605 | 2LEBANON EK | 69 | BB-1403 | 12.5278
324889 | 2LEBANON SO | 69 | BB-1403 | 11.44
325020 | 2LEBANON E | 69 | BB-1403 | 14.02
324468 | 2CENTRL CI S | 69 | BB-1390 | 7.23
324652 | 2MUHLENBRG P | 69 | BB-1390 | 5.01
324817 | 2CENTRAL CIT | 69 | BB-1390 | 5.12
324746 | 2SUNOCO | 69 | BB-1425 | 1.51
324973 | 2STURGIS | 69 | BB-1425 | 6.34
324698 | 2RADCLIFF SO | 69 | BB-1436 | 4.21
326555 | 2RINEYVIL RD | 69 | BB-1436 | 3.68
324345 | 2BARDTWN IND | 69 | BB-1321 | 17.37
324395 | 2WISE | 69 | BB-1343 | 6.07
324517 | 2ESSERVILLE | 69 | BB-1343 | 8.99
324824 | 2CLINCH VALL | 69 | BB-1343 | 8.95
324369 | 1WENTZ | 34.5 | BB-1300 | 3.87
324670 | 2OSAKA EAST | 69 | BB-1300 | 0.46
324380 | 2DANIEL BRAN | 69 | BB-1294 | 0.49
324393 | 2ROSE HILL | 69 | BB-1294 | 3.59
324696 | 2PUCKETT CRK | 69 | BB-1294 | 1.22
324815 | 2CAWOOD | 69 | BB-1294 | 2.48
324892 | 2LIGGETT | 69 | BB-1294 | 0.12
325068 | 2HAMBLIN | 69 | BB-1294 | 6.81
324347 | 2BEATTY 649 | 69 | BB-1327 | 2.56
324383 | 1YEL RK N | 34.5 | BB-1327 | 0.18
324496 | 2DARK HOLLOW | 69 | BB-1327 | 3.47
324880 | 2IRVINE | 69 | BB-1327 | 6.23
324435 | 2BEREA NORTH | 69 | BB-1336 | 11.01
324676 | 2PAINT LICK | 69 | BB-1336 | 1.03
324805 | 2BEREA 2 | 69 | BB-1336 | 11.66
324700 | 2RICHMND SO | 69 | BB-1446 | 13.92
324936 | 2RICHMND IND | 69 | BB-1446 | 12.29
324938 | 2RICHMND 3 | 69 | BB-1446 | 24.65
341008 | 2ALCAN | 69 | BB-1514 | 30.1274
341359 | 2CROOKSVIL | 69 | BB-1514 | 5.895
341611 | 2HICKORY PL | 69 | BB-1514 | 12.443
342103 | 2PPG | 69 | BB-1514 | 4.3099
342288 | 2SPEEDWELL | 69 | BB-1514 | 1.3
324715 | 2SALVISA | 69 | BB-1345 | 2
324721 | 2SHAKERTOWN | 69 | BB-1345 | 2.12
326974 | 2BRIDGPRT 2 | 69 | BB-1361 | 5.8078
324124 | 2CENTRTOWN S | 69 | BB-3000 | 0.95
324511 | 2ECHOLS | 69 | BB-3000 | 0.9
324703 | 2RIVERVIEW | 69 | BB-3000 | 1.48
324959 | 2SIMMONS | 69 | BB-3000 | 0.29
326564 | 2LEW BREC | 69 | BB-3000 | 0.14
324048 | 2PARKWY MINE | 69 | BB-1337 | 4.63
324060 | 1BEECH CR | 34.5 | BB-1337 | 1.09
324062 | 1BEECHMNT | 34.5 | BB-1337 | 2.57
324122 | 1DRAKESBO | 34.5 | BB-1337 | 2.14
324188 | 1REED MIN | 34.5 | BB-1337 | 0.48
324437 | 2BEVIER KU | 69 | BB-1337 | 0.52
324745 | 2STRINGTOWN | 69 | BB-1337 | 0.84
324659 | 2NELSON | 69 | BB-1432 | 0.98
324077 | 2GREENVILE W | 69 | BB-1461 | 1.98
324691 | 2POWDERLY | 69 | BB-1461 | 5.53
324870 | 2GREENVILLE | 69 | BB-1461 | 3.37
326593 | 2GREENVIL N | 69 | BB-1461 | 8.46
326594 | 2GREENVL 12 | 69 | BB-1461 | 5.87
324061 | 2BORG-WARNER | 69 | BB-1353 | 8.5
324079 | 2HANSON | 69 | BB-1353 | 9.89
324723 | 2SHAVER CHAP | 69 | BB-1353 | 9.23
324896 | 2MADSNV E | 69 | BB-1353 | 8.39
324902 | 2MCCOY AVE | 69 | BB-1353 | 9.26
325086 | 2KEN AMERI 2 | 69 | BB-1353 | 0.66
324505 | 2E DIAMOND | 69 | BB-1457 | 3.39
324810 | 2CALHOUN | 69 | BB-1457 | 2.53
324119 | 1CROSSRD | 34.5 | B-69-41 | 0.31
324121 | 1DANL BOONE | 34.5 | B-69-41 | 0.46
324327 | 1ST CHARL | 34.5 | B-69-41 | 2.79
324507 | 2EARLINGTON | 69 | B-69-41 | 6.17
324587 | 2KEN AMERICA | 69 | B-69-41 | 0.54
324820 | 2ISLAND MINE | 69 | B-69-41 | 0.67
324850 | 2DOZIER H | 69 | B-69-41 | 5.13
325062 | 2TEXAS GAS | 69 | B-69-41 | 2.64
324898 | 2MANITOU | 69 | BB-1299 | 1.4
324993 | 2WARRIOR CL | 69 | BB-1299 | 7.18
325761 | 2WARRIOR PRP | 69 | BB-1299 | 6.24
325767 | 2SENTRY | 69 | BB-1299 | 0.21
324081 | 2MADSNV GE | 69 | BB-1428 | 5.41
324083 | 2MADSNV W | 69 | BB-1428 | 17.4
324895 | 2MADSNV HO | 69 | BB-1428 | 9.41
324897 | 2MADSNV N | 69 | BB-1428 | 13.19
324081 | 2MADSNV GE | 69 | BB-1428A | 5.41
324083 | 2MADSNV W | 69 | BB-1428A | 17.4
324895 | 2MADSNV HO | 69 | BB-1428A | 9.41
324897 | 2MADSNV N | 69 | BB-1428A | 13.19
324118 | 1CROFTON | 34.5 | B-69-40 | 2.3
324181 | 1NORTNVL | 34.5 | B-69-40 | 4.1
324371 | 1WHIT PLN | 34.5 | B-69-40 | 2.74
324648 | 2MORTONS GAP | 69 | B-69-40 | 2.29
326506 | 1MANNIN | 34.5 | B-69-40 | 0.64
|  |  | BB-1464 | -
324065 | 2DAWSON 764 | 69 | BB-1410 | 3.55
324182 | 1OUTWOOD | 34.5 | BB-1410 | 0.35
324690 | 2DAWSON TAP | 69 | BB-1410 | 3.083
324720 | 1SIXTHVEIN | 34.5 | BB-1410 | 2.56
324747 | 2SUNSET MINE | 69 | BB-1410 | 0.27
324843 | 2DAWSON IND | 69 | BB-1410 | 2.02
324471 | 2CHRISTIAN | 69 | BB-1326 | 0.55
324822 | 2CLAY KU | 69 | BB-1326 | 2.83
324846 | 2DIAMOND | 69 | BB-1326 | 0.37
324931 | 2PROVIDNCE E | 69 | BB-1326 | 2.49
324932 | 2PROVIDENCE | 69 | BB-1326 | 4.18
325010 | 2WEBCOAL 2 | 69 | BB-1326 | 0.62
324086 | 2MORGANF IND | 69 | BB-1406 | 4.67
324097 | 2PEAB WASH | 69 | BB-1406 | 0.2
324571 | 2HIGHLAND MI | 69 | BB-1406 | 0.33
324726 | 2SHELBYVIL S | 69 | B-69-42 | 21.57
324725 | 2SHELBYVIL E | 69 | BB-1399 | 21.53
341317 | 2CLAY VILLAG | 69 | BB-1399 | 9.7015
341391 | 2DEFOE | 69 | BB-1399 | 4.021
341950 | 2NEW CASTLE | 69 | BB-1399 | 5.3063
324620 | 2LAWRENCEBRG | 69 | BB-1346 | 25.37
|  |  | B-69-78 | -
324710 | 2RVR CITY SH | 69 | BB-1332 | 2.73
324554 | 2GRENSBRG KU | 69 | BB-1402 | 4.57
324557 | 2GR RVR PLAZ | 69 | BB-1402 | 7.3221
324829 | 2CAMPBELVIL1 | 69 | BB-1402 | 12.53
324830 | 2CAMPBELV EK | 69 | BB-1402 | 11.5694
326970 | 2MILE LAN EK | 69 | BB-1402 | 9.7611
324358 | 2M-V CLARKSN | 69 | BB-1398 | 2.49
324509 | 2EASTVIEW | 69 | BB-1398 | 4.13
324607 | 2LEITCHF CIT | 69 | BB-1398 | 6.62
324608 | 2LEITCHF E | 69 | BB-1398 | 5.52
324821 | 2CLARKSON | 69 | BB-1398 | 3.73
326545 | 2LOCUST LGE | 69 | BB-1453 | 20.82
324444 | 2BLUELICK EK | 69 | BB-1274 | 9.0765
324809 | 2BROOKS EKPC | 69 | BB-1274 | 24.5121
325043 | 2SHEPHERDSV | 69 | BB-1274 | 8.36
324487 | 2CRESTWOOD | 69 | BB-1277 | 41.51
324616 | 2LONG RUN | 69 | BB-1277 | 5.9424
324649 | 2MORRIS FORM | 69 | BB-1289 | 5.64
|  |  | BB-1328 | -
324775 | 2WHAS | 69 | BB-1272 | 10.94
325022 | 2EASTWOOD W | 69 | BB-1272 | 21.31
|  |  | B-69-45 | -
341458 | 2ETOWN EK2 | 69 | BB-1512 | 9.3887
342337 | 2THARP | 69 | BB-1512 | 10.0175
324579 | 2HARMNY LAND | 69 | BB-1470 | 16.27
324729 | 2SIMPSONVILL | 69 | BB-1430 | 16.53
324653 | 2M-V SIMPSON | 69 | BB-1450 | 2.43
324737 | 2SOMERSET SO | 69 | BB-1424 | 7.33
324787 | 2UNION UNDWR | 69 | BB-1424 | 12.44
324990 | 2WAITSBORO | 69 | BB-1424 | 8.02
342232 | 2SEWELLTON | 69 | BB-1424 | 5.5615
324513 | 2EDDYVILLE | 69 | BB-1393 | 7.65
324852 | 2DYCUSBURG | 69 | BB-1393 | 0.23
324883 | 1SALEM | 34.5 | BB-1393 | 2.22
324885 | 2KUTTAWA | 69 | BB-1393 | 2.52
324949 | 2SALEM 673 | 69 | BB-1393 | 2.37
324960 | 2SKYLIGHT | 69 | BB-1392 | 6.86
324499 | 2DEL PARK | 69 | BB-1375 | 26.99
324406 | 2AIKEN | 69 | B-69-136 | 51.44
|  |  | B-69-137 | -
|  |  | B-69-140 | -
324623 | 2LYNDON | 69 | B-69-141 | 17.24
324348 | 2BRODHEAD CI | 69 | BB-1364 | 2.14
324350 | 2CRAB ORCHAR | 69 | BB-1364 | 1.41
324359 | 2MT VERN 589 | 69 | BB-1364 | 4.26
324597 | 2KY ST HOSP | 69 | BB-1355 | 4.35
324494 | 2DANVILLE 1 | 69 | BB-1354 | 11.6
324597 | 2KY ST HOSP | 69 | BB-1354 | 4.35
324840 | 2DANVILLE E | 69 | BB-1354 | 15.46
|  |  | BB-1270 | -
|  |  | BB-1271 | -
324740 | 2SOUTH PARK | 69 | BB-1275 | 17.61
362116 | 2KY HYDRO | 69 | PRIN-KYD-PAD | 23.68
324067 | 2EDDYV PRIS | 69 | PRIN-KYD-PAD | 3.61
|  |  | B-69-46 | -
324695 | 2PARKER SEAL | 69 | P1-1000 | 8.54
324749 | 2SYLVANIA | 69 | P1-1000 | 8.09
324118 | 1CROFTON | 34.5 | P1-1001 | 2.3
324181 | 1NORTNVL | 34.5 | P1-1001 | 4.1
324371 | 1WHIT PLN | 34.5 | P1-1001 | 2.74
324648 | 2MORTONS GAP | 69 | P1-1001 | 2.29
326506 | 1MANNIN | 34.5 | P1-1001 | 0.64
|  |  | B-69-25 | -
324274 | 4LOCKPORT | 138 | BB-1164 | 3.06
324306 | 4SHADRACK | 138 | BB-1164 | 3.69
326512 | 4AIRGAS | 138 | BB-1097 | 8.51
|  |  | B-138-114 | -
326526 | 4N SHARKEY | 138 | B-138-119 | 1.2322
326532 | 4SHARKEY | 138 | B-138-119 | 8.4668
324193 | 4FLEMINGB KU | 138 | B-138-113 | 4.82
324323 | 4WEDONIA | 138 | B-138-113 | 3.58
324221 | 4BUTLER | 138 | B-138-118 | 3.23
324192 | 4DAYTON-WALT | 138 | BB-1179 | 3.5
324283 | 4MIDWAY | 138 | BB-1192 | 6.61
326548 | 4IBM NORTH | 138 | BB-1201 | 2.67
324317 | 4VILEY ROAD | 138 | BB-1203 | 24.27
326560 | 4BG ARMY DEP | 138 | BB-1240 | 4.8
|  |  | B-138-122 | -
324230 | 4CLAYS MILL | 138 | BB-1143 | 19.88
325075 | 5KMPA COLEMN | 161 | BB-1049 | 66.99
|  |  | B-138-111 | -
|  |  | B-161-125 | -
|  |  | B-138-21 | -
324270 | 4LEBANON WES | 138 | BB-1133 | 6.91
|  |  | B-161-126 | -
324147 | 5HOWARDS BR | 161 | BB-1063 | 0.21
|  |  | B-161-24 | -
|  |  | B-161-23 | -
|  |  | B-161-124 | -
342739 | 5GREEN HALL | 161 | BB-1509 | 2.6482
|  |  | B-138-112 | -
342685 | 4UNION CITY | 138 | BB-1239 | 6.4748
324047 | 4BLACKBRANCH | 138 | BB-1216 | 13.06
|  |  | BB-1019 | -
342553 | 4BECKNERV | 138 | B-138-97 | 1.593
|  |  | B-161-108 | -
|  |  | BB-1057 | -
|  |  | B-161-106 | -
342772 | 5MARION IP | 161 | B-161-128 | 7.3059
342798 | 5S MARION IP | 161 | B-161-128 | 30.4021
342802 | 5SALOMA | 161 | B-161-128 | 12.0099
|  |  | B-69-18 | -
|  |  | B-69-19 | -
|  |  | B-138-28 | -
324170 | 1KNOB CRK | 34.5 | BB-1228 | 15.4897
325057 | 4KOSMOS CEME | 138 | BB-1229 | 27.23
324150 | 5LEBANON JCT | 161 | BB-1066 | 13.58
|  |  | BB-1026 | -
|  |  | B-345-475 | -
324215 | 4BRIDGPOR HE | 138 | BB-1139 | 5.9
324228 | 4CENTERFIELD | 138 | B-138-130 | 29.64
342601 | 4JACKSNVIL | 138 | B-138-12 | 3.3691
|  |  | B-69-13 | -
|  |  | B-69-15 | -
|  |  | B-69-20 | -
|  |  | B-69-26 | -
324243 | 4ETHEL | 138 | B-69-29 | 21.25
324277 | 4LYNDON SO | 138 | B-69-30 | 26.2
324285 | 4MUD LANE | 138 | B-69-31 | 62.72
324259 | 4HANCOCK | 138 | BB-1205 | 13.05
324292 | 4OKOLONA | 138 | BB-1187 | 26.56
|  |  | BB-1136 | -
324299 | 4PLEASUR RDG | 138 | BB-1112 | 37.32
324241 | 4DIXIE | 138 | BB-1098 | 30.86
|  |  | BB-1075 | -
|  |  | BB-1062 | -
|  |  | BB-1060 | -
|  |  | BB-1061 | -
|  |  | B-69-135 | -
|  |  | B-69-132 | -
|  |  | B-138-120 | -
|  |  | B-138-121 | -
|  |  | B-138-109 | -
325042 | 4JEFERSONTWN | 138 | BB-1226 | 30.39
|  |  | BB-1001 | -
|  |  | B-345-100 | -
|  |  | B-161-107 | -
|  |  | B-138-110 | -
|  |  | B-138-117 | -
|  |  | B-161-84 | -
|  |  | B-138-116 | -
|  |  | B-345-101 | -
|  |  | B-345-102 | -
|  |  | B-69-133 | -
|  |  | BB-1074 | -
|  |  | BB-1132 | -
|  |  | BB-1218 | -
|  |  | BB-2021 | -
249788 | 08LOUCEM | 138 | BB-1245B | 10.049
|  |  | B-69-35 | -
|  |  | B-69-32 | -
|  |  | B-69-33 | -
|  |  | P1-1002 | -
325044 | 4INTRNTL | 138 | P1-2-1004 | 30.17
324399 | 1CANERN11 | 14 | P1-2-1005 | 5.4
|  |  | SINGLE OPN LIN 1986 242691-243088(1) | -
|  |  | SINGLE OPN LIN 1987 242927-242938(1) | -
|  |  | SINGLE OPN LIN 1988 242938-243034(2) | -
|  |  | SINGLE OPN LIN 1989 242938-243034(3) | -
|  |  | SINGLE OPN LIN 1990 242938-246888(1) | -
|  |  | SINGLE OPN LIN 1991 242982-243047(1) | -
|  |  | SINGLE OPN LIN 1992 242988-242992(1) | -
|  |  | SINGLE OPN LIN 1993 242988-243042(1) | -
|  |  | SINGLE OPN LIN 1994 243013-243069(1) | -
|  |  | SINGLE OPN LIN 1995 243019-243102(1) | -
|  |  | SINGLE OPN LIN 1996 243042-243047(1) | -
|  |  | SINGLE OPN LIN 1997 243042-243069(1) | -
|  |  | SINGLE OPN LIN 1998 243042-243173(5) | -
|  |  | SINGLE OPN LIN 1999 243047-243087(1) | -
|  |  | SINGLE OPN LIN 2000 243047-243819(1) | -
|  |  | SINGLE OPN LIN 2001 243069-246782(1) | -
|  |  | SINGLE OPN LIN 2002 243088-243184(2) | -
|  |  | SINGLE OPN LIN 2003 243167-243171(1) | -
|  |  | SINGLE OPN LIN 2004 243167-243178(1) | -
|  |  | SINGLE OPN LIN 2005 243167-243725(1) | -
|  |  | SINGLE OPN LIN 2006 243171-243183(1) | -
|  |  | SINGLE OPN LIN 2007 243173-243181(1) | -
|  |  | SINGLE OPN LIN 2008 243173-243597(1) | -
|  |  | SINGLE OPN LIN 2009 243173-246916(1) | -
|  |  | SINGLE OPN LIN 2010 243173-246917(1) | -
|  |  | SINGLE OPN LIN 2011 243176-243178(1) | -
247476 | 05PLYMOUTHHT | 69 | SINGLE OPN LIN 2012 243178-247476(1) | 4.054
|  |  | SINGLE OPN LIN 2013 243181-243183(1) | -
|  |  | SINGLE OPN LIN 2014 243618-247072(1) | -
|  |  | SINGLE OPN LIN 2015 243656-243808(1) | -
|  |  | SINGLE OPN LIN 2016 243657-243808(1) | -
|  |  | SINGLE OPN LIN 2017 243663-243702(1) | -
|  |  | SINGLE OPN LIN 2018 243663-243750(1) | -
|  |  | SINGLE OPN LIN 2020 243678-243679(1) | -
|  |  | SINGLE OPN LIN 2021 243679-243702(1) | -
|  |  | SINGLE OPN LIN 2022 243684-243702(1) | -
|  |  | SINGLE OPN LIN 2023 243684-243804(1) | -
|  |  | SINGLE OPN LIN 2024 243684-244008(1) | -
244686 | 05VANCEBURG | 138 | SINGLE OPN LIN 2025 243688-244686(Z1) | 6.945
|  |  | SINGLE OPN LIN 2026 243702-246971(1) | -
|  |  | SINGLE OPN LIN 2027 243712-243716(1) | -
|  |  | SINGLE OPN LIN 2028 243714-243727(1) | -
|  |  | SINGLE OPN LIN 2029 243716-243732(1) | -
|  |  | SINGLE OPN LIN 2030 243716-243743(1) | -
|  |  | SINGLE OPN LIN 2031 243724-243737(1) | -
|  |  | SINGLE OPN LIN 2032 243724-243742(1) | -
|  |  | SINGLE OPN LIN 2033 243727-243734(1) | -
|  |  | SINGLE OPN LIN 2034 243728-243740(1) | -
|  |  | SINGLE OPN LIN 2035 243728-243741(1) | -
|  |  | SINGLE OPN LIN 2036 243732-243737(1) | -
|  |  | SINGLE OPN LIN 2037 243733-243812(1) | -
|  |  | SINGLE OPN LIN 2039 243734-243812(1) | -
|  |  | SINGLE OPN LIN 2041 243741-243742(1) | -
|  |  | SINGLE OPN LIN 2042 243750-244632(1) | -
243758 | 05MIDDLECR | 46 | SINGLE OPN LIN 2043 243758-243759(1) | 0.906
|  |  | SINGLE OPN LIN 2044 243808-244592(1) | -
|  |  | SINGLE OPN LIN 2045 243808-244616(1) | -
|  |  | SINGLE OPN LIN 2046 244632-246970(1) | -
|  |  | SINGLE OPN LIN 2047 246970-246971(1) | -
|  |  | SINGLE OPN TIE 2048 242691-242835(1) | -
|  |  | SINGLE OPN TIE 2049 242691-244720(1) | -
|  |  | SINGLE OPN TIE 2050 242918-244965(EQ) | -
|  |  | SINGLE OPN TIE 2051 242918-245615(4) | -
|  |  | SINGLE OPN TIE 2052 242927-242924(1) | -
|  |  | SINGLE OPN TIE 2053 242938-248005(1) | -
|  |  | SINGLE OPN TIE 2054 242938-248005(2) | -
|  |  | SINGLE OPN TIE 2055 242938-248013(1) | -
|  |  | SINGLE OPN TIE 2056 242938-253077(1) | -
|  |  | SINGLE OPN TIE 2057 242982-243815(2) | -
243124 | 05TEXEAS | 138 | SINGLE OPN TIE 2058 242992-243124(1) | 25.5
|  |  | SINGLE OPN TIE 2059 242992-243968(1) | -
|  |  | SINGLE OPN TIE 2060 243013-242698(1) | -
|  |  | SINGLE OPN TIE 2061 243013-242807(1) | -
|  |  | SINGLE OPN TIE 2062 243013-243611(1) | -
|  |  | SINGLE OPN TIE 2063 243013-243766(ZC) | -
|  |  | SINGLE OPN TIE 2064 243013-243766(ZD) | -
|  |  | SINGLE OPN TIE 2065 243013-244949(1) | -
|  |  | SINGLE OPN TIE 2066 243013-244949(2) | -
|  |  | SINGLE OPN TIE 2067 243013-246324(Z1) | -
|  |  | SINGLE OPN TIE 2068 243019-242787(1) | -
|  |  | SINGLE OPN TIE 2069 243019-246911(1) | -
|  |  | SINGLE OPN TIE 2070 243019-246946(1) | -
|  |  | SINGLE OPN TIE 2071 243019-249995(1) | -
|  |  | SINGLE OPN TIE 2072 243034-243501(1) | -
|  |  | SINGLE OPN TIE 2073 243034-243544(2) | -
|  |  | SINGLE OPN TIE 2074 243034-245632(1) | -
|  |  | SINGLE OPN TIE 2075 243042-245948(Z1) | -
|  |  | SINGLE OPN TIE 2076 243042-245949(Z1) | -
|  |  | SINGLE OPN TIE 2077 243064-242929(2) | -
|  |  | SINGLE OPN TIE 2078 243064-242999(1) | -
|  |  | SINGLE OPN TIE 2079 243064-243193(1) | -
|  |  | SINGLE OPN TIE 2080 243064-243675(1) | -
|  |  | SINGLE OPN TIE 2081 243064-245615(1) | -
|  |  | SINGLE OPN TIE 2082 243064-245664(1) | -
|  |  | SINGLE OPN TIE 2083 243064-290186(2) | -
|  |  | SINGLE OPN TIE 2084 243087-243140(1) | -
|  |  | SINGLE OPN TIE 2085 243088-245615(Z1) | -
|  |  | SINGLE OPN TIE 2086 243088-245948(1) | -
244942 | 05SINK SP8 | 138 | SINGLE OPN TIE 2087 243102-244942(Z1) | 3.365
|  |  | SINGLE OPN TIE 2088 243102-245948(1) | -
290138 | 05KOT COAL | 69 | SINGLE OPN TIE 2089 243171-290138(1) | 1.05
|  |  | SINGLE OPN TIE 2090 243173-246850(1) | -
|  |  | SINGLE OPN TIE 2091 243176-243164(1) | -
243827 | 05SUNCOKE | 69 | SINGLE OPN TIE 2092 243176-243827(1) | 10.95
|  |  | SINGLE OPN TIE 2093 243176-247033(1) | -
|  |  | SINGLE OPN TIE 2094 243184-244719(1) | -
|  |  | SINGLE OPN TIE 2095 243184-244968(1) | -
|  |  | SINGLE OPN TIE 2096 243184-244968(2) | -
|  |  | SINGLE OPN TIE 2097 243453-243454(1) | -
|  |  | SINGLE OPN TIE 2098 243453-243469(3) | -
|  |  | SINGLE OPN TIE 2099 243453-243469(4) | -
|  |  | SINGLE OPN TIE 2100 243453-244022(1) | -
|  |  | SINGLE OPN TIE 2101 243453-245769(1) | -
|  |  | SINGLE OPN TIE 2102 243453-253248(1) | -
|  |  | SINGLE OPN TIE 2103 243597-246741(1) | -
|  |  | SINGLE OPN TIE 2104 243618-253076(1) | -
|  |  | SINGLE OPN TIE 2105 243656-243671(1) | -
|  |  | SINGLE OPN TIE 2106 243657-243708(1) | -
|  |  | SINGLE OPN TIE 2107 243657-244688(1) | -
|  |  | SINGLE OPN TIE 2108 243678-243669(SR) | -
|  |  | SINGLE OPN TIE 2109 243688-245949(1) | -
|  |  | SINGLE OPN TIE 2111 243712-244727(1) | -
|  |  | SINGLE OPN TIE 2119 243743-244670(1) | -
|  |  | SINGLE OPN TIE 2120 243759-243753(1) | -
|  |  | SINGLE OPN TIE 2121 243759-243754(1) | -
|  |  | SINGLE OPN TIE 2122 243759-247415(1) | -
|  |  | SINGLE OPN TIE 2123 243804-244575(1) | -
|  |  | SINGLE OPN TIE 2126 243819-243822(1) | -
|  |  | SINGLE OPN TIE 2127 243819-243826(1) | -
|  |  | SINGLE OPN TIE 2128 244008-242915(Z1) | -
|  |  | SINGLE OPN TIE 2129 244592-244599(1) | -
|  |  | SINGLE OPN TIE 2130 244616-244626(1) | -
|  |  | SINGLE OPN TIE 2131 246782-247061(1) | -
|  |  | SINGLE OPN TIE 2132 246782-247062(1) | -
|  |  | SINGLE OPN TIE 2133 246888-243454(1) | -
|  |  | SINGLE OPN TIE 2134 246888-246889(1) | -
|  |  | SINGLE OPN TIE 2135 246916-243815(1) | -
|  |  | SINGLE OPN TIE 2136 246917-243815(1) | -
|  |  | SINGLE OPN TIE 2139 247072-246790(1) | -
247073 | 05RAVEN | 69 | SINGLE OPN TIE 2140 247072-247073(1) | 5.183
|  |  | SINGLE OPN LIN 2141 249564-249991(1) | -
|  |  | SINGLE OPN LIN 2142 249564-249991(46) | -
|  |  | SINGLE OPN LIN 2143 249566-249570(1) | -
|  |  | SINGLE OPN LIN 2144 249566-249578(1) | -
|  |  | SINGLE OPN LIN 2145 249566-249582(1) | -
|  |  | SINGLE OPN LIN 2146 249567-249575(1) | -
|  |  | SINGLE OPN LIN 2147 249567-250057(10) | -
|  |  | SINGLE OPN LIN 2148 249567-250057(9) | -
|  |  | SINGLE OPN LIN 2149 249570-249575(1) | -
|  |  | SINGLE OPN LIN 2150 249570-249577(1) | -
|  |  | SINGLE OPN LIN 2151 249570-250082(1) | -
|  |  | SINGLE OPN LIN 2152 249570-250083(1) | -
|  |  | SINGLE OPN LIN 2153 249571-249573(1) | -
|  |  | SINGLE OPN LIN 2154 249571-249575(1) | -
|  |  | SINGLE OPN LIN 2155 249573-249577(1) | -
|  |  | SINGLE OPN LIN 2156 249573-250097(1) | -
|  |  | SINGLE OPN LIN 2157 249577-249580(Z1) | -
|  |  | SINGLE OPN LIN 2158 249577-249581(1) | -
|  |  | SINGLE OPN LIN 2159 249578-250136(1) | -
|  |  | SINGLE OPN LIN 2160 249580-251968(1H) | -
|  |  | SINGLE OPN LIN 2161 249580-251969(1L) | -
|  |  | SINGLE OPN LIN 2162 249581-250145(1) | -
|  |  | SINGLE OPN LIN 2163 249990-250021(1) | -
|  |  | SINGLE OPN LIN 2164 249991-250028(1) | -
|  |  | SINGLE OPN LIN 2165 249991-250077(1) | -
|  |  | SINGLE OPN LIN 2166 249991-250148(1) | -
|  |  | SINGLE OPN LIN 2167 249991-251279(2) | -
|  |  | SINGLE OPN LIN 2168 249999-250007(1) | -
|  |  | SINGLE OPN LIN 2169 249999-250044(1) | -
|  |  | SINGLE OPN LIN 2170 250016-250057(1) | -
|  |  | SINGLE OPN LIN 2171 250044-250152(Z1) | -
250045 | 08HEBRN1 | 138 | SINGLE OPN LIN 2172 250045-250151(Z1) | 15.088
|  |  | SINGLE OPN LIN 2173 250054-250077(1) | -
|  |  | SINGLE OPN LIN 2174 250057-250058(1) | -
|  |  | SINGLE OPN LIN 2175 250057-250060(1) | -
|  |  | SINGLE OPN LIN 2176 250057-250070(1) | -
|  |  | SINGLE OPN LIN 2177 250057-250131(1) | -
|  |  | SINGLE OPN LIN 2178 250057-250151(1) | -
|  |  | SINGLE OPN LIN 2179 250058-251378(1) | -
|  |  | SINGLE OPN LIN 2180 250136-250141(1) | -
|  |  | SINGLE OPN LIN 2181 250145-250154(1) | -
|  |  | SINGLE OPN LIN 2182 250151-250152(Z1) | -
|  |  | SINGLE OPN LIN 2183 250154-251970(T1) | -
|  |  | SINGLE OPN LIN 2184 250154-251971(T2) | -
|  |  | SINGLE OPN LIN 2185 250154-251972(T3) | -
251276 | 08BROWER | 69 | SINGLE OPN LIN 2186 251276-251469(1) | 2.239
|  |  | SINGLE OPN LIN 2187 251291-251301(1) | -
|  |  | SINGLE OPN LIN 2188 251291-251315(1) | -
|  |  | SINGLE OPN LIN 2189 251301-251310(1) | -
|  |  | SINGLE OPN LIN 2190 251314-251315(1) | -
|  |  | SINGLE OPN LIN 2191 251314-251467(1) | -
251368 | 08LEVIB | 69 | SINGLE OPN LIN 2192 251367-251368(Z1) | 3.412
251373 | 08LMBRG1 | 69 | SINGLE OPN LIN 2192 251367-251368(Z1) | 8.787
251374 | 08LMBRG2 | 69 | SINGLE OPN LIN 2192 251367-251368(Z1) | 6.784
251367 | 08LEVIA | 69 | SINGLE OPN LIN 2193 251367-251467(1) | 4.648
251368 | 08LEVIB | 69 | SINGLE OPN LIN 2193 251367-251467(1) | 3.412
251373 | 08LMBRG1 | 69 | SINGLE OPN LIN 2193 251367-251467(1) | 8.787
251374 | 08LMBRG2 | 69 | SINGLE OPN LIN 2193 251367-251467(1) | 6.784
251406 | 08MONSTW | 69 | SINGLE OPN LIN 2194 251378-251406(1) | 6.923
|  |  | SINGLE OPN LIN 2195 251378-251469(1) | -
|  |  | SINGLE OPN LIN 2196 251378-251579(1) | -
|  |  | SINGLE OPN LIN 2197 251467-251579(1) | -
|  |  | SINGLE OPN LIN 2198 251468-251469(1) | -
|  |  | SINGLE OPN TIE 2199 249564-248002(1) | -
|  |  | SINGLE OPN TIE 2200 249564-248013(1) | -
|  |  | SINGLE OPN TIE 2201 249566-248013(1) | -
|  |  | SINGLE OPN TIE 2202 249566-250029(1) | -
|  |  | SINGLE OPN TIE 2203 249566-253006(1) | -
|  |  | SINGLE OPN TIE 2204 249566-253079(1) | -
|  |  | SINGLE OPN TIE 2205 249567-243233(1) | -
|  |  | SINGLE OPN TIE 2206 249567-249576(1) | -
|  |  | SINGLE OPN TIE 2207 249567-251950(7) | -
|  |  | SINGLE OPN TIE 2208 249567-251951(8) | -
|  |  | SINGLE OPN TIE 2209 249567-253090(1) | -
|  |  | SINGLE OPN TIE 2210 249571-250092(1) | -
|  |  | SINGLE OPN TIE 2211 249571-250093(1) | -
|  |  | SINGLE OPN TIE 2212 249575-249565(1) | -
|  |  | SINGLE OPN TIE 2213 249575-250117(1) | -
|  |  | SINGLE OPN TIE 2214 249575-250118(1) | -
|  |  | SINGLE OPN TIE 2215 249578-253077(1) | -
|  |  | SINGLE OPN TIE 2217 249582-249574(1) | -
|  |  | SINGLE OPN TIE 2218 249582-249583(1) | -
|  |  | SINGLE OPN TIE 2219 249582-250162(1) | -
|  |  | SINGLE OPN TIE 2220 249990-253076(1) | -
251277 | 08BROWN | 69 | SINGLE OPN TIE 2221 249990-251277-251792(1) | 2.678
251280 | 08BURNS | 69 | SINGLE OPN TIE 2221 249990-251277-251792(1) | 0.759
251324 | 08FLICTY | 69 | SINGLE OPN TIE 2221 249990-251277-251792(1) | 6.481
251407 | 08MOSCOW | 69 | SINGLE OPN TIE 2221 249990-251277-251792(1) | 3.084
251447 | 08S.BET2 | 69 | SINGLE OPN TIE 2221 249990-251277-251792(1) | 4.176
251566 | 08GTWNVI | 69 | SINGLE OPN TIE 2221 249990-251277-251792(1) | 9.247
251582 | 08GOODWN | 69 | SINGLE OPN TIE 2221 249990-251277-251792(1) | 4.105
251792 | 08BROWN | 34.5 | SINGLE OPN TIE 2221 249990-251277-251792(1) | 21.757
|  |  | SINGLE OPN TIE 2222 249991-251278(1) | -
|  |  | SINGLE OPN TIE 2223 249991-251278-252039(1) | -
|  |  | SINGLE OPN TIE 2224 250007-250014(1) | -
|  |  | SINGLE OPN TIE 2225 250007-250124(1) | -
|  |  | SINGLE OPN TIE 2226 250016-250061(1) | -
|  |  | SINGLE OPN TIE 2227 250016-251311(1) | -
|  |  | SINGLE OPN TIE 2228 250016-251312(1) | -
251793 | 08EBNZR6 | 34.5 | SINGLE OPN TIE 2229 250016-251793(1) | 34.168
|  |  | SINGLE OPN TIE 2230 250021-250020(Z1) | -
|  |  | SINGLE OPN TIE 2231 250028-250027(Z1) | -
|  |  | SINGLE OPN TIE 2233 250057-249736(1) | -
|  |  | SINGLE OPN TIE 2235 250058-251960-251961(18) | -
|  |  | SINGLE OPN TIE 2236 250060-250048(1) | -
|  |  | SINGLE OPN TIE 2237 250070-250032(1) | -
|  |  | SINGLE OPN TIE 2238 250082-249985(1) | -
|  |  | SINGLE OPN TIE 2239 250082-250050(1) | -
|  |  | SINGLE OPN TIE 2240 250082-250067(1) | -
|  |  | SINGLE OPN TIE 2241 250082-250096(1) | -
|  |  | SINGLE OPN TIE 2242 250082-250157(1) | -
|  |  | SINGLE OPN TIE 2243 250082-251428-251798(1) | -
|  |  | SINGLE OPN TIE 2244 250083-250013(1) | -
|  |  | SINGLE OPN TIE 2245 250083-250065(1) | -
|  |  | SINGLE OPN TIE 2246 250083-250160(1) | -
|  |  | SINGLE OPN TIE 2247 250083-251429(1) | -
251798 | 08PORTU6 | 34.5 | SINGLE OPN TIE 2248 250083-251798(1) | 29.482
252045 | 08PORTU2 | 12.47 | SINGLE OPN TIE 2249 250083-252045(5) | 29.183
|  |  | SINGLE OPN TIE 2250 250083-251428-252045(1) | -
|  |  | SINGLE OPN TIE 2251 250097-249988(1) | -
|  |  | SINGLE OPN TIE 2252 250097-250042(1) | -
|  |  | SINGLE OPN TIE 2253 250097-250052(1) | -
|  |  | SINGLE OPN TIE 2254 250097-250053(1) | -
|  |  | SINGLE OPN TIE 2255 250131-250032(1) | -
|  |  | SINGLE OPN TIE 2256 250131-250068(1) | -
|  |  | SINGLE OPN TIE 2257 250131-250155(1) | -
251826 | WILLEY 1 | 34.5 | SINGLE OPN TIE 2258 250131-251826(1) | 48.093
251827 | WILLYESP | 34.5 | SINGLE OPN TIE 2258 250131-251826(1) | 6.008
251832 | 08HLCRTG | 0.385 | SINGLE OPN TIE 2259 250136-250166(Z1) | 1.001
|  |  | SINGLE OPN TIE 2260 250141-250020(1) | -
|  |  | SINGLE OPN TIE 2261 250148-250043(1) | -
|  |  | SINGLE OPN TIE 2264 251279-251527(1) | -
|  |  | SINGLE OPN TIE 2265 251279-251543(1) | -
|  |  | SINGLE OPN TIE 2266 251310-251284(1) | -
251373 | 08LMBRG1 | 69 | SINGLE OPN TIE 2268 251368-251373(1) | 8.787
251374 | 08LMBRG2 | 69 | SINGLE OPN TIE 2268 251368-251373(1) | 6.784
251405 | 08MONSTE | 69 | SINGLE OPN TIE 2269 251405-251449(1) | 4.793
|  |  | SINGLE OPN TIE 2270 251468-251414(1) | -
|  |  | SINGLE OPN LIN 2272 360112-360450(1) | -
|  |  | SINGLE OPN LIN 2273 360145-360473(1) | -
|  |  | SINGLE OPN LIN 2274 360145-361771(1) | -
360333 | 5GLASGOW KY | 161 | SINGLE OPN LIN 2275 360333-361113(1) | 24.03
|  |  | SINGLE OPN LIN 2276 360334-360354(1) | -
|  |  | SINGLE OPN LIN 2277 360334-360448(1) | -
|  |  | SINGLE OPN LIN 2278 360334-361064(1) | -
|  |  | SINGLE OPN LIN 2279 360334-361788(1) | -
|  |  | SINGLE OPN LIN 2280 360338-361139(1) | -
|  |  | SINGLE OPN LIN 2281 360342-362499(1) | -
|  |  | SINGLE OPN LIN 2282 360354-361139(1) | -
|  |  | SINGLE OPN LIN 2283 360354-361265(1) | -
|  |  | SINGLE OPN LIN 2284 360354-361558(1) | -
|  |  | SINGLE OPN LIN 2285 360445-360450(1) | -
|  |  | SINGLE OPN LIN 2286 360448-360486(1) | -
|  |  | SINGLE OPN LIN 2287 360448-361618(1) | -
|  |  | SINGLE OPN LIN 2288 360448-361666(1) | -
|  |  | SINGLE OPN LIN 2289 360448-364620(1) | -
|  |  | SINGLE OPN LIN 2290 360448-364621(2) | -
|  |  | SINGLE OPN LIN 2291 360448-364622(3) | -
|  |  | SINGLE OPN LIN 2292 360450-361580(1) | -
|  |  | SINGLE OPN LIN 2293 360450-361618(1) | -
|  |  | SINGLE OPN LIN 2294 360454-361771(1) | -
360509 | 5W TOMPKINSV | 161 | SINGLE OPN LIN 2295 360509-361246(1) | 8.69
360509 | 5W TOMPKINSV | 161 | SINGLE OPN LIN 2296 361064-361246(1) | 8.69
361117 | 5TOMPKNSV PS | 161 | SINGLE OPN LIN 2296 361064-361246(1) | 23.58
|  |  | SINGLE OPN LIN 2297 361064-361666(1) | -
|  |  | SINGLE OPN LIN 2298 361113-361735(1) | -
|  |  | SINGLE OPN LIN 2299 361114-361735(1) | -
361117 | 5TOMPKNSV PS | 161 | SINGLE OPN LIN 2300 361117-361246(1) | 23.58
361266 | 5HARTSVLE TN | 161 | SINGLE OPN LIN 2301 361265-361266(1) | 4.93
|  |  | SINGLE OPN LIN 2302 361267-361558(1) | -
361559 | 5E SUMNER TN | 161 | SINGLE OPN LIN 2303 361558-361559(1) | 13.7
|  |  | SINGLE OPN LIN 2304 361579-361580(1) | -
361604 | 5E GLASGOW | 161 | SINGLE OPN LIN 2305 361603-361604(1) | 29.12
361619 | 5BYRDSTOWN | 161 | SINGLE OPN LIN 2306 361618-361619(1) | 11.11
361667 | 5BURKESVL KY | 161 | SINGLE OPN LIN 2307 361666-361667(1) | 14.07
|  |  | SINGLE OPN LIN 2308 362058-362059(1) | -
|  |  | SINGLE OPN LIN 2309 362058-362061(1) | -
363060 | 2MOSS TN | 69 | SINGLE OPN LIN 2310 362058-363060(1) | 6.39
|  |  | SINGLE OPN LIN 2311 362059-362060(1) | -
|  |  | SINGLE OPN LIN 2312 362060-362061(1) | -
|  |  | SINGLE OPN LIN 2313 362061-364614(1) | -
|  |  | SINGLE OPN LIN 2314 362061-364615(2) | -
|  |  | SINGLE OPN LIN 2315 362061-364616(3) | -
|  |  | SINGLE OPN TIE 2316 360112-361287(1) | -
|  |  | SINGLE OPN TIE 2319 360334-360607(1) | -
362059 | 2TOMPKINSVL | 69 | SINGLE OPN TIE 2320 360334-362060-362483(2) | 9.79
362060 | 2SUMMER SHAD | 69 | SINGLE OPN TIE 2320 360334-362060-362483(2) | 11.34
362061 | 2DALE HOLLOW | 69 | SINGLE OPN TIE 2320 360334-362060-362483(2) | 8.9
362483 | 1SUMMER SHAD | 13.2 | SINGLE OPN TIE 2320 360334-362060-362483(2) | 4.5
363060 | 2MOSS TN | 69 | SINGLE OPN TIE 2320 360334-362060-362483(2) | 6.39
361553 | 5N SCOTTSVLE | 161 | SINGLE OPN TIE 2321 360338-361553(1) | 18.74
|  |  | SINGLE OPN TIE 2322 360338-361621(1) | -
|  |  | SINGLE OPN TIE 2323 360342-361617(1) | -
|  |  | SINGLE OPN TIE 2324 360342-361731(1) | -
|  |  | SINGLE OPN TIE 2325 360352-360349(2) | -
360382 | 5HOEGANAES | 161 | SINGLE OPN TIE 2326 360352-360382(1) | 39.7
|  |  | SINGLE OPN TIE 2327 360352-360773(1) | -
|  |  | SINGLE OPN TIE 2328 360352-361128(1) | -
|  |  | SINGLE OPN TIE 2329 360352-361714(1) | -
|  |  | SINGLE OPN TIE 2330 360352-361827(1) | -
364121 | 1GALLATIN F1 | 24 | SINGLE OPN TIE 2331 360352-364121(1) | 15
364122 | 1GALLATIN F2 | 24 | SINGLE OPN TIE 2332 360352-364122(2) | 15
|  |  | SINGLE OPN TIE 2333 360352-364221-364222(T1) | -
|  |  | SINGLE OPN TIE 2334 360352-364223-364224(T2) | -
|  |  | SINGLE OPN TIE 2335 360445-361542(1) | -
|  |  | SINGLE OPN TIE 2337 360454-361330(1) | -
|  |  | SINGLE OPN TIE 2341 361113-360607(1) | -
|  |  | SINGLE OPN TIE 2342 361114-360332(1) | -
360335 | 5BRISTOW KY | 161 | SINGLE OPN TIE 2343 361114-360335(1) | 11.83
360684 | 5MAGNA KY | 161 | SINGLE OPN TIE 2343 361114-360335(1) | 11.83
|  |  | SINGLE OPN TIE 2344 361265-361827(1) | -
|  |  | SINGLE OPN TIE 2345 361267-360530(1) | -
|  |  | SINGLE OPN TIE 2348 361603-360607(1) | -
|  |  | SINGLE OPN LIN 2352 253006-253027(1) | -
|  |  | SINGLE OPN LIN 2353 253013-253014(1) | -
|  |  | SINGLE OPN LIN 2354 253013-253014(2) | -
|  |  | SINGLE OPN LIN 2355 253013-253094(1) | -
|  |  | SINGLE OPN LIN 2356 253013-253094(2) | -
|  |  | SINGLE OPN LIN 2357 253014-253027(1) | -
|  |  | SINGLE OPN LIN 2358 253026-253027(1) | -
|  |  | SINGLE OPN LIN 2359 253026-253027(2) | -
|  |  | SINGLE OPN LIN 2360 253027-253079(1) | -
|  |  | SINGLE OPN LIN 2361 253076-253077(1) | -
|  |  | SINGLE OPN LIN 2362 253077-253100(1) | -
|  |  | SINGLE OPN LIN 2363 253099-253100(1) | -
|  |  | SINGLE OPN LIN 2364 253099-253181(1) | -
|  |  | SINGLE OPN TIE 2366 253006-253005(1) | -
|  |  | SINGLE OPN TIE 2367 253006-253005(2) | -
|  |  | SINGLE OPN TIE 2368 253006-253047(1) | -
|  |  | SINGLE OPN TIE 2369 253014-253310(1) | -
|  |  | SINGLE OPN TIE 2370 253026-238623(1) | -
|  |  | SINGLE OPN TIE 2371 253026-253002(1) | -
|  |  | SINGLE OPN TIE 2372 253026-253040(1) | -
|  |  | SINGLE OPN TIE 2373 253026-253062(1) | -
|  |  | SINGLE OPN TIE 2374 253026-253083(1) | -
|  |  | SINGLE OPN TIE 2375 253026-253107(1) | -
|  |  | SINGLE OPN TIE 2376 253027-253248(1) | -
|  |  | SINGLE OPN TIE 2381 253077-253310(1) | -
253355 | AB1-169 CT1 | 25 | SINGLE OPN TIE 2382 253077-253352(1) | 9.6
253357 | AB1-169 CT2 | 25 | SINGLE OPN TIE 2382 253077-253352(1) | 9.6
|  |  | SINGLE OPN TIE 2385 253079-253078(1) | -
|  |  | SINGLE OPN TIE 2386 253079-253078(2) | -
|  |  | SINGLE OPN TIE 2387 253094-253043(1) | -
|  |  | SINGLE OPN TIE 2388 253094-253115(1) | -
253131 | 09COL ST | 69 | SINGLE OPN TIE 2389 253094-253131(1) | 31.894
|  |  | SINGLE OPN TIE 2390 253094-253237(1) | -
253325 | AC1-069 GEN | 0.357 | SINGLE OPN TIE 2391 253099-253322(1) | 0.119
253333 | AC1-068 GEN | 0.357 | SINGLE OPN TIE 2392 253099-253330(1) | 0.119
253338 | AC1-165 GEN | 0.357 | SINGLE OPN TIE 2393 253099-253335(1) | 0.119
253343 | AC1-166 GEN | 0.357 | SINGLE OPN TIE 2394 253099-253340(1) | 0.119
|  |  | SINGLE OPN TIE 2395 253100-245769(1) | -
|  |  | SINGLE OPN TIE 2396 253181-253201(1) | -
|  |  | SINGLE OPN LIN 2397 248005-248013(1) | -
|  |  | SINGLE OPN TIE 2398 248005-242528(1) | -
248026 | 06KYGER 1HP | 15.5 | SINGLE OPN TIE 2401 248005-248027-248026(1) | 9
248027 | 06KYGER 1LP | 15.5 | SINGLE OPN TIE 2401 248005-248027-248026(1) | 9
248028 | 06KYGER 2HP | 15.5 | SINGLE OPN TIE 2402 248005-248029-248028(1) | 9
248029 | 06KYGER 2LP | 15.5 | SINGLE OPN TIE 2402 248005-248029-248028(1) | 9
248030 | 06KYGER 3HP | 15.5 | SINGLE OPN TIE 2403 248005-248031-248030(1) | 9
248031 | 06KYGER 3LP | 15.5 | SINGLE OPN TIE 2403 248005-248031-248030(1) | 9
248032 | 06KYGER 4HP | 15.5 | SINGLE OPN TIE 2404 248005-248033-248032(1) | 9
248033 | 06KYGER 4LP | 15.5 | SINGLE OPN TIE 2404 248005-248033-248032(1) | 9
248034 | 06KYGER 5HP | 15.5 | SINGLE OPN TIE 2405 248005-248035-248034(1) | 9
248035 | 06KYGER 5LP | 15.5 | SINGLE OPN TIE 2405 248005-248035-248034(1) | 9
|  |  | SINGLE OPN TIE 2406 248009-248008(SR) | -
|  |  | SINGLE OPN TIE 2411 248013-248000(1) | -
|  |  | SINGLE OPN TIE 2412 248013-248000(2) | -
|  |  | SINGLE OPN TIE 2413 248013-248001(1) | -
|  |  | SINGLE OPN TIE 2416 248013-250086(17) | -
|  |  | SINGLE OPN TIE 2417 248013-250143(18) | -
|  |  | SINGLE OPN TIE 2418 249736-249754(1) | -