## N-1-1_Summary
EKPC Summary of study N-1-1 analysis results[TARA Ver 2201.2.0.0 64-bit - Sat Aug 13 07:58:26 2022]
Loadflow Case: C:\Users\03419\Desktop\2022 Gas Study\Alt 3A\2032S_gas_alt#3a_212mw.raw
Study Data File: C:\Users\03419\Desktop\2022 Gas Study\2022 series_sub_EKPC-LGEE.sub
Contingency File: C:\Users\03419\Desktop\2022 Gas Study\Option 3A N-1-1 con file.con (total 37 contingencies)/ First-Level Contingency File: C:\Users\03419\Desktop\2022 Gas Study\Option 3A N-1-1 con file.con (total 37 contingencies)
Monitor File: C:\Users\03419\Desktop\2022 Gas Study\2022 series_mon_EKPC-LGEE.mon
Exclude File: not provided
Solution Options (Pre/Post Contingency): Shunts[All Enabled/All Enabled] PAR[Adjusted/Fixed] XFMR Tap[Adjusted/Adjusted] Area Interchange [Disabled/Disabled]
First Level Scenario Index | First Level Scenario | First Level Case NotCnv? | First Level case AC Solve #Iterations
0 | Original Case |  | 16
1 | EKPC_P1-2_MAR-KU LEB138 |  | 5
2 | EKPC_P1-2_COOP-ELIHU161_SRT-A |  | 5
3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A |  | 5
4 | EKPC_P1-2_COOP-LAUREL161_SRT-A |  | 5
5 | EKPC_P1-2_COOP-DEN161_SRT-A |  | 5
6 | EKPC_P1-2_COOP 161 TIE_SRT-A |  | 5
7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A |  | 5
8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A |  | 5
9 | EKPC_P1-2_LIBJ-GAS161_SRT-A |  | 5
10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A |  | 5
11 | EKPC_P1-2_GRE-SUMSH161_SRT-A |  | 5
12 | EKPC_P1-2_BARR-SUMSH161_SRT-A |  | 5
13 | EKPC_P1-2_BULL-SUMSH161_SRT-A |  | 5
14 | EKPC_P1-2_SSHAD 161 TIE_SRT-A |  | 5
15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A |  | 5
16 | EKPC_P1-3_MAR 161/138_SRT-A |  | 5
17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A |  | 5
18 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A |  | 5
19 | EXT_324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1 _SRT-A |  | 5
20 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A |  | 5
21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A |  | 5
22 | EXT_324217 4BROWN PLANT 138 324219 4BROWN T1 138 1 _SRT-A |  | 5
23 | EXT_324217 4BROWN PLANT 138 324220 4BROWN T2 138 1 _SRT-A |  | 5
24 | EXT_324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1 _SRT-A |  | 5
25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A |  | 5
26 | EXT_B-138-111_SRT-A |  | 5
27 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A_27 |  | 5
28 | EXT_BB-1133_SRT-A |  | 5
29 | EXT_MERE SWS_SRT-A |  | 5
30 | EXT_B-138-115_SRT-A |  | 5
31 | EXT_B-138-120_SRT-A |  | 5
32 | EXT_B-138-121_SRT-A |  | 5
33 | EXT_324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1 _SRT-A |  | 5
34 | EXT_326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1 _SRT-A |  | 5
35 | EXT_B-69-18_SRT-A |  | 5
36 | EXT_B-69-19_SRT-A |  | 5
37 | EXT_BB-1066_SRT-A |  | 5

## N-1-1_Islands
EKPC New Islands Created by Outage/First-Level[TARA Ver 2201.2.0.0 64-bit - Sat Aug 13 07:58:26 2022]
Loadflow Case: C:\Users\03419\Desktop\2022 Gas Study\Alt 3A\2032S_gas_alt#3a_212mw.raw
Study Data File: C:\Users\03419\Desktop\2022 Gas Study\2022 series_sub_EKPC-LGEE.sub
Contingency File: C:\Users\03419\Desktop\2022 Gas Study\Option 3A N-1-1 con file.con (total 37 contingencies)/ First-Level Contingency File: C:\Users\03419\Desktop\2022 Gas Study\Option 3A N-1-1 con file.con (total 37 contingencies)
Monitor File: C:\Users\03419\Desktop\2022 Gas Study\2022 series_mon_EKPC-LGEE.mon
Exclude File: not provided
Solution Options (Pre/Post Contingency): Shunts[All Enabled/All Enabled] PAR[Adjusted/Fixed] XFMR Tap[Adjusted/Adjusted] Area Interchange [Disabled/Disabled]
First Level Scenario Index | First Level Scenario | Cont ID | Cont Name | Load_2ndOrigCaseMW | Load_2ndTopoCaseMW | Load_BaseTopoCaseMW | LoadIslandIncrease MW | Pgen_2ndOrigCaseMW | Pgen_2ndTopoCaseMW | Pgen_BaseTopoCaseMW | PgenIslandIncrease MW | Pmax_2ndOrigCaseMW | Pmax_2ndTopoCaseMW | Pmax_BaseTopoCaseMW | PmaxIslandIncrease MW
8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A | 9 | EKPC_P1-2_LIBJ-GAS161_SRT-A | 0 | 0 | 0 | 0 | 0 | 212 | 0 | 212 | 0 | 212 | 0 | 212
9 | EKPC_P1-2_LIBJ-GAS161_SRT-A | 8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A | 0 | 0 | 0 | 0 | 0 | 212 | 0 | 212 | 0 | 212 | 0 | 212
17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A | 21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A | 0 | 6.91 | 0 | 6.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A | 35 | EXT_B-69-18_SRT-A | 0 | 6.91 | 0 | 6.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A | 25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 0 | 61.86 | 0 | 61.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A | 30 | EXT_B-138-115_SRT-A | 0 | 61.86 | 0 | 61.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A | 17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A | 0 | 6.91 | 0 | 6.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A | 36 | EXT_B-69-19_SRT-A | 0 | 6.91 | 0 | 6.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 18 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A | 0 | 61.86 | 0 | 61.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 36 | EXT_B-69-19_SRT-A | 0 | 61.86 | 0 | 61.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | EXT_B-138-115_SRT-A | 18 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A | 0 | 61.86 | 0 | 61.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | EXT_B-138-115_SRT-A | 36 | EXT_B-69-19_SRT-A | 0 | 61.86 | 0 | 61.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
35 | EXT_B-69-18_SRT-A | 17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A | 0 | 6.91 | 0 | 6.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
35 | EXT_B-69-18_SRT-A | 36 | EXT_B-69-19_SRT-A | 0 | 6.91 | 0 | 6.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36 | EXT_B-69-19_SRT-A | 21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A | 0 | 6.91 | 0 | 6.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36 | EXT_B-69-19_SRT-A | 25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 0 | 61.86 | 0 | 61.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36 | EXT_B-69-19_SRT-A | 30 | EXT_B-138-115_SRT-A | 0 | 61.86 | 0 | 61.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36 | EXT_B-69-19_SRT-A | 35 | EXT_B-69-18_SRT-A | 0 | 6.91 | 0 | 6.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 0 | Base Case | 0 | 0 | 21.7 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 0 | Base Case | 0 | 0 | 49.72 | 49.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | EXT_BB-1133_SRT-A | 0 | Base Case | 0 | 0 | 6.91 | 6.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | EXT_BB-1066_SRT-A | 0 | Base Case | 0 | 0 | 13.58 | 13.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## BranchViol
EKPC N-1-1 AC Monitored Facility Loadings[TARA Ver 2201.2.0.0 64-bit - Sat Aug 13 07:58:26 2022]
Loadflow Case: C:\Users\03419\Desktop\2022 Gas Study\Alt 3A\2032S_gas_alt#3a_212mw.raw
Study Data File: C:\Users\03419\Desktop\2022 Gas Study\2022 series_sub_EKPC-LGEE.sub
Contingency File: C:\Users\03419\Desktop\2022 Gas Study\Option 3A N-1-1 con file.con (total 37 contingencies)/ First-Level Contingency File: C:\Users\03419\Desktop\2022 Gas Study\Option 3A N-1-1 con file.con (total 37 contingencies)
Monitor File: C:\Users\03419\Desktop\2022 Gas Study\2022 series_mon_EKPC-LGEE.mon (90.0% loading cutoff)
Exclude File: not provided
Solution Options (Pre/Post Contingency): Shunts[All Enabled/All Enabled] PAR[Adjusted/Fixed] XFMR Tap[Adjusted/Adjusted] Area Interchange [Disabled/Disabled]
First Level Scenario Index | First Level Scenario | Monitored Facility | Fr Bus | Fr Name | To Bus | To Name | CKT | kVs | Areas | Rate Base (MVA) | Rate Cont (MVA) | Cont Name | Cont ID | Base Flow (MVA) | Cont Flow (MVA) | Orig Case Cont AC %Loading | Final DC %Loading | Final AC %Loading | Severity Rank | Radial Index | Base MW Flow | Cont MW Flow | Base MVAR Flow | Cont MVAR Flow | Fr Base Volt | Fr Cont Volt | To Base Volt | To Cont Volt | Base dAngle [deg] | Cont dAngle [deg]
1 | EKPC_P1-2_MAR-KU LEB138 | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 10 | 161.8 | 265.9 | 110.38 | 172.86 | 173.8 | 1 | 0.95705 | 160.8 | 265.4 | -17.1 | -16.7 | 1 | 1 | 0.9968 | 0.9929 | 2.16 | 3.56
1 | EKPC_P1-2_MAR-KU LEB138 | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 15 | 161.8 | 174 | 95.51 | 112.46 | 113.75 | 2 | 0.90388 | 160.8 | 173.2 | -17.1 | -17.2 | 1 | 1 | 0.9968 | 0.9963 | 2.16 | 2.33
1 | EKPC_P1-2_MAR-KU LEB138 | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 3 | 161.8 | 170.5 | 100.11 | 110.35 | 111.44 | 3 | 0.90193 | 160.8 | 170.1 | -17.1 | -12.1 | 1 | 1 | 0.9968 | 0.9953 | 2.16 | 2.28
1 | EKPC_P1-2_MAR-KU LEB138 | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | Base Case | 0 | 161.8 | - | 96.55 | 107.83 | 109.29 | 0 | 0.89989 | 160.8 | - | -17.1 | - | 1 | - | 0.9968 | - | 2.16 | -
1 | EKPC_P1-2_MAR-KU LEB138 | 342769 5MARION CO 161 342775 5MARION IP T 161 1 | 342769 | 5MARION CO | 342775 | 5MARION IP T | 1 | 161 | 320 | 186 | 210 | EKPC_P1-2_LIBJ-GAS161_SRT-A | 9 | 119.5 | 222 | 62.41 | 107.14 | 105.71 | 1 | 0.9836 | 120.6 | 223.4 | 5.7 | -1.6 | 1.0106 | 1.0064 | 1.0075 | 1.0022 | 0.78 | 1.47
1 | EKPC_P1-2_MAR-KU LEB138 | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EXT_324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1 _SRT-A | 24 | 161.8 | 158.7 | 86.46 | 102.38 | 103.72 | 4 | 0.90004 | 160.8 | 157.8 | -17.1 | -17 | 1 | 1 | 0.9968 | 0.9969 | 2.16 | 2.12
1 | EKPC_P1-2_MAR-KU LEB138 | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EXT_B-138-115_SRT-A | 30 | 161.8 | 158.7 | 85.77 | 102.49 | 103.7 | 5 | 0.89992 | 160.8 | 157.8 | -17.1 | -16.8 | 1 | 1 | 0.9968 | 0.9968 | 2.16 | 2.12
1 | EKPC_P1-2_MAR-KU LEB138 | 341342 2CONTOWN T 69.0 341761 2LIBERTY J 69.0 1 | 341342 | 2CONTOWN T | 341761 | 2LIBERTY J | 1 | 69 | 320 | 53 | 63 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 7 | 34.8 | 64.7 | 85.11 | 101.42 | 102.63 | 1 | 0.9287 | -33.5 | -62.5 | 9.2 | 16 | 0.9965 | 0.9986 | 1.0003 | 1.0063 | 0.93 | 1.72
1 | EKPC_P1-2_MAR-KU LEB138 | 341342 2CONTOWN T 69.0 342067 2PHIL 69.0 1 | 341342 | 2CONTOWN T | 342067 | 2PHIL | 1 | 69 | 320 | 57 | 63 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 7 | 32.8 | 62.5 | 81.78 | 97.03 | 99.28 | 1 | 0.84848 | 31.2 | 60.3 | -9.6 | -16.3 | 0.9965 | 0.9986 | 0.9907 | 0.9864 | 1.89 | 3.61
1 | EKPC_P1-2_MAR-KU LEB138 | 341761 2LIBERTY J 69.0 341767 2LIBERTYKU T 69.0 1 | 341761 | 2LIBERTY J | 341767 | 2LIBERTYKU T | 1 | 69 | 320 | 53 | 66 | EKPC_P1-2_LIBJ-GAS161_SRT-A | 9 | 9.4 | 63.4 | 65.86 | 94.83 | 96 | 1 | 0.9268 | -7.7 | -58.3 | 5.3 | 21.6 | 1.0003 | 0.9816 | 0.9986 | 0.9795 | 0.27 | 1.99
1 | EKPC_P1-2_MAR-KU LEB138 | 342307 2STEPHENSBRG 69.0 342403 2UPTON T 69.0 1 | 342307 | 2STEPHENSBRG | 342403 | 2UPTON T | 1 | 69 | 320 | 35 | 39 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 25 | 13.3 | 36.6 | 85.66 | 92.15 | 93.75 | 1 | 0.67183 | 11.9 | 33.7 | -6 | -13.3 | 1.0001 | 0.9911 | 0.9957 | 0.9744 | 1.75 | 4.85
1 | EKPC_P1-2_MAR-KU LEB138 | 342769 5MARION CO 161 342775 5MARION IP T 161 1 | 342769 | 5MARION CO | 342775 | 5MARION IP T | 1 | 161 | 320 | 186 | 210 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 7 | 119.5 | 189.4 | 56.35 | 90.57 | 90.17 | 2 | 0.97835 | 120.6 | 191.3 | 5.7 | 1 | 1.0106 | 1.0101 | 1.0075 | 1.0062 | 0.78 | 1.25
2 | EKPC_P1-2_COOP-ELIHU161_SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 3 | 146.2 | 162.9 | 100.11 | 104.94 | 106.47 | 1 | 0.88962 | 146 | 162.3 | -8.5 | -14.5 | 1 | 1 | 0.9954 | 0.9961 | 1.95 | 2.18
2 | EKPC_P1-2_COOP-ELIHU161_SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | Base Case | 0 | 146.2 | - | 96.55 | 97.93 | 98.8 | 0 | 0.88449 | 146 | - | -8.5 | - | 1 | - | 0.9954 | - | 1.95 | -
2 | EKPC_P1-2_COOP-ELIHU161_SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 15 | 146.2 | 149.4 | 95.51 | 96.91 | 97.64 | 2 | 0.88497 | 146 | 149.2 | -8.5 | -8.3 | 1 | 1 | 0.9954 | 0.9952 | 1.95 | 1.99
2 | EKPC_P1-2_COOP-ELIHU161_SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A | 17 | 146.2 | 142.5 | 90.88 | 92.41 | 93.12 | 3 | 0.8866 | 146 | 142.2 | -8.5 | -8.3 | 1 | 1 | 0.9954 | 0.9955 | 1.95 | 1.9
2 | EKPC_P1-2_COOP-ELIHU161_SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A | 18 | 146.2 | 142.3 | 90.65 | 92.27 | 93.02 | 4 | 0.885 | 146 | 142.1 | -8.5 | -8.3 | 1 | 1 | 0.9954 | 0.9955 | 1.95 | 1.89
2 | EKPC_P1-2_COOP-ELIHU161_SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EXT_B-69-19_SRT-A | 36 | 146.2 | 142.2 | 90.58 | 92.21 | 92.95 | 5 | 0.8866 | 146 | 142 | -8.5 | -8.4 | 1 | 1 | 0.9954 | 0.9955 | 1.95 | 1.89
3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 10 | 153.2 | 175.3 | 110.38 | 113.72 | 114.6 | 1 | 0.89239 | 152.8 | 175 | -11.1 | -11.1 | 1 | 1 | 0.9957 | 0.9948 | 2.04 | 2.34
3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EKPC_P1-3_MAR 161/138_SRT-A | 16 | 153.2 | 170.5 | 105.73 | 110.44 | 111.43 | 2 | 0.90193 | 152.8 | 170.1 | -11.1 | -11.9 | 1 | 1 | 0.9957 | 0.9952 | 2.04 | 2.27
3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EKPC_P1-2_MAR-KU LEB138 | 1 | 153.2 | 170.5 | 105.72 | 110.43 | 111.42 | 3 | 0.90193 | 152.8 | 170.1 | -11.1 | -11.9 | 1 | 1 | 0.9957 | 0.9952 | 2.04 | 2.27
3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EXT_B-69-18_SRT-A | 35 | 153.2 | 163.7 | 101.35 | 106.43 | 106.98 | 4 | 0.90276 | 152.8 | 163.3 | -11.1 | -11.1 | 1 | 1 | 0.9957 | 0.9953 | 2.04 | 2.18
3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EKPC_P1-2_COOP-ELIHU161_SRT-A | 2 | 153.2 | 162.2 | 95.57 | 105.22 | 106.04 | 5 | 0.88962 | 152.8 | 162.1 | -11.1 | -7.4 | 1 | 1 | 0.9957 | 0.9945 | 2.04 | 2.16
3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | Base Case | 0 | 153.2 | - | 96.55 | 102.46 | 103.49 | 0 | 0.88281 | 152.8 | - | -11.1 | - | 1 | - | 0.9957 | - | 2.04 | -
3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 341342 2CONTOWN T 69.0 341761 2LIBERTY J 69.0 1 | 341342 | 2CONTOWN T | 341761 | 2LIBERTY J | 1 | 69 | 320 | 53 | 63 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 7 | 42.8 | 64.9 | 85.11 | 100.22 | 103.05 | 1 | 0.92823 | -40.7 | -62.6 | 12.6 | 16.6 | 0.9957 | 0.997 | 0.9996 | 1.0045 | 1.15 | 1.73
3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 341342 2CONTOWN T 69.0 342067 2PHIL 69.0 1 | 341342 | 2CONTOWN T | 342067 | 2PHIL | 1 | 69 | 320 | 57 | 63 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 7 | 40.7 | 62.8 | 81.78 | 95.41 | 99.71 | 1 | 0.8475 | 38.4 | 60.3 | -12.9 | -16.9 | 0.9957 | 0.997 | 0.9897 | 0.9854 | 2.37 | 3.64
3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 342703 5CASEY CO 161 342769 5MARION CO 161 1 | 342703 | 5CASEY CO | 342769 | 5MARION CO | 1 | 161 | 320 | 148 | 153 | EKPC_P1-2_LIBJ-GAS161_SRT-A | 9 | 40.2 | 148.8 | 101.09 | 93.72 | 97.24 | 1 | 0.91686 | 32.9 | 143.1 | -23.1 | -39.7 | 1.002 | 0.9979 | 1.0101 | 1.0055 | 1.12 | 4.57
3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 342000 5GAS 161 342703 5CASEY CO 161 1 | 342000 | 5GAS | 342703 | 5CASEY CO | 1 | 161 | 320 | 148 | 153 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 7 | 63.6 | 141.7 | 96.78 | 89.23 | 92.65 | 1 | 0.94782 | 59.2 | 137.5 | -23.3 | -34.3 | 1 | 1 | 1.002 | 1.0013 | 0.68 | 1.54
4 | EKPC_P1-2_COOP-LAUREL161_SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 10 | 137.3 | 163.4 | 110.38 | 105.18 | 106.78 | 1 | 0.89182 | 135.7 | 161.9 | -20.6 | -22.1 | 1 | 1 | 0.9986 | 0.9979 | 1.84 | 2.19
4 | EKPC_P1-2_COOP-LAUREL161_SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EKPC_P1-3_MAR 161/138_SRT-A | 16 | 137.3 | 158 | 105.73 | 101.61 | 103.27 | 2 | 0.90025 | 135.7 | 156.4 | -20.6 | -22.2 | 1 | 1 | 0.9986 | 0.9981 | 1.84 | 2.12
4 | EKPC_P1-2_COOP-LAUREL161_SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EKPC_P1-2_MAR-KU LEB138 | 1 | 137.3 | 158 | 105.72 | 101.61 | 103.27 | 3 | 0.90025 | 135.7 | 156.4 | -20.6 | -22.2 | 1 | 1 | 0.9986 | 0.9981 | 1.84 | 2.12
4 | EKPC_P1-2_COOP-LAUREL161_SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EXT_B-69-18_SRT-A | 35 | 137.3 | 151.6 | 101.35 | 97.82 | 99.05 | 4 | 0.90103 | 135.7 | 150 | -20.6 | -21.5 | 1 | 1 | 0.9986 | 0.9982 | 1.84 | 2.03
4 | EKPC_P1-2_COOP-LAUREL161_SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 3 | 137.3 | 146.7 | 100.11 | 94.51 | 95.88 | 5 | 0.88399 | 135.7 | 145.7 | -20.6 | -17.1 | 1 | 1 | 0.9986 | 0.9974 | 1.84 | 1.96
4 | EKPC_P1-2_COOP-LAUREL161_SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | Base Case | 0 | 137.3 | - | 96.55 | 91.1 | 92.76 | 0 | 0.88122 | 135.7 | - | -20.6 | - | 1 | - | 0.9986 | - | 1.84 | -
6 | EKPC_P1-2_COOP 161 TIE_SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 10 | 133.4 | 158.1 | 110.38 | 102.49 | 103.35 | 1 | 0.89792 | 132.9 | 157.7 | -11.2 | -12.2 | 1 | 1 | 0.9965 | 0.9958 | 1.78 | 2.11
6 | EKPC_P1-2_COOP 161 TIE_SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EKPC_P1-3_MAR 161/138_SRT-A | 16 | 133.4 | 153.1 | 105.73 | 99.15 | 100.04 | 2 | 0.90402 | 132.9 | 152.6 | -11.2 | -12.3 | 1 | 1 | 0.9965 | 0.996 | 1.78 | 2.04
6 | EKPC_P1-2_COOP 161 TIE_SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EKPC_P1-2_MAR-KU LEB138 | 1 | 133.4 | 153 | 105.72 | 99.14 | 100.03 | 3 | 0.90402 | 132.9 | 152.6 | -11.2 | -12.3 | 1 | 1 | 0.9965 | 0.996 | 1.78 | 2.04
6 | EKPC_P1-2_COOP 161 TIE_SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 3 | 133.4 | 148.5 | 100.11 | 96.36 | 97.07 | 4 | 0.89835 | 132.9 | 148.5 | -11.2 | 0.7 | 1 | 1 | 0.9965 | 0.9932 | 1.78 | 1.96
6 | EKPC_P1-2_COOP 161 TIE_SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EXT_B-69-18_SRT-A | 35 | 133.4 | 147.4 | 101.35 | 95.78 | 96.31 | 5 | 0.90464 | 132.9 | 146.9 | -11.2 | -11.9 | 1 | 1 | 0.9965 | 0.9961 | 1.78 | 1.97
6 | EKPC_P1-2_COOP 161 TIE_SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | Base Case | 0 | 133.4 | - | 96.55 | 89.25 | 90.15 | 0 | 0.88823 | 132.9 | - | -11.2 | - | 1 | - | 0.9965 | - | 1.78 | -
7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 342760 5LIBERTY J 161 341761 2LIBERTY J 69.0 1 | 342760 | 5LIBERTY J | 341761 | 2LIBERTY J | 1 | 161/69 | 320 | 89 | 109 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A | 8 | 68.3 | 213.6 | 57.92 | 194.06 | 195.92 | 1 | 1 | 67.7 | 209.8 | -4.7 | 9 | 0.9978 | 0.9867 | 1.0048 | 1.0034 | 4.98 | 15.78
7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 341342 2CONTOWN T 69.0 341761 2LIBERTY J 69.0 1 | 341342 | 2CONTOWN T | 341761 | 2LIBERTY J | 1 | 69 | 320 | 53 | 63 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A | 8 | 53.6 | 120.2 | 54.05 | 188.7 | 190.78 | 1 | 0.95607 | -51.7 | -115.9 | 13.7 | 24.9 | 0.9987 | 0.9863 | 1.0048 | 1.0034 | 1.43 | 3.17
7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 341342 2CONTOWN T 69.0 342067 2PHIL 69.0 1 | 341342 | 2CONTOWN T | 342067 | 2PHIL | 1 | 69 | 320 | 57 | 63 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A | 8 | 51.5 | 118 | 50.76 | 183.11 | 187.37 | 1 | 0.90665 | 49.5 | 113.6 | -14.1 | -25.4 | 0.9987 | 0.9863 | 0.9891 | 0.9615 | 2.97 | 6.93
7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 342067 2PHIL 69.0 342505 2WINDSOR 69.0 1 | 342067 | 2PHIL | 342505 | 2WINDSOR | 1 | 69 | 320 | 53 | 63 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A | 8 | 41.4 | 107.5 | 35.5 | 163.1 | 170.6 | 1 | 0.88491 | 36.6 | 95.3 | -18.3 | -39.9 | 0.9891 | 0.9615 | 0.9886 | 0.9573 | 3.03 | 8.11
7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 341515 2GARRARD CO 69.0 942410 AE2-254 TAP 69.0 1 | 341515 | 2GARRARD CO | 942410 | AE2-254 TAP | 1 | 69 | 320 | 57 | 63 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A | 8 | 45.8 | 85.8 | 56.94 | 143.52 | 136.17 | 1 | 0.96959 | -41 | -79.4 | 21.7 | 34.5 | 1.0126 | 1.0094 | 1.0131 | 1.0128 | 0.87 | 1.62
7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 341761 2LIBERTY J 69.0 341896 2MT OLIVE J 69.0 1 | 341761 | 2LIBERTY J | 341896 | 2MT OLIVE J | 1 | 69 | 320 | 53 | 63 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A | 8 | 22.2 | 72.7 | 18.6 | 112.28 | 115.46 | 1 | 0.94235 | 21.8 | 70.3 | -4.7 | -19.5 | 1.0048 | 1.0034 | 1.0011 | 0.9946 | 0.77 | 2.57
7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 341617 2HIGHLAND EK 69.0 341896 2MT OLIVE J 69.0 1 | 341617 | 2HIGHLAND EK | 341896 | 2MT OLIVE J | 1 | 69 | 320 | 57 | 63 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A | 8 | 17.9 | 68.5 | 11.64 | 104.9 | 108.79 | 1 | 0.81741 | -16.7 | -59.7 | 6 | 31.3 | 0.9956 | 0.9846 | 1.0011 | 0.9946 | 2.02 | 7.9
7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 341342 2CONTOWN T 69.0 341761 2LIBERTY J 69.0 1 | 341342 | 2CONTOWN T | 341761 | 2LIBERTY J | 1 | 69 | 320 | 53 | 63 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 10 | 53.6 | 67 | 59.9 | 104.02 | 106.32 | 2 | 0.92845 | -51.7 | -64.7 | 13.7 | 16.4 | 0.9987 | 0.9975 | 1.0048 | 1.0056 | 1.43 | 1.78
7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 342703 5CASEY CO 161 342769 5MARION CO 161 1 | 342703 | 5CASEY CO | 342769 | 5MARION CO | 1 | 161 | 320 | 148 | 153 | EKPC_P1-2_LIBJ-GAS161_SRT-A | 9 | 123.1 | 158.3 | 101.09 | 99.87 | 103.49 | 1 | 0.9286 | 117.9 | 153.1 | -35.7 | -39.3 | 1.001 | 0.9981 | 1.0083 | 1.0049 | 3.76 | 4.87
7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 341342 2CONTOWN T 69.0 341761 2LIBERTY J 69.0 1 | 341342 | 2CONTOWN T | 341761 | 2LIBERTY J | 1 | 69 | 320 | 53 | 63 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 3 | 53.6 | 64.9 | 67.88 | 99.18 | 103 | 3 | 0.92823 | -51.7 | -62.3 | 13.7 | 18 | 0.9987 | 0.9991 | 1.0048 | 1.0059 | 1.43 | 1.73
7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 341342 2CONTOWN T 69.0 342067 2PHIL 69.0 1 | 341342 | 2CONTOWN T | 342067 | 2PHIL | 1 | 69 | 320 | 57 | 63 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 10 | 51.5 | 64.9 | 56.56 | 98.43 | 102.96 | 2 | 0.84796 | 49.5 | 62.5 | -14.1 | -16.8 | 0.9987 | 0.9975 | 0.9891 | 0.9849 | 2.97 | 3.75
7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 341342 2CONTOWN T 69.0 341761 2LIBERTY J 69.0 1 | 341342 | 2CONTOWN T | 341761 | 2LIBERTY J | 1 | 69 | 320 | 53 | 63 | EKPC_P1-3_MAR 161/138_SRT-A | 16 | 53.6 | 64.7 | 55.31 | 100.08 | 102.63 | 4 | 0.9287 | -51.7 | -62.5 | 13.7 | 16 | 0.9987 | 0.9986 | 1.0048 | 1.0063 | 1.43 | 1.72
7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 341342 2CONTOWN T 69.0 341761 2LIBERTY J 69.0 1 | 341342 | 2CONTOWN T | 341761 | 2LIBERTY J | 1 | 69 | 320 | 53 | 63 | EKPC_P1-2_MAR-KU LEB138 | 1 | 53.6 | 64.7 | 55.31 | 100.07 | 102.63 | 5 | 0.9287 | -51.7 | -62.5 | 13.7 | 16 | 0.9987 | 0.9986 | 1.0048 | 1.0063 | 1.43 | 1.72
7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 341209 2BROUGTWN T 69.0 341617 2HIGHLAND EK 69.0 1 | 341209 | 2BROUGTWN T | 341617 | 2HIGHLAND EK | 1 | 69 | 320 | 57 | 63 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A | 8 | 13 | 63.8 | 5.95 | 94.85 | 101.31 | 1 | 0.93812 | -10.7 | -52.2 | 7.3 | 35.1 | 0.9964 | 0.9871 | 0.9956 | 0.9846 | 0.51 | 2.53
7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 341342 2CONTOWN T 69.0 341761 2LIBERTY J 69.0 1 | 341342 | 2CONTOWN T | 341761 | 2LIBERTY J | 1 | 69 | 320 | 53 | 63 | Base Case | 0 | 53.6 | - | 61.71 | 97.63 | 101.17 | 0 | 0.92534 | -51.7 | - | 13.7 | - | 0.9987 | - | 1.0048 | - | 1.43 | -
7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 324191 2LEBANON E T 69.0 324603 2LEBANON CIT 69.0 1 | 324191 | 2LEBANON E T | 324603 | 2LEBANON CIT | 1 | 69 | 363 | 52 | 66 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 10 | 36.9 | 66.1 | 88.42 | 100.05 | 100.13 | 1 | 0.97633 | 36.7 | 66.3 | -6 | -5.9 | 1.0081 | 1.007 | 1.0063 | 1.0032 | 0.33 | 0.58
7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 342000 5GAS 161 342703 5CASEY CO 161 1 | 342000 | 5GAS | 342703 | 5CASEY CO | 1 | 161 | 320 | 148 | 153 | Base Case | 0 | 148.1 | - | 50.23 | 97.38 | 100.05 | 0 | 0.94748 | 144.1 | - | -34 | - | 1 | - | 1.001 | - | 1.61 | -
7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 341342 2CONTOWN T 69.0 342067 2PHIL 69.0 1 | 341342 | 2CONTOWN T | 342067 | 2PHIL | 1 | 69 | 320 | 57 | 63 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 3 | 51.5 | 62.8 | 64.6 | 93.59 | 99.69 | 3 | 0.8475 | 49.5 | 60 | -14.1 | -18.4 | 0.9987 | 0.9991 | 0.9891 | 0.989 | 2.97 | 3.64
7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 341342 2CONTOWN T 69.0 342067 2PHIL 69.0 1 | 341342 | 2CONTOWN T | 342067 | 2PHIL | 1 | 69 | 320 | 57 | 63 | EKPC_P1-3_MAR 161/138_SRT-A | 16 | 51.5 | 62.5 | 51.99 | 94.49 | 99.28 | 4 | 0.84848 | 49.5 | 60.3 | -14.1 | -16.3 | 0.9987 | 0.9986 | 0.9891 | 0.9864 | 2.97 | 3.61
7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 341342 2CONTOWN T 69.0 342067 2PHIL 69.0 1 | 341342 | 2CONTOWN T | 342067 | 2PHIL | 1 | 69 | 320 | 57 | 63 | EKPC_P1-2_MAR-KU LEB138 | 1 | 51.5 | 62.5 | 51.99 | 94.48 | 99.28 | 5 | 0.84848 | 49.5 | 60.3 | -14.1 | -16.3 | 0.9987 | 0.9986 | 0.9891 | 0.9864 | 2.97 | 3.61
7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 342000 5GAS 161 342703 5CASEY CO 161 1 | 342000 | 5GAS | 342703 | 5CASEY CO | 1 | 161 | 320 | 148 | 153 | EXT_B-138-115_SRT-A | 30 | 148.1 | 151.3 | 55.92 | 96.66 | 98.86 | 1 | 0.94755 | 144.1 | 148 | -34 | -31.3 | 1 | 1 | 1.001 | 1.0004 | 1.61 | 1.64
7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 341209 2BROUGTWN T 69.0 342367 2TOMM GOOC T 69.0 1 | 341209 | 2BROUGTWN T | 342367 | 2TOMM GOOC T | 1 | 69 | 320 | 57 | 63 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A | 8 | 10.6 | 60.8 | 9.73 | 87.71 | 96.53 | 1 | 0.95716 | 6.2 | 47.7 | -8.6 | -36.4 | 0.9964 | 0.9871 | 0.9985 | 0.9915 | 0.26 | 1.65
7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 342000 5GAS 161 342703 5CASEY CO 161 1 | 342000 | 5GAS | 342703 | 5CASEY CO | 1 | 161 | 320 | 148 | 153 | EXT_B-138-111_SRT-A | 26 | 148.1 | 145 | 48.59 | 94.2 | 94.77 | 2 | 0.94855 | 144.1 | 141.4 | -34 | -32.2 | 1 | 1 | 1.001 | 1.0008 | 1.61 | 1.58
7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 342000 5GAS 161 342703 5CASEY CO 161 1 | 342000 | 5GAS | 342703 | 5CASEY CO | 1 | 161 | 320 | 148 | 153 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 3 | 148.1 | 142 | 41.59 | 90.19 | 92.8 | 3 | 0.94782 | 144.1 | 137.6 | -34 | -35 | 1 | 1 | 1.001 | 1.0014 | 1.61 | 1.54
7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 342769 5MARION CO 161 342775 5MARION IP T 161 1 | 342769 | 5MARION CO | 342775 | 5MARION IP T | 1 | 161 | 320 | 186 | 210 | EXT_B-69-18_SRT-A | 35 | 118.3 | 192.8 | 60.69 | 91.78 | 91.8 | 1 | 0.97852 | 119.3 | 194.4 | 2.5 | 8.6 | 1.0083 | 1.0098 | 1.0056 | 1.0049 | 0.78 | 1.26
7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 324603 2LEBANON CIT 69.0 324605 2LEBANON EK 69.0 1 | 324603 | 2LEBANON CIT | 324605 | 2LEBANON EK | 1 | 69 | 363 | 52 | 66 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 10 | 31.2 | 60 | 79.94 | 90.45 | 90.96 | 1 | 0.99152 | 30.4 | 59.8 | 7.8 | 7.4 | 1.0063 | 1.0032 | 1.0051 | 1.0012 | 0.08 | 0.17
7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 341342 2CONTOWN T 69.0 342067 2PHIL 69.0 1 | 341342 | 2CONTOWN T | 342067 | 2PHIL | 1 | 69 | 320 | 57 | 63 | Base Case | 0 | 51.5 | - | 53.72 | 84.6 | 90.39 | 0 | 0.84134 | 49.5 | - | -14.1 | - | 0.9987 | - | 0.9891 | - | 2.97 | -
7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 342769 5MARION CO 161 342775 5MARION IP T 161 1 | 342769 | 5MARION CO | 342775 | 5MARION IP T | 1 | 161 | 320 | 186 | 210 | EKPC_P1-3_MAR 161/138_SRT-A | 16 | 118.3 | 189.4 | 56.89 | 90.31 | 90.17 | 2 | 0.97835 | 119.3 | 191.3 | 2.5 | 1 | 1.0083 | 1.0101 | 1.0056 | 1.0062 | 0.78 | 1.25
7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 342769 5MARION CO 161 342775 5MARION IP T 161 1 | 342769 | 5MARION CO | 342775 | 5MARION IP T | 1 | 161 | 320 | 186 | 210 | EKPC_P1-2_MAR-KU LEB138 | 1 | 118.3 | 189.3 | 56.88 | 90.29 | 90.17 | 3 | 0.97835 | 119.3 | 191.3 | 2.5 | 1 | 1.0083 | 1.0101 | 1.0056 | 1.0062 | 0.78 | 1.25
8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A | 342760 5LIBERTY J 161 341761 2LIBERTY J 69.0 1 | 342760 | 5LIBERTY J | 341761 | 2LIBERTY J | 1 | 161/69 | 320 | 89 | 109 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 7 | 63.1 | 213.4 | 62.63 | 192.9 | 195.77 | 1 | 1 | 63 | 209.8 | -1.5 | 9.7 | 0.9945 | 0.9865 | 0.9972 | 1.0024 | 4.68 | 15.8
8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A | 341342 2CONTOWN T 69.0 341761 2LIBERTY J 69.0 1 | 341342 | 2CONTOWN T | 341761 | 2LIBERTY J | 1 | 69 | 320 | 53 | 63 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 7 | 34.1 | 120.2 | 85.11 | 190.06 | 190.77 | 1 | 0.95607 | -32.4 | -115.9 | 9.6 | 24 | 0.9939 | 0.9848 | 0.9972 | 1.0024 | 0.92 | 3.16
8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A | 341342 2CONTOWN T 69.0 342067 2PHIL 69.0 1 | 341342 | 2CONTOWN T | 342067 | 2PHIL | 1 | 69 | 320 | 57 | 63 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 7 | 32 | 118 | 81.78 | 185.71 | 187.27 | 1 | 0.90665 | 30.2 | 113.6 | -10 | -24.5 | 0.9939 | 0.9848 | 0.9889 | 0.9592 | 1.86 | 6.93
8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A | 342067 2PHIL 69.0 342505 2WINDSOR 69.0 1 | 342067 | 2PHIL | 342505 | 2WINDSOR | 1 | 69 | 320 | 53 | 63 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 7 | 22.4 | 107.3 | 65.71 | 166.85 | 170.33 | 1 | 0.88491 | 18.1 | 95.2 | -12.7 | -39 | 0.9889 | 0.9592 | 0.9924 | 0.9541 | 1.62 | 8.11
8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | Base Case | 0 | 212.6 | - | 96.55 | 141.78 | 143.63 | 0 | 1 | 212 | - | -15.6 | - | 1 | - | 0.9945 | - | 2.84 | -
8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A | 341515 2GARRARD CO 69.0 942410 AE2-254 TAP 69.0 1 | 341515 | 2GARRARD CO | 942410 | AE2-254 TAP | 1 | 69 | 320 | 57 | 63 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 7 | 35.9 | 85.9 | 72.73 | 145.47 | 136.38 | 1 | 0.96959 | -31.2 | -79.6 | 18.5 | 34.3 | 1.0134 | 1.0093 | 1.0132 | 1.0128 | 0.68 | 1.63
8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A | 341761 2LIBERTY J 69.0 341896 2MT OLIVE J 69.0 1 | 341761 | 2LIBERTY J | 341896 | 2MT OLIVE J | 1 | 69 | 320 | 53 | 63 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 7 | 11.7 | 72.8 | 35.2 | 113.85 | 115.58 | 1 | 0.94235 | 11.6 | 70.3 | -1.7 | -19.8 | 0.9972 | 1.0024 | 0.9947 | 0.9938 | 0.4 | 2.58
8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A | 341617 2HIGHLAND EK 69.0 341896 2MT OLIVE J 69.0 1 | 341617 | 2HIGHLAND EK | 341896 | 2MT OLIVE J | 1 | 69 | 320 | 57 | 63 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 7 | 7.3 | 68.6 | 28.39 | 106.48 | 108.91 | 1 | 0.81741 | -6.8 | -59.6 | 2.2 | 31.5 | 0.9924 | 0.9842 | 0.9947 | 0.9938 | 0.83 | 7.91
8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A | 341209 2BROUGTWN T 69.0 341617 2HIGHLAND EK 69.0 1 | 341209 | 2BROUGTWN T | 341617 | 2HIGHLAND EK | 1 | 69 | 320 | 57 | 63 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 7 | 3.7 | 63.9 | 20.69 | 96.9 | 101.45 | 1 | 0.93812 | -0.9 | -52.2 | 3.5 | 35.3 | 0.9942 | 0.9869 | 0.9924 | 0.9842 | 0.1 | 2.54
8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A | 341209 2BROUGTWN T 69.0 342367 2TOMM GOOC T 69.0 1 | 341209 | 2BROUGTWN T | 342367 | 2TOMM GOOC T | 1 | 69 | 320 | 57 | 63 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 7 | 6 | 60.9 | 16.82 | 89.79 | 96.69 | 1 | 0.95716 | -3.6 | 47.7 | -4.8 | -36.6 | 0.9942 | 0.9869 | 0.997 | 0.9913 | 0.02 | 1.65
8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A | 342307 2STEPHENSBRG 69.0 342403 2UPTON T 69.0 1 | 342307 | 2STEPHENSBRG | 342403 | 2UPTON T | 1 | 69 | 320 | 35 | 39 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 25 | 13.1 | 35.5 | 85.66 | 88.65 | 90.99 | 1 | 0.67019 | 11.4 | 32.1 | -6.5 | -14.6 | 1.0014 | 0.9934 | 0.9987 | 0.9812 | 1.73 | 4.73
9 | EKPC_P1-2_LIBJ-GAS161_SRT-A | 342000 5GAS 161 342703 5CASEY CO 161 1 | 342000 | 5GAS | 342703 | 5CASEY CO | 1 | 161 | 320 | 148 | 153 | Base Case | 0 | 214.2 | - | 50.23 | 143.24 | 144.7 | 0 | 1 | 212 | - | -30.3 | - | 1 | - | 0.9981 | - | 2.33 | -
9 | EKPC_P1-2_LIBJ-GAS161_SRT-A | 342769 5MARION CO 161 342775 5MARION IP T 161 1 | 342769 | 5MARION CO | 342775 | 5MARION IP T | 1 | 161 | 320 | 186 | 210 | EXT_B-69-18_SRT-A | 35 | 131.1 | 225.1 | 60.69 | 106.78 | 107.21 | 1 | 0.98369 | 131.7 | 225.7 | -0.9 | 4 | 1.0051 | 1.0025 | 1.0025 | 0.9976 | 0.87 | 1.49
9 | EKPC_P1-2_LIBJ-GAS161_SRT-A | 324191 2LEBANON E T 69.0 324603 2LEBANON CIT 69.0 1 | 324191 | 2LEBANON E T | 324603 | 2LEBANON CIT | 1 | 69 | 363 | 52 | 66 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 10 | 37.8 | 70.3 | 88.42 | 106.69 | 106.53 | 1 | 0.97649 | 37.5 | 70.3 | -6.3 | -7.3 | 1.007 | 1.0054 | 1.0052 | 1.0015 | 0.34 | 0.62
9 | EKPC_P1-2_LIBJ-GAS161_SRT-A | 342769 5MARION CO 161 342775 5MARION IP T 161 1 | 342769 | 5MARION CO | 342775 | 5MARION IP T | 1 | 161 | 320 | 186 | 210 | EKPC_P1-3_MAR 161/138_SRT-A | 16 | 131.1 | 222.1 | 56.89 | 105.75 | 105.74 | 2 | 0.9836 | 131.7 | 223.5 | -0.9 | -1.3 | 1.0051 | 1.0065 | 1.0025 | 1.0023 | 0.87 | 1.47
9 | EKPC_P1-2_LIBJ-GAS161_SRT-A | 342769 5MARION CO 161 342775 5MARION IP T 161 1 | 342769 | 5MARION CO | 342775 | 5MARION IP T | 1 | 161 | 320 | 186 | 210 | EKPC_P1-2_MAR-KU LEB138 | 1 | 131.1 | 222 | 56.88 | 105.72 | 105.74 | 3 | 0.9836 | 131.7 | 223.5 | -0.9 | -1.3 | 1.0051 | 1.0065 | 1.0025 | 1.0023 | 0.87 | 1.47
9 | EKPC_P1-2_LIBJ-GAS161_SRT-A | 342703 5CASEY CO 161 342769 5MARION CO 161 1 | 342703 | 5CASEY CO | 342769 | 5MARION CO | 1 | 161 | 320 | 148 | 153 | Base Case | 0 | 154.7 | - | 35.52 | 99.09 | 104.51 | 0 | 0.91612 | 149.3 | - | -39.2 | - | 0.9981 | - | 1.0051 | - | 4.76 | -
9 | EKPC_P1-2_LIBJ-GAS161_SRT-A | 342703 5CASEY CO 161 342769 5MARION CO 161 1 | 342703 | 5CASEY CO | 342769 | 5MARION CO | 1 | 161 | 320 | 148 | 153 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 7 | 154.7 | 158.3 | 80.44 | 97.94 | 103.49 | 1 | 0.9286 | 149.3 | 153.1 | -39.2 | -39.3 | 0.9981 | 0.9981 | 1.0051 | 1.0048 | 4.76 | 4.87
9 | EKPC_P1-2_LIBJ-GAS161_SRT-A | 342703 5CASEY CO 161 342769 5MARION CO 161 1 | 342703 | 5CASEY CO | 342769 | 5MARION CO | 1 | 161 | 320 | 148 | 153 | EXT_B-138-115_SRT-A | 30 | 154.7 | 158.2 | 42.32 | 98.51 | 103.39 | 2 | 0.91634 | 149.3 | 153.5 | -39.2 | -36.6 | 0.9981 | 0.9977 | 1.0051 | 1.003 | 4.76 | 4.88
9 | EKPC_P1-2_LIBJ-GAS161_SRT-A | 324271 4LEBANON 138 342770 4MARION CO 138 1 | 324271 | 4LEBANON | 342770 | 4MARION CO | 1 | 138 | 363/320 | 187 | 220 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 10 | 110.4 | 225 | 50.7 | 102.37 | 102.28 | 1 | 0.99955 | -110.9 | -226 | 6.2 | 15 | 1.0059 | 1.0066 | 1.006 | 1.0068 | 0.02 | 0.04
9 | EKPC_P1-2_LIBJ-GAS161_SRT-A | 342703 5CASEY CO 161 342769 5MARION CO 161 1 | 342703 | 5CASEY CO | 342769 | 5MARION CO | 1 | 161 | 320 | 148 | 153 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A | 20 | 154.7 | 151.5 | 36.67 | 95.86 | 99.05 | 3 | 0.91929 | 149.3 | 146.6 | -39.2 | -37 | 0.9981 | 0.9977 | 1.0051 | 1.0037 | 4.76 | 4.67
9 | EKPC_P1-2_LIBJ-GAS161_SRT-A | 342703 5CASEY CO 161 342769 5MARION CO 161 1 | 342703 | 5CASEY CO | 342769 | 5MARION CO | 1 | 161 | 320 | 148 | 153 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A_Dup1 | 27 | 154.7 | 151.5 | 36.67 | 95.86 | 99.05 | 4 | 0.91929 | 149.3 | 146.6 | -39.2 | -37 | 0.9981 | 0.9977 | 1.0051 | 1.0037 | 4.76 | 4.67
9 | EKPC_P1-2_LIBJ-GAS161_SRT-A | 342703 5CASEY CO 161 342769 5MARION CO 161 1 | 342703 | 5CASEY CO | 342769 | 5MARION CO | 1 | 161 | 320 | 148 | 153 | EXT_B-138-111_SRT-A | 26 | 154.7 | 150.8 | 34.36 | 93.69 | 98.59 | 5 | 0.91932 | 149.3 | 145.9 | -39.2 | -37 | 0.9981 | 0.9977 | 1.0051 | 1.0037 | 4.76 | 4.65
9 | EKPC_P1-2_LIBJ-GAS161_SRT-A | 324603 2LEBANON CIT 69.0 324605 2LEBANON EK 69.0 1 | 324603 | 2LEBANON CIT | 324605 | 2LEBANON EK | 1 | 69 | 363 | 52 | 66 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 10 | 31.9 | 63.9 | 79.94 | 97.08 | 96.83 | 1 | 0.99157 | 31.2 | 63.7 | 7.5 | 5.8 | 1.0052 | 1.0015 | 1.004 | 0.9995 | 0.08 | 0.18
9 | EKPC_P1-2_LIBJ-GAS161_SRT-A | 342769 5MARION CO 161 342770 4MARION CO 138 1 | 342769 | 5MARION CO | 342770 | 4MARION CO | 1 | 161/138 | 320 | 192 | 234 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 10 | 111.1 | 226.5 | 48.17 | 96.28 | 96.81 | 1 | 0.95642 | 110.9 | 226.2 | -2.6 | -0.2 | 1.0051 | 1.0053 | 1.006 | 1.0068 | 1.83 | 3.73
9 | EKPC_P1-2_LIBJ-GAS161_SRT-A | 341761 2LIBERTY J 69.0 341767 2LIBERTYKU T 69.0 1 | 341761 | 2LIBERTY J | 341767 | 2LIBERTYKU T | 1 | 69 | 320 | 53 | 66 | EKPC_P1-3_MAR 161/138_SRT-A | 16 | 43.5 | 63.4 | 14.31 | 91.96 | 96.02 | 1 | 0.9268 | -40.5 | -58.3 | 14 | 21.6 | 0.9859 | 0.9816 | 0.9848 | 0.9794 | 1.36 | 1.99
9 | EKPC_P1-2_LIBJ-GAS161_SRT-A | 341761 2LIBERTY J 69.0 341767 2LIBERTYKU T 69.0 1 | 341761 | 2LIBERTY J | 341767 | 2LIBERTYKU T | 1 | 69 | 320 | 53 | 66 | EKPC_P1-2_MAR-KU LEB138 | 1 | 43.5 | 63.4 | 14.31 | 91.94 | 96.02 | 2 | 0.9268 | -40.5 | -58.3 | 14 | 21.6 | 0.9859 | 0.9816 | 0.9848 | 0.9794 | 1.36 | 1.99
9 | EKPC_P1-2_LIBJ-GAS161_SRT-A | 341761 2LIBERTY J 69.0 341767 2LIBERTYKU T 69.0 1 | 341761 | 2LIBERTY J | 341767 | 2LIBERTYKU T | 1 | 69 | 320 | 53 | 66 | EXT_B-69-18_SRT-A | 35 | 43.5 | 61.2 | 13.03 | 88.56 | 92.77 | 3 | 0.92724 | -40.5 | -56.4 | 14 | 20.8 | 0.9859 | 0.9817 | 0.9848 | 0.9796 | 1.36 | 1.92
9 | EKPC_P1-2_LIBJ-GAS161_SRT-A | 341761 2LIBERTY J 69.0 341767 2LIBERTYKU T 69.0 1 | 341761 | 2LIBERTY J | 341767 | 2LIBERTYKU T | 1 | 69 | 320 | 53 | 66 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 10 | 43.5 | 60.6 | 15.8 | 87.56 | 91.76 | 4 | 0.92243 | -40.5 | -55.8 | 14 | 20.4 | 0.9859 | 0.9818 | 0.9848 | 0.9798 | 1.36 | 1.9
10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EKPC_P1-3_MAR 161/138_SRT-A | 16 | 168.9 | 265.9 | 105.73 | 172.86 | 173.81 | 1 | 0.95705 | 168 | 265.4 | -17.1 | -16.7 | 1 | 1 | 0.9965 | 0.9929 | 2.26 | 3.56
10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EKPC_P1-2_MAR-KU LEB138 | 1 | 168.9 | 265.9 | 105.72 | 172.82 | 173.8 | 2 | 0.95705 | 168 | 265.4 | -17.1 | -16.7 | 1 | 1 | 0.9965 | 0.9929 | 2.26 | 3.56
10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EXT_B-69-18_SRT-A | 35 | 168.9 | 265.9 | 101.35 | 172.73 | 173.79 | 3 | 0.95705 | 168 | 265.3 | -17.1 | -17.8 | 1 | 1 | 0.9965 | 0.9931 | 2.26 | 3.56
10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 324557 2GR RVR PLAZ 69.0 324829 2CAMPBELVIL1 69.0 1 | 324557 | 2GR RVR PLAZ | 324829 | 2CAMPBELVIL1 | 1 | 69 | 363 | 39 | 39 | EXT_B-69-18_SRT-A | 35 | 13.8 | 55.5 | 7.52 | 132.33 | 142.3 | 1 | 0.99066 | 10.3 | 52.4 | 8.5 | 8.6 | 0.9656 | 0.9565 | 0.9644 | 0.9535 | 0.03 | 0.25
10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 324557 2GR RVR PLAZ 69.0 324830 2CAMPBELV EK 69.0 1 | 324557 | 2GR RVR PLAZ | 324830 | 2CAMPBELV EK | 1 | 69 | 363 | 47 | 47 | EXT_B-69-18_SRT-A | 35 | 20 | 62.9 | 34.28 | 125.46 | 133.86 | 1 | 0.98053 | -17.6 | -59.7 | 7.9 | 7.4 | 0.9656 | 0.9565 | 0.9657 | 0.9606 | 0.23 | 0.68
10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 3 | 168.9 | 175.4 | 100.11 | 113.34 | 114.61 | 4 | 0.89239 | 168 | 175 | -17.1 | -11.3 | 1 | 1 | 0.9965 | 0.9949 | 2.26 | 2.34
10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | Base Case | 0 | 168.9 | - | 96.55 | 112.6 | 114.11 | 0 | 0.89112 | 168 | - | -17.1 | - | 1 | - | 0.9965 | - | 2.26 | -
10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EXT_B-138-111_SRT-A | 26 | 168.9 | 173 | 93.4 | 111.39 | 113.09 | 5 | 0.90461 | 168 | 172.1 | -17.1 | -17.6 | 1 | 1 | 0.9965 | 0.9964 | 2.26 | 2.31
10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 324191 2LEBANON E T 69.0 324603 2LEBANON CIT 69.0 1 | 324191 | 2LEBANON E T | 324603 | 2LEBANON CIT | 1 | 69 | 363 | 52 | 66 | Base Case | 0 | 58.3 | - | 69.15 | 112.36 | 112.17 | 0 | 0.97606 | 58.4 | - | -4.3 | - | 1.0044 | - | 1.0009 | - | 0.51 | -
10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 324191 2LEBANON E T 69.0 324603 2LEBANON CIT 69.0 1 | 324191 | 2LEBANON E T | 324603 | 2LEBANON CIT | 1 | 69 | 363 | 52 | 66 | EKPC_P1-2_LIBJ-GAS161_SRT-A | 9 | 58.3 | 70.3 | 57.23 | 108.21 | 106.52 | 1 | 0.97649 | 58.4 | 70.3 | -4.3 | -7.4 | 1.0044 | 1.0054 | 1.0009 | 1.0015 | 0.51 | 0.62
10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 341342 2CONTOWN T 69.0 341761 2LIBERTY J 69.0 1 | 341342 | 2CONTOWN T | 341761 | 2LIBERTY J | 1 | 69 | 320 | 53 | 63 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 7 | 37.7 | 67 | 85.11 | 105.04 | 106.32 | 1 | 0.92845 | -36.3 | -64.7 | 9.8 | 16.5 | 0.9957 | 0.9976 | 0.9999 | 1.0056 | 1.01 | 1.78
10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 341342 2CONTOWN T 69.0 342067 2PHIL 69.0 1 | 341342 | 2CONTOWN T | 342067 | 2PHIL | 1 | 69 | 320 | 57 | 63 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 7 | 35.6 | 64.9 | 81.78 | 100.5 | 102.96 | 1 | 0.84796 | 34 | 62.5 | -10.2 | -16.8 | 0.9957 | 0.9976 | 0.9892 | 0.9849 | 2.06 | 3.75
10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 324271 4LEBANON 138 342770 4MARION CO 138 1 | 324271 | 4LEBANON | 342770 | 4MARION CO | 1 | 138 | 363/320 | 187 | 220 | EKPC_P1-2_LIBJ-GAS161_SRT-A | 9 | 111.5 | 225 | 50.18 | 103.76 | 102.28 | 1 | 0.99955 | -112.3 | -226 | -4.8 | 15.1 | 1.0081 | 1.0066 | 1.0082 | 1.0068 | 0.02 | 0.04
10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 324191 2LEBANON E T 69.0 324603 2LEBANON CIT 69.0 1 | 324191 | 2LEBANON E T | 324603 | 2LEBANON CIT | 1 | 69 | 363 | 52 | 66 | EKPC_P1-2_GRE-SUMSH161_SRT-A | 11 | 58.3 | 67 | 58.91 | 101.45 | 101.51 | 2 | 0.97774 | 58.4 | 66.8 | -4.3 | -9.9 | 1.0044 | 1.0081 | 1.0009 | 1.0049 | 0.51 | 0.6
10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 324603 2LEBANON CIT 69.0 324605 2LEBANON EK 69.0 1 | 324603 | 2LEBANON CIT | 324605 | 2LEBANON EK | 1 | 69 | 363 | 52 | 66 | Base Case | 0 | 52.7 | - | 58.26 | 99.81 | 101.37 | 0 | 0.99142 | 52 | - | 9.1 | - | 1.0009 | - | 0.999 | - | 0.14 | -
10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 324191 2LEBANON E T 69.0 324603 2LEBANON CIT 69.0 1 | 324191 | 2LEBANON E T | 324603 | 2LEBANON CIT | 1 | 69 | 363 | 52 | 66 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 7 | 58.3 | 66.1 | 54.48 | 100.71 | 100.14 | 3 | 0.97633 | 58.4 | 66.3 | -4.3 | -5.9 | 1.0044 | 1.007 | 1.0009 | 1.0032 | 0.51 | 0.58
10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 324554 2GRENSBRG KU 69.0 341563 2GREEN CO 69.0 1 | 324554 | 2GRENSBRG KU | 341563 | 2GREEN CO | 1 | 69 | 363/320 | 52 | 66 | EXT_B-69-18_SRT-A | 35 | 38.8 | 65.7 | 48.79 | 93.18 | 99.56 | 1 | 0.9752 | -38.4 | -65.9 | -1.8 | -9.8 | 0.9909 | 1.0133 | 0.9937 | 1.019 | 0.29 | 0.45
10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 324736 2SPRINGFL KU 69.0 341935 2N SPRINGFLD 69.0 1 | 324736 | 2SPRINGFL KU | 341935 | 2N SPRINGFLD | 1 | 69 | 363/320 | 49 | 50 | EXT_B-69-18_SRT-A | 35 | 16.9 | 49.5 | 61.14 | 97.15 | 98.97 | 1 | 0.89125 | 13.7 | -46.7 | -10 | -4.1 | 1.0009 | 0.9479 | 1.0022 | 0.9829 | 1.09 | 2.59
10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 324603 2LEBANON CIT 69.0 324605 2LEBANON EK 69.0 1 | 324603 | 2LEBANON CIT | 324605 | 2LEBANON EK | 1 | 69 | 363 | 52 | 66 | EKPC_P1-2_LIBJ-GAS161_SRT-A | 9 | 52.7 | 63.9 | 48.36 | 98.32 | 96.82 | 1 | 0.99157 | 52 | 63.7 | 9.1 | 5.8 | 1.0009 | 1.0015 | 0.999 | 0.9995 | 0.14 | 0.18
10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 342769 5MARION CO 161 342770 4MARION CO 138 1 | 342769 | 5MARION CO | 342770 | 4MARION CO | 1 | 161/138 | 320 | 192 | 234 | EKPC_P1-2_LIBJ-GAS161_SRT-A | 9 | 112.7 | 226.5 | 47.46 | 97.58 | 96.81 | 1 | 0.95642 | 112.4 | 226.2 | 8.5 | -0.2 | 1.0105 | 1.0053 | 1.0082 | 1.0068 | 1.84 | 3.73
10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 341143 2BLUE G PW T 69.0 342508 2WOODLAWN 69.0 1 | 341143 | 2BLUE G PW T | 342508 | 2WOODLAWN | 1 | 69 | 320 | 41 | 46 | EXT_B-69-18_SRT-A | 35 | 19.5 | 44.2 | 77.87 | 86.83 | 96.16 | 1 | 0.90187 | 15.5 | 40.7 | -11.4 | -15.7 | 0.9903 | 0.9864 | 0.9921 | 0.9844 | 0.6 | 1.39
10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 341494 2FREDRIKBG T 69.0 342508 2WOODLAWN 69.0 1 | 341494 | 2FREDRIKBG T | 342508 | 2WOODLAWN | 1 | 69 | 320 | 41 | 46 | EXT_B-69-18_SRT-A | 35 | 19.4 | 44.2 | 77.81 | 86.83 | 96.1 | 1 | 0.88205 | -15.3 | -39.6 | 11.6 | 17.6 | 0.994 | 0.9818 | 0.9921 | 0.9844 | 0.73 | 1.7
10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 341407 2E BARDSTOWN 69.0 342019 2OWENS IL J 69.0 1 | 341407 | 2E BARDSTOWN | 342019 | 2OWENS IL J | 1 | 69 | 320 | 57 | 63 | EXT_B-69-18_SRT-A | 35 | 34.6 | 60.5 | 84.41 | 93.45 | 96.07 | 1 | 0.98786 | 34.4 | 59.9 | 0 | -3.6 | 0.9933 | 0.9922 | 0.9921 | 0.9903 | 0.12 | 0.22
10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 324271 4LEBANON 138 324606 2LEBANON 69.0 2 | 324271 | 4LEBANON | 324606 | 2LEBANON | 2 | 138/69 | 363 | 72 | 101 | Base Case | 0 | 68.2 | - | 69.78 | 94.51 | 94.79 | 0 | 0.56302 | 68.2 | - | -0.8 | - | 1.0081 | - | 1.0077 | - | 2.7 | -
10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 324554 2GRENSBRG KU 69.0 324830 2CAMPBELV EK 69.0 1 | 324554 | 2GRENSBRG KU | 324830 | 2CAMPBELV EK | 1 | 69 | 363 | 52 | 66 | EXT_B-69-18_SRT-A | 35 | 34.2 | 61.2 | 41.95 | 84.85 | 92.79 | 1 | 0.73719 | 33.8 | 61.3 | 1.5 | 9.5 | 0.9909 | 1.0133 | 0.9657 | 0.9606 | 2.77 | 4.65
10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 341761 2LIBERTY J 69.0 341767 2LIBERTYKU T 69.0 1 | 341761 | 2LIBERTY J | 341767 | 2LIBERTYKU T | 1 | 69 | 320 | 53 | 66 | EKPC_P1-2_LIBJ-GAS161_SRT-A | 9 | 10.4 | 60.6 | 65.86 | 90.13 | 91.76 | 1 | 0.92243 | -8.8 | -55.8 | 5.5 | 20.4 | 0.9999 | 0.9817 | 0.9983 | 0.9798 | 0.31 | 1.9
10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 324603 2LEBANON CIT 69.0 324605 2LEBANON EK 69.0 1 | 324603 | 2LEBANON CIT | 324605 | 2LEBANON EK | 1 | 69 | 363 | 52 | 66 | EKPC_P1-2_GRE-SUMSH161_SRT-A | 11 | 52.7 | 60.1 | 50.79 | 91.55 | 91.03 | 2 | 0.99202 | 52 | 60.3 | 9.1 | 3.4 | 1.0009 | 1.0049 | 0.999 | 1.0031 | 0.14 | 0.18
10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 324603 2LEBANON CIT 69.0 324605 2LEBANON EK 69.0 1 | 324603 | 2LEBANON CIT | 324605 | 2LEBANON EK | 1 | 69 | 363 | 52 | 66 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 7 | 52.7 | 60 | 45.9 | 90.82 | 90.96 | 3 | 0.99152 | 52 | 59.8 | 9.1 | 7.4 | 1.0009 | 1.0032 | 0.999 | 1.0012 | 0.14 | 0.17
10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 324191 2LEBANON E T 69.0 324603 2LEBANON CIT 69.0 1 | 324191 | 2LEBANON E T | 324603 | 2LEBANON CIT | 1 | 69 | 363 | 52 | 66 | EXT_BB-1066_SRT-A | 37 | 58.3 | 59.8 | 54.48 | 91.03 | 90.65 | 4 | 0.97611 | 58.4 | 59.9 | -4.3 | -4.7 | 1.0044 | 1.0043 | 1.0009 | 1.0007 | 0.51 | 0.52
10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 324191 2LEBANON E T 69.0 324603 2LEBANON CIT 69.0 1 | 324191 | 2LEBANON E T | 324603 | 2LEBANON CIT | 1 | 69 | 363 | 52 | 66 | EXT_324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1 _SRT-A | 33 | 58.3 | 59.8 | 54.48 | 90.89 | 90.57 | 5 | 0.97611 | 58.4 | 59.8 | -4.3 | -4.7 | 1.0044 | 1.0043 | 1.0009 | 1.0007 | 0.51 | 0.52
10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 342703 5CASEY CO 161 342769 5MARION CO 161 1 | 342703 | 5CASEY CO | 342769 | 5MARION CO | 1 | 161 | 320 | 148 | 153 | EKPC_P1-2_LIBJ-GAS161_SRT-A | 9 | 26.2 | 138.2 | 101.09 | 86.49 | 90.31 | 1 | 0.92073 | 16.5 | 132.3 | -20.5 | -38.5 | 1.0022 | 0.9976 | 1.0105 | 1.0053 | 0.61 | 4.24
11 | EKPC_P1-2_GRE-SUMSH161_SRT-A | 324191 2LEBANON E T 69.0 324603 2LEBANON CIT 69.0 1 | 324191 | 2LEBANON E T | 324603 | 2LEBANON CIT | 1 | 69 | 363 | 52 | 66 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 10 | 38.9 | 67 | 88.42 | 100.53 | 101.51 | 1 | 0.97774 | 38.6 | 66.8 | -4.8 | -9.9 | 1.0008 | 1.0081 | 0.9988 | 1.0049 | 0.35 | 0.6
11 | EKPC_P1-2_GRE-SUMSH161_SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EKPC_P1-3_MAR 161/138_SRT-A | 16 | 135 | 153.4 | 105.73 | 98.97 | 100.24 | 1 | 0.91327 | 134.2 | 152.5 | -14.6 | -16.3 | 1 | 1 | 0.9973 | 0.9969 | 1.81 | 2.05
11 | EKPC_P1-2_GRE-SUMSH161_SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EKPC_P1-2_MAR-KU LEB138 | 1 | 135 | 153.4 | 105.72 | 98.97 | 100.24 | 2 | 0.91327 | 134.2 | 152.5 | -14.6 | -16.3 | 1 | 1 | 0.9973 | 0.9969 | 1.81 | 2.05
11 | EKPC_P1-2_GRE-SUMSH161_SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 3 | 135 | 141.5 | 100.11 | 92.08 | 92.45 | 3 | 0.887 | 134.2 | 141.1 | -14.6 | -10.5 | 1 | 1 | 0.9973 | 0.996 | 1.81 | 1.89
11 | EKPC_P1-2_GRE-SUMSH161_SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EXT_B-69-18_SRT-A | 35 | 135 | 139.9 | 101.35 | 92.13 | 91.44 | 4 | 0.9153 | 134.2 | 139 | -14.6 | -15.5 | 1 | 1 | 0.9973 | 0.9973 | 1.81 | 1.87
11 | EKPC_P1-2_GRE-SUMSH161_SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | Base Case | 0 | 135 | - | 96.55 | 90.09 | 91.22 | 0 | 0.88551 | 134.2 | - | -14.6 | - | 1 | - | 0.9973 | - | 1.81 | -
11 | EKPC_P1-2_GRE-SUMSH161_SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 15 | 135 | 139.4 | 95.51 | 90.11 | 91.12 | 5 | 0.88659 | 134.2 | 138.6 | -14.6 | -14.6 | 1 | 1 | 0.9973 | 0.9971 | 1.81 | 1.86
11 | EKPC_P1-2_GRE-SUMSH161_SRT-A | 324603 2LEBANON CIT 69.0 324605 2LEBANON EK 69.0 1 | 324603 | 2LEBANON CIT | 324605 | 2LEBANON EK | 1 | 69 | 363 | 52 | 66 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 10 | 33.5 | 60.1 | 79.94 | 90.91 | 91.03 | 1 | 0.99202 | 32.3 | 60.3 | 8.8 | 3.4 | 0.9988 | 1.0049 | 0.9975 | 1.0031 | 0.08 | 0.18
12 | EKPC_P1-2_BARR-SUMSH161_SRT-A | 342307 2STEPHENSBRG 69.0 342403 2UPTON T 69.0 1 | 342307 | 2STEPHENSBRG | 342403 | 2UPTON T | 1 | 69 | 320 | 35 | 39 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 25 | 14.3 | 36.8 | 85.66 | 92.35 | 94.35 | 1 | 0.67387 | 12.9 | 33.8 | -6.3 | -13.7 | 1.0008 | 0.9923 | 0.9958 | 0.9762 | 1.88 | 4.88
12 | EKPC_P1-2_BARR-SUMSH161_SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EXT_B-138-111_SRT-A | 26 | 142.4 | 139.3 | 93.4 | 89.89 | 91.06 | 1 | 0.88795 | 141.6 | 138.4 | -15.7 | -15.7 | 1 | 1 | 0.9972 | 0.9973 | 1.91 | 1.86
12 | EKPC_P1-2_BARR-SUMSH161_SRT-A | 342307 2STEPHENSBRG 69.0 342403 2UPTON T 69.0 1 | 342307 | 2STEPHENSBRG | 342403 | 2UPTON T | 1 | 69 | 320 | 35 | 39 | EXT_B-69-19_SRT-A | 36 | 14.3 | 35.1 | 71.65 | 87.92 | 90.05 | 2 | 0.79555 | 12.9 | 34.5 | -6.3 | -6.2 | 1.0008 | 0.9971 | 0.9958 | 0.9652 | 1.88 | 4.39
13 | EKPC_P1-2_BULL-SUMSH161_SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EXT_B-138-111_SRT-A | 26 | 142.3 | 138.7 | 93.4 | 89.48 | 90.63 | 1 | 0.88802 | 141.4 | 137.8 | -15.7 | -15.6 | 1 | 1 | 0.9972 | 0.9974 | 1.9 | 1.86
15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 324557 2GR RVR PLAZ 69.0 324829 2CAMPBELVIL1 69.0 1 | 324557 | 2GR RVR PLAZ | 324829 | 2CAMPBELVIL1 | 1 | 69 | 363 | 39 | 39 | EXT_B-69-18_SRT-A | 35 | 17.8 | 57.5 | 7.52 | 137.31 | 147.5 | 1 | 0.99061 | 15.8 | 53.5 | 6.7 | 6.4 | 0.9655 | 0.9367 | 0.9642 | 0.9338 | 0.06 | 0.27
15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 324557 2GR RVR PLAZ 69.0 324830 2CAMPBELV EK 69.0 1 | 324557 | 2GR RVR PLAZ | 324830 | 2CAMPBELV EK | 1 | 69 | 363 | 47 | 47 | EXT_B-69-18_SRT-A | 35 | 25.9 | 65.6 | 34.28 | 129.64 | 139.58 | 1 | 0.98042 | -23.1 | -60.8 | 9.6 | 8.8 | 0.9655 | 0.9367 | 0.9658 | 0.9408 | 0.29 | 0.73
15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EKPC_P1-3_MAR 161/138_SRT-A | 16 | 146.1 | 174 | 105.73 | 112.57 | 113.76 | 1 | 0.90388 | 145.3 | 173.2 | -15.5 | -17.2 | 1 | 1 | 0.997 | 0.9963 | 1.95 | 2.33
15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EKPC_P1-2_MAR-KU LEB138 | 1 | 146.1 | 174 | 105.72 | 112.56 | 113.75 | 2 | 0.90388 | 145.3 | 173.2 | -15.5 | -17.2 | 1 | 1 | 0.997 | 0.9963 | 1.95 | 2.33
15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EXT_B-69-18_SRT-A | 35 | 146.1 | 170 | 101.35 | 110.26 | 111.14 | 3 | 0.90409 | 145.3 | 169.2 | -15.5 | -17.4 | 1 | 1 | 0.997 | 0.9965 | 1.95 | 2.27
15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 324554 2GRENSBRG KU 69.0 341563 2GREEN CO 69.0 1 | 324554 | 2GRENSBRG KU | 341563 | 2GREEN CO | 1 | 69 | 363/320 | 52 | 66 | EXT_B-69-18_SRT-A | 35 | 44.4 | 72.6 | 48.79 | 106.28 | 109.99 | 1 | 0.97448 | -44.1 | -71.7 | -0.5 | -3 | 0.9927 | 0.988 | 0.9957 | 0.9933 | 0.34 | 0.54
15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 324554 2GRENSBRG KU 69.0 324830 2CAMPBELV EK 69.0 1 | 324554 | 2GRENSBRG KU | 324830 | 2CAMPBELV EK | 1 | 69 | 363 | 52 | 66 | EXT_B-69-18_SRT-A | 35 | 39.8 | 68 | 41.95 | 97.47 | 102.97 | 1 | 0.7295 | 39.5 | 67.1 | 0.1 | 2.7 | 0.9927 | 0.988 | 0.9658 | 0.9408 | 3.29 | 5.67
15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 3 | 146.1 | 156.9 | 100.11 | 101.48 | 102.55 | 4 | 0.88334 | 145.3 | 156.6 | -15.5 | -10.2 | 1 | 1 | 0.997 | 0.9954 | 1.95 | 2.09
15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 324191 2LEBANON E T 69.0 324603 2LEBANON CIT 69.0 1 | 324191 | 2LEBANON E T | 324603 | 2LEBANON CIT | 1 | 69 | 363 | 52 | 66 | Base Case | 0 | 52.5 | - | 69.15 | 101.03 | 101.02 | 0 | 0.97473 | 52.5 | - | -2.7 | - | 1.0014 | - | 0.9981 | - | 0.46 | -
15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | Base Case | 0 | 146.1 | - | 96.55 | 97.49 | 98.74 | 0 | 0.88095 | 145.3 | - | -15.5 | - | 1 | - | 0.997 | - | 1.95 | -
15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 324736 2SPRINGFL KU 69.0 341935 2N SPRINGFLD 69.0 1 | 324736 | 2SPRINGFL KU | 341935 | 2N SPRINGFLD | 1 | 69 | 363/320 | 49 | 50 | EXT_B-69-18_SRT-A | 35 | 10.8 | 49.3 | 61.14 | 91.62 | 98.51 | 1 | 0.89063 | 7.7 | -45.7 | -7.6 | -7.3 | 0.9987 | 0.9395 | 1.0012 | 0.9772 | 0.68 | 2.45
15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EKPC_P1-2_COOP-ELIHU161_SRT-A | 2 | 146.1 | 149.4 | 95.57 | 96.98 | 97.64 | 5 | 0.88497 | 145.3 | 149.2 | -15.5 | -8.3 | 1 | 1 | 0.997 | 0.9952 | 1.95 | 1.99
15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 341407 2E BARDSTOWN 69.0 342019 2OWENS IL J 69.0 1 | 341407 | 2E BARDSTOWN | 342019 | 2OWENS IL J | 1 | 69 | 320 | 57 | 63 | EXT_B-69-18_SRT-A | 35 | 37.3 | 60.2 | 84.41 | 92.26 | 95.56 | 1 | 0.98786 | 37 | 59.6 | -0.8 | -2.2 | 0.9932 | 0.9899 | 0.992 | 0.9879 | 0.13 | 0.21
15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 341143 2BLUE G PW T 69.0 342508 2WOODLAWN 69.0 1 | 341143 | 2BLUE G PW T | 342508 | 2WOODLAWN | 1 | 69 | 320 | 41 | 46 | EXT_B-69-18_SRT-A | 35 | 22.1 | 43.5 | 77.87 | 85.1 | 94.55 | 1 | 0.90183 | 18.1 | 40.3 | -12.3 | -14.3 | 0.99 | 0.9837 | 0.9917 | 0.981 | 0.69 | 1.37
15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 341494 2FREDRIKBG T 69.0 342508 2WOODLAWN 69.0 1 | 341494 | 2FREDRIKBG T | 342508 | 2WOODLAWN | 1 | 69 | 320 | 41 | 46 | EXT_B-69-18_SRT-A | 35 | 22.1 | 43.5 | 77.81 | 85.1 | 94.49 | 1 | 0.88199 | -17.8 | -39.3 | 12.6 | 16.1 | 0.9934 | 0.9777 | 0.9917 | 0.981 | 0.83 | 1.67
15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 324603 2LEBANON CIT 69.0 324605 2LEBANON EK 69.0 1 | 324603 | 2LEBANON CIT | 324605 | 2LEBANON EK | 1 | 69 | 363 | 52 | 66 | Base Case | 0 | 47.4 | - | 58.26 | 88.59 | 91.21 | 0 | 0.99094 | 46.1 | - | 10.6 | - | 0.9981 | - | 0.9963 | - | 0.12 | -
16 | EKPC_P1-3_MAR 161/138_SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 10 | 161.8 | 265.9 | 110.38 | 172.88 | 173.81 | 1 | 0.95705 | 160.9 | 265.4 | -17.1 | -16.7 | 1 | 1 | 0.9968 | 0.9929 | 2.16 | 3.56
16 | EKPC_P1-3_MAR 161/138_SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 15 | 161.8 | 174 | 95.51 | 112.46 | 113.76 | 2 | 0.90388 | 160.9 | 173.2 | -17.1 | -17.2 | 1 | 1 | 0.9968 | 0.9963 | 2.16 | 2.33
16 | EKPC_P1-3_MAR 161/138_SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 3 | 161.8 | 170.5 | 100.11 | 110.35 | 111.44 | 3 | 0.90193 | 160.9 | 170.1 | -17.1 | -12.1 | 1 | 1 | 0.9968 | 0.9953 | 2.16 | 2.28
16 | EKPC_P1-3_MAR 161/138_SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | Base Case | 0 | 161.8 | - | 96.55 | 107.84 | 109.3 | 0 | 0.89989 | 160.9 | - | -17.1 | - | 1 | - | 0.9968 | - | 2.16 | -
16 | EKPC_P1-3_MAR 161/138_SRT-A | 342769 5MARION CO 161 342775 5MARION IP T 161 1 | 342769 | 5MARION CO | 342775 | 5MARION IP T | 1 | 161 | 320 | 186 | 210 | EKPC_P1-2_LIBJ-GAS161_SRT-A | 9 | 119.5 | 222 | 62.41 | 107.14 | 105.72 | 1 | 0.9836 | 120.6 | 223.4 | 5.7 | -1.6 | 1.0106 | 1.0064 | 1.0075 | 1.0022 | 0.78 | 1.47
16 | EKPC_P1-3_MAR 161/138_SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EXT_324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1 _SRT-A | 24 | 161.8 | 158.7 | 86.46 | 102.38 | 103.72 | 4 | 0.90004 | 160.9 | 157.8 | -17.1 | -17 | 1 | 1 | 0.9968 | 0.9969 | 2.16 | 2.12
16 | EKPC_P1-3_MAR 161/138_SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EXT_B-138-115_SRT-A | 30 | 161.8 | 158.7 | 85.77 | 102.5 | 103.71 | 5 | 0.89992 | 160.9 | 157.8 | -17.1 | -16.8 | 1 | 1 | 0.9968 | 0.9968 | 2.16 | 2.12
16 | EKPC_P1-3_MAR 161/138_SRT-A | 341342 2CONTOWN T 69.0 341761 2LIBERTY J 69.0 1 | 341342 | 2CONTOWN T | 341761 | 2LIBERTY J | 1 | 69 | 320 | 53 | 63 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 7 | 34.8 | 64.7 | 85.11 | 101.42 | 102.64 | 1 | 0.9287 | -33.5 | -62.5 | 9.2 | 16 | 0.9965 | 0.9986 | 1.0003 | 1.0063 | 0.93 | 1.72
16 | EKPC_P1-3_MAR 161/138_SRT-A | 341342 2CONTOWN T 69.0 342067 2PHIL 69.0 1 | 341342 | 2CONTOWN T | 342067 | 2PHIL | 1 | 69 | 320 | 57 | 63 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 7 | 32.8 | 62.6 | 81.78 | 97.03 | 99.29 | 1 | 0.84848 | 31.2 | 60.3 | -9.6 | -16.3 | 0.9965 | 0.9986 | 0.9907 | 0.9864 | 1.89 | 3.61
16 | EKPC_P1-3_MAR 161/138_SRT-A | 341761 2LIBERTY J 69.0 341767 2LIBERTYKU T 69.0 1 | 341761 | 2LIBERTY J | 341767 | 2LIBERTYKU T | 1 | 69 | 320 | 53 | 66 | EKPC_P1-2_LIBJ-GAS161_SRT-A | 9 | 9.4 | 63.4 | 65.86 | 94.84 | 96.01 | 1 | 0.9268 | -7.7 | -58.3 | 5.3 | 21.6 | 1.0003 | 0.9816 | 0.9986 | 0.9795 | 0.27 | 1.99
16 | EKPC_P1-3_MAR 161/138_SRT-A | 342307 2STEPHENSBRG 69.0 342403 2UPTON T 69.0 1 | 342307 | 2STEPHENSBRG | 342403 | 2UPTON T | 1 | 69 | 320 | 35 | 39 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 25 | 13.3 | 36.6 | 85.66 | 92.15 | 93.75 | 1 | 0.67183 | 11.9 | 33.7 | -6 | -13.3 | 1.0001 | 0.9911 | 0.9957 | 0.9744 | 1.75 | 4.85
16 | EKPC_P1-3_MAR 161/138_SRT-A | 342769 5MARION CO 161 342775 5MARION IP T 161 1 | 342769 | 5MARION CO | 342775 | 5MARION IP T | 1 | 161 | 320 | 186 | 210 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 7 | 119.5 | 189.4 | 56.35 | 90.57 | 90.17 | 2 | 0.97835 | 120.6 | 191.3 | 5.7 | 1 | 1.0106 | 1.0101 | 1.0075 | 1.0062 | 0.78 | 1.25
17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A | 342307 2STEPHENSBRG 69.0 342403 2UPTON T 69.0 1 | 342307 | 2STEPHENSBRG | 342403 | 2UPTON T | 1 | 69 | 320 | 35 | 39 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 25 | 8.7 | 42.4 | 85.66 | 109.46 | 108.84 | 1 | 0.71787 | 8.1 | 41.7 | -3.1 | -10.1 | 0.9983 | 1.0116 | 0.9932 | 0.9794 | 1.12 | 5.36
17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 3 | 139 | 148.9 | 100.11 | 96.34 | 97.34 | 1 | 0.88501 | 138.2 | 148.5 | -15.4 | -10.7 | 1 | 1 | 0.9973 | 0.9958 | 1.86 | 1.99
17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A | 342307 2STEPHENSBRG 69.0 342403 2UPTON T 69.0 1 | 342307 | 2STEPHENSBRG | 342403 | 2UPTON T | 1 | 69 | 320 | 35 | 39 | EXT_B-138-115_SRT-A | 30 | 8.7 | 37.5 | 69.47 | 96.13 | 96.08 | 2 | 0.72071 | 8.1 | 35.4 | -3.1 | -11.2 | 0.9983 | 0.9913 | 0.9932 | 0.9681 | 1.12 | 4.91
17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | Base Case | 0 | 139 | - | 96.55 | 92.75 | 93.95 | 0 | 0.88279 | 138.2 | - | -15.4 | - | 1 | - | 0.9973 | - | 1.86 | -
17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EKPC_P1-2_COOP-ELIHU161_SRT-A | 2 | 139 | 142.5 | 95.57 | 92.49 | 93.12 | 2 | 0.8866 | 138.2 | 142.2 | -15.4 | -8.3 | 1 | 1 | 0.9973 | 0.9955 | 1.86 | 1.9
17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 15 | 139 | 142.3 | 95.51 | 91.99 | 93.01 | 3 | 0.88332 | 138.2 | 141.5 | -15.4 | -15.2 | 1 | 1 | 0.9973 | 0.9971 | 1.86 | 1.9
17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A | 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1 | 324213 | 4BONNIEVILLE | 324447 | 2BONNIE KU | 1 | 138/69 | 363 | 33 | 40 | EXT_B-138-115_SRT-A | 30 | 4.2 | 36.3 | 65.55 | 90.71 | 90.87 | 1 | 0.73225 | -3.3 | -36.1 | -2.4 | 4.4 | 0.9741 | 0.9383 | 0.9805 | 0.9359 | 0.45 | 5.59
18 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 10 | 138.7 | 164.1 | 110.38 | 106.1 | 107.25 | 1 | 0.89214 | 137.8 | 163.2 | -15.3 | -16.8 | 1 | 1 | 0.9973 | 0.9966 | 1.86 | 2.2
18 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 3 | 138.7 | 149 | 100.11 | 96.35 | 97.36 | 2 | 0.8834 | 137.8 | 148.6 | -15.3 | -10.6 | 1 | 1 | 0.9973 | 0.9958 | 1.86 | 1.99
18 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | Base Case | 0 | 138.7 | - | 96.55 | 92.52 | 93.71 | 0 | 0.88104 | 137.8 | - | -15.3 | - | 1 | - | 0.9973 | - | 1.86 | -
18 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EKPC_P1-2_COOP-ELIHU161_SRT-A | 2 | 138.7 | 142.3 | 95.57 | 92.4 | 93.02 | 3 | 0.885 | 137.8 | 142.1 | -15.3 | -8.3 | 1 | 1 | 0.9973 | 0.9955 | 1.86 | 1.89
18 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 15 | 138.7 | 141.9 | 95.51 | 91.73 | 92.77 | 4 | 0.88155 | 137.8 | 141.1 | -15.3 | -15.2 | 1 | 1 | 0.9973 | 0.9971 | 1.86 | 1.9
20 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 10 | 139.5 | 172.8 | 110.38 | 111.29 | 112.97 | 1 | 0.90461 | 138.7 | 172 | -15.4 | -17.3 | 1 | 1 | 0.9973 | 0.9964 | 1.87 | 2.31
20 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A | 342703 5CASEY CO 161 342769 5MARION CO 161 1 | 342703 | 5CASEY CO | 342769 | 5MARION CO | 1 | 161 | 320 | 148 | 153 | EKPC_P1-2_LIBJ-GAS161_SRT-A | 9 | 56.1 | 149.9 | 101.09 | 96.17 | 97.99 | 1 | 0.91929 | 49.9 | 145.4 | -25.9 | -36.2 | 1.0019 | 0.9992 | 1.0098 | 1.0048 | 1.65 | 4.61
20 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 3 | 139.5 | 149.6 | 100.11 | 96.86 | 97.81 | 2 | 0.89038 | 138.7 | 149.3 | -15.4 | -10.6 | 1 | 1 | 0.9973 | 0.9957 | 1.87 | 2
20 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | Base Case | 0 | 139.5 | - | 96.55 | 93.08 | 94.29 | 0 | 0.88793 | 138.7 | - | -15.4 | - | 1 | - | 0.9973 | - | 1.87 | -
20 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 15 | 139.5 | 142.9 | 95.51 | 92.4 | 93.43 | 3 | 0.88849 | 138.7 | 142.1 | -15.4 | -15.2 | 1 | 1 | 0.9973 | 0.9971 | 1.87 | 1.91
20 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A | 342307 2STEPHENSBRG 69.0 342403 2UPTON T 69.0 1 | 342307 | 2STEPHENSBRG | 342403 | 2UPTON T | 1 | 69 | 320 | 35 | 39 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 25 | 12.6 | 35.5 | 85.66 | 88.74 | 90.9 | 1 | 0.67295 | 11 | 32.2 | -6.3 | -14.2 | 1.0015 | 0.9928 | 0.999 | 0.9795 | 1.66 | 4.72
21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A | 342307 2STEPHENSBRG 69.0 342403 2UPTON T 69.0 1 | 342307 | 2STEPHENSBRG | 342403 | 2UPTON T | 1 | 69 | 320 | 35 | 39 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 25 | 9.8 | 44.8 | 85.66 | 114.78 | 114.9 | 1 | 0.71787 | 9.1 | 44.1 | -3.7 | -10.6 | 0.9987 | 1.0111 | 0.9935 | 0.9772 | 1.27 | 5.67
21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A | 342307 2STEPHENSBRG 69.0 342403 2UPTON T 69.0 1 | 342307 | 2STEPHENSBRG | 342403 | 2UPTON T | 1 | 69 | 320 | 35 | 39 | EXT_B-138-115_SRT-A | 30 | 9.8 | 39.8 | 69.47 | 101.45 | 102.1 | 2 | 0.72071 | 9.1 | 37.7 | -3.7 | -11.7 | 0.9987 | 0.9908 | 0.9935 | 0.966 | 1.27 | 5.22
21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A | 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1 | 324213 | 4BONNIEVILLE | 324447 | 2BONNIE KU | 1 | 138/69 | 363 | 33 | 40 | EXT_B-138-115_SRT-A | 30 | 5 | 38.7 | 65.55 | 96.62 | 96.8 | 1 | 0.73225 | -4.6 | -38.4 | -1.9 | 5.3 | 0.9751 | 0.9367 | 0.9805 | 0.9328 | 0.64 | 5.98
21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A | 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1 | 324213 | 4BONNIEVILLE | 324447 | 2BONNIE KU | 1 | 138/69 | 363 | 33 | 40 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 25 | 5 | 37.5 | 64.59 | 92.06 | 93.67 | 2 | 0.73194 | -4.6 | -37.1 | -1.9 | 4.9 | 0.9751 | 0.9426 | 0.9805 | 0.9392 | 0.64 | 5.71
24 | EXT_324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1 _SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 10 | 132.3 | 158.2 | 110.38 | 102.11 | 103.37 | 1 | 0.89678 | 131.4 | 157.3 | -14.8 | -16.6 | 1 | 1 | 0.9974 | 0.9968 | 1.77 | 2.12
24 | EXT_324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1 _SRT-A | 342307 2STEPHENSBRG 69.0 342403 2UPTON T 69.0 1 | 342307 | 2STEPHENSBRG | 342403 | 2UPTON T | 1 | 69 | 320 | 35 | 39 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 25 | 13.7 | 36.5 | 85.66 | 91.38 | 93.59 | 1 | 0.67088 | 12 | 33.2 | -6.6 | -14.4 | 1.001 | 0.9926 | 0.9977 | 0.9786 | 1.81 | 4.86
24 | EXT_324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1 _SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 3 | 132.3 | 142.4 | 100.11 | 92.14 | 93.05 | 2 | 0.886 | 131.4 | 142 | -14.8 | -10.3 | 1 | 1 | 0.9974 | 0.996 | 1.77 | 1.9
25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 342307 2STEPHENSBRG 69.0 342403 2UPTON T 69.0 1 | 342307 | 2STEPHENSBRG | 342403 | 2UPTON T | 1 | 69 | 320 | 35 | 39 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A | 21 | 33.4 | 44.8 | 25.13 | 105.85 | 114.77 | 1 | 0.71787 | 30.1 | 44 | -14 | -10.8 | 0.994 | 1.0112 | 0.9828 | 0.9778 | 4.45 | 5.67
25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 342307 2STEPHENSBRG 69.0 342403 2UPTON T 69.0 1 | 342307 | 2STEPHENSBRG | 342403 | 2UPTON T | 1 | 69 | 320 | 35 | 39 | EXT_B-69-18_SRT-A | 35 | 33.4 | 44.1 | 23.47 | 104.29 | 113.06 | 2 | 0.718 | 30.1 | 43.3 | -14 | -10.6 | 0.994 | 1.0114 | 0.9828 | 0.9782 | 4.45 | 5.58
25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 342307 2STEPHENSBRG 69.0 342403 2UPTON T 69.0 1 | 342307 | 2STEPHENSBRG | 342403 | 2UPTON T | 1 | 69 | 320 | 35 | 39 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A | 17 | 33.4 | 42.4 | 22.33 | 99.7 | 108.71 | 3 | 0.71787 | 30.1 | 41.6 | -14 | -10.3 | 0.994 | 1.0117 | 0.9828 | 0.98 | 4.45 | 5.37
25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 342307 2STEPHENSBRG 69.0 342403 2UPTON T 69.0 1 | 342307 | 2STEPHENSBRG | 342403 | 2UPTON T | 1 | 69 | 320 | 35 | 39 | EXT_BB-1133_SRT-A | 28 | 33.4 | 42.4 | 22.37 | 99.67 | 108.68 | 4 | 0.71787 | 30.1 | 41.6 | -14 | -10.3 | 0.994 | 1.0118 | 0.9828 | 0.9801 | 4.45 | 5.36
25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 10 | 132.2 | 155.8 | 110.38 | 100.69 | 101.8 | 1 | 0.89214 | 131.4 | 154.9 | -14.6 | -16.2 | 1 | 1 | 0.9974 | 0.9968 | 1.77 | 2.08
25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 342307 2STEPHENSBRG 69.0 342403 2UPTON T 69.0 1 | 342307 | 2STEPHENSBRG | 342403 | 2UPTON T | 1 | 69 | 320 | 35 | 39 | Base Case | 0 | 33.4 | - | 34.75 | 81.8 | 95.45 | 0 | 0.66905 | 30.1 | - | -14 | - | 0.994 | - | 0.9828 | - | 4.45 | -
25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 342307 2STEPHENSBRG 69.0 342403 2UPTON T 69.0 1 | 342307 | 2STEPHENSBRG | 342403 | 2UPTON T | 1 | 69 | 320 | 35 | 39 | EKPC_P1-2_BARR-SUMSH161_SRT-A | 12 | 33.4 | 36.8 | 36.74 | 83.22 | 94.36 | 5 | 0.67387 | 30.1 | 33.8 | -14 | -13.7 | 0.994 | 0.9922 | 0.9828 | 0.9761 | 4.45 | 4.88
25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1 | 324213 | 4BONNIEVILLE | 324447 | 2BONNIE KU | 1 | 138/69 | 363 | 33 | 40 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A | 21 | 25.8 | 37.5 | 12.64 | 95.45 | 93.68 | 1 | 0.73194 | -25.3 | -37.1 | 5 | 5 | 0.9738 | 0.9434 | 0.9665 | 0.9398 | 3.67 | 5.71
25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1 | 324213 | 4BONNIEVILLE | 324447 | 2BONNIE KU | 1 | 138/69 | 363 | 33 | 40 | EXT_B-69-18_SRT-A | 35 | 25.8 | 37.3 | 12.05 | 95.12 | 93.32 | 2 | 0.73203 | -25.3 | -37 | 5 | 5 | 0.9738 | 0.9437 | 0.9665 | 0.94 | 3.67 | 5.68
25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 3 | 132.2 | 142.5 | 100.11 | 92.2 | 93.13 | 2 | 0.8834 | 131.4 | 142.1 | -14.6 | -10 | 1 | 1 | 0.9974 | 0.9959 | 1.77 | 1.9
25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EXT_BB-1133_SRT-A | 28 | 132.2 | 139.3 | 93.4 | 89.94 | 91.08 | 3 | 0.88279 | 131.4 | 138.5 | -14.6 | -15.5 | 1 | 1 | 0.9974 | 0.9973 | 1.77 | 1.86
25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A | 21 | 132.2 | 139.2 | 93.4 | 89.86 | 90.98 | 4 | 0.88279 | 131.4 | 138.3 | -14.6 | -15.5 | 1 | 1 | 0.9974 | 0.9973 | 1.77 | 1.86
26 | EXT_B-138-111_SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 10 | 140 | 173 | 110.38 | 111.39 | 113.09 | 1 | 0.90461 | 139.1 | 172.1 | -15.7 | -17.6 | 1 | 1 | 0.9973 | 0.9964 | 1.87 | 2.31
26 | EXT_B-138-111_SRT-A | 342703 5CASEY CO 161 342769 5MARION CO 161 1 | 342703 | 5CASEY CO | 342769 | 5MARION CO | 1 | 161 | 320 | 148 | 153 | EKPC_P1-2_LIBJ-GAS161_SRT-A | 9 | 55.2 | 150.8 | 101.09 | 95.73 | 98.59 | 1 | 0.91932 | 48.9 | 145.9 | -25.7 | -37 | 1.0019 | 0.9977 | 1.0098 | 1.0037 | 1.62 | 4.65
26 | EXT_B-138-111_SRT-A | 342000 5GAS 161 342703 5CASEY CO 161 1 | 342000 | 5GAS | 342703 | 5CASEY CO | 1 | 161 | 320 | 148 | 153 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 7 | 77.2 | 145 | 96.78 | 91.92 | 94.77 | 1 | 0.94855 | 72.9 | 141.4 | -25.4 | -32.2 | 1 | 1 | 1.0019 | 1.0008 | 0.83 | 1.58
26 | EXT_B-138-111_SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EKPC_P1-2_COOP-ELIHU161_SRT-A | 2 | 140 | 143.1 | 95.57 | 92.9 | 93.53 | 2 | 0.891 | 139.1 | 142.8 | -15.7 | -8.6 | 1 | 1 | 0.9973 | 0.9955 | 1.87 | 1.91
26 | EXT_B-138-111_SRT-A | 342307 2STEPHENSBRG 69.0 342403 2UPTON T 69.0 1 | 342307 | 2STEPHENSBRG | 342403 | 2UPTON T | 1 | 69 | 320 | 35 | 39 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 25 | 12.7 | 35.6 | 85.66 | 89.02 | 91.19 | 1 | 0.67295 | 11 | 32.3 | -6.3 | -14.2 | 1.0015 | 0.9928 | 0.999 | 0.9795 | 1.67 | 4.73
27 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A_27 | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 10 | 139.5 | 172.8 | 110.38 | 111.29 | 112.97 | 1 | 0.90461 | 138.7 | 172 | -15.4 | -17.3 | 1 | 1 | 0.9973 | 0.9964 | 1.87 | 2.31
27 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A_27 | 342703 5CASEY CO 161 342769 5MARION CO 161 1 | 342703 | 5CASEY CO | 342769 | 5MARION CO | 1 | 161 | 320 | 148 | 153 | EKPC_P1-2_LIBJ-GAS161_SRT-A | 9 | 56.1 | 149.9 | 101.09 | 96.17 | 97.99 | 1 | 0.91929 | 49.9 | 145.4 | -25.9 | -36.2 | 1.0019 | 0.9992 | 1.0098 | 1.0048 | 1.65 | 4.61
27 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A_27 | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 3 | 139.5 | 149.6 | 100.11 | 96.86 | 97.81 | 2 | 0.89038 | 138.7 | 149.3 | -15.4 | -10.6 | 1 | 1 | 0.9973 | 0.9957 | 1.87 | 2
27 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A_27 | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | Base Case | 0 | 139.5 | - | 96.55 | 93.08 | 94.29 | 0 | 0.88793 | 138.7 | - | -15.4 | - | 1 | - | 0.9973 | - | 1.87 | -
27 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A_27 | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 15 | 139.5 | 142.9 | 95.51 | 92.4 | 93.43 | 3 | 0.88849 | 138.7 | 142.1 | -15.4 | -15.2 | 1 | 1 | 0.9973 | 0.9971 | 1.87 | 1.91
27 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A_27 | 342307 2STEPHENSBRG 69.0 342403 2UPTON T 69.0 1 | 342307 | 2STEPHENSBRG | 342403 | 2UPTON T | 1 | 69 | 320 | 35 | 39 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 25 | 12.6 | 35.5 | 85.66 | 88.74 | 90.9 | 1 | 0.67295 | 11 | 32.2 | -6.3 | -14.2 | 1.0015 | 0.9928 | 0.999 | 0.9795 | 1.66 | 4.72
28 | EXT_BB-1133_SRT-A | 342307 2STEPHENSBRG 69.0 342403 2UPTON T 69.0 1 | 342307 | 2STEPHENSBRG | 342403 | 2UPTON T | 1 | 69 | 320 | 35 | 39 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 25 | 8.7 | 43 | 85.66 | 109.43 | 110.17 | 1 | 0.71787 | 8.1 | 40.5 | -3.1 | -12.7 | 0.9984 | 0.9882 | 0.9933 | 0.9621 | 1.12 | 5.66
28 | EXT_BB-1133_SRT-A | 342307 2STEPHENSBRG 69.0 342403 2UPTON T 69.0 1 | 342307 | 2STEPHENSBRG | 342403 | 2UPTON T | 1 | 69 | 320 | 35 | 39 | EXT_B-138-115_SRT-A | 30 | 8.7 | 37 | 69.47 | 96.12 | 94.76 | 2 | 0.72071 | 8.1 | 36.7 | -3.1 | -8.2 | 0.9984 | 1.0175 | 0.9933 | 0.9875 | 1.12 | 4.6
28 | EXT_BB-1133_SRT-A | 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1 | 324213 | 4BONNIEVILLE | 324447 | 2BONNIE KU | 1 | 138/69 | 363 | 33 | 40 | EXT_B-138-115_SRT-A | 30 | 4.2 | 36.4 | 65.55 | 90.67 | 90.95 | 1 | 0.73225 | -3.3 | -36 | -2.4 | 5.5 | 0.9742 | 0.9515 | 0.9805 | 0.9463 | 0.45 | 5.44
30 | EXT_B-138-115_SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EKPC_P1-3_MAR 161/138_SRT-A | 16 | 131.2 | 158.7 | 105.73 | 102.55 | 103.72 | 1 | 0.89992 | 130.4 | 157.8 | -14.5 | -16.6 | 1 | 1 | 0.9974 | 0.9968 | 1.76 | 2.12
30 | EXT_B-138-115_SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EKPC_P1-2_MAR-KU LEB138 | 1 | 131.2 | 158.7 | 105.72 | 102.54 | 103.72 | 2 | 0.89992 | 130.4 | 157.8 | -14.5 | -16.6 | 1 | 1 | 0.9974 | 0.9968 | 1.76 | 2.12
30 | EXT_B-138-115_SRT-A | 342703 5CASEY CO 161 342769 5MARION CO 161 1 | 342703 | 5CASEY CO | 342769 | 5MARION CO | 1 | 161 | 320 | 148 | 153 | EKPC_P1-2_LIBJ-GAS161_SRT-A | 9 | 64.7 | 158.2 | 101.09 | 100.52 | 103.39 | 1 | 0.91634 | 59.1 | 153.5 | -26.7 | -36.6 | 1.0017 | 0.9977 | 1.0091 | 1.003 | 1.93 | 4.88
30 | EXT_B-138-115_SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 10 | 131.2 | 154.7 | 110.38 | 100 | 101.09 | 3 | 0.89215 | 130.4 | 153.8 | -14.5 | -16.1 | 1 | 1 | 0.9974 | 0.9968 | 1.76 | 2.07
30 | EXT_B-138-115_SRT-A | 342307 2STEPHENSBRG 69.0 342403 2UPTON T 69.0 1 | 342307 | 2STEPHENSBRG | 342403 | 2UPTON T | 1 | 69 | 320 | 35 | 39 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A | 21 | 27.1 | 39.3 | 25.13 | 94.51 | 100.67 | 1 | 0.72071 | 24.5 | 38.9 | -11.4 | -8.9 | 0.9972 | 1.017 | 0.9877 | 0.9858 | 3.59 | 4.9
30 | EXT_B-138-115_SRT-A | 342307 2STEPHENSBRG 69.0 342403 2UPTON T 69.0 1 | 342307 | 2STEPHENSBRG | 342403 | 2UPTON T | 1 | 69 | 320 | 35 | 39 | EXT_B-69-18_SRT-A | 35 | 27.1 | 38.6 | 23.47 | 92.84 | 98.86 | 2 | 0.72084 | 24.5 | 38.3 | -11.4 | -8.6 | 0.9972 | 1.0173 | 0.9877 | 0.9863 | 3.59 | 4.81
30 | EXT_B-138-115_SRT-A | 342000 5GAS 161 342703 5CASEY CO 161 1 | 342000 | 5GAS | 342703 | 5CASEY CO | 1 | 161 | 320 | 148 | 153 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 7 | 85.6 | 151.2 | 96.78 | 96.11 | 98.86 | 1 | 0.94755 | 81.6 | 148 | -25.8 | -31.3 | 1 | 1 | 1.0017 | 1.0004 | 0.92 | 1.64
30 | EXT_B-138-115_SRT-A | 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1 | 324213 | 4BONNIEVILLE | 324447 | 2BONNIE KU | 1 | 138/69 | 363 | 33 | 40 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A | 21 | 26.2 | 38.8 | 12.64 | 98.4 | 96.97 | 1 | 0.73225 | -25.6 | -38.2 | 5.5 | 6.5 | 0.9768 | 0.9505 | 0.9684 | 0.9436 | 3.7 | 5.82
30 | EXT_B-138-115_SRT-A | 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1 | 324213 | 4BONNIEVILLE | 324447 | 2BONNIE KU | 1 | 138/69 | 363 | 33 | 40 | EXT_B-69-18_SRT-A | 35 | 26.2 | 38.7 | 12.05 | 98.11 | 96.66 | 2 | 0.73234 | -25.6 | -38.1 | 5.5 | 6.5 | 0.9768 | 0.951 | 0.9684 | 0.9439 | 3.7 | 5.79
30 | EXT_B-138-115_SRT-A | 342307 2STEPHENSBRG 69.0 342403 2UPTON T 69.0 1 | 342307 | 2STEPHENSBRG | 342403 | 2UPTON T | 1 | 69 | 320 | 35 | 39 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A | 17 | 27.1 | 36.9 | 22.33 | 88.39 | 94.71 | 3 | 0.72071 | 24.5 | 36.6 | -11.4 | -8.4 | 0.9972 | 1.0175 | 0.9877 | 0.9878 | 3.59 | 4.6
30 | EXT_B-138-115_SRT-A | 342307 2STEPHENSBRG 69.0 342403 2UPTON T 69.0 1 | 342307 | 2STEPHENSBRG | 342403 | 2UPTON T | 1 | 69 | 320 | 35 | 39 | EXT_BB-1133_SRT-A | 28 | 27.1 | 36.9 | 22.37 | 88.37 | 94.7 | 4 | 0.72071 | 24.5 | 36.6 | -11.4 | -8.4 | 0.9972 | 1.0176 | 0.9877 | 0.9879 | 3.59 | 4.6
30 | EXT_B-138-115_SRT-A | 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1 | 326975 | 5CEDAR GRV | 342700 | 5BULLITT CO | 1 | 161 | 363/320 | 219 | 277 | Base Case | 0 | 204.3 | - | 91.13 | 93.07 | 93.27 | 0 | 0.87729 | 203.8 | - | -4.5 | - | 0.9981 | - | 0.9927 | - | 2.26 | -
30 | EXT_B-138-115_SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 3 | 131.2 | 141.5 | 100.11 | 91.56 | 92.5 | 4 | 0.88342 | 130.4 | 141.2 | -14.5 | -9.8 | 1 | 1 | 0.9974 | 0.9959 | 1.76 | 1.89
30 | EXT_B-138-115_SRT-A | 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1 | 324213 | 4BONNIEVILLE | 324447 | 2BONNIE KU | 1 | 138/69 | 363 | 33 | 40 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A | 17 | 26.2 | 36.4 | 10.42 | 92.3 | 91 | 3 | 0.73225 | -25.6 | -36 | 5.5 | 5.5 | 0.9768 | 0.952 | 0.9684 | 0.9466 | 3.7 | 5.44
30 | EXT_B-138-115_SRT-A | 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1 | 324213 | 4BONNIEVILLE | 324447 | 2BONNIE KU | 1 | 138/69 | 363 | 33 | 40 | EXT_BB-1133_SRT-A | 28 | 26.2 | 36.4 | 10.43 | 92.26 | 90.96 | 4 | 0.73225 | -25.6 | -36 | 5.5 | 5.6 | 0.9768 | 0.9521 | 0.9684 | 0.9467 | 3.7 | 5.44
30 | EXT_B-138-115_SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EXT_BB-1133_SRT-A | 28 | 131.2 | 138.8 | 93.4 | 89.58 | 90.74 | 5 | 0.8828 | 130.4 | 138 | -14.5 | -15.5 | 1 | 1 | 0.9974 | 0.9973 | 1.76 | 1.86
33 | EXT_324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1 _SRT-A | 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1 | 326975 | 5CEDAR GRV | 342700 | 5BULLITT CO | 1 | 161 | 363/320 | 219 | 277 | Base Case | 0 | 204.6 | - | 91.13 | 93.3 | 93.44 | 0 | 0.87788 | 204.3 | - | -5.2 | - | 0.9988 | - | 0.9935 | - | 2.27 | -
33 | EXT_324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1 _SRT-A | 324191 2LEBANON E T 69.0 324603 2LEBANON CIT 69.0 1 | 324191 | 2LEBANON E T | 324603 | 2LEBANON CIT | 1 | 69 | 363 | 52 | 66 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 10 | 36.8 | 59.8 | 88.42 | 90.09 | 90.57 | 1 | 0.97611 | 36.5 | 59.9 | -6.3 | -4.7 | 1.0066 | 1.0043 | 1.005 | 1.0007 | 0.33 | 0.52
33 | EXT_324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1 _SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EXT_B-138-111_SRT-A | 26 | 142 | 138.2 | 93.4 | 89.18 | 90.33 | 1 | 0.88802 | 141.1 | 137.3 | -15.7 | -15.5 | 1 | 1 | 0.9972 | 0.9974 | 1.9 | 1.85
34 | EXT_326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1 _SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EXT_B-138-111_SRT-A | 26 | 142.3 | 138.7 | 93.4 | 89.5 | 90.65 | 1 | 0.88801 | 141.4 | 137.8 | -15.7 | -15.6 | 1 | 1 | 0.9972 | 0.9974 | 1.9 | 1.86
35 | EXT_B-69-18_SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 10 | 155.1 | 265.9 | 110.38 | 172.76 | 173.79 | 1 | 0.95705 | 154.2 | 265.3 | -16.4 | -17.8 | 1 | 1 | 0.9969 | 0.9931 | 2.07 | 3.56
35 | EXT_B-69-18_SRT-A | 324557 2GR RVR PLAZ 69.0 324829 2CAMPBELVIL1 69.0 1 | 324557 | 2GR RVR PLAZ | 324829 | 2CAMPBELVIL1 | 1 | 69 | 363 | 39 | 39 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 15 | 2.9 | 57.5 | 45.49 | 139.88 | 147.5 | 1 | 0.99061 | -0.4 | 53.5 | 2.9 | 6.4 | 0.9828 | 0.9367 | 0.9826 | 0.9338 | 0.01 | 0.27
35 | EXT_B-69-18_SRT-A | 324557 2GR RVR PLAZ 69.0 324829 2CAMPBELVIL1 69.0 1 | 324557 | 2GR RVR PLAZ | 324829 | 2CAMPBELVIL1 | 1 | 69 | 363 | 39 | 39 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 10 | 2.9 | 55.5 | 33.72 | 134.16 | 142.3 | 2 | 0.99066 | -0.4 | 52.4 | 2.9 | 8.6 | 0.9828 | 0.9565 | 0.9826 | 0.9535 | 0.01 | 0.25
35 | EXT_B-69-18_SRT-A | 324557 2GR RVR PLAZ 69.0 324830 2CAMPBELV EK 69.0 1 | 324557 | 2GR RVR PLAZ | 324830 | 2CAMPBELV EK | 1 | 69 | 363 | 47 | 47 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 15 | 16.1 | 65.6 | 55.13 | 131.7 | 139.59 | 1 | 0.98042 | -7 | -60.8 | 14.2 | 8.8 | 0.9828 | 0.9367 | 0.9809 | 0.9408 | 0.14 | 0.73
35 | EXT_B-69-18_SRT-A | 324557 2GR RVR PLAZ 69.0 324830 2CAMPBELV EK 69.0 1 | 324557 | 2GR RVR PLAZ | 324830 | 2CAMPBELV EK | 1 | 69 | 363 | 47 | 47 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 10 | 16.1 | 62.9 | 42.55 | 126.95 | 133.86 | 2 | 0.98053 | -7 | -59.7 | 14.2 | 7.4 | 0.9828 | 0.9565 | 0.9809 | 0.9606 | 0.14 | 0.68
35 | EXT_B-69-18_SRT-A | 342307 2STEPHENSBRG 69.0 342403 2UPTON T 69.0 1 | 342307 | 2STEPHENSBRG | 342403 | 2UPTON T | 1 | 69 | 320 | 35 | 39 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 25 | 9.2 | 44.1 | 85.66 | 113.21 | 113.17 | 1 | 0.718 | 8.4 | 42.7 | -3.7 | -11.3 | 0.9959 | 1.002 | 0.9916 | 0.9708 | 1.19 | 5.68
35 | EXT_B-69-18_SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 15 | 155.1 | 170 | 95.51 | 110.01 | 111.14 | 2 | 0.90409 | 154.2 | 169.2 | -16.4 | -17.4 | 1 | 1 | 0.9969 | 0.9965 | 2.07 | 2.27
35 | EXT_B-69-18_SRT-A | 324554 2GRENSBRG KU 69.0 341563 2GREEN CO 69.0 1 | 324554 | 2GRENSBRG KU | 341563 | 2GREEN CO | 1 | 69 | 363/320 | 52 | 66 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 15 | 32.2 | 72.6 | 67.34 | 106.53 | 109.99 | 1 | 0.97448 | -31.8 | -71.7 | 3.7 | -3 | 0.9939 | 0.988 | 0.9955 | 0.9933 | 0.26 | 0.54
35 | EXT_B-69-18_SRT-A | 342769 5MARION CO 161 342775 5MARION IP T 161 1 | 342769 | 5MARION CO | 342775 | 5MARION IP T | 1 | 161 | 320 | 186 | 210 | EKPC_P1-2_LIBJ-GAS161_SRT-A | 9 | 127.4 | 225.1 | 62.41 | 108.33 | 107.21 | 1 | 0.98369 | 128 | 225.7 | 13.3 | 4.1 | 1.0102 | 1.0025 | 1.0061 | 0.9976 | 0.82 | 1.49
35 | EXT_B-69-18_SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 3 | 155.1 | 163.7 | 100.11 | 106 | 106.99 | 3 | 0.90276 | 154.2 | 163.3 | -16.4 | -11.2 | 1 | 1 | 0.9969 | 0.9953 | 2.07 | 2.18
35 | EXT_B-69-18_SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | Base Case | 0 | 155.1 | - | 96.55 | 103.4 | 104.77 | 0 | 0.90068 | 154.2 | - | -16.4 | - | 1 | - | 0.9969 | - | 2.07 | -
35 | EXT_B-69-18_SRT-A | 324554 2GRENSBRG KU 69.0 324830 2CAMPBELV EK 69.0 1 | 324554 | 2GRENSBRG KU | 324830 | 2CAMPBELV EK | 1 | 69 | 363 | 52 | 66 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 15 | 27.7 | 68 | 60.31 | 98.68 | 102.97 | 1 | 0.7295 | 27.2 | 67.1 | -4 | 2.7 | 0.9939 | 0.988 | 0.9809 | 0.9408 | 2.4 | 5.67
35 | EXT_B-69-18_SRT-A | 341342 2CONTOWN T 69.0 341761 2LIBERTY J 69.0 1 | 341342 | 2CONTOWN T | 341761 | 2LIBERTY J | 1 | 69 | 320 | 53 | 63 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 7 | 34.9 | 63.5 | 85.11 | 99.35 | 100.82 | 1 | 0.92875 | -33.5 | -61.4 | 9.2 | 15.7 | 0.9962 | 0.9984 | 0.9999 | 1.006 | 0.94 | 1.69
35 | EXT_B-69-18_SRT-A | 324554 2GRENSBRG KU 69.0 341563 2GREEN CO 69.0 1 | 324554 | 2GRENSBRG KU | 341563 | 2GREEN CO | 1 | 69 | 363/320 | 52 | 66 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 10 | 32.2 | 65.7 | 58.85 | 93.14 | 99.56 | 2 | 0.9752 | -31.8 | -65.9 | 3.7 | -9.8 | 0.9939 | 1.0133 | 0.9955 | 1.019 | 0.26 | 0.45
35 | EXT_B-69-18_SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EKPC_P1-2_COOP-LAUREL161_SRT-A | 4 | 155.1 | 151.5 | 89.73 | 97.23 | 99.05 | 4 | 0.90103 | 154.2 | 150 | -16.4 | -21.5 | 1 | 1 | 0.9969 | 0.9982 | 2.07 | 2.03
35 | EXT_B-69-18_SRT-A | 324736 2SPRINGFL KU 69.0 341935 2N SPRINGFLD 69.0 1 | 324736 | 2SPRINGFL KU | 341935 | 2N SPRINGFLD | 1 | 69 | 363/320 | 49 | 50 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 10 | 30.6 | 49.5 | 33.86 | 95.54 | 98.97 | 1 | 0.89125 | -28.9 | -46.7 | -3.3 | -4.1 | 0.951 | 0.9479 | 0.9731 | 0.9829 | 1.59 | 2.59
35 | EXT_B-69-18_SRT-A | 342307 2STEPHENSBRG 69.0 342403 2UPTON T 69.0 1 | 342307 | 2STEPHENSBRG | 342403 | 2UPTON T | 1 | 69 | 320 | 35 | 39 | EXT_B-138-115_SRT-A | 30 | 9.2 | 38.6 | 69.47 | 99.76 | 98.86 | 2 | 0.72084 | 8.4 | 38.3 | -3.7 | -8.6 | 0.9959 | 1.0173 | 0.9916 | 0.9863 | 1.19 | 4.81
35 | EXT_B-69-18_SRT-A | 324736 2SPRINGFL KU 69.0 341935 2N SPRINGFLD 69.0 1 | 324736 | 2SPRINGFL KU | 341935 | 2N SPRINGFLD | 1 | 69 | 363/320 | 49 | 50 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 15 | 30.6 | 49.3 | 21.68 | 90.79 | 98.51 | 2 | 0.89063 | -28.9 | -45.7 | -3.3 | -7.3 | 0.951 | 0.9395 | 0.9731 | 0.9772 | 1.59 | 2.45
35 | EXT_B-69-18_SRT-A | 341342 2CONTOWN T 69.0 342067 2PHIL 69.0 1 | 341342 | 2CONTOWN T | 342067 | 2PHIL | 1 | 69 | 320 | 57 | 63 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 7 | 32.8 | 61.4 | 81.78 | 94.96 | 97.47 | 1 | 0.8486 | 31.2 | 59.2 | -9.5 | -16 | 0.9962 | 0.9984 | 0.9903 | 0.9864 | 1.9 | 3.54
35 | EXT_B-69-18_SRT-A | 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1 | 324213 | 4BONNIEVILLE | 324447 | 2BONNIE KU | 1 | 138/69 | 363 | 33 | 40 | EXT_B-138-115_SRT-A | 30 | 4.8 | 38.7 | 65.55 | 96.26 | 96.66 | 1 | 0.73234 | -4.3 | -38.1 | -1.9 | 6.5 | 0.9738 | 0.951 | 0.9791 | 0.9439 | 0.61 | 5.79
35 | EXT_B-69-18_SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EKPC_P1-2_COOP 161 TIE_SRT-A | 6 | 155.1 | 147.4 | 87.2 | 95.34 | 96.31 | 5 | 0.90464 | 154.2 | 146.9 | -16.4 | -11.9 | 1 | 1 | 0.9969 | 0.9961 | 2.07 | 1.97
35 | EXT_B-69-18_SRT-A | 341143 2BLUE G PW T 69.0 342508 2WOODLAWN 69.0 1 | 341143 | 2BLUE G PW T | 342508 | 2WOODLAWN | 1 | 69 | 320 | 41 | 46 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 10 | 35.8 | 44.2 | 42.29 | 87.18 | 96.16 | 1 | 0.90187 | 33.3 | 40.7 | -11 | -15.7 | 0.9805 | 0.9864 | 0.9779 | 0.9844 | 1.13 | 1.39
35 | EXT_B-69-18_SRT-A | 341494 2FREDRIKBG T 69.0 342508 2WOODLAWN 69.0 1 | 341494 | 2FREDRIKBG T | 342508 | 2WOODLAWN | 1 | 69 | 320 | 41 | 46 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 10 | 35.8 | 44.2 | 42.19 | 87.18 | 96.1 | 1 | 0.88205 | -32.6 | -39.6 | 12.2 | 17.6 | 0.9745 | 0.9818 | 0.9779 | 0.9844 | 1.37 | 1.7
35 | EXT_B-69-18_SRT-A | 341407 2E BARDSTOWN 69.0 342019 2OWENS IL J 69.0 1 | 341407 | 2E BARDSTOWN | 342019 | 2OWENS IL J | 1 | 69 | 320 | 57 | 63 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 10 | 53.2 | 60.5 | 55 | 94.31 | 96.06 | 1 | 0.98786 | 52.4 | 59.9 | 0.8 | -3.6 | 0.9866 | 0.9922 | 0.9847 | 0.9903 | 0.18 | 0.22
35 | EXT_B-69-18_SRT-A | 341407 2E BARDSTOWN 69.0 342019 2OWENS IL J 69.0 1 | 341407 | 2E BARDSTOWN | 342019 | 2OWENS IL J | 1 | 69 | 320 | 57 | 63 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 15 | 53.2 | 60.2 | 57.97 | 93.2 | 95.56 | 2 | 0.98786 | 52.4 | 59.6 | 0.8 | -2.2 | 0.9866 | 0.9899 | 0.9847 | 0.9879 | 0.18 | 0.21
35 | EXT_B-69-18_SRT-A | 341143 2BLUE G PW T 69.0 342508 2WOODLAWN 69.0 1 | 341143 | 2BLUE G PW T | 342508 | 2WOODLAWN | 1 | 69 | 320 | 41 | 46 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 15 | 35.8 | 43.5 | 46.76 | 85.65 | 94.55 | 2 | 0.90183 | 33.3 | 40.3 | -11 | -14.3 | 0.9805 | 0.9837 | 0.9779 | 0.981 | 1.13 | 1.37
35 | EXT_B-69-18_SRT-A | 341494 2FREDRIKBG T 69.0 342508 2WOODLAWN 69.0 1 | 341494 | 2FREDRIKBG T | 342508 | 2WOODLAWN | 1 | 69 | 320 | 41 | 46 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 15 | 35.8 | 43.5 | 46.66 | 85.65 | 94.49 | 2 | 0.88199 | -32.6 | -39.3 | 12.2 | 16.1 | 0.9745 | 0.9777 | 0.9779 | 0.981 | 1.37 | 1.67
35 | EXT_B-69-18_SRT-A | 324479 2CAMPBELVL T 69.0 324751 2TAYLOR CO 69.0 1 | 324479 | 2CAMPBELVL T | 324751 | 2TAYLOR CO | 1 | 69 | 363 | 52 | 66 | Base Case | 0 | 49 | - | 19.68 | 92.09 | 94.24 | 0 | 0.99216 | -47.9 | - | -5.1 | - | 0.9826 | - | 0.9844 | - | 0.16 | -
35 | EXT_B-69-18_SRT-A | 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1 | 324213 | 4BONNIEVILLE | 324447 | 2BONNIE KU | 1 | 138/69 | 363 | 33 | 40 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 25 | 4.8 | 37.3 | 64.59 | 91.65 | 93.35 | 2 | 0.73203 | -4.3 | -37 | -1.9 | 4.7 | 0.9738 | 0.9382 | 0.9791 | 0.9353 | 0.61 | 5.75
35 | EXT_B-69-18_SRT-A | 341407 2E BARDSTOWN 69.0 342019 2OWENS IL J 69.0 1 | 341407 | 2E BARDSTOWN | 342019 | 2OWENS IL J | 1 | 69 | 320 | 57 | 63 | Base Case | 0 | 53.2 | - | 64.08 | 91.83 | 93.27 | 0 | 0.9877 | 52.4 | - | 0.8 | - | 0.9866 | - | 0.9847 | - | 0.18 | -
35 | EXT_B-69-18_SRT-A | 324554 2GRENSBRG KU 69.0 324830 2CAMPBELV EK 69.0 1 | 324554 | 2GRENSBRG KU | 324830 | 2CAMPBELV EK | 1 | 69 | 363 | 52 | 66 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 10 | 27.7 | 61.2 | 51.81 | 85.3 | 92.79 | 2 | 0.73719 | 27.2 | 61.3 | -4 | 9.5 | 0.9939 | 1.0133 | 0.9809 | 0.9606 | 2.4 | 4.65
35 | EXT_B-69-18_SRT-A | 341761 2LIBERTY J 69.0 341767 2LIBERTYKU T 69.0 1 | 341761 | 2LIBERTY J | 341767 | 2LIBERTYKU T | 1 | 69 | 320 | 53 | 66 | EKPC_P1-2_LIBJ-GAS161_SRT-A | 9 | 8.6 | 61.2 | 65.86 | 91.04 | 92.77 | 1 | 0.92724 | -6.9 | -56.3 | 5.1 | 20.8 | 0.9999 | 0.9817 | 0.9983 | 0.9795 | 0.25 | 1.92
35 | EXT_B-69-18_SRT-A | 342769 5MARION CO 161 342775 5MARION IP T 161 1 | 342769 | 5MARION CO | 342775 | 5MARION IP T | 1 | 161 | 320 | 186 | 210 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 7 | 127.4 | 192.8 | 56.35 | 92.17 | 91.8 | 2 | 0.97852 | 128 | 194.4 | 13.3 | 8.7 | 1.0102 | 1.0098 | 1.0061 | 1.0049 | 0.82 | 1.26
36 | EXT_B-69-19_SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 3 | 138.6 | 148.3 | 100.11 | 95.9 | 96.91 | 1 | 0.88502 | 137.7 | 147.9 | -15.5 | -10.9 | 1 | 1 | 0.9973 | 0.9959 | 1.85 | 1.98
36 | EXT_B-69-19_SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | Base Case | 0 | 138.6 | - | 96.55 | 92.44 | 93.64 | 0 | 0.8828 | 137.7 | - | -15.5 | - | 1 | - | 0.9973 | - | 1.85 | -
36 | EXT_B-69-19_SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EKPC_P1-2_COOP-ELIHU161_SRT-A | 2 | 138.6 | 142.2 | 95.57 | 92.32 | 92.95 | 2 | 0.8866 | 137.7 | 142 | -15.5 | -8.4 | 1 | 1 | 0.9973 | 0.9955 | 1.85 | 1.89
36 | EXT_B-69-19_SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 15 | 138.6 | 141.8 | 95.51 | 91.69 | 92.71 | 3 | 0.88332 | 137.7 | 141 | -15.5 | -15.3 | 1 | 1 | 0.9973 | 0.9971 | 1.85 | 1.9
36 | EXT_B-69-19_SRT-A | 342307 2STEPHENSBRG 69.0 342403 2UPTON T 69.0 1 | 342307 | 2STEPHENSBRG | 342403 | 2UPTON T | 1 | 69 | 320 | 35 | 39 | EKPC_P1-2_BARR-SUMSH161_SRT-A | 12 | 27.9 | 35.2 | 36.74 | 84.34 | 90.17 | 1 | 0.79555 | 26.5 | 34.5 | -8.9 | -6.2 | 1.0019 | 0.9971 | 0.9851 | 0.9651 | 3.61 | 4.39
37 | EXT_BB-1066_SRT-A | 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1 | 326975 | 5CEDAR GRV | 342700 | 5BULLITT CO | 1 | 161 | 363/320 | 219 | 277 | Base Case | 0 | 205.1 | - | 91.13 | 93.53 | 93.67 | 0 | 0.87788 | 204.8 | - | -5.1 | - | 0.9988 | - | 0.9935 | - | 2.27 | -
37 | EXT_BB-1066_SRT-A | 324191 2LEBANON E T 69.0 324603 2LEBANON CIT 69.0 1 | 324191 | 2LEBANON E T | 324603 | 2LEBANON CIT | 1 | 69 | 363 | 52 | 66 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 10 | 36.9 | 59.8 | 88.42 | 90.17 | 90.66 | 1 | 0.97611 | 36.6 | 59.9 | -6.3 | -4.7 | 1.0066 | 1.0043 | 1.0049 | 1.0007 | 0.33 | 0.52
37 | EXT_BB-1066_SRT-A | 342000 5GAS 161 342760 5LIBERTY J 161 1 | 342000 | 5GAS | 342760 | 5LIBERTY J | 1 | 161 | 320 | 148 | 153 | EXT_B-138-111_SRT-A | 26 | 142 | 138.2 | 93.4 | 89.2 | 90.34 | 1 | 0.88802 | 141.2 | 137.3 | -15.7 | -15.5 | 1 | 1 | 0.9972 | 0.9974 | 1.9 | 1.85

## VoltViol
EKPC N-1-1 AC Voltage Result [TARA Ver 2201.2.0.0 64-bit - Sat Aug 13 07:58:26 2022]
Loadflow Case: C:\Users\03419\Desktop\2022 Gas Study\Alt 3A\2032S_gas_alt#3a_212mw.raw
Study Data File: C:\Users\03419\Desktop\2022 Gas Study\2022 series_sub_EKPC-LGEE.sub
Contingency File: C:\Users\03419\Desktop\2022 Gas Study\Option 3A N-1-1 con file.con (total 37 contingencies)/ First-Level Contingency File: C:\Users\03419\Desktop\2022 Gas Study\Option 3A N-1-1 con file.con (total 37 contingencies)
Monitor File: C:\Users\03419\Desktop\2022 Gas Study\2022 series_mon_EKPC-LGEE.mon (N-0-1<->N-1-1:0.20%/N-1-0<->N-1-1:0.20% voltage change cutoff)
Exclude File: not provided
Solution Options (Pre/Post Contingency): Shunts[All Enabled/All Enabled] PAR[Adjusted/Fixed] XFMR Tap[Adjusted/Adjusted] Area Interchange [Disabled/Disabled]
First Level Scenario Index | First Level Scenario | Bus # | Bus Name | Base kV | Area | Bus Type | Pgen | Pload | G Shunt | B Shunt | Min Volt Limit | Max Volt Limit | %Vdrop Limit | %Vrise Limit | Cont Name | Cont ID | Orig Case Cont Volt | Base Volt | Cont Volt | %Vdrop | Vmag Violation | # of Branches | Radial Index | Max MW Flow
9 | EKPC_P1-2_LIBJ-GAS161_SRT-A | 324605 | 2LEBANON EK | 69 | 363 | Load | 0 | 12.5 | 0 | 0 | 0.94 | 1.06 | - | - | EXT_B-69-18_SRT-A | 35 | 0.9419 | 1.004 | 0.9397 | 6.426 | WLow | 2 | 0.9786 | 27.6
10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 325020 | 2LEBANON E | 69 | 363 | Load | 0 | 14 | 0 | 0 | 0.94 | 1.06 | - | - | EXT_B-69-18_SRT-A | 35 | 0.9381 | 1.0052 | 0.924 | 8.118 | WLow | 1 | 1 | 14
10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 324889 | 2LEBANON SO | 69 | 363 | Load | 0 | 11.4 | 0 | 0 | 0.94 | 1.06 | - | - | EXT_B-69-18_SRT-A | 35 | 0.943 | 0.9951 | 0.9246 | 7.049 | WLow | 2 | 0.7339 | 14.7
10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 324605 | 2LEBANON EK | 69 | 363 | Load | 0 | 12.5 | 0 | 0 | 0.94 | 1.06 | - | - | EXT_B-69-18_SRT-A | 35 | 0.9419 | 0.999 | 0.9249 | 7.41 | WLow | 2 | 0.9811 | 12.5
10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 324604 | 2LEBANON IND | 69 | 363 | Load | 0 | 2.4 | 0 | 0 | 0.94 | 1.06 | - | - | EXT_B-69-18_SRT-A | 35 | 0.9392 | 1.0062 | 0.9252 | 8.109 | WLow | 2 | 1 | 16.5
10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 324603 | 2LEBANON CIT | 69 | 363 | Load | 0 | 6.2 | 0 | 14.4 | 0.94 | 1.06 | - | - | EXT_B-69-18_SRT-A | 35 | 0.9422 | 1.0009 | 0.9257 | 7.522 | WLow | 2 | 0.9832 | 15.8
10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 324191 | 2LEBANON E T | 69 | 363 | Load | 0 | 0 | 0 | 0 | 0.94 | 1.06 | - | - | EXT_B-69-18_SRT-A | 35 | 0.9416 | 1.0044 | 0.9264 | 7.805 | WLow | 2 | 0.972 | 15.8
10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 324606 | 2LEBANON | 69 | 363 | Load | 0 | 0 | 0 | 0 | 0.94 | 1.06 | - | - | EXT_B-69-18_SRT-A | 35 | 0.9407 | 1.0077 | 0.9267 | 8.096 | WLow | 3 | 0.8719 | 32.3
10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 324068 | 2E CAMPBELVL | 69 | 363 | Load | 0 | 7.2 | 0 | 0 | 0.94 | 1.06 | - | - | EXT_B-69-18_SRT-A | 35 | 0.9771 | 0.9567 | 0.9367 | 1.993 | WLow | 1 | 1 | 7.2
10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 324349 | 2CAMPBELVIL2 | 69 | 363 | Load | 0 | 7.5 | 0 | 0 | 0.94 | 1.06 | - | - | EXT_B-69-18_SRT-A | 35 | 0.9785 | 0.9581 | 0.9382 | 1.99 | WLow | 2 | 1 | 14.8
15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 324889 | 2LEBANON SO | 69 | 363 | Load | 0 | 11.4 | 0 | 0 | 0.94 | 1.06 | - | - | EXT_B-69-18_SRT-A | 35 | 0.943 | 0.9926 | 0.9109 | 8.167 | WLow | 2 | 0.7324 | 15.8
15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 324605 | 2LEBANON EK | 69 | 363 | Load | 0 | 12.5 | 0 | 0 | 0.94 | 1.06 | - | - | EXT_B-69-18_SRT-A | 35 | 0.9419 | 0.9963 | 0.9116 | 8.464 | WLow | 2 | 0.981 | 12.5
15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 325020 | 2LEBANON E | 69 | 363 | Load | 0 | 14 | 0 | 0 | 0.94 | 1.06 | - | - | EXT_B-69-18_SRT-A | 35 | 0.9381 | 1.0021 | 0.9121 | 9.007 | WLow | 1 | 1 | 14
15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 324603 | 2LEBANON CIT | 69 | 363 | Load | 0 | 6.2 | 0 | 14.4 | 0.94 | 1.06 | - | - | EXT_B-69-18_SRT-A | 35 | 0.9422 | 0.9981 | 0.9125 | 8.554 | WLow | 2 | 0.9831 | 14.8
15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 324604 | 2LEBANON IND | 69 | 363 | Load | 0 | 2.4 | 0 | 0 | 0.94 | 1.06 | - | - | EXT_B-69-18_SRT-A | 35 | 0.9392 | 1.0032 | 0.9132 | 8.997 | WLow | 2 | 1 | 16.5
15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 324191 | 2LEBANON E T | 69 | 363 | Load | 0 | 0 | 0 | 0 | 0.94 | 1.06 | - | - | EXT_B-69-18_SRT-A | 35 | 0.9416 | 1.0014 | 0.9137 | 8.775 | WLow | 2 | 0.9718 | 14.8
15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 324606 | 2LEBANON | 69 | 363 | Load | 0 | 0 | 0 | 0 | 0.94 | 1.06 | - | - | EXT_B-69-18_SRT-A | 35 | 0.9407 | 1.0046 | 0.9148 | 8.982 | WLow | 3 | 0.8712 | 31.3
15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 324068 | 2E CAMPBELVL | 69 | 363 | Load | 0 | 7.2 | 0 | 0 | 0.94 | 1.06 | - | - | EXT_B-69-18_SRT-A | 35 | 0.9771 | 0.9561 | 0.9175 | 3.865 | WLow | 1 | 1 | 7.2
15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 324349 | 2CAMPBELVIL2 | 69 | 363 | Load | 0 | 7.5 | 0 | 0 | 0.94 | 1.06 | - | - | EXT_B-69-18_SRT-A | 35 | 0.9785 | 0.9575 | 0.919 | 3.859 | WLow | 2 | 1 | 14.8
15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 326970 | 2MILE LAN EK | 69 | 363 | Load | 0 | 9.8 | 0 | 0 | 0.94 | 1.06 | - | - | EXT_B-69-18_SRT-A | 35 | 0.9808 | 0.9581 | 0.9208 | 3.735 | WLow | 1 | 1 | 9.8
15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 324479 | 2CAMPBELVL T | 69 | 363 | Load | 0 | 0 | 0 | 0 | 0.94 | 1.06 | - | - | EXT_B-69-18_SRT-A | 35 | 0.9827 | 0.9618 | 0.9234 | 3.84 | WLow | 3 | 0.7324 | 30.6
15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 325921 | 5TAYLOR CO | 161 | 363 | Load | 0 | 0 | 0 | 0 | 0.94 | 1.06 | - | - | EXT_B-69-18_SRT-A | 35 | 0.9963 | 0.9617 | 0.9244 | 3.727 | WLow | 1 | 1 | 0
15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 324751 | 2TAYLOR CO | 69 | 363 | Load | 0 | 0 | 0 | 0 | 0.94 | 1.06 | - | - | EXT_B-69-18_SRT-A | 35 | 0.9844 | 0.9617 | 0.9244 | 3.727 | WLow | 3 | 0.9931 | 30.7
15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 324641 | 2MILE LAN TP | 69 | 363 | Load | 0 | 0 | 0 | 0 | 0.94 | 1.06 | - | - | EXT_B-69-18_SRT-A | 35 | 0.9844 | 0.9617 | 0.9245 | 3.72 | WLow | 3 | 0.9603 | 40.5
15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 324829 | 2CAMPBELVIL1 | 69 | 363 | Load | 0 | 12.5 | 0 | 0 | 0.94 | 1.06 | - | - | EXT_B-69-18_SRT-A | 35 | 0.9826 | 0.9642 | 0.9338 | 3.038 | WLow | 2 | 0.9603 | 53.5
15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 324557 | 2GR RVR PLAZ | 69 | 363 | Load | 0 | 7.3 | 0 | 20.4 | 0.94 | 1.06 | - | - | EXT_B-69-18_SRT-A | 35 | 0.9828 | 0.9655 | 0.9367 | 2.872 | WLow | 2 | 0.9804 | 60.8
15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 324736 | 2SPRINGFL KU | 69 | 363 | Load | 0 | 13.8 | 0 | 0 | 0.94 | 1.06 | - | - | EXT_B-69-18_SRT-A | 35 | 0.9511 | 0.9987 | 0.9395 | 5.924 | WLow | 2 | 0.8712 | 45.7
17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A | 324362 | 2RIO | 69 | 363 | Load | 0 | 1.6 | 0 | 0 | 0.94 | 1.06 | - | - | EXT_B-138-115_SRT-A | 30 | 0.9596 | 0.9717 | 0.9267 | 4.502 | WLow | 1 | 1 | 1.6
17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A | 324050 | 2JONESVILLE | 69 | 363 | Load | 0 | 4.5 | 0 | 0 | 0.94 | 1.06 | - | - | EXT_B-138-115_SRT-A | 30 | 0.9613 | 0.9734 | 0.9285 | 4.494 | WLow | 2 | 1 | 6.1
17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A | 324362 | 2RIO | 69 | 363 | Load | 0 | 1.6 | 0 | 0 | 0.94 | 1.06 | - | - | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 25 | 0.9576 | 0.9717 | 0.9331 | 3.868 | Low | 1 | 1 | 1.6
17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A | 324050 | 2JONESVILLE | 69 | 363 | Load | 0 | 4.5 | 0 | 0 | 0.94 | 1.06 | - | - | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 25 | 0.9593 | 0.9734 | 0.9348 | 3.859 | Low | 2 | 1 | 6.1
17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A | 324800 | 4MERE TVA | 138 | 363 | Load | 0 | 61.9 | 0 | 30 | 0.94 | 1.06 | - | - | EXT_B-138-115_SRT-A | 30 | 0.9765 | 0.9829 | 0.9358 | 4.715 | WLow | 1 | 1 | 62.7
17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A | 324447 | 2BONNIE KU | 69 | 363 | Load | 0 | 1.5 | 0 | 0 | 0.94 | 1.06 | - | - | EXT_B-138-115_SRT-A | 30 | 0.9684 | 0.9805 | 0.9359 | 4.46 | WLow | 3 | 0.7322 | 43.9
17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A | 324213 | 4BONNIEVILLE | 138 | 363 | Load | 0 | 0 | 0 | 0 | 0.94 | 1.06 | - | - | EXT_B-138-115_SRT-A | 30 | 0.9769 | 0.9741 | 0.9383 | 3.579 | WLow | 3 | 0.7322 | 62.7
21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A | 324362 | 2RIO | 69 | 363 | Load | 0 | 1.6 | 0 | 0 | 0.94 | 1.06 | - | - | EXT_B-138-115_SRT-A | 30 | 0.9596 | 0.9717 | 0.9236 | 4.817 | WLow | 1 | 1 | 1.6
21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A | 324050 | 2JONESVILLE | 69 | 363 | Load | 0 | 4.5 | 0 | 0 | 0.94 | 1.06 | - | - | EXT_B-138-115_SRT-A | 30 | 0.9613 | 0.9734 | 0.9253 | 4.809 | WLow | 2 | 1 | 6.1
21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A | 324362 | 2RIO | 69 | 363 | Load | 0 | 1.6 | 0 | 0 | 0.94 | 1.06 | - | - | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 25 | 0.9576 | 0.9717 | 0.93 | 4.174 | Low | 1 | 1 | 1.6
21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A | 324050 | 2JONESVILLE | 69 | 363 | Load | 0 | 4.5 | 0 | 0 | 0.94 | 1.06 | - | - | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 25 | 0.9593 | 0.9734 | 0.9318 | 4.165 | Low | 2 | 1 | 6.1
21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A | 324447 | 2BONNIE KU | 69 | 363 | Load | 0 | 1.5 | 0 | 0 | 0.94 | 1.06 | - | - | EXT_B-138-115_SRT-A | 30 | 0.9684 | 0.9805 | 0.9328 | 4.773 | WLow | 3 | 0.7322 | 46.2
21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A | 324800 | 4MERE TVA | 138 | 363 | Load | 0 | 61.9 | 0 | 30 | 0.94 | 1.06 | - | - | EXT_B-138-115_SRT-A | 30 | 0.9765 | 0.9832 | 0.9341 | 4.912 | WLow | 1 | 1 | 62.7
21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A | 324270 | 4LEBANON WES | 138 | 363 | Load | 0 | 6.9 | 0 | 0 | 0.94 | 1.06 | - | - | EXT_B-138-115_SRT-A | 30 | 1.0029 | 0.9746 | 0.936 | 3.861 | WLow | 1 | 1 | 6.9
21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A | 324213 | 4BONNIEVILLE | 138 | 363 | Load | 0 | 0 | 0 | 0 | 0.94 | 1.06 | - | - | EXT_B-138-115_SRT-A | 30 | 0.9769 | 0.9751 | 0.9367 | 3.838 | WLow | 4 | 0.7322 | 69.6
21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A | 324447 | 2BONNIE KU | 69 | 363 | Load | 0 | 1.5 | 0 | 0 | 0.94 | 1.06 | - | - | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 25 | 0.9665 | 0.9805 | 0.9392 | 4.13 | Low | 3 | 0.7319 | 45
25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 324800 | 4MERE TVA | 138 | 363 | Load | 0 | 61.9 | 0 | 30 | 0.94 | 1.06 | - | - | EXT_MERE SWS_SRT-A | 29 | 0.9661 | 0.9732 | 0.9247 | 4.85 | WLow | 1 | 1 | 62.8
25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 324362 | 2RIO | 69 | 363 | Load | 0 | 1.6 | 0 | 0 | 0.94 | 1.06 | - | - | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A | 21 | 0.9717 | 0.9576 | 0.9306 | 2.704 | WLow | 1 | 1 | 1.6
25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 324362 | 2RIO | 69 | 363 | Load | 0 | 1.6 | 0 | 0 | 0.94 | 1.06 | - | - | EXT_B-69-18_SRT-A | 35 | 0.9704 | 0.9576 | 0.9308 | 2.681 | Low | 1 | 1 | 1.6
25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 324050 | 2JONESVILLE | 69 | 363 | Load | 0 | 4.5 | 0 | 0 | 0.94 | 1.06 | - | - | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A | 21 | 0.9733 | 0.9593 | 0.9323 | 2.698 | WLow | 2 | 1 | 6.1
25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 324050 | 2JONESVILLE | 69 | 363 | Load | 0 | 4.5 | 0 | 0 | 0.94 | 1.06 | - | - | EXT_B-69-18_SRT-A | 35 | 0.972 | 0.9593 | 0.9326 | 2.675 | Low | 2 | 1 | 6.1
25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 324362 | 2RIO | 69 | 363 | Load | 0 | 1.6 | 0 | 0 | 0.94 | 1.06 | - | - | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A | 17 | 0.9717 | 0.9576 | 0.9336 | 2.397 | Low | 1 | 1 | 1.6
25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 324362 | 2RIO | 69 | 363 | Load | 0 | 1.6 | 0 | 0 | 0.94 | 1.06 | - | - | EXT_BB-1133_SRT-A | 28 | 0.9717 | 0.9576 | 0.9337 | 2.388 | Low | 1 | 1 | 1.6
25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 324050 | 2JONESVILLE | 69 | 363 | Load | 0 | 4.5 | 0 | 0 | 0.94 | 1.06 | - | - | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A | 17 | 0.9733 | 0.9593 | 0.9354 | 2.392 | Low | 2 | 1 | 6.1
25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 324050 | 2JONESVILLE | 69 | 363 | Load | 0 | 4.5 | 0 | 0 | 0.94 | 1.06 | - | - | EXT_BB-1133_SRT-A | 28 | 0.9734 | 0.9593 | 0.9355 | 2.383 | Low | 2 | 1 | 6.1
25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 324447 | 2BONNIE KU | 69 | 363 | Load | 0 | 1.5 | 0 | 0 | 0.94 | 1.06 | - | - | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A | 21 | 0.9804 | 0.9665 | 0.9398 | 2.675 | WLow | 3 | 0.7319 | 44.9
25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 324447 | 2BONNIE KU | 69 | 363 | Load | 0 | 1.5 | 0 | 0 | 0.94 | 1.06 | - | - | EXT_B-69-18_SRT-A | 35 | 0.9791 | 0.9665 | 0.94 | 2.652 | Low | 3 | 0.732 | 44.8
28 | EXT_BB-1133_SRT-A | 324362 | 2RIO | 69 | 363 | Load | 0 | 1.6 | 0 | 0 | 0.94 | 1.06 | - | - | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 25 | 0.9576 | 0.9718 | 0.9238 | 4.798 | WLow | 1 | 1 | 1.6
28 | EXT_BB-1133_SRT-A | 324050 | 2JONESVILLE | 69 | 363 | Load | 0 | 4.5 | 0 | 0 | 0.94 | 1.06 | - | - | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 25 | 0.9593 | 0.9735 | 0.9256 | 4.79 | WLow | 2 | 1 | 6.1
28 | EXT_BB-1133_SRT-A | 324800 | 4MERE TVA | 138 | 363 | Load | 0 | 61.9 | 0 | 30 | 0.94 | 1.06 | - | - | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 25 | 0.9732 | 0.983 | 0.9295 | 5.345 | WLow | 1 | 1 | 62.7
28 | EXT_BB-1133_SRT-A | 324213 | 4BONNIEVILLE | 138 | 363 | Load | 0 | 0 | 0 | 0 | 0.94 | 1.06 | - | - | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 25 | 0.9738 | 0.9742 | 0.9324 | 4.173 | WLow | 3 | 0.7319 | 62.7
28 | EXT_BB-1133_SRT-A | 324447 | 2BONNIE KU | 69 | 363 | Load | 0 | 1.5 | 0 | 0 | 0.94 | 1.06 | - | - | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 25 | 0.9665 | 0.9805 | 0.933 | 4.754 | WLow | 3 | 0.7319 | 42.7
28 | EXT_BB-1133_SRT-A | 324362 | 2RIO | 69 | 363 | Load | 0 | 1.6 | 0 | 0 | 0.94 | 1.06 | - | - | EXT_B-138-115_SRT-A | 30 | 0.9596 | 0.9718 | 0.9371 | 3.465 | Low | 1 | 1 | 1.6
28 | EXT_BB-1133_SRT-A | 324050 | 2JONESVILLE | 69 | 363 | Load | 0 | 4.5 | 0 | 0 | 0.94 | 1.06 | - | - | EXT_B-138-115_SRT-A | 30 | 0.9613 | 0.9735 | 0.9389 | 3.457 | Low | 2 | 1 | 6.1
29 | EXT_MERE SWS_SRT-A | 324800 | 4MERE TVA | 138 | 363 | Load | 0 | 61.9 | 0 | 30 | 0.94 | 1.06 | - | - | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 25 | 0.9732 | 0.9661 | 0.9189 | 4.724 | WLow | 1 | 1 | 62.7
29 | EXT_MERE SWS_SRT-A | 324800 | 4MERE TVA | 138 | 363 | Load | 0 | 61.9 | 0 | 30 | 0.94 | 1.06 | - | - | EXT_B-138-115_SRT-A | 30 | 0.9765 | 0.9661 | 0.9195 | 4.665 | Low | 1 | 1 | 62.7
29 | EXT_MERE SWS_SRT-A | 324362 | 2RIO | 69 | 363 | Load | 0 | 1.6 | 0 | 0 | 0.94 | 1.06 | - | - | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 25 | 0.9576 | 0.9694 | 0.9394 | 2.993 | WLow | 1 | 1 | 1.6
29 | EXT_MERE SWS_SRT-A | 324362 | 2RIO | 69 | 363 | Load | 0 | 1.6 | 0 | 0 | 0.94 | 1.06 | - | - | EXT_B-138-115_SRT-A | 30 | 0.9596 | 0.9694 | 0.9397 | 2.969 | Low | 1 | 1 | 1.6
30 | EXT_B-138-115_SRT-A | 324800 | 4MERE TVA | 138 | 363 | Load | 0 | 61.9 | 0 | 30 | 0.94 | 1.06 | - | - | EXT_MERE SWS_SRT-A | 29 | 0.9661 | 0.9764 | 0.9192 | 5.72 | WLow | 1 | 1 | 62.8
30 | EXT_B-138-115_SRT-A | 324362 | 2RIO | 69 | 363 | Load | 0 | 1.6 | 0 | 0 | 0.94 | 1.06 | - | - | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A | 21 | 0.9717 | 0.9595 | 0.9345 | 2.502 | WLow | 1 | 1 | 1.6
30 | EXT_B-138-115_SRT-A | 324362 | 2RIO | 69 | 363 | Load | 0 | 1.6 | 0 | 0 | 0.94 | 1.06 | - | - | EXT_B-69-18_SRT-A | 35 | 0.9704 | 0.9595 | 0.9347 | 2.476 | Low | 1 | 1 | 1.6
30 | EXT_B-138-115_SRT-A | 324050 | 2JONESVILLE | 69 | 363 | Load | 0 | 4.5 | 0 | 0 | 0.94 | 1.06 | - | - | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A | 21 | 0.9733 | 0.9612 | 0.9362 | 2.497 | WLow | 2 | 1 | 6.1
30 | EXT_B-138-115_SRT-A | 324050 | 2JONESVILLE | 69 | 363 | Load | 0 | 4.5 | 0 | 0 | 0.94 | 1.06 | - | - | EXT_B-69-18_SRT-A | 35 | 0.972 | 0.9612 | 0.9365 | 2.471 | Low | 2 | 1 | 6.1
30 | EXT_B-138-115_SRT-A | 324362 | 2RIO | 69 | 363 | Load | 0 | 1.6 | 0 | 0 | 0.94 | 1.06 | - | - | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A | 17 | 0.9717 | 0.9595 | 0.9375 | 2.203 | Low | 1 | 1 | 1.6
30 | EXT_B-138-115_SRT-A | 324362 | 2RIO | 69 | 363 | Load | 0 | 1.6 | 0 | 0 | 0.94 | 1.06 | - | - | EXT_BB-1133_SRT-A | 28 | 0.9717 | 0.9595 | 0.9376 | 2.193 | Low | 1 | 1 | 1.6
30 | EXT_B-138-115_SRT-A | 324050 | 2JONESVILLE | 69 | 363 | Load | 0 | 4.5 | 0 | 0 | 0.94 | 1.06 | - | - | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A | 17 | 0.9733 | 0.9612 | 0.9392 | 2.198 | Low | 2 | 1 | 6.1
30 | EXT_B-138-115_SRT-A | 324050 | 2JONESVILLE | 69 | 363 | Load | 0 | 4.5 | 0 | 0 | 0.94 | 1.06 | - | - | EXT_BB-1133_SRT-A | 28 | 0.9734 | 0.9612 | 0.9393 | 2.189 | Low | 2 | 1 | 6.1
30 | EXT_B-138-115_SRT-A | 324362 | 2RIO | 69 | 363 | Load | 0 | 1.6 | 0 | 0 | 0.94 | 1.06 | - | - | EXT_MERE SWS_SRT-A | 29 | 0.9694 | 0.9595 | 0.9395 | 2.002 | Low | 1 | 1 | 1.6
35 | EXT_B-69-18_SRT-A | 324889 | 2LEBANON SO | 69 | 363 | Load | 0 | 11.4 | 0 | 0 | 0.94 | 1.06 | - | - | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 15 | 0.9925 | 0.9429 | 0.9109 | 3.203 | WLow | 2 | 0.7324 | 15.8
35 | EXT_B-69-18_SRT-A | 324605 | 2LEBANON EK | 69 | 363 | Load | 0 | 12.5 | 0 | 0 | 0.94 | 1.06 | - | - | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 15 | 0.9963 | 0.9418 | 0.9116 | 3.02 | WLow | 2 | 0.981 | 12.5
35 | EXT_B-69-18_SRT-A | 325020 | 2LEBANON E | 69 | 363 | Load | 0 | 14 | 0 | 0 | 0.94 | 1.06 | - | - | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 15 | 1.0022 | 0.938 | 0.9121 | 2.593 | WLow | 1 | 1 | 14
35 | EXT_B-69-18_SRT-A | 324603 | 2LEBANON CIT | 69 | 363 | Load | 0 | 6.2 | 0 | 14.4 | 0.94 | 1.06 | - | - | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 15 | 0.9981 | 0.9421 | 0.9125 | 2.96 | WLow | 2 | 0.9831 | 14.8
35 | EXT_B-69-18_SRT-A | 324604 | 2LEBANON IND | 69 | 363 | Load | 0 | 2.4 | 0 | 0 | 0.94 | 1.06 | - | - | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 15 | 1.0032 | 0.9391 | 0.9132 | 2.59 | WLow | 2 | 1 | 16.5
35 | EXT_B-69-18_SRT-A | 324191 | 2LEBANON E T | 69 | 363 | Load | 0 | 0 | 0 | 0 | 0.94 | 1.06 | - | - | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 15 | 1.0014 | 0.9416 | 0.9137 | 2.788 | WLow | 2 | 0.9718 | 14.8
35 | EXT_B-69-18_SRT-A | 324606 | 2LEBANON | 69 | 363 | Load | 0 | 0 | 0 | 0 | 0.94 | 1.06 | - | - | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 15 | 1.0046 | 0.9407 | 0.9148 | 2.585 | WLow | 3 | 0.8712 | 31.3
35 | EXT_B-69-18_SRT-A | 324068 | 2E CAMPBELVL | 69 | 363 | Load | 0 | 7.2 | 0 | 0 | 0.94 | 1.06 | - | - | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 15 | 0.9561 | 0.9771 | 0.9175 | 5.962 | WLow | 1 | 1 | 7.2
35 | EXT_B-69-18_SRT-A | 324349 | 2CAMPBELVIL2 | 69 | 363 | Load | 0 | 7.5 | 0 | 0 | 0.94 | 1.06 | - | - | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 15 | 0.9575 | 0.9785 | 0.919 | 5.953 | WLow | 2 | 1 | 14.8
35 | EXT_B-69-18_SRT-A | 326970 | 2MILE LAN EK | 69 | 363 | Load | 0 | 9.8 | 0 | 0 | 0.94 | 1.06 | - | - | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 15 | 0.9581 | 0.9808 | 0.9208 | 6.007 | WLow | 1 | 1 | 9.8
35 | EXT_B-69-18_SRT-A | 324479 | 2CAMPBELVL T | 69 | 363 | Load | 0 | 0 | 0 | 0 | 0.94 | 1.06 | - | - | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 15 | 0.9618 | 0.9826 | 0.9234 | 5.926 | WLow | 3 | 0.7324 | 30.6
35 | EXT_B-69-18_SRT-A | 325020 | 2LEBANON E | 69 | 363 | Load | 0 | 14 | 0 | 0 | 0.94 | 1.06 | - | - | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 10 | 1.0055 | 0.938 | 0.924 | 1.397 | Low | 1 | 1 | 14
35 | EXT_B-69-18_SRT-A | 325921 | 5TAYLOR CO | 161 | 363 | Load | 0 | 0 | 0 | 0 | 0.94 | 1.06 | - | - | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 15 | 0.9617 | 0.9963 | 0.9244 | 7.191 | WLow | 1 | 1 | 0
35 | EXT_B-69-18_SRT-A | 324751 | 2TAYLOR CO | 69 | 363 | Load | 0 | 0 | 0 | 0 | 0.94 | 1.06 | - | - | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 15 | 0.9617 | 0.9844 | 0.9244 | 5.996 | WLow | 3 | 0.9931 | 30.7
35 | EXT_B-69-18_SRT-A | 324641 | 2MILE LAN TP | 69 | 363 | Load | 0 | 0 | 0 | 0 | 0.94 | 1.06 | - | - | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 15 | 0.9617 | 0.9843 | 0.9245 | 5.983 | WLow | 3 | 0.9603 | 40.5
35 | EXT_B-69-18_SRT-A | 324889 | 2LEBANON SO | 69 | 363 | Load | 0 | 11.4 | 0 | 0 | 0.94 | 1.06 | - | - | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 10 | 0.9951 | 0.9429 | 0.9246 | 1.83 | Low | 2 | 0.7339 | 14.7
35 | EXT_B-69-18_SRT-A | 324605 | 2LEBANON EK | 69 | 363 | Load | 0 | 12.5 | 0 | 0 | 0.94 | 1.06 | - | - | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 10 | 0.999 | 0.9418 | 0.9249 | 1.691 | Low | 2 | 0.9811 | 12.5
35 | EXT_B-69-18_SRT-A | 324604 | 2LEBANON IND | 69 | 363 | Load | 0 | 2.4 | 0 | 0 | 0.94 | 1.06 | - | - | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 10 | 1.0065 | 0.9391 | 0.9251 | 1.396 | Low | 2 | 1 | 16.5
35 | EXT_B-69-18_SRT-A | 324603 | 2LEBANON CIT | 69 | 363 | Load | 0 | 6.2 | 0 | 14.4 | 0.94 | 1.06 | - | - | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 10 | 1.0009 | 0.9421 | 0.9257 | 1.645 | Low | 2 | 0.9832 | 15.8
35 | EXT_B-69-18_SRT-A | 324362 | 2RIO | 69 | 363 | Load | 0 | 1.6 | 0 | 0 | 0.94 | 1.06 | - | - | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 25 | 0.9576 | 0.9704 | 0.9261 | 4.43 | WLow | 1 | 1 | 1.6
35 | EXT_B-69-18_SRT-A | 324191 | 2LEBANON E T | 69 | 363 | Load | 0 | 0 | 0 | 0 | 0.94 | 1.06 | - | - | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 10 | 1.0044 | 0.9416 | 0.9264 | 1.518 | Low | 2 | 0.972 | 15.8
35 | EXT_B-69-18_SRT-A | 324606 | 2LEBANON | 69 | 363 | Load | 0 | 0 | 0 | 0 | 0.94 | 1.06 | - | - | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 10 | 1.008 | 0.9407 | 0.9267 | 1.393 | Low | 3 | 0.8719 | 32.3
35 | EXT_B-69-18_SRT-A | 324050 | 2JONESVILLE | 69 | 363 | Load | 0 | 4.5 | 0 | 0 | 0.94 | 1.06 | - | - | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 25 | 0.9593 | 0.972 | 0.9278 | 4.422 | WLow | 2 | 1 | 6.1
35 | EXT_B-69-18_SRT-A | 324829 | 2CAMPBELVIL1 | 69 | 363 | Load | 0 | 12.5 | 0 | 0 | 0.94 | 1.06 | - | - | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 15 | 0.9642 | 0.9826 | 0.9338 | 4.873 | WLow | 2 | 0.9603 | 53.5
35 | EXT_B-69-18_SRT-A | 324362 | 2RIO | 69 | 363 | Load | 0 | 1.6 | 0 | 0 | 0.94 | 1.06 | - | - | EXT_B-138-115_SRT-A | 30 | 0.9596 | 0.9704 | 0.9347 | 3.561 | Low | 1 | 1 | 1.6
35 | EXT_B-69-18_SRT-A | 324447 | 2BONNIE KU | 69 | 363 | Load | 0 | 1.5 | 0 | 0 | 0.94 | 1.06 | - | - | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 25 | 0.9665 | 0.9791 | 0.9353 | 4.387 | WLow | 3 | 0.732 | 44.8
35 | EXT_B-69-18_SRT-A | 324800 | 4MERE TVA | 138 | 363 | Load | 0 | 61.9 | 0 | 30 | 0.94 | 1.06 | - | - | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 25 | 0.9732 | 0.982 | 0.9356 | 4.643 | WLow | 1 | 1 | 62.7
35 | EXT_B-69-18_SRT-A | 324050 | 2JONESVILLE | 69 | 363 | Load | 0 | 4.5 | 0 | 0 | 0.94 | 1.06 | - | - | EXT_B-138-115_SRT-A | 30 | 0.9613 | 0.972 | 0.9365 | 3.554 | Low | 2 | 1 | 6.1
35 | EXT_B-69-18_SRT-A | 324068 | 2E CAMPBELVL | 69 | 363 | Load | 0 | 7.2 | 0 | 0 | 0.94 | 1.06 | - | - | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 10 | 0.9567 | 0.9771 | 0.9367 | 4.035 | Low | 1 | 1 | 7.2
35 | EXT_B-69-18_SRT-A | 324557 | 2GR RVR PLAZ | 69 | 363 | Load | 0 | 7.3 | 0 | 20.4 | 0.94 | 1.06 | - | - | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 15 | 0.9655 | 0.9828 | 0.9367 | 4.605 | WLow | 2 | 0.9804 | 60.8
35 | EXT_B-69-18_SRT-A | 324270 | 4LEBANON WES | 138 | 363 | Load | 0 | 6.9 | 0 | 0 | 0.94 | 1.06 | - | - | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 25 | 1.0019 | 0.9733 | 0.9374 | 3.584 | WLow | 1 | 1 | 6.9
35 | EXT_B-69-18_SRT-A | 325020 | 2LEBANON E | 69 | 363 | Load | 0 | 14 | 0 | 0 | 0.94 | 1.06 | - | - | Base Case | 0 | 1.0055 | 0.938 | - | - | Low | 1 | 1 | 14
35 | EXT_B-69-18_SRT-A | 324213 | 4BONNIEVILLE | 138 | 363 | Load | 0 | 0 | 0 | 0 | 0.94 | 1.06 | - | - | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 25 | 0.9738 | 0.9738 | 0.9382 | 3.563 | WLow | 4 | 0.732 | 69.6
35 | EXT_B-69-18_SRT-A | 324349 | 2CAMPBELVIL2 | 69 | 363 | Load | 0 | 7.5 | 0 | 0 | 0.94 | 1.06 | - | - | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 10 | 0.9581 | 0.9785 | 0.9382 | 4.029 | Low | 2 | 1 | 14.8
35 | EXT_B-69-18_SRT-A | 324604 | 2LEBANON IND | 69 | 363 | Load | 0 | 2.4 | 0 | 0 | 0.94 | 1.06 | - | - | Base Case | 0 | 1.0065 | 0.9391 | - | - | Low | 2 | 1 | 16.5
35 | EXT_B-69-18_SRT-A | 324736 | 2SPRINGFL KU | 69 | 363 | Load | 0 | 13.8 | 0 | 0 | 0.94 | 1.06 | - | - | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 15 | 0.9987 | 0.951 | 0.9395 | 1.157 | WLow | 2 | 0.8712 | 45.7
35 | EXT_B-69-18_SRT-A | 324605 | 2LEBANON EK | 69 | 363 | Load | 0 | 12.5 | 0 | 0 | 0.94 | 1.06 | - | - | EKPC_P1-2_LIBJ-GAS161_SRT-A | 9 | 1.004 | 0.9418 | 0.9397 | 0.219 | Low | 2 | 0.9786 | 27.6

## ACContSumAll
EKPC AC contingency analysis summary[TARA Ver 2201.2.0.0 64-bit - Sat Aug 13 07:58:26 2022]
Loadflow Case: C:\Users\03419\Desktop\2022 Gas Study\Alt 3A\2032S_gas_alt#3a_212mw.raw
Study Data File: C:\Users\03419\Desktop\2022 Gas Study\2022 series_sub_EKPC-LGEE.sub
Contingency File: C:\Users\03419\Desktop\2022 Gas Study\Option 3A N-1-1 con file.con (total 37 contingencies)/ First-Level Contingency File: C:\Users\03419\Desktop\2022 Gas Study\Option 3A N-1-1 con file.con (total 37 contingencies)
Monitor File: C:\Users\03419\Desktop\2022 Gas Study\2022 series_mon_EKPC-LGEE.mon
Exclude File: not provided
Solution Options (Pre/Post Contingency): Shunts[All Enabled/All Enabled] PAR[Adjusted/Fixed] XFMR Tap[Adjusted/Adjusted] Area Interchange [Disabled/Disabled]
First Level Scenario Index | First Level Scenario | Cont ID | Cont Name | Status | #Itr | #Pms | #Qms | PmaxMism | Bus# | Bus Name | Volt | VoltMagPU | QmaxMism | Bus# | Bus Name | Volt | VoltMagPU | OvlSever | #Ovl | Worst | VltSevrInd | VLow | VHi | Drop | Rise
0 | Original Case | 1 | EKPC_P1-2_MAR-KU LEB138 |  | 2 | 0 | 0 | 0.23 | 325118 | 1RHUDES INV | 34.5 | 1.077 | 0.59 | 324002 | 1BROWN 3 | 24 | 1.0527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | Original Case | 2 | EKPC_P1-2_COOP-ELIHU161_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.03 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | Original Case | 3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A |  | 4 | 0 | 0 | 0.11 | 325118 | 1RHUDES INV | 34.5 | 1.0757 | 0.42 | 324002 | 1BROWN 3 | 24 | 1.0526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | Original Case | 4 | EKPC_P1-2_COOP-LAUREL161_SRT-A |  | 3 | 0 | 0 | 0.15 | 324446 | 2BOND | 69 | 1.0164 | 0.56 | 324002 | 1BROWN 3 | 24 | 1.0515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | Original Case | 5 | EKPC_P1-2_COOP-DEN161_SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.03 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | Original Case | 6 | EKPC_P1-2_COOP 161 TIE_SRT-A |  | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.19 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | Original Case | 7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A |  | 3 | 0 | 0 | 0.05 | 341971 | 2NORWOOD | 69 | 0.9639 | 0.15 | 324002 | 1BROWN 3 | 24 | 1.052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | Original Case | 8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.26 | 340576 | WILSON | 24 | 1.0039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | Original Case | 9 | EKPC_P1-2_LIBJ-GAS161_SRT-A |  | 3 | 0 | 0 | 0.09 | 325118 | 1RHUDES INV | 34.5 | 1.0745 | 0.18 | 325117 | 1RHUDES COL | 34.5 | 1.069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | Original Case | 10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A |  | 2 | 0 | 0 | 0.1 | 316293 | AC1-161 COL2 | 34.5 | 1.0794 | 0.33 | 364622 | 1WOLFCR H5-6 | 13.8 | 1.0096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | Original Case | 11 | EKPC_P1-2_GRE-SUMSH161_SRT-A |  | 3 | 0 | 0 | 0.08 | 325118 | 1RHUDES INV | 34.5 | 1.0771 | 0.17 | 325117 | 1RHUDES COL | 34.5 | 1.0714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | Original Case | 12 | EKPC_P1-2_BARR-SUMSH161_SRT-A |  | 3 | 0 | 0 | 0.06 | 325118 | 1RHUDES INV | 34.5 | 1.0756 | 0.13 | 325117 | 1RHUDES COL | 34.5 | 1.0701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | Original Case | 13 | EKPC_P1-2_BULL-SUMSH161_SRT-A |  | 2 | 0 | 0 | 0.18 | 325118 | 1RHUDES INV | 34.5 | 1.0764 | 0.38 | 325117 | 1RHUDES COL | 34.5 | 1.0708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | Original Case | 14 | EKPC_P1-2_SSHAD 161 TIE_SRT-A |  | 1 | 0 | 0 | 0.12 | 542969 | STILWEL5 | 161 | 1.0122 | 0.84 | 360334 | 5SUMMER SHAD | 161 | 1.0261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | Original Case | 15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.18 | 324002 | 1BROWN 3 | 24 | 1.0519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | Original Case | 16 | EKPC_P1-3_MAR 161/138_SRT-A |  | 2 | 0 | 0 | 0.23 | 325118 | 1RHUDES INV | 34.5 | 1.077 | 0.59 | 324002 | 1BROWN 3 | 24 | 1.0527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | Original Case | 17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A |  | 2 | 0 | 0 | 0.34 | 325118 | 1RHUDES INV | 34.5 | 1.078 | 0.72 | 325117 | 1RHUDES COL | 34.5 | 1.0723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | Original Case | 18 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.17 | 340576 | WILSON | 24 | 1.0011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | Original Case | 19 | EXT_324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1 _SRT-A |  | 1 | 0 | 0 | 0.3 | 342577 | 4FAWKES EK | 138 | 1.0037 | 0.46 | 342577 | 4FAWKES EK | 138 | 1.0037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | Original Case | 20 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.15 | 324002 | 1BROWN 3 | 24 | 1.0514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | Original Case | 21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A |  | 2 | 0 | 0 | 0.31 | 325118 | 1RHUDES INV | 34.5 | 1.0777 | 0.65 | 325117 | 1RHUDES COL | 34.5 | 1.072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | Original Case | 22 | EXT_324217 4BROWN PLANT 138 324219 4BROWN T1 138 1 _SRT-A |  | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.03 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | Original Case | 23 | EXT_324217 4BROWN PLANT 138 324220 4BROWN T2 138 1 _SRT-A |  | 1 | 0 | 0 | 0.12 | 542969 | STILWEL5 | 161 | 1.0122 | 0.24 | 324015 | 1DIX DAM 2 | 13.2 | 1.0085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | Original Case | 24 | EXT_324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1 _SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.52 | 340576 | WILSON | 24 | 1.0039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | Original Case | 25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.12 | 324002 | 1BROWN 3 | 24 | 1.0524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | Original Case | 26 | EXT_B-138-111_SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.03 | 324002 | 1BROWN 3 | 24 | 1.052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | Original Case | 27 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A_Dup1 |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.15 | 324002 | 1BROWN 3 | 24 | 1.0514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | Original Case | 28 | EXT_BB-1133_SRT-A |  | 2 | 0 | 0 | 0.32 | 325118 | 1RHUDES INV | 34.5 | 1.0778 | 0.68 | 325117 | 1RHUDES COL | 34.5 | 1.0721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | Original Case | 29 | EXT_MERE SWS_SRT-A |  | 2 | 0 | 0 | 0.42 | 325118 | 1RHUDES INV | 34.5 | 1.0789 | 0.9 | 325117 | 1RHUDES COL | 34.5 | 1.0732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | Original Case | 30 | EXT_B-138-115_SRT-A |  | 3 | 0 | 0 | 0.04 | 542969 | STILWEL5 | 161 | 1.0122 | 0.35 | 324002 | 1BROWN 3 | 24 | 1.0523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | Original Case | 31 | EXT_B-138-120_SRT-A |  | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.03 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | Original Case | 32 | EXT_B-138-121_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.03 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | Original Case | 33 | EXT_324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1 _SRT-A |  | 2 | 0 | 0 | 0.08 | 325118 | 1RHUDES INV | 34.5 | 1.0754 | 0.17 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | Original Case | 34 | EXT_326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1 _SRT-A |  | 2 | 0 | 0 | 0.17 | 325118 | 1RHUDES INV | 34.5 | 1.0763 | 0.36 | 325117 | 1RHUDES COL | 34.5 | 1.0707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | Original Case | 35 | EXT_B-69-18_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.24 | 324002 | 1BROWN 3 | 24 | 1.0522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | Original Case | 36 | EXT_B-69-19_SRT-A |  | 4 | 0 | 0 | 0.33 | 325118 | 1RHUDES INV | 34.5 | 1.0748 | 0.7 | 325117 | 1RHUDES COL | 34.5 | 1.0694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | Original Case | 37 | EXT_BB-1066_SRT-A |  | 2 | 0 | 0 | 0.09 | 316293 | AC1-161 COL2 | 34.5 | 1.0794 | 0.17 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | EKPC_P1-2_MAR-KU LEB138 | 2 | EKPC_P1-2_COOP-ELIHU161_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | EKPC_P1-2_MAR-KU LEB138 | 3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | Ovl | 4 | 0 | 0 | 0.05 | 324830 | 2CAMPBELV EK | 69 | 0.9925 | 0.51 | 324002 | 1BROWN 3 | 24 | 1.0536 | 12418 | 1 | 111.4 | 0 | 0 | 0 | 0 | 0
1 | EKPC_P1-2_MAR-KU LEB138 | 4 | EKPC_P1-2_COOP-LAUREL161_SRT-A | Ovl | 3 | 0 | 0 | 0.15 | 324446 | 2BOND | 69 | 1.0163 | 0.57 | 324002 | 1BROWN 3 | 24 | 1.0526 | 10664 | 1 | 103.3 | 0 | 0 | 0 | 0 | 0
1 | EKPC_P1-2_MAR-KU LEB138 | 5 | EKPC_P1-2_COOP-DEN161_SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | EKPC_P1-2_MAR-KU LEB138 | 6 | EKPC_P1-2_COOP 161 TIE_SRT-A | Ovl | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.2 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0099 | 10006.6 | 1 | 100 | 0 | 0 | 0 | 0 | 0
1 | EKPC_P1-2_MAR-KU LEB138 | 7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | Ovl | 3 | 0 | 0 | 0.05 | 341971 | 2NORWOOD | 69 | 0.9627 | 0.12 | 324002 | 1BROWN 3 | 24 | 1.0531 | 10533.6 | 1 | 102.6 | 0 | 0 | 0 | 0 | 0
1 | EKPC_P1-2_MAR-KU LEB138 | 8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.1 | 364001 | 1BR FERRY N1 | 22 | 1.0424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | EKPC_P1-2_MAR-KU LEB138 | 9 | EKPC_P1-2_LIBJ-GAS161_SRT-A | Ovl | 3 | 0 | 0 | 0.1 | 341563 | 2GREEN CO | 69 | 0.9998 | 0.34 | 342769 | 5MARION CO | 161 | 1.0064 | 11175 | 1 | 105.7 | 0 | 0 | 0 | 0 | 0
1 | EKPC_P1-2_MAR-KU LEB138 | 10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | Ovl | 4 | 0 | 0 | 0.04 | 542969 | STILWEL5 | 161 | 1.0122 | 0.18 | 340576 | WILSON | 24 | 1.0047 | 30207.4 | 1 | 173.8 | 0 | 0 | 0 | 0 | 0
1 | EKPC_P1-2_MAR-KU LEB138 | 11 | EKPC_P1-2_GRE-SUMSH161_SRT-A | Ovl | 2 | 0 | 0 | 0.12 | 325118 | 1RHUDES INV | 34.5 | 1.0787 | 0.25 | 325117 | 1RHUDES COL | 34.5 | 1.073 | 10047.3 | 1 | 100.2 | 0 | 0 | 0 | 0 | 0
1 | EKPC_P1-2_MAR-KU LEB138 | 12 | EKPC_P1-2_BARR-SUMSH161_SRT-A |  | 3 | 0 | 0 | 0.04 | 542969 | STILWEL5 | 161 | 1.0122 | 0.09 | 340576 | WILSON | 24 | 1.0048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | EKPC_P1-2_MAR-KU LEB138 | 13 | EKPC_P1-2_BULL-SUMSH161_SRT-A |  | 2 | 0 | 0 | 0.13 | 325118 | 1RHUDES INV | 34.5 | 1.0787 | 0.27 | 325117 | 1RHUDES COL | 34.5 | 1.073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | EKPC_P1-2_MAR-KU LEB138 | 14 | EKPC_P1-2_SSHAD 161 TIE_SRT-A |  | 1 | 0 | 0 | 0.1 | 542969 | STILWEL5 | 161 | 1.0122 | 0.86 | 360334 | 5SUMMER SHAD | 161 | 1.0259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | EKPC_P1-2_MAR-KU LEB138 | 15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | Ovl | 3 | 0 | 0 | 0.04 | 542969 | STILWEL5 | 161 | 1.0122 | 0.08 | 324002 | 1BROWN 3 | 24 | 1.0534 | 12939.5 | 1 | 113.8 | 0 | 0 | 0 | 0 | 0
1 | EKPC_P1-2_MAR-KU LEB138 | 16 | EKPC_P1-3_MAR 161/138_SRT-A |  | 1 | 0 | 0 | 0.1 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | EKPC_P1-2_MAR-KU LEB138 | 17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A |  | 2 | 0 | 0 | 0.13 | 325118 | 1RHUDES INV | 34.5 | 1.0787 | 0.79 | 340576 | WILSON | 24 | 1.0044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | EKPC_P1-2_MAR-KU LEB138 | 18 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A |  | 3 | 0 | 0 | 0.04 | 542969 | STILWEL5 | 161 | 1.0122 | 0.17 | 340576 | WILSON | 24 | 1.0014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | EKPC_P1-2_MAR-KU LEB138 | 19 | EXT_324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1 _SRT-A |  | 1 | 0 | 0 | 0.27 | 342577 | 4FAWKES EK | 138 | 1.0036 | 0.47 | 340576 | WILSON | 24 | 1.0044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | EKPC_P1-2_MAR-KU LEB138 | 20 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.09 | 340576 | WILSON | 24 | 1.0059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | EKPC_P1-2_MAR-KU LEB138 | 21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A |  | 2 | 0 | 0 | 0.13 | 325118 | 1RHUDES INV | 34.5 | 1.0787 | 0.82 | 340576 | WILSON | 24 | 1.0044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | EKPC_P1-2_MAR-KU LEB138 | 22 | EXT_324217 4BROWN PLANT 138 324219 4BROWN T1 138 1 _SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | EKPC_P1-2_MAR-KU LEB138 | 23 | EXT_324217 4BROWN PLANT 138 324220 4BROWN T2 138 1 _SRT-A |  | 1 | 0 | 0 | 0.1 | 542969 | STILWEL5 | 161 | 1.0122 | 0.32 | 324016 | 1DIX DAM 3 | 13.2 | 1.016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | EKPC_P1-2_MAR-KU LEB138 | 24 | EXT_324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1 _SRT-A | Ovl | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.28 | 324002 | 1BROWN 3 | 24 | 1.0526 | 10756.9 | 1 | 103.7 | 0 | 0 | 0 | 0 | 0
1 | EKPC_P1-2_MAR-KU LEB138 | 25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A |  | 4 | 0 | 0 | 0.09 | 340576 | WILSON | 24 | 1.0036 | 0.66 | 340576 | WILSON | 24 | 1.0036 | 0 | 0 | 93.8 | 0 | 0 | 0 | 0 | 0
1 | EKPC_P1-2_MAR-KU LEB138 | 26 | EXT_B-138-111_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.21 | 324002 | 1BROWN 3 | 24 | 1.0525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | EKPC_P1-2_MAR-KU LEB138 | 27 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A_Dup1 |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.09 | 340576 | WILSON | 24 | 1.0059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | EKPC_P1-2_MAR-KU LEB138 | 28 | EXT_BB-1133_SRT-A |  | 2 | 0 | 0 | 0.13 | 325118 | 1RHUDES INV | 34.5 | 1.0787 | 0.81 | 340576 | WILSON | 24 | 1.0043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | EKPC_P1-2_MAR-KU LEB138 | 29 | EXT_MERE SWS_SRT-A |  | 3 | 0 | 0 | 0.04 | 542969 | STILWEL5 | 161 | 1.0122 | 0.06 | 324002 | 1BROWN 3 | 24 | 1.0534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | EKPC_P1-2_MAR-KU LEB138 | 30 | EXT_B-138-115_SRT-A | Ovl | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.4 | 324002 | 1BROWN 3 | 24 | 1.054 | 10754.5 | 1 | 103.7 | 0 | 0 | 0 | 0 | 0
1 | EKPC_P1-2_MAR-KU LEB138 | 31 | EXT_B-138-120_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | EKPC_P1-2_MAR-KU LEB138 | 32 | EXT_B-138-121_SRT-A |  | 3 | 0 | 0 | 0.04 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | EKPC_P1-2_MAR-KU LEB138 | 33 | EXT_324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1 _SRT-A |  | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.16 | 325117 | 1RHUDES COL | 34.5 | 1.0725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | EKPC_P1-2_MAR-KU LEB138 | 34 | EXT_326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1 _SRT-A |  | 2 | 0 | 0 | 0.13 | 325118 | 1RHUDES INV | 34.5 | 1.0787 | 0.27 | 325117 | 1RHUDES COL | 34.5 | 1.073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | EKPC_P1-2_MAR-KU LEB138 | 35 | EXT_B-69-18_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.19 | 324002 | 1BROWN 3 | 24 | 1.0522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | EKPC_P1-2_MAR-KU LEB138 | 36 | EXT_B-69-19_SRT-A |  | 3 | 0 | 0 | 0.27 | 325118 | 1RHUDES INV | 34.5 | 1.0759 | 0.57 | 325117 | 1RHUDES COL | 34.5 | 1.0704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | EKPC_P1-2_MAR-KU LEB138 | 37 | EXT_BB-1066_SRT-A |  | 2 | 0 | 0 | 0.09 | 542969 | STILWEL5 | 161 | 1.0122 | 0.16 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | EKPC_P1-2_COOP-ELIHU161_SRT-A | 1 | EKPC_P1-2_MAR-KU LEB138 |  | 2 | 0 | 0 | 0.23 | 325118 | 1RHUDES INV | 34.5 | 1.0762 | 0.56 | 324002 | 1BROWN 3 | 24 | 1.0521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | EKPC_P1-2_COOP-ELIHU161_SRT-A | 3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | Ovl | 5 | 0 | 0 | 0.04 | 324446 | 2BOND | 69 | 1.0182 | 0.09 | 243764 | 05BSG1 | 22 | 0.9919 | 11335.6 | 1 | 106.5 | 0 | 0 | 0 | 0 | 0
2 | EKPC_P1-2_COOP-ELIHU161_SRT-A | 4 | EKPC_P1-2_COOP-LAUREL161_SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 243764 | 05BSG1 | 22 | 0.9922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | EKPC_P1-2_COOP-ELIHU161_SRT-A | 5 | EKPC_P1-2_COOP-DEN161_SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | EKPC_P1-2_COOP-ELIHU161_SRT-A | 6 | EKPC_P1-2_COOP 161 TIE_SRT-A |  | 4 | 0 | 0 | 0.03 | 324446 | 2BOND | 69 | 1.0187 | 0.07 | 243764 | 05BSG1 | 22 | 0.9918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | EKPC_P1-2_COOP-ELIHU161_SRT-A | 7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.13 | 324002 | 1BROWN 3 | 24 | 1.0516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | EKPC_P1-2_COOP-ELIHU161_SRT-A | 8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.23 | 340576 | WILSON | 24 | 1.0039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | EKPC_P1-2_COOP-ELIHU161_SRT-A | 9 | EKPC_P1-2_LIBJ-GAS161_SRT-A |  | 3 | 0 | 0 | 0.09 | 325118 | 1RHUDES INV | 34.5 | 1.0738 | 0.19 | 325117 | 1RHUDES COL | 34.5 | 1.0683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | EKPC_P1-2_COOP-ELIHU161_SRT-A | 10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A |  | 2 | 0 | 0 | 0.1 | 542969 | STILWEL5 | 161 | 1.0122 | 0.33 | 364622 | 1WOLFCR H5-6 | 13.8 | 1.0126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | EKPC_P1-2_COOP-ELIHU161_SRT-A | 11 | EKPC_P1-2_GRE-SUMSH161_SRT-A |  | 3 | 0 | 0 | 0.08 | 325118 | 1RHUDES INV | 34.5 | 1.0764 | 0.17 | 325117 | 1RHUDES COL | 34.5 | 1.0708 | 0 | 0 | 90.4 | 0 | 0 | 0 | 0 | 0
2 | EKPC_P1-2_COOP-ELIHU161_SRT-A | 12 | EKPC_P1-2_BARR-SUMSH161_SRT-A |  | 3 | 0 | 0 | 0.06 | 325118 | 1RHUDES INV | 34.5 | 1.0749 | 0.13 | 325117 | 1RHUDES COL | 34.5 | 1.0694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | EKPC_P1-2_COOP-ELIHU161_SRT-A | 13 | EKPC_P1-2_BULL-SUMSH161_SRT-A |  | 2 | 0 | 0 | 0.18 | 325118 | 1RHUDES INV | 34.5 | 1.0756 | 0.38 | 325117 | 1RHUDES COL | 34.5 | 1.0701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | EKPC_P1-2_COOP-ELIHU161_SRT-A | 14 | EKPC_P1-2_SSHAD 161 TIE_SRT-A |  | 1 | 0 | 0 | 0.11 | 542969 | STILWEL5 | 161 | 1.0122 | 0.84 | 360334 | 5SUMMER SHAD | 161 | 1.026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | EKPC_P1-2_COOP-ELIHU161_SRT-A | 15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.18 | 324002 | 1BROWN 3 | 24 | 1.0513 | 0 | 0 | 97.6 | 0 | 0 | 0 | 0 | 0
2 | EKPC_P1-2_COOP-ELIHU161_SRT-A | 16 | EKPC_P1-3_MAR 161/138_SRT-A |  | 2 | 0 | 0 | 0.23 | 325118 | 1RHUDES INV | 34.5 | 1.0762 | 0.56 | 324002 | 1BROWN 3 | 24 | 1.0521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | EKPC_P1-2_COOP-ELIHU161_SRT-A | 17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A |  | 2 | 0 | 0 | 0.34 | 325118 | 1RHUDES INV | 34.5 | 1.0773 | 0.72 | 325117 | 1RHUDES COL | 34.5 | 1.0716 | 0 | 0 | 93.1 | 0 | 0 | 0 | 0 | 0
2 | EKPC_P1-2_COOP-ELIHU161_SRT-A | 18 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.17 | 340576 | WILSON | 24 | 1.0011 | 0 | 0 | 93 | 0 | 0 | 0 | 0 | 0
2 | EKPC_P1-2_COOP-ELIHU161_SRT-A | 19 | EXT_324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1 _SRT-A |  | 1 | 0 | 0 | 0.3 | 342577 | 4FAWKES EK | 138 | 1.0036 | 0.47 | 342577 | 4FAWKES EK | 138 | 1.0036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | EKPC_P1-2_COOP-ELIHU161_SRT-A | 20 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.16 | 324002 | 1BROWN 3 | 24 | 1.0508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | EKPC_P1-2_COOP-ELIHU161_SRT-A | 21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A |  | 2 | 0 | 0 | 0.31 | 325118 | 1RHUDES INV | 34.5 | 1.077 | 0.65 | 325117 | 1RHUDES COL | 34.5 | 1.0713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | EKPC_P1-2_COOP-ELIHU161_SRT-A | 22 | EXT_324217 4BROWN PLANT 138 324219 4BROWN T1 138 1 _SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | EKPC_P1-2_COOP-ELIHU161_SRT-A | 23 | EXT_324217 4BROWN PLANT 138 324220 4BROWN T2 138 1 _SRT-A |  | 1 | 0 | 0 | 0.11 | 542969 | STILWEL5 | 161 | 1.0122 | 0.24 | 324015 | 1DIX DAM 2 | 13.2 | 1.0082 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | EKPC_P1-2_COOP-ELIHU161_SRT-A | 24 | EXT_324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1 _SRT-A |  | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.54 | 340576 | WILSON | 24 | 1.0039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | EKPC_P1-2_COOP-ELIHU161_SRT-A | 25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.11 | 324002 | 1BROWN 3 | 24 | 1.0518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | EKPC_P1-2_COOP-ELIHU161_SRT-A | 26 | EXT_B-138-111_SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | EKPC_P1-2_COOP-ELIHU161_SRT-A | 27 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A_Dup1 |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.16 | 324002 | 1BROWN 3 | 24 | 1.0508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | EKPC_P1-2_COOP-ELIHU161_SRT-A | 28 | EXT_BB-1133_SRT-A |  | 2 | 0 | 0 | 0.32 | 325118 | 1RHUDES INV | 34.5 | 1.0771 | 0.68 | 325117 | 1RHUDES COL | 34.5 | 1.0714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | EKPC_P1-2_COOP-ELIHU161_SRT-A | 29 | EXT_MERE SWS_SRT-A |  | 2 | 0 | 0 | 0.47 | 325118 | 1RHUDES INV | 34.5 | 1.0787 | 1 | 325117 | 1RHUDES COL | 34.5 | 1.0729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | EKPC_P1-2_COOP-ELIHU161_SRT-A | 30 | EXT_B-138-115_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.32 | 324002 | 1BROWN 3 | 24 | 1.0517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | EKPC_P1-2_COOP-ELIHU161_SRT-A | 31 | EXT_B-138-120_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | EKPC_P1-2_COOP-ELIHU161_SRT-A | 32 | EXT_B-138-121_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | EKPC_P1-2_COOP-ELIHU161_SRT-A | 33 | EXT_324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1 _SRT-A |  | 2 | 0 | 0 | 0.09 | 542969 | STILWEL5 | 161 | 1.0122 | 0.18 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | EKPC_P1-2_COOP-ELIHU161_SRT-A | 34 | EXT_326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1 _SRT-A |  | 2 | 0 | 0 | 0.17 | 325118 | 1RHUDES INV | 34.5 | 1.0756 | 0.36 | 325117 | 1RHUDES COL | 34.5 | 1.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | EKPC_P1-2_COOP-ELIHU161_SRT-A | 35 | EXT_B-69-18_SRT-A |  | 3 | 0 | 0 | 0.06 | 325118 | 1RHUDES INV | 34.5 | 1.0775 | 0.24 | 324002 | 1BROWN 3 | 24 | 1.0516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | EKPC_P1-2_COOP-ELIHU161_SRT-A | 36 | EXT_B-69-19_SRT-A |  | 4 | 0 | 0 | 0.33 | 325118 | 1RHUDES INV | 34.5 | 1.0741 | 0.7 | 325117 | 1RHUDES COL | 34.5 | 1.0687 | 0 | 0 | 93 | 0 | 0 | 0 | 0 | 0
2 | EKPC_P1-2_COOP-ELIHU161_SRT-A | 37 | EXT_BB-1066_SRT-A |  | 2 | 0 | 0 | 0.1 | 542969 | STILWEL5 | 161 | 1.0122 | 0.19 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 1 | EKPC_P1-2_MAR-KU LEB138 | Ovl | 2 | 0 | 0 | 0.22 | 325118 | 1RHUDES INV | 34.5 | 1.0779 | 0.57 | 324002 | 1BROWN 3 | 24 | 1.0534 | 12415.4 | 1 | 111.4 | 0 | 0 | 0 | 0 | 0
3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 2 | EKPC_P1-2_COOP-ELIHU161_SRT-A | Ovl | 3 | 0 | 0 | 0.06 | 324446 | 2BOND | 69 | 1.0161 | 0.35 | 324002 | 1BROWN 3 | 24 | 1.0516 | 11245 | 1 | 106 | 0 | 0 | 0 | 0 | 0
3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 4 | EKPC_P1-2_COOP-LAUREL161_SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 243764 | 05BSG1 | 22 | 0.9925 | 0 | 0 | 95.9 | 0 | 0 | 0 | 0 | 0
3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 5 | EKPC_P1-2_COOP-DEN161_SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 324002 | 1BROWN 3 | 24 | 1.0521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 6 | EKPC_P1-2_COOP 161 TIE_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.16 | 324002 | 1BROWN 3 | 24 | 1.0522 | 0 | 0 | 97.1 | 0 | 0 | 0 | 0 | 0
3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | Ovl | 3 | 0 | 0 | 0.05 | 341971 | 2NORWOOD | 69 | 0.9572 | 0.17 | 324002 | 1BROWN 3 | 24 | 1.0529 | 10619.3 | 1 | 103.1 | 0 | 0 | 0 | 0 | 0
3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.2 | 340576 | WILSON | 24 | 1.0039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 9 | EKPC_P1-2_LIBJ-GAS161_SRT-A |  | 3 | 0 | 0 | 0.09 | 325118 | 1RHUDES INV | 34.5 | 1.076 | 0.18 | 325117 | 1RHUDES COL | 34.5 | 1.0704 | 0 | 0 | 97.2 | 0 | 0 | 0 | 0 | 0
3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | Ovl | 2 | 0 | 0 | 0.1 | 542969 | STILWEL5 | 161 | 1.0122 | 0.26 | 364622 | 1WOLFCR H5-6 | 13.8 | 0.9924 | 13134 | 1 | 114.6 | 0 | 0 | 0 | 0 | 0
3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 11 | EKPC_P1-2_GRE-SUMSH161_SRT-A |  | 3 | 0 | 0 | 0.06 | 325118 | 1RHUDES INV | 34.5 | 1.0787 | 0.14 | 325117 | 1RHUDES COL | 34.5 | 1.073 | 0 | 0 | 92.8 | 0 | 0 | 0 | 0 | 0
3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 12 | EKPC_P1-2_BARR-SUMSH161_SRT-A |  | 3 | 0 | 0 | 0.06 | 325118 | 1RHUDES INV | 34.5 | 1.0766 | 0.13 | 325117 | 1RHUDES COL | 34.5 | 1.0711 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 13 | EKPC_P1-2_BULL-SUMSH161_SRT-A |  | 2 | 0 | 0 | 0.19 | 325118 | 1RHUDES INV | 34.5 | 1.0775 | 0.4 | 325117 | 1RHUDES COL | 34.5 | 1.0718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 14 | EKPC_P1-2_SSHAD 161 TIE_SRT-A |  | 1 | 0 | 0 | 0.1 | 542969 | STILWEL5 | 161 | 1.0122 | 0.81 | 361788 | 5SUM SHAD TP | 161 | 1.026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | Ovl | 2 | 0 | 0 | 0.07 | 325118 | 1RHUDES INV | 34.5 | 1.0763 | 0.27 | 324002 | 1BROWN 3 | 24 | 1.0527 | 10516.5 | 1 | 102.5 | 0 | 0 | 0 | 0 | 0
3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 16 | EKPC_P1-3_MAR 161/138_SRT-A | Ovl | 2 | 0 | 0 | 0.22 | 325118 | 1RHUDES INV | 34.5 | 1.0779 | 0.57 | 324002 | 1BROWN 3 | 24 | 1.0534 | 12416.4 | 1 | 111.4 | 0 | 0 | 0 | 0 | 0
3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A |  | 2 | 0 | 0 | 0.32 | 325118 | 1RHUDES INV | 34.5 | 1.0788 | 0.68 | 325117 | 1RHUDES COL | 34.5 | 1.0731 | 0 | 0 | 97.3 | 0 | 0 | 0 | 0 | 0
3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 18 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A |  | 3 | 0 | 0 | 0.04 | 542969 | STILWEL5 | 161 | 1.0122 | 0.17 | 340576 | WILSON | 24 | 1.0013 | 0 | 0 | 97.4 | 0 | 0 | 0 | 0 | 0
3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 19 | EXT_324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1 _SRT-A |  | 1 | 0 | 0 | 0.29 | 342577 | 4FAWKES EK | 138 | 1.0029 | 0.43 | 342577 | 4FAWKES EK | 138 | 1.0029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 20 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.16 | 324002 | 1BROWN 3 | 24 | 1.0521 | 0 | 0 | 97.8 | 0 | 0 | 0 | 0 | 0
3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A |  | 2 | 0 | 0 | 0.29 | 325118 | 1RHUDES INV | 34.5 | 1.0786 | 0.63 | 340576 | WILSON | 24 | 1.0043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 22 | EXT_324217 4BROWN PLANT 138 324219 4BROWN T1 138 1 _SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 23 | EXT_324217 4BROWN PLANT 138 324220 4BROWN T2 138 1 _SRT-A |  | 1 | 0 | 0 | 0.1 | 542969 | STILWEL5 | 161 | 1.0122 | 0.24 | 324015 | 1DIX DAM 2 | 13.2 | 1.0078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 24 | EXT_324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1 _SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.42 | 340576 | WILSON | 24 | 1.004 | 0 | 0 | 93 | 0 | 0 | 0 | 0 | 0
3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A |  | 3 | 0 | 0 | 0.09 | 340576 | WILSON | 24 | 1.0033 | 0.74 | 340576 | WILSON | 24 | 1.0033 | 0 | 0 | 93.1 | 0 | 0 | 0 | 0 | 0
3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 26 | EXT_B-138-111_SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 98.1 | 0 | 0 | 0 | 0 | 0
3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 27 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A_Dup1 |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.16 | 324002 | 1BROWN 3 | 24 | 1.0521 | 0 | 0 | 97.8 | 0 | 0 | 0 | 0 | 0
3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 28 | EXT_BB-1133_SRT-A |  | 2 | 0 | 0 | 0.31 | 325118 | 1RHUDES INV | 34.5 | 1.0787 | 0.67 | 340576 | WILSON | 24 | 1.0042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 29 | EXT_MERE SWS_SRT-A |  | 2 | 0 | 0 | 0.3 | 325118 | 1RHUDES INV | 34.5 | 1.0783 | 0.66 | 325117 | 1RHUDES COL | 34.5 | 1.0726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 30 | EXT_B-138-115_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.26 | 340576 | WILSON | 24 | 1.0019 | 0 | 0 | 92.5 | 0 | 0 | 0 | 0 | 0
3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 31 | EXT_B-138-120_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 32 | EXT_B-138-121_SRT-A |  | 3 | 0 | 0 | 0.04 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 33 | EXT_324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1 _SRT-A |  | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.15 | 325117 | 1RHUDES COL | 34.5 | 1.0707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 34 | EXT_326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1 _SRT-A |  | 2 | 0 | 0 | 0.18 | 325118 | 1RHUDES INV | 34.5 | 1.0774 | 0.38 | 325117 | 1RHUDES COL | 34.5 | 1.0717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 35 | EXT_B-69-18_SRT-A | Ovl | 3 | 0 | 0 | 0.04 | 542969 | STILWEL5 | 161 | 1.0122 | 0.27 | 324002 | 1BROWN 3 | 24 | 1.0529 | 11444.4 | 1 | 107 | 0 | 0 | 0 | 0 | 0
3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 36 | EXT_B-69-19_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.13 | 340576 | WILSON | 24 | 1.0015 | 0 | 0 | 96.8 | 0 | 0 | 0 | 0 | 0
3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 37 | EXT_BB-1066_SRT-A |  | 2 | 0 | 0 | 0.09 | 542969 | STILWEL5 | 161 | 1.0122 | 0.14 | 364620 | 1WOLFCR H1-2 | 13.8 | 0.9919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | EKPC_P1-2_COOP-LAUREL161_SRT-A | 1 | EKPC_P1-2_MAR-KU LEB138 | Ovl | 3 | 0 | 0 | 0.04 | 542969 | STILWEL5 | 161 | 1.0122 | 0.1 | 325130 | 1RHUDES GEN | 0.6 | 1.1042 | 10664 | 1 | 103.3 | 0 | 0 | 0 | 0 | 0
4 | EKPC_P1-2_COOP-LAUREL161_SRT-A | 2 | EKPC_P1-2_COOP-ELIHU161_SRT-A |  | 3 | 0 | 0 | 0.04 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | EKPC_P1-2_COOP-LAUREL161_SRT-A | 3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A |  | 5 | 0 | 0 | 0.02 | 342172 | 2RUSS SPR EK | 69 | 0.9936 | 0.12 | 324002 | 1BROWN 3 | 24 | 1.0519 | 0 | 0 | 95.9 | 0 | 0 | 0 | 0 | 0
4 | EKPC_P1-2_COOP-LAUREL161_SRT-A | 5 | EKPC_P1-2_COOP-DEN161_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.07 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | EKPC_P1-2_COOP-LAUREL161_SRT-A | 6 | EKPC_P1-2_COOP 161 TIE_SRT-A |  | 3 | 0 | 0 | 0.04 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | EKPC_P1-2_COOP-LAUREL161_SRT-A | 7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.21 | 324002 | 1BROWN 3 | 24 | 1.0515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | EKPC_P1-2_COOP-LAUREL161_SRT-A | 8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A |  | 3 | 0 | 0 | 0.12 | 942410 | AE2-254 TAP | 69 | 1.0133 | 0.43 | 324002 | 1BROWN 3 | 24 | 1.0516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | EKPC_P1-2_COOP-LAUREL161_SRT-A | 9 | EKPC_P1-2_LIBJ-GAS161_SRT-A |  | 3 | 0 | 0 | 0.08 | 325118 | 1RHUDES INV | 34.5 | 1.0738 | 0.17 | 325117 | 1RHUDES COL | 34.5 | 1.0684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | EKPC_P1-2_COOP-LAUREL161_SRT-A | 10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | Ovl | 2 | 0 | 0 | 0.1 | 542969 | STILWEL5 | 161 | 1.0122 | 0.23 | 364622 | 1WOLFCR H5-6 | 13.8 | 1.0069 | 11402.3 | 1 | 106.8 | 0 | 0 | 0 | 0 | 0
4 | EKPC_P1-2_COOP-LAUREL161_SRT-A | 11 | EKPC_P1-2_GRE-SUMSH161_SRT-A |  | 4 | 0 | 0 | 0.03 | 325118 | 1RHUDES INV | 34.5 | 1.0766 | 0.13 | 324002 | 1BROWN 3 | 24 | 1.0519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | EKPC_P1-2_COOP-LAUREL161_SRT-A | 12 | EKPC_P1-2_BARR-SUMSH161_SRT-A |  | 3 | 0 | 0 | 0.06 | 325118 | 1RHUDES INV | 34.5 | 1.075 | 0.13 | 325117 | 1RHUDES COL | 34.5 | 1.0695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | EKPC_P1-2_COOP-LAUREL161_SRT-A | 13 | EKPC_P1-2_BULL-SUMSH161_SRT-A |  | 2 | 0 | 0 | 0.18 | 325118 | 1RHUDES INV | 34.5 | 1.0758 | 0.39 | 325117 | 1RHUDES COL | 34.5 | 1.0702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | EKPC_P1-2_COOP-LAUREL161_SRT-A | 14 | EKPC_P1-2_SSHAD 161 TIE_SRT-A |  | 1 | 0 | 0 | 0.11 | 542969 | STILWEL5 | 161 | 1.0122 | 0.84 | 360334 | 5SUMMER SHAD | 161 | 1.0263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | EKPC_P1-2_COOP-LAUREL161_SRT-A | 15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.19 | 324002 | 1BROWN 3 | 24 | 1.0515 | 0 | 0 | 91.9 | 0 | 0 | 0 | 0 | 0
4 | EKPC_P1-2_COOP-LAUREL161_SRT-A | 16 | EKPC_P1-3_MAR 161/138_SRT-A | Ovl | 3 | 0 | 0 | 0.04 | 542969 | STILWEL5 | 161 | 1.0122 | 0.1 | 325130 | 1RHUDES GEN | 0.6 | 1.1042 | 10665 | 1 | 103.3 | 0 | 0 | 0 | 0 | 0
4 | EKPC_P1-2_COOP-LAUREL161_SRT-A | 17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A |  | 2 | 0 | 0 | 0.34 | 325118 | 1RHUDES INV | 34.5 | 1.0774 | 0.72 | 325117 | 1RHUDES COL | 34.5 | 1.0717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | EKPC_P1-2_COOP-LAUREL161_SRT-A | 18 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.16 | 340576 | WILSON | 24 | 1.0011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | EKPC_P1-2_COOP-LAUREL161_SRT-A | 19 | EXT_324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1 _SRT-A |  | 1 | 0 | 0 | 0.34 | 342577 | 4FAWKES EK | 138 | 1.0036 | 0.56 | 324248 | 4FAWKES KU | 138 | 1.0035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | EKPC_P1-2_COOP-LAUREL161_SRT-A | 20 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.13 | 324002 | 1BROWN 3 | 24 | 1.051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | EKPC_P1-2_COOP-LAUREL161_SRT-A | 21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A |  | 2 | 0 | 0 | 0.31 | 325118 | 1RHUDES INV | 34.5 | 1.0771 | 0.65 | 325117 | 1RHUDES COL | 34.5 | 1.0714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | EKPC_P1-2_COOP-LAUREL161_SRT-A | 22 | EXT_324217 4BROWN PLANT 138 324219 4BROWN T1 138 1 _SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | EKPC_P1-2_COOP-LAUREL161_SRT-A | 23 | EXT_324217 4BROWN PLANT 138 324220 4BROWN T2 138 1 _SRT-A |  | 1 | 0 | 0 | 0.11 | 542969 | STILWEL5 | 161 | 1.0122 | 0.23 | 324015 | 1DIX DAM 2 | 13.2 | 1.0079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | EKPC_P1-2_COOP-LAUREL161_SRT-A | 24 | EXT_324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1 _SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.21 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | EKPC_P1-2_COOP-LAUREL161_SRT-A | 25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.08 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | EKPC_P1-2_COOP-LAUREL161_SRT-A | 26 | EXT_B-138-111_SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | EKPC_P1-2_COOP-LAUREL161_SRT-A | 27 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A_Dup1 |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.13 | 324002 | 1BROWN 3 | 24 | 1.051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | EKPC_P1-2_COOP-LAUREL161_SRT-A | 28 | EXT_BB-1133_SRT-A |  | 2 | 0 | 0 | 0.32 | 325118 | 1RHUDES INV | 34.5 | 1.0772 | 0.68 | 325117 | 1RHUDES COL | 34.5 | 1.0715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | EKPC_P1-2_COOP-LAUREL161_SRT-A | 29 | EXT_MERE SWS_SRT-A |  | 2 | 0 | 0 | 0.47 | 325118 | 1RHUDES INV | 34.5 | 1.0788 | 1 | 325117 | 1RHUDES COL | 34.5 | 1.073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | EKPC_P1-2_COOP-LAUREL161_SRT-A | 30 | EXT_B-138-115_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.41 | 324002 | 1BROWN 3 | 24 | 1.0519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | EKPC_P1-2_COOP-LAUREL161_SRT-A | 31 | EXT_B-138-120_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | EKPC_P1-2_COOP-LAUREL161_SRT-A | 32 | EXT_B-138-121_SRT-A |  | 3 | 0 | 0 | 0.04 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | EKPC_P1-2_COOP-LAUREL161_SRT-A | 33 | EXT_324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1 _SRT-A |  | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.16 | 325117 | 1RHUDES COL | 34.5 | 1.0692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | EKPC_P1-2_COOP-LAUREL161_SRT-A | 34 | EXT_326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1 _SRT-A |  | 2 | 0 | 0 | 0.17 | 325118 | 1RHUDES INV | 34.5 | 1.0757 | 0.37 | 325117 | 1RHUDES COL | 34.5 | 1.0701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | EKPC_P1-2_COOP-LAUREL161_SRT-A | 35 | EXT_B-69-18_SRT-A |  | 3 | 0 | 0 | 0.05 | 325118 | 1RHUDES INV | 34.5 | 1.0775 | 0.24 | 324002 | 1BROWN 3 | 24 | 1.0518 | 0 | 0 | 99.1 | 0 | 0 | 0 | 0 | 0
4 | EKPC_P1-2_COOP-LAUREL161_SRT-A | 36 | EXT_B-69-19_SRT-A |  | 4 | 0 | 0 | 0.33 | 325118 | 1RHUDES INV | 34.5 | 1.0742 | 0.7 | 325117 | 1RHUDES COL | 34.5 | 1.0688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | EKPC_P1-2_COOP-LAUREL161_SRT-A | 37 | EXT_BB-1066_SRT-A |  | 2 | 0 | 0 | 0.1 | 542969 | STILWEL5 | 161 | 1.0122 | 0.16 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | EKPC_P1-2_COOP-DEN161_SRT-A | 1 | EKPC_P1-2_MAR-KU LEB138 |  | 2 | 0 | 0 | 0.23 | 325118 | 1RHUDES INV | 34.5 | 1.0764 | 0.59 | 324002 | 1BROWN 3 | 24 | 1.0524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | EKPC_P1-2_COOP-DEN161_SRT-A | 2 | EKPC_P1-2_COOP-ELIHU161_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | EKPC_P1-2_COOP-DEN161_SRT-A | 3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A |  | 4 | 0 | 0 | 0.11 | 325118 | 1RHUDES INV | 34.5 | 1.0751 | 0.41 | 324002 | 1BROWN 3 | 24 | 1.0522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | EKPC_P1-2_COOP-DEN161_SRT-A | 4 | EKPC_P1-2_COOP-LAUREL161_SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 243764 | 05BSG1 | 22 | 0.9922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | EKPC_P1-2_COOP-DEN161_SRT-A | 6 | EKPC_P1-2_COOP 161 TIE_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.22 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | EKPC_P1-2_COOP-DEN161_SRT-A | 7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.15 | 324002 | 1BROWN 3 | 24 | 1.0515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | EKPC_P1-2_COOP-DEN161_SRT-A | 8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.26 | 340576 | WILSON | 24 | 1.0038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | EKPC_P1-2_COOP-DEN161_SRT-A | 9 | EKPC_P1-2_LIBJ-GAS161_SRT-A |  | 3 | 0 | 0 | 0.08 | 325118 | 1RHUDES INV | 34.5 | 1.074 | 0.17 | 325117 | 1RHUDES COL | 34.5 | 1.0685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | EKPC_P1-2_COOP-DEN161_SRT-A | 10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A |  | 2 | 0 | 0 | 0.1 | 542969 | STILWEL5 | 161 | 1.0122 | 0.33 | 364622 | 1WOLFCR H5-6 | 13.8 | 1.0056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | EKPC_P1-2_COOP-DEN161_SRT-A | 11 | EKPC_P1-2_GRE-SUMSH161_SRT-A |  | 3 | 0 | 0 | 0.08 | 325118 | 1RHUDES INV | 34.5 | 1.0765 | 0.17 | 325117 | 1RHUDES COL | 34.5 | 1.0709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | EKPC_P1-2_COOP-DEN161_SRT-A | 12 | EKPC_P1-2_BARR-SUMSH161_SRT-A |  | 3 | 0 | 0 | 0.06 | 325118 | 1RHUDES INV | 34.5 | 1.0751 | 0.13 | 325117 | 1RHUDES COL | 34.5 | 1.0696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | EKPC_P1-2_COOP-DEN161_SRT-A | 13 | EKPC_P1-2_BULL-SUMSH161_SRT-A |  | 2 | 0 | 0 | 0.18 | 325118 | 1RHUDES INV | 34.5 | 1.0759 | 0.38 | 325117 | 1RHUDES COL | 34.5 | 1.0703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | EKPC_P1-2_COOP-DEN161_SRT-A | 14 | EKPC_P1-2_SSHAD 161 TIE_SRT-A |  | 1 | 0 | 0 | 0.11 | 542969 | STILWEL5 | 161 | 1.0122 | 0.83 | 360334 | 5SUMMER SHAD | 161 | 1.0263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | EKPC_P1-2_COOP-DEN161_SRT-A | 15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.18 | 324002 | 1BROWN 3 | 24 | 1.0516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | EKPC_P1-2_COOP-DEN161_SRT-A | 16 | EKPC_P1-3_MAR 161/138_SRT-A |  | 2 | 0 | 0 | 0.23 | 325118 | 1RHUDES INV | 34.5 | 1.0764 | 0.58 | 324002 | 1BROWN 3 | 24 | 1.0524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | EKPC_P1-2_COOP-DEN161_SRT-A | 17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A |  | 2 | 0 | 0 | 0.34 | 325118 | 1RHUDES INV | 34.5 | 1.0775 | 0.72 | 325117 | 1RHUDES COL | 34.5 | 1.0718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | EKPC_P1-2_COOP-DEN161_SRT-A | 18 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.17 | 340576 | WILSON | 24 | 1.0011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | EKPC_P1-2_COOP-DEN161_SRT-A | 19 | EXT_324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1 _SRT-A |  | 1 | 0 | 0 | 0.3 | 342577 | 4FAWKES EK | 138 | 1.0041 | 0.49 | 342577 | 4FAWKES EK | 138 | 1.0041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | EKPC_P1-2_COOP-DEN161_SRT-A | 20 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.15 | 324002 | 1BROWN 3 | 24 | 1.051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | EKPC_P1-2_COOP-DEN161_SRT-A | 21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A |  | 2 | 0 | 0 | 0.31 | 325118 | 1RHUDES INV | 34.5 | 1.0772 | 0.65 | 325117 | 1RHUDES COL | 34.5 | 1.0715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | EKPC_P1-2_COOP-DEN161_SRT-A | 22 | EXT_324217 4BROWN PLANT 138 324219 4BROWN T1 138 1 _SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | EKPC_P1-2_COOP-DEN161_SRT-A | 23 | EXT_324217 4BROWN PLANT 138 324220 4BROWN T2 138 1 _SRT-A |  | 1 | 0 | 0 | 0.11 | 542969 | STILWEL5 | 161 | 1.0122 | 0.23 | 324015 | 1DIX DAM 2 | 13.2 | 1.0082 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | EKPC_P1-2_COOP-DEN161_SRT-A | 24 | EXT_324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1 _SRT-A |  | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.49 | 340576 | WILSON | 24 | 1.0039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | EKPC_P1-2_COOP-DEN161_SRT-A | 25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.11 | 324002 | 1BROWN 3 | 24 | 1.052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | EKPC_P1-2_COOP-DEN161_SRT-A | 26 | EXT_B-138-111_SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | EKPC_P1-2_COOP-DEN161_SRT-A | 27 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A_Dup1 |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.15 | 324002 | 1BROWN 3 | 24 | 1.051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | EKPC_P1-2_COOP-DEN161_SRT-A | 28 | EXT_BB-1133_SRT-A |  | 2 | 0 | 0 | 0.32 | 325118 | 1RHUDES INV | 34.5 | 1.0773 | 0.68 | 325117 | 1RHUDES COL | 34.5 | 1.0717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | EKPC_P1-2_COOP-DEN161_SRT-A | 29 | EXT_MERE SWS_SRT-A |  | 2 | 0 | 0 | 0.47 | 325118 | 1RHUDES INV | 34.5 | 1.0789 | 1 | 325117 | 1RHUDES COL | 34.5 | 1.0731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | EKPC_P1-2_COOP-DEN161_SRT-A | 30 | EXT_B-138-115_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.3 | 324002 | 1BROWN 3 | 24 | 1.0519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | EKPC_P1-2_COOP-DEN161_SRT-A | 31 | EXT_B-138-120_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | EKPC_P1-2_COOP-DEN161_SRT-A | 32 | EXT_B-138-121_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | EKPC_P1-2_COOP-DEN161_SRT-A | 33 | EXT_324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1 _SRT-A |  | 2 | 0 | 0 | 0.09 | 542969 | STILWEL5 | 161 | 1.0122 | 0.17 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | EKPC_P1-2_COOP-DEN161_SRT-A | 34 | EXT_326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1 _SRT-A |  | 2 | 0 | 0 | 0.17 | 325118 | 1RHUDES INV | 34.5 | 1.0758 | 0.36 | 325117 | 1RHUDES COL | 34.5 | 1.0702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | EKPC_P1-2_COOP-DEN161_SRT-A | 35 | EXT_B-69-18_SRT-A |  | 3 | 0 | 0 | 0.05 | 325118 | 1RHUDES INV | 34.5 | 1.0775 | 0.24 | 324002 | 1BROWN 3 | 24 | 1.0518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | EKPC_P1-2_COOP-DEN161_SRT-A | 36 | EXT_B-69-19_SRT-A |  | 4 | 0 | 0 | 0.33 | 325118 | 1RHUDES INV | 34.5 | 1.0743 | 0.7 | 325117 | 1RHUDES COL | 34.5 | 1.0689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | EKPC_P1-2_COOP-DEN161_SRT-A | 37 | EXT_BB-1066_SRT-A |  | 2 | 0 | 0 | 0.1 | 542969 | STILWEL5 | 161 | 1.0122 | 0.18 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | EKPC_P1-2_COOP 161 TIE_SRT-A | 1 | EKPC_P1-2_MAR-KU LEB138 | Ovl | 3 | 0 | 0 | 0.04 | 542969 | STILWEL5 | 161 | 1.0122 | 0.1 | 325130 | 1RHUDES GEN | 0.6 | 1.1048 | 10006.5 | 1 | 100 | 0 | 0 | 0 | 0 | 0
6 | EKPC_P1-2_COOP 161 TIE_SRT-A | 2 | EKPC_P1-2_COOP-ELIHU161_SRT-A |  | 4 | 0 | 0 | 0.03 | 324446 | 2BOND | 69 | 1.0187 | 0.07 | 243764 | 05BSG1 | 22 | 0.9918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | EKPC_P1-2_COOP 161 TIE_SRT-A | 3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A |  | 4 | 0 | 0 | 0.11 | 325118 | 1RHUDES INV | 34.5 | 1.0753 | 0.4 | 324002 | 1BROWN 3 | 24 | 1.0522 | 0 | 0 | 97.1 | 0 | 0 | 0 | 0 | 0
6 | EKPC_P1-2_COOP 161 TIE_SRT-A | 4 | EKPC_P1-2_COOP-LAUREL161_SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 243764 | 05BSG1 | 22 | 0.9922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | EKPC_P1-2_COOP 161 TIE_SRT-A | 5 | EKPC_P1-2_COOP-DEN161_SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | EKPC_P1-2_COOP 161 TIE_SRT-A | 7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.15 | 324002 | 1BROWN 3 | 24 | 1.052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | EKPC_P1-2_COOP 161 TIE_SRT-A | 8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.31 | 340576 | WILSON | 24 | 1.0039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | EKPC_P1-2_COOP 161 TIE_SRT-A | 9 | EKPC_P1-2_LIBJ-GAS161_SRT-A |  | 3 | 0 | 0 | 0.08 | 325118 | 1RHUDES INV | 34.5 | 1.0744 | 0.18 | 325117 | 1RHUDES COL | 34.5 | 1.0689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | EKPC_P1-2_COOP 161 TIE_SRT-A | 10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | Ovl | 2 | 0 | 0 | 0.1 | 542969 | STILWEL5 | 161 | 1.0122 | 0.33 | 364622 | 1WOLFCR H5-6 | 13.8 | 1.0102 | 10681.2 | 1 | 103.3 | 0 | 0 | 0 | 0 | 0
6 | EKPC_P1-2_COOP 161 TIE_SRT-A | 11 | EKPC_P1-2_GRE-SUMSH161_SRT-A |  | 3 | 0 | 0 | 0.08 | 325118 | 1RHUDES INV | 34.5 | 1.0768 | 0.18 | 325117 | 1RHUDES COL | 34.5 | 1.0712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | EKPC_P1-2_COOP 161 TIE_SRT-A | 12 | EKPC_P1-2_BARR-SUMSH161_SRT-A |  | 3 | 0 | 0 | 0.06 | 325118 | 1RHUDES INV | 34.5 | 1.0754 | 0.13 | 325117 | 1RHUDES COL | 34.5 | 1.0699 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | EKPC_P1-2_COOP 161 TIE_SRT-A | 13 | EKPC_P1-2_BULL-SUMSH161_SRT-A |  | 2 | 0 | 0 | 0.18 | 325118 | 1RHUDES INV | 34.5 | 1.0762 | 0.39 | 325117 | 1RHUDES COL | 34.5 | 1.0706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | EKPC_P1-2_COOP 161 TIE_SRT-A | 14 | EKPC_P1-2_SSHAD 161 TIE_SRT-A |  | 1 | 0 | 0 | 0.11 | 542969 | STILWEL5 | 161 | 1.0122 | 0.84 | 360334 | 5SUMMER SHAD | 161 | 1.0262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | EKPC_P1-2_COOP 161 TIE_SRT-A | 15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.18 | 324002 | 1BROWN 3 | 24 | 1.0517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | EKPC_P1-2_COOP 161 TIE_SRT-A | 16 | EKPC_P1-3_MAR 161/138_SRT-A | Ovl | 3 | 0 | 0 | 0.04 | 542969 | STILWEL5 | 161 | 1.0122 | 0.11 | 325130 | 1RHUDES GEN | 0.6 | 1.1048 | 10007.4 | 1 | 100 | 0 | 0 | 0 | 0 | 0
6 | EKPC_P1-2_COOP 161 TIE_SRT-A | 17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A |  | 2 | 0 | 0 | 0.34 | 325118 | 1RHUDES INV | 34.5 | 1.0778 | 0.72 | 325117 | 1RHUDES COL | 34.5 | 1.0721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | EKPC_P1-2_COOP 161 TIE_SRT-A | 18 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.16 | 340576 | WILSON | 24 | 1.0011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | EKPC_P1-2_COOP 161 TIE_SRT-A | 19 | EXT_324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1 _SRT-A |  | 1 | 0 | 0 | 0.3 | 342577 | 4FAWKES EK | 138 | 1.0038 | 0.48 | 342577 | 4FAWKES EK | 138 | 1.0038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | EKPC_P1-2_COOP 161 TIE_SRT-A | 20 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.13 | 324002 | 1BROWN 3 | 24 | 1.0513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | EKPC_P1-2_COOP 161 TIE_SRT-A | 21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A |  | 2 | 0 | 0 | 0.31 | 325118 | 1RHUDES INV | 34.5 | 1.0775 | 0.65 | 325117 | 1RHUDES COL | 34.5 | 1.0718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | EKPC_P1-2_COOP 161 TIE_SRT-A | 22 | EXT_324217 4BROWN PLANT 138 324219 4BROWN T1 138 1 _SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | EKPC_P1-2_COOP 161 TIE_SRT-A | 23 | EXT_324217 4BROWN PLANT 138 324220 4BROWN T2 138 1 _SRT-A |  | 1 | 0 | 0 | 0.11 | 542969 | STILWEL5 | 161 | 1.0122 | 0.24 | 324015 | 1DIX DAM 2 | 13.2 | 1.0091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | EKPC_P1-2_COOP 161 TIE_SRT-A | 24 | EXT_324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1 _SRT-A |  | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.53 | 340576 | WILSON | 24 | 1.0039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | EKPC_P1-2_COOP 161 TIE_SRT-A | 25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.12 | 324002 | 1BROWN 3 | 24 | 1.0522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | EKPC_P1-2_COOP 161 TIE_SRT-A | 26 | EXT_B-138-111_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.12 | 324002 | 1BROWN 3 | 24 | 1.0519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | EKPC_P1-2_COOP 161 TIE_SRT-A | 27 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A_Dup1 |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.13 | 324002 | 1BROWN 3 | 24 | 1.0513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | EKPC_P1-2_COOP 161 TIE_SRT-A | 28 | EXT_BB-1133_SRT-A |  | 2 | 0 | 0 | 0.32 | 325118 | 1RHUDES INV | 34.5 | 1.0776 | 0.69 | 325117 | 1RHUDES COL | 34.5 | 1.0719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | EKPC_P1-2_COOP 161 TIE_SRT-A | 29 | EXT_MERE SWS_SRT-A |  | 2 | 0 | 0 | 0.45 | 325118 | 1RHUDES INV | 34.5 | 1.0789 | 0.95 | 325117 | 1RHUDES COL | 34.5 | 1.0732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | EKPC_P1-2_COOP 161 TIE_SRT-A | 30 | EXT_B-138-115_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.4 | 324002 | 1BROWN 3 | 24 | 1.0521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | EKPC_P1-2_COOP 161 TIE_SRT-A | 31 | EXT_B-138-120_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | EKPC_P1-2_COOP 161 TIE_SRT-A | 32 | EXT_B-138-121_SRT-A |  | 3 | 0 | 0 | 0.04 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | EKPC_P1-2_COOP 161 TIE_SRT-A | 33 | EXT_324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1 _SRT-A |  | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.17 | 325117 | 1RHUDES COL | 34.5 | 1.0696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | EKPC_P1-2_COOP 161 TIE_SRT-A | 34 | EXT_326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1 _SRT-A |  | 2 | 0 | 0 | 0.17 | 325118 | 1RHUDES INV | 34.5 | 1.0761 | 0.37 | 325117 | 1RHUDES COL | 34.5 | 1.0705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | EKPC_P1-2_COOP 161 TIE_SRT-A | 35 | EXT_B-69-18_SRT-A |  | 3 | 0 | 0 | 0.05 | 325118 | 1RHUDES INV | 34.5 | 1.0774 | 0.25 | 324002 | 1BROWN 3 | 24 | 1.0521 | 0 | 0 | 96.3 | 0 | 0 | 0 | 0 | 0
6 | EKPC_P1-2_COOP 161 TIE_SRT-A | 36 | EXT_B-69-19_SRT-A |  | 4 | 0 | 0 | 0.33 | 325118 | 1RHUDES INV | 34.5 | 1.0746 | 0.7 | 325117 | 1RHUDES COL | 34.5 | 1.0692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | EKPC_P1-2_COOP 161 TIE_SRT-A | 37 | EXT_BB-1066_SRT-A |  | 2 | 0 | 0 | 0.1 | 542969 | STILWEL5 | 161 | 1.0122 | 0.17 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 1 | EKPC_P1-2_MAR-KU LEB138 | Ovl | 3 | 0 | 0 | 0.05 | 325118 | 1RHUDES INV | 34.5 | 1.0772 | 0.15 | 325130 | 1RHUDES GEN | 0.6 | 1.1049 | 10532.6 | 1 | 102.6 | 0 | 0 | 0 | 0 | 0
7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 2 | EKPC_P1-2_COOP-ELIHU161_SRT-A |  | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.33 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | Ovl | 5 | 0 | 0 | 0.03 | 324446 | 2BOND | 69 | 1.0159 | 0.09 | 324002 | 1BROWN 3 | 24 | 1.0522 | 10609.1 | 1 | 103 | 0 | 0 | 0 | 0 | 0
7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 4 | EKPC_P1-2_COOP-LAUREL161_SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 243764 | 05BSG1 | 22 | 0.9924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 5 | EKPC_P1-2_COOP-DEN161_SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 324002 | 1BROWN 3 | 24 | 1.0515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 6 | EKPC_P1-2_COOP 161 TIE_SRT-A |  | 1 | 0 | 0 | 0.31 | 341344 | 2COOPER | 69 | 0.9948 | 0.54 | 341344 | 2COOPER | 69 | 0.9948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A | Ovl | 4 | 0 | 0 | 0.24 | 341761 | 2LIBERTY J | 69 | 1.0034 | 0.28 | 341761 | 2LIBERTY J | 69 | 1.0034 | 192963.8 | 8 | 195.9 | 0 | 0 | 0 | 0 | 0
7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 9 | EKPC_P1-2_LIBJ-GAS161_SRT-A | Ovl | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.08 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0099 | 10709.4 | 1 | 103.5 | 0 | 0 | 0 | 0 | 0
7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | Ovl | 3 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.16 | 324002 | 1BROWN 3 | 24 | 1.0519 | 31930.8 | 3 | 106.3 | 0 | 0 | 0 | 0 | 0
7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 11 | EKPC_P1-2_GRE-SUMSH161_SRT-A |  | 2 | 0 | 0 | 0.21 | 325118 | 1RHUDES INV | 34.5 | 1.0762 | 0.44 | 325117 | 1RHUDES COL | 34.5 | 1.0706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 12 | EKPC_P1-2_BARR-SUMSH161_SRT-A |  | 3 | 0 | 0 | 0.07 | 325118 | 1RHUDES INV | 34.5 | 1.0751 | 0.15 | 325117 | 1RHUDES COL | 34.5 | 1.0696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 13 | EKPC_P1-2_BULL-SUMSH161_SRT-A |  | 2 | 0 | 0 | 0.18 | 325118 | 1RHUDES INV | 34.5 | 1.0759 | 0.38 | 325117 | 1RHUDES COL | 34.5 | 1.0703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 14 | EKPC_P1-2_SSHAD 161 TIE_SRT-A |  | 1 | 0 | 0 | 0.11 | 542969 | STILWEL5 | 161 | 1.0122 | 0.87 | 360334 | 5SUMMER SHAD | 161 | 1.0262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.27 | 324002 | 1BROWN 3 | 24 | 1.0521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 16 | EKPC_P1-3_MAR 161/138_SRT-A | Ovl | 3 | 0 | 0 | 0.05 | 325118 | 1RHUDES INV | 34.5 | 1.0772 | 0.15 | 325130 | 1RHUDES GEN | 0.6 | 1.1049 | 10533.4 | 1 | 102.6 | 0 | 0 | 0 | 0 | 0
7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.14 | 325130 | 1RHUDES GEN | 0.6 | 1.1053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 18 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.14 | 340576 | WILSON | 24 | 1.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 19 | EXT_324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1 _SRT-A |  | 1 | 0 | 0 | 0.34 | 342577 | 4FAWKES EK | 138 | 1.0031 | 0.55 | 324248 | 4FAWKES KU | 138 | 1.003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 20 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.09 | 325117 | 1RHUDES COL | 34.5 | 1.069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.12 | 325130 | 1RHUDES GEN | 0.6 | 1.1048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 22 | EXT_324217 4BROWN PLANT 138 324219 4BROWN T1 138 1 _SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 23 | EXT_324217 4BROWN PLANT 138 324220 4BROWN T2 138 1 _SRT-A |  | 1 | 0 | 0 | 0.11 | 542969 | STILWEL5 | 161 | 1.0122 | 0.24 | 324015 | 1DIX DAM 2 | 13.2 | 1.0136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 24 | EXT_324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1 _SRT-A |  | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.18 | 340576 | WILSON | 24 | 1.0036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.1 | 324002 | 1BROWN 3 | 24 | 1.0526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 26 | EXT_B-138-111_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.16 | 324002 | 1BROWN 3 | 24 | 1.0523 | 0 | 0 | 94.8 | 0 | 0 | 0 | 0 | 0
7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 27 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A_Dup1 |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.09 | 325117 | 1RHUDES COL | 34.5 | 1.069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 28 | EXT_BB-1133_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.13 | 325130 | 1RHUDES GEN | 0.6 | 1.1051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 29 | EXT_MERE SWS_SRT-A |  | 3 | 0 | 0 | 0.06 | 325118 | 1RHUDES INV | 34.5 | 1.0786 | 0.11 | 325117 | 1RHUDES COL | 34.5 | 1.0729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 30 | EXT_B-138-115_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.27 | 340576 | WILSON | 24 | 1.0016 | 0 | 0 | 98.9 | 0 | 0 | 0 | 0 | 0
7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 31 | EXT_B-138-120_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 32 | EXT_B-138-121_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 33 | EXT_324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1 _SRT-A |  | 2 | 0 | 0 | 0.09 | 542969 | STILWEL5 | 161 | 1.0122 | 0.17 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 34 | EXT_326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1 _SRT-A |  | 2 | 0 | 0 | 0.17 | 325118 | 1RHUDES INV | 34.5 | 1.0758 | 0.36 | 325117 | 1RHUDES COL | 34.5 | 1.0702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 35 | EXT_B-69-18_SRT-A | Ovl | 3 | 0 | 0 | 0.05 | 325118 | 1RHUDES INV | 34.5 | 1.0775 | 0.3 | 324002 | 1BROWN 3 | 24 | 1.0524 | 10163.8 | 1 | 100.8 | 0 | 0 | 0 | 0 | 0
7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 36 | EXT_B-69-19_SRT-A |  | 4 | 0 | 0 | 0.33 | 325118 | 1RHUDES INV | 34.5 | 1.0743 | 0.7 | 325117 | 1RHUDES COL | 34.5 | 1.0689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 37 | EXT_BB-1066_SRT-A |  | 2 | 0 | 0 | 0.1 | 542969 | STILWEL5 | 161 | 1.0122 | 0.17 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A | 1 | EKPC_P1-2_MAR-KU LEB138 |  | 2 | 0 | 0 | 0.19 | 325118 | 1RHUDES INV | 34.5 | 1.0774 | 0.41 | 325117 | 1RHUDES COL | 34.5 | 1.0718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A | 2 | EKPC_P1-2_COOP-ELIHU161_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A | 3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A |  | 4 | 0 | 0 | 0.13 | 325118 | 1RHUDES INV | 34.5 | 1.0762 | 0.55 | 324002 | 1BROWN 3 | 24 | 1.0526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A | 4 | EKPC_P1-2_COOP-LAUREL161_SRT-A |  | 3 | 0 | 0 | 0.15 | 324446 | 2BOND | 69 | 1.0161 | 0.55 | 324002 | 1BROWN 3 | 24 | 1.0517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A | 5 | EKPC_P1-2_COOP-DEN161_SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A | 6 | EKPC_P1-2_COOP 161 TIE_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.2 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A | 7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | Ovl | 3 | 0 | 0 | 0.19 | 341761 | 2LIBERTY J | 69 | 1.0024 | 0.35 | 364001 | 1BR FERRY N1 | 22 | 1.0429 | 192915.3 | 8 | 195.8 | 0 | 0 | 0 | 0 | 0
8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A | 9 | EKPC_P1-2_LIBJ-GAS161_SRT-A |  | 3 | 0 | 0 | 0.08 | 360408 | 5NICKJACK HP | 161 | 1.0311 | 0.19 | 364521 | 1NICKAJACK 1 | 13.8 | 0.9877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A | 10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A |  | 2 | 0 | 0 | 0.1 | 316293 | AC1-161 COL2 | 34.5 | 1.0794 | 0.26 | 340576 | WILSON | 24 | 1.0033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A | 11 | EKPC_P1-2_GRE-SUMSH161_SRT-A |  | 2 | 0 | 0 | 0.22 | 325118 | 1RHUDES INV | 34.5 | 1.0777 | 0.46 | 325117 | 1RHUDES COL | 34.5 | 1.0721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A | 12 | EKPC_P1-2_BARR-SUMSH161_SRT-A |  | 3 | 0 | 0 | 0.06 | 325118 | 1RHUDES INV | 34.5 | 1.0765 | 0.13 | 325117 | 1RHUDES COL | 34.5 | 1.071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A | 13 | EKPC_P1-2_BULL-SUMSH161_SRT-A |  | 2 | 0 | 0 | 0.18 | 325118 | 1RHUDES INV | 34.5 | 1.0772 | 0.39 | 325117 | 1RHUDES COL | 34.5 | 1.0716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A | 14 | EKPC_P1-2_SSHAD 161 TIE_SRT-A |  | 1 | 0 | 0 | 0.11 | 542969 | STILWEL5 | 161 | 1.0122 | 0.84 | 360334 | 5SUMMER SHAD | 161 | 1.0257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A | 15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.17 | 324002 | 1BROWN 3 | 24 | 1.052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A | 16 | EKPC_P1-3_MAR 161/138_SRT-A |  | 2 | 0 | 0 | 0.19 | 325118 | 1RHUDES INV | 34.5 | 1.0774 | 0.41 | 325117 | 1RHUDES COL | 34.5 | 1.0718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A | 17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A |  | 2 | 0 | 0 | 0.33 | 325118 | 1RHUDES INV | 34.5 | 1.0788 | 0.74 | 340576 | WILSON | 24 | 1.0044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A | 18 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.18 | 340576 | WILSON | 24 | 1.0013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A | 19 | EXT_324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1 _SRT-A |  | 1 | 0 | 0 | 0.27 | 342577 | 4FAWKES EK | 138 | 1.0036 | 0.42 | 340576 | WILSON | 24 | 1.0039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A | 20 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.29 | 340576 | WILSON | 24 | 1.0042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A | 21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A |  | 2 | 0 | 0 | 0.3 | 325118 | 1RHUDES INV | 34.5 | 1.0785 | 0.76 | 340576 | WILSON | 24 | 1.0045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A | 22 | EXT_324217 4BROWN PLANT 138 324219 4BROWN T1 138 1 _SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A | 23 | EXT_324217 4BROWN PLANT 138 324220 4BROWN T2 138 1 _SRT-A |  | 1 | 0 | 0 | 0.11 | 542969 | STILWEL5 | 161 | 1.0122 | 0.25 | 324015 | 1DIX DAM 2 | 13.2 | 1.0094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A | 24 | EXT_324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1 _SRT-A |  | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.45 | 340576 | WILSON | 24 | 1.0044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A | 25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A |  | 4 | 0 | 0 | 0.09 | 340576 | WILSON | 24 | 1.0033 | 0.68 | 340576 | WILSON | 24 | 1.0033 | 0 | 0 | 91 | 0 | 0 | 0 | 0 | 0
8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A | 26 | EXT_B-138-111_SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A | 27 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A_Dup1 |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.29 | 340576 | WILSON | 24 | 1.0042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A | 28 | EXT_BB-1133_SRT-A |  | 2 | 0 | 0 | 0.31 | 325118 | 1RHUDES INV | 34.5 | 1.0786 | 0.76 | 340576 | WILSON | 24 | 1.0044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A | 29 | EXT_MERE SWS_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.08 | 325117 | 1RHUDES COL | 34.5 | 1.0724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A | 30 | EXT_B-138-115_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.28 | 340576 | WILSON | 24 | 1.0019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A | 31 | EXT_B-138-120_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A | 32 | EXT_B-138-121_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A | 33 | EXT_324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1 _SRT-A |  | 2 | 0 | 0 | 0.09 | 542969 | STILWEL5 | 161 | 1.0122 | 0.17 | 325117 | 1RHUDES COL | 34.5 | 1.0707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A | 34 | EXT_326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1 _SRT-A |  | 2 | 0 | 0 | 0.17 | 325118 | 1RHUDES INV | 34.5 | 1.0771 | 0.37 | 325117 | 1RHUDES COL | 34.5 | 1.0715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A | 35 | EXT_B-69-18_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.23 | 324002 | 1BROWN 3 | 24 | 1.0522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A | 36 | EXT_B-69-19_SRT-A |  | 4 | 0 | 0 | 0.29 | 325118 | 1RHUDES INV | 34.5 | 1.0756 | 0.61 | 325117 | 1RHUDES COL | 34.5 | 1.0701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A | 37 | EXT_BB-1066_SRT-A |  | 2 | 0 | 0 | 0.1 | 542969 | STILWEL5 | 161 | 1.0122 | 0.18 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | EKPC_P1-2_LIBJ-GAS161_SRT-A | 1 | EKPC_P1-2_MAR-KU LEB138 | Ovl | 3 | 0 | 0 | 0.04 | 325118 | 1RHUDES INV | 34.5 | 1.0779 | 0.14 | 325130 | 1RHUDES GEN | 0.6 | 1.1059 | 11180.4 | 1 | 105.7 | 0 | 0 | 0 | 0 | 0
9 | EKPC_P1-2_LIBJ-GAS161_SRT-A | 2 | EKPC_P1-2_COOP-ELIHU161_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | EKPC_P1-2_LIBJ-GAS161_SRT-A | 3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A |  | 5 | 0 | 0 | 0.06 | 324446 | 2BOND | 69 | 1.018 | 0.18 | 324002 | 1BROWN 3 | 24 | 1.0516 | 0 | 0 | 96.8 | 0 | 0 | 0 | 0 | 0
9 | EKPC_P1-2_LIBJ-GAS161_SRT-A | 4 | EKPC_P1-2_COOP-LAUREL161_SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 243764 | 05BSG1 | 22 | 0.9925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | EKPC_P1-2_LIBJ-GAS161_SRT-A | 5 | EKPC_P1-2_COOP-DEN161_SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | EKPC_P1-2_LIBJ-GAS161_SRT-A | 6 | EKPC_P1-2_COOP 161 TIE_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.2 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | EKPC_P1-2_LIBJ-GAS161_SRT-A | 7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | Ovl | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.24 | 324002 | 1BROWN 3 | 24 | 1.0523 | 10709.9 | 1 | 103.5 | 0 | 0 | 0 | 0 | 0
9 | EKPC_P1-2_LIBJ-GAS161_SRT-A | 8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A |  | 3 | 0 | 0 | 0.1 | 325118 | 1RHUDES INV | 34.5 | 1.0787 | 0.31 | 324002 | 1BROWN 3 | 24 | 1.0527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | EKPC_P1-2_LIBJ-GAS161_SRT-A | 10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | Ovl | 3 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.12 | 325117 | 1RHUDES COL | 34.5 | 1.0689 | 21809.6 | 2 | 106.5 | 0 | 0 | 0 | 0 | 0
9 | EKPC_P1-2_LIBJ-GAS161_SRT-A | 11 | EKPC_P1-2_GRE-SUMSH161_SRT-A |  | 2 | 0 | 0 | 0.2 | 325118 | 1RHUDES INV | 34.5 | 1.0767 | 0.43 | 325117 | 1RHUDES COL | 34.5 | 1.071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | EKPC_P1-2_LIBJ-GAS161_SRT-A | 12 | EKPC_P1-2_BARR-SUMSH161_SRT-A |  | 3 | 0 | 0 | 0.07 | 325118 | 1RHUDES INV | 34.5 | 1.0756 | 0.15 | 325117 | 1RHUDES COL | 34.5 | 1.0701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | EKPC_P1-2_LIBJ-GAS161_SRT-A | 13 | EKPC_P1-2_BULL-SUMSH161_SRT-A |  | 2 | 0 | 0 | 0.18 | 325118 | 1RHUDES INV | 34.5 | 1.0764 | 0.38 | 325117 | 1RHUDES COL | 34.5 | 1.0708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | EKPC_P1-2_LIBJ-GAS161_SRT-A | 14 | EKPC_P1-2_SSHAD 161 TIE_SRT-A |  | 1 | 0 | 0 | 0.11 | 542969 | STILWEL5 | 161 | 1.0122 | 0.89 | 360334 | 5SUMMER SHAD | 161 | 1.0259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | EKPC_P1-2_LIBJ-GAS161_SRT-A | 15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.28 | 324002 | 1BROWN 3 | 24 | 1.0525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | EKPC_P1-2_LIBJ-GAS161_SRT-A | 16 | EKPC_P1-3_MAR 161/138_SRT-A | Ovl | 3 | 0 | 0 | 0.04 | 325118 | 1RHUDES INV | 34.5 | 1.0779 | 0.14 | 325130 | 1RHUDES GEN | 0.6 | 1.1059 | 11181.7 | 1 | 105.7 | 0 | 0 | 0 | 0 | 0
9 | EKPC_P1-2_LIBJ-GAS161_SRT-A | 17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A |  | 2 | 0 | 0 | 0.31 | 325118 | 1RHUDES INV | 34.5 | 1.0778 | 0.66 | 325117 | 1RHUDES COL | 34.5 | 1.0721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | EKPC_P1-2_LIBJ-GAS161_SRT-A | 18 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.13 | 340576 | WILSON | 24 | 1.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | EKPC_P1-2_LIBJ-GAS161_SRT-A | 19 | EXT_324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1 _SRT-A |  | 1 | 0 | 0 | 0.34 | 342577 | 4FAWKES EK | 138 | 1.0032 | 0.54 | 324248 | 4FAWKES KU | 138 | 1.0031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | EKPC_P1-2_LIBJ-GAS161_SRT-A | 20 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.13 | 325117 | 1RHUDES COL | 34.5 | 1.0697 | 0 | 0 | 99.1 | 0 | 0 | 0 | 0 | 0
9 | EKPC_P1-2_LIBJ-GAS161_SRT-A | 21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A |  | 2 | 0 | 0 | 0.27 | 325118 | 1RHUDES INV | 34.5 | 1.0774 | 0.57 | 325117 | 1RHUDES COL | 34.5 | 1.0717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | EKPC_P1-2_LIBJ-GAS161_SRT-A | 22 | EXT_324217 4BROWN PLANT 138 324219 4BROWN T1 138 1 _SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | EKPC_P1-2_LIBJ-GAS161_SRT-A | 23 | EXT_324217 4BROWN PLANT 138 324220 4BROWN T2 138 1 _SRT-A |  | 1 | 0 | 0 | 0.11 | 542969 | STILWEL5 | 161 | 1.0122 | 0.26 | 324015 | 1DIX DAM 2 | 13.2 | 1.0085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | EKPC_P1-2_LIBJ-GAS161_SRT-A | 24 | EXT_324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1 _SRT-A |  | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.14 | 325117 | 1RHUDES COL | 34.5 | 1.0697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | EKPC_P1-2_LIBJ-GAS161_SRT-A | 25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.1 | 324002 | 1BROWN 3 | 24 | 1.0529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | EKPC_P1-2_LIBJ-GAS161_SRT-A | 26 | EXT_B-138-111_SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 98.6 | 0 | 0 | 0 | 0 | 0
9 | EKPC_P1-2_LIBJ-GAS161_SRT-A | 27 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A_Dup1 |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.13 | 325117 | 1RHUDES COL | 34.5 | 1.0697 | 0 | 0 | 99.1 | 0 | 0 | 0 | 0 | 0
9 | EKPC_P1-2_LIBJ-GAS161_SRT-A | 28 | EXT_BB-1133_SRT-A |  | 2 | 0 | 0 | 0.29 | 325118 | 1RHUDES INV | 34.5 | 1.0776 | 0.62 | 325117 | 1RHUDES COL | 34.5 | 1.0719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | EKPC_P1-2_LIBJ-GAS161_SRT-A | 29 | EXT_MERE SWS_SRT-A |  | 2 | 0 | 0 | 0.42 | 325118 | 1RHUDES INV | 34.5 | 1.0789 | 0.89 | 325117 | 1RHUDES COL | 34.5 | 1.0732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | EKPC_P1-2_LIBJ-GAS161_SRT-A | 30 | EXT_B-138-115_SRT-A | Ovl | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.27 | 340576 | WILSON | 24 | 1.0016 | 10689.4 | 1 | 103.4 | 0 | 0 | 0 | 0 | 0
9 | EKPC_P1-2_LIBJ-GAS161_SRT-A | 31 | EXT_B-138-120_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | EKPC_P1-2_LIBJ-GAS161_SRT-A | 32 | EXT_B-138-121_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | EKPC_P1-2_LIBJ-GAS161_SRT-A | 33 | EXT_324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1 _SRT-A |  | 2 | 0 | 0 | 0.09 | 542969 | STILWEL5 | 161 | 1.0122 | 0.17 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | EKPC_P1-2_LIBJ-GAS161_SRT-A | 34 | EXT_326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1 _SRT-A |  | 2 | 0 | 0 | 0.17 | 325118 | 1RHUDES INV | 34.5 | 1.0763 | 0.36 | 325117 | 1RHUDES COL | 34.5 | 1.0707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | EKPC_P1-2_LIBJ-GAS161_SRT-A | 35 | EXT_B-69-18_SRT-A | Ovl Vlt | 3 | 0 | 0 | 0.05 | 325118 | 1RHUDES INV | 34.5 | 1.0773 | 0.32 | 324002 | 1BROWN 3 | 24 | 1.0527 | 11494.2 | 1 | 107.2 | 0 | 1 | 0 | 0 | 0
9 | EKPC_P1-2_LIBJ-GAS161_SRT-A | 36 | EXT_B-69-19_SRT-A |  | 4 | 0 | 0 | 0.34 | 325118 | 1RHUDES INV | 34.5 | 1.0746 | 0.72 | 325117 | 1RHUDES COL | 34.5 | 1.0691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | EKPC_P1-2_LIBJ-GAS161_SRT-A | 37 | EXT_BB-1066_SRT-A |  | 2 | 0 | 0 | 0.1 | 542969 | STILWEL5 | 161 | 1.0122 | 0.17 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 1 | EKPC_P1-2_MAR-KU LEB138 | Ovl | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.19 | 340576 | WILSON | 24 | 1.0047 | 30207.4 | 1 | 173.8 | 0 | 0 | 0 | 0 | 0
10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 2 | EKPC_P1-2_COOP-ELIHU161_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | Ovl | 4 | 0 | 0 | 0.15 | 325118 | 1RHUDES INV | 34.5 | 1.0753 | 0.48 | 324002 | 1BROWN 3 | 24 | 1.0525 | 13135.3 | 1 | 114.6 | 0 | 0 | 0 | 0 | 0
10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 4 | EKPC_P1-2_COOP-LAUREL161_SRT-A | Ovl | 3 | 0 | 0 | 0.15 | 324446 | 2BOND | 69 | 1.0163 | 0.55 | 324002 | 1BROWN 3 | 24 | 1.0514 | 11401.6 | 1 | 106.8 | 0 | 0 | 0 | 0 | 0
10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 5 | EKPC_P1-2_COOP-DEN161_SRT-A |  | 4 | 0 | 0 | 0.04 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 6 | EKPC_P1-2_COOP 161 TIE_SRT-A | Ovl | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.21 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0108 | 10681.5 | 1 | 103.4 | 0 | 0 | 0 | 0 | 0
10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | Ovl | 3 | 0 | 0 | 0.06 | 542969 | STILWEL5 | 161 | 1.0122 | 0.13 | 324002 | 1BROWN 3 | 24 | 1.052 | 31932.6 | 3 | 106.3 | 0 | 0 | 0 | 0 | 0
10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A |  | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.1 | 340576 | WILSON | 24 | 1.0033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 9 | EKPC_P1-2_LIBJ-GAS161_SRT-A | Ovl | 4 | 0 | 0 | 0.04 | 325118 | 1RHUDES INV | 34.5 | 1.0743 | 0.1 | 324002 | 1BROWN 3 | 24 | 1.0525 | 21807.9 | 2 | 106.5 | 0 | 0 | 0 | 0 | 0
10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 11 | EKPC_P1-2_GRE-SUMSH161_SRT-A | Ovl | 6 | 0 | 0 | 0.09 | 325118 | 1RHUDES INV | 34.5 | 1.0705 | 0.33 | 325130 | 1RHUDES GEN | 0.6 | 1.0956 | 10304 | 1 | 101.5 | 0 | 0 | 0 | 0 | 0
10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 12 | EKPC_P1-2_BARR-SUMSH161_SRT-A |  | 3 | 0 | 0 | 0.07 | 325118 | 1RHUDES INV | 34.5 | 1.075 | 0.15 | 325117 | 1RHUDES COL | 34.5 | 1.0695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 13 | EKPC_P1-2_BULL-SUMSH161_SRT-A |  | 2 | 0 | 0 | 0.17 | 325118 | 1RHUDES INV | 34.5 | 1.0758 | 0.37 | 325117 | 1RHUDES COL | 34.5 | 1.0702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 14 | EKPC_P1-2_SSHAD 161 TIE_SRT-A |  | 1 | 0 | 0 | 0.13 | 542969 | STILWEL5 | 161 | 1.0122 | 0.86 | 361788 | 5SUM SHAD TP | 161 | 1.0251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A |  | 1 | 0 | 0 | 0.13 | 542969 | STILWEL5 | 161 | 1.0122 | 0.09 | 324751 | 2TAYLOR CO | 69 | 0.9612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 16 | EKPC_P1-3_MAR 161/138_SRT-A | Ovl | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.19 | 340576 | WILSON | 24 | 1.0047 | 30211 | 1 | 173.8 | 0 | 0 | 0 | 0 | 0
10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A |  | 2 | 0 | 0 | 0.36 | 325118 | 1RHUDES INV | 34.5 | 1.0778 | 0.76 | 325117 | 1RHUDES COL | 34.5 | 1.0721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 18 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A | Ovl | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.14 | 340576 | WILSON | 24 | 1.0009 | 11502.5 | 1 | 107.2 | 0 | 0 | 0 | 0 | 0
10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 19 | EXT_324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1 _SRT-A |  | 1 | 0 | 0 | 0.32 | 342577 | 4FAWKES EK | 138 | 1.0037 | 0.52 | 324248 | 4FAWKES KU | 138 | 1.0036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 20 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A | Ovl | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 12762.6 | 1 | 113 | 0 | 0 | 0 | 0 | 0
10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A |  | 2 | 0 | 0 | 0.32 | 325118 | 1RHUDES INV | 34.5 | 1.0774 | 0.69 | 325117 | 1RHUDES COL | 34.5 | 1.0717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 22 | EXT_324217 4BROWN PLANT 138 324219 4BROWN T1 138 1 _SRT-A |  | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 23 | EXT_324217 4BROWN PLANT 138 324220 4BROWN T2 138 1 _SRT-A |  | 1 | 0 | 0 | 0.13 | 542969 | STILWEL5 | 161 | 1.0122 | 0.24 | 324015 | 1DIX DAM 2 | 13.2 | 1.0097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 24 | EXT_324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1 _SRT-A | Ovl | 2 | 0 | 0 | 0.09 | 542969 | STILWEL5 | 161 | 1.0122 | 0.19 | 340576 | WILSON | 24 | 1.0034 | 10685.8 | 1 | 103.4 | 0 | 0 | 0 | 0 | 0
10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | Ovl | 4 | 0 | 0 | 0.04 | 542969 | STILWEL5 | 161 | 1.0122 | 0.08 | 324002 | 1BROWN 3 | 24 | 1.0522 | 10364.1 | 1 | 101.8 | 0 | 0 | 0 | 0 | 0
10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 26 | EXT_B-138-111_SRT-A | Ovl | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.14 | 324002 | 1BROWN 3 | 24 | 1.052 | 12788.7 | 1 | 113.1 | 0 | 0 | 0 | 0 | 0
10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 27 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A_Dup1 | Ovl | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 12762.6 | 1 | 113 | 0 | 0 | 0 | 0 | 0
10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 28 | EXT_BB-1133_SRT-A |  | 2 | 0 | 0 | 0.34 | 325118 | 1RHUDES INV | 34.5 | 1.0776 | 0.73 | 325117 | 1RHUDES COL | 34.5 | 1.0719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 29 | EXT_MERE SWS_SRT-A |  | 3 | 0 | 0 | 0.05 | 325118 | 1RHUDES INV | 34.5 | 1.0786 | 0.11 | 325117 | 1RHUDES COL | 34.5 | 1.0729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 30 | EXT_B-138-115_SRT-A | Ovl | 3 | 0 | 0 | 0.06 | 542969 | STILWEL5 | 161 | 1.0122 | 0.25 | 340576 | WILSON | 24 | 1.0015 | 10219.2 | 1 | 101.1 | 0 | 0 | 0 | 0 | 0
10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 31 | EXT_B-138-120_SRT-A |  | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 32 | EXT_B-138-121_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 33 | EXT_324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1 _SRT-A |  | 2 | 0 | 0 | 0.1 | 542969 | STILWEL5 | 161 | 1.0122 | 0.21 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0095 | 0 | 0 | 90.6 | 0 | 0 | 0 | 0 | 0
10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 34 | EXT_326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1 _SRT-A |  | 2 | 0 | 0 | 0.16 | 325118 | 1RHUDES INV | 34.5 | 1.0757 | 0.35 | 325117 | 1RHUDES COL | 34.5 | 1.0701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 35 | EXT_B-69-18_SRT-A | Ovl Vlt | 5 | 0 | 0 | 0.37 | 325118 | 1RHUDES INV | 34.5 | 1.0748 | 0.78 | 325117 | 1RHUDES COL | 34.5 | 1.0693 | 68369.1 | 3 | 173.8 | 1.5 | 9 | 0 | 0 | 0
10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 36 | EXT_B-69-19_SRT-A |  | 4 | 0 | 0 | 0.35 | 325118 | 1RHUDES INV | 34.5 | 1.0746 | 0.73 | 325117 | 1RHUDES COL | 34.5 | 1.0691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | 37 | EXT_BB-1066_SRT-A |  | 2 | 0 | 0 | 0.11 | 542969 | STILWEL5 | 161 | 1.0122 | 0.22 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0095 | 0 | 0 | 90.7 | 0 | 0 | 0 | 0 | 0
11 | EKPC_P1-2_GRE-SUMSH161_SRT-A | 1 | EKPC_P1-2_MAR-KU LEB138 | Ovl | 3 | 0 | 0 | 0.04 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 324002 | 1BROWN 3 | 24 | 1.053 | 10047.2 | 1 | 100.2 | 0 | 0 | 0 | 0 | 0
11 | EKPC_P1-2_GRE-SUMSH161_SRT-A | 2 | EKPC_P1-2_COOP-ELIHU161_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 90.4 | 0 | 0 | 0 | 0 | 0
11 | EKPC_P1-2_GRE-SUMSH161_SRT-A | 3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A |  | 5 | 0 | 0 | 0.34 | 325118 | 1RHUDES INV | 34.5 | 1.075 | 0.73 | 325117 | 1RHUDES COL | 34.5 | 1.0695 | 0 | 0 | 92.5 | 0 | 0 | 0 | 0 | 0
11 | EKPC_P1-2_GRE-SUMSH161_SRT-A | 4 | EKPC_P1-2_COOP-LAUREL161_SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | EKPC_P1-2_GRE-SUMSH161_SRT-A | 5 | EKPC_P1-2_COOP-DEN161_SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | EKPC_P1-2_GRE-SUMSH161_SRT-A | 6 | EKPC_P1-2_COOP 161 TIE_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.18 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | EKPC_P1-2_GRE-SUMSH161_SRT-A | 7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.18 | 324002 | 1BROWN 3 | 24 | 1.0525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | EKPC_P1-2_GRE-SUMSH161_SRT-A | 8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A |  | 3 | 0 | 0 | 0.04 | 542969 | STILWEL5 | 161 | 1.0122 | 0.17 | 324002 | 1BROWN 3 | 24 | 1.0522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | EKPC_P1-2_GRE-SUMSH161_SRT-A | 9 | EKPC_P1-2_LIBJ-GAS161_SRT-A |  | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.39 | 324002 | 1BROWN 3 | 24 | 1.0527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | EKPC_P1-2_GRE-SUMSH161_SRT-A | 10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | Ovl | 6 | 0 | 0 | 0.09 | 325118 | 1RHUDES INV | 34.5 | 1.0705 | 0.33 | 325130 | 1RHUDES GEN | 0.6 | 1.0956 | 10304 | 1 | 101.5 | 0 | 0 | 0 | 0 | 0
11 | EKPC_P1-2_GRE-SUMSH161_SRT-A | 12 | EKPC_P1-2_BARR-SUMSH161_SRT-A |  | 3 | 0 | 0 | 0.04 | 542969 | STILWEL5 | 161 | 1.0122 | 0.09 | 340576 | WILSON | 24 | 1.0044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | EKPC_P1-2_GRE-SUMSH161_SRT-A | 13 | EKPC_P1-2_BULL-SUMSH161_SRT-A |  | 2 | 0 | 0 | 0.15 | 325118 | 1RHUDES INV | 34.5 | 1.0787 | 0.31 | 325117 | 1RHUDES COL | 34.5 | 1.073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | EKPC_P1-2_GRE-SUMSH161_SRT-A | 14 | EKPC_P1-2_SSHAD 161 TIE_SRT-A |  | 1 | 0 | 0 | 0.1 | 542969 | STILWEL5 | 161 | 1.0122 | 0.7 | 361788 | 5SUM SHAD TP | 161 | 1.0293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | EKPC_P1-2_GRE-SUMSH161_SRT-A | 15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.25 | 324002 | 1BROWN 3 | 24 | 1.0523 | 0 | 0 | 91.1 | 0 | 0 | 0 | 0 | 0
11 | EKPC_P1-2_GRE-SUMSH161_SRT-A | 16 | EKPC_P1-3_MAR 161/138_SRT-A | Ovl | 3 | 0 | 0 | 0.04 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 324002 | 1BROWN 3 | 24 | 1.053 | 10048.5 | 1 | 100.2 | 0 | 0 | 0 | 0 | 0
11 | EKPC_P1-2_GRE-SUMSH161_SRT-A | 17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A |  | 2 | 0 | 0 | 0.13 | 325118 | 1RHUDES INV | 34.5 | 1.0783 | 0.49 | 340576 | WILSON | 24 | 1.0043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | EKPC_P1-2_GRE-SUMSH161_SRT-A | 18 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A |  | 3 | 0 | 0 | 0.04 | 542969 | STILWEL5 | 161 | 1.0122 | 0.17 | 340576 | WILSON | 24 | 1.0013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | EKPC_P1-2_GRE-SUMSH161_SRT-A | 19 | EXT_324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1 _SRT-A |  | 1 | 0 | 0 | 0.29 | 342577 | 4FAWKES EK | 138 | 1.0036 | 0.44 | 342577 | 4FAWKES EK | 138 | 1.0036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | EKPC_P1-2_GRE-SUMSH161_SRT-A | 20 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A |  | 3 | 0 | 0 | 0.42 | 325118 | 1RHUDES INV | 34.5 | 1.0744 | 0.89 | 325117 | 1RHUDES COL | 34.5 | 1.069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | EKPC_P1-2_GRE-SUMSH161_SRT-A | 21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A |  | 2 | 0 | 0 | 0.14 | 325118 | 1RHUDES INV | 34.5 | 1.0787 | 0.66 | 340576 | WILSON | 24 | 1.0044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | EKPC_P1-2_GRE-SUMSH161_SRT-A | 22 | EXT_324217 4BROWN PLANT 138 324219 4BROWN T1 138 1 _SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | EKPC_P1-2_GRE-SUMSH161_SRT-A | 23 | EXT_324217 4BROWN PLANT 138 324220 4BROWN T2 138 1 _SRT-A |  | 1 | 0 | 0 | 0.1 | 542969 | STILWEL5 | 161 | 1.0122 | 0.27 | 324015 | 1DIX DAM 2 | 13.2 | 1.0108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | EKPC_P1-2_GRE-SUMSH161_SRT-A | 24 | EXT_324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1 _SRT-A |  | 3 | 0 | 0 | 0.36 | 325118 | 1RHUDES INV | 34.5 | 1.075 | 0.76 | 325117 | 1RHUDES COL | 34.5 | 1.0696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | EKPC_P1-2_GRE-SUMSH161_SRT-A | 25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A |  | 4 | 0 | 0 | 0.08 | 340576 | WILSON | 24 | 1.0032 | 0.84 | 340576 | WILSON | 24 | 1.0032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | EKPC_P1-2_GRE-SUMSH161_SRT-A | 26 | EXT_B-138-111_SRT-A |  | 3 | 0 | 0 | 0.42 | 325118 | 1RHUDES INV | 34.5 | 1.0744 | 0.89 | 325117 | 1RHUDES COL | 34.5 | 1.0689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | EKPC_P1-2_GRE-SUMSH161_SRT-A | 27 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A_Dup1 |  | 3 | 0 | 0 | 0.42 | 325118 | 1RHUDES INV | 34.5 | 1.0744 | 0.89 | 325117 | 1RHUDES COL | 34.5 | 1.069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | EKPC_P1-2_GRE-SUMSH161_SRT-A | 28 | EXT_BB-1133_SRT-A |  | 2 | 0 | 0 | 0.14 | 325118 | 1RHUDES INV | 34.5 | 1.0787 | 0.69 | 340576 | WILSON | 24 | 1.0043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | EKPC_P1-2_GRE-SUMSH161_SRT-A | 29 | EXT_MERE SWS_SRT-A |  | 2 | 0 | 0 | 0.11 | 325118 | 1RHUDES INV | 34.5 | 1.0777 | 0.48 | 324002 | 1BROWN 3 | 24 | 1.0525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | EKPC_P1-2_GRE-SUMSH161_SRT-A | 30 | EXT_B-138-115_SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.23 | 324002 | 1BROWN 3 | 24 | 1.0524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | EKPC_P1-2_GRE-SUMSH161_SRT-A | 31 | EXT_B-138-120_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | EKPC_P1-2_GRE-SUMSH161_SRT-A | 32 | EXT_B-138-121_SRT-A |  | 3 | 0 | 0 | 0.04 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | EKPC_P1-2_GRE-SUMSH161_SRT-A | 33 | EXT_324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1 _SRT-A |  | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.2 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | EKPC_P1-2_GRE-SUMSH161_SRT-A | 34 | EXT_326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1 _SRT-A |  | 2 | 0 | 0 | 0.15 | 325118 | 1RHUDES INV | 34.5 | 1.0787 | 0.31 | 325117 | 1RHUDES COL | 34.5 | 1.073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | EKPC_P1-2_GRE-SUMSH161_SRT-A | 35 | EXT_B-69-18_SRT-A |  | 5 | 0 | 0 | 0.07 | 342000 | 5GAS | 161 | 1 | 0.19 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0062 | 0 | 0 | 91.4 | 0 | 0 | 0 | 0 | 0
11 | EKPC_P1-2_GRE-SUMSH161_SRT-A | 36 | EXT_B-69-19_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.13 | 324002 | 1BROWN 3 | 24 | 1.0522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | EKPC_P1-2_GRE-SUMSH161_SRT-A | 37 | EXT_BB-1066_SRT-A |  | 2 | 0 | 0 | 0.09 | 542969 | STILWEL5 | 161 | 1.0122 | 0.21 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | EKPC_P1-2_BARR-SUMSH161_SRT-A | 1 | EKPC_P1-2_MAR-KU LEB138 |  | 3 | 0 | 0 | 0.04 | 542969 | STILWEL5 | 161 | 1.0122 | 0.07 | 325130 | 1RHUDES GEN | 0.6 | 1.1067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | EKPC_P1-2_BARR-SUMSH161_SRT-A | 2 | EKPC_P1-2_COOP-ELIHU161_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | EKPC_P1-2_BARR-SUMSH161_SRT-A | 3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A |  | 4 | 0 | 0 | 0.11 | 325118 | 1RHUDES INV | 34.5 | 1.0768 | 0.43 | 324002 | 1BROWN 3 | 24 | 1.0526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | EKPC_P1-2_BARR-SUMSH161_SRT-A | 4 | EKPC_P1-2_COOP-LAUREL161_SRT-A |  | 3 | 0 | 0 | 0.15 | 324446 | 2BOND | 69 | 1.0164 | 0.56 | 324002 | 1BROWN 3 | 24 | 1.0516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | EKPC_P1-2_BARR-SUMSH161_SRT-A | 5 | EKPC_P1-2_COOP-DEN161_SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | EKPC_P1-2_BARR-SUMSH161_SRT-A | 6 | EKPC_P1-2_COOP 161 TIE_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.19 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0082 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | EKPC_P1-2_BARR-SUMSH161_SRT-A | 7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.15 | 324002 | 1BROWN 3 | 24 | 1.052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | EKPC_P1-2_BARR-SUMSH161_SRT-A | 8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.27 | 340576 | WILSON | 24 | 1.0043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | EKPC_P1-2_BARR-SUMSH161_SRT-A | 9 | EKPC_P1-2_LIBJ-GAS161_SRT-A |  | 3 | 0 | 0 | 0.09 | 325118 | 1RHUDES INV | 34.5 | 1.0755 | 0.18 | 325117 | 1RHUDES COL | 34.5 | 1.0699 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | EKPC_P1-2_BARR-SUMSH161_SRT-A | 10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A |  | 2 | 0 | 0 | 0.1 | 542969 | STILWEL5 | 161 | 1.0122 | 0.33 | 364622 | 1WOLFCR H5-6 | 13.8 | 1.008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | EKPC_P1-2_BARR-SUMSH161_SRT-A | 11 | EKPC_P1-2_GRE-SUMSH161_SRT-A |  | 3 | 0 | 0 | 0.09 | 325118 | 1RHUDES INV | 34.5 | 1.0783 | 0.19 | 325117 | 1RHUDES COL | 34.5 | 1.0726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | EKPC_P1-2_BARR-SUMSH161_SRT-A | 13 | EKPC_P1-2_BULL-SUMSH161_SRT-A |  | 2 | 0 | 0 | 0.19 | 325118 | 1RHUDES INV | 34.5 | 1.0775 | 0.41 | 325117 | 1RHUDES COL | 34.5 | 1.0718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | EKPC_P1-2_BARR-SUMSH161_SRT-A | 14 | EKPC_P1-2_SSHAD 161 TIE_SRT-A |  | 1 | 0 | 0 | 0.11 | 542969 | STILWEL5 | 161 | 1.0122 | 0.7 | 361788 | 5SUM SHAD TP | 161 | 1.0277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | EKPC_P1-2_BARR-SUMSH161_SRT-A | 15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.18 | 324002 | 1BROWN 3 | 24 | 1.0519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | EKPC_P1-2_BARR-SUMSH161_SRT-A | 16 | EKPC_P1-3_MAR 161/138_SRT-A |  | 3 | 0 | 0 | 0.04 | 542969 | STILWEL5 | 161 | 1.0122 | 0.07 | 325130 | 1RHUDES GEN | 0.6 | 1.1067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | EKPC_P1-2_BARR-SUMSH161_SRT-A | 17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A |  | 2 | 0 | 0 | 0.32 | 325118 | 1RHUDES INV | 34.5 | 1.0788 | 0.69 | 325117 | 1RHUDES COL | 34.5 | 1.0731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | EKPC_P1-2_BARR-SUMSH161_SRT-A | 18 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.17 | 340576 | WILSON | 24 | 1.0012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | EKPC_P1-2_BARR-SUMSH161_SRT-A | 19 | EXT_324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1 _SRT-A |  | 1 | 0 | 0 | 0.29 | 342577 | 4FAWKES EK | 138 | 1.0037 | 0.46 | 342577 | 4FAWKES EK | 138 | 1.0037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | EKPC_P1-2_BARR-SUMSH161_SRT-A | 20 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.17 | 340576 | WILSON | 24 | 1.0041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | EKPC_P1-2_BARR-SUMSH161_SRT-A | 21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A |  | 2 | 0 | 0 | 0.32 | 325118 | 1RHUDES INV | 34.5 | 1.0788 | 0.68 | 325117 | 1RHUDES COL | 34.5 | 1.0731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | EKPC_P1-2_BARR-SUMSH161_SRT-A | 22 | EXT_324217 4BROWN PLANT 138 324219 4BROWN T1 138 1 _SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | EKPC_P1-2_BARR-SUMSH161_SRT-A | 23 | EXT_324217 4BROWN PLANT 138 324220 4BROWN T2 138 1 _SRT-A |  | 1 | 0 | 0 | 0.11 | 542969 | STILWEL5 | 161 | 1.0122 | 0.24 | 324015 | 1DIX DAM 2 | 13.2 | 1.0086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | EKPC_P1-2_BARR-SUMSH161_SRT-A | 24 | EXT_324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1 _SRT-A |  | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.56 | 340576 | WILSON | 24 | 1.0043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | EKPC_P1-2_BARR-SUMSH161_SRT-A | 25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A |  | 4 | 0 | 0 | 0.09 | 340576 | WILSON | 24 | 1.0033 | 0.65 | 340576 | WILSON | 24 | 1.0033 | 0 | 0 | 94.3 | 0 | 0 | 0 | 0 | 0
12 | EKPC_P1-2_BARR-SUMSH161_SRT-A | 26 | EXT_B-138-111_SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 91.1 | 0 | 0 | 0 | 0 | 0
12 | EKPC_P1-2_BARR-SUMSH161_SRT-A | 27 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A_Dup1 |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.17 | 340576 | WILSON | 24 | 1.0041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | EKPC_P1-2_BARR-SUMSH161_SRT-A | 28 | EXT_BB-1133_SRT-A |  | 2 | 0 | 0 | 0.32 | 325118 | 1RHUDES INV | 34.5 | 1.0788 | 0.69 | 325117 | 1RHUDES COL | 34.5 | 1.0731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | EKPC_P1-2_BARR-SUMSH161_SRT-A | 29 | EXT_MERE SWS_SRT-A |  | 3 | 0 | 0 | 0.04 | 542969 | STILWEL5 | 161 | 1.0122 | 0.16 | 324002 | 1BROWN 3 | 24 | 1.0521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | EKPC_P1-2_BARR-SUMSH161_SRT-A | 30 | EXT_B-138-115_SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.06 | 324002 | 1BROWN 3 | 24 | 1.0525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | EKPC_P1-2_BARR-SUMSH161_SRT-A | 31 | EXT_B-138-120_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | EKPC_P1-2_BARR-SUMSH161_SRT-A | 32 | EXT_B-138-121_SRT-A |  | 3 | 0 | 0 | 0.04 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | EKPC_P1-2_BARR-SUMSH161_SRT-A | 33 | EXT_324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1 _SRT-A |  | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.17 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | EKPC_P1-2_BARR-SUMSH161_SRT-A | 34 | EXT_326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1 _SRT-A |  | 2 | 0 | 0 | 0.18 | 325118 | 1RHUDES INV | 34.5 | 1.0774 | 0.39 | 325117 | 1RHUDES COL | 34.5 | 1.0717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | EKPC_P1-2_BARR-SUMSH161_SRT-A | 35 | EXT_B-69-18_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.26 | 324002 | 1BROWN 3 | 24 | 1.0522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | EKPC_P1-2_BARR-SUMSH161_SRT-A | 36 | EXT_B-69-19_SRT-A |  | 5 | 0 | 0 | 0.02 | 342403 | 2UPTON T | 69 | 0.9652 | 0.81 | 325130 | 1RHUDES GEN | 0.6 | 1.1068 | 0 | 0 | 90.1 | 0 | 0 | 0 | 0 | 0
12 | EKPC_P1-2_BARR-SUMSH161_SRT-A | 37 | EXT_BB-1066_SRT-A |  | 2 | 0 | 0 | 0.1 | 542969 | STILWEL5 | 161 | 1.0122 | 0.18 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | EKPC_P1-2_BULL-SUMSH161_SRT-A | 1 | EKPC_P1-2_MAR-KU LEB138 |  | 2 | 0 | 0 | 0.2 | 325118 | 1RHUDES INV | 34.5 | 1.0788 | 0.57 | 324002 | 1BROWN 3 | 24 | 1.0529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | EKPC_P1-2_BULL-SUMSH161_SRT-A | 2 | EKPC_P1-2_COOP-ELIHU161_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | EKPC_P1-2_BULL-SUMSH161_SRT-A | 3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A |  | 4 | 0 | 0 | 0.06 | 325118 | 1RHUDES INV | 34.5 | 1.0779 | 0.42 | 324002 | 1BROWN 3 | 24 | 1.0528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | EKPC_P1-2_BULL-SUMSH161_SRT-A | 4 | EKPC_P1-2_COOP-LAUREL161_SRT-A |  | 3 | 0 | 0 | 0.15 | 324446 | 2BOND | 69 | 1.0164 | 0.56 | 324002 | 1BROWN 3 | 24 | 1.0517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | EKPC_P1-2_BULL-SUMSH161_SRT-A | 5 | EKPC_P1-2_COOP-DEN161_SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | EKPC_P1-2_BULL-SUMSH161_SRT-A | 6 | EKPC_P1-2_COOP 161 TIE_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.19 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | EKPC_P1-2_BULL-SUMSH161_SRT-A | 7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.15 | 324002 | 1BROWN 3 | 24 | 1.0522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | EKPC_P1-2_BULL-SUMSH161_SRT-A | 8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A |  | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.27 | 340576 | WILSON | 24 | 1.0039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | EKPC_P1-2_BULL-SUMSH161_SRT-A | 9 | EKPC_P1-2_LIBJ-GAS161_SRT-A |  | 3 | 0 | 0 | 0.08 | 325118 | 1RHUDES INV | 34.5 | 1.0766 | 0.17 | 325117 | 1RHUDES COL | 34.5 | 1.071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | EKPC_P1-2_BULL-SUMSH161_SRT-A | 10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A |  | 3 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.06 | 325117 | 1RHUDES COL | 34.5 | 1.0705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | EKPC_P1-2_BULL-SUMSH161_SRT-A | 11 | EKPC_P1-2_GRE-SUMSH161_SRT-A |  | 3 | 0 | 0 | 0.04 | 542969 | STILWEL5 | 161 | 1.0122 | 0.08 | 324002 | 1BROWN 3 | 24 | 1.0525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | EKPC_P1-2_BULL-SUMSH161_SRT-A | 12 | EKPC_P1-2_BARR-SUMSH161_SRT-A |  | 3 | 0 | 0 | 0.06 | 325118 | 1RHUDES INV | 34.5 | 1.0779 | 0.12 | 325117 | 1RHUDES COL | 34.5 | 1.0722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | EKPC_P1-2_BULL-SUMSH161_SRT-A | 14 | EKPC_P1-2_SSHAD 161 TIE_SRT-A |  | 4 | 0 | 0 | 0.19 | 325118 | 1RHUDES INV | 34.5 | 1.0765 | 0.4 | 325117 | 1RHUDES COL | 34.5 | 1.071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | EKPC_P1-2_BULL-SUMSH161_SRT-A | 15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A |  | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.19 | 324002 | 1BROWN 3 | 24 | 1.0521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | EKPC_P1-2_BULL-SUMSH161_SRT-A | 16 | EKPC_P1-3_MAR 161/138_SRT-A |  | 2 | 0 | 0 | 0.2 | 325118 | 1RHUDES INV | 34.5 | 1.0788 | 0.57 | 324002 | 1BROWN 3 | 24 | 1.0529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | EKPC_P1-2_BULL-SUMSH161_SRT-A | 17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A |  | 2 | 0 | 0 | 0.19 | 325118 | 1RHUDES INV | 34.5 | 1.0784 | 0.42 | 325117 | 1RHUDES COL | 34.5 | 1.0726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | EKPC_P1-2_BULL-SUMSH161_SRT-A | 18 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.17 | 340576 | WILSON | 24 | 1.0011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | EKPC_P1-2_BULL-SUMSH161_SRT-A | 19 | EXT_324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1 _SRT-A |  | 1 | 0 | 0 | 0.3 | 342577 | 4FAWKES EK | 138 | 1.0036 | 0.46 | 342577 | 4FAWKES EK | 138 | 1.0036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | EKPC_P1-2_BULL-SUMSH161_SRT-A | 20 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.08 | 340576 | WILSON | 24 | 1.0038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | EKPC_P1-2_BULL-SUMSH161_SRT-A | 21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A |  | 2 | 0 | 0 | 0.2 | 325118 | 1RHUDES INV | 34.5 | 1.0788 | 0.57 | 340576 | WILSON | 24 | 1.0044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | EKPC_P1-2_BULL-SUMSH161_SRT-A | 22 | EXT_324217 4BROWN PLANT 138 324219 4BROWN T1 138 1 _SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | EKPC_P1-2_BULL-SUMSH161_SRT-A | 23 | EXT_324217 4BROWN PLANT 138 324220 4BROWN T2 138 1 _SRT-A |  | 1 | 0 | 0 | 0.11 | 542969 | STILWEL5 | 161 | 1.0122 | 0.24 | 324015 | 1DIX DAM 2 | 13.2 | 1.0086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | EKPC_P1-2_BULL-SUMSH161_SRT-A | 24 | EXT_324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1 _SRT-A |  | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.53 | 340576 | WILSON | 24 | 1.004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | EKPC_P1-2_BULL-SUMSH161_SRT-A | 25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.07 | 324002 | 1BROWN 3 | 24 | 1.0527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | EKPC_P1-2_BULL-SUMSH161_SRT-A | 26 | EXT_B-138-111_SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.06 | 340576 | WILSON | 24 | 1.0038 | 0 | 0 | 90.6 | 0 | 0 | 0 | 0 | 0
13 | EKPC_P1-2_BULL-SUMSH161_SRT-A | 27 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A_Dup1 |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.08 | 340576 | WILSON | 24 | 1.0038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | EKPC_P1-2_BULL-SUMSH161_SRT-A | 28 | EXT_BB-1133_SRT-A |  | 2 | 0 | 0 | 0.21 | 325118 | 1RHUDES INV | 34.5 | 1.0788 | 0.96 | 325055 | 4RHUDES TP | 138 | 1.0145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | EKPC_P1-2_BULL-SUMSH161_SRT-A | 29 | EXT_MERE SWS_SRT-A |  | 2 | 0 | 0 | 0.18 | 325118 | 1RHUDES INV | 34.5 | 1.078 | 0.4 | 325117 | 1RHUDES COL | 34.5 | 1.0722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | EKPC_P1-2_BULL-SUMSH161_SRT-A | 30 | EXT_B-138-115_SRT-A |  | 3 | 0 | 0 | 0.06 | 542969 | STILWEL5 | 161 | 1.0122 | 0.36 | 324002 | 1BROWN 3 | 24 | 1.0525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | EKPC_P1-2_BULL-SUMSH161_SRT-A | 31 | EXT_B-138-120_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | EKPC_P1-2_BULL-SUMSH161_SRT-A | 32 | EXT_B-138-121_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | EKPC_P1-2_BULL-SUMSH161_SRT-A | 33 | EXT_324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1 _SRT-A |  | 2 | 0 | 0 | 0.09 | 542969 | STILWEL5 | 161 | 1.0122 | 0.21 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | EKPC_P1-2_BULL-SUMSH161_SRT-A | 35 | EXT_B-69-18_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.26 | 324002 | 1BROWN 3 | 24 | 1.0524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | EKPC_P1-2_BULL-SUMSH161_SRT-A | 36 | EXT_B-69-19_SRT-A |  | 5 | 0 | 0 | 0.22 | 325118 | 1RHUDES INV | 34.5 | 1.0763 | 0.46 | 325117 | 1RHUDES COL | 34.5 | 1.0707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | EKPC_P1-2_BULL-SUMSH161_SRT-A | 37 | EXT_BB-1066_SRT-A |  | 2 | 0 | 0 | 0.1 | 542969 | STILWEL5 | 161 | 1.0122 | 0.22 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | EKPC_P1-2_SSHAD 161 TIE_SRT-A | 1 | EKPC_P1-2_MAR-KU LEB138 |  | 2 | 0 | 0 | 0.23 | 325118 | 1RHUDES INV | 34.5 | 1.077 | 0.59 | 324002 | 1BROWN 3 | 24 | 1.0527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | EKPC_P1-2_SSHAD 161 TIE_SRT-A | 2 | EKPC_P1-2_COOP-ELIHU161_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | EKPC_P1-2_SSHAD 161 TIE_SRT-A | 3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A |  | 4 | 0 | 0 | 0.11 | 325118 | 1RHUDES INV | 34.5 | 1.0758 | 0.42 | 324002 | 1BROWN 3 | 24 | 1.0526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | EKPC_P1-2_SSHAD 161 TIE_SRT-A | 4 | EKPC_P1-2_COOP-LAUREL161_SRT-A |  | 3 | 0 | 0 | 0.15 | 324446 | 2BOND | 69 | 1.0164 | 0.56 | 324002 | 1BROWN 3 | 24 | 1.0515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | EKPC_P1-2_SSHAD 161 TIE_SRT-A | 5 | EKPC_P1-2_COOP-DEN161_SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | EKPC_P1-2_SSHAD 161 TIE_SRT-A | 6 | EKPC_P1-2_COOP 161 TIE_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.19 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | EKPC_P1-2_SSHAD 161 TIE_SRT-A | 7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.15 | 324002 | 1BROWN 3 | 24 | 1.052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | EKPC_P1-2_SSHAD 161 TIE_SRT-A | 8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.26 | 340576 | WILSON | 24 | 1.0039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | EKPC_P1-2_SSHAD 161 TIE_SRT-A | 9 | EKPC_P1-2_LIBJ-GAS161_SRT-A |  | 3 | 0 | 0 | 0.09 | 325118 | 1RHUDES INV | 34.5 | 1.0746 | 0.18 | 325117 | 1RHUDES COL | 34.5 | 1.0691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | EKPC_P1-2_SSHAD 161 TIE_SRT-A | 10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A |  | 2 | 0 | 0 | 0.1 | 542969 | STILWEL5 | 161 | 1.0122 | 0.32 | 364622 | 1WOLFCR H5-6 | 13.8 | 1.0096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | EKPC_P1-2_SSHAD 161 TIE_SRT-A | 11 | EKPC_P1-2_GRE-SUMSH161_SRT-A |  | 3 | 0 | 0 | 0.08 | 325118 | 1RHUDES INV | 34.5 | 1.0771 | 0.17 | 325117 | 1RHUDES COL | 34.5 | 1.0715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | EKPC_P1-2_SSHAD 161 TIE_SRT-A | 12 | EKPC_P1-2_BARR-SUMSH161_SRT-A |  | 3 | 0 | 0 | 0.06 | 325118 | 1RHUDES INV | 34.5 | 1.0757 | 0.13 | 325117 | 1RHUDES COL | 34.5 | 1.0701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | EKPC_P1-2_SSHAD 161 TIE_SRT-A | 13 | EKPC_P1-2_BULL-SUMSH161_SRT-A |  | 4 | 0 | 0 | 0.19 | 325118 | 1RHUDES INV | 34.5 | 1.0765 | 0.4 | 325117 | 1RHUDES COL | 34.5 | 1.071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | EKPC_P1-2_SSHAD 161 TIE_SRT-A | 15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.18 | 324002 | 1BROWN 3 | 24 | 1.0519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | EKPC_P1-2_SSHAD 161 TIE_SRT-A | 16 | EKPC_P1-3_MAR 161/138_SRT-A |  | 2 | 0 | 0 | 0.23 | 325118 | 1RHUDES INV | 34.5 | 1.077 | 0.59 | 324002 | 1BROWN 3 | 24 | 1.0527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | EKPC_P1-2_SSHAD 161 TIE_SRT-A | 17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A |  | 2 | 0 | 0 | 0.34 | 325118 | 1RHUDES INV | 34.5 | 1.0781 | 0.72 | 325117 | 1RHUDES COL | 34.5 | 1.0723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | EKPC_P1-2_SSHAD 161 TIE_SRT-A | 18 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.17 | 340576 | WILSON | 24 | 1.0011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | EKPC_P1-2_SSHAD 161 TIE_SRT-A | 19 | EXT_324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1 _SRT-A |  | 1 | 0 | 0 | 0.3 | 342577 | 4FAWKES EK | 138 | 1.0037 | 0.46 | 342577 | 4FAWKES EK | 138 | 1.0037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | EKPC_P1-2_SSHAD 161 TIE_SRT-A | 20 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.15 | 324002 | 1BROWN 3 | 24 | 1.0514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | EKPC_P1-2_SSHAD 161 TIE_SRT-A | 21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A |  | 2 | 0 | 0 | 0.31 | 325118 | 1RHUDES INV | 34.5 | 1.0777 | 0.65 | 325117 | 1RHUDES COL | 34.5 | 1.072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | EKPC_P1-2_SSHAD 161 TIE_SRT-A | 22 | EXT_324217 4BROWN PLANT 138 324219 4BROWN T1 138 1 _SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | EKPC_P1-2_SSHAD 161 TIE_SRT-A | 23 | EXT_324217 4BROWN PLANT 138 324220 4BROWN T2 138 1 _SRT-A |  | 1 | 0 | 0 | 0.11 | 542969 | STILWEL5 | 161 | 1.0122 | 0.24 | 324015 | 1DIX DAM 2 | 13.2 | 1.0085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | EKPC_P1-2_SSHAD 161 TIE_SRT-A | 24 | EXT_324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1 _SRT-A |  | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.53 | 340576 | WILSON | 24 | 1.0039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | EKPC_P1-2_SSHAD 161 TIE_SRT-A | 25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.12 | 324002 | 1BROWN 3 | 24 | 1.0524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | EKPC_P1-2_SSHAD 161 TIE_SRT-A | 26 | EXT_B-138-111_SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | EKPC_P1-2_SSHAD 161 TIE_SRT-A | 27 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A_Dup1 |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.15 | 324002 | 1BROWN 3 | 24 | 1.0514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | EKPC_P1-2_SSHAD 161 TIE_SRT-A | 28 | EXT_BB-1133_SRT-A |  | 2 | 0 | 0 | 0.32 | 325118 | 1RHUDES INV | 34.5 | 1.0779 | 0.68 | 325117 | 1RHUDES COL | 34.5 | 1.0722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | EKPC_P1-2_SSHAD 161 TIE_SRT-A | 29 | EXT_MERE SWS_SRT-A |  | 2 | 0 | 0 | 0.42 | 325118 | 1RHUDES INV | 34.5 | 1.0789 | 0.89 | 325117 | 1RHUDES COL | 34.5 | 1.0732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | EKPC_P1-2_SSHAD 161 TIE_SRT-A | 30 | EXT_B-138-115_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.37 | 324002 | 1BROWN 3 | 24 | 1.0523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | EKPC_P1-2_SSHAD 161 TIE_SRT-A | 31 | EXT_B-138-120_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | EKPC_P1-2_SSHAD 161 TIE_SRT-A | 32 | EXT_B-138-121_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | EKPC_P1-2_SSHAD 161 TIE_SRT-A | 33 | EXT_324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1 _SRT-A |  | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.17 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | EKPC_P1-2_SSHAD 161 TIE_SRT-A | 34 | EXT_326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1 _SRT-A |  | 2 | 0 | 0 | 0.17 | 325118 | 1RHUDES INV | 34.5 | 1.0763 | 0.36 | 325117 | 1RHUDES COL | 34.5 | 1.0707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | EKPC_P1-2_SSHAD 161 TIE_SRT-A | 35 | EXT_B-69-18_SRT-A |  | 3 | 0 | 0 | 0.05 | 325118 | 1RHUDES INV | 34.5 | 1.0774 | 0.25 | 324002 | 1BROWN 3 | 24 | 1.0522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | EKPC_P1-2_SSHAD 161 TIE_SRT-A | 36 | EXT_B-69-19_SRT-A |  | 4 | 0 | 0 | 0.33 | 325118 | 1RHUDES INV | 34.5 | 1.0749 | 0.7 | 325117 | 1RHUDES COL | 34.5 | 1.0694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | EKPC_P1-2_SSHAD 161 TIE_SRT-A | 37 | EXT_BB-1066_SRT-A |  | 2 | 0 | 0 | 0.1 | 542969 | STILWEL5 | 161 | 1.0122 | 0.17 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 1 | EKPC_P1-2_MAR-KU LEB138 | Ovl | 3 | 0 | 0 | 0.04 | 542969 | STILWEL5 | 161 | 1.0122 | 0.08 | 324002 | 1BROWN 3 | 24 | 1.0534 | 12939.5 | 1 | 113.8 | 0 | 0 | 0 | 0 | 0
15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 2 | EKPC_P1-2_COOP-ELIHU161_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 97.6 | 0 | 0 | 0 | 0 | 0
15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | Ovl | 4 | 0 | 0 | 0.13 | 325118 | 1RHUDES INV | 34.5 | 1.0769 | 0.47 | 324002 | 1BROWN 3 | 24 | 1.0528 | 10517.3 | 1 | 102.6 | 0 | 0 | 0 | 0 | 0
15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 4 | EKPC_P1-2_COOP-LAUREL161_SRT-A |  | 3 | 0 | 0 | 0.15 | 324446 | 2BOND | 69 | 1.0163 | 0.56 | 324002 | 1BROWN 3 | 24 | 1.0517 | 0 | 0 | 91.8 | 0 | 0 | 0 | 0 | 0
15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 5 | EKPC_P1-2_COOP-DEN161_SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 6 | EKPC_P1-2_COOP 161 TIE_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.19 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.14 | 324002 | 1BROWN 3 | 24 | 1.0521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.24 | 340576 | WILSON | 24 | 1.0039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 9 | EKPC_P1-2_LIBJ-GAS161_SRT-A |  | 3 | 0 | 0 | 0.09 | 325118 | 1RHUDES INV | 34.5 | 1.0756 | 0.2 | 325117 | 1RHUDES COL | 34.5 | 1.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A |  | 2 | 0 | 0 | 0.12 | 325118 | 1RHUDES INV | 34.5 | 1.0741 | 0.28 | 340576 | WILSON | 24 | 1.0032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 11 | EKPC_P1-2_GRE-SUMSH161_SRT-A |  | 5 | 0 | 0 | 0.02 | 325118 | 1RHUDES INV | 34.5 | 1.074 | 0.08 | 324002 | 1BROWN 3 | 24 | 1.0519 | 0 | 0 | 90.6 | 0 | 0 | 0 | 0 | 0
15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 12 | EKPC_P1-2_BARR-SUMSH161_SRT-A |  | 3 | 0 | 0 | 0.06 | 325118 | 1RHUDES INV | 34.5 | 1.0766 | 0.13 | 325117 | 1RHUDES COL | 34.5 | 1.0711 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 13 | EKPC_P1-2_BULL-SUMSH161_SRT-A |  | 2 | 0 | 0 | 0.18 | 325118 | 1RHUDES INV | 34.5 | 1.0774 | 0.38 | 325117 | 1RHUDES COL | 34.5 | 1.0717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 14 | EKPC_P1-2_SSHAD 161 TIE_SRT-A |  | 1 | 0 | 0 | 0.11 | 542969 | STILWEL5 | 161 | 1.0122 | 0.86 | 360334 | 5SUMMER SHAD | 161 | 1.0257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 16 | EKPC_P1-3_MAR 161/138_SRT-A | Ovl | 3 | 0 | 0 | 0.04 | 542969 | STILWEL5 | 161 | 1.0122 | 0.08 | 324002 | 1BROWN 3 | 24 | 1.0534 | 12940.7 | 1 | 113.8 | 0 | 0 | 0 | 0 | 0
15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A |  | 2 | 0 | 0 | 0.32 | 325118 | 1RHUDES INV | 34.5 | 1.0788 | 0.69 | 325117 | 1RHUDES COL | 34.5 | 1.0731 | 0 | 0 | 93 | 0 | 0 | 0 | 0 | 0
15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 18 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.17 | 340576 | WILSON | 24 | 1.0012 | 0 | 0 | 92.8 | 0 | 0 | 0 | 0 | 0
15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 19 | EXT_324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1 _SRT-A |  | 1 | 0 | 0 | 0.29 | 342577 | 4FAWKES EK | 138 | 1.0036 | 0.46 | 342577 | 4FAWKES EK | 138 | 1.0036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 20 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.18 | 340576 | WILSON | 24 | 1.0038 | 0 | 0 | 93.4 | 0 | 0 | 0 | 0 | 0
15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A |  | 2 | 0 | 0 | 0.3 | 325118 | 1RHUDES INV | 34.5 | 1.0786 | 0.63 | 325117 | 1RHUDES COL | 34.5 | 1.0729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 22 | EXT_324217 4BROWN PLANT 138 324219 4BROWN T1 138 1 _SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 23 | EXT_324217 4BROWN PLANT 138 324220 4BROWN T2 138 1 _SRT-A |  | 1 | 0 | 0 | 0.11 | 542969 | STILWEL5 | 161 | 1.0122 | 0.25 | 324015 | 1DIX DAM 2 | 13.2 | 1.0092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 24 | EXT_324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1 _SRT-A |  | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.55 | 340576 | WILSON | 24 | 1.004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A |  | 4 | 0 | 0 | 0.09 | 340576 | WILSON | 24 | 1.0033 | 0.66 | 340576 | WILSON | 24 | 1.0033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 26 | EXT_B-138-111_SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 27 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A_Dup1 |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.18 | 340576 | WILSON | 24 | 1.0038 | 0 | 0 | 93.4 | 0 | 0 | 0 | 0 | 0
15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 28 | EXT_BB-1133_SRT-A |  | 2 | 0 | 0 | 0.31 | 325118 | 1RHUDES INV | 34.5 | 1.0787 | 0.66 | 325117 | 1RHUDES COL | 34.5 | 1.073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 29 | EXT_MERE SWS_SRT-A |  | 3 | 0 | 0 | 0.04 | 542969 | STILWEL5 | 161 | 1.0122 | 0.15 | 324002 | 1BROWN 3 | 24 | 1.0522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 30 | EXT_B-138-115_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.41 | 324002 | 1BROWN 3 | 24 | 1.0524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 31 | EXT_B-138-120_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 32 | EXT_B-138-121_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 33 | EXT_324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1 _SRT-A |  | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.17 | 325117 | 1RHUDES COL | 34.5 | 1.0708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 34 | EXT_326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1 _SRT-A |  | 2 | 0 | 0 | 0.17 | 325118 | 1RHUDES INV | 34.5 | 1.0773 | 0.37 | 325117 | 1RHUDES COL | 34.5 | 1.0716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 35 | EXT_B-69-18_SRT-A | Ovl Vlt | 5 | 0 | 0 | 0.02 | 158981 | ARMOW_BUS2 | 34.5 | 1.025 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 76292 | 5 | 147.5 | 7.6 | 17 | 0 | 0 | 0
15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 36 | EXT_B-69-19_SRT-A |  | 4 | 0 | 0 | 0.28 | 325118 | 1RHUDES INV | 34.5 | 1.0757 | 0.59 | 325117 | 1RHUDES COL | 34.5 | 1.0702 | 0 | 0 | 92.7 | 0 | 0 | 0 | 0 | 0
15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | 37 | EXT_BB-1066_SRT-A |  | 2 | 0 | 0 | 0.1 | 542969 | STILWEL5 | 161 | 1.0122 | 0.17 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | EKPC_P1-3_MAR 161/138_SRT-A | 1 | EKPC_P1-2_MAR-KU LEB138 |  | 1 | 0 | 0 | 0.1 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | EKPC_P1-3_MAR 161/138_SRT-A | 2 | EKPC_P1-2_COOP-ELIHU161_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | EKPC_P1-3_MAR 161/138_SRT-A | 3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | Ovl | 4 | 0 | 0 | 0.05 | 324830 | 2CAMPBELV EK | 69 | 0.9925 | 0.51 | 324002 | 1BROWN 3 | 24 | 1.0536 | 12419.1 | 1 | 111.4 | 0 | 0 | 0 | 0 | 0
16 | EKPC_P1-3_MAR 161/138_SRT-A | 4 | EKPC_P1-2_COOP-LAUREL161_SRT-A | Ovl | 3 | 0 | 0 | 0.15 | 324446 | 2BOND | 69 | 1.0163 | 0.57 | 324002 | 1BROWN 3 | 24 | 1.0526 | 10665 | 1 | 103.3 | 0 | 0 | 0 | 0 | 0
16 | EKPC_P1-3_MAR 161/138_SRT-A | 5 | EKPC_P1-2_COOP-DEN161_SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | EKPC_P1-3_MAR 161/138_SRT-A | 6 | EKPC_P1-2_COOP 161 TIE_SRT-A | Ovl | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.2 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0099 | 10007.4 | 1 | 100 | 0 | 0 | 0 | 0 | 0
16 | EKPC_P1-3_MAR 161/138_SRT-A | 7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | Ovl | 3 | 0 | 0 | 0.05 | 341971 | 2NORWOOD | 69 | 0.9627 | 0.12 | 324002 | 1BROWN 3 | 24 | 1.0531 | 10534.4 | 1 | 102.6 | 0 | 0 | 0 | 0 | 0
16 | EKPC_P1-3_MAR 161/138_SRT-A | 8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.1 | 364001 | 1BR FERRY N1 | 22 | 1.0424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | EKPC_P1-3_MAR 161/138_SRT-A | 9 | EKPC_P1-2_LIBJ-GAS161_SRT-A | Ovl | 3 | 0 | 0 | 0.1 | 341563 | 2GREEN CO | 69 | 0.9998 | 0.34 | 342769 | 5MARION CO | 161 | 1.0064 | 11176.4 | 1 | 105.7 | 0 | 0 | 0 | 0 | 0
16 | EKPC_P1-3_MAR 161/138_SRT-A | 10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | Ovl | 4 | 0 | 0 | 0.04 | 542969 | STILWEL5 | 161 | 1.0122 | 0.18 | 340576 | WILSON | 24 | 1.0047 | 30211 | 1 | 173.8 | 0 | 0 | 0 | 0 | 0
16 | EKPC_P1-3_MAR 161/138_SRT-A | 11 | EKPC_P1-2_GRE-SUMSH161_SRT-A | Ovl | 2 | 0 | 0 | 0.12 | 325118 | 1RHUDES INV | 34.5 | 1.0787 | 0.25 | 325117 | 1RHUDES COL | 34.5 | 1.073 | 10048.6 | 1 | 100.2 | 0 | 0 | 0 | 0 | 0
16 | EKPC_P1-3_MAR 161/138_SRT-A | 12 | EKPC_P1-2_BARR-SUMSH161_SRT-A |  | 3 | 0 | 0 | 0.04 | 542969 | STILWEL5 | 161 | 1.0122 | 0.09 | 340576 | WILSON | 24 | 1.0048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | EKPC_P1-3_MAR 161/138_SRT-A | 13 | EKPC_P1-2_BULL-SUMSH161_SRT-A |  | 2 | 0 | 0 | 0.13 | 325118 | 1RHUDES INV | 34.5 | 1.0787 | 0.27 | 325117 | 1RHUDES COL | 34.5 | 1.073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | EKPC_P1-3_MAR 161/138_SRT-A | 14 | EKPC_P1-2_SSHAD 161 TIE_SRT-A |  | 1 | 0 | 0 | 0.1 | 542969 | STILWEL5 | 161 | 1.0122 | 0.86 | 360334 | 5SUMMER SHAD | 161 | 1.0259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | EKPC_P1-3_MAR 161/138_SRT-A | 15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | Ovl | 3 | 0 | 0 | 0.04 | 542969 | STILWEL5 | 161 | 1.0122 | 0.08 | 324002 | 1BROWN 3 | 24 | 1.0534 | 12940.7 | 1 | 113.8 | 0 | 0 | 0 | 0 | 0
16 | EKPC_P1-3_MAR 161/138_SRT-A | 17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A |  | 2 | 0 | 0 | 0.13 | 325118 | 1RHUDES INV | 34.5 | 1.0787 | 0.79 | 340576 | WILSON | 24 | 1.0044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | EKPC_P1-3_MAR 161/138_SRT-A | 18 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A |  | 3 | 0 | 0 | 0.04 | 542969 | STILWEL5 | 161 | 1.0122 | 0.17 | 340576 | WILSON | 24 | 1.0014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | EKPC_P1-3_MAR 161/138_SRT-A | 19 | EXT_324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1 _SRT-A |  | 1 | 0 | 0 | 0.27 | 342577 | 4FAWKES EK | 138 | 1.0036 | 0.47 | 340576 | WILSON | 24 | 1.0044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | EKPC_P1-3_MAR 161/138_SRT-A | 20 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.09 | 340576 | WILSON | 24 | 1.0059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | EKPC_P1-3_MAR 161/138_SRT-A | 21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A |  | 2 | 0 | 0 | 0.13 | 325118 | 1RHUDES INV | 34.5 | 1.0787 | 0.82 | 340576 | WILSON | 24 | 1.0044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | EKPC_P1-3_MAR 161/138_SRT-A | 22 | EXT_324217 4BROWN PLANT 138 324219 4BROWN T1 138 1 _SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | EKPC_P1-3_MAR 161/138_SRT-A | 23 | EXT_324217 4BROWN PLANT 138 324220 4BROWN T2 138 1 _SRT-A |  | 1 | 0 | 0 | 0.1 | 542969 | STILWEL5 | 161 | 1.0122 | 0.32 | 324016 | 1DIX DAM 3 | 13.2 | 1.016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | EKPC_P1-3_MAR 161/138_SRT-A | 24 | EXT_324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1 _SRT-A | Ovl | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.28 | 324002 | 1BROWN 3 | 24 | 1.0526 | 10757.9 | 1 | 103.7 | 0 | 0 | 0 | 0 | 0
16 | EKPC_P1-3_MAR 161/138_SRT-A | 25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A |  | 4 | 0 | 0 | 0.09 | 340576 | WILSON | 24 | 1.0036 | 0.66 | 340576 | WILSON | 24 | 1.0036 | 0 | 0 | 93.8 | 0 | 0 | 0 | 0 | 0
16 | EKPC_P1-3_MAR 161/138_SRT-A | 26 | EXT_B-138-111_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.21 | 324002 | 1BROWN 3 | 24 | 1.0525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | EKPC_P1-3_MAR 161/138_SRT-A | 27 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A_Dup1 |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.09 | 340576 | WILSON | 24 | 1.0059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | EKPC_P1-3_MAR 161/138_SRT-A | 28 | EXT_BB-1133_SRT-A |  | 2 | 0 | 0 | 0.13 | 325118 | 1RHUDES INV | 34.5 | 1.0787 | 0.81 | 340576 | WILSON | 24 | 1.0043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | EKPC_P1-3_MAR 161/138_SRT-A | 29 | EXT_MERE SWS_SRT-A |  | 3 | 0 | 0 | 0.04 | 542969 | STILWEL5 | 161 | 1.0122 | 0.06 | 324002 | 1BROWN 3 | 24 | 1.0534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | EKPC_P1-3_MAR 161/138_SRT-A | 30 | EXT_B-138-115_SRT-A | Ovl | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.4 | 324002 | 1BROWN 3 | 24 | 1.054 | 10755.5 | 1 | 103.7 | 0 | 0 | 0 | 0 | 0
16 | EKPC_P1-3_MAR 161/138_SRT-A | 31 | EXT_B-138-120_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | EKPC_P1-3_MAR 161/138_SRT-A | 32 | EXT_B-138-121_SRT-A |  | 3 | 0 | 0 | 0.04 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | EKPC_P1-3_MAR 161/138_SRT-A | 33 | EXT_324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1 _SRT-A |  | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.16 | 325117 | 1RHUDES COL | 34.5 | 1.0725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | EKPC_P1-3_MAR 161/138_SRT-A | 34 | EXT_326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1 _SRT-A |  | 2 | 0 | 0 | 0.13 | 325118 | 1RHUDES INV | 34.5 | 1.0787 | 0.27 | 325117 | 1RHUDES COL | 34.5 | 1.073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | EKPC_P1-3_MAR 161/138_SRT-A | 35 | EXT_B-69-18_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.19 | 324002 | 1BROWN 3 | 24 | 1.0522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | EKPC_P1-3_MAR 161/138_SRT-A | 36 | EXT_B-69-19_SRT-A |  | 3 | 0 | 0 | 0.27 | 325118 | 1RHUDES INV | 34.5 | 1.0759 | 0.57 | 325117 | 1RHUDES COL | 34.5 | 1.0704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | EKPC_P1-3_MAR 161/138_SRT-A | 37 | EXT_BB-1066_SRT-A |  | 2 | 0 | 0 | 0.09 | 542969 | STILWEL5 | 161 | 1.0122 | 0.16 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A | 1 | EKPC_P1-2_MAR-KU LEB138 |  | 3 | 0 | 0 | 0.04 | 542969 | STILWEL5 | 161 | 1.0122 | 0.07 | 324002 | 1BROWN 3 | 24 | 1.0527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A | 2 | EKPC_P1-2_COOP-ELIHU161_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 93.1 | 0 | 0 | 0 | 0 | 0
17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A | 3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A |  | 4 | 0 | 0 | 0.05 | 324830 | 2CAMPBELV EK | 69 | 0.993 | 0.45 | 324002 | 1BROWN 3 | 24 | 1.0525 | 0 | 0 | 97.3 | 0 | 0 | 0 | 0 | 0
17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A | 4 | EKPC_P1-2_COOP-LAUREL161_SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.08 | 324002 | 1BROWN 3 | 24 | 1.0514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A | 5 | EKPC_P1-2_COOP-DEN161_SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A | 6 | EKPC_P1-2_COOP 161 TIE_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.18 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A | 7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.17 | 324002 | 1BROWN 3 | 24 | 1.0518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A | 8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A | 9 | EKPC_P1-2_LIBJ-GAS161_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.09 | 325117 | 1RHUDES COL | 34.5 | 1.0724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A | 10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A |  | 2 | 0 | 0 | 0.1 | 542969 | STILWEL5 | 161 | 1.0122 | 0.33 | 364622 | 1WOLFCR H5-6 | 13.8 | 1.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A | 11 | EKPC_P1-2_GRE-SUMSH161_SRT-A |  | 3 | 0 | 0 | 0.04 | 542969 | STILWEL5 | 161 | 1.0122 | 0.21 | 340576 | WILSON | 24 | 1.0042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A | 12 | EKPC_P1-2_BARR-SUMSH161_SRT-A |  | 3 | 0 | 0 | 0.04 | 542969 | STILWEL5 | 161 | 1.0122 | 0.11 | 340576 | WILSON | 24 | 1.0048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A | 13 | EKPC_P1-2_BULL-SUMSH161_SRT-A |  | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.33 | 340576 | WILSON | 24 | 1.0042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A | 14 | EKPC_P1-2_SSHAD 161 TIE_SRT-A |  | 1 | 0 | 0 | 0.11 | 542969 | STILWEL5 | 161 | 1.0122 | 0.85 | 360334 | 5SUMMER SHAD | 161 | 1.0257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A | 15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.19 | 324002 | 1BROWN 3 | 24 | 1.0518 | 0 | 0 | 93 | 0 | 0 | 0 | 0 | 0
17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A | 16 | EKPC_P1-3_MAR 161/138_SRT-A |  | 3 | 0 | 0 | 0.04 | 542969 | STILWEL5 | 161 | 1.0122 | 0.07 | 324002 | 1BROWN 3 | 24 | 1.0527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A | 18 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A |  | 2 | 0 | 0 | 0.09 | 340576 | WILSON | 24 | 1.0016 | 0.76 | 340576 | WILSON | 24 | 1.0016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A | 19 | EXT_324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1 _SRT-A |  | 1 | 0 | 0 | 0.29 | 342577 | 4FAWKES EK | 138 | 1.0036 | 0.45 | 342577 | 4FAWKES EK | 138 | 1.0036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A | 20 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.15 | 324002 | 1BROWN 3 | 24 | 1.0515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A | 21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A |  | 1 | 0 | 0 | 0.11 | 542969 | STILWEL5 | 161 | 1.0122 | 0.31 | 364001 | 1BR FERRY N1 | 22 | 1.0423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A | 22 | EXT_324217 4BROWN PLANT 138 324219 4BROWN T1 138 1 _SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A | 23 | EXT_324217 4BROWN PLANT 138 324220 4BROWN T2 138 1 _SRT-A |  | 1 | 0 | 0 | 0.11 | 542969 | STILWEL5 | 161 | 1.0122 | 0.22 | 324015 | 1DIX DAM 2 | 13.2 | 1.0068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A | 24 | EXT_324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1 _SRT-A |  | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.12 | 364001 | 1BR FERRY N1 | 22 | 1.0424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A | 25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | Ovl Vlt | 6 | 0 | 0 | 0.09 | 341161 | 2BONNIV EK | 69 | 0.9637 | 0.37 | 340576 | WILSON | 24 | 1.0025 | 11845.1 | 1 | 108.8 | 0.1 | 2 | 0 | 0 | 0
17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A | 26 | EXT_B-138-111_SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A | 27 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A_Dup1 |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.15 | 324002 | 1BROWN 3 | 24 | 1.0515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A | 28 | EXT_BB-1133_SRT-A |  | 1 | 0 | 0 | 0.11 | 542969 | STILWEL5 | 161 | 1.0122 | 0.31 | 364001 | 1BR FERRY N1 | 22 | 1.0423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A | 29 | EXT_MERE SWS_SRT-A |  | 3 | 0 | 0 | 0.04 | 542969 | STILWEL5 | 161 | 1.0122 | 0.07 | 324002 | 1BROWN 3 | 24 | 1.0519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A | 30 | EXT_B-138-115_SRT-A | Vlt | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.26 | 364122 | 1GALLATIN F2 | 24 | 0.9973 | 0 | 0 | 96.1 | 0.3 | 5 | 0 | 0 | 0
17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A | 31 | EXT_B-138-120_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A | 32 | EXT_B-138-121_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A | 33 | EXT_324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1 _SRT-A |  | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.17 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A | 34 | EXT_326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1 _SRT-A |  | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.31 | 340576 | WILSON | 24 | 1.0042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A | 35 | EXT_B-69-18_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.22 | 324002 | 1BROWN 3 | 24 | 1.0522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A | 36 | EXT_B-69-19_SRT-A |  | 3 | 0 | 0 | 0.05 | 325118 | 1RHUDES INV | 34.5 | 1.0776 | 0.17 | 340576 | WILSON | 24 | 1.0014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A | 37 | EXT_BB-1066_SRT-A |  | 2 | 0 | 0 | 0.1 | 542969 | STILWEL5 | 161 | 1.0122 | 0.18 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A | 1 | EKPC_P1-2_MAR-KU LEB138 |  | 3 | 0 | 0 | 0.04 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A | 2 | EKPC_P1-2_COOP-ELIHU161_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 93 | 0 | 0 | 0 | 0 | 0
18 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A | 3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A |  | 5 | 0 | 0 | 0.02 | 342172 | 2RUSS SPR EK | 69 | 0.9896 | 0.11 | 324002 | 1BROWN 3 | 24 | 1.0526 | 0 | 0 | 97.4 | 0 | 0 | 0 | 0 | 0
18 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A | 4 | EKPC_P1-2_COOP-LAUREL161_SRT-A |  | 3 | 0 | 0 | 0.15 | 324446 | 2BOND | 69 | 1.0164 | 0.56 | 324002 | 1BROWN 3 | 24 | 1.0516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A | 5 | EKPC_P1-2_COOP-DEN161_SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A | 6 | EKPC_P1-2_COOP 161 TIE_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.18 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A | 7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.14 | 324002 | 1BROWN 3 | 24 | 1.0521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A | 8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A |  | 2 | 0 | 0 | 0.08 | 325118 | 1RHUDES INV | 34.5 | 1.0762 | 0.25 | 324002 | 1BROWN 3 | 24 | 1.052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A | 9 | EKPC_P1-2_LIBJ-GAS161_SRT-A |  | 3 | 0 | 0 | 0.1 | 325118 | 1RHUDES INV | 34.5 | 1.0753 | 0.22 | 325117 | 1RHUDES COL | 34.5 | 1.0698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A | 10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | Ovl | 2 | 0 | 0 | 0.1 | 542969 | STILWEL5 | 161 | 1.0122 | 0.31 | 364622 | 1WOLFCR H5-6 | 13.8 | 1.01 | 11502 | 1 | 107.2 | 0 | 0 | 0 | 0 | 0
18 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A | 11 | EKPC_P1-2_GRE-SUMSH161_SRT-A |  | 3 | 0 | 0 | 0.1 | 325118 | 1RHUDES INV | 34.5 | 1.0781 | 0.21 | 325117 | 1RHUDES COL | 34.5 | 1.0725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A | 12 | EKPC_P1-2_BARR-SUMSH161_SRT-A |  | 3 | 0 | 0 | 0.07 | 325118 | 1RHUDES INV | 34.5 | 1.0767 | 0.14 | 325117 | 1RHUDES COL | 34.5 | 1.0711 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A | 13 | EKPC_P1-2_BULL-SUMSH161_SRT-A |  | 2 | 0 | 0 | 0.18 | 325118 | 1RHUDES INV | 34.5 | 1.0771 | 0.38 | 325117 | 1RHUDES COL | 34.5 | 1.0715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A | 14 | EKPC_P1-2_SSHAD 161 TIE_SRT-A |  | 1 | 0 | 0 | 0.11 | 542969 | STILWEL5 | 161 | 1.0122 | 0.84 | 360334 | 5SUMMER SHAD | 161 | 1.0255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A | 15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.19 | 324002 | 1BROWN 3 | 24 | 1.052 | 0 | 0 | 92.8 | 0 | 0 | 0 | 0 | 0
18 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A | 16 | EKPC_P1-3_MAR 161/138_SRT-A |  | 3 | 0 | 0 | 0.04 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A | 17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A |  | 2 | 0 | 0 | 0.32 | 325118 | 1RHUDES INV | 34.5 | 1.078 | 0.7 | 325117 | 1RHUDES COL | 34.5 | 1.0723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A | 19 | EXT_324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1 _SRT-A |  | 1 | 0 | 0 | 0.29 | 342577 | 4FAWKES EK | 138 | 1.0036 | 0.44 | 342577 | 4FAWKES EK | 138 | 1.0036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A | 20 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.25 | 325130 | 1RHUDES GEN | 0.6 | 1.1028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A | 21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A |  | 2 | 0 | 0 | 0.32 | 325118 | 1RHUDES INV | 34.5 | 1.0781 | 0.69 | 325117 | 1RHUDES COL | 34.5 | 1.0723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A | 22 | EXT_324217 4BROWN PLANT 138 324219 4BROWN T1 138 1 _SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A | 23 | EXT_324217 4BROWN PLANT 138 324220 4BROWN T2 138 1 _SRT-A |  | 1 | 0 | 0 | 0.11 | 542969 | STILWEL5 | 161 | 1.0122 | 0.24 | 324015 | 1DIX DAM 2 | 13.2 | 1.0082 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A | 24 | EXT_324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1 _SRT-A |  | 3 | 0 | 0 | 0.05 | 325118 | 1RHUDES INV | 34.5 | 1.0764 | 0.11 | 325117 | 1RHUDES COL | 34.5 | 1.0708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A | 25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A |  | 3 | 0 | 0 | 0.21 | 325118 | 1RHUDES INV | 34.5 | 1.078 | 0.52 | 340576 | WILSON | 24 | 1.0026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A | 26 | EXT_B-138-111_SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A | 27 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A_Dup1 |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.25 | 325130 | 1RHUDES GEN | 0.6 | 1.1028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A | 28 | EXT_BB-1133_SRT-A |  | 2 | 0 | 0 | 0.32 | 325118 | 1RHUDES INV | 34.5 | 1.0781 | 0.7 | 325117 | 1RHUDES COL | 34.5 | 1.0723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A | 29 | EXT_MERE SWS_SRT-A |  | 2 | 0 | 0 | 0.34 | 325118 | 1RHUDES INV | 34.5 | 1.0789 | 0.73 | 325117 | 1RHUDES COL | 34.5 | 1.0731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A | 30 | EXT_B-138-115_SRT-A |  | 3 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.22 | 340576 | WILSON | 24 | 1.0012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A | 31 | EXT_B-138-120_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A | 32 | EXT_B-138-121_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A | 33 | EXT_324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1 _SRT-A |  | 2 | 0 | 0 | 0.09 | 542969 | STILWEL5 | 161 | 1.0122 | 0.17 | 325117 | 1RHUDES COL | 34.5 | 1.0706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A | 34 | EXT_326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1 _SRT-A |  | 2 | 0 | 0 | 0.17 | 325118 | 1RHUDES INV | 34.5 | 1.077 | 0.36 | 325117 | 1RHUDES COL | 34.5 | 1.0714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A | 35 | EXT_B-69-18_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.27 | 324002 | 1BROWN 3 | 24 | 1.0523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A | 36 | EXT_B-69-19_SRT-A |  | 3 | 0 | 0 | 0.31 | 325118 | 1RHUDES INV | 34.5 | 1.0747 | 0.65 | 325117 | 1RHUDES COL | 34.5 | 1.0693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A | 37 | EXT_BB-1066_SRT-A |  | 2 | 0 | 0 | 0.1 | 542969 | STILWEL5 | 161 | 1.0122 | 0.18 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | EXT_324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1 _SRT-A | 1 | EKPC_P1-2_MAR-KU LEB138 |  | 2 | 0 | 0 | 0.23 | 325118 | 1RHUDES INV | 34.5 | 1.0764 | 0.55 | 324002 | 1BROWN 3 | 24 | 1.0526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | EXT_324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1 _SRT-A | 2 | EKPC_P1-2_COOP-ELIHU161_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | EXT_324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1 _SRT-A | 3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A |  | 4 | 0 | 0 | 0.11 | 325118 | 1RHUDES INV | 34.5 | 1.0752 | 0.38 | 324002 | 1BROWN 3 | 24 | 1.0525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | EXT_324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1 _SRT-A | 4 | EKPC_P1-2_COOP-LAUREL161_SRT-A |  | 3 | 0 | 0 | 0.15 | 324446 | 2BOND | 69 | 1.0162 | 0.46 | 324002 | 1BROWN 3 | 24 | 1.0515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | EXT_324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1 _SRT-A | 5 | EKPC_P1-2_COOP-DEN161_SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | EXT_324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1 _SRT-A | 6 | EKPC_P1-2_COOP 161 TIE_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.19 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | EXT_324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1 _SRT-A | 7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.1 | 324002 | 1BROWN 3 | 24 | 1.0519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | EXT_324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1 _SRT-A | 8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.25 | 340576 | WILSON | 24 | 1.0038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | EXT_324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1 _SRT-A | 9 | EKPC_P1-2_LIBJ-GAS161_SRT-A |  | 3 | 0 | 0 | 0.09 | 325118 | 1RHUDES INV | 34.5 | 1.074 | 0.18 | 325117 | 1RHUDES COL | 34.5 | 1.0685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | EXT_324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1 _SRT-A | 10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A |  | 2 | 0 | 0 | 0.1 | 542969 | STILWEL5 | 161 | 1.0122 | 0.33 | 364622 | 1WOLFCR H5-6 | 13.8 | 1.0097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | EXT_324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1 _SRT-A | 11 | EKPC_P1-2_GRE-SUMSH161_SRT-A |  | 3 | 0 | 0 | 0.08 | 325118 | 1RHUDES INV | 34.5 | 1.0765 | 0.17 | 325117 | 1RHUDES COL | 34.5 | 1.0709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | EXT_324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1 _SRT-A | 12 | EKPC_P1-2_BARR-SUMSH161_SRT-A |  | 3 | 0 | 0 | 0.06 | 325118 | 1RHUDES INV | 34.5 | 1.0751 | 0.13 | 325117 | 1RHUDES COL | 34.5 | 1.0696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | EXT_324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1 _SRT-A | 13 | EKPC_P1-2_BULL-SUMSH161_SRT-A |  | 2 | 0 | 0 | 0.18 | 325118 | 1RHUDES INV | 34.5 | 1.0758 | 0.38 | 325117 | 1RHUDES COL | 34.5 | 1.0703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | EXT_324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1 _SRT-A | 14 | EKPC_P1-2_SSHAD 161 TIE_SRT-A |  | 1 | 0 | 0 | 0.11 | 542969 | STILWEL5 | 161 | 1.0122 | 0.84 | 360334 | 5SUMMER SHAD | 161 | 1.0261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | EXT_324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1 _SRT-A | 15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.18 | 324002 | 1BROWN 3 | 24 | 1.0518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | EXT_324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1 _SRT-A | 16 | EKPC_P1-3_MAR 161/138_SRT-A |  | 2 | 0 | 0 | 0.23 | 325118 | 1RHUDES INV | 34.5 | 1.0764 | 0.55 | 324002 | 1BROWN 3 | 24 | 1.0526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | EXT_324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1 _SRT-A | 17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A |  | 2 | 0 | 0 | 0.34 | 325118 | 1RHUDES INV | 34.5 | 1.0775 | 0.72 | 325117 | 1RHUDES COL | 34.5 | 1.0718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | EXT_324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1 _SRT-A | 18 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.17 | 340576 | WILSON | 24 | 1.0011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | EXT_324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1 _SRT-A | 20 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.16 | 324002 | 1BROWN 3 | 24 | 1.0513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | EXT_324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1 _SRT-A | 21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A |  | 2 | 0 | 0 | 0.31 | 325118 | 1RHUDES INV | 34.5 | 1.0772 | 0.65 | 325117 | 1RHUDES COL | 34.5 | 1.0715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | EXT_324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1 _SRT-A | 22 | EXT_324217 4BROWN PLANT 138 324219 4BROWN T1 138 1 _SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | EXT_324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1 _SRT-A | 23 | EXT_324217 4BROWN PLANT 138 324220 4BROWN T2 138 1 _SRT-A |  | 1 | 0 | 0 | 0.11 | 542969 | STILWEL5 | 161 | 1.0122 | 0.23 | 324015 | 1DIX DAM 2 | 13.2 | 1.007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | EXT_324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1 _SRT-A | 24 | EXT_324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1 _SRT-A |  | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.52 | 340576 | WILSON | 24 | 1.0038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | EXT_324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1 _SRT-A | 25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.11 | 324002 | 1BROWN 3 | 24 | 1.0523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | EXT_324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1 _SRT-A | 26 | EXT_B-138-111_SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | EXT_324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1 _SRT-A | 27 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A_Dup1 |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.16 | 324002 | 1BROWN 3 | 24 | 1.0513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | EXT_324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1 _SRT-A | 28 | EXT_BB-1133_SRT-A |  | 2 | 0 | 0 | 0.32 | 325118 | 1RHUDES INV | 34.5 | 1.0773 | 0.68 | 325117 | 1RHUDES COL | 34.5 | 1.0716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | EXT_324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1 _SRT-A | 29 | EXT_MERE SWS_SRT-A |  | 2 | 0 | 0 | 0.47 | 325118 | 1RHUDES INV | 34.5 | 1.0789 | 1 | 325117 | 1RHUDES COL | 34.5 | 1.0731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | EXT_324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1 _SRT-A | 30 | EXT_B-138-115_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.32 | 324002 | 1BROWN 3 | 24 | 1.0522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | EXT_324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1 _SRT-A | 31 | EXT_B-138-120_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | EXT_324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1 _SRT-A | 32 | EXT_B-138-121_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | EXT_324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1 _SRT-A | 33 | EXT_324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1 _SRT-A |  | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.17 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | EXT_324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1 _SRT-A | 34 | EXT_326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1 _SRT-A |  | 2 | 0 | 0 | 0.17 | 325118 | 1RHUDES INV | 34.5 | 1.0757 | 0.36 | 325117 | 1RHUDES COL | 34.5 | 1.0702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | EXT_324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1 _SRT-A | 35 | EXT_B-69-18_SRT-A |  | 3 | 0 | 0 | 0.05 | 325118 | 1RHUDES INV | 34.5 | 1.0775 | 0.23 | 324002 | 1BROWN 3 | 24 | 1.0521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | EXT_324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1 _SRT-A | 36 | EXT_B-69-19_SRT-A |  | 4 | 0 | 0 | 0.33 | 325118 | 1RHUDES INV | 34.5 | 1.0743 | 0.7 | 325117 | 1RHUDES COL | 34.5 | 1.0689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | EXT_324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1 _SRT-A | 37 | EXT_BB-1066_SRT-A |  | 2 | 0 | 0 | 0.1 | 542969 | STILWEL5 | 161 | 1.0122 | 0.17 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A | 1 | EKPC_P1-2_MAR-KU LEB138 |  | 3 | 0 | 0 | 0.1 | 342000 | 5GAS | 161 | 1 | 0.31 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A | 2 | EKPC_P1-2_COOP-ELIHU161_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A | 3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A |  | 5 | 0 | 0 | 0.02 | 158981 | ARMOW_BUS2 | 34.5 | 1.025 | 0.07 | 340576 | WILSON | 24 | 1.0039 | 0 | 0 | 97.8 | 0 | 0 | 0 | 0 | 0
20 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A | 4 | EKPC_P1-2_COOP-LAUREL161_SRT-A |  | 3 | 0 | 0 | 0.15 | 324446 | 2BOND | 69 | 1.0164 | 0.55 | 324002 | 1BROWN 3 | 24 | 1.0511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A | 5 | EKPC_P1-2_COOP-DEN161_SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A | 6 | EKPC_P1-2_COOP 161 TIE_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.19 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A | 7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.14 | 324002 | 1BROWN 3 | 24 | 1.0516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A | 8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A |  | 3 | 0 | 0 | 0.2 | 325118 | 1RHUDES INV | 34.5 | 1.0758 | 0.42 | 325117 | 1RHUDES COL | 34.5 | 1.0702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A | 9 | EKPC_P1-2_LIBJ-GAS161_SRT-A |  | 3 | 0 | 0 | 0.2 | 325118 | 1RHUDES INV | 34.5 | 1.0755 | 0.43 | 325117 | 1RHUDES COL | 34.5 | 1.07 | 0 | 0 | 98 | 0 | 0 | 0 | 0 | 0
20 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A | 10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | Ovl | 4 | 0 | 0 | 0.04 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 12762.8 | 1 | 113 | 0 | 0 | 0 | 0 | 0
20 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A | 11 | EKPC_P1-2_GRE-SUMSH161_SRT-A |  | 3 | 0 | 0 | 0.42 | 325118 | 1RHUDES INV | 34.5 | 1.0743 | 0.89 | 325117 | 1RHUDES COL | 34.5 | 1.0689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A | 12 | EKPC_P1-2_BARR-SUMSH161_SRT-A |  | 3 | 0 | 0 | 0.07 | 325118 | 1RHUDES INV | 34.5 | 1.0761 | 0.15 | 325117 | 1RHUDES COL | 34.5 | 1.0705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A | 13 | EKPC_P1-2_BULL-SUMSH161_SRT-A |  | 2 | 0 | 0 | 0.18 | 325118 | 1RHUDES INV | 34.5 | 1.0767 | 0.38 | 325117 | 1RHUDES COL | 34.5 | 1.0711 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A | 14 | EKPC_P1-2_SSHAD 161 TIE_SRT-A |  | 1 | 0 | 0 | 0.11 | 542969 | STILWEL5 | 161 | 1.0122 | 0.84 | 361788 | 5SUM SHAD TP | 161 | 1.0255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A | 15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.23 | 325130 | 1RHUDES GEN | 0.6 | 1.1027 | 0 | 0 | 93.4 | 0 | 0 | 0 | 0 | 0
20 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A | 16 | EKPC_P1-3_MAR 161/138_SRT-A |  | 3 | 0 | 0 | 0.1 | 342000 | 5GAS | 161 | 1 | 0.31 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A | 17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.14 | 325130 | 1RHUDES GEN | 0.6 | 1.1061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A | 18 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.17 | 340576 | WILSON | 24 | 1.0012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A | 19 | EXT_324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1 _SRT-A |  | 1 | 0 | 0 | 0.31 | 342577 | 4FAWKES EK | 138 | 1.0037 | 0.49 | 342577 | 4FAWKES EK | 138 | 1.0037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A | 21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.13 | 325130 | 1RHUDES GEN | 0.6 | 1.1055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A | 22 | EXT_324217 4BROWN PLANT 138 324219 4BROWN T1 138 1 _SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A | 23 | EXT_324217 4BROWN PLANT 138 324220 4BROWN T2 138 1 _SRT-A |  | 1 | 0 | 0 | 0.11 | 542969 | STILWEL5 | 161 | 1.0122 | 0.21 | 324015 | 1DIX DAM 2 | 13.2 | 1.0054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A | 24 | EXT_324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1 _SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.28 | 324002 | 1BROWN 3 | 24 | 1.0518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A | 25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A |  | 4 | 0 | 0 | 0.09 | 340576 | WILSON | 24 | 1.0033 | 0.66 | 340576 | WILSON | 24 | 1.0033 | 0 | 0 | 90.9 | 0 | 0 | 0 | 0 | 0
20 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A | 26 | EXT_B-138-111_SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A | 28 | EXT_BB-1133_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.14 | 325130 | 1RHUDES GEN | 0.6 | 1.1058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A | 29 | EXT_MERE SWS_SRT-A |  | 2 | 0 | 0 | 0.37 | 325118 | 1RHUDES INV | 34.5 | 1.0784 | 0.8 | 325117 | 1RHUDES COL | 34.5 | 1.0726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A | 30 | EXT_B-138-115_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.31 | 340576 | WILSON | 24 | 1.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A | 31 | EXT_B-138-120_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A | 32 | EXT_B-138-121_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A | 33 | EXT_324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1 _SRT-A |  | 2 | 0 | 0 | 0.09 | 542969 | STILWEL5 | 161 | 1.0122 | 0.18 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A | 34 | EXT_326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1 _SRT-A |  | 2 | 0 | 0 | 0.17 | 325118 | 1RHUDES INV | 34.5 | 1.0766 | 0.36 | 325117 | 1RHUDES COL | 34.5 | 1.071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A | 35 | EXT_B-69-18_SRT-A |  | 3 | 0 | 0 | 0.09 | 342000 | 5GAS | 161 | 1 | 0.27 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A | 36 | EXT_B-69-19_SRT-A |  | 4 | 0 | 0 | 0.33 | 325118 | 1RHUDES INV | 34.5 | 1.0748 | 0.7 | 325117 | 1RHUDES COL | 34.5 | 1.0694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A | 37 | EXT_BB-1066_SRT-A |  | 2 | 0 | 0 | 0.1 | 542969 | STILWEL5 | 161 | 1.0122 | 0.19 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A | 1 | EKPC_P1-2_MAR-KU LEB138 |  | 3 | 0 | 0 | 0.04 | 542969 | STILWEL5 | 161 | 1.0122 | 0.06 | 324002 | 1BROWN 3 | 24 | 1.0525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A | 2 | EKPC_P1-2_COOP-ELIHU161_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A | 3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A |  | 4 | 0 | 0 | 0.05 | 324830 | 2CAMPBELV EK | 69 | 0.9932 | 0.43 | 324002 | 1BROWN 3 | 24 | 1.0525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A | 4 | EKPC_P1-2_COOP-LAUREL161_SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.08 | 324002 | 1BROWN 3 | 24 | 1.0513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A | 5 | EKPC_P1-2_COOP-DEN161_SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A | 6 | EKPC_P1-2_COOP 161 TIE_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.18 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A | 7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.17 | 324002 | 1BROWN 3 | 24 | 1.0518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A | 8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A | 9 | EKPC_P1-2_LIBJ-GAS161_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.08 | 325117 | 1RHUDES COL | 34.5 | 1.072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A | 10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A |  | 3 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.06 | 325117 | 1RHUDES COL | 34.5 | 1.072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A | 11 | EKPC_P1-2_GRE-SUMSH161_SRT-A |  | 3 | 0 | 0 | 0.04 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A | 12 | EKPC_P1-2_BARR-SUMSH161_SRT-A |  | 3 | 0 | 0 | 0.04 | 542969 | STILWEL5 | 161 | 1.0122 | 0.11 | 340576 | WILSON | 24 | 1.0049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A | 13 | EKPC_P1-2_BULL-SUMSH161_SRT-A |  | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.94 | 325055 | 4RHUDES TP | 138 | 1.0145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A | 14 | EKPC_P1-2_SSHAD 161 TIE_SRT-A |  | 1 | 0 | 0 | 0.11 | 542969 | STILWEL5 | 161 | 1.0122 | 0.85 | 360334 | 5SUMMER SHAD | 161 | 1.0257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A | 15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.18 | 324002 | 1BROWN 3 | 24 | 1.0518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A | 16 | EKPC_P1-3_MAR 161/138_SRT-A |  | 3 | 0 | 0 | 0.04 | 542969 | STILWEL5 | 161 | 1.0122 | 0.06 | 324002 | 1BROWN 3 | 24 | 1.0525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A | 17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A |  | 1 | 0 | 0 | 0.13 | 341161 | 2BONNIV EK | 69 | 0.9934 | 0.48 | 340576 | WILSON | 24 | 1.0042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A | 18 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A |  | 2 | 0 | 0 | 0.09 | 340576 | WILSON | 24 | 1.0017 | 0.91 | 340576 | WILSON | 24 | 1.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A | 19 | EXT_324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1 _SRT-A |  | 1 | 0 | 0 | 0.29 | 342577 | 4FAWKES EK | 138 | 1.0037 | 0.45 | 342577 | 4FAWKES EK | 138 | 1.0037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A | 20 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.14 | 324002 | 1BROWN 3 | 24 | 1.0514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A | 22 | EXT_324217 4BROWN PLANT 138 324219 4BROWN T1 138 1 _SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A | 23 | EXT_324217 4BROWN PLANT 138 324220 4BROWN T2 138 1 _SRT-A |  | 1 | 0 | 0 | 0.11 | 542969 | STILWEL5 | 161 | 1.0122 | 0.22 | 324015 | 1DIX DAM 2 | 13.2 | 1.0067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A | 24 | EXT_324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1 _SRT-A |  | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.11 | 364001 | 1BR FERRY N1 | 22 | 1.0424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A | 25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | Ovl Vlt | 6 | 0 | 0 | 0.09 | 341161 | 2BONNIV EK | 69 | 0.9608 | 0.4 | 340576 | WILSON | 24 | 1.0026 | 13202.6 | 1 | 114.9 | 0.2 | 3 | 0 | 0 | 0
21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A | 26 | EXT_B-138-111_SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A | 27 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A_Dup1 |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.14 | 324002 | 1BROWN 3 | 24 | 1.0514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A | 28 | EXT_BB-1133_SRT-A |  | 1 | 0 | 0 | 0.13 | 341161 | 2BONNIV EK | 69 | 0.9934 | 0.48 | 340576 | WILSON | 24 | 1.0042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A | 29 | EXT_MERE SWS_SRT-A |  | 3 | 0 | 0 | 0.04 | 542969 | STILWEL5 | 161 | 1.0122 | 0.07 | 324002 | 1BROWN 3 | 24 | 1.0519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A | 30 | EXT_B-138-115_SRT-A | Ovl Vlt | 3 | 0 | 0 | 0.06 | 341161 | 2BONNIV EK | 69 | 0.9552 | 0.27 | 364122 | 1GALLATIN F2 | 24 | 0.9974 | 10424.2 | 1 | 102.1 | 0.6 | 6 | 0 | 0 | 0
21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A | 31 | EXT_B-138-120_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A | 32 | EXT_B-138-121_SRT-A |  | 3 | 0 | 0 | 0.04 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A | 33 | EXT_324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1 _SRT-A |  | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.17 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A | 34 | EXT_326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1 _SRT-A |  | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.21 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A | 35 | EXT_B-69-18_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.22 | 324002 | 1BROWN 3 | 24 | 1.0522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A | 36 | EXT_B-69-19_SRT-A |  | 3 | 0 | 0 | 0.05 | 325118 | 1RHUDES INV | 34.5 | 1.0774 | 0.19 | 340576 | WILSON | 24 | 1.0013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A | 37 | EXT_BB-1066_SRT-A |  | 2 | 0 | 0 | 0.1 | 542969 | STILWEL5 | 161 | 1.0122 | 0.17 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | EXT_324217 4BROWN PLANT 138 324219 4BROWN T1 138 1 _SRT-A | 1 | EKPC_P1-2_MAR-KU LEB138 |  | 2 | 0 | 0 | 0.23 | 325118 | 1RHUDES INV | 34.5 | 1.077 | 0.58 | 324002 | 1BROWN 3 | 24 | 1.0526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | EXT_324217 4BROWN PLANT 138 324219 4BROWN T1 138 1 _SRT-A | 2 | EKPC_P1-2_COOP-ELIHU161_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | EXT_324217 4BROWN PLANT 138 324219 4BROWN T1 138 1 _SRT-A | 3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A |  | 4 | 0 | 0 | 0.11 | 325118 | 1RHUDES INV | 34.5 | 1.0757 | 0.42 | 324002 | 1BROWN 3 | 24 | 1.0525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | EXT_324217 4BROWN PLANT 138 324219 4BROWN T1 138 1 _SRT-A | 4 | EKPC_P1-2_COOP-LAUREL161_SRT-A |  | 3 | 0 | 0 | 0.15 | 324446 | 2BOND | 69 | 1.0164 | 0.55 | 324002 | 1BROWN 3 | 24 | 1.0514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | EXT_324217 4BROWN PLANT 138 324219 4BROWN T1 138 1 _SRT-A | 5 | EKPC_P1-2_COOP-DEN161_SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | EXT_324217 4BROWN PLANT 138 324219 4BROWN T1 138 1 _SRT-A | 6 | EKPC_P1-2_COOP 161 TIE_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.19 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | EXT_324217 4BROWN PLANT 138 324219 4BROWN T1 138 1 _SRT-A | 7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.14 | 324002 | 1BROWN 3 | 24 | 1.0519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | EXT_324217 4BROWN PLANT 138 324219 4BROWN T1 138 1 _SRT-A | 8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.26 | 340576 | WILSON | 24 | 1.0039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | EXT_324217 4BROWN PLANT 138 324219 4BROWN T1 138 1 _SRT-A | 9 | EKPC_P1-2_LIBJ-GAS161_SRT-A |  | 3 | 0 | 0 | 0.09 | 325118 | 1RHUDES INV | 34.5 | 1.0745 | 0.18 | 325117 | 1RHUDES COL | 34.5 | 1.069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | EXT_324217 4BROWN PLANT 138 324219 4BROWN T1 138 1 _SRT-A | 10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A |  | 2 | 0 | 0 | 0.1 | 542969 | STILWEL5 | 161 | 1.0122 | 0.33 | 364622 | 1WOLFCR H5-6 | 13.8 | 1.0096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | EXT_324217 4BROWN PLANT 138 324219 4BROWN T1 138 1 _SRT-A | 11 | EKPC_P1-2_GRE-SUMSH161_SRT-A |  | 3 | 0 | 0 | 0.08 | 325118 | 1RHUDES INV | 34.5 | 1.0771 | 0.18 | 325117 | 1RHUDES COL | 34.5 | 1.0714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | EXT_324217 4BROWN PLANT 138 324219 4BROWN T1 138 1 _SRT-A | 12 | EKPC_P1-2_BARR-SUMSH161_SRT-A |  | 3 | 0 | 0 | 0.06 | 325118 | 1RHUDES INV | 34.5 | 1.0756 | 0.13 | 325117 | 1RHUDES COL | 34.5 | 1.0701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | EXT_324217 4BROWN PLANT 138 324219 4BROWN T1 138 1 _SRT-A | 13 | EKPC_P1-2_BULL-SUMSH161_SRT-A |  | 2 | 0 | 0 | 0.18 | 325118 | 1RHUDES INV | 34.5 | 1.0764 | 0.38 | 325117 | 1RHUDES COL | 34.5 | 1.0708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | EXT_324217 4BROWN PLANT 138 324219 4BROWN T1 138 1 _SRT-A | 14 | EKPC_P1-2_SSHAD 161 TIE_SRT-A |  | 1 | 0 | 0 | 0.11 | 542969 | STILWEL5 | 161 | 1.0122 | 0.84 | 360334 | 5SUMMER SHAD | 161 | 1.0261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | EXT_324217 4BROWN PLANT 138 324219 4BROWN T1 138 1 _SRT-A | 15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.18 | 324002 | 1BROWN 3 | 24 | 1.0518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | EXT_324217 4BROWN PLANT 138 324219 4BROWN T1 138 1 _SRT-A | 16 | EKPC_P1-3_MAR 161/138_SRT-A |  | 2 | 0 | 0 | 0.23 | 325118 | 1RHUDES INV | 34.5 | 1.077 | 0.58 | 324002 | 1BROWN 3 | 24 | 1.0526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | EXT_324217 4BROWN PLANT 138 324219 4BROWN T1 138 1 _SRT-A | 17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A |  | 2 | 0 | 0 | 0.34 | 325118 | 1RHUDES INV | 34.5 | 1.078 | 0.72 | 325117 | 1RHUDES COL | 34.5 | 1.0723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | EXT_324217 4BROWN PLANT 138 324219 4BROWN T1 138 1 _SRT-A | 18 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.17 | 340576 | WILSON | 24 | 1.0011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | EXT_324217 4BROWN PLANT 138 324219 4BROWN T1 138 1 _SRT-A | 19 | EXT_324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1 _SRT-A |  | 1 | 0 | 0 | 0.29 | 342577 | 4FAWKES EK | 138 | 1.0037 | 0.46 | 342577 | 4FAWKES EK | 138 | 1.0037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | EXT_324217 4BROWN PLANT 138 324219 4BROWN T1 138 1 _SRT-A | 20 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.14 | 324002 | 1BROWN 3 | 24 | 1.0513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | EXT_324217 4BROWN PLANT 138 324219 4BROWN T1 138 1 _SRT-A | 21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A |  | 2 | 0 | 0 | 0.31 | 325118 | 1RHUDES INV | 34.5 | 1.0777 | 0.65 | 325117 | 1RHUDES COL | 34.5 | 1.072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | EXT_324217 4BROWN PLANT 138 324219 4BROWN T1 138 1 _SRT-A | 23 | EXT_324217 4BROWN PLANT 138 324220 4BROWN T2 138 1 _SRT-A |  | 4 | 0 | 0 | 0.04 | 542969 | STILWEL5 | 161 | 1.0122 | 0.07 | 253357 | AB1-169 CT2 | 25 | 1.0107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | EXT_324217 4BROWN PLANT 138 324219 4BROWN T1 138 1 _SRT-A | 24 | EXT_324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1 _SRT-A |  | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.52 | 340576 | WILSON | 24 | 1.0039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | EXT_324217 4BROWN PLANT 138 324219 4BROWN T1 138 1 _SRT-A | 25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.12 | 324002 | 1BROWN 3 | 24 | 1.0523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | EXT_324217 4BROWN PLANT 138 324219 4BROWN T1 138 1 _SRT-A | 26 | EXT_B-138-111_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.13 | 324002 | 1BROWN 3 | 24 | 1.052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | EXT_324217 4BROWN PLANT 138 324219 4BROWN T1 138 1 _SRT-A | 27 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A_Dup1 |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.14 | 324002 | 1BROWN 3 | 24 | 1.0513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | EXT_324217 4BROWN PLANT 138 324219 4BROWN T1 138 1 _SRT-A | 28 | EXT_BB-1133_SRT-A |  | 2 | 0 | 0 | 0.32 | 325118 | 1RHUDES INV | 34.5 | 1.0778 | 0.68 | 325117 | 1RHUDES COL | 34.5 | 1.0721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | EXT_324217 4BROWN PLANT 138 324219 4BROWN T1 138 1 _SRT-A | 29 | EXT_MERE SWS_SRT-A |  | 2 | 0 | 0 | 0.43 | 325118 | 1RHUDES INV | 34.5 | 1.0789 | 0.9 | 325117 | 1RHUDES COL | 34.5 | 1.0732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | EXT_324217 4BROWN PLANT 138 324219 4BROWN T1 138 1 _SRT-A | 30 | EXT_B-138-115_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.36 | 324002 | 1BROWN 3 | 24 | 1.0521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | EXT_324217 4BROWN PLANT 138 324219 4BROWN T1 138 1 _SRT-A | 31 | EXT_B-138-120_SRT-A |  | 1 | 0 | 0 | 0.11 | 542969 | STILWEL5 | 161 | 1.0122 | 0.3 | 324218 | 4BROWN CT | 138 | 1.0149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | EXT_324217 4BROWN PLANT 138 324219 4BROWN T1 138 1 _SRT-A | 32 | EXT_B-138-121_SRT-A |  | 4 | 0 | 0 | 0.04 | 542969 | STILWEL5 | 161 | 1.0122 | 0.07 | 253357 | AB1-169 CT2 | 25 | 1.0107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | EXT_324217 4BROWN PLANT 138 324219 4BROWN T1 138 1 _SRT-A | 33 | EXT_324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1 _SRT-A |  | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.17 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | EXT_324217 4BROWN PLANT 138 324219 4BROWN T1 138 1 _SRT-A | 34 | EXT_326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1 _SRT-A |  | 2 | 0 | 0 | 0.17 | 325118 | 1RHUDES INV | 34.5 | 1.0763 | 0.36 | 325117 | 1RHUDES COL | 34.5 | 1.0707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | EXT_324217 4BROWN PLANT 138 324219 4BROWN T1 138 1 _SRT-A | 35 | EXT_B-69-18_SRT-A |  | 3 | 0 | 0 | 0.05 | 325118 | 1RHUDES INV | 34.5 | 1.0774 | 0.24 | 324002 | 1BROWN 3 | 24 | 1.0521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | EXT_324217 4BROWN PLANT 138 324219 4BROWN T1 138 1 _SRT-A | 36 | EXT_B-69-19_SRT-A |  | 4 | 0 | 0 | 0.33 | 325118 | 1RHUDES INV | 34.5 | 1.0748 | 0.7 | 325117 | 1RHUDES COL | 34.5 | 1.0693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | EXT_324217 4BROWN PLANT 138 324219 4BROWN T1 138 1 _SRT-A | 37 | EXT_BB-1066_SRT-A |  | 2 | 0 | 0 | 0.1 | 542969 | STILWEL5 | 161 | 1.0122 | 0.17 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | EXT_324217 4BROWN PLANT 138 324220 4BROWN T2 138 1 _SRT-A | 1 | EKPC_P1-2_MAR-KU LEB138 |  | 2 | 0 | 0 | 0.23 | 325118 | 1RHUDES INV | 34.5 | 1.077 | 0.59 | 324002 | 1BROWN 3 | 24 | 1.0527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | EXT_324217 4BROWN PLANT 138 324220 4BROWN T2 138 1 _SRT-A | 2 | EKPC_P1-2_COOP-ELIHU161_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | EXT_324217 4BROWN PLANT 138 324220 4BROWN T2 138 1 _SRT-A | 3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A |  | 4 | 0 | 0 | 0.11 | 325118 | 1RHUDES INV | 34.5 | 1.0757 | 0.42 | 324002 | 1BROWN 3 | 24 | 1.0526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | EXT_324217 4BROWN PLANT 138 324220 4BROWN T2 138 1 _SRT-A | 4 | EKPC_P1-2_COOP-LAUREL161_SRT-A |  | 3 | 0 | 0 | 0.15 | 324446 | 2BOND | 69 | 1.0164 | 0.56 | 324002 | 1BROWN 3 | 24 | 1.0515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | EXT_324217 4BROWN PLANT 138 324220 4BROWN T2 138 1 _SRT-A | 5 | EKPC_P1-2_COOP-DEN161_SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | EXT_324217 4BROWN PLANT 138 324220 4BROWN T2 138 1 _SRT-A | 6 | EKPC_P1-2_COOP 161 TIE_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.19 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | EXT_324217 4BROWN PLANT 138 324220 4BROWN T2 138 1 _SRT-A | 7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.14 | 324002 | 1BROWN 3 | 24 | 1.0519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | EXT_324217 4BROWN PLANT 138 324220 4BROWN T2 138 1 _SRT-A | 8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.26 | 340576 | WILSON | 24 | 1.0039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | EXT_324217 4BROWN PLANT 138 324220 4BROWN T2 138 1 _SRT-A | 9 | EKPC_P1-2_LIBJ-GAS161_SRT-A |  | 3 | 0 | 0 | 0.09 | 325118 | 1RHUDES INV | 34.5 | 1.0745 | 0.18 | 325117 | 1RHUDES COL | 34.5 | 1.069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | EXT_324217 4BROWN PLANT 138 324220 4BROWN T2 138 1 _SRT-A | 10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A |  | 2 | 0 | 0 | 0.1 | 542969 | STILWEL5 | 161 | 1.0122 | 0.33 | 364622 | 1WOLFCR H5-6 | 13.8 | 1.0096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | EXT_324217 4BROWN PLANT 138 324220 4BROWN T2 138 1 _SRT-A | 11 | EKPC_P1-2_GRE-SUMSH161_SRT-A |  | 3 | 0 | 0 | 0.08 | 325118 | 1RHUDES INV | 34.5 | 1.0771 | 0.17 | 325117 | 1RHUDES COL | 34.5 | 1.0714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | EXT_324217 4BROWN PLANT 138 324220 4BROWN T2 138 1 _SRT-A | 12 | EKPC_P1-2_BARR-SUMSH161_SRT-A |  | 3 | 0 | 0 | 0.06 | 325118 | 1RHUDES INV | 34.5 | 1.0756 | 0.13 | 325117 | 1RHUDES COL | 34.5 | 1.0701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | EXT_324217 4BROWN PLANT 138 324220 4BROWN T2 138 1 _SRT-A | 13 | EKPC_P1-2_BULL-SUMSH161_SRT-A |  | 2 | 0 | 0 | 0.18 | 325118 | 1RHUDES INV | 34.5 | 1.0764 | 0.38 | 325117 | 1RHUDES COL | 34.5 | 1.0708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | EXT_324217 4BROWN PLANT 138 324220 4BROWN T2 138 1 _SRT-A | 14 | EKPC_P1-2_SSHAD 161 TIE_SRT-A |  | 1 | 0 | 0 | 0.11 | 542969 | STILWEL5 | 161 | 1.0122 | 0.84 | 360334 | 5SUMMER SHAD | 161 | 1.0261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | EXT_324217 4BROWN PLANT 138 324220 4BROWN T2 138 1 _SRT-A | 15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.18 | 324002 | 1BROWN 3 | 24 | 1.0519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | EXT_324217 4BROWN PLANT 138 324220 4BROWN T2 138 1 _SRT-A | 16 | EKPC_P1-3_MAR 161/138_SRT-A |  | 2 | 0 | 0 | 0.23 | 325118 | 1RHUDES INV | 34.5 | 1.077 | 0.59 | 324002 | 1BROWN 3 | 24 | 1.0527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | EXT_324217 4BROWN PLANT 138 324220 4BROWN T2 138 1 _SRT-A | 17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A |  | 2 | 0 | 0 | 0.34 | 325118 | 1RHUDES INV | 34.5 | 1.078 | 0.72 | 325117 | 1RHUDES COL | 34.5 | 1.0723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | EXT_324217 4BROWN PLANT 138 324220 4BROWN T2 138 1 _SRT-A | 18 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.17 | 340576 | WILSON | 24 | 1.0011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | EXT_324217 4BROWN PLANT 138 324220 4BROWN T2 138 1 _SRT-A | 19 | EXT_324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1 _SRT-A |  | 1 | 0 | 0 | 0.29 | 342577 | 4FAWKES EK | 138 | 1.0037 | 0.44 | 342577 | 4FAWKES EK | 138 | 1.0037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | EXT_324217 4BROWN PLANT 138 324220 4BROWN T2 138 1 _SRT-A | 20 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.15 | 324002 | 1BROWN 3 | 24 | 1.0514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | EXT_324217 4BROWN PLANT 138 324220 4BROWN T2 138 1 _SRT-A | 21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A |  | 2 | 0 | 0 | 0.31 | 325118 | 1RHUDES INV | 34.5 | 1.0777 | 0.65 | 325117 | 1RHUDES COL | 34.5 | 1.072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | EXT_324217 4BROWN PLANT 138 324220 4BROWN T2 138 1 _SRT-A | 22 | EXT_324217 4BROWN PLANT 138 324219 4BROWN T1 138 1 _SRT-A |  | 4 | 0 | 0 | 0.04 | 542969 | STILWEL5 | 161 | 1.0122 | 0.07 | 253357 | AB1-169 CT2 | 25 | 1.0107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | EXT_324217 4BROWN PLANT 138 324220 4BROWN T2 138 1 _SRT-A | 24 | EXT_324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1 _SRT-A |  | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.52 | 340576 | WILSON | 24 | 1.0039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | EXT_324217 4BROWN PLANT 138 324220 4BROWN T2 138 1 _SRT-A | 25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.12 | 324002 | 1BROWN 3 | 24 | 1.0524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | EXT_324217 4BROWN PLANT 138 324220 4BROWN T2 138 1 _SRT-A | 26 | EXT_B-138-111_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.12 | 324002 | 1BROWN 3 | 24 | 1.052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | EXT_324217 4BROWN PLANT 138 324220 4BROWN T2 138 1 _SRT-A | 27 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A_Dup1 |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.15 | 324002 | 1BROWN 3 | 24 | 1.0514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | EXT_324217 4BROWN PLANT 138 324220 4BROWN T2 138 1 _SRT-A | 28 | EXT_BB-1133_SRT-A |  | 2 | 0 | 0 | 0.32 | 325118 | 1RHUDES INV | 34.5 | 1.0778 | 0.68 | 325117 | 1RHUDES COL | 34.5 | 1.0721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | EXT_324217 4BROWN PLANT 138 324220 4BROWN T2 138 1 _SRT-A | 29 | EXT_MERE SWS_SRT-A |  | 2 | 0 | 0 | 0.43 | 325118 | 1RHUDES INV | 34.5 | 1.0789 | 0.91 | 325117 | 1RHUDES COL | 34.5 | 1.0732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | EXT_324217 4BROWN PLANT 138 324220 4BROWN T2 138 1 _SRT-A | 30 | EXT_B-138-115_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.36 | 324002 | 1BROWN 3 | 24 | 1.0523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | EXT_324217 4BROWN PLANT 138 324220 4BROWN T2 138 1 _SRT-A | 31 | EXT_B-138-120_SRT-A |  | 4 | 0 | 0 | 0.04 | 542969 | STILWEL5 | 161 | 1.0122 | 0.07 | 253357 | AB1-169 CT2 | 25 | 1.0107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | EXT_324217 4BROWN PLANT 138 324220 4BROWN T2 138 1 _SRT-A | 32 | EXT_B-138-121_SRT-A |  | 3 | 0 | 0 | 0.04 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | EXT_324217 4BROWN PLANT 138 324220 4BROWN T2 138 1 _SRT-A | 33 | EXT_324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1 _SRT-A |  | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.17 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | EXT_324217 4BROWN PLANT 138 324220 4BROWN T2 138 1 _SRT-A | 34 | EXT_326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1 _SRT-A |  | 2 | 0 | 0 | 0.17 | 325118 | 1RHUDES INV | 34.5 | 1.0763 | 0.36 | 325117 | 1RHUDES COL | 34.5 | 1.0707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | EXT_324217 4BROWN PLANT 138 324220 4BROWN T2 138 1 _SRT-A | 35 | EXT_B-69-18_SRT-A |  | 3 | 0 | 0 | 0.05 | 325118 | 1RHUDES INV | 34.5 | 1.0774 | 0.25 | 324002 | 1BROWN 3 | 24 | 1.0522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | EXT_324217 4BROWN PLANT 138 324220 4BROWN T2 138 1 _SRT-A | 36 | EXT_B-69-19_SRT-A |  | 4 | 0 | 0 | 0.33 | 325118 | 1RHUDES INV | 34.5 | 1.0748 | 0.7 | 325117 | 1RHUDES COL | 34.5 | 1.0693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | EXT_324217 4BROWN PLANT 138 324220 4BROWN T2 138 1 _SRT-A | 37 | EXT_BB-1066_SRT-A |  | 2 | 0 | 0 | 0.1 | 542969 | STILWEL5 | 161 | 1.0122 | 0.17 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | EXT_324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1 _SRT-A | 1 | EKPC_P1-2_MAR-KU LEB138 |  | 3 | 0 | 0 | 0.09 | 342000 | 5GAS | 161 | 1 | 0.3 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | EXT_324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1 _SRT-A | 2 | EKPC_P1-2_COOP-ELIHU161_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | EXT_324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1 _SRT-A | 3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A |  | 4 | 0 | 0 | 0.16 | 325118 | 1RHUDES INV | 34.5 | 1.0765 | 0.43 | 324002 | 1BROWN 3 | 24 | 1.0524 | 0 | 0 | 93.1 | 0 | 0 | 0 | 0 | 0
24 | EXT_324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1 _SRT-A | 4 | EKPC_P1-2_COOP-LAUREL161_SRT-A |  | 3 | 0 | 0 | 0.15 | 324446 | 2BOND | 69 | 1.0164 | 0.55 | 324002 | 1BROWN 3 | 24 | 1.0513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | EXT_324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1 _SRT-A | 5 | EKPC_P1-2_COOP-DEN161_SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | EXT_324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1 _SRT-A | 6 | EKPC_P1-2_COOP 161 TIE_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.18 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | EXT_324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1 _SRT-A | 7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.17 | 324002 | 1BROWN 3 | 24 | 1.0517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | EXT_324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1 _SRT-A | 8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A |  | 3 | 0 | 0 | 0.12 | 325118 | 1RHUDES INV | 34.5 | 1.0762 | 0.25 | 325117 | 1RHUDES COL | 34.5 | 1.0706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | EXT_324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1 _SRT-A | 9 | EKPC_P1-2_LIBJ-GAS161_SRT-A |  | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.41 | 324002 | 1BROWN 3 | 24 | 1.0518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | EXT_324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1 _SRT-A | 10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | Ovl | 3 | 0 | 0 | 0.07 | 325118 | 1RHUDES INV | 34.5 | 1.0743 | 0.15 | 325117 | 1RHUDES COL | 34.5 | 1.0688 | 10685.1 | 1 | 103.4 | 0 | 0 | 0 | 0 | 0
24 | EXT_324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1 _SRT-A | 11 | EKPC_P1-2_GRE-SUMSH161_SRT-A |  | 3 | 0 | 0 | 0.39 | 325118 | 1RHUDES INV | 34.5 | 1.075 | 0.82 | 325117 | 1RHUDES COL | 34.5 | 1.0695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | EXT_324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1 _SRT-A | 12 | EKPC_P1-2_BARR-SUMSH161_SRT-A |  | 3 | 0 | 0 | 0.07 | 325118 | 1RHUDES INV | 34.5 | 1.0766 | 0.15 | 325117 | 1RHUDES COL | 34.5 | 1.071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | EXT_324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1 _SRT-A | 13 | EKPC_P1-2_BULL-SUMSH161_SRT-A |  | 2 | 0 | 0 | 0.18 | 325118 | 1RHUDES INV | 34.5 | 1.0772 | 0.38 | 325117 | 1RHUDES COL | 34.5 | 1.0715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | EXT_324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1 _SRT-A | 14 | EKPC_P1-2_SSHAD 161 TIE_SRT-A |  | 1 | 0 | 0 | 0.11 | 542969 | STILWEL5 | 161 | 1.0122 | 0.85 | 361788 | 5SUM SHAD TP | 161 | 1.025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | EXT_324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1 _SRT-A | 15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.21 | 325130 | 1RHUDES GEN | 0.6 | 1.1033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | EXT_324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1 _SRT-A | 16 | EKPC_P1-3_MAR 161/138_SRT-A |  | 3 | 0 | 0 | 0.09 | 342000 | 5GAS | 161 | 1 | 0.3 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | EXT_324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1 _SRT-A | 17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.11 | 325130 | 1RHUDES GEN | 0.6 | 1.1062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | EXT_324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1 _SRT-A | 18 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.18 | 340576 | WILSON | 24 | 1.0012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | EXT_324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1 _SRT-A | 19 | EXT_324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1 _SRT-A |  | 1 | 0 | 0 | 0.35 | 342577 | 4FAWKES EK | 138 | 1.0037 | 0.57 | 324248 | 4FAWKES KU | 138 | 1.0036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | EXT_324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1 _SRT-A | 20 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.19 | 324002 | 1BROWN 3 | 24 | 1.0518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | EXT_324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1 _SRT-A | 21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.1 | 325130 | 1RHUDES GEN | 0.6 | 1.1056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | EXT_324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1 _SRT-A | 22 | EXT_324217 4BROWN PLANT 138 324219 4BROWN T1 138 1 _SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | EXT_324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1 _SRT-A | 23 | EXT_324217 4BROWN PLANT 138 324220 4BROWN T2 138 1 _SRT-A |  | 1 | 0 | 0 | 0.11 | 542969 | STILWEL5 | 161 | 1.0122 | 0.22 | 324016 | 1DIX DAM 3 | 13.2 | 1.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | EXT_324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1 _SRT-A | 25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A |  | 4 | 0 | 0 | 0.09 | 340576 | WILSON | 24 | 1.0033 | 0.67 | 340576 | WILSON | 24 | 1.0033 | 0 | 0 | 93.6 | 0 | 0 | 0 | 0 | 0
24 | EXT_324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1 _SRT-A | 26 | EXT_B-138-111_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.09 | 324002 | 1BROWN 3 | 24 | 1.052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | EXT_324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1 _SRT-A | 27 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A_Dup1 |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.19 | 324002 | 1BROWN 3 | 24 | 1.0518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | EXT_324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1 _SRT-A | 28 | EXT_BB-1133_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.11 | 325130 | 1RHUDES GEN | 0.6 | 1.1059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | EXT_324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1 _SRT-A | 29 | EXT_MERE SWS_SRT-A |  | 2 | 0 | 0 | 0.32 | 325118 | 1RHUDES INV | 34.5 | 1.0783 | 0.7 | 325117 | 1RHUDES COL | 34.5 | 1.0725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | EXT_324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1 _SRT-A | 30 | EXT_B-138-115_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.3 | 340576 | WILSON | 24 | 1.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | EXT_324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1 _SRT-A | 31 | EXT_B-138-120_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | EXT_324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1 _SRT-A | 32 | EXT_B-138-121_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | EXT_324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1 _SRT-A | 33 | EXT_324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1 _SRT-A |  | 2 | 0 | 0 | 0.09 | 542969 | STILWEL5 | 161 | 1.0122 | 0.18 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | EXT_324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1 _SRT-A | 34 | EXT_326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1 _SRT-A |  | 2 | 0 | 0 | 0.17 | 325118 | 1RHUDES INV | 34.5 | 1.0771 | 0.36 | 325117 | 1RHUDES COL | 34.5 | 1.0714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | EXT_324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1 _SRT-A | 35 | EXT_B-69-18_SRT-A |  | 3 | 0 | 0 | 0.09 | 342000 | 5GAS | 161 | 1 | 0.26 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | EXT_324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1 _SRT-A | 36 | EXT_B-69-19_SRT-A |  | 4 | 0 | 0 | 0.33 | 325118 | 1RHUDES INV | 34.5 | 1.0749 | 0.7 | 325117 | 1RHUDES COL | 34.5 | 1.0694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | EXT_324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1 _SRT-A | 37 | EXT_BB-1066_SRT-A |  | 2 | 0 | 0 | 0.1 | 542969 | STILWEL5 | 161 | 1.0122 | 0.19 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 1 | EKPC_P1-2_MAR-KU LEB138 |  | 3 | 0 | 0 | 0.1 | 342000 | 5GAS | 161 | 1 | 0.31 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0113 | 0 | 0 | 93.8 | 0 | 0 | 0 | 0 | 0
25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 2 | EKPC_P1-2_COOP-ELIHU161_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A |  | 4 | 0 | 0 | 0.05 | 942410 | AE2-254 TAP | 69 | 1.0132 | 0.56 | 324002 | 1BROWN 3 | 24 | 1.0532 | 0 | 0 | 93.1 | 0 | 0 | 0 | 0 | 0
25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 4 | EKPC_P1-2_COOP-LAUREL161_SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 5 | EKPC_P1-2_COOP-DEN161_SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 6 | EKPC_P1-2_COOP 161 TIE_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.18 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.19 | 324002 | 1BROWN 3 | 24 | 1.0526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.31 | 324002 | 1BROWN 3 | 24 | 1.0525 | 0 | 0 | 91 | 0 | 0 | 0 | 0 | 0
25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 9 | EKPC_P1-2_LIBJ-GAS161_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.49 | 324002 | 1BROWN 3 | 24 | 1.053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | Ovl | 3 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.17 | 324002 | 1BROWN 3 | 24 | 1.0522 | 10363.8 | 1 | 101.8 | 0 | 0 | 0 | 0 | 0
25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 11 | EKPC_P1-2_GRE-SUMSH161_SRT-A |  | 3 | 0 | 0 | 0.04 | 542969 | STILWEL5 | 161 | 1.0122 | 0.23 | 324002 | 1BROWN 3 | 24 | 1.0525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 12 | EKPC_P1-2_BARR-SUMSH161_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.1 | 340576 | WILSON | 24 | 1.0032 | 0 | 0 | 94.4 | 0 | 0 | 0 | 0 | 0
25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 13 | EKPC_P1-2_BULL-SUMSH161_SRT-A |  | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.23 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 14 | EKPC_P1-2_SSHAD 161 TIE_SRT-A |  | 1 | 0 | 0 | 0.11 | 542969 | STILWEL5 | 161 | 1.0122 | 0.86 | 361788 | 5SUM SHAD TP | 161 | 1.0236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.3 | 324002 | 1BROWN 3 | 24 | 1.0525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 16 | EKPC_P1-3_MAR 161/138_SRT-A |  | 3 | 0 | 0 | 0.1 | 342000 | 5GAS | 161 | 1 | 0.31 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0113 | 0 | 0 | 93.8 | 0 | 0 | 0 | 0 | 0
25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A | Ovl Vlt | 5 | 0 | 0 | 0.03 | 342403 | 2UPTON T | 69 | 0.98 | 0.08 | 324002 | 1BROWN 3 | 24 | 1.0518 | 11817 | 1 | 108.7 | 0.1 | 2 | 0 | 0 | 0
25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 18 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A |  | 2 | 0 | 0 | 0.12 | 316293 | AC1-161 COL2 | 34.5 | 1.0794 | 0.27 | 364001 | 1BR FERRY N1 | 22 | 1.0415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 19 | EXT_324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1 _SRT-A |  | 1 | 0 | 0 | 0.27 | 342577 | 4FAWKES EK | 138 | 1.0035 | 0.41 | 342577 | 4FAWKES EK | 138 | 1.0035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 20 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A |  | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.18 | 324002 | 1BROWN 3 | 24 | 1.0519 | 0 | 0 | 90.9 | 0 | 0 | 0 | 0 | 0
25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A | Ovl Vlt | 5 | 0 | 0 | 0.03 | 342403 | 2UPTON T | 69 | 0.9778 | 0.09 | 324002 | 1BROWN 3 | 24 | 1.0518 | 13171.4 | 1 | 114.8 | 0.1 | 3 | 0 | 0 | 0
25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 22 | EXT_324217 4BROWN PLANT 138 324219 4BROWN T1 138 1 _SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 23 | EXT_324217 4BROWN PLANT 138 324220 4BROWN T2 138 1 _SRT-A |  | 1 | 0 | 0 | 0.11 | 542969 | STILWEL5 | 161 | 1.0122 | 0.25 | 324015 | 1DIX DAM 2 | 13.2 | 1.0089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 24 | EXT_324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1 _SRT-A |  | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.18 | 340576 | WILSON | 24 | 1.0031 | 0 | 0 | 93.6 | 0 | 0 | 0 | 0 | 0
25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 26 | EXT_B-138-111_SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 91.2 | 0 | 0 | 0 | 0 | 0
25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 27 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A_Dup1 |  | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.18 | 324002 | 1BROWN 3 | 24 | 1.0519 | 0 | 0 | 90.9 | 0 | 0 | 0 | 0 | 0
25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 28 | EXT_BB-1133_SRT-A | Ovl Vlt | 5 | 0 | 0 | 0.03 | 342403 | 2UPTON T | 69 | 0.9801 | 0.08 | 324002 | 1BROWN 3 | 24 | 1.0517 | 11811.5 | 1 | 108.7 | 0.1 | 2 | 0 | 0 | 0
25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 29 | EXT_MERE SWS_SRT-A | Vlt | 4 | 0 | 0 | 0.06 | 341161 | 2BONNIV EK | 69 | 0.9681 | 0.5 | 324002 | 1BROWN 3 | 24 | 1.0526 | 0 | 0 | 0 | 0.2 | 1 | 0 | 0 | 0
25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 30 | EXT_B-138-115_SRT-A |  | 6 | 0 | 0 | 0.09 | 325118 | 1RHUDES INV | 34.5 | 1.0708 | 0.33 | 325130 | 1RHUDES GEN | 0.6 | 1.096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 31 | EXT_B-138-120_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 32 | EXT_B-138-121_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 33 | EXT_324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1 _SRT-A |  | 2 | 0 | 0 | 0.09 | 542969 | STILWEL5 | 161 | 1.0122 | 0.19 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 34 | EXT_326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1 _SRT-A |  | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.23 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 35 | EXT_B-69-18_SRT-A | Ovl Vlt | 5 | 0 | 0 | 0.04 | 342403 | 2UPTON T | 69 | 0.9782 | 0.12 | 324002 | 1BROWN 3 | 24 | 1.0521 | 12783.1 | 1 | 113.1 | 0.1 | 3 | 0 | 0 | 0
25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 36 | EXT_B-69-19_SRT-A |  | 5 | 0 | 0 | 0.09 | 325118 | 1RHUDES INV | 34.5 | 1.0667 | 0.49 | 325130 | 1RHUDES GEN | 0.6 | 1.0905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | 37 | EXT_BB-1066_SRT-A |  | 2 | 0 | 0 | 0.1 | 542969 | STILWEL5 | 161 | 1.0122 | 0.2 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | EXT_B-138-111_SRT-A | 1 | EKPC_P1-2_MAR-KU LEB138 |  | 3 | 0 | 0 | 0.09 | 342000 | 5GAS | 161 | 1 | 0.29 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | EXT_B-138-111_SRT-A | 2 | EKPC_P1-2_COOP-ELIHU161_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 93.5 | 0 | 0 | 0 | 0 | 0
26 | EXT_B-138-111_SRT-A | 3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A |  | 5 | 0 | 0 | 0.02 | 158981 | ARMOW_BUS2 | 34.5 | 1.025 | 0.07 | 340576 | WILSON | 24 | 1.0039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | EXT_B-138-111_SRT-A | 4 | EKPC_P1-2_COOP-LAUREL161_SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | EXT_B-138-111_SRT-A | 5 | EKPC_P1-2_COOP-DEN161_SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | EXT_B-138-111_SRT-A | 6 | EKPC_P1-2_COOP 161 TIE_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.19 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | EXT_B-138-111_SRT-A | 7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.14 | 324002 | 1BROWN 3 | 24 | 1.0524 | 0 | 0 | 94.8 | 0 | 0 | 0 | 0 | 0
26 | EXT_B-138-111_SRT-A | 8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A |  | 3 | 0 | 0 | 0.2 | 325118 | 1RHUDES INV | 34.5 | 1.0757 | 0.42 | 325117 | 1RHUDES COL | 34.5 | 1.0701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | EXT_B-138-111_SRT-A | 9 | EKPC_P1-2_LIBJ-GAS161_SRT-A |  | 3 | 0 | 0 | 0.18 | 325118 | 1RHUDES INV | 34.5 | 1.0757 | 0.37 | 325117 | 1RHUDES COL | 34.5 | 1.0702 | 0 | 0 | 98.6 | 0 | 0 | 0 | 0 | 0
26 | EXT_B-138-111_SRT-A | 10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | Ovl | 4 | 0 | 0 | 0.04 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 12788.7 | 1 | 113.1 | 0 | 0 | 0 | 0 | 0
26 | EXT_B-138-111_SRT-A | 11 | EKPC_P1-2_GRE-SUMSH161_SRT-A |  | 3 | 0 | 0 | 0.42 | 325118 | 1RHUDES INV | 34.5 | 1.0743 | 0.89 | 325117 | 1RHUDES COL | 34.5 | 1.0688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | EXT_B-138-111_SRT-A | 12 | EKPC_P1-2_BARR-SUMSH161_SRT-A |  | 3 | 0 | 0 | 0.07 | 325118 | 1RHUDES INV | 34.5 | 1.0761 | 0.15 | 325117 | 1RHUDES COL | 34.5 | 1.0705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | EXT_B-138-111_SRT-A | 13 | EKPC_P1-2_BULL-SUMSH161_SRT-A |  | 2 | 0 | 0 | 0.18 | 325118 | 1RHUDES INV | 34.5 | 1.0767 | 0.38 | 325117 | 1RHUDES COL | 34.5 | 1.0711 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | EXT_B-138-111_SRT-A | 14 | EKPC_P1-2_SSHAD 161 TIE_SRT-A |  | 1 | 0 | 0 | 0.11 | 542969 | STILWEL5 | 161 | 1.0122 | 0.84 | 361788 | 5SUM SHAD TP | 161 | 1.0255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | EXT_B-138-111_SRT-A | 15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.23 | 325130 | 1RHUDES GEN | 0.6 | 1.1027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | EXT_B-138-111_SRT-A | 16 | EKPC_P1-3_MAR 161/138_SRT-A |  | 3 | 0 | 0 | 0.09 | 342000 | 5GAS | 161 | 1 | 0.29 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | EXT_B-138-111_SRT-A | 17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.14 | 325130 | 1RHUDES GEN | 0.6 | 1.106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | EXT_B-138-111_SRT-A | 18 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.17 | 340576 | WILSON | 24 | 1.0012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | EXT_B-138-111_SRT-A | 19 | EXT_324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1 _SRT-A |  | 1 | 0 | 0 | 0.33 | 342577 | 4FAWKES EK | 138 | 1.0036 | 0.52 | 324248 | 4FAWKES KU | 138 | 1.0035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | EXT_B-138-111_SRT-A | 21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A |  | 3 | 0 | 0 | 0.06 | 342000 | 5GAS | 161 | 1 | 0.2 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | EXT_B-138-111_SRT-A | 22 | EXT_324217 4BROWN PLANT 138 324219 4BROWN T1 138 1 _SRT-A |  | 1 | 0 | 0 | 0.11 | 542969 | STILWEL5 | 161 | 1.0122 | 0.65 | 324217 | 4BROWN PLANT | 138 | 1.0139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | EXT_B-138-111_SRT-A | 23 | EXT_324217 4BROWN PLANT 138 324220 4BROWN T2 138 1 _SRT-A |  | 1 | 0 | 0 | 0.11 | 542969 | STILWEL5 | 161 | 1.0122 | 0.23 | 324217 | 4BROWN PLANT | 138 | 1.0141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | EXT_B-138-111_SRT-A | 25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A |  | 4 | 0 | 0 | 0.09 | 340576 | WILSON | 24 | 1.0033 | 0.66 | 340576 | WILSON | 24 | 1.0033 | 0 | 0 | 91.2 | 0 | 0 | 0 | 0 | 0
26 | EXT_B-138-111_SRT-A | 28 | EXT_BB-1133_SRT-A |  | 3 | 0 | 0 | 0.06 | 342000 | 5GAS | 161 | 1 | 0.2 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | EXT_B-138-111_SRT-A | 29 | EXT_MERE SWS_SRT-A |  | 2 | 0 | 0 | 0.38 | 325118 | 1RHUDES INV | 34.5 | 1.0784 | 0.81 | 325117 | 1RHUDES COL | 34.5 | 1.0726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | EXT_B-138-111_SRT-A | 30 | EXT_B-138-115_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.31 | 340576 | WILSON | 24 | 1.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | EXT_B-138-111_SRT-A | 31 | EXT_B-138-120_SRT-A |  | 1 | 0 | 0 | 0.11 | 542969 | STILWEL5 | 161 | 1.0122 | 0.65 | 324217 | 4BROWN PLANT | 138 | 1.0139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | EXT_B-138-111_SRT-A | 32 | EXT_B-138-121_SRT-A |  | 2 | 0 | 0 | 0.08 | 325956 | 4BROWN N 2 | 138 | 1.0145 | 0.74 | 324002 | 1BROWN 3 | 24 | 1.0522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | EXT_B-138-111_SRT-A | 33 | EXT_324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1 _SRT-A |  | 2 | 0 | 0 | 0.09 | 542969 | STILWEL5 | 161 | 1.0122 | 0.18 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | EXT_B-138-111_SRT-A | 34 | EXT_326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1 _SRT-A |  | 2 | 0 | 0 | 0.17 | 325118 | 1RHUDES INV | 34.5 | 1.0766 | 0.36 | 325117 | 1RHUDES COL | 34.5 | 1.071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | EXT_B-138-111_SRT-A | 35 | EXT_B-69-18_SRT-A |  | 3 | 0 | 0 | 0.09 | 342000 | 5GAS | 161 | 1 | 0.25 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | EXT_B-138-111_SRT-A | 36 | EXT_B-69-19_SRT-A |  | 4 | 0 | 0 | 0.33 | 325118 | 1RHUDES INV | 34.5 | 1.0748 | 0.7 | 325117 | 1RHUDES COL | 34.5 | 1.0693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | EXT_B-138-111_SRT-A | 37 | EXT_BB-1066_SRT-A |  | 2 | 0 | 0 | 0.1 | 542969 | STILWEL5 | 161 | 1.0122 | 0.19 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A_27 | 1 | EKPC_P1-2_MAR-KU LEB138 |  | 3 | 0 | 0 | 0.1 | 342000 | 5GAS | 161 | 1 | 0.31 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A_27 | 2 | EKPC_P1-2_COOP-ELIHU161_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A_27 | 3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A |  | 5 | 0 | 0 | 0.02 | 158981 | ARMOW_BUS2 | 34.5 | 1.025 | 0.07 | 340576 | WILSON | 24 | 1.0039 | 0 | 0 | 97.8 | 0 | 0 | 0 | 0 | 0
27 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A_27 | 4 | EKPC_P1-2_COOP-LAUREL161_SRT-A |  | 3 | 0 | 0 | 0.15 | 324446 | 2BOND | 69 | 1.0164 | 0.55 | 324002 | 1BROWN 3 | 24 | 1.0511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A_27 | 5 | EKPC_P1-2_COOP-DEN161_SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A_27 | 6 | EKPC_P1-2_COOP 161 TIE_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.19 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A_27 | 7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.14 | 324002 | 1BROWN 3 | 24 | 1.0516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A_27 | 8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A |  | 3 | 0 | 0 | 0.2 | 325118 | 1RHUDES INV | 34.5 | 1.0758 | 0.42 | 325117 | 1RHUDES COL | 34.5 | 1.0702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A_27 | 9 | EKPC_P1-2_LIBJ-GAS161_SRT-A |  | 3 | 0 | 0 | 0.2 | 325118 | 1RHUDES INV | 34.5 | 1.0755 | 0.43 | 325117 | 1RHUDES COL | 34.5 | 1.07 | 0 | 0 | 98 | 0 | 0 | 0 | 0 | 0
27 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A_27 | 10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | Ovl | 4 | 0 | 0 | 0.04 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 12762.8 | 1 | 113 | 0 | 0 | 0 | 0 | 0
27 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A_27 | 11 | EKPC_P1-2_GRE-SUMSH161_SRT-A |  | 3 | 0 | 0 | 0.42 | 325118 | 1RHUDES INV | 34.5 | 1.0743 | 0.89 | 325117 | 1RHUDES COL | 34.5 | 1.0689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A_27 | 12 | EKPC_P1-2_BARR-SUMSH161_SRT-A |  | 3 | 0 | 0 | 0.07 | 325118 | 1RHUDES INV | 34.5 | 1.0761 | 0.15 | 325117 | 1RHUDES COL | 34.5 | 1.0705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A_27 | 13 | EKPC_P1-2_BULL-SUMSH161_SRT-A |  | 2 | 0 | 0 | 0.18 | 325118 | 1RHUDES INV | 34.5 | 1.0767 | 0.38 | 325117 | 1RHUDES COL | 34.5 | 1.0711 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A_27 | 14 | EKPC_P1-2_SSHAD 161 TIE_SRT-A |  | 1 | 0 | 0 | 0.11 | 542969 | STILWEL5 | 161 | 1.0122 | 0.84 | 361788 | 5SUM SHAD TP | 161 | 1.0255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A_27 | 15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.23 | 325130 | 1RHUDES GEN | 0.6 | 1.1027 | 0 | 0 | 93.4 | 0 | 0 | 0 | 0 | 0
27 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A_27 | 16 | EKPC_P1-3_MAR 161/138_SRT-A |  | 3 | 0 | 0 | 0.1 | 342000 | 5GAS | 161 | 1 | 0.31 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A_27 | 17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.14 | 325130 | 1RHUDES GEN | 0.6 | 1.1061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A_27 | 18 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.17 | 340576 | WILSON | 24 | 1.0012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A_27 | 19 | EXT_324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1 _SRT-A |  | 1 | 0 | 0 | 0.31 | 342577 | 4FAWKES EK | 138 | 1.0037 | 0.49 | 342577 | 4FAWKES EK | 138 | 1.0037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A_27 | 21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.13 | 325130 | 1RHUDES GEN | 0.6 | 1.1055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A_27 | 22 | EXT_324217 4BROWN PLANT 138 324219 4BROWN T1 138 1 _SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A_27 | 23 | EXT_324217 4BROWN PLANT 138 324220 4BROWN T2 138 1 _SRT-A |  | 1 | 0 | 0 | 0.11 | 542969 | STILWEL5 | 161 | 1.0122 | 0.21 | 324015 | 1DIX DAM 2 | 13.2 | 1.0054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A_27 | 24 | EXT_324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1 _SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.28 | 324002 | 1BROWN 3 | 24 | 1.0518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A_27 | 25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A |  | 4 | 0 | 0 | 0.09 | 340576 | WILSON | 24 | 1.0033 | 0.66 | 340576 | WILSON | 24 | 1.0033 | 0 | 0 | 90.9 | 0 | 0 | 0 | 0 | 0
27 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A_27 | 26 | EXT_B-138-111_SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A_27 | 28 | EXT_BB-1133_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.14 | 325130 | 1RHUDES GEN | 0.6 | 1.1058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A_27 | 29 | EXT_MERE SWS_SRT-A |  | 2 | 0 | 0 | 0.37 | 325118 | 1RHUDES INV | 34.5 | 1.0784 | 0.8 | 325117 | 1RHUDES COL | 34.5 | 1.0726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A_27 | 30 | EXT_B-138-115_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.31 | 340576 | WILSON | 24 | 1.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A_27 | 31 | EXT_B-138-120_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A_27 | 32 | EXT_B-138-121_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A_27 | 33 | EXT_324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1 _SRT-A |  | 2 | 0 | 0 | 0.09 | 542969 | STILWEL5 | 161 | 1.0122 | 0.18 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A_27 | 34 | EXT_326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1 _SRT-A |  | 2 | 0 | 0 | 0.17 | 325118 | 1RHUDES INV | 34.5 | 1.0766 | 0.36 | 325117 | 1RHUDES COL | 34.5 | 1.071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A_27 | 35 | EXT_B-69-18_SRT-A |  | 3 | 0 | 0 | 0.09 | 342000 | 5GAS | 161 | 1 | 0.27 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A_27 | 36 | EXT_B-69-19_SRT-A |  | 4 | 0 | 0 | 0.33 | 325118 | 1RHUDES INV | 34.5 | 1.0748 | 0.7 | 325117 | 1RHUDES COL | 34.5 | 1.0694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A_27 | 37 | EXT_BB-1066_SRT-A |  | 2 | 0 | 0 | 0.1 | 542969 | STILWEL5 | 161 | 1.0122 | 0.19 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | EXT_BB-1133_SRT-A | 1 | EKPC_P1-2_MAR-KU LEB138 |  | 3 | 0 | 0 | 0.04 | 542969 | STILWEL5 | 161 | 1.0122 | 0.06 | 324002 | 1BROWN 3 | 24 | 1.0526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | EXT_BB-1133_SRT-A | 2 | EKPC_P1-2_COOP-ELIHU161_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | EXT_BB-1133_SRT-A | 3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A |  | 4 | 0 | 0 | 0.05 | 324830 | 2CAMPBELV EK | 69 | 0.9931 | 0.44 | 324002 | 1BROWN 3 | 24 | 1.0525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | EXT_BB-1133_SRT-A | 4 | EKPC_P1-2_COOP-LAUREL161_SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.08 | 324002 | 1BROWN 3 | 24 | 1.0513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | EXT_BB-1133_SRT-A | 5 | EKPC_P1-2_COOP-DEN161_SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | EXT_BB-1133_SRT-A | 6 | EKPC_P1-2_COOP 161 TIE_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.18 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | EXT_BB-1133_SRT-A | 7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.17 | 324002 | 1BROWN 3 | 24 | 1.0518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | EXT_BB-1133_SRT-A | 8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | EXT_BB-1133_SRT-A | 9 | EKPC_P1-2_LIBJ-GAS161_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.08 | 325117 | 1RHUDES COL | 34.5 | 1.0722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | EXT_BB-1133_SRT-A | 10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A |  | 3 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.06 | 325117 | 1RHUDES COL | 34.5 | 1.0722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | EXT_BB-1133_SRT-A | 11 | EKPC_P1-2_GRE-SUMSH161_SRT-A |  | 3 | 0 | 0 | 0.04 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | EXT_BB-1133_SRT-A | 12 | EKPC_P1-2_BARR-SUMSH161_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.11 | 340576 | WILSON | 24 | 1.0048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | EXT_BB-1133_SRT-A | 13 | EKPC_P1-2_BULL-SUMSH161_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.21 | 340576 | WILSON | 24 | 1.0041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | EXT_BB-1133_SRT-A | 14 | EKPC_P1-2_SSHAD 161 TIE_SRT-A |  | 1 | 0 | 0 | 0.11 | 542969 | STILWEL5 | 161 | 1.0122 | 0.85 | 360334 | 5SUMMER SHAD | 161 | 1.0258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | EXT_BB-1133_SRT-A | 15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.18 | 324002 | 1BROWN 3 | 24 | 1.0518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | EXT_BB-1133_SRT-A | 16 | EKPC_P1-3_MAR 161/138_SRT-A |  | 3 | 0 | 0 | 0.04 | 542969 | STILWEL5 | 161 | 1.0122 | 0.06 | 324002 | 1BROWN 3 | 24 | 1.0526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | EXT_BB-1133_SRT-A | 18 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A |  | 2 | 0 | 0 | 0.09 | 340576 | WILSON | 24 | 1.0016 | 0.78 | 340576 | WILSON | 24 | 1.0016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | EXT_BB-1133_SRT-A | 19 | EXT_324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1 _SRT-A |  | 1 | 0 | 0 | 0.29 | 342577 | 4FAWKES EK | 138 | 1.0036 | 0.45 | 342577 | 4FAWKES EK | 138 | 1.0036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | EXT_BB-1133_SRT-A | 20 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.14 | 324002 | 1BROWN 3 | 24 | 1.0515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | EXT_BB-1133_SRT-A | 22 | EXT_324217 4BROWN PLANT 138 324219 4BROWN T1 138 1 _SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | EXT_BB-1133_SRT-A | 23 | EXT_324217 4BROWN PLANT 138 324220 4BROWN T2 138 1 _SRT-A |  | 1 | 0 | 0 | 0.11 | 542969 | STILWEL5 | 161 | 1.0122 | 0.22 | 324015 | 1DIX DAM 2 | 13.2 | 1.0067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | EXT_BB-1133_SRT-A | 24 | EXT_324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1 _SRT-A |  | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.11 | 364001 | 1BR FERRY N1 | 22 | 1.0423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | EXT_BB-1133_SRT-A | 25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | Ovl Vlt | 4 | 0 | 0 | 0.09 | 340576 | WILSON | 24 | 1.0037 | 0.57 | 340576 | WILSON | 24 | 1.0037 | 12138.3 | 1 | 110.2 | 0.7 | 5 | 0 | 0 | 0
28 | EXT_BB-1133_SRT-A | 26 | EXT_B-138-111_SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | EXT_BB-1133_SRT-A | 27 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A_Dup1 |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.14 | 324002 | 1BROWN 3 | 24 | 1.0515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | EXT_BB-1133_SRT-A | 29 | EXT_MERE SWS_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.07 | 324002 | 1BROWN 3 | 24 | 1.0519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | EXT_BB-1133_SRT-A | 30 | EXT_B-138-115_SRT-A | Vlt | 4 | 0 | 0 | 0.09 | 341161 | 2BONNIV EK | 69 | 0.972 | 0.65 | 340576 | WILSON | 24 | 1.0014 | 0 | 0 | 94.8 | 0 | 2 | 0 | 0 | 0
28 | EXT_BB-1133_SRT-A | 31 | EXT_B-138-120_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | EXT_BB-1133_SRT-A | 32 | EXT_B-138-121_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | EXT_BB-1133_SRT-A | 33 | EXT_324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1 _SRT-A |  | 2 | 0 | 0 | 0.09 | 542969 | STILWEL5 | 161 | 1.0122 | 0.17 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | EXT_BB-1133_SRT-A | 34 | EXT_326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1 _SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.19 | 340576 | WILSON | 24 | 1.0041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | EXT_BB-1133_SRT-A | 35 | EXT_B-69-18_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.23 | 324002 | 1BROWN 3 | 24 | 1.0522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | EXT_BB-1133_SRT-A | 36 | EXT_B-69-19_SRT-A |  | 4 | 0 | 0 | 0.34 | 325118 | 1RHUDES INV | 34.5 | 1.0746 | 0.73 | 325117 | 1RHUDES COL | 34.5 | 1.0692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | EXT_BB-1133_SRT-A | 37 | EXT_BB-1066_SRT-A |  | 2 | 0 | 0 | 0.1 | 542969 | STILWEL5 | 161 | 1.0122 | 0.17 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | EXT_MERE SWS_SRT-A | 1 | EKPC_P1-2_MAR-KU LEB138 |  | 3 | 0 | 0 | 0.1 | 342000 | 5GAS | 161 | 1 | 0.33 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | EXT_MERE SWS_SRT-A | 2 | EKPC_P1-2_COOP-ELIHU161_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | EXT_MERE SWS_SRT-A | 3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A |  | 5 | 0 | 0 | 0.02 | 158981 | ARMOW_BUS2 | 34.5 | 1.025 | 0.11 | 324004 | 1BROWN 6 | 18 | 1.0227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | EXT_MERE SWS_SRT-A | 4 | EKPC_P1-2_COOP-LAUREL161_SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | EXT_MERE SWS_SRT-A | 5 | EKPC_P1-2_COOP-DEN161_SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | EXT_MERE SWS_SRT-A | 6 | EKPC_P1-2_COOP 161 TIE_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.19 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | EXT_MERE SWS_SRT-A | 7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.17 | 324002 | 1BROWN 3 | 24 | 1.0523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | EXT_MERE SWS_SRT-A | 8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.29 | 324002 | 1BROWN 3 | 24 | 1.0521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | EXT_MERE SWS_SRT-A | 9 | EKPC_P1-2_LIBJ-GAS161_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.44 | 324002 | 1BROWN 3 | 24 | 1.0528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | EXT_MERE SWS_SRT-A | 10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A |  | 3 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.18 | 324002 | 1BROWN 3 | 24 | 1.0519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | EXT_MERE SWS_SRT-A | 11 | EKPC_P1-2_GRE-SUMSH161_SRT-A |  | 2 | 0 | 0 | 0.06 | 542969 | STILWEL5 | 161 | 1.0122 | 0.3 | 324002 | 1BROWN 3 | 24 | 1.0526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | EXT_MERE SWS_SRT-A | 12 | EKPC_P1-2_BARR-SUMSH161_SRT-A |  | 3 | 0 | 0 | 0.04 | 542969 | STILWEL5 | 161 | 1.0122 | 0.12 | 340576 | WILSON | 24 | 1.0065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | EXT_MERE SWS_SRT-A | 13 | EKPC_P1-2_BULL-SUMSH161_SRT-A |  | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.22 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | EXT_MERE SWS_SRT-A | 14 | EKPC_P1-2_SSHAD 161 TIE_SRT-A |  | 1 | 0 | 0 | 0.11 | 542969 | STILWEL5 | 161 | 1.0122 | 0.86 | 361788 | 5SUM SHAD TP | 161 | 1.0251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | EXT_MERE SWS_SRT-A | 15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.28 | 324002 | 1BROWN 3 | 24 | 1.0521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | EXT_MERE SWS_SRT-A | 16 | EKPC_P1-3_MAR 161/138_SRT-A |  | 3 | 0 | 0 | 0.1 | 342000 | 5GAS | 161 | 1 | 0.33 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | EXT_MERE SWS_SRT-A | 17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.14 | 324002 | 1BROWN 3 | 24 | 1.0519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | EXT_MERE SWS_SRT-A | 18 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.18 | 340576 | WILSON | 24 | 1.0054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | EXT_MERE SWS_SRT-A | 19 | EXT_324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1 _SRT-A |  | 1 | 0 | 0 | 0.29 | 342577 | 4FAWKES EK | 138 | 1.0036 | 0.46 | 340576 | WILSON | 24 | 1.006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | EXT_MERE SWS_SRT-A | 20 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.13 | 324002 | 1BROWN 3 | 24 | 1.0515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | EXT_MERE SWS_SRT-A | 21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A |  | 3 | 0 | 0 | 0.07 | 342000 | 5GAS | 161 | 1 | 0.24 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | EXT_MERE SWS_SRT-A | 22 | EXT_324217 4BROWN PLANT 138 324219 4BROWN T1 138 1 _SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | EXT_MERE SWS_SRT-A | 23 | EXT_324217 4BROWN PLANT 138 324220 4BROWN T2 138 1 _SRT-A |  | 1 | 0 | 0 | 0.11 | 542969 | STILWEL5 | 161 | 1.0122 | 0.25 | 324015 | 1DIX DAM 2 | 13.2 | 1.0097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | EXT_MERE SWS_SRT-A | 24 | EXT_324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1 _SRT-A |  | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.29 | 340576 | WILSON | 24 | 1.0064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | EXT_MERE SWS_SRT-A | 25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | Vlt | 5 | 0 | 0 | 0.03 | 360448 | 5WOLF CRK HP | 161 | 1.0311 | 0.15 | 340576 | WILSON | 24 | 1.0034 | 0 | 0 | 0 | 0.4 | 2 | 0 | 0 | 0
29 | EXT_MERE SWS_SRT-A | 26 | EXT_B-138-111_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.12 | 324002 | 1BROWN 3 | 24 | 1.0522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | EXT_MERE SWS_SRT-A | 27 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A_Dup1 |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.13 | 324002 | 1BROWN 3 | 24 | 1.0515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | EXT_MERE SWS_SRT-A | 28 | EXT_BB-1133_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.15 | 324002 | 1BROWN 3 | 24 | 1.0519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | EXT_MERE SWS_SRT-A | 30 | EXT_B-138-115_SRT-A | Vlt | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.25 | 340576 | WILSON | 24 | 1.0021 | 0 | 0 | 0 | 0.4 | 2 | 0 | 0 | 0
29 | EXT_MERE SWS_SRT-A | 31 | EXT_B-138-120_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | EXT_MERE SWS_SRT-A | 32 | EXT_B-138-121_SRT-A |  | 3 | 0 | 0 | 0.04 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | EXT_MERE SWS_SRT-A | 33 | EXT_324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1 _SRT-A |  | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.17 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | EXT_MERE SWS_SRT-A | 34 | EXT_326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1 _SRT-A |  | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.22 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | EXT_MERE SWS_SRT-A | 35 | EXT_B-69-18_SRT-A |  | 6 | 0 | 0 | 0.22 | 325118 | 1RHUDES INV | 34.5 | 1.0763 | 0.47 | 325117 | 1RHUDES COL | 34.5 | 1.0708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | EXT_MERE SWS_SRT-A | 36 | EXT_B-69-19_SRT-A |  | 3 | 0 | 0 | 0.07 | 342307 | 2STEPHENSBRG | 69 | 0.9959 | 0.57 | 340576 | WILSON | 24 | 1.0055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | EXT_MERE SWS_SRT-A | 37 | EXT_BB-1066_SRT-A |  | 2 | 0 | 0 | 0.1 | 542969 | STILWEL5 | 161 | 1.0122 | 0.18 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | EXT_B-138-115_SRT-A | 1 | EKPC_P1-2_MAR-KU LEB138 | Ovl | 3 | 0 | 0 | 0.09 | 342000 | 5GAS | 161 | 1 | 0.3 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0112 | 10756.9 | 1 | 103.7 | 0 | 0 | 0 | 0 | 0
30 | EXT_B-138-115_SRT-A | 2 | EKPC_P1-2_COOP-ELIHU161_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | EXT_B-138-115_SRT-A | 3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A |  | 5 | 0 | 0 | 0.02 | 158981 | ARMOW_BUS2 | 34.5 | 1.025 | 0.09 | 324004 | 1BROWN 6 | 18 | 1.0237 | 0 | 0 | 92.5 | 0 | 0 | 0 | 0 | 0
30 | EXT_B-138-115_SRT-A | 4 | EKPC_P1-2_COOP-LAUREL161_SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 243764 | 05BSG1 | 22 | 0.9924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | EXT_B-138-115_SRT-A | 5 | EKPC_P1-2_COOP-DEN161_SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | EXT_B-138-115_SRT-A | 6 | EKPC_P1-2_COOP 161 TIE_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.18 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | EXT_B-138-115_SRT-A | 7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.19 | 324002 | 1BROWN 3 | 24 | 1.0525 | 0 | 0 | 98.9 | 0 | 0 | 0 | 0 | 0
30 | EXT_B-138-115_SRT-A | 8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.33 | 324002 | 1BROWN 3 | 24 | 1.0525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | EXT_B-138-115_SRT-A | 9 | EKPC_P1-2_LIBJ-GAS161_SRT-A | Ovl | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.47 | 324002 | 1BROWN 3 | 24 | 1.0529 | 10689 | 1 | 103.4 | 0 | 0 | 0 | 0 | 0
30 | EXT_B-138-115_SRT-A | 10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | Ovl | 3 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.17 | 324002 | 1BROWN 3 | 24 | 1.0521 | 10218.8 | 1 | 101.1 | 0 | 0 | 0 | 0 | 0
30 | EXT_B-138-115_SRT-A | 11 | EKPC_P1-2_GRE-SUMSH161_SRT-A |  | 3 | 0 | 0 | 0.04 | 542969 | STILWEL5 | 161 | 1.0122 | 0.24 | 324002 | 1BROWN 3 | 24 | 1.0524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | EXT_B-138-115_SRT-A | 12 | EKPC_P1-2_BARR-SUMSH161_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.09 | 324002 | 1BROWN 3 | 24 | 1.0525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | EXT_B-138-115_SRT-A | 13 | EKPC_P1-2_BULL-SUMSH161_SRT-A |  | 2 | 0 | 0 | 0.09 | 542969 | STILWEL5 | 161 | 1.0122 | 0.24 | 324002 | 1BROWN 3 | 24 | 1.0526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | EXT_B-138-115_SRT-A | 14 | EKPC_P1-2_SSHAD 161 TIE_SRT-A |  | 1 | 0 | 0 | 0.11 | 542969 | STILWEL5 | 161 | 1.0122 | 0.85 | 361788 | 5SUM SHAD TP | 161 | 1.0238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | EXT_B-138-115_SRT-A | 15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A |  | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.3 | 324002 | 1BROWN 3 | 24 | 1.0525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | EXT_B-138-115_SRT-A | 16 | EKPC_P1-3_MAR 161/138_SRT-A | Ovl | 3 | 0 | 0 | 0.09 | 342000 | 5GAS | 161 | 1 | 0.3 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0112 | 10757.9 | 1 | 103.7 | 0 | 0 | 0 | 0 | 0
30 | EXT_B-138-115_SRT-A | 17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A | Vlt | 5 | 0 | 0 | 0.03 | 342403 | 2UPTON T | 69 | 0.9878 | 0.09 | 324002 | 1BROWN 3 | 24 | 1.0517 | 0 | 0 | 94.7 | 0 | 2 | 0 | 0 | 0
30 | EXT_B-138-115_SRT-A | 18 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A |  | 3 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.06 | 324004 | 1BROWN 6 | 18 | 1.0206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | EXT_B-138-115_SRT-A | 19 | EXT_324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1 _SRT-A |  | 1 | 0 | 0 | 0.26 | 342577 | 4FAWKES EK | 138 | 1.0035 | 0.4 | 342577 | 4FAWKES EK | 138 | 1.0035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | EXT_B-138-115_SRT-A | 20 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A |  | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.18 | 324002 | 1BROWN 3 | 24 | 1.0519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | EXT_B-138-115_SRT-A | 21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A | Ovl Vlt | 5 | 0 | 0 | 0.03 | 342403 | 2UPTON T | 69 | 0.9858 | 0.1 | 324002 | 1BROWN 3 | 24 | 1.0517 | 10134.6 | 1 | 100.7 | 0 | 2 | 0 | 0 | 0
30 | EXT_B-138-115_SRT-A | 22 | EXT_324217 4BROWN PLANT 138 324219 4BROWN T1 138 1 _SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | EXT_B-138-115_SRT-A | 23 | EXT_324217 4BROWN PLANT 138 324220 4BROWN T2 138 1 _SRT-A |  | 1 | 0 | 0 | 0.11 | 542969 | STILWEL5 | 161 | 1.0122 | 0.25 | 324015 | 1DIX DAM 2 | 13.2 | 1.0083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | EXT_B-138-115_SRT-A | 24 | EXT_324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1 _SRT-A |  | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.17 | 340576 | WILSON | 24 | 1.0019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | EXT_B-138-115_SRT-A | 26 | EXT_B-138-111_SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | EXT_B-138-115_SRT-A | 27 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A_Dup1 |  | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.18 | 324002 | 1BROWN 3 | 24 | 1.0519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | EXT_B-138-115_SRT-A | 28 | EXT_BB-1133_SRT-A | Vlt | 6 | 0 | 0 | 0.02 | 158981 | ARMOW_BUS2 | 34.5 | 1.025 | 0.73 | 325130 | 1RHUDES GEN | 0.6 | 1.1068 | 0 | 0 | 94.7 | 0 | 2 | 0 | 0 | 0
30 | EXT_B-138-115_SRT-A | 29 | EXT_MERE SWS_SRT-A | Vlt | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.46 | 324002 | 1BROWN 3 | 24 | 1.053 | 0 | 0 | 0 | 0.4 | 2 | 0 | 0 | 0
30 | EXT_B-138-115_SRT-A | 31 | EXT_B-138-120_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | EXT_B-138-115_SRT-A | 32 | EXT_B-138-121_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | EXT_B-138-115_SRT-A | 33 | EXT_324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1 _SRT-A |  | 2 | 0 | 0 | 0.09 | 542969 | STILWEL5 | 161 | 1.0122 | 0.19 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | EXT_B-138-115_SRT-A | 34 | EXT_326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1 _SRT-A |  | 2 | 0 | 0 | 0.09 | 542969 | STILWEL5 | 161 | 1.0122 | 0.23 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | EXT_B-138-115_SRT-A | 35 | EXT_B-69-18_SRT-A | Vlt | 5 | 0 | 0 | 0.03 | 342403 | 2UPTON T | 69 | 0.9863 | 0.13 | 324002 | 1BROWN 3 | 24 | 1.0521 | 0 | 0 | 98.9 | 0 | 2 | 0 | 0 | 0
30 | EXT_B-138-115_SRT-A | 36 | EXT_B-69-19_SRT-A |  | 3 | 0 | 0 | 0.08 | 342403 | 2UPTON T | 69 | 0.983 | 0.36 | 340576 | WILSON | 24 | 1.0012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | EXT_B-138-115_SRT-A | 37 | EXT_BB-1066_SRT-A |  | 2 | 0 | 0 | 0.1 | 542969 | STILWEL5 | 161 | 1.0122 | 0.2 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | EXT_B-138-120_SRT-A | 1 | EKPC_P1-2_MAR-KU LEB138 |  | 2 | 0 | 0 | 0.23 | 325118 | 1RHUDES INV | 34.5 | 1.0769 | 0.58 | 324002 | 1BROWN 3 | 24 | 1.0526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | EXT_B-138-120_SRT-A | 2 | EKPC_P1-2_COOP-ELIHU161_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | EXT_B-138-120_SRT-A | 3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A |  | 4 | 0 | 0 | 0.11 | 325118 | 1RHUDES INV | 34.5 | 1.0757 | 0.42 | 324002 | 1BROWN 3 | 24 | 1.0525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | EXT_B-138-120_SRT-A | 4 | EKPC_P1-2_COOP-LAUREL161_SRT-A |  | 3 | 0 | 0 | 0.15 | 324446 | 2BOND | 69 | 1.0164 | 0.55 | 324002 | 1BROWN 3 | 24 | 1.0514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | EXT_B-138-120_SRT-A | 5 | EKPC_P1-2_COOP-DEN161_SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | EXT_B-138-120_SRT-A | 6 | EKPC_P1-2_COOP 161 TIE_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.19 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | EXT_B-138-120_SRT-A | 7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.14 | 324002 | 1BROWN 3 | 24 | 1.0519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | EXT_B-138-120_SRT-A | 8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.26 | 340576 | WILSON | 24 | 1.0039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | EXT_B-138-120_SRT-A | 9 | EKPC_P1-2_LIBJ-GAS161_SRT-A |  | 3 | 0 | 0 | 0.09 | 325118 | 1RHUDES INV | 34.5 | 1.0745 | 0.18 | 325117 | 1RHUDES COL | 34.5 | 1.069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | EXT_B-138-120_SRT-A | 10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A |  | 2 | 0 | 0 | 0.1 | 542969 | STILWEL5 | 161 | 1.0122 | 0.33 | 364622 | 1WOLFCR H5-6 | 13.8 | 1.0096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | EXT_B-138-120_SRT-A | 11 | EKPC_P1-2_GRE-SUMSH161_SRT-A |  | 3 | 0 | 0 | 0.08 | 325118 | 1RHUDES INV | 34.5 | 1.077 | 0.17 | 325117 | 1RHUDES COL | 34.5 | 1.0714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | EXT_B-138-120_SRT-A | 12 | EKPC_P1-2_BARR-SUMSH161_SRT-A |  | 3 | 0 | 0 | 0.06 | 325118 | 1RHUDES INV | 34.5 | 1.0756 | 0.13 | 325117 | 1RHUDES COL | 34.5 | 1.0701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | EXT_B-138-120_SRT-A | 13 | EKPC_P1-2_BULL-SUMSH161_SRT-A |  | 2 | 0 | 0 | 0.18 | 325118 | 1RHUDES INV | 34.5 | 1.0763 | 0.38 | 325117 | 1RHUDES COL | 34.5 | 1.0707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | EXT_B-138-120_SRT-A | 14 | EKPC_P1-2_SSHAD 161 TIE_SRT-A |  | 1 | 0 | 0 | 0.11 | 542969 | STILWEL5 | 161 | 1.0122 | 0.84 | 360334 | 5SUMMER SHAD | 161 | 1.0261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | EXT_B-138-120_SRT-A | 15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.18 | 324002 | 1BROWN 3 | 24 | 1.0518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | EXT_B-138-120_SRT-A | 16 | EKPC_P1-3_MAR 161/138_SRT-A |  | 2 | 0 | 0 | 0.23 | 325118 | 1RHUDES INV | 34.5 | 1.0769 | 0.58 | 324002 | 1BROWN 3 | 24 | 1.0526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | EXT_B-138-120_SRT-A | 17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A |  | 2 | 0 | 0 | 0.34 | 325118 | 1RHUDES INV | 34.5 | 1.078 | 0.72 | 325117 | 1RHUDES COL | 34.5 | 1.0723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | EXT_B-138-120_SRT-A | 18 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.17 | 340576 | WILSON | 24 | 1.0011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | EXT_B-138-120_SRT-A | 19 | EXT_324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1 _SRT-A |  | 1 | 0 | 0 | 0.29 | 342577 | 4FAWKES EK | 138 | 1.0037 | 0.46 | 342577 | 4FAWKES EK | 138 | 1.0037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | EXT_B-138-120_SRT-A | 20 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.14 | 324002 | 1BROWN 3 | 24 | 1.0513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | EXT_B-138-120_SRT-A | 21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A |  | 2 | 0 | 0 | 0.31 | 325118 | 1RHUDES INV | 34.5 | 1.0776 | 0.65 | 325117 | 1RHUDES COL | 34.5 | 1.072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | EXT_B-138-120_SRT-A | 23 | EXT_324217 4BROWN PLANT 138 324220 4BROWN T2 138 1 _SRT-A |  | 4 | 0 | 0 | 0.04 | 542969 | STILWEL5 | 161 | 1.0122 | 0.07 | 253357 | AB1-169 CT2 | 25 | 1.0107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | EXT_B-138-120_SRT-A | 24 | EXT_324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1 _SRT-A |  | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.52 | 340576 | WILSON | 24 | 1.0039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | EXT_B-138-120_SRT-A | 25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.12 | 324002 | 1BROWN 3 | 24 | 1.0523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | EXT_B-138-120_SRT-A | 26 | EXT_B-138-111_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.13 | 324002 | 1BROWN 3 | 24 | 1.052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | EXT_B-138-120_SRT-A | 27 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A_Dup1 |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.14 | 324002 | 1BROWN 3 | 24 | 1.0513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | EXT_B-138-120_SRT-A | 28 | EXT_BB-1133_SRT-A |  | 2 | 0 | 0 | 0.32 | 325118 | 1RHUDES INV | 34.5 | 1.0778 | 0.68 | 325117 | 1RHUDES COL | 34.5 | 1.0721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | EXT_B-138-120_SRT-A | 29 | EXT_MERE SWS_SRT-A |  | 2 | 0 | 0 | 0.43 | 325118 | 1RHUDES INV | 34.5 | 1.0789 | 0.91 | 325117 | 1RHUDES COL | 34.5 | 1.0732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | EXT_B-138-120_SRT-A | 30 | EXT_B-138-115_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.36 | 324002 | 1BROWN 3 | 24 | 1.0522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | EXT_B-138-120_SRT-A | 32 | EXT_B-138-121_SRT-A |  | 4 | 0 | 0 | 0.04 | 542969 | STILWEL5 | 161 | 1.0122 | 0.07 | 253357 | AB1-169 CT2 | 25 | 1.0107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | EXT_B-138-120_SRT-A | 33 | EXT_324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1 _SRT-A |  | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.17 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | EXT_B-138-120_SRT-A | 34 | EXT_326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1 _SRT-A |  | 2 | 0 | 0 | 0.17 | 325118 | 1RHUDES INV | 34.5 | 1.0762 | 0.36 | 325117 | 1RHUDES COL | 34.5 | 1.0706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | EXT_B-138-120_SRT-A | 35 | EXT_B-69-18_SRT-A |  | 3 | 0 | 0 | 0.05 | 325118 | 1RHUDES INV | 34.5 | 1.0774 | 0.24 | 324002 | 1BROWN 3 | 24 | 1.0521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | EXT_B-138-120_SRT-A | 36 | EXT_B-69-19_SRT-A |  | 4 | 0 | 0 | 0.33 | 325118 | 1RHUDES INV | 34.5 | 1.0748 | 0.7 | 325117 | 1RHUDES COL | 34.5 | 1.0693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | EXT_B-138-120_SRT-A | 37 | EXT_BB-1066_SRT-A |  | 2 | 0 | 0 | 0.1 | 542969 | STILWEL5 | 161 | 1.0122 | 0.17 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | EXT_B-138-121_SRT-A | 1 | EKPC_P1-2_MAR-KU LEB138 |  | 3 | 0 | 0 | 0.04 | 542969 | STILWEL5 | 161 | 1.0122 | 0.1 | 325130 | 1RHUDES GEN | 0.6 | 1.1048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | EXT_B-138-121_SRT-A | 2 | EKPC_P1-2_COOP-ELIHU161_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | EXT_B-138-121_SRT-A | 3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A |  | 4 | 0 | 0 | 0.11 | 325118 | 1RHUDES INV | 34.5 | 1.0756 | 0.43 | 324002 | 1BROWN 3 | 24 | 1.0527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | EXT_B-138-121_SRT-A | 4 | EKPC_P1-2_COOP-LAUREL161_SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | EXT_B-138-121_SRT-A | 5 | EKPC_P1-2_COOP-DEN161_SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | EXT_B-138-121_SRT-A | 6 | EKPC_P1-2_COOP 161 TIE_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.19 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | EXT_B-138-121_SRT-A | 7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.15 | 324002 | 1BROWN 3 | 24 | 1.052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | EXT_B-138-121_SRT-A | 8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.26 | 340576 | WILSON | 24 | 1.0039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | EXT_B-138-121_SRT-A | 9 | EKPC_P1-2_LIBJ-GAS161_SRT-A |  | 3 | 0 | 0 | 0.09 | 325118 | 1RHUDES INV | 34.5 | 1.0744 | 0.18 | 325117 | 1RHUDES COL | 34.5 | 1.069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | EXT_B-138-121_SRT-A | 10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A |  | 2 | 0 | 0 | 0.1 | 542969 | STILWEL5 | 161 | 1.0122 | 0.33 | 364622 | 1WOLFCR H5-6 | 13.8 | 1.0096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | EXT_B-138-121_SRT-A | 11 | EKPC_P1-2_GRE-SUMSH161_SRT-A |  | 3 | 0 | 0 | 0.08 | 325118 | 1RHUDES INV | 34.5 | 1.077 | 0.17 | 325117 | 1RHUDES COL | 34.5 | 1.0714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | EXT_B-138-121_SRT-A | 12 | EKPC_P1-2_BARR-SUMSH161_SRT-A |  | 3 | 0 | 0 | 0.06 | 325118 | 1RHUDES INV | 34.5 | 1.0755 | 0.13 | 325117 | 1RHUDES COL | 34.5 | 1.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | EXT_B-138-121_SRT-A | 13 | EKPC_P1-2_BULL-SUMSH161_SRT-A |  | 2 | 0 | 0 | 0.18 | 325118 | 1RHUDES INV | 34.5 | 1.0763 | 0.38 | 325117 | 1RHUDES COL | 34.5 | 1.0707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | EXT_B-138-121_SRT-A | 14 | EKPC_P1-2_SSHAD 161 TIE_SRT-A |  | 1 | 0 | 0 | 0.11 | 542969 | STILWEL5 | 161 | 1.0122 | 0.84 | 360334 | 5SUMMER SHAD | 161 | 1.0261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | EXT_B-138-121_SRT-A | 15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.18 | 324002 | 1BROWN 3 | 24 | 1.052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | EXT_B-138-121_SRT-A | 16 | EKPC_P1-3_MAR 161/138_SRT-A |  | 3 | 0 | 0 | 0.04 | 542969 | STILWEL5 | 161 | 1.0122 | 0.1 | 325130 | 1RHUDES GEN | 0.6 | 1.1048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | EXT_B-138-121_SRT-A | 17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A |  | 2 | 0 | 0 | 0.34 | 325118 | 1RHUDES INV | 34.5 | 1.0779 | 0.72 | 325117 | 1RHUDES COL | 34.5 | 1.0722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | EXT_B-138-121_SRT-A | 18 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.17 | 340576 | WILSON | 24 | 1.0011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | EXT_B-138-121_SRT-A | 19 | EXT_324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1 _SRT-A |  | 1 | 0 | 0 | 0.28 | 342577 | 4FAWKES EK | 138 | 1.0037 | 0.44 | 342577 | 4FAWKES EK | 138 | 1.0037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | EXT_B-138-121_SRT-A | 20 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.16 | 324002 | 1BROWN 3 | 24 | 1.0515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | EXT_B-138-121_SRT-A | 21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A |  | 2 | 0 | 0 | 0.31 | 325118 | 1RHUDES INV | 34.5 | 1.0776 | 0.65 | 325117 | 1RHUDES COL | 34.5 | 1.0719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | EXT_B-138-121_SRT-A | 22 | EXT_324217 4BROWN PLANT 138 324219 4BROWN T1 138 1 _SRT-A |  | 4 | 0 | 0 | 0.04 | 542969 | STILWEL5 | 161 | 1.0122 | 0.07 | 253357 | AB1-169 CT2 | 25 | 1.0107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | EXT_B-138-121_SRT-A | 24 | EXT_324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1 _SRT-A |  | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.52 | 340576 | WILSON | 24 | 1.0039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | EXT_B-138-121_SRT-A | 25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.13 | 324002 | 1BROWN 3 | 24 | 1.0525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | EXT_B-138-121_SRT-A | 26 | EXT_B-138-111_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.12 | 324002 | 1BROWN 3 | 24 | 1.0521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | EXT_B-138-121_SRT-A | 27 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A_Dup1 |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.16 | 324002 | 1BROWN 3 | 24 | 1.0515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | EXT_B-138-121_SRT-A | 28 | EXT_BB-1133_SRT-A |  | 2 | 0 | 0 | 0.32 | 325118 | 1RHUDES INV | 34.5 | 1.0777 | 0.68 | 325117 | 1RHUDES COL | 34.5 | 1.072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | EXT_B-138-121_SRT-A | 29 | EXT_MERE SWS_SRT-A |  | 2 | 0 | 0 | 0.43 | 325118 | 1RHUDES INV | 34.5 | 1.0789 | 0.92 | 325117 | 1RHUDES COL | 34.5 | 1.0732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | EXT_B-138-121_SRT-A | 30 | EXT_B-138-115_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.35 | 324002 | 1BROWN 3 | 24 | 1.0524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | EXT_B-138-121_SRT-A | 31 | EXT_B-138-120_SRT-A |  | 4 | 0 | 0 | 0.04 | 542969 | STILWEL5 | 161 | 1.0122 | 0.07 | 253357 | AB1-169 CT2 | 25 | 1.0107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | EXT_B-138-121_SRT-A | 33 | EXT_324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1 _SRT-A |  | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.17 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | EXT_B-138-121_SRT-A | 34 | EXT_326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1 _SRT-A |  | 2 | 0 | 0 | 0.17 | 325118 | 1RHUDES INV | 34.5 | 1.0762 | 0.36 | 325117 | 1RHUDES COL | 34.5 | 1.0706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | EXT_B-138-121_SRT-A | 35 | EXT_B-69-18_SRT-A |  | 3 | 0 | 0 | 0.05 | 325118 | 1RHUDES INV | 34.5 | 1.0774 | 0.25 | 324002 | 1BROWN 3 | 24 | 1.0523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | EXT_B-138-121_SRT-A | 36 | EXT_B-69-19_SRT-A |  | 4 | 0 | 0 | 0.33 | 325118 | 1RHUDES INV | 34.5 | 1.0747 | 0.7 | 325117 | 1RHUDES COL | 34.5 | 1.0693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | EXT_B-138-121_SRT-A | 37 | EXT_BB-1066_SRT-A |  | 2 | 0 | 0 | 0.1 | 542969 | STILWEL5 | 161 | 1.0122 | 0.17 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | EXT_324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1 _SRT-A | 1 | EKPC_P1-2_MAR-KU LEB138 |  | 2 | 0 | 0 | 0.23 | 325118 | 1RHUDES INV | 34.5 | 1.0778 | 0.56 | 324002 | 1BROWN 3 | 24 | 1.0529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | EXT_324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1 _SRT-A | 2 | EKPC_P1-2_COOP-ELIHU161_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | EXT_324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1 _SRT-A | 3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A |  | 4 | 0 | 0 | 0.11 | 325118 | 1RHUDES INV | 34.5 | 1.0765 | 0.42 | 324002 | 1BROWN 3 | 24 | 1.0527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | EXT_324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1 _SRT-A | 4 | EKPC_P1-2_COOP-LAUREL161_SRT-A |  | 3 | 0 | 0 | 0.15 | 324446 | 2BOND | 69 | 1.0164 | 0.56 | 324002 | 1BROWN 3 | 24 | 1.0517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | EXT_324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1 _SRT-A | 5 | EKPC_P1-2_COOP-DEN161_SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | EXT_324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1 _SRT-A | 6 | EKPC_P1-2_COOP 161 TIE_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.19 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | EXT_324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1 _SRT-A | 7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.15 | 324002 | 1BROWN 3 | 24 | 1.0521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | EXT_324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1 _SRT-A | 8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A |  | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.27 | 340576 | WILSON | 24 | 1.0039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | EXT_324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1 _SRT-A | 9 | EKPC_P1-2_LIBJ-GAS161_SRT-A |  | 3 | 0 | 0 | 0.09 | 325118 | 1RHUDES INV | 34.5 | 1.0754 | 0.18 | 325117 | 1RHUDES COL | 34.5 | 1.0698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | EXT_324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1 _SRT-A | 10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A |  | 3 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.06 | 325117 | 1RHUDES COL | 34.5 | 1.0694 | 0 | 0 | 90.6 | 0 | 0 | 0 | 0 | 0
33 | EXT_324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1 _SRT-A | 11 | EKPC_P1-2_GRE-SUMSH161_SRT-A |  | 3 | 0 | 0 | 0.08 | 325118 | 1RHUDES INV | 34.5 | 1.0779 | 0.17 | 325117 | 1RHUDES COL | 34.5 | 1.0722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | EXT_324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1 _SRT-A | 12 | EKPC_P1-2_BARR-SUMSH161_SRT-A |  | 3 | 0 | 0 | 0.06 | 325118 | 1RHUDES INV | 34.5 | 1.0766 | 0.13 | 325117 | 1RHUDES COL | 34.5 | 1.071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | EXT_324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1 _SRT-A | 13 | EKPC_P1-2_BULL-SUMSH161_SRT-A |  | 2 | 0 | 0 | 0.18 | 325118 | 1RHUDES INV | 34.5 | 1.0772 | 0.38 | 325117 | 1RHUDES COL | 34.5 | 1.0716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | EXT_324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1 _SRT-A | 14 | EKPC_P1-2_SSHAD 161 TIE_SRT-A |  | 1 | 0 | 0 | 0.11 | 542969 | STILWEL5 | 161 | 1.0122 | 0.86 | 360334 | 5SUMMER SHAD | 161 | 1.0264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | EXT_324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1 _SRT-A | 15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A |  | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.19 | 324002 | 1BROWN 3 | 24 | 1.052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | EXT_324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1 _SRT-A | 16 | EKPC_P1-3_MAR 161/138_SRT-A |  | 2 | 0 | 0 | 0.23 | 325118 | 1RHUDES INV | 34.5 | 1.0778 | 0.56 | 324002 | 1BROWN 3 | 24 | 1.0529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | EXT_324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1 _SRT-A | 17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A |  | 2 | 0 | 0 | 0.33 | 325118 | 1RHUDES INV | 34.5 | 1.0788 | 0.71 | 325117 | 1RHUDES COL | 34.5 | 1.0731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | EXT_324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1 _SRT-A | 18 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.17 | 340576 | WILSON | 24 | 1.0011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | EXT_324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1 _SRT-A | 19 | EXT_324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1 _SRT-A |  | 1 | 0 | 0 | 0.29 | 342577 | 4FAWKES EK | 138 | 1.0036 | 0.46 | 342577 | 4FAWKES EK | 138 | 1.0036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | EXT_324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1 _SRT-A | 20 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A |  | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.19 | 340576 | WILSON | 24 | 1.0038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | EXT_324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1 _SRT-A | 21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A |  | 2 | 0 | 0 | 0.31 | 325118 | 1RHUDES INV | 34.5 | 1.0786 | 0.66 | 325117 | 1RHUDES COL | 34.5 | 1.0729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | EXT_324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1 _SRT-A | 22 | EXT_324217 4BROWN PLANT 138 324219 4BROWN T1 138 1 _SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | EXT_324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1 _SRT-A | 23 | EXT_324217 4BROWN PLANT 138 324220 4BROWN T2 138 1 _SRT-A |  | 1 | 0 | 0 | 0.11 | 542969 | STILWEL5 | 161 | 1.0122 | 0.24 | 324015 | 1DIX DAM 2 | 13.2 | 1.0083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | EXT_324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1 _SRT-A | 24 | EXT_324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1 _SRT-A |  | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.55 | 340576 | WILSON | 24 | 1.004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | EXT_324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1 _SRT-A | 25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A |  | 4 | 0 | 0 | 0.04 | 542969 | STILWEL5 | 161 | 1.0122 | 0.08 | 324002 | 1BROWN 3 | 24 | 1.0526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | EXT_324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1 _SRT-A | 26 | EXT_B-138-111_SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 90.3 | 0 | 0 | 0 | 0 | 0
33 | EXT_324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1 _SRT-A | 27 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A_Dup1 |  | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.19 | 340576 | WILSON | 24 | 1.0038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | EXT_324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1 _SRT-A | 28 | EXT_BB-1133_SRT-A |  | 2 | 0 | 0 | 0.33 | 325118 | 1RHUDES INV | 34.5 | 1.0788 | 0.69 | 325117 | 1RHUDES COL | 34.5 | 1.073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | EXT_324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1 _SRT-A | 29 | EXT_MERE SWS_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.14 | 324002 | 1BROWN 3 | 24 | 1.0522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | EXT_324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1 _SRT-A | 30 | EXT_B-138-115_SRT-A |  | 3 | 0 | 0 | 0.06 | 542969 | STILWEL5 | 161 | 1.0122 | 0.4 | 324002 | 1BROWN 3 | 24 | 1.0525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | EXT_324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1 _SRT-A | 31 | EXT_B-138-120_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | EXT_324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1 _SRT-A | 32 | EXT_B-138-121_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | EXT_324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1 _SRT-A | 34 | EXT_326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1 _SRT-A |  | 2 | 0 | 0 | 0.17 | 325118 | 1RHUDES INV | 34.5 | 1.0771 | 0.36 | 325117 | 1RHUDES COL | 34.5 | 1.0715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | EXT_324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1 _SRT-A | 35 | EXT_B-69-18_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.25 | 324002 | 1BROWN 3 | 24 | 1.0523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | EXT_324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1 _SRT-A | 36 | EXT_B-69-19_SRT-A |  | 4 | 0 | 0 | 0.27 | 325118 | 1RHUDES INV | 34.5 | 1.0757 | 0.58 | 325117 | 1RHUDES COL | 34.5 | 1.0702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | EXT_324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1 _SRT-A | 37 | EXT_BB-1066_SRT-A |  | 2 | 0 | 0 | 0.09 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | EXT_326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1 _SRT-A | 1 | EKPC_P1-2_MAR-KU LEB138 |  | 2 | 0 | 0 | 0.21 | 325118 | 1RHUDES INV | 34.5 | 1.0788 | 0.57 | 324002 | 1BROWN 3 | 24 | 1.0529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | EXT_326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1 _SRT-A | 2 | EKPC_P1-2_COOP-ELIHU161_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | EXT_326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1 _SRT-A | 3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A |  | 4 | 0 | 0 | 0.08 | 325118 | 1RHUDES INV | 34.5 | 1.0778 | 0.42 | 324002 | 1BROWN 3 | 24 | 1.0528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | EXT_326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1 _SRT-A | 4 | EKPC_P1-2_COOP-LAUREL161_SRT-A |  | 3 | 0 | 0 | 0.15 | 324446 | 2BOND | 69 | 1.0164 | 0.56 | 324002 | 1BROWN 3 | 24 | 1.0517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | EXT_326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1 _SRT-A | 5 | EKPC_P1-2_COOP-DEN161_SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | EXT_326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1 _SRT-A | 6 | EKPC_P1-2_COOP 161 TIE_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.19 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | EXT_326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1 _SRT-A | 7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.15 | 324002 | 1BROWN 3 | 24 | 1.0522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | EXT_326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1 _SRT-A | 8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A |  | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.27 | 340576 | WILSON | 24 | 1.0039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | EXT_326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1 _SRT-A | 9 | EKPC_P1-2_LIBJ-GAS161_SRT-A |  | 3 | 0 | 0 | 0.08 | 325118 | 1RHUDES INV | 34.5 | 1.0765 | 0.17 | 325117 | 1RHUDES COL | 34.5 | 1.0709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | EXT_326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1 _SRT-A | 10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A |  | 3 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.06 | 325117 | 1RHUDES COL | 34.5 | 1.0704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | EXT_326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1 _SRT-A | 11 | EKPC_P1-2_GRE-SUMSH161_SRT-A |  | 3 | 0 | 0 | 0.04 | 542969 | STILWEL5 | 161 | 1.0122 | 0.08 | 324002 | 1BROWN 3 | 24 | 1.0524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | EXT_326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1 _SRT-A | 12 | EKPC_P1-2_BARR-SUMSH161_SRT-A |  | 3 | 0 | 0 | 0.06 | 325118 | 1RHUDES INV | 34.5 | 1.0777 | 0.12 | 325117 | 1RHUDES COL | 34.5 | 1.0721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | EXT_326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1 _SRT-A | 13 | EKPC_P1-2_BULL-SUMSH161_SRT-A |  | 1 | 0 | 0 | 0.11 | 542969 | STILWEL5 | 161 | 1.0122 | 0.96 | 342814 | 5SUMM SHADE | 161 | 1.027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | EXT_326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1 _SRT-A | 14 | EKPC_P1-2_SSHAD 161 TIE_SRT-A |  | 1 | 0 | 0 | 0.11 | 542969 | STILWEL5 | 161 | 1.0122 | 0.8 | 360334 | 5SUMMER SHAD | 161 | 1.0273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | EXT_326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1 _SRT-A | 15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A |  | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.19 | 324002 | 1BROWN 3 | 24 | 1.0521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | EXT_326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1 _SRT-A | 16 | EKPC_P1-3_MAR 161/138_SRT-A |  | 2 | 0 | 0 | 0.21 | 325118 | 1RHUDES INV | 34.5 | 1.0788 | 0.57 | 324002 | 1BROWN 3 | 24 | 1.0529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | EXT_326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1 _SRT-A | 17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.12 | 340576 | WILSON | 24 | 1.0042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | EXT_326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1 _SRT-A | 18 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.17 | 340576 | WILSON | 24 | 1.0011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | EXT_326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1 _SRT-A | 19 | EXT_324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1 _SRT-A |  | 1 | 0 | 0 | 0.3 | 342577 | 4FAWKES EK | 138 | 1.0036 | 0.46 | 342577 | 4FAWKES EK | 138 | 1.0036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | EXT_326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1 _SRT-A | 20 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.17 | 324002 | 1BROWN 3 | 24 | 1.0516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | EXT_326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1 _SRT-A | 21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A |  | 2 | 0 | 0 | 0.22 | 325118 | 1RHUDES INV | 34.5 | 1.0788 | 0.57 | 340576 | WILSON | 24 | 1.0044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | EXT_326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1 _SRT-A | 22 | EXT_324217 4BROWN PLANT 138 324219 4BROWN T1 138 1 _SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | EXT_326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1 _SRT-A | 23 | EXT_324217 4BROWN PLANT 138 324220 4BROWN T2 138 1 _SRT-A |  | 1 | 0 | 0 | 0.11 | 542969 | STILWEL5 | 161 | 1.0122 | 0.24 | 324015 | 1DIX DAM 2 | 13.2 | 1.0086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | EXT_326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1 _SRT-A | 24 | EXT_324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1 _SRT-A |  | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.52 | 340576 | WILSON | 24 | 1.004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | EXT_326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1 _SRT-A | 25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.07 | 324002 | 1BROWN 3 | 24 | 1.0526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | EXT_326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1 _SRT-A | 26 | EXT_B-138-111_SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 90.6 | 0 | 0 | 0 | 0 | 0
34 | EXT_326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1 _SRT-A | 27 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A_Dup1 |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.17 | 324002 | 1BROWN 3 | 24 | 1.0516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | EXT_326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1 _SRT-A | 28 | EXT_BB-1133_SRT-A |  | 2 | 0 | 0 | 0.22 | 325118 | 1RHUDES INV | 34.5 | 1.0788 | 0.86 | 325055 | 4RHUDES TP | 138 | 1.0145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | EXT_326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1 _SRT-A | 29 | EXT_MERE SWS_SRT-A |  | 2 | 0 | 0 | 0.19 | 325118 | 1RHUDES INV | 34.5 | 1.078 | 0.43 | 325117 | 1RHUDES COL | 34.5 | 1.0723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | EXT_326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1 _SRT-A | 30 | EXT_B-138-115_SRT-A |  | 3 | 0 | 0 | 0.06 | 542969 | STILWEL5 | 161 | 1.0122 | 0.35 | 324002 | 1BROWN 3 | 24 | 1.0525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | EXT_326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1 _SRT-A | 31 | EXT_B-138-120_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | EXT_326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1 _SRT-A | 32 | EXT_B-138-121_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | EXT_326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1 _SRT-A | 33 | EXT_324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1 _SRT-A |  | 2 | 0 | 0 | 0.09 | 542969 | STILWEL5 | 161 | 1.0122 | 0.21 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | EXT_326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1 _SRT-A | 35 | EXT_B-69-18_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.26 | 324002 | 1BROWN 3 | 24 | 1.0524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | EXT_326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1 _SRT-A | 36 | EXT_B-69-19_SRT-A |  | 5 | 0 | 0 | 0.23 | 325118 | 1RHUDES INV | 34.5 | 1.0762 | 0.49 | 325117 | 1RHUDES COL | 34.5 | 1.0706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | EXT_326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1 _SRT-A | 37 | EXT_BB-1066_SRT-A |  | 2 | 0 | 0 | 0.1 | 542969 | STILWEL5 | 161 | 1.0122 | 0.22 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
35 | EXT_B-69-18_SRT-A | 2 | EKPC_P1-2_COOP-ELIHU161_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
35 | EXT_B-69-18_SRT-A | 3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | Ovl | 4 | 0 | 0 | 0.05 | 324830 | 2CAMPBELV EK | 69 | 0.9836 | 0.49 | 324002 | 1BROWN 3 | 24 | 1.0531 | 11446.5 | 1 | 107 | 0 | 0 | 0 | 0 | 0
35 | EXT_B-69-18_SRT-A | 4 | EKPC_P1-2_COOP-LAUREL161_SRT-A |  | 3 | 0 | 0 | 0.15 | 324446 | 2BOND | 69 | 1.0163 | 0.57 | 324002 | 1BROWN 3 | 24 | 1.052 | 0 | 0 | 99.1 | 0 | 0 | 0 | 0 | 0
35 | EXT_B-69-18_SRT-A | 5 | EKPC_P1-2_COOP-DEN161_SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
35 | EXT_B-69-18_SRT-A | 6 | EKPC_P1-2_COOP 161 TIE_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.2 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.011 | 0 | 0 | 96.3 | 0 | 0 | 0 | 0 | 0
35 | EXT_B-69-18_SRT-A | 7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | Ovl | 3 | 0 | 0 | 0.05 | 341971 | 2NORWOOD | 69 | 0.9627 | 0.13 | 324002 | 1BROWN 3 | 24 | 1.0525 | 10165.2 | 1 | 100.8 | 0 | 0 | 0 | 0 | 0
35 | EXT_B-69-18_SRT-A | 8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
35 | EXT_B-69-18_SRT-A | 9 | EKPC_P1-2_LIBJ-GAS161_SRT-A | Ovl Vlt | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.11 | 324002 | 1BROWN 3 | 24 | 1.0527 | 11494.9 | 1 | 107.2 | 0 | 1 | 0 | 0 | 0
35 | EXT_B-69-18_SRT-A | 10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A | Ovl Vlt | 5 | 0 | 0 | 0.37 | 325118 | 1RHUDES INV | 34.5 | 1.0748 | 0.78 | 325117 | 1RHUDES COL | 34.5 | 1.0693 | 68369.9 | 3 | 173.8 | 1.5 | 9 | 0 | 0 | 0
35 | EXT_B-69-18_SRT-A | 11 | EKPC_P1-2_GRE-SUMSH161_SRT-A |  | 4 | 0 | 0 | 0.07 | 342000 | 5GAS | 161 | 1 | 0.19 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0062 | 0 | 0 | 91.4 | 0 | 0 | 0 | 0 | 0
35 | EXT_B-69-18_SRT-A | 12 | EKPC_P1-2_BARR-SUMSH161_SRT-A |  | 3 | 0 | 0 | 0.04 | 542969 | STILWEL5 | 161 | 1.0122 | 0.14 | 340576 | WILSON | 24 | 1.0054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
35 | EXT_B-69-18_SRT-A | 13 | EKPC_P1-2_BULL-SUMSH161_SRT-A |  | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.22 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
35 | EXT_B-69-18_SRT-A | 14 | EKPC_P1-2_SSHAD 161 TIE_SRT-A |  | 1 | 0 | 0 | 0.11 | 542969 | STILWEL5 | 161 | 1.0122 | 0.9 | 360334 | 5SUMMER SHAD | 161 | 1.0246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
35 | EXT_B-69-18_SRT-A | 15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A | Ovl Vlt | 5 | 0 | 0 | 0.02 | 158981 | ARMOW_BUS2 | 34.5 | 1.025 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 76292.3 | 5 | 147.5 | 7.6 | 17 | 0 | 0 | 0
35 | EXT_B-69-18_SRT-A | 16 | EKPC_P1-3_MAR 161/138_SRT-A |  | 1 | 0 | 0 | 0.11 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
35 | EXT_B-69-18_SRT-A | 17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A |  | 1 | 0 | 0 | 0.13 | 341161 | 2BONNIV EK | 69 | 0.992 | 0.47 | 340576 | WILSON | 24 | 1.0047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
35 | EXT_B-69-18_SRT-A | 18 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.09 | 340576 | WILSON | 24 | 1.0019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
35 | EXT_B-69-18_SRT-A | 19 | EXT_324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1 _SRT-A |  | 1 | 0 | 0 | 0.29 | 342577 | 4FAWKES EK | 138 | 1.0034 | 0.45 | 342577 | 4FAWKES EK | 138 | 1.0034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
35 | EXT_B-69-18_SRT-A | 22 | EXT_324217 4BROWN PLANT 138 324219 4BROWN T1 138 1 _SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
35 | EXT_B-69-18_SRT-A | 23 | EXT_324217 4BROWN PLANT 138 324220 4BROWN T2 138 1 _SRT-A |  | 1 | 0 | 0 | 0.11 | 542969 | STILWEL5 | 161 | 1.0122 | 0.23 | 324015 | 1DIX DAM 2 | 13.2 | 1.0116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
35 | EXT_B-69-18_SRT-A | 24 | EXT_324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1 _SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.13 | 324002 | 1BROWN 3 | 24 | 1.0527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
35 | EXT_B-69-18_SRT-A | 25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A | Ovl Vlt | 6 | 0 | 0 | 0.02 | 158981 | ARMOW_BUS2 | 34.5 | 1.025 | 0.05 | 324002 | 1BROWN 3 | 24 | 1.0524 | 12806.7 | 1 | 113.2 | 0.4 | 6 | 0 | 0 | 0
35 | EXT_B-69-18_SRT-A | 26 | EXT_B-138-111_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.15 | 324002 | 1BROWN 3 | 24 | 1.0528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
35 | EXT_B-69-18_SRT-A | 28 | EXT_BB-1133_SRT-A |  | 1 | 0 | 0 | 0.13 | 341161 | 2BONNIV EK | 69 | 0.992 | 0.47 | 340576 | WILSON | 24 | 1.0047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
35 | EXT_B-69-18_SRT-A | 29 | EXT_MERE SWS_SRT-A |  | 5 | 0 | 0 | 0.22 | 325118 | 1RHUDES INV | 34.5 | 1.0763 | 0.47 | 325117 | 1RHUDES COL | 34.5 | 1.0708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
35 | EXT_B-69-18_SRT-A | 30 | EXT_B-138-115_SRT-A | Vlt | 5 | 0 | 0 | 0.03 | 342403 | 2UPTON T | 69 | 0.9863 | 0.12 | 324002 | 1BROWN 3 | 24 | 1.0521 | 0 | 0 | 98.9 | 0 | 2 | 0 | 0 | 0
35 | EXT_B-69-18_SRT-A | 31 | EXT_B-138-120_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
35 | EXT_B-69-18_SRT-A | 32 | EXT_B-138-121_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
35 | EXT_B-69-18_SRT-A | 33 | EXT_324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1 _SRT-A |  | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.17 | 364119 | 1CUMBRL F1HL | 22 | 1.0725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
35 | EXT_B-69-18_SRT-A | 34 | EXT_326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1 _SRT-A |  | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.21 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
35 | EXT_B-69-18_SRT-A | 36 | EXT_B-69-19_SRT-A |  | 3 | 0 | 0 | 0.06 | 342307 | 2STEPHENSBRG | 69 | 0.9996 | 0.56 | 340576 | WILSON | 24 | 1.0015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
35 | EXT_B-69-18_SRT-A | 37 | EXT_BB-1066_SRT-A |  | 2 | 0 | 0 | 0.1 | 542969 | STILWEL5 | 161 | 1.0122 | 0.17 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36 | EXT_B-69-19_SRT-A | 1 | EKPC_P1-2_MAR-KU LEB138 |  | 3 | 0 | 0 | 0.04 | 542969 | STILWEL5 | 161 | 1.0122 | 0.06 | 324002 | 1BROWN 3 | 24 | 1.0526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36 | EXT_B-69-19_SRT-A | 2 | EKPC_P1-2_COOP-ELIHU161_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 93 | 0 | 0 | 0 | 0 | 0
36 | EXT_B-69-19_SRT-A | 3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A |  | 4 | 0 | 0 | 0.12 | 325118 | 1RHUDES INV | 34.5 | 1.0752 | 0.42 | 324002 | 1BROWN 3 | 24 | 1.0525 | 0 | 0 | 96.9 | 0 | 0 | 0 | 0 | 0
36 | EXT_B-69-19_SRT-A | 4 | EKPC_P1-2_COOP-LAUREL161_SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 243764 | 05BSG1 | 22 | 0.9924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36 | EXT_B-69-19_SRT-A | 5 | EKPC_P1-2_COOP-DEN161_SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36 | EXT_B-69-19_SRT-A | 6 | EKPC_P1-2_COOP 161 TIE_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.19 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36 | EXT_B-69-19_SRT-A | 7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.17 | 324002 | 1BROWN 3 | 24 | 1.0518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36 | EXT_B-69-19_SRT-A | 8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36 | EXT_B-69-19_SRT-A | 9 | EKPC_P1-2_LIBJ-GAS161_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.08 | 325117 | 1RHUDES COL | 34.5 | 1.0684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36 | EXT_B-69-19_SRT-A | 10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A |  | 3 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.06 | 325117 | 1RHUDES COL | 34.5 | 1.0684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36 | EXT_B-69-19_SRT-A | 11 | EKPC_P1-2_GRE-SUMSH161_SRT-A |  | 3 | 0 | 0 | 0.04 | 542969 | STILWEL5 | 161 | 1.0122 | 0.06 | 325130 | 1RHUDES GEN | 0.6 | 1.1031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36 | EXT_B-69-19_SRT-A | 12 | EKPC_P1-2_BARR-SUMSH161_SRT-A |  | 2 | 0 | 0 | 0.24 | 325118 | 1RHUDES INV | 34.5 | 1.0767 | 0.52 | 325117 | 1RHUDES COL | 34.5 | 1.0711 | 0 | 0 | 90.2 | 0 | 0 | 0 | 0 | 0
36 | EXT_B-69-19_SRT-A | 13 | EKPC_P1-2_BULL-SUMSH161_SRT-A |  | 2 | 0 | 0 | 0.18 | 325118 | 1RHUDES INV | 34.5 | 1.076 | 0.38 | 325117 | 1RHUDES COL | 34.5 | 1.0704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36 | EXT_B-69-19_SRT-A | 14 | EKPC_P1-2_SSHAD 161 TIE_SRT-A |  | 1 | 0 | 0 | 0.11 | 542969 | STILWEL5 | 161 | 1.0122 | 0.82 | 361788 | 5SUM SHAD TP | 161 | 1.0268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36 | EXT_B-69-19_SRT-A | 15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.19 | 324002 | 1BROWN 3 | 24 | 1.0518 | 0 | 0 | 92.7 | 0 | 0 | 0 | 0 | 0
36 | EXT_B-69-19_SRT-A | 16 | EKPC_P1-3_MAR 161/138_SRT-A |  | 3 | 0 | 0 | 0.04 | 542969 | STILWEL5 | 161 | 1.0122 | 0.06 | 324002 | 1BROWN 3 | 24 | 1.0526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36 | EXT_B-69-19_SRT-A | 19 | EXT_324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1 _SRT-A |  | 1 | 0 | 0 | 0.29 | 342577 | 4FAWKES EK | 138 | 1.0036 | 0.45 | 342577 | 4FAWKES EK | 138 | 1.0036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36 | EXT_B-69-19_SRT-A | 20 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.16 | 324002 | 1BROWN 3 | 24 | 1.0514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36 | EXT_B-69-19_SRT-A | 21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A |  | 1 | 0 | 0 | 0.12 | 542969 | STILWEL5 | 161 | 1.0122 | 0.31 | 364001 | 1BR FERRY N1 | 22 | 1.0423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36 | EXT_B-69-19_SRT-A | 22 | EXT_324217 4BROWN PLANT 138 324219 4BROWN T1 138 1 _SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36 | EXT_B-69-19_SRT-A | 23 | EXT_324217 4BROWN PLANT 138 324220 4BROWN T2 138 1 _SRT-A |  | 1 | 0 | 0 | 0.11 | 542969 | STILWEL5 | 161 | 1.0122 | 0.22 | 324015 | 1DIX DAM 2 | 13.2 | 1.0065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36 | EXT_B-69-19_SRT-A | 24 | EXT_324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1 _SRT-A |  | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.12 | 364001 | 1BR FERRY N1 | 22 | 1.0424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36 | EXT_B-69-19_SRT-A | 25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A |  | 3 | 0 | 0 | 0.34 | 325118 | 1RHUDES INV | 34.5 | 1.0783 | 0.74 | 325117 | 1RHUDES COL | 34.5 | 1.0726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36 | EXT_B-69-19_SRT-A | 26 | EXT_B-138-111_SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36 | EXT_B-69-19_SRT-A | 27 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A_Dup1 |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.16 | 324002 | 1BROWN 3 | 24 | 1.0514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36 | EXT_B-69-19_SRT-A | 28 | EXT_BB-1133_SRT-A |  | 1 | 0 | 0 | 0.12 | 542969 | STILWEL5 | 161 | 1.0122 | 0.31 | 364001 | 1BR FERRY N1 | 22 | 1.0423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36 | EXT_B-69-19_SRT-A | 29 | EXT_MERE SWS_SRT-A |  | 2 | 0 | 0 | 0.41 | 325118 | 1RHUDES INV | 34.5 | 1.0783 | 0.86 | 325117 | 1RHUDES COL | 34.5 | 1.0726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36 | EXT_B-69-19_SRT-A | 30 | EXT_B-138-115_SRT-A |  | 3 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.4 | 340576 | WILSON | 24 | 1.0011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36 | EXT_B-69-19_SRT-A | 31 | EXT_B-138-120_SRT-A |  | 2 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36 | EXT_B-69-19_SRT-A | 32 | EXT_B-138-121_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36 | EXT_B-69-19_SRT-A | 33 | EXT_324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1 _SRT-A |  | 2 | 0 | 0 | 0.09 | 542969 | STILWEL5 | 161 | 1.0122 | 0.2 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36 | EXT_B-69-19_SRT-A | 34 | EXT_326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1 _SRT-A |  | 2 | 0 | 0 | 0.17 | 325118 | 1RHUDES INV | 34.5 | 1.0759 | 0.36 | 325117 | 1RHUDES COL | 34.5 | 1.0703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36 | EXT_B-69-19_SRT-A | 35 | EXT_B-69-18_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.17 | 324002 | 1BROWN 3 | 24 | 1.0521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36 | EXT_B-69-19_SRT-A | 37 | EXT_BB-1066_SRT-A |  | 2 | 0 | 0 | 0.1 | 542969 | STILWEL5 | 161 | 1.0122 | 0.21 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | EXT_BB-1066_SRT-A | 1 | EKPC_P1-2_MAR-KU LEB138 |  | 2 | 0 | 0 | 0.23 | 325118 | 1RHUDES INV | 34.5 | 1.0776 | 0.56 | 324002 | 1BROWN 3 | 24 | 1.0529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | EXT_BB-1066_SRT-A | 2 | EKPC_P1-2_COOP-ELIHU161_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | EXT_BB-1066_SRT-A | 3 | EKPC_P1-2_COP-RUS-WLF161_SRT-A |  | 4 | 0 | 0 | 0.11 | 325118 | 1RHUDES INV | 34.5 | 1.0763 | 0.42 | 324002 | 1BROWN 3 | 24 | 1.0527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | EXT_BB-1066_SRT-A | 4 | EKPC_P1-2_COOP-LAUREL161_SRT-A |  | 3 | 0 | 0 | 0.15 | 324446 | 2BOND | 69 | 1.0164 | 0.56 | 324002 | 1BROWN 3 | 24 | 1.0517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | EXT_BB-1066_SRT-A | 5 | EKPC_P1-2_COOP-DEN161_SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | EXT_BB-1066_SRT-A | 6 | EKPC_P1-2_COOP 161 TIE_SRT-A |  | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.19 | 364620 | 1WOLFCR H1-2 | 13.8 | 1.0093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | EXT_BB-1066_SRT-A | 7 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A |  | 3 | 0 | 0 | 0.06 | 542969 | STILWEL5 | 161 | 1.0122 | 0.15 | 324002 | 1BROWN 3 | 24 | 1.0521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | EXT_BB-1066_SRT-A | 8 | EKPC_P1-2_MARION-CAS-GAS161_SRT-A |  | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.27 | 340576 | WILSON | 24 | 1.0038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | EXT_BB-1066_SRT-A | 9 | EKPC_P1-2_LIBJ-GAS161_SRT-A |  | 3 | 0 | 0 | 0.09 | 325118 | 1RHUDES INV | 34.5 | 1.0752 | 0.18 | 325117 | 1RHUDES COL | 34.5 | 1.0696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | EXT_BB-1066_SRT-A | 10 | EKPC_P1-2_GRE-TAY-MAR161_SRT-A |  | 3 | 0 | 0 | 0.07 | 542969 | STILWEL5 | 161 | 1.0122 | 0.06 | 325117 | 1RHUDES COL | 34.5 | 1.0692 | 0 | 0 | 90.7 | 0 | 0 | 0 | 0 | 0
37 | EXT_BB-1066_SRT-A | 11 | EKPC_P1-2_GRE-SUMSH161_SRT-A |  | 3 | 0 | 0 | 0.08 | 325118 | 1RHUDES INV | 34.5 | 1.0776 | 0.17 | 325117 | 1RHUDES COL | 34.5 | 1.072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | EXT_BB-1066_SRT-A | 12 | EKPC_P1-2_BARR-SUMSH161_SRT-A |  | 3 | 0 | 0 | 0.06 | 325118 | 1RHUDES INV | 34.5 | 1.0764 | 0.13 | 325117 | 1RHUDES COL | 34.5 | 1.0708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | EXT_BB-1066_SRT-A | 13 | EKPC_P1-2_BULL-SUMSH161_SRT-A |  | 2 | 0 | 0 | 0.18 | 325118 | 1RHUDES INV | 34.5 | 1.077 | 0.38 | 325117 | 1RHUDES COL | 34.5 | 1.0714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | EXT_BB-1066_SRT-A | 14 | EKPC_P1-2_SSHAD 161 TIE_SRT-A |  | 1 | 0 | 0 | 0.12 | 542969 | STILWEL5 | 161 | 1.0122 | 0.86 | 360334 | 5SUMMER SHAD | 161 | 1.0264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | EXT_BB-1066_SRT-A | 15 | EKPC_P1-2_TAYL J-KU TAYL 161_SRT-A |  | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.19 | 324002 | 1BROWN 3 | 24 | 1.0521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | EXT_BB-1066_SRT-A | 16 | EKPC_P1-3_MAR 161/138_SRT-A |  | 2 | 0 | 0 | 0.23 | 325118 | 1RHUDES INV | 34.5 | 1.0776 | 0.56 | 324002 | 1BROWN 3 | 24 | 1.0529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | EXT_BB-1066_SRT-A | 17 | EXT_324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1 _SRT-A |  | 2 | 0 | 0 | 0.34 | 325118 | 1RHUDES INV | 34.5 | 1.0787 | 0.73 | 325117 | 1RHUDES COL | 34.5 | 1.073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | EXT_BB-1066_SRT-A | 18 | EXT_324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1 _SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.17 | 340576 | WILSON | 24 | 1.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | EXT_BB-1066_SRT-A | 19 | EXT_324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1 _SRT-A |  | 1 | 0 | 0 | 0.3 | 342577 | 4FAWKES EK | 138 | 1.0036 | 0.46 | 342577 | 4FAWKES EK | 138 | 1.0036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | EXT_BB-1066_SRT-A | 20 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A |  | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.19 | 340576 | WILSON | 24 | 1.0037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | EXT_BB-1066_SRT-A | 21 | EXT_324270 4LEBANON WES 138 324271 4LEBANON 138 1 _SRT-A |  | 2 | 0 | 0 | 0.31 | 325118 | 1RHUDES INV | 34.5 | 1.0784 | 0.66 | 325117 | 1RHUDES COL | 34.5 | 1.0727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | EXT_BB-1066_SRT-A | 22 | EXT_324217 4BROWN PLANT 138 324219 4BROWN T1 138 1 _SRT-A |  | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | EXT_BB-1066_SRT-A | 23 | EXT_324217 4BROWN PLANT 138 324220 4BROWN T2 138 1 _SRT-A |  | 1 | 0 | 0 | 0.12 | 542969 | STILWEL5 | 161 | 1.0122 | 0.24 | 324015 | 1DIX DAM 2 | 13.2 | 1.0083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | EXT_BB-1066_SRT-A | 24 | EXT_324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1 _SRT-A |  | 2 | 0 | 0 | 0.09 | 542969 | STILWEL5 | 161 | 1.0122 | 0.55 | 340576 | WILSON | 24 | 1.0039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | EXT_BB-1066_SRT-A | 25 | EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 _SRT-A |  | 4 | 0 | 0 | 0.04 | 542969 | STILWEL5 | 161 | 1.0122 | 0.08 | 324002 | 1BROWN 3 | 24 | 1.0526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | EXT_BB-1066_SRT-A | 26 | EXT_B-138-111_SRT-A |  | 4 | 0 | 0 | 0.04 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 90.3 | 0 | 0 | 0 | 0 | 0
37 | EXT_BB-1066_SRT-A | 27 | EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A_Dup1 |  | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.19 | 340576 | WILSON | 24 | 1.0037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | EXT_BB-1066_SRT-A | 28 | EXT_BB-1133_SRT-A |  | 2 | 0 | 0 | 0.33 | 325118 | 1RHUDES INV | 34.5 | 1.0786 | 0.69 | 325117 | 1RHUDES COL | 34.5 | 1.0728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | EXT_BB-1066_SRT-A | 29 | EXT_MERE SWS_SRT-A |  | 4 | 0 | 0 | 0.03 | 542969 | STILWEL5 | 161 | 1.0122 | 0.12 | 324002 | 1BROWN 3 | 24 | 1.0522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | EXT_BB-1066_SRT-A | 30 | EXT_B-138-115_SRT-A |  | 3 | 0 | 0 | 0.06 | 542969 | STILWEL5 | 161 | 1.0122 | 0.39 | 324002 | 1BROWN 3 | 24 | 1.0525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | EXT_BB-1066_SRT-A | 31 | EXT_B-138-120_SRT-A |  | 2 | 0 | 0 | 0.08 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | EXT_BB-1066_SRT-A | 32 | EXT_B-138-121_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.05 | 158983 | ARMOW_AG2 | 0.69 | 0.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | EXT_BB-1066_SRT-A | 34 | EXT_326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1 _SRT-A |  | 2 | 0 | 0 | 0.17 | 325118 | 1RHUDES INV | 34.5 | 1.0769 | 0.36 | 325117 | 1RHUDES COL | 34.5 | 1.0713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | EXT_BB-1066_SRT-A | 35 | EXT_B-69-18_SRT-A |  | 3 | 0 | 0 | 0.05 | 542969 | STILWEL5 | 161 | 1.0122 | 0.25 | 324002 | 1BROWN 3 | 24 | 1.0523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | EXT_BB-1066_SRT-A | 36 | EXT_B-69-19_SRT-A |  | 4 | 0 | 0 | 0.3 | 325118 | 1RHUDES INV | 34.5 | 1.0755 | 0.63 | 325117 | 1RHUDES COL | 34.5 | 1.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## ACContSumNotCnv
EKPC Not Converged AC contingency analysis summary[TARA Ver 2201.2.0.0 64-bit - Sat Aug 13 07:58:26 2022]
Loadflow Case: C:\Users\03419\Desktop\2022 Gas Study\Alt 3A\2032S_gas_alt#3a_212mw.raw
Study Data File: C:\Users\03419\Desktop\2022 Gas Study\2022 series_sub_EKPC-LGEE.sub
Contingency File: C:\Users\03419\Desktop\2022 Gas Study\Option 3A N-1-1 con file.con (total 37 contingencies)/ First-Level Contingency File: C:\Users\03419\Desktop\2022 Gas Study\Option 3A N-1-1 con file.con (total 37 contingencies)
Monitor File: C:\Users\03419\Desktop\2022 Gas Study\2022 series_mon_EKPC-LGEE.mon
Exclude File: not provided
Solution Options (Pre/Post Contingency): Shunts[All Enabled/All Enabled] PAR[Adjusted/Fixed] XFMR Tap[Adjusted/Adjusted] Area Interchange [Disabled/Disabled]
First Level Scenario Index | First Level Scenario | Cont ID | Cont Name | Status

## Warn_Sum
EKPC Warnings Summary[TARA Ver 2201.2.0.0 64-bit - Sat Aug 13 07:55:40 2022]
Loadflow Case: C:\Users\03419\Desktop\2022 Gas Study\Alt 3A\2032S_gas_alt#3a_212mw.raw
Study Data File: C:\Users\03419\Desktop\2022 Gas Study\2022 series_sub_EKPC-LGEE.sub
Contingency File: C:\Users\03419\Desktop\2022 Gas Study\Option 3A N-1-1 con file.con (total 37 contingencies)/ First-Level Contingency File: C:\Users\03419\Desktop\2022 Gas Study\Option 3A N-1-1 con file.con (total 37 contingencies)
Monitor File: C:\Users\03419\Desktop\2022 Gas Study\2022 series_mon_EKPC-LGEE.mon
Exclude File: not provided
Pre/Post Contingency PAR Adjustment: Adjusted/Fixed
Severity Level: 1-info; 2-error; 3-potentially critical; 4-critical error
WarnID | #Warn | Sever | Message
1009 | 23 | 2-error ! | Bus number not found | File C:\Users\03419\Desktop\2022 Gas Study\2022 series_sub_EKPC-LGEE.sub
1826 | 2 | 2-error ! | Oscilating switched shunt could not reach its voltage target. Consider changing target range or locking.
3083 | 1 | 2-error ! | Duplicate Contingency Names are defined. Modifying name of duplicate - adding _DupX where X is number of duplicate instances at this point. | File C:\Users\03419\Desktop\2022 Gas Study\Option 3A N-1-1 con file.con
3168 | 4 | 2-error ! | END statement may cause portions of the file to be skipped | File C:\Users\03419\Desktop\2022 Gas Study\2022 series_mon_EKPC-LGEE.mon
1417 | 1 | 1-info | Initial switched shunt value cannot be reached by following block order (possibly has adjustment mode 1) | File 2032S_gas_alt#3a_212mw.raw
1436 | 3 | 1-info | FACTS Device has mode online but no capability or it is unsupported mode or it has a data error. | File 2032S_gas_alt#3a_212mw.raw
1830 | 1 | 1-info | PAR table used for LTC. Transformer impedance will not be adjusted with Tap ratio adjustments
1850 | 2 | 1-info | PAR Max angle is too big. Set to Max
1851 | 2 | 1-info | PAR Min angle is too small. Set to Min
1863 | 14 | 1-info | TAP Desired voltage range is too small comparing to step. Expanded
1867 | 119 | 1-info | Transformer is radial. Disabling tap adjustments
1938 | 1 | 1-info | Reg bus is not a generator for discrete shunt controlling reactive power output of the plant at remote bus-fixed
1945 | 4 | 1-info | Reg plant Q range too small for discrete shunt controlling reactive power output of the plant at remote bus-fixed
4040 | 8 | 1-info | Subsystem has total zero participation factor
5702 | 11 | 1-info | No participating buses can be scaled. Using uniform distr
6155 | 2 | 1-info | Suspicious PAR has R=0 and small X=0.00000. Increased X to improve flat start
6159 | 9 | 1-info | Branch has high suspicious R/X ratio - make R smaller and X bigger to improve case convergence | File 2032S_gas_alt#3a_212mw.raw
6160 | 11 | 1-info | Transformer has high suspicious R/X ratio - make R smaller and X bigger to improve case convergence | File 2032S_gas_alt#3a_212mw.raw
1100 | 5 | 0-comment | Number of completed input files. See warnings details for # of lines read in
1878 | 88 | 0-comment | Transformer remote control bus is connected to its terminal via low impedance line - controlling terminal instead

## Warn_List
EKPC Warnings List[TARA Ver 2201.2.0.0 64-bit - Sat Aug 13 07:55:40 2022]
Loadflow Case: C:\Users\03419\Desktop\2022 Gas Study\Alt 3A\2032S_gas_alt#3a_212mw.raw
Study Data File: C:\Users\03419\Desktop\2022 Gas Study\2022 series_sub_EKPC-LGEE.sub
Contingency File: C:\Users\03419\Desktop\2022 Gas Study\Option 3A N-1-1 con file.con (total 37 contingencies)/ First-Level Contingency File: C:\Users\03419\Desktop\2022 Gas Study\Option 3A N-1-1 con file.con (total 37 contingencies)
Monitor File: C:\Users\03419\Desktop\2022 Gas Study\2022 series_mon_EKPC-LGEE.mon
Exclude File: not provided
Pre/Post Contingency PAR Adjustment: Adjusted/Fixed
WarnInd | WarnID | SeverLvl | Message | File | Line
1 | 6159 | 1 | Branch [135527 SANTR404 34.5 102 145 135536 SANBORN3 34.5 102 145 ] has high suspicious R/X ratio [ 20.00] > 10.00. R= 0.00020 X= 0.00001 Suggested R= 0.00010 | 2032S_gas_alt#3a_212mw.raw | 164189
2 | 6159 | 1 | Branch [135536 SANBORN3 34.5 102 145 135539 SANTR403 34.5 102 145 ] has high suspicious R/X ratio [ 20.00] > 10.00. R= 0.00020 X= 0.00001 Suggested R= 0.00010 | 2032S_gas_alt#3a_212mw.raw | 164199
3 | 6159 | 1 | Branch [318409 MS SLR4 COL 34.5 349 1398 318410 MS SLR4 PAD 34.5 349 1398 ] has high suspicious R/X ratio [ 10.01] > 10.00. R= 0.02670 X= 0.00267 Suggested R= 0.02667 | 2032S_gas_alt#3a_212mw.raw | 206815
4 | 6159 | 1 | Branch [336007 6VACHRE! 230 351 387 336029 J1142J1158 230 351 387 ] has high suspicious R/X ratio [ 12.20] > 10.00. R= 0.00024 X= 0.00002 Suggested R= 0.00020 | 2032S_gas_alt#3a_212mw.raw | 209188
5 | 6159 | 1 | Branch [337038 3INDIANOLATP 115 326 390 337039 3INDIANOLALD 115 326 390 ] has high suspicious R/X ratio [ 30.00] > 10.00. R= 0.00009 X= 0.00000 Suggested R= 0.00003 | 2032S_gas_alt#3a_212mw.raw | 209700
6 | 6159 | 1 | Branch [400503 MELROSTP 115 401 401 406698 MELROSE 115 401 412 ] has high suspicious R/X ratio [ 10.53] > 10.00. R= 0.00200 X= 0.00019 Suggested R= 0.00190 | 2032S_gas_alt#3a_212mw.raw | 223012
7 | 6159 | 1 | Branch [539810 BUS-0421 34.5 534 1541 539811 SUB34.5KVB 34.5 534 1541 ] has high suspicious R/X ratio [ 22.76] > 10.00. R= 0.00382 X= 0.00017 Suggested R= 0.00168 | 2032S_gas_alt#3a_212mw.raw | 231258
8 | 6159 | 1 | Branch [629602 VINING REC 8 69.0 627 665 629604 VINING TAP 8 69.0 627 665 ] has high suspicious R/X ratio [ 43.59] > 10.00. R= 0.00667 X= 0.00015 Suggested R= 0.00153 | 2032S_gas_alt#3a_212mw.raw | 235135
9 | 6159 | 1 | Branch [658129 LUVERNEMNS19 25.0 652 1624 658131 LUVERNEMNS29 25.0 652 1624 ] has high suspicious R/X ratio [ 13.06] > 10.00. R= 0.38800 X= 0.02970 Suggested R= 0.29700 | 2032S_gas_alt#3a_212mw.raw | 239227
10 | 1878 | 0 | Transformer [100439 NEWPAGE BUS7 13.8 101 100 100211 NEWPAGEPAPER 115 ] remotely controlled bus {100416 NEWPAGE BUS3 13.8 ] connected to fromBus via ZIL - changed to control fromBus
11 | 6155 | 1 | Suspicious PAR [100780 OXFORD 12.5 101 100 102193 OXFORD 34.5 101 100 ] has R=0 and small X=0.00050 with Phase angle =30.000 Check data. Winding=1 Increased X to improve flat start
12 | 1878 | 0 | Transformer [110822 WALTHAM A 115 101 110 110987 WALT PS-D 115 ] remotely controlled bus {110809 WALTHAM B 115 ] connected to fromBus via ZIL - changed to control fromBus
13 | 6160 | 1 | 3W Transformer [121839 NUTMEG 34.5 101 116 999974 NUTMEG-MAIN 34.5 101 116 ] Wind=1 has high suspicious R/X ratio [ -17.51] > 10.00. R= 0.00876 X= -0.00050 Suggested R= -0.00500 | 2032S_gas_alt#3a_212mw.raw | 352762
14 | 6160 | 1 | 2W Transformer [121766 WILLIMANTIC 27.6 101 116 121764 WILLIMANTCM1 99.0 101 116 ] has high suspicious R/X ratio [ 11.55] > 10.00. R= 0.00578 X= 0.00050 Suggested R= 0.00500 | 2032S_gas_alt#3a_212mw.raw | 352762
15 | 1878 | 0 | Transformer [128835 SHORE RD 345 102 156 129294 SHORE RD2 138 ] remotely controlled bus {129293 SHORE RD 138 ] connected to ToBus via ZIL - changed to control toBus
16 | 1878 | 0 | Transformer [129685 PILGRM1 69.0 102 156 129355 PILGRIM 138 ] remotely controlled bus {129686 PILGRM2 69.0 ] connected to fromBus via ZIL - changed to control fromBus
17 | 1878 | 0 | Transformer [129361 RULND RD 138 102 156 129693 RULAND RD2 69.0 ] remotely controlled bus {129692 RULND RD 69.0 ] connected to ToBus via ZIL - changed to control toBus
18 | 1878 | 0 | Transformer [129791 BRKHAVEN2 69.0 102 156 129416 BRKHVEN4 138 ] remotely controlled bus {129790 BRKHAVEN1 69.0 ] connected to fromBus via ZIL - changed to control fromBus
19 | 6160 | 1 | 3W Transformer [130664 Q678_COLL 34.5 102 156 999925 Q678_POI 34.5 102 156 ] Wind=1 has high suspicious R/X ratio [ -20.40] > 10.00. R= 0.01020 X= -0.00050 Suggested R= -0.00500 | 2032S_gas_alt#3a_212mw.raw | 352762
20 | 1878 | 0 | Transformer [147481 LOVETT_2 138 102 155 999902 BANK 192 138 ] remotely controlled bus {146766 LOVET138 138 ] connected to fromBus via ZIL - changed to control fromBus
21 | 6160 | 1 | 3W Transformer [151664 MOOSE_LK_B2 44.0 103 1101 999881 103:MOOSE L 44.0 103 1101 ] Wind=1 has high suspicious R/X ratio [ -26.85] > 10.00. R= 0.03693 X= -0.00137 Suggested R= -0.01375 | 2032S_gas_alt#3a_212mw.raw | 352762
22 | 6160 | 1 | 2W Transformer [151789 LOWER_WHITER 4.16 103 1101 151790 LOWER_WHITEG 0.60 103 1101 ] has high suspicious R/X ratio [ 16.67] > 10.00. R=200.00000 X= 12.00000 Suggested R=120.00000 | 2032S_gas_alt#3a_212mw.raw | 352762
23 | 1878 | 0 | Transformer [160658 NOVA_MOORE_A 13.8 103 1110 160152 N_MOORE_L27V 220 ] remotely controlled bus {160656 NOVA_MOORE_B 13.8 ] connected to fromBus via ZIL - changed to control fromBus
24 | 1878 | 0 | Transformer [184165 MANIWA 120 104 1143 184401 MANI69 A 69.0 ] remotely controlled bus {184400 MANI69 69.0 ] connected to ToBus via ZIL - changed to control toBus
25 | 1878 | 0 | Transformer [185430 ORFORA 120 104 1153 185445 ORFORD-25B 26.4 ] remotely controlled bus {185444 ORFORD-25A 26.4 ] connected to ToBus via ZIL - changed to control toBus
26 | 1878 | 0 | Transformer [185430 ORFORA 120 104 1153 185445 ORFORD-25B 26.4 ] remotely controlled bus {185444 ORFORD-25A 26.4 ] connected to ToBus via ZIL - changed to control toBus
27 | 1878 | 0 | Transformer [213586 EDDYSTN3 230 230 241 213587 EDDYSTN3 24.0 ] remotely controlled bus {213579 EDDYSTN 230 ] connected to fromBus via ZIL - changed to control fromBus
28 | 1878 | 0 | Transformer [213588 EDDYSTN4 230 230 241 213589 EDDYSTN4 24.0 ] remotely controlled bus {213579 EDDYSTN 230 ] connected to fromBus via ZIL - changed to control fromBus
29 | 1878 | 0 | Transformer [213909 PLYMTH2 138 230 241 213806 COVANTA PLYM 13.8 ] remotely controlled bus {213905 PLYMTG 138 ] connected to fromBus via ZIL - changed to control fromBus
30 | 1878 | 0 | Transformer [213954 SOUTHWK1 69.0 230 242 213958 STHWK5-6 13.8 ] remotely controlled bus {213955 SOUTHWK2 69.0 ] connected to fromBus via ZIL - changed to control fromBus
31 | 1878 | 0 | Transformer [213955 SOUTHWK2 69.0 230 242 213957 STHWK3-4 13.8 ] remotely controlled bus {213954 SOUTHWK1 69.0 ] connected to fromBus via ZIL - changed to control fromBus
32 | 1878 | 0 | Transformer [214269 CROYDONCT 230 230 241 999237 CROYDONCT 13.8 ] remotely controlled bus {213543 CROYDON30 230 ] connected to fromBus via ZIL - changed to control fromBus
33 | 1878 | 0 | Transformer [214269 CROYDONCT 230 230 241 999236 CROYDONCT _1 13.8 ] remotely controlled bus {213543 CROYDON30 230 ] connected to fromBus via ZIL - changed to control fromBus
34 | 1878 | 0 | Transformer [214269 CROYDONCT 230 230 241 999235 CROYDONCT _2 13.8 ] remotely controlled bus {213543 CROYDON30 230 ] connected to fromBus via ZIL - changed to control fromBus
35 | 1878 | 0 | Transformer [214269 CROYDONCT 230 230 241 999234 CROYDONCT _3 13.8 ] remotely controlled bus {213543 CROYDON30 230 ] connected to fromBus via ZIL - changed to control fromBus
36 | 1878 | 0 | Transformer [214275 RICHMONDCT 230 230 241 999233 RICHMONDCT 13.8 ] remotely controlled bus {213922 RICHMOND7T 230 ] connected to fromBus via ZIL - changed to control fromBus
37 | 1878 | 0 | Transformer [217046 FAIRLAWN 230 231 250 217173 FAIRLAWN_4 138 ] remotely controlled bus {217047 FAIRLAWN_2 138 ] connected to ToBus via ZIL - changed to control toBus
38 | 1878 | 0 | Transformer [234254 MNTN TR1 69.0 236 296 234251 MOUNT-H1 230 ] remotely controlled bus {234257 MOUNT 2 69.0 ] connected to fromBus via ZIL - changed to control fromBus
39 | 1878 | 0 | Transformer [234255 MNTN TR2 69.0 236 296 234253 MOUNT-H2 230 ] remotely controlled bus {234257 MOUNT 2 69.0 ] connected to fromBus via ZIL - changed to control fromBus
40 | 1878 | 0 | Transformer [247354 05SUNNYSID 69.0 205 1256 246126 05SUNNYSIDE2 138 ] remotely controlled bus {243120 05SUNNYSIDE1 138 ] connected to ToBus via ZIL - changed to control toBus
41 | 1878 | 0 | Transformer [249623 08LAFAYE 230 208 1220 249771 08LAF 2 138 ] remotely controlled bus {249770 08LAF 1 138 ] connected to ToBus via ZIL - changed to control toBus
42 | 1878 | 0 | Transformer [311688 6CARFOREST 230 344 342 312530 3CARFOR2 115 ] remotely controlled bus {312813 3CARFOREST 115 ] connected to ToBus via ZIL - changed to control toBus
43 | 1878 | 0 | Transformer [312526 6BENNET2 230 344 341 312500 2BENNET2 69.0 ] remotely controlled bus {312885 2BENNETT 69.0 ] connected to ToBus via ZIL - changed to control toBus
44 | 1878 | 0 | Transformer [312501 6BLUFFT2 230 344 340 312502 3BLUFFT2 115 ] remotely controlled bus {312747 3BLUFFTN 115 ] connected to ToBus via ZIL - changed to control toBus
45 | 1878 | 0 | Transformer [312711 6DARLING 230 344 341 312506 2DARLING2 69.0 ] remotely controlled bus {312921 2DARLING 69.0 ] connected to ToBus via ZIL - changed to control toBus
46 | 1878 | 0 | Transformer [312529 6LK CTY2 230 344 341 312514 2LK CTY2 69.0 ] remotely controlled bus {312968 2LK CITY 69.0 ] connected to ToBus via ZIL - changed to control toBus
47 | 1878 | 0 | Transformer [312802 3MARIONSC 115 344 341 312515 2MARION2 69.0 ] remotely controlled bus {312984 2MARION-SC 69.0 ] connected to ToBus via ZIL - changed to control toBus
48 | 1878 | 0 | Transformer [312802 3MARIONSC 115 344 341 312515 2MARION2 69.0 ] remotely controlled bus {312984 2MARION-SC 69.0 ] connected to ToBus via ZIL - changed to control toBus
49 | 1878 | 0 | Transformer [312516 6PRY RD2 230 344 342 312517 3PRY RD2 115 ] remotely controlled bus {312819 3PERRY R 115 ] connected to ToBus via ZIL - changed to control toBus
50 | 1878 | 0 | Transformer [312531 6PMARIA2 230 344 341 312518 2PMARIA2 69.0 ] remotely controlled bus {312993 2POMARIA 69.0 ] connected to ToBus via ZIL - changed to control toBus
51 | 1878 | 0 | Transformer [312524 6RDBLUF2 230 344 342 312519 3REDBLF2 115 ] remotely controlled bus {312868 3REDBLUF 115 ] connected to ToBus via ZIL - changed to control toBus
52 | 1878 | 0 | Transformer [312536 6RICHB2 230 344 341 312520 2RCHBRG2 69.0 ] remotely controlled bus {311399 2RICHBRG 69.0 ] connected to ToBus via ZIL - changed to control toBus
53 | 1878 | 0 | Transformer [312535 6WINSBO2 230 344 341 312523 2WINSBO2 69.0 ] remotely controlled bus {311059 2WINNSBO 69.0 ] connected to ToBus via ZIL - changed to control toBus
54 | 1878 | 0 | Transformer [312527 6AIKEN32 230 344 340 312543 3AIKEN2 115 ] remotely controlled bus {312856 3AIKEN3 115 ] connected to ToBus via ZIL - changed to control toBus
55 | 1878 | 0 | Transformer [312724 6JISCPSA 230 344 340 312528 3JISCPS2 115 ] remotely controlled bus {312854 3JISCPSA 115 ] connected to ToBus via ZIL - changed to control toBus
56 | 1878 | 0 | Transformer [334521 2HELBIG1! 69.0 351 385 998712 6HELBIG ] remotely controlled bus {334517 2HELBIG2! 69.0 ] connected to fromBus via ZIL - changed to control fromBus
57 | 1878 | 0 | Transformer [334729 2ORANGE5! 69.0 351 1 998698 4ORANGE2! 69.0 ] remotely controlled bus {334730 2ORANGE6! 69.0 ] connected to fromBus via ZIL - changed to control fromBus
58 | 1878 | 0 | Transformer [334728 2ORANGE4! 69.0 351 1 998697 4ORANGETIE 69.0 ] remotely controlled bus {334730 2ORANGE6! 69.0 ] connected to fromBus via ZIL - changed to control fromBus
59 | 1878 | 0 | Transformer [335448 2CHAMPAGNE_2 69.0 351 1 998680 4CHAMPAGNE! 69.0 ] remotely controlled bus {335442 2CHAMPAGNE_1 69.0 ] connected to fromBus via ZIL - changed to control fromBus
60 | 1878 | 0 | Transformer [335680 2TIGER_1! 69.0 351 1 998674 6TIGER! 69.0 ] remotely controlled bus {335669 2TIGER_2! 69.0 ] connected to fromBus via ZIL - changed to control fromBus
61 | 1878 | 0 | Transformer [335732 2COLY_3! 69.0 351 1 998670 6COLY ] remotely controlled bus {335713 2COLY_1! 69.0 ] connected to fromBus via ZIL - changed to control fromBus
62 | 1878 | 0 | Transformer [335803 4PORT_HUD5! 138 351 386 998665 6PORT_HUD ] remotely controlled bus {335805 4PORT_HUD! 138 ] connected to fromBus via ZIL - changed to control fromBus
63 | 1878 | 0 | Transformer [346190 1BAILEY 2 34.5 356 1334 344088 4BAILEY 3 138 ] remotely controlled bus {346012 1BAILEY 1 34.5 ] connected to fromBus via ZIL - changed to control fromBus
64 | 1878 | 0 | Transformer [346190 1BAILEY 2 34.5 356 1334 344090 4BAILEY 2 138 ] remotely controlled bus {346012 1BAILEY 1 34.5 ] connected to fromBus via ZIL - changed to control fromBus
65 | 1878 | 0 | Transformer [346200 1BERKELEY 3 34.5 356 1331 344125 4BERKELEY 3 138 ] remotely controlled bus {346018 1BERKELEY 2 34.5 ] connected to fromBus via ZIL - changed to control fromBus
66 | 1878 | 0 | Transformer [346201 1BERKELEY 4 34.5 356 1331 344126 4BERKELEY 4 138 ] remotely controlled bus {346017 1BERKELEY 1 34.5 ] connected to fromBus via ZIL - changed to control fromBus
67 | 1878 | 0 | Transformer [346202 1BIG RIVR 2 34.5 356 1334 344138 4BIG RIVR 2 138 ] remotely controlled bus {346021 1BIG RIVR 1 34.5 ] connected to fromBus via ZIL - changed to control fromBus
68 | 1878 | 0 | Transformer [344424 1CONWAY 2 34.5 356 1334 344419 4CONWAY 2 138 ] remotely controlled bus {344423 1CONWAY 1 34.5 ] connected to fromBus via ZIL - changed to control fromBus
69 | 1878 | 0 | Transformer [344425 1CONWAY 4 34.5 356 1334 344420 4CONWAY 4 138 ] remotely controlled bus {346040 1CONWAY 3 34.5 ] connected to fromBus via ZIL - changed to control fromBus
70 | 1878 | 0 | Transformer [346210 1EUCLID 3 34.5 356 1333 344550 4EUCLID 3 138 ] remotely controlled bus {346047 1EUCLID 1 34.5 ] connected to fromBus via ZIL - changed to control fromBus
71 | 1878 | 0 | Transformer [346204 1FTZUM 3 34.5 356 1330 344601 4FTZUM 3 138 ] remotely controlled bus {346053 1FTZUM 1 34.5 ] connected to fromBus via ZIL - changed to control fromBus
72 | 1878 | 0 | Transformer [345902 1HALL_ST1 34.5 356 1333 344682 4HALL_ST 1 138 ] remotely controlled bus {346064 1HALL_ST 3 34.5 ] connected to fromBus via ZIL - changed to control fromBus
73 | 1878 | 0 | Transformer [345903 1HALL_ST 2 34.5 356 1333 344683 4HALL_ST 2 138 ] remotely controlled bus {346064 1HALL_ST 3 34.5 ] connected to fromBus via ZIL - changed to control fromBus
74 | 1878 | 0 | Transformer [346206 1HUNTER 2 34.5 356 1333 344755 4HUNTER 2 138 ] remotely controlled bus {346068 1HUNTER 1 34.5 ] connected to fromBus via ZIL - changed to control fromBus
75 | 1878 | 0 | Transformer [346207 1HUNTER 3 34.5 356 1333 344756 4HUNTER 3 138 ] remotely controlled bus {346068 1HUNTER 1 34.5 ] connected to fromBus via ZIL - changed to control fromBus
76 | 1878 | 0 | Transformer [346208 1LKSIDE 2 34.5 356 1331 344958 4LKSIDE 2 138 ] remotely controlled bus {346095 1LKSIDE 1 34.5 ] connected to fromBus via ZIL - changed to control fromBus
77 | 1878 | 0 | Transformer [346191 1MALINE 2 34.5 356 1333 345008 4MALINE 2 138 ] remotely controlled bus {346097 1MALINE 1 34.5 ] connected to fromBus via ZIL - changed to control fromBus
78 | 1878 | 0 | Transformer [346192 1MALINE 4 34.5 356 1333 345010 4MALINE 4 138 ] remotely controlled bus {346098 1MALINE 3 34.5 ] connected to fromBus via ZIL - changed to control fromBus
79 | 1878 | 0 | Transformer [346214 1MASON34 3 34.5 356 1332 345057 4MASON34 3 138 ] remotely controlled bus {346102 1MASON34 1 34.5 ] connected to fromBus via ZIL - changed to control fromBus
80 | 1878 | 0 | Transformer [346212 1MCCLAY 3 34.5 356 1332 345080 4MCCLAY 3 138 ] remotely controlled bus {346103 1MCCLAY 1 34.5 ] connected to fromBus via ZIL - changed to control fromBus
81 | 1878 | 0 | Transformer [345220 2MOBERLY 2 69.0 356 1331 345219 5MOBERLY 2 161 ] remotely controlled bus {345222 2MOBERLY 1 69.0 ] connected to fromBus via ZIL - changed to control fromBus
82 | 1878 | 0 | Transformer [346205 1OFALLON 2 34.5 356 1330 345358 4OFALLON 2 138 ] remotely controlled bus {346112 1OFALLON 1 34.5 ] connected to fromBus via ZIL - changed to control fromBus
83 | 1878 | 0 | Transformer [346198 1PAGE 2 34.5 356 1333 345426 4BUGLE 138 ] remotely controlled bus {346118 1PAGE 1 34.5 ] connected to fromBus via ZIL - changed to control fromBus
84 | 1878 | 0 | Transformer [346199 1PAGE 3 34.5 356 1333 345426 4BUGLE 138 ] remotely controlled bus {346118 1PAGE 1 34.5 ] connected to fromBus via ZIL - changed to control fromBus
85 | 1878 | 0 | Transformer [346197 1SANDY_CK 2 34.5 356 1334 345706 4SANDY_CK 2 138 ] remotely controlled bus {346137 1SANDY_CK 1 34.5 ] connected to fromBus via ZIL - changed to control fromBus
86 | 1878 | 0 | Transformer [346193 1WARSON 2 34.5 356 1332 345947 4WARSON 2 138 ] remotely controlled bus {346153 1WARSON 1 34.5 ] connected to fromBus via ZIL - changed to control fromBus
87 | 1878 | 0 | Transformer [346194 1WARSON 4 34.5 356 1332 345948 4WARSON 4 138 ] remotely controlled bus {346154 1WARSON 3 34.5 ] connected to fromBus via ZIL - changed to control fromBus
88 | 1878 | 0 | Transformer [346195 1WATSON 2 34.5 356 1333 345961 4WATSON2 138 ] remotely controlled bus {346155 1WATSON 1 34.5 ] connected to fromBus via ZIL - changed to control fromBus
89 | 1878 | 0 | Transformer [346196 1WATSON 3 34.5 356 1333 345963 4WATSON3 138 ] remotely controlled bus {346155 1WATSON 1 34.5 ] connected to fromBus via ZIL - changed to control fromBus
90 | 1878 | 0 | Transformer [347707 1MISS 1 34.5 357 1340 347709 4MISS 1 138 ] remotely controlled bus {349409 1MISS 3 34.5 ] connected to fromBus via ZIL - changed to control fromBus
91 | 1878 | 0 | Transformer [348095 1RIDGE 1 34.5 357 1341 348093 4RIDGE 2 138 ] remotely controlled bus {349410 1RIDGE 3 34.5 ] connected to fromBus via ZIL - changed to control fromBus
92 | 1878 | 0 | Transformer [348096 1RIDGE 2 34.5 357 1341 348093 4RIDGE 2 138 ] remotely controlled bus {349410 1RIDGE 3 34.5 ] connected to fromBus via ZIL - changed to control fromBus
93 | 1878 | 0 | Transformer [401892 PMR9-COLLE 230 401 401 401885 PMR9-CTA 18.0 ] remotely controlled bus {400265 MARTIN 2 230 ] connected to fromBus via ZIL - changed to control fromBus
94 | 1878 | 0 | Transformer [401892 PMR9-COLLE 230 401 401 401886 PMR9-CTB 18.0 ] remotely controlled bus {400265 MARTIN 2 230 ] connected to fromBus via ZIL - changed to control fromBus
95 | 6155 | 1 | Suspicious PAR [406869 SRNGBNKTR_2 13.2 412 412 997988 SPRNGBNK 2 115 412 412 ] has R=0 and small X=0.00010 with Phase angle =13.200 Check data. Winding=3 Increased X to improve flat start
96 | 1878 | 0 | Transformer [407892 OSCEOLA_RX 69.0 416 416 997967 OSCEOL230/69 69.0 ] remotely controlled bus {407891 OSCEOLA 69.0 ] connected to fromBus via ZIL - changed to control fromBus
97 | 1878 | 0 | Transformer [512636 CATSAGR4 138 523 554 997713 CATAUTO1 _1 138 ] remotely controlled bus {509790 CATOOSA4 138 ] connected to fromBus via ZIL - changed to control fromBus
98 | 1878 | 0 | Transformer [512636 CATSAGR4 138 523 554 997712 CATAUTO2 _1 138 ] remotely controlled bus {509790 CATOOSA4 138 ] connected to fromBus via ZIL - changed to control fromBus
99 | 1878 | 0 | Transformer [512636 CATSAGR4 138 523 554 997711 CATAUTO3 _1 138 ] remotely controlled bus {509790 CATOOSA4 138 ] connected to fromBus via ZIL - changed to control fromBus
100 | 1878 | 0 | Transformer [528363 MADDOX_3 1 12.5 526 1508 528353 MADDOXG23 3 115 ] remotely controlled bus {528355 MADDOX 3 115 ] connected to ToBus via ZIL - changed to control toBus
101 | 6160 | 1 | 3W Transformer [531505 CIMWD2 1 34.5 534 1541 997283 CIMRNWND2 MP 34.5 534 1541 ] Wind=1 has high suspicious R/X ratio [ -11.01] > 10.00. R= -0.00551 X= 0.00050 Suggested R= 0.00500 | 2032S_gas_alt#3a_212mw.raw | 352762
102 | 6160 | 1 | 3W Transformer [539724 PHLBURG1 34.5 534 1524 997118 PHLBURG3 34.5 534 1529 ] Wind=0 has high suspicious R/X ratio [ 31.54] > 10.00. R= 0.01577 X= 0.00050 Suggested R= 0.00500 | 2032S_gas_alt#3a_212mw.raw | 352762
103 | 6160 | 1 | 3W Transformer [543154 WHGNSVL1 12.5 541 1552 997029 WEST HIGGI1 12.5 541 1552 ] Wind=1 has high suspicious R/X ratio [ 43.42] > 10.00. R= -0.12113 X= -0.00279 Suggested R= -0.02790 | 2032S_gas_alt#3a_212mw.raw | 352762
104 | 1878 | 0 | Transformer [630759 MARION J2 8 69.0 627 665 631195 MARION K2 7 115 ] remotely controlled bus {629183 MARION J1 8 69.0 ] connected to fromBus via ZIL - changed to control fromBus
105 | 6160 | 1 | 3W Transformer [640202 GR ISLD9 34.5 640 686 996700 GRAND.ISD T1 34.5 640 686 ] Wind=0 has high suspicious R/X ratio [ -12.80] > 10.00. R= 0.01280 X= -0.00100 Suggested R= -0.01000 | 2032S_gas_alt#3a_212mw.raw | 352762
106 | 1878 | 0 | Transformer [640304 OGALALANPPD7 115 640 686 996651 OGALLALA T1 115 ] remotely controlled bus {659801 OGALALA_-TS7 115 ] connected to fromBus via ZIL - changed to control fromBus
107 | 6160 | 1 | 3W Transformer [647976 S976 8 69.0 645 691 996534 FREMONT T4 69.0 640 686 ] Wind=0 has high suspicious R/X ratio [ -12.40] > 10.00. R= 0.00620 X= -0.00050 Suggested R= -0.00500 | 2032S_gas_alt#3a_212mw.raw | 352762
108 | 6160 | 1 | 3W Transformer [648610 NC2HS 5 161 645 694 996518 NC2HST2 4.20 645 694 ] Wind=2 has high suspicious R/X ratio [ -15.12] > 10.00. R= -0.00756 X= 0.00050 Suggested R= 0.00500 | 2032S_gas_alt#3a_212mw.raw | 352762
109 | 1878 | 0 | Transformer [668433 PFBK10 8 65.1 667 1647 668052 PA2-TAP7 110 ] remotely controlled bus {668413 PF-BK9 8 65.1 ] connected to fromBus via ZIL - changed to control fromBus
110 | 1878 | 0 | Transformer [693681 J855 CL1 34.5 694 1684 693684 RED BARN LLC 138 ] remotely controlled bus {693680 EBENEZER 138 ] connected to ToBus via ZIL - changed to control toBus
111 | 1830 | 1 | PAR table 2 range [-70.00:70.00] used for LTC 403223 FIGUR SL_COL 34.5 998077 FIGUR SL_COL 34.5 30 with regul range [0.03:0.03]. change table# to zero
112 | 1436 | 1 | FACTS Device has mode online but no capability or it is unsupported mode or it has a data error. [29 GROTON_DVAR ] Series link operating as a SSSC and shunt link is disabled by SHMX=0 and TRMX=0. Mode=1 | 2032S_gas_alt#3a_212mw.raw | 354164
113 | 1436 | 1 | FACTS Device has mode online but no capability or it is unsupported mode or it has a data error. [33 KIBBY_DVAR ] Series link operating as a SSSC and shunt link is disabled by SHMX=0 and TRMX=0. Mode=1 | 2032S_gas_alt#3a_212mw.raw | 354164
114 | 1436 | 1 | FACTS Device has mode online but no capability or it is unsupported mode or it has a data error. [43 WEAVERDVAR ] Series link operating as a SSSC and shunt link is disabled by SHMX=0 and TRMX=0. Mode=1 | 2032S_gas_alt#3a_212mw.raw | 354164
115 | 1417 | 1 | Initial switched shunt [180326 OUT315 315 104 1143 ] value [ 700.00] cannot be reached by following block order (possibly has adjustment mode 1). New value is [ 710.33] | 2032S_gas_alt#3a_212mw.raw | 355360
116 | 1100 | 0 | Read in 362281 records from File [2032S_gas_alt#3a_212mw.raw] (Lev=1)
117 | 1850 | 1 | PAR Max angle 180.1 is too big. Set Max= 180.0 for 668090 WHITESH7 110 668091 WHSL1PH7 110 7
118 | 1851 | 1 | PAR Min angle -180.1 is too big (negative). Set Min= -180.0 for 668090 WHITESH7 110 668091 WHSL1PH7 110 7
119 | 1850 | 1 | PAR Max angle 180.1 is too big. Set Max= 180.0 for 668090 WHITESH7 110 668092 WHSL2PH7 110 8
120 | 1851 | 1 | PAR Min angle -180.1 is too big (negative). Set Min= -180.0 for 668090 WHITESH7 110 668092 WHSL2PH7 110 8
121 | 1867 | 1 | Transformer 100565 MERRILL RD 345 100566 CONV_ME 382 1 is radial. LTC control is disabled.
122 | 1867 | 1 | Transformer 109277 NEWPORT HY 12.5 108121 NEWPORT_T2LS 46.0 1 is radial. LTC control is disabled.
123 | 1867 | 1 | Transformer 109002 MORRISVIL2_D 12.0 108623 MORRISVILL 2 34.5 1 is radial. LTC control is disabled.
124 | 1867 | 1 | Transformer 116541 N-CANAL 3 13.8 116228 N-CANAL 115 3 is radial. LTC control is disabled.
125 | 1867 | 1 | Transformer 122526 NOERA STREET 4.80 122527 NOERA STREET 13.8 1 is radial. LTC control is disabled.
126 | 1867 | 1 | Transformer 125011 EFISH115 115 126281 E FISHKILL 345 2 is radial. LTC control is disabled.
127 | 1867 | 1 | Transformer 126139 HURLEY_13._A 13.8 125104 HURLEY 6 69.0 5 is radial. LTC control is disabled.
128 | 1867 | 1 | Transformer 131129 AMENIA46 46.0 131121 AMENIA69 69.0 1 is radial. LTC control is disabled.
129 | 1867 | 1 | Transformer 135383 S219-182 115 135846 PARKCLUB 13.2 1 is radial. LTC control is disabled.
130 | 1867 | 1 | Transformer 151664 MOOSE_LK_B2 44.0 999881 103:MOOSE L 44.0 T2 is radial. LTC control is disabled.
131 | 1867 | 1 | Transformer 151673 PERRAU_FLS_B 12.5 151303 PERRAULT_FLS 118 T1 is radial. LTC control is disabled.
132 | 1867 | 1 | Transformer 152096 TEMBEC_SP_FL 220 152726 TEMB_SP_FLT6 6.60 T6 is radial. LTC control is disabled.
133 | 1867 | 1 | Transformer 152604 HOLLOW_#3TR2 4.16 152608 HOLLOWAY_#3 4.16 R2 is radial. LTC control is disabled.
134 | 1867 | 1 | Transformer 152679 MASSEY_DS_B 12.5 152678 MASSEY_DS_R1 12.5 R1 is radial. LTC control is disabled.
135 | 1867 | 1 | Transformer 153099 BRACEBRIDGE 220 153650 BRACEBRIDGE 44.0 T1 is radial. LTC control is disabled.
136 | 1867 | 1 | Transformer 154626 LIMEBANK_B1 27.6 154228 LIMEBANK_H1 118 T1 is radial. LTC control is disabled.
137 | 1867 | 1 | Transformer 154639 NAVAN_DS_B1 8.32 154240 NAVAN_DS 118 T1 is radial. LTC control is disabled.
138 | 1867 | 1 | Transformer 154644 NAVAN_DS_NL2 27.6 154240 NAVAN_DS 118 T2 is radial. LTC control is disabled.
139 | 1867 | 1 | Transformer 154654 RICHMOND_DSB 27.6 154248 RCHMND_S_MTS 118 T1 is radial. LTC control is disabled.
140 | 1867 | 1 | Transformer 154610 CUMBRLD_DSB2 8.32 154291 CUMBRLD_DS_B 118 T2 is radial. LTC control is disabled.
141 | 1867 | 1 | Transformer 154608 CUMBRLD_DSB1 8.32 154609 CUMBRLD_DSR1 8.32 R1 is radial. LTC control is disabled.
142 | 1867 | 1 | Transformer 154661 RUSSELL_DS 8.32 154662 RUSSELL_DSR1 8.32 R1 is radial. LTC control is disabled.
143 | 1867 | 1 | Transformer 155607 COBDEN_DS 13.4 155213 COBDEN_TSX2Y 118 T3 is radial. LTC control is disabled.
144 | 1867 | 1 | Transformer 155610 MT_CHUTE_DS 12.5 155218 MT_CHUTE_DS 118 T1 is radial. LTC control is disabled.
145 | 1867 | 1 | Transformer 155699 NORTHBROOK_B 12.5 155262 NORTHBROOK 118 T1 is radial. LTC control is disabled.
146 | 1867 | 1 | Transformer 155672 DOBBIN_DS_B1 27.6 155279 DOBBIN_DS 118 T1 is radial. LTC control is disabled.
147 | 1867 | 1 | Transformer 156625 GERDAU_AW_B 44.0 156089 GERDAU_T24C 220 T2 is radial. LTC control is disabled.
148 | 1867 | 1 | Transformer 156623 GERDAU_AW_L1 44.0 156090 GERDAU_T26C 220 T4 is radial. LTC control is disabled.
149 | 1867 | 1 | Transformer 160676 TILBURY_TS 27.6 160247 TILBURY_TS 118 T1 is radial. LTC control is disabled.
150 | 1867 | 1 | Transformer 160750 EWCC_LD1 0.60 160748 EAST_WIBD_G2 13.8 T1 is radial. LTC control is disabled.
151 | 1867 | 1 | Transformer 160751 EWCC_LD2 0.60 160749 EAST_WIND_G1 13.8 T1 is radial. LTC control is disabled.
152 | 1867 | 1 | Transformer 214293 LIMERICK7 230 213741 LIM10 13.8 1 is radial. LTC control is disabled.
153 | 1867 | 1 | Transformer 213771 LMSAFEGD 13.8 213745 LIMRICK8 69.0 1 is radial. LTC control is disabled.
154 | 1867 | 1 | Transformer 213771 LMSAFEGD 13.8 213745 LIMRICK8 69.0 2 is radial. LTC control is disabled.
155 | 1867 | 1 | Transformer 213871 PCHSU343 13.8 213868 PCHBTM2 230 1 is radial. LTC control is disabled.
156 | 1867 | 1 | Transformer 221357 NEWGT030 34.5 221771 NEWGT -7 13.8 1 is radial. LTC control is disabled.
157 | 1867 | 1 | Transformer 221365 NEWGT032 34.5 221773 NEWGT -9 13.8 1 is radial. LTC control is disabled.
158 | 1867 | 1 | Transformer 221365 NEWGT032 34.5 221777 NEWGT -6 13.8 1 is radial. LTC control is disabled.
159 | 1867 | 1 | Transformer 224072 BUZZ 1W 13.8 224014 BUZZ 138 138 1 is radial. LTC control is disabled.
160 | 1867 | 1 | Transformer 224073 BUZZ 2W 13.8 224014 BUZZ 138 138 1 is radial. LTC control is disabled.
161 | 1867 | 1 | Transformer 224074 BUZZ 3W 13.8 224014 BUZZ 138 138 1 is radial. LTC control is disabled.
162 | 1867 | 1 | Transformer 224075 BUZZ 1E 13.8 224014 BUZZ 138 138 1 is radial. LTC control is disabled.
163 | 1867 | 1 | Transformer 224076 BUZZ 2E 13.8 224014 BUZZ 138 138 1 is radial. LTC control is disabled.
164 | 1867 | 1 | Transformer 224077 BUZZ 3E 13.8 224014 BUZZ 138 138 1 is radial. LTC control is disabled.
165 | 1867 | 1 | Transformer 227115 MT VICTORIA 69.0 227202 LOWMTVICTOR2 12.5 1 is radial. LTC control is disabled.
166 | 1867 | 1 | Transformer 232508 LYNCH 2 24.9 232200 LYNCH 69.0 1 is radial. LTC control is disabled.
167 | 1867 | 1 | Transformer 232610 VIENNAL1 12.5 232242 VIENNALC 69.0 1 is radial. LTC control is disabled.
168 | 1867 | 1 | Transformer 243481 05CANAL 138 246576 05CANAL L 13.8 1 is radial. LTC control is disabled.
169 | 1867 | 1 | Transformer 243491 05CORRID 138 246644 05CORRIDR 34.5 4 is radial. LTC control is disabled.
170 | 1867 | 1 | Transformer 243507 05FIFTH 138 246655 05FIFTH L 13.8 1 is radial. LTC control is disabled.
171 | 1867 | 1 | Transformer 243511 05GAY 138 246577 05GAY L 13.8 1 is radial. LTC control is disabled.
172 | 1867 | 1 | Transformer 243524 05HESS NORTH 138 246659 05HESS L 13.8 1 is radial. LTC control is disabled.
173 | 1867 | 1 | Transformer 243532 05KIRK 138 246717 05KIRK L 34.5 1 is radial. LTC control is disabled.
174 | 1867 | 1 | Transformer 243551 05OSU 138 246667 05OSU L 13.8 1 is radial. LTC control is disabled.
175 | 1867 | 1 | Transformer 243553 05POLARS 138 246641 05POLARISL 34.5 1 is radial. LTC control is disabled.
176 | 1867 | 1 | Transformer 243575 05ST.CLR 138 246619 05ST.CLR L 13.8 1 is radial. LTC control is disabled.
177 | 1867 | 1 | Transformer 243581 05TAYLOR 138 246721 05TAYLOR L 34.5 1 is radial. LTC control is disabled.
178 | 1867 | 1 | Transformer 243584 05VINE 138 246579 05VINE L 13.8 1 is radial. LTC control is disabled.
179 | 1867 | 1 | Transformer 252193 HOPPLE P 12.5 251343 08HOPPLP 69.0 1 is radial. LTC control is disabled.
180 | 1867 | 1 | Transformer 251807 EVENDL 1 34.5 251794 08EVNDL1 34.5 1 is radial. LTC control is disabled.
181 | 1867 | 1 | Transformer 312845 3WINYAH 115 311600 1WINYAH 34.5 1 is radial. LTC control is disabled.
182 | 1867 | 1 | Transformer 312845 3WINYAH 115 311600 1WINYAH 34.5 2 is radial. LTC control is disabled.
183 | 1867 | 1 | Transformer 314552 3WINDSORDP 115 313857 6WINDSORDP 230 1 is radial. LTC control is disabled.
184 | 1867 | 1 | Transformer 314115 3GAINSV1 115 314037 6GAINSVL 230 1 is radial. LTC control is disabled.
185 | 1867 | 1 | Transformer 314789 2BEARSKN 69.0 314671 4BEARSKN 138 1 is radial. LTC control is disabled.
186 | 1867 | 1 | Transformer 338472 2FRAZIER! 69.0 337358 3FRAZIER 115 1 is radial. LTC control is disabled.
187 | 1867 | 1 | Transformer 338472 2FRAZIER! 69.0 337358 3FRAZIER 115 2 is radial. LTC control is disabled.
188 | 1867 | 1 | Transformer 346072 1BLANCHET2 34.5 344147 4BLANCHET2 138 1 is radial. LTC control is disabled.
189 | 1867 | 1 | Transformer 344556 1FNLK 2 12.5 344555 4FNLK 2 138 1 is radial. LTC control is disabled.
190 | 1867 | 1 | Transformer 346075 1JC FAIR 13.8 344805 2JC FAIR 69.0 1 is radial. LTC control is disabled.
191 | 1867 | 1 | Transformer 346075 1JC FAIR 13.8 344805 2JC FAIR 69.0 2 is radial. LTC control is disabled.
192 | 1867 | 1 | Transformer 345032 2OAKWOOD 34.5 345033 5FINN 161 1 is radial. LTC control is disabled.
193 | 1867 | 1 | Transformer 345121 1VESSEL1 34.5 345120 4VESSEL 138 1 is radial. LTC control is disabled.
194 | 1867 | 1 | Transformer 345122 1VESSEL2 34.4 345120 4VESSEL 138 1 is radial. LTC control is disabled.
195 | 1867 | 1 | Transformer 348995 1CLINTN_RATA 6.90 348846 7CLINTON 345 1 is radial. LTC control is disabled.
196 | 1867 | 1 | Transformer 348997 1CLINTN_RATC 4.16 348846 7CLINTON 345 1 is radial. LTC control is disabled.
197 | 1867 | 1 | Transformer 349180 1CENTRAL 4.16 349284 2CENTRAL_AM 69.0 1 is radial. LTC control is disabled.
198 | 1867 | 1 | Transformer 372421 2SANTEE115 46.0 370390 3SANTEE! 115 3 is radial. LTC control is disabled.
199 | 1867 | 1 | Transformer 400019 NORMANDY 1 69.0 998369 49-1007 69.0 1 is radial. LTC control is disabled.
200 | 1867 | 1 | Transformer 533900 WCGS_TX1_1 13.8 997234 WOLF CREEK T 13.8 1 is radial. LTC control is disabled.
201 | 1867 | 1 | Transformer 533905 WCGS_TX7_1 13.8 997232 WOLF CREEK T 13.8 1 is radial. LTC control is disabled.
202 | 1867 | 1 | Transformer 532940 EDWRDVL1 12.5 997212 EDWARDSVIL1 115 1 is radial. LTC control is disabled.
203 | 1867 | 1 | Transformer 532948 SPRINGH1 12.5 997210 SPRNGHL TX-4 115 1 is radial. LTC control is disabled.
204 | 1867 | 1 | Transformer 533113 64TH 1 13.8 997171 64TH TX-5 69.0 1 is radial. LTC control is disabled.
205 | 1867 | 1 | Transformer 533890 NTHLAND1 12.5 997166 NORTHLAND TX 12.5 3 is radial. LTC control is disabled.
206 | 1867 | 1 | Transformer 533891 NTHLAND_TER1 4.16 997166 NORTHLAND TX 12.5 3 is radial. LTC control is disabled.
207 | 1867 | 1 | Transformer 541178 LAKERD1_TER1 7.27 997078 LAKE ROAD 1 36.0 1 is radial. LTC control is disabled.
208 | 1867 | 1 | Transformer 541179 LAKERD2_TER1 7.27 997077 LAKE ROAD 2 36.0 2 is radial. LTC control is disabled.
209 | 1867 | 1 | Transformer 541374 POSTOAK_TER1 2.40 997076 POST OAK11 34.5 11 is radial. LTC control is disabled.
210 | 1867 | 1 | Transformer 541326 APCITY_TER1 2.40 997074 APPLETON C11 34.5 11 is radial. LTC control is disabled.
211 | 1867 | 1 | Transformer 541357 METZ_TER1 2.40 997073 METZ11 34.5 11 is radial. LTC control is disabled.
212 | 1867 | 1 | Transformer 541330 GRDNCTY_TER1 4.80 997072 GARDEN CIT11 34.5 11 is radial. LTC control is disabled.
213 | 1867 | 1 | Transformer 541353 MRVL77_TER1 13.1 997069 MARYVILLE77 34.5 77 is radial. LTC control is disabled.
214 | 1867 | 1 | Transformer 541328 BRWNCRV_TER1 13.1 997068 BROWNS CU22 34.5 22 is radial. LTC control is disabled.
215 | 1867 | 1 | Transformer 541195 MRVL44_TER1 13.1 997064 MARYVILLE44 34.5 44 is radial. LTC control is disabled.
216 | 1867 | 1 | Transformer 543660 LACYGN7_TER1 6.90 997045 LACYGNE 7 69.0 7 is radial. LTC control is disabled.
217 | 1867 | 1 | Transformer 543119 BRNSW_TER1 12.5 997039 BRUNSWICK1 34.5 1 is radial. LTC control is disabled.
218 | 1867 | 1 | Transformer 543124 NORTON_TER1 12.5 997038 NORTON1 34.5 1 is radial. LTC control is disabled.
219 | 1867 | 1 | Transformer 543125 S.OTWA1_TER1 12.5 997037 SOUTH OTTA1 34.5 1 is radial. LTC control is disabled.
220 | 1867 | 1 | Transformer 543122 S.OTTWA_TER1 12.5 997036 SOUTH OTTA4 34.5 4 is radial. LTC control is disabled.
221 | 1867 | 1 | Transformer 543083 PAOLA6_TER1 7.62 997035 PAOLA6 34.5 6 is radial. LTC control is disabled.
222 | 1867 | 1 | Transformer 543113 PAOLA7_TER1 7.62 997034 PAOLA7 34.5 7 is radial. LTC control is disabled.
223 | 1867 | 1 | Transformer 543115 PLSTVL2_TER1 7.62 997033 PLEASANT V2 34.5 2 is radial. LTC control is disabled.
224 | 1867 | 1 | Transformer 543161 BLUSPRG1 12.5 997032 BLUE SPRINGS 12.5 1 is radial. LTC control is disabled.
225 | 1867 | 1 | Transformer 543162 BLUSPRG_TER1 4.00 997032 BLUE SPRINGS 12.5 1 is radial. LTC control is disabled.
226 | 1867 | 1 | Transformer 543151 CORDER_TER1 7.20 997031 CORDER1 12.5 1 is radial. LTC control is disabled.
227 | 1867 | 1 | Transformer 543155 WHGNSVL_TER1 7.20 997029 WEST HIGGI1 12.5 1 is radial. LTC control is disabled.
228 | 1867 | 1 | Transformer 599891 OKLAUN 7 345 590001 OKLEHV24 138 1 is radial. LTC control is disabled.
229 | 1867 | 1 | Transformer 627067 W.BRCH TAP8 69.0 629096 W.BRCH 9 34.5 1 is radial. LTC control is disabled.
230 | 1867 | 1 | Transformer 631091 BEVERLY5 161 629097 BEVERL19 34.5 1 is radial. LTC control is disabled.
231 | 1867 | 1 | Transformer 629150 BELMOND 34.5 630469 BELMNDJ8 69.0 1 is radial. LTC control is disabled.
232 | 1867 | 1 | Transformer 680575 YORK T74D 34.5 631068 YORK 5 161 1 is radial. LTC control is disabled.
233 | 1867 | 1 | Transformer 640241 JOHN.1 9 34.5 640014 JOHN.1 G 6.90 1 is radial. LTC control is disabled.
234 | 1867 | 1 | Transformer 652227 FLANDR19 12.5 652228 FLANDRU9 12.5 1 is radial. LTC control is disabled.
235 | 1867 | 1 | Transformer 659350 BISON___-GE7 115 659351 BISON___-GE4 230 1 is radial. LTC control is disabled.
236 | 1867 | 1 | Transformer 669847 PRKDL 9 12.5 668040 PARKDAL7 110 5 is radial. LTC control is disabled.
237 | 1867 | 1 | Transformer 693716 CRNBRY F244 24.9 699778 CRANBERY 115 1 is radial. LTC control is disabled.
238 | 1867 | 1 | Transformer 698276 BROOKS CRNRS 24.9 698391 BRC 69 69.0 1 is radial. LTC control is disabled.
239 | 1867 | 1 | Transformer 698455 GREVES5 13.8 699496 GREVES T 138 1 is radial. LTC control is disabled.
240 | 1863 | 1 | TAP 100230 LARRABEE RD 115 999992 LARRABEE T1 115 1 Desired voltage range=0.0080 [1.0390:1.0470] is too small comparing to step=0.0062. Expanded to [1.0383:1.0477]
241 | 1863 | 1 | TAP 108902 INDSTRL PK_D 12.5 108550 INDSTRL PARK 34.5 1 Desired voltage range=0.0400 [1.0000:1.0400] is too small comparing to step=0.0333. Expanded to [0.9950:1.0450]
242 | 1863 | 1 | TAP 109290 PUDDNG HIL_D 12.5 108554 PUDDING HILL 34.5 1 Desired voltage range=0.0400 [1.0000:1.0400] is too small comparing to step=0.0333. Expanded to [0.9950:1.0450]
243 | 1863 | 1 | TAP 108911 BURKE_DIST 12.5 108556 BURKE MOUNTN 34.5 1 Desired voltage range=0.0400 [1.0000:1.0400] is too small comparing to step=0.0333. Expanded to [0.9950:1.0450]
244 | 1863 | 1 | TAP 108937 VIL HYDE PRK 12.5 108559 V OF HYDE PK 34.5 1 Desired voltage range=0.0400 [1.0000:1.0400] is too small comparing to step=0.0333. Expanded to [0.9950:1.0450]
245 | 1863 | 1 | TAP 109100 PLAINFIELD_D 12.5 108634 PLAINFIELD 34.5 1 Desired voltage range=0.0400 [1.0000:1.0400] is too small comparing to step=0.0333. Expanded to [0.9950:1.0450]
246 | 1863 | 1 | TAP 109022 HOUSTON1 12.5 108702 HOUSTON 34.5 1 Desired voltage range=0.0400 [1.0000:1.0400] is too small comparing to step=0.0333. Expanded to [0.9950:1.0450]
247 | 1863 | 1 | TAP 109024 HOUSTON2 12.5 108702 HOUSTON 34.5 1 Desired voltage range=0.0400 [1.0000:1.0400] is too small comparing to step=0.0333. Expanded to [0.9950:1.0450]
248 | 1863 | 1 | TAP 109036 LODGE_D 12.5 108703 LODGE 34.5 1 Desired voltage range=0.0400 [1.0000:1.0400] is too small comparing to step=0.0333. Expanded to [0.9950:1.0450]
249 | 1863 | 1 | TAP 109026 WILKINS_D1 12.5 108708 STOWE35 34.5 1 Desired voltage range=0.0400 [1.0000:1.0400] is too small comparing to step=0.0333. Expanded to [0.9950:1.0450]
250 | 1863 | 1 | TAP 109032 WILKINS_D2 12.5 108708 STOWE35 34.5 1 Desired voltage range=0.0400 [1.0000:1.0400] is too small comparing to step=0.0333. Expanded to [0.9950:1.0450]
251 | 1863 | 1 | TAP 111313 WING LANE T2 13.2 111273 WING LANE 115 1 Desired voltage range=0.0126 [1.0287:1.0413] is too small comparing to step=0.0102. Expanded to [1.0273:1.0427]
252 | 1863 | 1 | TAP 122228 CAMPVILLE 27.6 120398 CAMPVILLE 115 1 Desired voltage range=0.0070 [1.0350:1.0420] is too small comparing to step=0.0063. Expanded to [1.0338:1.0432]
253 | 1863 | 1 | TAP 122228 CAMPVILLE 27.6 120398 CAMPVILLE 115 2 Desired voltage range=0.0070 [1.0350:1.0420] is too small comparing to step=0.0052. Expanded to [1.0346:1.0424]
254 | 1938 | 1 | Reg bus is not a generator for Switch Shunt Mode 3 - discrete shunt at bus [135081 Q644_COL1 34.5 102 NYISO 165 NYSEG ME ] control MVAR output at remote plant [135081 Q644_COL1 34.5 ]. Ffixed
255 | 1945 | 1 | Reg plant Q range too small for Switch Shunt Mode 3 - discrete shunt at bus [152860 PRINCE2_CTS 34.5 103 IESO 1102 NORTH-EAST ] control MVAR output at remote plant [152860 PRINCE2_CTS 34.5 ]. Ffixed
256 | 1945 | 1 | Reg plant Q range too small for Switch Shunt Mode 3 - discrete shunt at bus [158865 SUMERHA_345 34.5 103 IESO 1108 SOUTH-WEST ] control MVAR output at remote plant [158865 SUMERHA_345 34.5 ]. Ffixed
257 | 1945 | 1 | Reg plant Q range too small for Switch Shunt Mode 3 - discrete shunt at bus [160611 PBURWELL_345 34.5 103 IESO 1110 WEST ] control MVAR output at remote plant [160611 PBURWELL_345 34.5 ]. Ffixed
258 | 1945 | 1 | Reg plant Q range too small for Switch Shunt Mode 3 - discrete shunt at bus [160785 GOSFIELD_345 34.5 103 IESO 1110 WEST ] control MVAR output at remote plant [160785 GOSFIELD_345 34.5 ]. Ffixed
259 | 1826 | 2 | Switched shunt at bus [121456 GLENBROOK_C1 115 101 116 ] could not reach target during initial solution (possibly oscillating).
260 | 1826 | 2 | Switched shunt at bus [121458 GLENBROOK_C2 115 101 116 ] could not reach target during initial solution (possibly oscillating).
261 | 1009 | 2 | Bus number [243760] not found | C:\Users\03419\Desktop\2022 Gas Study\2022 series_sub_EKPC-LGEE.sub | 6
262 | 4040 | 1 | Subsystem EKPC_EXT has total zero participation factor.
263 | 5702 | 1 | No participating buses can be scaled for EKPC_EXT . Using uniform distr - Found 1 online buses
264 | 4040 | 1 | Subsystem EKPC has total zero participation factor.
265 | 5702 | 1 | No participating buses can be scaled for EKPC . Using uniform distr - Found 579 online buses
266 | 4040 | 1 | Subsystem LGEE has total zero participation factor.
267 | 5702 | 1 | No participating buses can be scaled for LGEE . Using uniform distr - Found 999 online buses
268 | 1009 | 2 | Bus number [243003] not found | C:\Users\03419\Desktop\2022 Gas Study\2022 series_sub_EKPC-LGEE.sub | 37
269 | 1009 | 2 | Bus number [243746] not found | C:\Users\03419\Desktop\2022 Gas Study\2022 series_sub_EKPC-LGEE.sub | 84
270 | 1009 | 2 | Bus number [243755] not found | C:\Users\03419\Desktop\2022 Gas Study\2022 series_sub_EKPC-LGEE.sub | 86
271 | 1009 | 2 | Bus number [243757] not found | C:\Users\03419\Desktop\2022 Gas Study\2022 series_sub_EKPC-LGEE.sub | 87
272 | 1009 | 2 | Bus number [243760] not found | C:\Users\03419\Desktop\2022 Gas Study\2022 series_sub_EKPC-LGEE.sub | 90
273 | 1009 | 2 | Bus number [243761] not found | C:\Users\03419\Desktop\2022 Gas Study\2022 series_sub_EKPC-LGEE.sub | 91
274 | 1009 | 2 | Bus number [244603] not found | C:\Users\03419\Desktop\2022 Gas Study\2022 series_sub_EKPC-LGEE.sub | 99
275 | 1009 | 2 | Bus number [244629] not found | C:\Users\03419\Desktop\2022 Gas Study\2022 series_sub_EKPC-LGEE.sub | 101
276 | 1009 | 2 | Bus number [247414] not found | C:\Users\03419\Desktop\2022 Gas Study\2022 series_sub_EKPC-LGEE.sub | 112
277 | 4040 | 1 | Subsystem AEP has total zero participation factor.
278 | 5702 | 1 | No participating buses can be scaled for AEP . Using uniform distr - Found 75 online buses
279 | 1009 | 2 | Bus number [248003] not found | C:\Users\03419\Desktop\2022 Gas Study\2022 series_sub_EKPC-LGEE.sub | 121
280 | 4040 | 1 | Subsystem OVEC has total zero participation factor.
281 | 5702 | 1 | No participating buses can be scaled for OVEC . Using uniform distr - Found 4 online buses
282 | 1009 | 2 | Bus number [253038] not found | C:\Users\03419\Desktop\2022 Gas Study\2022 series_sub_EKPC-LGEE.sub | 138
283 | 1009 | 2 | Bus number [253110] not found | C:\Users\03419\Desktop\2022 Gas Study\2022 series_sub_EKPC-LGEE.sub | 145
284 | 4040 | 1 | Subsystem DPL has total zero participation factor.
285 | 5702 | 1 | No participating buses can be scaled for DPL . Using uniform distr - Found 12 online buses
286 | 1009 | 2 | Bus number [250035] not found | C:\Users\03419\Desktop\2022 Gas Study\2022 series_sub_EKPC-LGEE.sub | 173
287 | 1009 | 2 | Bus number [251814] not found | C:\Users\03419\Desktop\2022 Gas Study\2022 series_sub_EKPC-LGEE.sub | 209
288 | 1009 | 2 | Bus number [252089] not found | C:\Users\03419\Desktop\2022 Gas Study\2022 series_sub_EKPC-LGEE.sub | 215
289 | 1009 | 2 | Bus number [252090] not found | C:\Users\03419\Desktop\2022 Gas Study\2022 series_sub_EKPC-LGEE.sub | 216
290 | 1009 | 2 | Bus number [252091] not found | C:\Users\03419\Desktop\2022 Gas Study\2022 series_sub_EKPC-LGEE.sub | 217
291 | 1009 | 2 | Bus number [252114] not found | C:\Users\03419\Desktop\2022 Gas Study\2022 series_sub_EKPC-LGEE.sub | 218
292 | 1009 | 2 | Bus number [252115] not found | C:\Users\03419\Desktop\2022 Gas Study\2022 series_sub_EKPC-LGEE.sub | 219
293 | 1009 | 2 | Bus number [252189] not found | C:\Users\03419\Desktop\2022 Gas Study\2022 series_sub_EKPC-LGEE.sub | 220
294 | 1009 | 2 | Bus number [252229] not found | C:\Users\03419\Desktop\2022 Gas Study\2022 series_sub_EKPC-LGEE.sub | 221
295 | 1009 | 2 | Bus number [252271] not found | C:\Users\03419\Desktop\2022 Gas Study\2022 series_sub_EKPC-LGEE.sub | 222
296 | 4040 | 1 | Subsystem DEOK has total zero participation factor.
297 | 5702 | 1 | No participating buses can be scaled for DEOK . Using uniform distr - Found 59 online buses
298 | 4040 | 1 | Subsystem TVA has total zero participation factor.
299 | 5702 | 1 | No participating buses can be scaled for TVA . Using uniform distr - Found 49 online buses
300 | 3168 | 2 | END statement may cause portions of the file to be skipped | C:\Users\03419\Desktop\2022 Gas Study\2022 series_sub_EKPC-LGEE.sub | 283
301 | 1100 | 0 | Read in 283 records from File [C:\Users\03419\Desktop\2022 Gas Study\2022 series_sub_EKPC-LGEE.sub] (Lev=1)
302 | 3083 | 2 | Duplicate Contingency Names are defined. Modifying name of duplicate - adding _DupX to name to make unique. Duplicate name was changed to EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A_Dup1 | C:\Users\03419\Desktop\2022 Gas Study\Option 3A N-1-1 con file.con | 200
303 | 3168 | 2 | END statement may cause portions of the file to be skipped | C:\Users\03419\Desktop\2022 Gas Study\Option 3A N-1-1 con file.con | 285
304 | 1100 | 0 | Read in 285 records from File [C:\Users\03419\Desktop\2022 Gas Study\Option 3A N-1-1 con file.con] (Lev=1)
305 | 3168 | 2 | END statement may cause portions of the file to be skipped | C:\Users\03419\Desktop\2022 Gas Study\Option 3A N-1-1 con file.con | 285
306 | 1100 | 0 | Read in 285 records from File [C:\Users\03419\Desktop\2022 Gas Study\Option 3A N-1-1 con file.con] (Lev=1)
307 | 3168 | 2 | END statement may cause portions of the file to be skipped | C:\Users\03419\Desktop\2022 Gas Study\2022 series_mon_EKPC-LGEE.mon | 17
308 | 1100 | 0 | Read in 17 records from File [C:\Users\03419\Desktop\2022 Gas Study\2022 series_mon_EKPC-LGEE.mon] (Lev=1)
309 | 5702 | 1 | No participating buses can be scaled for EKPC_EXT . Using uniform distr - Found 1 online buses
310 | 5702 | 1 | No participating buses can be scaled for OVEC . Using uniform distr - Found 4 online buses
311 | 5702 | 1 | No participating buses can be scaled for DPL . Using uniform distr - Found 12 online buses

## CaseSum
EKPC LF case summary[TARA Ver 2201.2.0.0 64-bit - Sat Aug 13 07:55:40 2022]
Loadflow Case: C:\Users\03419\Desktop\2022 Gas Study\Alt 3A\2032S_gas_alt#3a_212mw.raw
Study Data File: C:\Users\03419\Desktop\2022 Gas Study\2022 series_sub_EKPC-LGEE.sub
Contingency File: C:\Users\03419\Desktop\2022 Gas Study\Option 3A N-1-1 con file.con (total 37 contingencies)/ First-Level Contingency File: C:\Users\03419\Desktop\2022 Gas Study\Option 3A N-1-1 con file.con (total 37 contingencies)
Monitor File: C:\Users\03419\Desktop\2022 Gas Study\2022 series_mon_EKPC-LGEE.mon
Exclude File: not provided
Pre/Post Contingency PAR Adjustment: Adjusted/Fixed
ConvStatus | Solved
Iterations | 16
busPmismMax | 0.0371
Buses | 95955
LoadBuses | 86086
GenBuses | 8939
SwingBuses | 9
ShutDown | 921
Loads | 52162
Machines | 10843
NonTranBrn | 119265
Transformers | 34005
Phase Shifters | 117
Two-term.DC | 40
SwitcShunts | 10551
TransImpdCorrTables | 50
Multi-term DC | 0
MultiSection lines | 40
Interarea Transfers | 0
FACTS control devices | 46
Total Areas | 134
Total Zones | 746
Swing bus dispatch summary
Bus# | Bus Name | Volt | Area | AreaName | Zon | ZoneName | curPGen | MinPGen | MaxPGen | curQGen | MinQGen | MaxQGen | VltSched
180700 | EQUILIBRE | 735 | 104 | TE | 1144 | STLAUREN | 1.41 | -50 | 50 | 0 | -5 | 5 | 1
181436 | OTTOHD | 120 | 104 | TE | 1151 | INTERLG | -69.02 | -100 | 100 | 75.03 | -61.97 | 75 | 1.0235
195205 | BBK B1 | 230 | 108 | NF | 185 | Zon_185 | 376.86 | -1000 | 1000 | -66.41 | -600 | 600 | 1
364003 | 1BR FERRY N3 | 22 | 347 | TVA | 1360 | MUSCLE SHOAL | 1287.33 | 1256 | 1302.5 | 139.28 | 50 | 278.9 | 1.04
590002 | OKLAUN1G | 24 | 998 | ERCOT | 998 | Zon_998 | 401.61 | 175 | 670 | 87.82 | -280 | 400 | 1.035
590012 | MOSES3 G | 24 | 998 | ERCOT | 998 | Zon_998 | 762.16 | 463 | 765 | 216.63 | -200 | 275 | 1.032
599956 | PNM-DC7 | 345 | 999 | WECC | 999 | WECC | 451.2 | -1000 | 1000 | -133.04 | -500 | 500 | 1
652585 | NB WEST4 | 230 | 997 | WBDC-WECC | 1603 | WAPA_1603 | 173.56 | -250 | 250 | -13 | -250 | 250 | 1.03
669732 | KETTLE3G | 13.8 | 667 | MH | 1649 | MHRURALN | 100.4 | 6 | 102 | 34.18 | -63 | 63 | 1.01

## LogFile
*** Created [C:\Users\03419\Desktop\2022 Gas Study\temp\taralog.txt] Current directory - [C:\Users\03419\Desktop\2022 Gas Study\temp]
***** PowerGEM Log Utility. File=C:\Users\03419\Desktop\2022 Gas Study\temp\taralog.txt. Created Sat Aug 13 07:55:37 2022. TARA Ver 2201.2.0.0 64-bit
Select main menu function(L1): [ %txt] Using TXT format
[ opt] = Selected Function 10 - Options - TARA analysis options
Select data category:(L2): [ cont] = Selected Function 1 - CONTING - Contingency analysis option
**** Current **** Contingency analysis options:
1: monBranRatingBase 1 // Base case rating (1-A;2-B;3-C;4-D)
2: monBranRatingCont 2 // Contingency rating (1-A;2-B;3-C;4-D)
3: monBranRatingMultBase 100.00 // Base case rating multipliers
4: monBranRatingMultCont 100.00 // Contingency rating multipliers
5: contChanCutOffMW 0.1 // MW cutoff to ignore constraints if cont.flow doesn't changes from the base case more than
6: contChanCutOffPercent 10.0 // Rating %% cutoff to ignore if cont.flow changes from the base case is less than
7: PAR_AdjEnabledContAnal 1 // Phase shifter model for the base case (0-fixed angle;1-control flow), always fixed in contingency
8: adjustRatingMVA 0 // Adjust branch MW rating based on MVAR flow (DC analysis)
9: limitTypeLine 0 // Use AMP (=0) or MVA (1) limit to check lines violation in AC mode
10: limitTypeTran 1 // Use AMP (=0) or MVA (1) limit to check transformer violation in AC mode
11: voltMinChange 0.0010 // Voltage change cutoff in PU to ignore voltage violations with change from the base case is smaller
12: numContMaxAlloc 20000 // Max number of contingencies
13: numEventsAlloc 100000 // Max number of contingency events
14: numDispEventAlloc 100000 // Max number of generation redispatch events
15: numLFgatesMaxAlloc 30000 // Max number of flowgates
16: maxFgateBranches 70 // Max number of branches (events) per flowgate
17: mulSecPrintMode 1 // Multi-section line modeling (0-ignore;1-honor)
18: smartCutOff 0 // Use Smart cutoff based on Max conting impact using base case and conting rating difference (0-no;1-yes)
19: maxExcludesAlloc 10000 // Max number of exclude records
20: showConAnalLFLog 0 // Show LF convergence during ACCONT
21: MAXOUTAGES 1000 // Maximum number of outages
22: maxORAFlowResults 2000000 // Maximum number of ORA or N-1-1 results to report
23: ACCONTRepeatSolution 0 // If first AC solution failed, repeat with alternative Flat/Hot start(0-no,1-yes),2-limit to the best iteration
24: showNotMappedContEvents 1 // When generating contingency file, show not mapped event(0-no,1-yes)
25: monBranRatingEnAdd1 0 // Enable first additional rating reporting (0-no,1-yes)
26: monBranRatingEnAdd2 0 // Enable second additional rating reporting (0-no,1-yes)
27: monBranRatingAdd1 3 // Additional Rating 1 (1-A;2-B;3-C;4-D)
28: monBranRatingAdd2 3 // Additional Rating 2 (1-A;2-B;3-C;4-D)
29: monBranRatingMultAdd1 100.00 // Additional Rating 1 multiplier
30: monBranRatingMultAdd2 100.00 // Additional Rating 2 multiplier
31: LoadingCutOff 0.00 // Loading cutoff in percent for displaying cont analysis flow results
32: showAllHighPreSCD 0 // Show SCD result if pre-SCD above cutoff but post-SCD below
33: N11MODE 0 // Run in N-1+Application Mode
34: multiCoreN1 0 // Run in N-1 ACCont in multi-core mode? [0-No, 1-Yes]
35: numLowestLoading 5 // Max number of lowest loading results to report
36: VoltLimAdder 0.00000 // Add this to voltage limit to expand or limit hi/low voltage viol results
37: StudyFiles 0 // Show Names of Input Files on all reports
38: MonConMode 1 // Select Mon/Con mode (1:Regular, 2:Flowgate, 3:Voltgate, 4:Flowgate & Voltgate
39: MaxMonConMode 100000 // Maximum Number of mon/con mode entries
40: keepDuplicates 1 // Keep contingency even if exact duplicate? [0=no, 1=yes]
41: correctiveSwitchingMode 0 // Run in corrective switching mode? [0=no, 1=yes]
42: lodfCutoff 0.01000 // Cutoff for LODF report (absolute value)
43: lodfImpCutoff 1.00 // MW cutoff for LODF Impact report (lodf*(event rating))
44: maxFgEventTotal 100000 // Max number of all branches and events for all flowgatesflowgate
45: maxEvPerCont 70 // Max number of events (events) per contingency
46: maxSPSLogic 10000 // Max number of SPS logic elements
47: maxInjGroups 500 // Max number of SPS AUX Injections Groups
48: maxSPSInterfaces 1000 // Max number of SPS AUX Interfaces
49: co_mode 0 // Cascading mode, 0=no, 1=yes
50: co_branchoutage 1 // Trip Overloaded Branches in Cascading Outage, 0=no, 1=yes
51: co_genoutage 1 // Trip Generators in Cascading Outage, 0=no, 1=yes
52: co_genterminalbus 0 // Trip Generators with low voltage violation at generator terminal bus, 0=no, 1=yes
53: co_loadoutage 1 // Trip Loads in Cascading Outage, 0=no, 1=yes
54: co_maxlevel 10 // Maximum cascading outage test level
55: saveCOCases 0 // Save a case for each cascading step case
56: COSaveDirectory [] // Folder to save each cascading outage case
57: kVLayer12_Volt 100.0 // Voltage between Layer 1 and Layer 2
58: kVLayer23_Volt 230.0 // Voltage between Layer 2 and Layer 3
59: kVLayer34_Volt 345.0 // Voltage between Layer 3 and Layer 4
60: kVLayer45_Volt 500.0 // Voltage between Layer 4 and Layer 5
61: kVLayer1_LDCutoff 115.0 // Layer 1 RelayLoadability Percent
62: kVLayer2_LDCutoff 115.0 // Layer 2 RelayLoadability Percent
63: kVLayer3_LDCutoff 115.0 // Layer 3 RelayLoadability Percent
64: kVLayer4_LDCutoff 115.0 // Layer 4 RelayLoadability Percent
65: kVLayer5_LDCutoff 115.0 // Layer 5 RelayLoadability Percent
66: zeroRatingCutoff 0.000100 // If rating is below this, set rating to 9999
67: saveN11Cases 0 // Save a case for each N-1-1 first-level case
68: N11SaveDirectory [] // Folder to save each N-1-1 first-level case
69: acVerifyFgate 0 // Enable flowgate AC verification (0-No;1-Yes)
70: useContingencyComments 0 // Use Comments in contingency file in contingency reporting
71: ignoreEnd2Exit 0 // Ignore END statement to exit reading sub mon con exc files (0-No, 1-Yes)
72: nearSyskVLayer1 5 // Subsystem proximity screen 1st kV Layer
73: nearSyskVLayer2 5 // Subsystem proximity screen 2nd kV Layer
74: nearSyskVLayer3 5 // Subsystem proximity screen 3rd kV Layer
75: nearSyskVLayer4 5 // Subsystem proximity screen 4rd kV Layer
76: nearSyskVLayer5 5 // Subsystem proximity screen 5th kV Layer
77: nearSyskVLayer12_Volt 100.0 // Subsystem proximity screen Voltage between Layer 1 and Layer 2
78: nearSyskVLayer23_Volt 230.0 // Subsystem proximity screen Voltage between Layer 2 and Layer 3
79: nearSyskVLayer34_Volt 345.0 // Subsystem proximity screen Voltage between Layer 3 and Layer 4
80: nearSyskVLayer45_Volt 500.0 // Subsystem proximity screen Voltage between Layer 4 and Layer 5
81: nearSysScrnMod 0 // Subsystem Screening for nearby contingencies (1st and 2nd)
82: nearSyskVCutoff 0.00 // Subsystem proximity Specify kV Cutoff
83: nearSysApplykVCutoffOption 0 // Subsystem proximity [0-one side only, 1-both sides]
84: nearByLayerSubSysName [Undefined] // - Subsystem Name for proximity contingency layer screen
Specify option name (or number) and value : [ N11Mode][ 1]
Specify option name (or number) and value : [ 0]
**** New **** Contingency analysis options:
1: monBranRatingBase 1 // Base case rating (1-A;2-B;3-C;4-D)
2: monBranRatingCont 2 // Contingency rating (1-A;2-B;3-C;4-D)
3: monBranRatingMultBase 100.00 // Base case rating multipliers
4: monBranRatingMultCont 100.00 // Contingency rating multipliers
5: contChanCutOffMW 0.1 // MW cutoff to ignore constraints if cont.flow doesn't changes from the base case more than
6: contChanCutOffPercent 10.0 // Rating %% cutoff to ignore if cont.flow changes from the base case is less than
7: PAR_AdjEnabledContAnal 1 // Phase shifter model for the base case (0-fixed angle;1-control flow), always fixed in contingency
8: adjustRatingMVA 0 // Adjust branch MW rating based on MVAR flow (DC analysis)
9: limitTypeLine 0 // Use AMP (=0) or MVA (1) limit to check lines violation in AC mode
10: limitTypeTran 1 // Use AMP (=0) or MVA (1) limit to check transformer violation in AC mode
11: voltMinChange 0.0010 // Voltage change cutoff in PU to ignore voltage violations with change from the base case is smaller
12: numContMaxAlloc 20000 // Max number of contingencies
13: numEventsAlloc 100000 // Max number of contingency events
14: numDispEventAlloc 100000 // Max number of generation redispatch events
15: numLFgatesMaxAlloc 30000 // Max number of flowgates
16: maxFgateBranches 70 // Max number of branches (events) per flowgate
17: mulSecPrintMode 1 // Multi-section line modeling (0-ignore;1-honor)
18: smartCutOff 0 // Use Smart cutoff based on Max conting impact using base case and conting rating difference (0-no;1-yes)
19: maxExcludesAlloc 10000 // Max number of exclude records
20: showConAnalLFLog 0 // Show LF convergence during ACCONT
21: MAXOUTAGES 1000 // Maximum number of outages
22: maxORAFlowResults 2000000 // Maximum number of ORA or N-1-1 results to report
23: ACCONTRepeatSolution 0 // If first AC solution failed, repeat with alternative Flat/Hot start(0-no,1-yes),2-limit to the best iteration
24: showNotMappedContEvents 1 // When generating contingency file, show not mapped event(0-no,1-yes)
25: monBranRatingEnAdd1 0 // Enable first additional rating reporting (0-no,1-yes)
26: monBranRatingEnAdd2 0 // Enable second additional rating reporting (0-no,1-yes)
27: monBranRatingAdd1 3 // Additional Rating 1 (1-A;2-B;3-C;4-D)
28: monBranRatingAdd2 3 // Additional Rating 2 (1-A;2-B;3-C;4-D)
29: monBranRatingMultAdd1 100.00 // Additional Rating 1 multiplier
30: monBranRatingMultAdd2 100.00 // Additional Rating 2 multiplier
31: LoadingCutOff 0.00 // Loading cutoff in percent for displaying cont analysis flow results
32: showAllHighPreSCD 0 // Show SCD result if pre-SCD above cutoff but post-SCD below
33: N11MODE 1 // Run in N-1+Application Mode
34: multiCoreN1 0 // Run in N-1 ACCont in multi-core mode? [0-No, 1-Yes]
35: numLowestLoading 5 // Max number of lowest loading results to report
36: VoltLimAdder 0.00000 // Add this to voltage limit to expand or limit hi/low voltage viol results
37: StudyFiles 0 // Show Names of Input Files on all reports
38: MonConMode 1 // Select Mon/Con mode (1:Regular, 2:Flowgate, 3:Voltgate, 4:Flowgate & Voltgate
39: MaxMonConMode 100000 // Maximum Number of mon/con mode entries
40: keepDuplicates 1 // Keep contingency even if exact duplicate? [0=no, 1=yes]
41: correctiveSwitchingMode 0 // Run in corrective switching mode? [0=no, 1=yes]
42: lodfCutoff 0.01000 // Cutoff for LODF report (absolute value)
43: lodfImpCutoff 1.00 // MW cutoff for LODF Impact report (lodf*(event rating))
44: maxFgEventTotal 100000 // Max number of all branches and events for all flowgatesflowgate
45: maxEvPerCont 70 // Max number of events (events) per contingency
46: maxSPSLogic 10000 // Max number of SPS logic elements
47: maxInjGroups 500 // Max number of SPS AUX Injections Groups
48: maxSPSInterfaces 1000 // Max number of SPS AUX Interfaces
49: co_mode 0 // Cascading mode, 0=no, 1=yes
50: co_branchoutage 1 // Trip Overloaded Branches in Cascading Outage, 0=no, 1=yes
51: co_genoutage 1 // Trip Generators in Cascading Outage, 0=no, 1=yes
52: co_genterminalbus 0 // Trip Generators with low voltage violation at generator terminal bus, 0=no, 1=yes
53: co_loadoutage 1 // Trip Loads in Cascading Outage, 0=no, 1=yes
54: co_maxlevel 10 // Maximum cascading outage test level
55: saveCOCases 0 // Save a case for each cascading step case
56: COSaveDirectory [] // Folder to save each cascading outage case
57: kVLayer12_Volt 100.0 // Voltage between Layer 1 and Layer 2
58: kVLayer23_Volt 230.0 // Voltage between Layer 2 and Layer 3
59: kVLayer34_Volt 345.0 // Voltage between Layer 3 and Layer 4
60: kVLayer45_Volt 500.0 // Voltage between Layer 4 and Layer 5
61: kVLayer1_LDCutoff 115.0 // Layer 1 RelayLoadability Percent
62: kVLayer2_LDCutoff 115.0 // Layer 2 RelayLoadability Percent
63: kVLayer3_LDCutoff 115.0 // Layer 3 RelayLoadability Percent
64: kVLayer4_LDCutoff 115.0 // Layer 4 RelayLoadability Percent
65: kVLayer5_LDCutoff 115.0 // Layer 5 RelayLoadability Percent
66: zeroRatingCutoff 0.000100 // If rating is below this, set rating to 9999
67: saveN11Cases 0 // Save a case for each N-1-1 first-level case
68: N11SaveDirectory [] // Folder to save each N-1-1 first-level case
69: acVerifyFgate 0 // Enable flowgate AC verification (0-No;1-Yes)
70: useContingencyComments 0 // Use Comments in contingency file in contingency reporting
71: ignoreEnd2Exit 0 // Ignore END statement to exit reading sub mon con exc files (0-No, 1-Yes)
72: nearSyskVLayer1 5 // Subsystem proximity screen 1st kV Layer
73: nearSyskVLayer2 5 // Subsystem proximity screen 2nd kV Layer
74: nearSyskVLayer3 5 // Subsystem proximity screen 3rd kV Layer
75: nearSyskVLayer4 5 // Subsystem proximity screen 4rd kV Layer
76: nearSyskVLayer5 5 // Subsystem proximity screen 5th kV Layer
77: nearSyskVLayer12_Volt 100.0 // Subsystem proximity screen Voltage between Layer 1 and Layer 2
78: nearSyskVLayer23_Volt 230.0 // Subsystem proximity screen Voltage between Layer 2 and Layer 3
79: nearSyskVLayer34_Volt 345.0 // Subsystem proximity screen Voltage between Layer 3 and Layer 4
80: nearSyskVLayer45_Volt 500.0 // Subsystem proximity screen Voltage between Layer 4 and Layer 5
81: nearSysScrnMod 0 // Subsystem Screening for nearby contingencies (1st and 2nd)
82: nearSyskVCutoff 0.00 // Subsystem proximity Specify kV Cutoff
83: nearSysApplykVCutoffOption 0 // Subsystem proximity [0-one side only, 1-both sides]
84: nearByLayerSubSysName [Undefined] // - Subsystem Name for proximity contingency layer screen
Select data category:(L2): [ 0]
Select main menu function(L1): [ opt] = Selected Function 10 - Options - TARA analysis options
Select data category:(L2): [ ora] = Selected Function 8 - ORA - Outage evaluation options
**** Current **** ORA Options
1: ORA_ON -1 // Enable ORA analysis (Transmission Outage Request Analyzer) (0-no,1-yes)
2: ORA_mode_BaseCase 3 // ORA Base case setup mode (1- N-1, no redispatch, 2-SCRD, 3 - SCED)
3: ORA_mode_Study 3 // ORA study analysis mode (1- N-1, no redispatch, 2-SCRD, 3 - SCED)
4: useContReduction 1 // Use contingency reduction for outage analysis (0-no,1-yes)
5: mwContReductionCutoff 15.00 // MW impact cutoff for determining nearness of contingency and outage
6: percentContReductionCutoff 99.00 // Percent change cutoff for determining nearness of contingency and outage
7: ORA_runOpportunityWindow 0 // Find Outage Opportunity Window? (0-no,1-yes)
8: ComparativeACMode 0 // Enable Comparative AC Contingency Analysis (0- no (DC only), 1- yes (run AC))
9: acScreenPctLdCutoff 90.00 // AC Contingency Screen Cutoff - % Branch Loading Cutoff
10: acScreenMWCutoff 5.00 // AC Contingency Screen Cutoff - Flow Change in MW
11: acScreenPctRatCutoff 2.00 // AC Contingency Screen Cutoff - Flow Change as % of Branch Rating
12: comparePctLdCutoff 90.00 // Comparative Flow Cutoff - % Branch Loading Cutoff
13: compareMWCutoff 5.00 // Comparative Flow Cutoff - Flow Change in MW
14: comparePctRatCutoff 2.00 // Comparative Flow Cutoff - Flow Change as % of Branch Rating
15: voltPrePostCutoff 0.0020 // Comparative Voltage Cutoff - Diff between post-cont and pre-cont
16: voltCompareCutoff 0.0020 // Comparative Voltage Cutoff - Diff between post cont with & without outage
17: shadowPriceChangeCutoff 30.0000 // Comparative Shadow Price value change cutoff - Diff with & without outage
18: shadowPricePctChangeCutoff 25.0000 // Comparative Shadow Price perchange change cutoff - Change as % of max(pre,post) with & without outage
19: trendingChangeMWCutoff 100.0000 // Outage trending status cutoff - Flow Change in MW
20: trendingPercentLoadingChangeCutoff 20.0000 // Outage trending status cutoff - Flow Change as % of Branch Rating
21: trendingShadowPriceChangeCutoff 1000.0000 // Outage trending status cutoff - Change in shadow price
22: conflPctLdCutoff 0.00 // Conflicting Cont Flow Cutoff - % Branch Loading Cutoff
23: conflMWCutoff 0.00 // Conflicting Cont Flow Cutoff - Flow Change in MW
24: conflPctRatCutoff 0.00 // Conflicting Cont Flow Cutoff - Flow Change as % of Branch Rating
25: consPerMonBran 10000 // Number of top contingencies to show per monitored branch
26: consPerMonBus 10000 // Number of top contingencies to show per monitored bus
27: declineModeORA 0 // Decline Mode (0 - Do not apply failed outage subsequent eval, 1 - Apply failed outage in subsequent eval)
28: ORA_ignoreOutageTime 0 // For multi-core opportunity window. Apply outage regardless of outage start/end? (0-no,1-yes)
29: saveAMBSeed 0 // Save AMB seed case before for each time period
30: ambSaveDirectory [] // Directory to save cases for saveAMBSeed option
31: savePreOut 0 // Save case before applying Study Outage
32: preOutSaveDirectory [] // Directory to save cases for savePreOut option
33: saveFinalApproved 0 // After evaluation finished, create cases with all APPROVED outages
34: finalSaveDirectory [] // Directory to save cases for saveFinalApproved option
35: saveInitialApproved 0 // Before evaluation starts, create cases with all PREAPPROVED and APPROVED outages
36: initialSaveDirectory [] // Directory to save cases for saveInitialApproved option
37: oraACVerifyMode 0 // ORA AC Verify Mode [0-traditional AC screening, 1-AC Verify by Loading Cutoff only, 2-Full ACCont
38: usePriorityOrder 0 // Order for outage evaluation [0-Queue Date, 1-Priority Number
39: oraConvScreen 0 // Perform screening for non-convergent outages [0-No, 1-Yes
40: restoreAlreadyOut 0 // If outage already applied to base, restore to in-service before analysis [0-No, 1-Yes]
41: oraModeUsePreviousApprovedResults 0 // Save results after each study outage and use as base results for next one
42: oraModeRunApprovedScenario 1 // Run the approved base scenario (usually 1)
43: oraModeSavePreviousApprovedResults 0 // Save approved base scenario results (usually 0)
44: oraModeSaveStudyResultsAsApproved 0 // Save approved base scenario results (usually 0)
45: fullSizePrevResults 1 // Big results file if loading cutoff is zero. Set this to zero to reduce results size
46: oraSnapshotIndex -1 // Loadflow Case (Snapshot) index used in ORA multi-core 1=first loaded case
47: oraApprRestoreIndex -1 // Index of approved outage to study for ORA multi-core - only used for RestoreAppr mode
48: kVLayer1 5 // 1st kV Layer
49: kVLayer2 5 // 2nd kV Layer
50: kVLayer3 5 // 3rd kV Layer
51: kVLayer4 5 // 4rd kV Layer
52: kVLayer5 5 // 5th kV Layer
53: kVLayer12_Volt 100.0 // Voltage between Layer 1 and Layer 2
54: kVLayer23_Volt 230.0 // Voltage between Layer 2 and Layer 3
55: kVLayer34_Volt 345.0 // Voltage between Layer 3 and Layer 4
56: kVLayer45_Volt 500.0 // Voltage between Layer 4 and Layer 5
57: kVCutoff 0.00 // Specify kV Cutoff
58: ApplykVCutoffOption 0 // [0-one side only, 1-both sides]
59: N11ContScrnVolt 0 // N-1-1 Contingency Screening for voltage
60: dckVLayer1 5 // Primary proximity screen 1st kV Layer
61: dckVLayer2 5 // Primary proximity screen 2nd kV Layer
62: dckVLayer3 5 // Primary proximity screen 3rd kV Layer
63: dckVLayer4 5 // Primary proximity screen 4rd kV Layer
64: dckVLayer5 5 // Primary proximity screen 5th kV Layer
65: dckVLayer12_Volt 100.0 // Primary proximity screen Voltage between Layer 1 and Layer 2
66: dckVLayer23_Volt 230.0 // Primary proximity screen Voltage between Layer 2 and Layer 3
67: dckVLayer34_Volt 345.0 // Primary proximity screen Voltage between Layer 3 and Layer 4
68: dckVLayer45_Volt 500.0 // Primary proximity screen Voltage between Layer 4 and Layer 5
69: N11ContScrnDCAC 0 // N-1-1 Contingency Screening for nearby seconds - do for both DC and AC
70: dckVCutoff 0.00 // Primary proximity Specify kV Cutoff
71: dcApplykVCutoffOption 0 // Primary proximity [0-one side only, 1-both sides]
72: conReduceModeEnabled 0 // Reduce contingency set for each first-level based on region impact screening
73: saveConReduceToFile 0 // Save to file reduced contingency set for each first-level based on region impact screening
74: readConReduceFromFile 0 // Reduce contingency set for each first-level based on region impact screening
75: snapReadConReduceFromFile 1 // Snap Index for reading reduced contingency set for each first-level based on region impact screening
76: oraApprovedOverlapForDaily 0 // If using daily case and approved outage does not overlap the study outage, then do not apply to the base case [1- do not apply, 0 - apply
77: oraGenSenRun 0 // Run Generator Sensitivity analysis on outage-impacted constraint
78: oraLoadSenRun 0 // Run Load Sensitivity analysis on outage-impacted constraint
79: showAllLoadings 0 // Show all loadings in branch flows report if Sensitivity analysis enabled
80: genSenDfaxCutoff 0.02000 // ORA Gen Sen Dfax Cutoff
81: genSenUpMWCutoff 2000.00 // ORA Gen Sen MW Up Cutoff
82: genSenDownMWCutoff 2000.00 // ORA Gen Sen MW Down Cutoff
83: genSenBranLoadingPctCutoff 90.00 // ORA Gen Sen Branch Pct Loading Cutoff
84: trlimDfaxCutoff 0.02000 // ORA TrLim Dfax Cutoff
85: trlimMWCutoff 50000.00 // ORA TrLim MW Cutoff
86: SysNameGenSen [undefined] // - Study Subsystem Name
87: RefNameGenSen [undefined] // - Reference Subsystem Name
88: rejModeRedisp 0 // Enforce MW redispatch limit for rejecting an outage
89: mwRedispLimit 1000.00 // MW redispatch max for rejecting an outage
90: ignoreHotLineRestore 0 // If close line event is already closed in the base, do not open when restoring outages to normal status
91: ignoreNotHappeningEvents 0 // If branch event is NOT already applied to the base, completely ignore for all analysis - did not actually happen
92: preventShunt 0 // Preventive Shunt Mode (0 - no, 1 - yes)
93: voltDecline 0 // Decline outage if causes voltage violation (0 - no, 1 - yes)
94: outcommImpMWCutoff 0.50 // Outage Common Impact MW Cutoff
95: outcommImpPctLoadingCutoff 9999.00 // Outage Common Impact Pct loading Cutoff
96: outcommImpMISONomogramsOnly 1 // When in MISO FTR mode show only nomograms
Specify option name (or number) and value : [ ORA_ON][ 0]
Specify option name (or number) and value : [ 0]
**** New **** ORA Options
1: ORA_ON 0 // Enable ORA analysis (Transmission Outage Request Analyzer) (0-no,1-yes)
2: ORA_mode_BaseCase 3 // ORA Base case setup mode (1- N-1, no redispatch, 2-SCRD, 3 - SCED)
3: ORA_mode_Study 3 // ORA study analysis mode (1- N-1, no redispatch, 2-SCRD, 3 - SCED)
4: useContReduction 1 // Use contingency reduction for outage analysis (0-no,1-yes)
5: mwContReductionCutoff 15.00 // MW impact cutoff for determining nearness of contingency and outage
6: percentContReductionCutoff 99.00 // Percent change cutoff for determining nearness of contingency and outage
7: ORA_runOpportunityWindow 0 // Find Outage Opportunity Window? (0-no,1-yes)
8: ComparativeACMode 0 // Enable Comparative AC Contingency Analysis (0- no (DC only), 1- yes (run AC))
9: acScreenPctLdCutoff 90.00 // AC Contingency Screen Cutoff - % Branch Loading Cutoff
10: acScreenMWCutoff 5.00 // AC Contingency Screen Cutoff - Flow Change in MW
11: acScreenPctRatCutoff 2.00 // AC Contingency Screen Cutoff - Flow Change as % of Branch Rating
12: comparePctLdCutoff 90.00 // Comparative Flow Cutoff - % Branch Loading Cutoff
13: compareMWCutoff 5.00 // Comparative Flow Cutoff - Flow Change in MW
14: comparePctRatCutoff 2.00 // Comparative Flow Cutoff - Flow Change as % of Branch Rating
15: voltPrePostCutoff 0.0020 // Comparative Voltage Cutoff - Diff between post-cont and pre-cont
16: voltCompareCutoff 0.0020 // Comparative Voltage Cutoff - Diff between post cont with & without outage
17: shadowPriceChangeCutoff 30.0000 // Comparative Shadow Price value change cutoff - Diff with & without outage
18: shadowPricePctChangeCutoff 25.0000 // Comparative Shadow Price perchange change cutoff - Change as % of max(pre,post) with & without outage
19: trendingChangeMWCutoff 100.0000 // Outage trending status cutoff - Flow Change in MW
20: trendingPercentLoadingChangeCutoff 20.0000 // Outage trending status cutoff - Flow Change as % of Branch Rating
21: trendingShadowPriceChangeCutoff 1000.0000 // Outage trending status cutoff - Change in shadow price
22: conflPctLdCutoff 0.00 // Conflicting Cont Flow Cutoff - % Branch Loading Cutoff
23: conflMWCutoff 0.00 // Conflicting Cont Flow Cutoff - Flow Change in MW
24: conflPctRatCutoff 0.00 // Conflicting Cont Flow Cutoff - Flow Change as % of Branch Rating
25: consPerMonBran 10000 // Number of top contingencies to show per monitored branch
26: consPerMonBus 10000 // Number of top contingencies to show per monitored bus
27: declineModeORA 0 // Decline Mode (0 - Do not apply failed outage subsequent eval, 1 - Apply failed outage in subsequent eval)
28: ORA_ignoreOutageTime 0 // For multi-core opportunity window. Apply outage regardless of outage start/end? (0-no,1-yes)
29: saveAMBSeed 0 // Save AMB seed case before for each time period
30: ambSaveDirectory [] // Directory to save cases for saveAMBSeed option
31: savePreOut 0 // Save case before applying Study Outage
32: preOutSaveDirectory [] // Directory to save cases for savePreOut option
33: saveFinalApproved 0 // After evaluation finished, create cases with all APPROVED outages
34: finalSaveDirectory [] // Directory to save cases for saveFinalApproved option
35: saveInitialApproved 0 // Before evaluation starts, create cases with all PREAPPROVED and APPROVED outages
36: initialSaveDirectory [] // Directory to save cases for saveInitialApproved option
37: oraACVerifyMode 0 // ORA AC Verify Mode [0-traditional AC screening, 1-AC Verify by Loading Cutoff only, 2-Full ACCont
38: usePriorityOrder 0 // Order for outage evaluation [0-Queue Date, 1-Priority Number
39: oraConvScreen 0 // Perform screening for non-convergent outages [0-No, 1-Yes
40: restoreAlreadyOut 0 // If outage already applied to base, restore to in-service before analysis [0-No, 1-Yes]
41: oraModeUsePreviousApprovedResults 0 // Save results after each study outage and use as base results for next one
42: oraModeRunApprovedScenario 1 // Run the approved base scenario (usually 1)
43: oraModeSavePreviousApprovedResults 0 // Save approved base scenario results (usually 0)
44: oraModeSaveStudyResultsAsApproved 0 // Save approved base scenario results (usually 0)
45: fullSizePrevResults 1 // Big results file if loading cutoff is zero. Set this to zero to reduce results size
46: oraSnapshotIndex -1 // Loadflow Case (Snapshot) index used in ORA multi-core 1=first loaded case
47: oraApprRestoreIndex -1 // Index of approved outage to study for ORA multi-core - only used for RestoreAppr mode
48: kVLayer1 5 // 1st kV Layer
49: kVLayer2 5 // 2nd kV Layer
50: kVLayer3 5 // 3rd kV Layer
51: kVLayer4 5 // 4rd kV Layer
52: kVLayer5 5 // 5th kV Layer
53: kVLayer12_Volt 100.0 // Voltage between Layer 1 and Layer 2
54: kVLayer23_Volt 230.0 // Voltage between Layer 2 and Layer 3
55: kVLayer34_Volt 345.0 // Voltage between Layer 3 and Layer 4
56: kVLayer45_Volt 500.0 // Voltage between Layer 4 and Layer 5
57: kVCutoff 0.00 // Specify kV Cutoff
58: ApplykVCutoffOption 0 // [0-one side only, 1-both sides]
59: N11ContScrnVolt 0 // N-1-1 Contingency Screening for voltage
60: dckVLayer1 5 // Primary proximity screen 1st kV Layer
61: dckVLayer2 5 // Primary proximity screen 2nd kV Layer
62: dckVLayer3 5 // Primary proximity screen 3rd kV Layer
63: dckVLayer4 5 // Primary proximity screen 4rd kV Layer
64: dckVLayer5 5 // Primary proximity screen 5th kV Layer
65: dckVLayer12_Volt 100.0 // Primary proximity screen Voltage between Layer 1 and Layer 2
66: dckVLayer23_Volt 230.0 // Primary proximity screen Voltage between Layer 2 and Layer 3
67: dckVLayer34_Volt 345.0 // Primary proximity screen Voltage between Layer 3 and Layer 4
68: dckVLayer45_Volt 500.0 // Primary proximity screen Voltage between Layer 4 and Layer 5
69: N11ContScrnDCAC 0 // N-1-1 Contingency Screening for nearby seconds - do for both DC and AC
70: dckVCutoff 0.00 // Primary proximity Specify kV Cutoff
71: dcApplykVCutoffOption 0 // Primary proximity [0-one side only, 1-both sides]
72: conReduceModeEnabled 0 // Reduce contingency set for each first-level based on region impact screening
73: saveConReduceToFile 0 // Save to file reduced contingency set for each first-level based on region impact screening
74: readConReduceFromFile 0 // Reduce contingency set for each first-level based on region impact screening
75: snapReadConReduceFromFile 1 // Snap Index for reading reduced contingency set for each first-level based on region impact screening
76: oraApprovedOverlapForDaily 0 // If using daily case and approved outage does not overlap the study outage, then do not apply to the base case [1- do not apply, 0 - apply
77: oraGenSenRun 0 // Run Generator Sensitivity analysis on outage-impacted constraint
78: oraLoadSenRun 0 // Run Load Sensitivity analysis on outage-impacted constraint
79: showAllLoadings 0 // Show all loadings in branch flows report if Sensitivity analysis enabled
80: genSenDfaxCutoff 0.02000 // ORA Gen Sen Dfax Cutoff
81: genSenUpMWCutoff 2000.00 // ORA Gen Sen MW Up Cutoff
82: genSenDownMWCutoff 2000.00 // ORA Gen Sen MW Down Cutoff
83: genSenBranLoadingPctCutoff 90.00 // ORA Gen Sen Branch Pct Loading Cutoff
84: trlimDfaxCutoff 0.02000 // ORA TrLim Dfax Cutoff
85: trlimMWCutoff 50000.00 // ORA TrLim MW Cutoff
86: SysNameGenSen [undefined] // - Study Subsystem Name
87: RefNameGenSen [undefined] // - Reference Subsystem Name
88: rejModeRedisp 0 // Enforce MW redispatch limit for rejecting an outage
89: mwRedispLimit 1000.00 // MW redispatch max for rejecting an outage
90: ignoreHotLineRestore 0 // If close line event is already closed in the base, do not open when restoring outages to normal status
91: ignoreNotHappeningEvents 0 // If branch event is NOT already applied to the base, completely ignore for all analysis - did not actually happen
92: preventShunt 0 // Preventive Shunt Mode (0 - no, 1 - yes)
93: voltDecline 0 // Decline outage if causes voltage violation (0 - no, 1 - yes)
94: outcommImpMWCutoff 0.50 // Outage Common Impact MW Cutoff
95: outcommImpPctLoadingCutoff 9999.00 // Outage Common Impact Pct loading Cutoff
96: outcommImpMISONomogramsOnly 1 // When in MISO FTR mode show only nomograms
Select data category:(L2): [ 0]
Select main menu function(L1): [ lfopt] = Selected Function 11 - LFOPTIONS - LF options
Select data category:(L2): [ adj] = Selected Function 2 - Adjustment - LF adjustment options
**** Current **** LF adjustment options:
1: iterCheckVarLimitHotStart 0 // Iteration to start generator VAR limit checking - hot start
2: iterCheckVarLimitFlat 3 // Iteration to start generator VAR limit checking - flat start
3: PAR_AdjEnabledLF 0 // Phase Shifter Adjustment (0-off: 1-ON)
4: areaInterAdjustEnabled 0 // Area interchange control (0-no:1-ties;2-ties and external load,3-scale area load)
5: TAP_AdjEnabledLF 0 // Enable TAP adjustment(0-no:1-yes)
6: shuntAdjEnabled 1 // Enable shunt adjustment(0-no;1-continuous only;2-continuous and discrete )
7: DCLineAdjEnabled 1 // Enable DC lines TAP adjustments(0-no:1-yes)
8: showParAdj 0 // Report Phase shifter adjustments per iteration(0-no:1-summary Only: 2-Violated. 3-All)
9: showTapAdj 0 // Report TAP and DC lines adjustments per iteration(0-no:1-summary: 2-all)
10: showShuntAdj 0 // Report Shunt adjustments per iteration(0-;o:1-viol; Only: 2-all)
11: showAreaInterAdj 0 // Report Area interchange adjustments (0-no;1-summary;2-failed tolerance;3-all)
12: showDCLineAdj 0 // Report DC lines TAP adjustment-same as TAP for now
13: busMismTolerAreaInter 10.0000 // Bus Mismatch tolerance to start area adjustments
14: maxVarLimitsBusTypeChanges 6 // Max times voltage controlled bus can change PV-->PQ type. Stop checking limit after
15: iterCheckVarLimitLast 30 // Iteration to stop checking var limits
16: maxAdjustIterVolt 30 // Iteration to stop TAP and Shunt adjustments
17: deacFactRTap 1.0000 // Voltage adjustment deacceleration factor
18: deacFactShunt 1.0000 // Shunt adjustment deacceleration factor (for discrete step shunts)
19: maxTapChange 0.0300 // Max tap ratio change per iteration
20: voltAdjTrigger 0.0050 // Max voltage magnitude change to activate TAP and Shunt adjustments
21: angleAdjTrigger 0.2000 // Max voltage angle change (in degrees) to activate PAR and area interchange adjustments
22: showBusTypeChan 0 // Show voltage controlled buses type changes (0-no;1-summary;2-per iteration)
23: showMismOnFail 2 // Show bus Mismatches if ACLF failed (0-no,1-list of buses, 2- bus flow details)
24: deOscilFactor 0.7000 // De-oscillation factor (if 1.0-not activated) for FastDec solution step
25: areaInterAdjustEdit 0 // Adjust area interchange when editing generation and load. 0-no:1-ties;2-ties and external load)
26: fixedToSwitched 0 // Convert all fixed bus shunts in the case to switched discrete shunts.
27: inServiceSwitchedShunts 0 // When reading the case, set status of all switched shunts in the case to in-service.
28: changeSwitchedShuntsMode1 0 // When reading the case, set control mode of all mode 0 switched shunts to mode 1.
Specify option name (or number) and value : [ areaInterAdjustEdit][ 1]
Specify option name (or number) and value : [ 0]
**** New **** LF adjustment options:
1: iterCheckVarLimitHotStart 0 // Iteration to start generator VAR limit checking - hot start
2: iterCheckVarLimitFlat 3 // Iteration to start generator VAR limit checking - flat start
3: PAR_AdjEnabledLF 0 // Phase Shifter Adjustment (0-off: 1-ON)
4: areaInterAdjustEnabled 0 // Area interchange control (0-no:1-ties;2-ties and external load,3-scale area load)
5: TAP_AdjEnabledLF 0 // Enable TAP adjustment(0-no:1-yes)
6: shuntAdjEnabled 1 // Enable shunt adjustment(0-no;1-continuous only;2-continuous and discrete )
7: DCLineAdjEnabled 1 // Enable DC lines TAP adjustments(0-no:1-yes)
8: showParAdj 0 // Report Phase shifter adjustments per iteration(0-no:1-summary Only: 2-Violated. 3-All)
9: showTapAdj 0 // Report TAP and DC lines adjustments per iteration(0-no:1-summary: 2-all)
10: showShuntAdj 0 // Report Shunt adjustments per iteration(0-;o:1-viol; Only: 2-all)
11: showAreaInterAdj 0 // Report Area interchange adjustments (0-no;1-summary;2-failed tolerance;3-all)
12: showDCLineAdj 0 // Report DC lines TAP adjustment-same as TAP for now
13: busMismTolerAreaInter 10.0000 // Bus Mismatch tolerance to start area adjustments
14: maxVarLimitsBusTypeChanges 6 // Max times voltage controlled bus can change PV-->PQ type. Stop checking limit after
15: iterCheckVarLimitLast 30 // Iteration to stop checking var limits
16: maxAdjustIterVolt 30 // Iteration to stop TAP and Shunt adjustments
17: deacFactRTap 1.0000 // Voltage adjustment deacceleration factor
18: deacFactShunt 1.0000 // Shunt adjustment deacceleration factor (for discrete step shunts)
19: maxTapChange 0.0300 // Max tap ratio change per iteration
20: voltAdjTrigger 0.0050 // Max voltage magnitude change to activate TAP and Shunt adjustments
21: angleAdjTrigger 0.2000 // Max voltage angle change (in degrees) to activate PAR and area interchange adjustments
22: showBusTypeChan 0 // Show voltage controlled buses type changes (0-no;1-summary;2-per iteration)
23: showMismOnFail 2 // Show bus Mismatches if ACLF failed (0-no,1-list of buses, 2- bus flow details)
24: deOscilFactor 0.7000 // De-oscillation factor (if 1.0-not activated) for FastDec solution step
25: areaInterAdjustEdit 1 // Adjust area interchange when editing generation and load. 0-no:1-ties;2-ties and external load)
26: fixedToSwitched 0 // Convert all fixed bus shunts in the case to switched discrete shunts.
27: inServiceSwitchedShunts 0 // When reading the case, set status of all switched shunts in the case to in-service.
28: changeSwitchedShuntsMode1 0 // When reading the case, set control mode of all mode 0 switched shunts to mode 1.
Select data category:(L2): [ 0]
Select main menu function(L1): [ opt] = Selected Function 10 - Options - TARA analysis options
Select data category:(L2): [ cont] = Selected Function 1 - CONTING - Contingency analysis option
**** Current **** Contingency analysis options:
1: monBranRatingBase 1 // Base case rating (1-A;2-B;3-C;4-D)
2: monBranRatingCont 2 // Contingency rating (1-A;2-B;3-C;4-D)
3: monBranRatingMultBase 100.00 // Base case rating multipliers
4: monBranRatingMultCont 100.00 // Contingency rating multipliers
5: contChanCutOffMW 0.1 // MW cutoff to ignore constraints if cont.flow doesn't changes from the base case more than
6: contChanCutOffPercent 10.0 // Rating %% cutoff to ignore if cont.flow changes from the base case is less than
7: PAR_AdjEnabledContAnal 1 // Phase shifter model for the base case (0-fixed angle;1-control flow), always fixed in contingency
8: adjustRatingMVA 0 // Adjust branch MW rating based on MVAR flow (DC analysis)
9: limitTypeLine 0 // Use AMP (=0) or MVA (1) limit to check lines violation in AC mode
10: limitTypeTran 1 // Use AMP (=0) or MVA (1) limit to check transformer violation in AC mode
11: voltMinChange 0.0010 // Voltage change cutoff in PU to ignore voltage violations with change from the base case is smaller
12: numContMaxAlloc 20000 // Max number of contingencies
13: numEventsAlloc 100000 // Max number of contingency events
14: numDispEventAlloc 100000 // Max number of generation redispatch events
15: numLFgatesMaxAlloc 30000 // Max number of flowgates
16: maxFgateBranches 70 // Max number of branches (events) per flowgate
17: mulSecPrintMode 1 // Multi-section line modeling (0-ignore;1-honor)
18: smartCutOff 0 // Use Smart cutoff based on Max conting impact using base case and conting rating difference (0-no;1-yes)
19: maxExcludesAlloc 10000 // Max number of exclude records
20: showConAnalLFLog 0 // Show LF convergence during ACCONT
21: MAXOUTAGES 1000 // Maximum number of outages
22: maxORAFlowResults 2000000 // Maximum number of ORA or N-1-1 results to report
23: ACCONTRepeatSolution 0 // If first AC solution failed, repeat with alternative Flat/Hot start(0-no,1-yes),2-limit to the best iteration
24: showNotMappedContEvents 1 // When generating contingency file, show not mapped event(0-no,1-yes)
25: monBranRatingEnAdd1 0 // Enable first additional rating reporting (0-no,1-yes)
26: monBranRatingEnAdd2 0 // Enable second additional rating reporting (0-no,1-yes)
27: monBranRatingAdd1 3 // Additional Rating 1 (1-A;2-B;3-C;4-D)
28: monBranRatingAdd2 3 // Additional Rating 2 (1-A;2-B;3-C;4-D)
29: monBranRatingMultAdd1 100.00 // Additional Rating 1 multiplier
30: monBranRatingMultAdd2 100.00 // Additional Rating 2 multiplier
31: LoadingCutOff 0.00 // Loading cutoff in percent for displaying cont analysis flow results
32: showAllHighPreSCD 0 // Show SCD result if pre-SCD above cutoff but post-SCD below
33: N11MODE 1 // Run in N-1+Application Mode
34: multiCoreN1 0 // Run in N-1 ACCont in multi-core mode? [0-No, 1-Yes]
35: numLowestLoading 5 // Max number of lowest loading results to report
36: VoltLimAdder 0.00000 // Add this to voltage limit to expand or limit hi/low voltage viol results
37: StudyFiles 0 // Show Names of Input Files on all reports
38: MonConMode 1 // Select Mon/Con mode (1:Regular, 2:Flowgate, 3:Voltgate, 4:Flowgate & Voltgate
39: MaxMonConMode 100000 // Maximum Number of mon/con mode entries
40: keepDuplicates 1 // Keep contingency even if exact duplicate? [0=no, 1=yes]
41: correctiveSwitchingMode 0 // Run in corrective switching mode? [0=no, 1=yes]
42: lodfCutoff 0.01000 // Cutoff for LODF report (absolute value)
43: lodfImpCutoff 1.00 // MW cutoff for LODF Impact report (lodf*(event rating))
44: maxFgEventTotal 100000 // Max number of all branches and events for all flowgatesflowgate
45: maxEvPerCont 70 // Max number of events (events) per contingency
46: maxSPSLogic 10000 // Max number of SPS logic elements
47: maxInjGroups 500 // Max number of SPS AUX Injections Groups
48: maxSPSInterfaces 1000 // Max number of SPS AUX Interfaces
49: co_mode 0 // Cascading mode, 0=no, 1=yes
50: co_branchoutage 1 // Trip Overloaded Branches in Cascading Outage, 0=no, 1=yes
51: co_genoutage 1 // Trip Generators in Cascading Outage, 0=no, 1=yes
52: co_genterminalbus 0 // Trip Generators with low voltage violation at generator terminal bus, 0=no, 1=yes
53: co_loadoutage 1 // Trip Loads in Cascading Outage, 0=no, 1=yes
54: co_maxlevel 10 // Maximum cascading outage test level
55: saveCOCases 0 // Save a case for each cascading step case
56: COSaveDirectory [] // Folder to save each cascading outage case
57: kVLayer12_Volt 100.0 // Voltage between Layer 1 and Layer 2
58: kVLayer23_Volt 230.0 // Voltage between Layer 2 and Layer 3
59: kVLayer34_Volt 345.0 // Voltage between Layer 3 and Layer 4
60: kVLayer45_Volt 500.0 // Voltage between Layer 4 and Layer 5
61: kVLayer1_LDCutoff 115.0 // Layer 1 RelayLoadability Percent
62: kVLayer2_LDCutoff 115.0 // Layer 2 RelayLoadability Percent
63: kVLayer3_LDCutoff 115.0 // Layer 3 RelayLoadability Percent
64: kVLayer4_LDCutoff 115.0 // Layer 4 RelayLoadability Percent
65: kVLayer5_LDCutoff 115.0 // Layer 5 RelayLoadability Percent
66: zeroRatingCutoff 0.000100 // If rating is below this, set rating to 9999
67: saveN11Cases 0 // Save a case for each N-1-1 first-level case
68: N11SaveDirectory [] // Folder to save each N-1-1 first-level case
69: acVerifyFgate 0 // Enable flowgate AC verification (0-No;1-Yes)
70: useContingencyComments 0 // Use Comments in contingency file in contingency reporting
71: ignoreEnd2Exit 0 // Ignore END statement to exit reading sub mon con exc files (0-No, 1-Yes)
72: nearSyskVLayer1 5 // Subsystem proximity screen 1st kV Layer
73: nearSyskVLayer2 5 // Subsystem proximity screen 2nd kV Layer
74: nearSyskVLayer3 5 // Subsystem proximity screen 3rd kV Layer
75: nearSyskVLayer4 5 // Subsystem proximity screen 4rd kV Layer
76: nearSyskVLayer5 5 // Subsystem proximity screen 5th kV Layer
77: nearSyskVLayer12_Volt 100.0 // Subsystem proximity screen Voltage between Layer 1 and Layer 2
78: nearSyskVLayer23_Volt 230.0 // Subsystem proximity screen Voltage between Layer 2 and Layer 3
79: nearSyskVLayer34_Volt 345.0 // Subsystem proximity screen Voltage between Layer 3 and Layer 4
80: nearSyskVLayer45_Volt 500.0 // Subsystem proximity screen Voltage between Layer 4 and Layer 5
81: nearSysScrnMod 0 // Subsystem Screening for nearby contingencies (1st and 2nd)
82: nearSyskVCutoff 0.00 // Subsystem proximity Specify kV Cutoff
83: nearSysApplykVCutoffOption 0 // Subsystem proximity [0-one side only, 1-both sides]
84: nearByLayerSubSysName [Undefined] // - Subsystem Name for proximity contingency layer screen
Specify option name (or number) and value : [ monBranRatingBase][ 1]
Specify option name (or number) and value : [ monBranRatingCont][ 2]
Specify option name (or number) and value : [ monBranRatingMultBase][ 100]
Specify option name (or number) and value : [ monBranRatingMultCont][ 100]
Specify option name (or number) and value : [ monBranRatingEnAdd1][ 0]
Specify option name (or number) and value : [ monBranRatingEnAdd2][ 0]
Specify option name (or number) and value : [ contChanCutOffMW][ 5]
Specify option name (or number) and value : [ contChanCutOffPercent][ 2]
Specify option name (or number) and value : [ MonConMode][ 1]
Specify option name (or number) and value : [ PAR_AdjEnabledContAnal][ 1]
Specify option name (or number) and value : [ adjustRatingMVA][ 0]
Specify option name (or number) and value : [ limitTypeLine][ 0]
Specify option name (or number) and value : [ limitTypeTran][ 1]
Specify option name (or number) and value : [ voltMinChange][ 0.005]
Specify option name (or number) and value : [ numContMaxAlloc][ 15000]
Specify option name (or number) and value : [ maxEvPerCont][ 60]
Specify option name (or number) and value : [ numEventsAlloc][ 35000]
Specify option name (or number) and value : [ numDispEventAlloc][ 60000]
Specify option name (or number) and value : [ numLFgatesMaxAlloc][ 10000]
Specify option name (or number) and value : [ mulSecPrintMode][ 0]
Specify option name (or number) and value : [ MAXOUTAGES][ 15000]
Specify option name (or number) and value : [ maxORAFlowResults][ 2000000]
Specify option name (or number) and value : [ maxFgateBranches][ 100]
Specify option name (or number) and value : [ maxFgEventTotal][ 30000]
Specify option name (or number) and value : [ useContingencyComments][ 0]
Specify option name (or number) and value : [ 0]
**** New **** Contingency analysis options:
1: monBranRatingBase 1 // Base case rating (1-A;2-B;3-C;4-D)
2: monBranRatingCont 2 // Contingency rating (1-A;2-B;3-C;4-D)
3: monBranRatingMultBase 100.00 // Base case rating multipliers
4: monBranRatingMultCont 100.00 // Contingency rating multipliers
5: contChanCutOffMW 5.0 // MW cutoff to ignore constraints if cont.flow doesn't changes from the base case more than
6: contChanCutOffPercent 2.0 // Rating %% cutoff to ignore if cont.flow changes from the base case is less than
7: PAR_AdjEnabledContAnal 1 // Phase shifter model for the base case (0-fixed angle;1-control flow), always fixed in contingency
8: adjustRatingMVA 0 // Adjust branch MW rating based on MVAR flow (DC analysis)
9: limitTypeLine 0 // Use AMP (=0) or MVA (1) limit to check lines violation in AC mode
10: limitTypeTran 1 // Use AMP (=0) or MVA (1) limit to check transformer violation in AC mode
11: voltMinChange 0.0050 // Voltage change cutoff in PU to ignore voltage violations with change from the base case is smaller
12: numContMaxAlloc 15000 // Max number of contingencies
13: numEventsAlloc 35000 // Max number of contingency events
14: numDispEventAlloc 60000 // Max number of generation redispatch events
15: numLFgatesMaxAlloc 10000 // Max number of flowgates
16: maxFgateBranches 100 // Max number of branches (events) per flowgate
17: mulSecPrintMode 0 // Multi-section line modeling (0-ignore;1-honor)
18: smartCutOff 0 // Use Smart cutoff based on Max conting impact using base case and conting rating difference (0-no;1-yes)
19: maxExcludesAlloc 10000 // Max number of exclude records
20: showConAnalLFLog 0 // Show LF convergence during ACCONT
21: MAXOUTAGES 15000 // Maximum number of outages
22: maxORAFlowResults 2000000 // Maximum number of ORA or N-1-1 results to report
23: ACCONTRepeatSolution 0 // If first AC solution failed, repeat with alternative Flat/Hot start(0-no,1-yes),2-limit to the best iteration
24: showNotMappedContEvents 1 // When generating contingency file, show not mapped event(0-no,1-yes)
25: monBranRatingEnAdd1 0 // Enable first additional rating reporting (0-no,1-yes)
26: monBranRatingEnAdd2 0 // Enable second additional rating reporting (0-no,1-yes)
27: monBranRatingAdd1 3 // Additional Rating 1 (1-A;2-B;3-C;4-D)
28: monBranRatingAdd2 3 // Additional Rating 2 (1-A;2-B;3-C;4-D)
29: monBranRatingMultAdd1 100.00 // Additional Rating 1 multiplier
30: monBranRatingMultAdd2 100.00 // Additional Rating 2 multiplier
31: LoadingCutOff 0.00 // Loading cutoff in percent for displaying cont analysis flow results
32: showAllHighPreSCD 0 // Show SCD result if pre-SCD above cutoff but post-SCD below
33: N11MODE 1 // Run in N-1+Application Mode
34: multiCoreN1 0 // Run in N-1 ACCont in multi-core mode? [0-No, 1-Yes]
35: numLowestLoading 5 // Max number of lowest loading results to report
36: VoltLimAdder 0.00000 // Add this to voltage limit to expand or limit hi/low voltage viol results
37: StudyFiles 0 // Show Names of Input Files on all reports
38: MonConMode 1 // Select Mon/Con mode (1:Regular, 2:Flowgate, 3:Voltgate, 4:Flowgate & Voltgate
39: MaxMonConMode 100000 // Maximum Number of mon/con mode entries
40: keepDuplicates 1 // Keep contingency even if exact duplicate? [0=no, 1=yes]
41: correctiveSwitchingMode 0 // Run in corrective switching mode? [0=no, 1=yes]
42: lodfCutoff 0.01000 // Cutoff for LODF report (absolute value)
43: lodfImpCutoff 1.00 // MW cutoff for LODF Impact report (lodf*(event rating))
44: maxFgEventTotal 30000 // Max number of all branches and events for all flowgatesflowgate
45: maxEvPerCont 60 // Max number of events (events) per contingency
46: maxSPSLogic 10000 // Max number of SPS logic elements
47: maxInjGroups 500 // Max number of SPS AUX Injections Groups
48: maxSPSInterfaces 1000 // Max number of SPS AUX Interfaces
49: co_mode 0 // Cascading mode, 0=no, 1=yes
50: co_branchoutage 1 // Trip Overloaded Branches in Cascading Outage, 0=no, 1=yes
51: co_genoutage 1 // Trip Generators in Cascading Outage, 0=no, 1=yes
52: co_genterminalbus 0 // Trip Generators with low voltage violation at generator terminal bus, 0=no, 1=yes
53: co_loadoutage 1 // Trip Loads in Cascading Outage, 0=no, 1=yes
54: co_maxlevel 10 // Maximum cascading outage test level
55: saveCOCases 0 // Save a case for each cascading step case
56: COSaveDirectory [] // Folder to save each cascading outage case
57: kVLayer12_Volt 100.0 // Voltage between Layer 1 and Layer 2
58: kVLayer23_Volt 230.0 // Voltage between Layer 2 and Layer 3
59: kVLayer34_Volt 345.0 // Voltage between Layer 3 and Layer 4
60: kVLayer45_Volt 500.0 // Voltage between Layer 4 and Layer 5
61: kVLayer1_LDCutoff 115.0 // Layer 1 RelayLoadability Percent
62: kVLayer2_LDCutoff 115.0 // Layer 2 RelayLoadability Percent
63: kVLayer3_LDCutoff 115.0 // Layer 3 RelayLoadability Percent
64: kVLayer4_LDCutoff 115.0 // Layer 4 RelayLoadability Percent
65: kVLayer5_LDCutoff 115.0 // Layer 5 RelayLoadability Percent
66: zeroRatingCutoff 0.000100 // If rating is below this, set rating to 9999
67: saveN11Cases 0 // Save a case for each N-1-1 first-level case
68: N11SaveDirectory [] // Folder to save each N-1-1 first-level case
69: acVerifyFgate 0 // Enable flowgate AC verification (0-No;1-Yes)
70: useContingencyComments 0 // Use Comments in contingency file in contingency reporting
71: ignoreEnd2Exit 0 // Ignore END statement to exit reading sub mon con exc files (0-No, 1-Yes)
72: nearSyskVLayer1 5 // Subsystem proximity screen 1st kV Layer
73: nearSyskVLayer2 5 // Subsystem proximity screen 2nd kV Layer
74: nearSyskVLayer3 5 // Subsystem proximity screen 3rd kV Layer
75: nearSyskVLayer4 5 // Subsystem proximity screen 4rd kV Layer
76: nearSyskVLayer5 5 // Subsystem proximity screen 5th kV Layer
77: nearSyskVLayer12_Volt 100.0 // Subsystem proximity screen Voltage between Layer 1 and Layer 2
78: nearSyskVLayer23_Volt 230.0 // Subsystem proximity screen Voltage between Layer 2 and Layer 3
79: nearSyskVLayer34_Volt 345.0 // Subsystem proximity screen Voltage between Layer 3 and Layer 4
80: nearSyskVLayer45_Volt 500.0 // Subsystem proximity screen Voltage between Layer 4 and Layer 5
81: nearSysScrnMod 0 // Subsystem Screening for nearby contingencies (1st and 2nd)
82: nearSyskVCutoff 0.00 // Subsystem proximity Specify kV Cutoff
83: nearSysApplykVCutoffOption 0 // Subsystem proximity [0-one side only, 1-both sides]
84: nearByLayerSubSysName [Undefined] // - Subsystem Name for proximity contingency layer screen
Select data category:(L2): [ 0]
Select main menu function(L1): [ opt] = Selected Function 10 - Options - TARA analysis options
Select data category:(L2): [ N-1-1] = Selected Function 16 - N-1-1 - N-1-1 evaluation options
**** Current **** N-1-1 Options
1: ORA_mode_BaseCase 3 // N-1-1 Base case setup mode (1- N-1, no redispatch, 2-SCRD, 3 - SCED)
2: ORA_mode_Study 3 // N-1-1 study analysis mode (1- N-1, no redispatch, 2-SCRD, 3 - SCED)
3: ComparativeACMode 0 // Enable Comparative AC Contingency Analysis (0- no (DC only), 1- yes (run AC))
4: acScreenPctLdCutoff 90.00 // AC Contingency Screen Cutoff - % Branch Loading Cutoff
5: acScreenMWCutoff 5.00 // AC Contingency Screen Cutoff - Flow Change in MW
6: acScreenPctRatCutoff 2.00 // AC Contingency Screen Cutoff - Flow Change as % of Branch Rating
7: comparePctLdCutoff 90.00 // Comparative Flow Cutoff - % Branch Loading Cutoff
8: compareMWCutoff 5.00 // Comparative Flow Cutoff - Flow Change in MW
9: comparePctRatCutoff 2.00 // Comparative Flow Cutoff - Flow Change as % of Branch Rating
10: voltPrePostCutoff 0.0020 // Comparative Voltage Cutoff - Diff between post-cont and pre-cont
11: voltCompareCutoff 0.0020 // Comparative Voltage Cutoff - Diff between post cont with & without outage
12: shadowPriceChangeCutoff 30.0000 // Comparative Shadow Price value change cutoff - Diff with & without outage
13: shadowPricePctChangeCutoff 25.0000 // Comparative Shadow Price perchange change cutoff - Change as % of max(pre,post) with & without outage
14: trendingChangeMWCutoff 100.0000 // Outage trending status cutoff - Flow Change in MW
15: trendingPercentLoadingChangeCutoff 20.0000 // Outage trending status cutoff - Flow Change as % of Branch Rating
16: trendingShadowPriceChangeCutoff 1000.0000 // Outage trending status cutoff - Change in shadow price
17: consPerMonBran 10000 // Number of top contingencies to show per monitored branch
18: consPerMonBus 10000 // Number of top contingencies to show per monitored bus
19: N11COMPAREMODE 0 // Compare fist-level results with original case results
20: N11ACSCREEN 0 // ACCont only for contingencies impacted by first-level contingency
21: N11SuppressOrig 0 // Do not print original case info in non-comparative mode
22: saveAMBSeed 0 // Save AMB seed case before for each time period
23: ambSaveDirectory [] // Directory to save cases for saveAMBSeed option
24: savePreOut 0 // Save case before applying Study Outage
25: preOutSaveDirectory [] // Directory to save cases for savePreOut option
26: saveFinalApproved 0 // After evaluation finished, create cases with all APPROVED outages
27: finalSaveDirectory [] // Directory to save cases for saveFinalApproved option
28: saveInitialApproved 0 // Before evaluation starts, create cases with all PREAPPROVED and APPROVED outages
29: initialSaveDirectory [] // Directory to save cases for saveInitialApproved option
30: kVLayer1 5 // 1st kV Layer
31: kVLayer2 5 // 2nd kV Layer
32: kVLayer3 5 // 3rd kV Layer
33: kVLayer4 5 // 4rd kV Layer
34: kVLayer5 5 // 5th kV Layer
35: kVLayer12_Volt 100.0 // Voltage between Layer 1 and Layer 2
36: kVLayer23_Volt 230.0 // Voltage between Layer 2 and Layer 3
37: kVLayer34_Volt 345.0 // Voltage between Layer 3 and Layer 4
38: kVLayer45_Volt 500.0 // Voltage between Layer 4 and Layer 5
39: N11ContScrnVolt 0 // N-1-1 Contingency Screening for voltage
40: kVCutoff 0.00 // Specify kV Cutoff
41: ApplykVCutoffOption 0 // [0-one side only, 1-both sides]
42: dckVLayer1 5 // Primary proximity screen 1st kV Layer
43: dckVLayer2 5 // Primary proximity screen 2nd kV Layer
44: dckVLayer3 5 // Primary proximity screen 3rd kV Layer
45: dckVLayer4 5 // Primary proximity screen 4rd kV Layer
46: dckVLayer5 5 // Primary proximity screen 5th kV Layer
47: dckVLayer12_Volt 100.0 // Primary proximity screen Voltage between Layer 1 and Layer 2
48: dckVLayer23_Volt 230.0 // Primary proximity screen Voltage between Layer 2 and Layer 3
49: dckVLayer34_Volt 345.0 // Primary proximity screen Voltage between Layer 3 and Layer 4
50: dckVLayer45_Volt 500.0 // Primary proximity screen Voltage between Layer 4 and Layer 5
51: N11ContScrnDCAC 0 // N-1-1 Contingency Screening for nearby seconds - do for both DC and AC
52: dckVCutoff 0.00 // Primary proximity Specify kV Cutoff
53: dcApplykVCutoffOption 0 // Primary proximity [0-one side only, 1-both sides]
54: conReduceModeEnabled 0 // Reduce contingency set for each first-level based on region impact screening
55: saveConReduceToFile 0 // Save to file reduced contingency set for each first-level based on region impact screening
56: readConReduceFromFile 0 // Read from file contingency set for each first-level based on region impact screening
57: snapReadConReduceFromFile 1 // Snap Index for reading reduced contingency set for each first-level based on region impact screening
Specify option name (or number) and value : [ consPerMonBran][ 5]
Specify option name (or number) and value : [ consPerMonBus][ 5]
Specify option name (or number) and value : [ 0]
**** New **** N-1-1 Options
1: ORA_mode_BaseCase 3 // N-1-1 Base case setup mode (1- N-1, no redispatch, 2-SCRD, 3 - SCED)
2: ORA_mode_Study 3 // N-1-1 study analysis mode (1- N-1, no redispatch, 2-SCRD, 3 - SCED)
3: ComparativeACMode 0 // Enable Comparative AC Contingency Analysis (0- no (DC only), 1- yes (run AC))
4: acScreenPctLdCutoff 90.00 // AC Contingency Screen Cutoff - % Branch Loading Cutoff
5: acScreenMWCutoff 5.00 // AC Contingency Screen Cutoff - Flow Change in MW
6: acScreenPctRatCutoff 2.00 // AC Contingency Screen Cutoff - Flow Change as % of Branch Rating
7: comparePctLdCutoff 90.00 // Comparative Flow Cutoff - % Branch Loading Cutoff
8: compareMWCutoff 5.00 // Comparative Flow Cutoff - Flow Change in MW
9: comparePctRatCutoff 2.00 // Comparative Flow Cutoff - Flow Change as % of Branch Rating
10: voltPrePostCutoff 0.0020 // Comparative Voltage Cutoff - Diff between post-cont and pre-cont
11: voltCompareCutoff 0.0020 // Comparative Voltage Cutoff - Diff between post cont with & without outage
12: shadowPriceChangeCutoff 30.0000 // Comparative Shadow Price value change cutoff - Diff with & without outage
13: shadowPricePctChangeCutoff 25.0000 // Comparative Shadow Price perchange change cutoff - Change as % of max(pre,post) with & without outage
14: trendingChangeMWCutoff 100.0000 // Outage trending status cutoff - Flow Change in MW
15: trendingPercentLoadingChangeCutoff 20.0000 // Outage trending status cutoff - Flow Change as % of Branch Rating
16: trendingShadowPriceChangeCutoff 1000.0000 // Outage trending status cutoff - Change in shadow price
17: consPerMonBran 5 // Number of top contingencies to show per monitored branch
18: consPerMonBus 5 // Number of top contingencies to show per monitored bus
19: N11COMPAREMODE 0 // Compare fist-level results with original case results
20: N11ACSCREEN 0 // ACCont only for contingencies impacted by first-level contingency
21: N11SuppressOrig 0 // Do not print original case info in non-comparative mode
22: saveAMBSeed 0 // Save AMB seed case before for each time period
23: ambSaveDirectory [] // Directory to save cases for saveAMBSeed option
24: savePreOut 0 // Save case before applying Study Outage
25: preOutSaveDirectory [] // Directory to save cases for savePreOut option
26: saveFinalApproved 0 // After evaluation finished, create cases with all APPROVED outages
27: finalSaveDirectory [] // Directory to save cases for saveFinalApproved option
28: saveInitialApproved 0 // Before evaluation starts, create cases with all PREAPPROVED and APPROVED outages
29: initialSaveDirectory [] // Directory to save cases for saveInitialApproved option
30: kVLayer1 5 // 1st kV Layer
31: kVLayer2 5 // 2nd kV Layer
32: kVLayer3 5 // 3rd kV Layer
33: kVLayer4 5 // 4rd kV Layer
34: kVLayer5 5 // 5th kV Layer
35: kVLayer12_Volt 100.0 // Voltage between Layer 1 and Layer 2
36: kVLayer23_Volt 230.0 // Voltage between Layer 2 and Layer 3
37: kVLayer34_Volt 345.0 // Voltage between Layer 3 and Layer 4
38: kVLayer45_Volt 500.0 // Voltage between Layer 4 and Layer 5
39: N11ContScrnVolt 0 // N-1-1 Contingency Screening for voltage
40: kVCutoff 0.00 // Specify kV Cutoff
41: ApplykVCutoffOption 0 // [0-one side only, 1-both sides]
42: dckVLayer1 5 // Primary proximity screen 1st kV Layer
43: dckVLayer2 5 // Primary proximity screen 2nd kV Layer
44: dckVLayer3 5 // Primary proximity screen 3rd kV Layer
45: dckVLayer4 5 // Primary proximity screen 4rd kV Layer
46: dckVLayer5 5 // Primary proximity screen 5th kV Layer
47: dckVLayer12_Volt 100.0 // Primary proximity screen Voltage between Layer 1 and Layer 2
48: dckVLayer23_Volt 230.0 // Primary proximity screen Voltage between Layer 2 and Layer 3
49: dckVLayer34_Volt 345.0 // Primary proximity screen Voltage between Layer 3 and Layer 4
50: dckVLayer45_Volt 500.0 // Primary proximity screen Voltage between Layer 4 and Layer 5
51: N11ContScrnDCAC 0 // N-1-1 Contingency Screening for nearby seconds - do for both DC and AC
52: dckVCutoff 0.00 // Primary proximity Specify kV Cutoff
53: dcApplykVCutoffOption 0 // Primary proximity [0-one side only, 1-both sides]
54: conReduceModeEnabled 0 // Reduce contingency set for each first-level based on region impact screening
55: saveConReduceToFile 0 // Save to file reduced contingency set for each first-level based on region impact screening
56: readConReduceFromFile 0 // Read from file contingency set for each first-level based on region impact screening
57: snapReadConReduceFromFile 1 // Snap Index for reading reduced contingency set for each first-level based on region impact screening
Select data category:(L2): [ 0]
Select main menu function(L1): [ opt] = Selected Function 10 - Options - TARA analysis options
Select data category:(L2): [ EMS] = Selected Function 6 - EMS - Option for EMS case processing/creation
**** Current **** EMS input Options
1: reduceCaseMode 0 // 0 no reduction, 1-basic, 2- remove radial cont/out events(TBD)
2: keepEventsNotActive 0 // 1- keep not active contingent events, 0- remove (PROBE MISO Topology Processor)
3: keepOutagedBreakers 1 // keep outaged breakers in reduced model, 0-no,1-yes (PROBE MISO Topology Porcessor)
4: keepBreakersInSeries 1 // keep breakers in series with physical branch is a part of contingency in reduced model, 0-no,1-yes (PROBE MISO Topology Porcessor)
5: keepShuntsSeparate 0 // keep shunts busbars separate - required for EMS AC solution
6: emsNamingMethod 1 // Method for naming EMS equipment (1-PJM, 2-MISO, 3-ISO-NE)
7: useAUXMonStatus 0 // Use Monitored Branch Status field in AUX file (0-No, 1-Yes)
8: useRateD 0 // if 1, use 4 ratings, A,B for Peak hours (7-23), C,D - off-peak other hours, will be saved in AUX
9: removeOpenedZIL 0 // 1- remove opened zero impedance lines during full study period, 0-do not remove
10: reduceOfflineZIL 0 // 1- remove opened zero impedance lines during full study period, 0-do not remove
11: openHangingBranches 0 // 0-no, 1-open branch if one of ends has opened CB/DIS, 2-only if both end has single CB/DIS
12: IgnoreOutageOverride 0 // Ignore outage override from outage file (used by TARA_OA only) (0-No, 1-Yes)
13: connectEMSGen 0 // Close generator breaker even if opened (1-yes,0-no)
14: studyDayStart [NA] // Define study date start time YYYYMMDDHH format
15: studyDayEnd [NA] // Define study date end time in YYYYMMDDHH format
16: DumpDevicePriorityLevel 0 // Dump device monitoring priority instead of monitoring flag to AUX (1-yes,0-no)
17: DevicePriorityMonit 0 // device priority monitoring criteria(0 - outage coordination(priority>0 and priority<7), 1 - Dayahead(priority==1))
18: auxSFTMode 0 // NE SFT Mode for handling virtual bids (adds load slot for every bus)? (0-no, 1-yes)
19: neOverrideFormat 1 // Format of NE Override Data (0-AUX, 1-CSV)
20: showFgatesSFT 1 // Show flowgate sensitivities in SFT reports? (0-no, 1-yes)
21: showInterfacesSFT 1 // Show flowgate sensitivities in SFT reports? (0-no, 1-yes)
22: misoZBRMethodForRAW34 0 // Ignore MISO ZBR flag and assign based on same station from-to buses? (0-no, 1-yes)
23: parsHoldMWBase 0 // Model PARs as fixed angle or as holding flow (0-fixed angle, 1-hold flow)
Specify option name (or number) and value : [ emsNamingMethod][ 1]
Specify option name (or number) and value : [ useAUXMonStatus][ 0]
Specify option name (or number) and value : [ reduceCaseMode][ 0]
Specify option name (or number) and value : [ neOverrideFormat][ 0]
Specify option name (or number) and value : [ 0]
**** New **** EMS input Options
1: reduceCaseMode 0 // 0 no reduction, 1-basic, 2- remove radial cont/out events(TBD)
2: keepEventsNotActive 0 // 1- keep not active contingent events, 0- remove (PROBE MISO Topology Processor)
3: keepOutagedBreakers 1 // keep outaged breakers in reduced model, 0-no,1-yes (PROBE MISO Topology Porcessor)
4: keepBreakersInSeries 1 // keep breakers in series with physical branch is a part of contingency in reduced model, 0-no,1-yes (PROBE MISO Topology Porcessor)
5: keepShuntsSeparate 0 // keep shunts busbars separate - required for EMS AC solution
6: emsNamingMethod 1 // Method for naming EMS equipment (1-PJM, 2-MISO, 3-ISO-NE)
7: useAUXMonStatus 0 // Use Monitored Branch Status field in AUX file (0-No, 1-Yes)
8: useRateD 0 // if 1, use 4 ratings, A,B for Peak hours (7-23), C,D - off-peak other hours, will be saved in AUX
9: removeOpenedZIL 0 // 1- remove opened zero impedance lines during full study period, 0-do not remove
10: reduceOfflineZIL 0 // 1- remove opened zero impedance lines during full study period, 0-do not remove
11: openHangingBranches 0 // 0-no, 1-open branch if one of ends has opened CB/DIS, 2-only if both end has single CB/DIS
12: IgnoreOutageOverride 0 // Ignore outage override from outage file (used by TARA_OA only) (0-No, 1-Yes)
13: connectEMSGen 0 // Close generator breaker even if opened (1-yes,0-no)
14: studyDayStart [NA] // Define study date start time YYYYMMDDHH format
15: studyDayEnd [NA] // Define study date end time in YYYYMMDDHH format
16: DumpDevicePriorityLevel 0 // Dump device monitoring priority instead of monitoring flag to AUX (1-yes,0-no)
17: DevicePriorityMonit 0 // device priority monitoring criteria(0 - outage coordination(priority>0 and priority<7), 1 - Dayahead(priority==1))
18: auxSFTMode 0 // NE SFT Mode for handling virtual bids (adds load slot for every bus)? (0-no, 1-yes)
19: neOverrideFormat 0 // Format of NE Override Data (0-AUX, 1-CSV)
20: showFgatesSFT 1 // Show flowgate sensitivities in SFT reports? (0-no, 1-yes)
21: showInterfacesSFT 1 // Show flowgate sensitivities in SFT reports? (0-no, 1-yes)
22: misoZBRMethodForRAW34 0 // Ignore MISO ZBR flag and assign based on same station from-to buses? (0-no, 1-yes)
23: parsHoldMWBase 0 // Model PARs as fixed angle or as holding flow (0-fixed angle, 1-hold flow)
Select data category:(L2): [ 0]
Select main menu function(L1): [ lfopt] = Selected Function 11 - LFOPTIONS - LF options
Select data category:(L2): [ solve] = Selected Function 1 - Solve - Solution options
**** Current **** Select LF solution and data options
1: busMismToler 0.1000 // Bus Mismatch tolerance
2: MaxIterLF 50 // Max N of iterations of iterative Load Flow Solution (AC and DC)
3: useFlatStart 0 // Use flat start during LF(0-current voltages;1-flat start)
4: ZeroImpThr 0.000100 // Zero impedance threshold in PU
5: lowVoltCutOffLoad 0.7000 // Scale load down if voltage becomes low
6: maxVoltChangeInit 0.2000 // Max volt magnit change in PU per iteration - init stage
7: maxAngleChangeInit 3.0000 // Max volt angle change in radians per iteration - init stage
8: maxVoltChangeFinal 0.1500 // Max volt magnit change in PU per iteration - final stage
9: maxAngleChangeFinal 1.0000 // Max volt angle change in radians per iteration - final stage
10: numIterInit 3 // Max iteration for initial stage
11: MemFactor 5 // Sparse methods fill in allocation factor
12: voltTolnUser 0.0000 // Voltage magnitude tolerance for voltage controlled buses (if 0.00, will be computed automatically)
13: highVoltCutOffShunt 1.300 // High Voltage cutoff to limit fixed shunts injection
14: lowVoltAddQGen 0 // Add Q at generator buses with low voltage(0-no,1-yes, add Qgen)
15: highVoltReduceShunt 1 // Remove fixed Shunt with high voltage(0-no,1-yes)
16: lowVoltAddShunt 0 // Add Shunts at buses with low voltage(0-no,1-yes, add Qgen)
17: lowVoltCutOffShunt 0.700 // Low voltage cutoff to add shunts if voltage becomes low
18: lowVoltCutOffQGen 0.700 // Low voltage cutoff to add Qgen if voltage becomes low (goes with option 14)
19: highVoltReduceQGen 0 // Reduce Q at generator buses with high voltage below Qmin (0-no,1-yes, add Qgen)
20: highVoltCutOffQGen 1.300 // High Voltage cutoff to reduce Q gen for high voltage
21: fixedQGenRelax 0 // Also, relax Q at generators with Qmin=Qmax (0-no,1-yes)
22: dfaxInjMethod 0 // Compute flows as sum of Dfax times injection
23: BreakerZeroImp 0.0000010000 // Low impedance value in PU to use for breakers and switches
24: ApplyBreakerImpOverride 0 // Apply breaker zero impedance override? (0-no, 1-yes) If disabled, breaker impedance in case will be used.
25: FastModeACCont 0 // Enable fast ACCont mode. Might be less accurate.
26: ToleranceFastModeAC 0.0005000000 // ACCont fast mode tolerance : higher-faster-less accurate, lower-slower-more accurate
Specify option name (or number) and value : [ ApplyBreakerImpOverride][ 0]
Specify option name (or number) and value : [ BreakerZeroImp][ 0.000001]
Specify option name (or number) and value : [ 0]
**** New **** Select LF solution and data options
1: busMismToler 0.1000 // Bus Mismatch tolerance
2: MaxIterLF 50 // Max N of iterations of iterative Load Flow Solution (AC and DC)
3: useFlatStart 0 // Use flat start during LF(0-current voltages;1-flat start)
4: ZeroImpThr 0.000100 // Zero impedance threshold in PU
5: lowVoltCutOffLoad 0.7000 // Scale load down if voltage becomes low
6: maxVoltChangeInit 0.2000 // Max volt magnit change in PU per iteration - init stage
7: maxAngleChangeInit 3.0000 // Max volt angle change in radians per iteration - init stage
8: maxVoltChangeFinal 0.1500 // Max volt magnit change in PU per iteration - final stage
9: maxAngleChangeFinal 1.0000 // Max volt angle change in radians per iteration - final stage
10: numIterInit 3 // Max iteration for initial stage
11: MemFactor 5 // Sparse methods fill in allocation factor
12: voltTolnUser 0.0000 // Voltage magnitude tolerance for voltage controlled buses (if 0.00, will be computed automatically)
13: highVoltCutOffShunt 1.300 // High Voltage cutoff to limit fixed shunts injection
14: lowVoltAddQGen 0 // Add Q at generator buses with low voltage(0-no,1-yes, add Qgen)
15: highVoltReduceShunt 1 // Remove fixed Shunt with high voltage(0-no,1-yes)
16: lowVoltAddShunt 0 // Add Shunts at buses with low voltage(0-no,1-yes, add Qgen)
17: lowVoltCutOffShunt 0.700 // Low voltage cutoff to add shunts if voltage becomes low
18: lowVoltCutOffQGen 0.700 // Low voltage cutoff to add Qgen if voltage becomes low (goes with option 14)
19: highVoltReduceQGen 0 // Reduce Q at generator buses with high voltage below Qmin (0-no,1-yes, add Qgen)
20: highVoltCutOffQGen 1.300 // High Voltage cutoff to reduce Q gen for high voltage
21: fixedQGenRelax 0 // Also, relax Q at generators with Qmin=Qmax (0-no,1-yes)
22: dfaxInjMethod 0 // Compute flows as sum of Dfax times injection
23: BreakerZeroImp 0.0000010000 // Low impedance value in PU to use for breakers and switches
24: ApplyBreakerImpOverride 0 // Apply breaker zero impedance override? (0-no, 1-yes) If disabled, breaker impedance in case will be used.
25: FastModeACCont 0 // Enable fast ACCont mode. Might be less accurate.
26: ToleranceFastModeAC 0.0005000000 // ACCont fast mode tolerance : higher-faster-less accurate, lower-slower-more accurate
Select data category:(L2): [ 0]
Select main menu function(L1): [ lfopt] = Selected Function 11 - LFOPTIONS - LF options
Select data category:(L2): [ misc] = Selected Function 3 - MISC - Miscellaneous options
**** Current **** Select Miscellaneous LF options
1: ZeroImpThr 0.000100 // Zero impedance threshold in PU
2: MemFactor 5 // Sparse methods fill in allocation factor
3: busRepMode 2 // Bus Output Order (1-by names; 2- by numbers)
4: busInputMode 2 // Default Bus input mode (1-names; 2-numbers; 3-branchnames)
5: busOutputMode 2 // Default Bus output mode (1-names; 2-numbers; 3-branchnames)
6: ShowContWarn 1 // Report contingency input warnings during input
7: branNamePrefix [/*] // Branchname prefix
8: branNameSuffix [] // Branchname suffix
9: maxRXRatio 10.00 // Max allowed R/X ratio
10: useCaseNameFullPath 1 // Use LF case name (0) or full path as scenario name(1)
11: readBranchNamesFromRAW 0 // Read branch names from RAW file? (1=yes, 0=no)
12: readEquipNamesFromRAW 0 // Read equipment names (bus, gen,load,branches, shunts) from RAW file (1=yes, 0=no)
13: reportBusAreaName 0 // Add area names to LF data reports(bus, gen,load,branches, shunts)(1=yes, 0=no)
14: reportBusZoneName 0 // Add zone names to LF data reports(bus, gen,load,branches, shunts)(1=yes, 0=no)
15: scaleFactorR 1.000 // Factor to scale down branch resistances (default 1.00 - do not adjust)
16: scaleFactorX 1.000 // Factor to scale down branch impedance (default 1.00 - do not adjust)
17: scaleFactorRLowVolt 1.000 // Factor to scale down branch resistances for low voltage branches
18: scaleFactorXLowVolt 1.000 // Factor to scale down branch impedance for low voltage branches
19: maxBuses 115000 // Maximum number of buses(default 95000)
20: maxBranches 230000 // Maximum number of branches(default 19000), includes 2 and 3 W transf
21: maxGenerators 25000 // Maximum number of generators and plants (default 25000)
22: maxLoads 230000 // Maximum number of loads
23: maxTransfor 40000 // Maximum number of 2W and 3W transformers total
24: maxShunts 20000 // Maximum number of shunts
25: maxStations 50000 // Maximum number of substations
26: rawIDMethod 0 // Remove PTI prefix from RAW number in report header? (1=yes, 0=no)
27: contFormatOut 0 // Contingency file format when creating cont file (0-PTI, 1-AUX,2-GE)
28: applyGenLocal 0 // Set generators to local voltage regulation (1=yes, 0=no)
29: LockSWShunt 0 // Set discrete switched shunt to a fixed mode (1=yes, 0=no)
30: maxEnodes 300000 // Maximum number of enodes for EMS apps
31: shuntMinVoltBand 0.0000 // Minimum voltage bands for shunts (default 0.00 - do not apply)
32: DCLFTapMode 0 // Branch flow model (0-include TAP ratio, 1-ignore TAP) for DC load flow
33: busNameQuotes 0 // DO NOT USE UNLESS YOU HAVE UNUSUAL BUS NAMES. Add single quote character around bus names in reports
34: NoStarBusNumbers 0 // Don't print bus numbers of 3-wind star buses in mon branch reports
35: autoDimensions 1 // Automatically increase case max dimensions if initial are too small [0-no, 1-yes]
Specify option name (or number) and value : [ maxBuses][ 110000]
Specify option name (or number) and value : [ maxBranches][ 190000]
Specify option name (or number) and value : [ maxLoads][ 190000]
Specify option name (or number) and value : [ maxShunts][ 15000]
Specify option name (or number) and value : [ maxTransfor][ 40000]
Specify option name (or number) and value : [ maxGenerators][ 25000]
Specify option name (or number) and value : [ 0]
**** New **** Select Miscellaneous LF options
1: ZeroImpThr 0.000100 // Zero impedance threshold in PU
2: MemFactor 5 // Sparse methods fill in allocation factor
3: busRepMode 2 // Bus Output Order (1-by names; 2- by numbers)
4: busInputMode 2 // Default Bus input mode (1-names; 2-numbers; 3-branchnames)
5: busOutputMode 2 // Default Bus output mode (1-names; 2-numbers; 3-branchnames)
6: ShowContWarn 1 // Report contingency input warnings during input
7: branNamePrefix [/*] // Branchname prefix
8: branNameSuffix [] // Branchname suffix
9: maxRXRatio 10.00 // Max allowed R/X ratio
10: useCaseNameFullPath 1 // Use LF case name (0) or full path as scenario name(1)
11: readBranchNamesFromRAW 0 // Read branch names from RAW file? (1=yes, 0=no)
12: readEquipNamesFromRAW 0 // Read equipment names (bus, gen,load,branches, shunts) from RAW file (1=yes, 0=no)
13: reportBusAreaName 0 // Add area names to LF data reports(bus, gen,load,branches, shunts)(1=yes, 0=no)
14: reportBusZoneName 0 // Add zone names to LF data reports(bus, gen,load,branches, shunts)(1=yes, 0=no)
15: scaleFactorR 1.000 // Factor to scale down branch resistances (default 1.00 - do not adjust)
16: scaleFactorX 1.000 // Factor to scale down branch impedance (default 1.00 - do not adjust)
17: scaleFactorRLowVolt 1.000 // Factor to scale down branch resistances for low voltage branches
18: scaleFactorXLowVolt 1.000 // Factor to scale down branch impedance for low voltage branches
19: maxBuses 110000 // Maximum number of buses(default 95000)
20: maxBranches 190000 // Maximum number of branches(default 19000), includes 2 and 3 W transf
21: maxGenerators 25000 // Maximum number of generators and plants (default 25000)
22: maxLoads 190000 // Maximum number of loads
23: maxTransfor 40000 // Maximum number of 2W and 3W transformers total
24: maxShunts 15000 // Maximum number of shunts
25: maxStations 50000 // Maximum number of substations
26: rawIDMethod 0 // Remove PTI prefix from RAW number in report header? (1=yes, 0=no)
27: contFormatOut 0 // Contingency file format when creating cont file (0-PTI, 1-AUX,2-GE)
28: applyGenLocal 0 // Set generators to local voltage regulation (1=yes, 0=no)
29: LockSWShunt 0 // Set discrete switched shunt to a fixed mode (1=yes, 0=no)
30: maxEnodes 300000 // Maximum number of enodes for EMS apps
31: shuntMinVoltBand 0.0000 // Minimum voltage bands for shunts (default 0.00 - do not apply)
32: DCLFTapMode 0 // Branch flow model (0-include TAP ratio, 1-ignore TAP) for DC load flow
33: busNameQuotes 0 // DO NOT USE UNLESS YOU HAVE UNUSUAL BUS NAMES. Add single quote character around bus names in reports
34: NoStarBusNumbers 0 // Don't print bus numbers of 3-wind star buses in mon branch reports
35: autoDimensions 1 // Automatically increase case max dimensions if initial are too small [0-no, 1-yes]
Select data category:(L2): [ 0]
Select main menu function(L1): [ opt] = Selected Function 10 - Options - TARA analysis options
Select data category:(L2): [ sced] = Selected Function 13 - SCED - SCED/SCRD Options
Select SCED group of options:(L3): [ options] = Selected Function 4 - Options - SCED options and parameters
**** Current **** Select SCED Parameters:
1: maxBidPoints 3000 // Maximum number of Pnodes
2: MAXBIDBLOCKS 3000 // Maximum number of bids/cost curves
3: maxZonFactors 3000 // Maximum number of zonal factors
4: maxOptimPars 100 // Maximum number of optimizable PARs
5: CPNODEMAX 10 // Maximum number of cp nodes for MISO ASM
6: CPNODEPERBUS 10 // Maximum number of cp nodes per bus for MISO ASM
Specify option name (or number) and value : [ CPNODEMAX][ 10]
Specify option name (or number) and value : [ CPNODEPERBUS][ 10]
Specify option name (or number) and value : [ 0]
**** New **** Select SCED Parameters:
1: maxBidPoints 3000 // Maximum number of Pnodes
2: MAXBIDBLOCKS 3000 // Maximum number of bids/cost curves
3: maxZonFactors 3000 // Maximum number of zonal factors
4: maxOptimPars 100 // Maximum number of optimizable PARs
5: CPNODEMAX 10 // Maximum number of cp nodes for MISO ASM
6: CPNODEPERBUS 10 // Maximum number of cp nodes per bus for MISO ASM
Select SCED group of options:(L3): [ 0]
Select data category:(L2): [ 0]
Select main menu function(L1): [ lfopt] = Selected Function 11 - LFOPTIONS - LF options
Select data category:(L2): [ solve] = Selected Function 1 - Solve - Solution options
**** Current **** Select LF solution and data options
1: busMismToler 0.1000 // Bus Mismatch tolerance
2: MaxIterLF 50 // Max N of iterations of iterative Load Flow Solution (AC and DC)
3: useFlatStart 0 // Use flat start during LF(0-current voltages;1-flat start)
4: ZeroImpThr 0.000100 // Zero impedance threshold in PU
5: lowVoltCutOffLoad 0.7000 // Scale load down if voltage becomes low
6: maxVoltChangeInit 0.2000 // Max volt magnit change in PU per iteration - init stage
7: maxAngleChangeInit 3.0000 // Max volt angle change in radians per iteration - init stage
8: maxVoltChangeFinal 0.1500 // Max volt magnit change in PU per iteration - final stage
9: maxAngleChangeFinal 1.0000 // Max volt angle change in radians per iteration - final stage
10: numIterInit 3 // Max iteration for initial stage
11: MemFactor 5 // Sparse methods fill in allocation factor
12: voltTolnUser 0.0000 // Voltage magnitude tolerance for voltage controlled buses (if 0.00, will be computed automatically)
13: highVoltCutOffShunt 1.300 // High Voltage cutoff to limit fixed shunts injection
14: lowVoltAddQGen 0 // Add Q at generator buses with low voltage(0-no,1-yes, add Qgen)
15: highVoltReduceShunt 1 // Remove fixed Shunt with high voltage(0-no,1-yes)
16: lowVoltAddShunt 0 // Add Shunts at buses with low voltage(0-no,1-yes, add Qgen)
17: lowVoltCutOffShunt 0.700 // Low voltage cutoff to add shunts if voltage becomes low
18: lowVoltCutOffQGen 0.700 // Low voltage cutoff to add Qgen if voltage becomes low (goes with option 14)
19: highVoltReduceQGen 0 // Reduce Q at generator buses with high voltage below Qmin (0-no,1-yes, add Qgen)
20: highVoltCutOffQGen 1.300 // High Voltage cutoff to reduce Q gen for high voltage
21: fixedQGenRelax 0 // Also, relax Q at generators with Qmin=Qmax (0-no,1-yes)
22: dfaxInjMethod 0 // Compute flows as sum of Dfax times injection
23: BreakerZeroImp 0.0000010000 // Low impedance value in PU to use for breakers and switches
24: ApplyBreakerImpOverride 0 // Apply breaker zero impedance override? (0-no, 1-yes) If disabled, breaker impedance in case will be used.
25: FastModeACCont 0 // Enable fast ACCont mode. Might be less accurate.
26: ToleranceFastModeAC 0.0005000000 // ACCont fast mode tolerance : higher-faster-less accurate, lower-slower-more accurate
Specify option name (or number) and value : [ busMismToler][ 1]
Specify option name (or number) and value : [ MaxIterLF][ 50]
Specify option name (or number) and value : [ useFlatStart][ 0]
Specify option name (or number) and value : [ ZeroImpThr][ 0.0001]
Specify option name (or number) and value : [ lowVoltCutOffLoad][ 0.8]
Specify option name (or number) and value : [ maxVoltChangeInit][ 0.2]
Specify option name (or number) and value : [ maxAngleChangeInit][ 3]
Specify option name (or number) and value : [ maxVoltChangeFinal][ 0.15]
Specify option name (or number) and value : [ maxAngleChangeFinal][ 1]
Specify option name (or number) and value : [ numIterInit][ 3]
Specify option name (or number) and value : [ MemFactor][ 5]
Specify option name (or number) and value : [ voltTolnUser][ 0]
Specify option name (or number) and value : [ lowVoltAddQGen][ 0]
Specify option name (or number) and value : [ lowVoltCutOffQGen][ 0.7]
Specify option name (or number) and value : [ highVoltReduceQGen][ 0]
Specify option name (or number) and value : [ highVoltCutOffQGen][ 1.3]
Specify option name (or number) and value : [ fixedQGenRelax][ 0]
Specify option name (or number) and value : [ lowVoltAddShunt][ 0]
Specify option name (or number) and value : [ lowVoltCutOffShunt][ 0.7]
Specify option name (or number) and value : [ highVoltReduceShunt][ 0]
Specify option name (or number) and value : [ highVoltCutOffShunt][ 1.25]
Specify option name (or number) and value : [ 0]
**** New **** Select LF solution and data options
1: busMismToler 1.0000 // Bus Mismatch tolerance
2: MaxIterLF 50 // Max N of iterations of iterative Load Flow Solution (AC and DC)
3: useFlatStart 0 // Use flat start during LF(0-current voltages;1-flat start)
4: ZeroImpThr 0.000100 // Zero impedance threshold in PU
5: lowVoltCutOffLoad 0.8000 // Scale load down if voltage becomes low
6: maxVoltChangeInit 0.2000 // Max volt magnit change in PU per iteration - init stage
7: maxAngleChangeInit 3.0000 // Max volt angle change in radians per iteration - init stage
8: maxVoltChangeFinal 0.1500 // Max volt magnit change in PU per iteration - final stage
9: maxAngleChangeFinal 1.0000 // Max volt angle change in radians per iteration - final stage
10: numIterInit 3 // Max iteration for initial stage
11: MemFactor 5 // Sparse methods fill in allocation factor
12: voltTolnUser 0.0000 // Voltage magnitude tolerance for voltage controlled buses (if 0.00, will be computed automatically)
13: highVoltCutOffShunt 1.250 // High Voltage cutoff to limit fixed shunts injection
14: lowVoltAddQGen 0 // Add Q at generator buses with low voltage(0-no,1-yes, add Qgen)
15: highVoltReduceShunt 0 // Remove fixed Shunt with high voltage(0-no,1-yes)
16: lowVoltAddShunt 0 // Add Shunts at buses with low voltage(0-no,1-yes, add Qgen)
17: lowVoltCutOffShunt 0.700 // Low voltage cutoff to add shunts if voltage becomes low
18: lowVoltCutOffQGen 0.700 // Low voltage cutoff to add Qgen if voltage becomes low (goes with option 14)
19: highVoltReduceQGen 0 // Reduce Q at generator buses with high voltage below Qmin (0-no,1-yes, add Qgen)
20: highVoltCutOffQGen 1.300 // High Voltage cutoff to reduce Q gen for high voltage
21: fixedQGenRelax 0 // Also, relax Q at generators with Qmin=Qmax (0-no,1-yes)
22: dfaxInjMethod 0 // Compute flows as sum of Dfax times injection
23: BreakerZeroImp 0.0000010000 // Low impedance value in PU to use for breakers and switches
24: ApplyBreakerImpOverride 0 // Apply breaker zero impedance override? (0-no, 1-yes) If disabled, breaker impedance in case will be used.
25: FastModeACCont 0 // Enable fast ACCont mode. Might be less accurate.
26: ToleranceFastModeAC 0.0005000000 // ACCont fast mode tolerance : higher-faster-less accurate, lower-slower-more accurate
Select data category:(L2): [ 0]
Select main menu function(L1): [ lfopt] = Selected Function 11 - LFOPTIONS - LF options
Select data category:(L2): [ adj] = Selected Function 2 - Adjustment - LF adjustment options
**** Current **** LF adjustment options:
1: iterCheckVarLimitHotStart 0 // Iteration to start generator VAR limit checking - hot start
2: iterCheckVarLimitFlat 3 // Iteration to start generator VAR limit checking - flat start
3: PAR_AdjEnabledLF 0 // Phase Shifter Adjustment (0-off: 1-ON)
4: areaInterAdjustEnabled 0 // Area interchange control (0-no:1-ties;2-ties and external load,3-scale area load)
5: TAP_AdjEnabledLF 0 // Enable TAP adjustment(0-no:1-yes)
6: shuntAdjEnabled 1 // Enable shunt adjustment(0-no;1-continuous only;2-continuous and discrete )
7: DCLineAdjEnabled 1 // Enable DC lines TAP adjustments(0-no:1-yes)
8: showParAdj 0 // Report Phase shifter adjustments per iteration(0-no:1-summary Only: 2-Violated. 3-All)
9: showTapAdj 0 // Report TAP and DC lines adjustments per iteration(0-no:1-summary: 2-all)
10: showShuntAdj 0 // Report Shunt adjustments per iteration(0-;o:1-viol; Only: 2-all)
11: showAreaInterAdj 0 // Report Area interchange adjustments (0-no;1-summary;2-failed tolerance;3-all)
12: showDCLineAdj 0 // Report DC lines TAP adjustment-same as TAP for now
13: busMismTolerAreaInter 10.0000 // Bus Mismatch tolerance to start area adjustments
14: maxVarLimitsBusTypeChanges 6 // Max times voltage controlled bus can change PV-->PQ type. Stop checking limit after
15: iterCheckVarLimitLast 30 // Iteration to stop checking var limits
16: maxAdjustIterVolt 30 // Iteration to stop TAP and Shunt adjustments
17: deacFactRTap 1.0000 // Voltage adjustment deacceleration factor
18: deacFactShunt 1.0000 // Shunt adjustment deacceleration factor (for discrete step shunts)
19: maxTapChange 0.0300 // Max tap ratio change per iteration
20: voltAdjTrigger 0.0050 // Max voltage magnitude change to activate TAP and Shunt adjustments
21: angleAdjTrigger 0.2000 // Max voltage angle change (in degrees) to activate PAR and area interchange adjustments
22: showBusTypeChan 0 // Show voltage controlled buses type changes (0-no;1-summary;2-per iteration)
23: showMismOnFail 2 // Show bus Mismatches if ACLF failed (0-no,1-list of buses, 2- bus flow details)
24: deOscilFactor 0.7000 // De-oscillation factor (if 1.0-not activated) for FastDec solution step
25: areaInterAdjustEdit 1 // Adjust area interchange when editing generation and load. 0-no:1-ties;2-ties and external load)
26: fixedToSwitched 0 // Convert all fixed bus shunts in the case to switched discrete shunts.
27: inServiceSwitchedShunts 0 // When reading the case, set status of all switched shunts in the case to in-service.
28: changeSwitchedShuntsMode1 0 // When reading the case, set control mode of all mode 0 switched shunts to mode 1.
Specify option name (or number) and value : [ iterCheckVarLimitHotStart][ 0]
Specify option name (or number) and value : [ iterCheckVarLimitFlat][ 3]
Specify option name (or number) and value : [ PAR_AdjEnabledLF][ 1]
Specify option name (or number) and value : [ areaInterAdjustEnabled][ 0]
Specify option name (or number) and value : [ TAP_AdjEnabledLF][ 1]
Specify option name (or number) and value : [ shuntAdjEnabled][ 2]
Specify option name (or number) and value : [ fixedToSwitched][ 0]
Specify option name (or number) and value : [ DCLineAdjEnabled][ 1]
Specify option name (or number) and value : [ showParAdj][ 1]
Specify option name (or number) and value : [ showTapAdj][ 1]
Specify option name (or number) and value : [ showShuntAdj][ 1]
Specify option name (or number) and value : [ showAreaInterAdj][ 1]
Specify option name (or number) and value : [ busMismTolerAreaInter][ 5]
Specify option name (or number) and value : [ maxVarLimitsBusTypeChanges][ 6]
Specify option name (or number) and value : [ iterCheckVarLimitLast][ 40]
Specify option name (or number) and value : [ maxAdjustIterVolt][ 30]
Specify option name (or number) and value : [ deacFactRTap][ 1]
Specify option name (or number) and value : [ maxTapChange][ 0.02]
Specify option name (or number) and value : [ voltAdjTrigger][ 0.05]
Specify option name (or number) and value : [ angleAdjTrigger][ 0.2]
Specify option name (or number) and value : [ showBusTypeChan][ 0]
Specify option name (or number) and value : [ deOscilFactor][ 0.7]
Specify option name (or number) and value : [ 0]
**** New **** LF adjustment options:
1: iterCheckVarLimitHotStart 0 // Iteration to start generator VAR limit checking - hot start
2: iterCheckVarLimitFlat 3 // Iteration to start generator VAR limit checking - flat start
3: PAR_AdjEnabledLF 1 // Phase Shifter Adjustment (0-off: 1-ON)
4: areaInterAdjustEnabled 0 // Area interchange control (0-no:1-ties;2-ties and external load,3-scale area load)
5: TAP_AdjEnabledLF 1 // Enable TAP adjustment(0-no:1-yes)
6: shuntAdjEnabled 2 // Enable shunt adjustment(0-no;1-continuous only;2-continuous and discrete )
7: DCLineAdjEnabled 1 // Enable DC lines TAP adjustments(0-no:1-yes)
8: showParAdj 1 // Report Phase shifter adjustments per iteration(0-no:1-summary Only: 2-Violated. 3-All)
9: showTapAdj 1 // Report TAP and DC lines adjustments per iteration(0-no:1-summary: 2-all)
10: showShuntAdj 1 // Report Shunt adjustments per iteration(0-;o:1-viol; Only: 2-all)
11: showAreaInterAdj 1 // Report Area interchange adjustments (0-no;1-summary;2-failed tolerance;3-all)
12: showDCLineAdj 0 // Report DC lines TAP adjustment-same as TAP for now
13: busMismTolerAreaInter 5.0000 // Bus Mismatch tolerance to start area adjustments
14: maxVarLimitsBusTypeChanges 6 // Max times voltage controlled bus can change PV-->PQ type. Stop checking limit after
15: iterCheckVarLimitLast 40 // Iteration to stop checking var limits
16: maxAdjustIterVolt 30 // Iteration to stop TAP and Shunt adjustments
17: deacFactRTap 1.0000 // Voltage adjustment deacceleration factor
18: deacFactShunt 1.0000 // Shunt adjustment deacceleration factor (for discrete step shunts)
19: maxTapChange 0.0200 // Max tap ratio change per iteration
20: voltAdjTrigger 0.0500 // Max voltage magnitude change to activate TAP and Shunt adjustments
21: angleAdjTrigger 0.2000 // Max voltage angle change (in degrees) to activate PAR and area interchange adjustments
22: showBusTypeChan 0 // Show voltage controlled buses type changes (0-no;1-summary;2-per iteration)
23: showMismOnFail 2 // Show bus Mismatches if ACLF failed (0-no,1-list of buses, 2- bus flow details)
24: deOscilFactor 0.7000 // De-oscillation factor (if 1.0-not activated) for FastDec solution step
25: areaInterAdjustEdit 1 // Adjust area interchange when editing generation and load. 0-no:1-ties;2-ties and external load)
26: fixedToSwitched 0 // Convert all fixed bus shunts in the case to switched discrete shunts.
27: inServiceSwitchedShunts 0 // When reading the case, set status of all switched shunts in the case to in-service.
28: changeSwitchedShuntsMode1 0 // When reading the case, set control mode of all mode 0 switched shunts to mode 1.
Select data category:(L2): [ 0]
Select main menu function(L1): [ lfopt] = Selected Function 11 - LFOPTIONS - LF options
Select data category:(L2): [ misc] = Selected Function 3 - MISC - Miscellaneous options
**** Current **** Select Miscellaneous LF options
1: ZeroImpThr 0.000100 // Zero impedance threshold in PU
2: MemFactor 5 // Sparse methods fill in allocation factor
3: busRepMode 2 // Bus Output Order (1-by names; 2- by numbers)
4: busInputMode 2 // Default Bus input mode (1-names; 2-numbers; 3-branchnames)
5: busOutputMode 2 // Default Bus output mode (1-names; 2-numbers; 3-branchnames)
6: ShowContWarn 1 // Report contingency input warnings during input
7: branNamePrefix [/*] // Branchname prefix
8: branNameSuffix [] // Branchname suffix
9: maxRXRatio 10.00 // Max allowed R/X ratio
10: useCaseNameFullPath 1 // Use LF case name (0) or full path as scenario name(1)
11: readBranchNamesFromRAW 0 // Read branch names from RAW file? (1=yes, 0=no)
12: readEquipNamesFromRAW 0 // Read equipment names (bus, gen,load,branches, shunts) from RAW file (1=yes, 0=no)
13: reportBusAreaName 0 // Add area names to LF data reports(bus, gen,load,branches, shunts)(1=yes, 0=no)
14: reportBusZoneName 0 // Add zone names to LF data reports(bus, gen,load,branches, shunts)(1=yes, 0=no)
15: scaleFactorR 1.000 // Factor to scale down branch resistances (default 1.00 - do not adjust)
16: scaleFactorX 1.000 // Factor to scale down branch impedance (default 1.00 - do not adjust)
17: scaleFactorRLowVolt 1.000 // Factor to scale down branch resistances for low voltage branches
18: scaleFactorXLowVolt 1.000 // Factor to scale down branch impedance for low voltage branches
19: maxBuses 110000 // Maximum number of buses(default 95000)
20: maxBranches 190000 // Maximum number of branches(default 19000), includes 2 and 3 W transf
21: maxGenerators 25000 // Maximum number of generators and plants (default 25000)
22: maxLoads 190000 // Maximum number of loads
23: maxTransfor 40000 // Maximum number of 2W and 3W transformers total
24: maxShunts 15000 // Maximum number of shunts
25: maxStations 50000 // Maximum number of substations
26: rawIDMethod 0 // Remove PTI prefix from RAW number in report header? (1=yes, 0=no)
27: contFormatOut 0 // Contingency file format when creating cont file (0-PTI, 1-AUX,2-GE)
28: applyGenLocal 0 // Set generators to local voltage regulation (1=yes, 0=no)
29: LockSWShunt 0 // Set discrete switched shunt to a fixed mode (1=yes, 0=no)
30: maxEnodes 300000 // Maximum number of enodes for EMS apps
31: shuntMinVoltBand 0.0000 // Minimum voltage bands for shunts (default 0.00 - do not apply)
32: DCLFTapMode 0 // Branch flow model (0-include TAP ratio, 1-ignore TAP) for DC load flow
33: busNameQuotes 0 // DO NOT USE UNLESS YOU HAVE UNUSUAL BUS NAMES. Add single quote character around bus names in reports
34: NoStarBusNumbers 0 // Don't print bus numbers of 3-wind star buses in mon branch reports
35: autoDimensions 1 // Automatically increase case max dimensions if initial are too small [0-no, 1-yes]
Specify option name (or number) and value : [ useCaseNameFullPath][ 0]
Specify option name (or number) and value : [ branNamePrefix][ "/* ["]
Specify option name (or number) and value : [ branNameSuffix][ "]"]
Specify option name (or number) and value : [ readEquipNamesFromRAW][ 0]
Specify option name (or number) and value : [ reportBusAreaName][ 0]
Specify option name (or number) and value : [ reportBusZoneName][ 0]
Specify option name (or number) and value : [ busNameQuotes][ 0]
Specify option name (or number) and value : [ NoStarBusNumbers][ 0]
Specify option name (or number) and value : [ 0]
**** New **** Select Miscellaneous LF options
1: ZeroImpThr 0.000100 // Zero impedance threshold in PU
2: MemFactor 5 // Sparse methods fill in allocation factor
3: busRepMode 2 // Bus Output Order (1-by names; 2- by numbers)
4: busInputMode 2 // Default Bus input mode (1-names; 2-numbers; 3-branchnames)
5: busOutputMode 2 // Default Bus output mode (1-names; 2-numbers; 3-branchnames)
6: ShowContWarn 1 // Report contingency input warnings during input
7: branNamePrefix [/* [] // Branchname prefix
8: branNameSuffix []] // Branchname suffix
9: maxRXRatio 10.00 // Max allowed R/X ratio
10: useCaseNameFullPath 0 // Use LF case name (0) or full path as scenario name(1)
11: readBranchNamesFromRAW 0 // Read branch names from RAW file? (1=yes, 0=no)
12: readEquipNamesFromRAW 0 // Read equipment names (bus, gen,load,branches, shunts) from RAW file (1=yes, 0=no)
13: reportBusAreaName 0 // Add area names to LF data reports(bus, gen,load,branches, shunts)(1=yes, 0=no)
14: reportBusZoneName 0 // Add zone names to LF data reports(bus, gen,load,branches, shunts)(1=yes, 0=no)
15: scaleFactorR 1.000 // Factor to scale down branch resistances (default 1.00 - do not adjust)
16: scaleFactorX 1.000 // Factor to scale down branch impedance (default 1.00 - do not adjust)
17: scaleFactorRLowVolt 1.000 // Factor to scale down branch resistances for low voltage branches
18: scaleFactorXLowVolt 1.000 // Factor to scale down branch impedance for low voltage branches
19: maxBuses 110000 // Maximum number of buses(default 95000)
20: maxBranches 190000 // Maximum number of branches(default 19000), includes 2 and 3 W transf
21: maxGenerators 25000 // Maximum number of generators and plants (default 25000)
22: maxLoads 190000 // Maximum number of loads
23: maxTransfor 40000 // Maximum number of 2W and 3W transformers total
24: maxShunts 15000 // Maximum number of shunts
25: maxStations 50000 // Maximum number of substations
26: rawIDMethod 0 // Remove PTI prefix from RAW number in report header? (1=yes, 0=no)
27: contFormatOut 0 // Contingency file format when creating cont file (0-PTI, 1-AUX,2-GE)
28: applyGenLocal 0 // Set generators to local voltage regulation (1=yes, 0=no)
29: LockSWShunt 0 // Set discrete switched shunt to a fixed mode (1=yes, 0=no)
30: maxEnodes 300000 // Maximum number of enodes for EMS apps
31: shuntMinVoltBand 0.0000 // Minimum voltage bands for shunts (default 0.00 - do not apply)
32: DCLFTapMode 0 // Branch flow model (0-include TAP ratio, 1-ignore TAP) for DC load flow
33: busNameQuotes 0 // DO NOT USE UNLESS YOU HAVE UNUSUAL BUS NAMES. Add single quote character around bus names in reports
34: NoStarBusNumbers 0 // Don't print bus numbers of 3-wind star buses in mon branch reports
35: autoDimensions 1 // Automatically increase case max dimensions if initial are too small [0-no, 1-yes]
Select data category:(L2): [ 0]
Select main menu function(L1): [ opt] = Selected Function 10 - Options - TARA analysis options
Select data category:(L2): [ cont] = Selected Function 1 - CONTING - Contingency analysis option
**** Current **** Contingency analysis options:
1: monBranRatingBase 1 // Base case rating (1-A;2-B;3-C;4-D)
2: monBranRatingCont 2 // Contingency rating (1-A;2-B;3-C;4-D)
3: monBranRatingMultBase 100.00 // Base case rating multipliers
4: monBranRatingMultCont 100.00 // Contingency rating multipliers
5: contChanCutOffMW 5.0 // MW cutoff to ignore constraints if cont.flow doesn't changes from the base case more than
6: contChanCutOffPercent 2.0 // Rating %% cutoff to ignore if cont.flow changes from the base case is less than
7: PAR_AdjEnabledContAnal 1 // Phase shifter model for the base case (0-fixed angle;1-control flow), always fixed in contingency
8: adjustRatingMVA 0 // Adjust branch MW rating based on MVAR flow (DC analysis)
9: limitTypeLine 0 // Use AMP (=0) or MVA (1) limit to check lines violation in AC mode
10: limitTypeTran 1 // Use AMP (=0) or MVA (1) limit to check transformer violation in AC mode
11: voltMinChange 0.0050 // Voltage change cutoff in PU to ignore voltage violations with change from the base case is smaller
12: numContMaxAlloc 15000 // Max number of contingencies
13: numEventsAlloc 35000 // Max number of contingency events
14: numDispEventAlloc 60000 // Max number of generation redispatch events
15: numLFgatesMaxAlloc 10000 // Max number of flowgates
16: maxFgateBranches 100 // Max number of branches (events) per flowgate
17: mulSecPrintMode 0 // Multi-section line modeling (0-ignore;1-honor)
18: smartCutOff 0 // Use Smart cutoff based on Max conting impact using base case and conting rating difference (0-no;1-yes)
19: maxExcludesAlloc 10000 // Max number of exclude records
20: showConAnalLFLog 0 // Show LF convergence during ACCONT
21: MAXOUTAGES 15000 // Maximum number of outages
22: maxORAFlowResults 2000000 // Maximum number of ORA or N-1-1 results to report
23: ACCONTRepeatSolution 0 // If first AC solution failed, repeat with alternative Flat/Hot start(0-no,1-yes),2-limit to the best iteration
24: showNotMappedContEvents 1 // When generating contingency file, show not mapped event(0-no,1-yes)
25: monBranRatingEnAdd1 0 // Enable first additional rating reporting (0-no,1-yes)
26: monBranRatingEnAdd2 0 // Enable second additional rating reporting (0-no,1-yes)
27: monBranRatingAdd1 3 // Additional Rating 1 (1-A;2-B;3-C;4-D)
28: monBranRatingAdd2 3 // Additional Rating 2 (1-A;2-B;3-C;4-D)
29: monBranRatingMultAdd1 100.00 // Additional Rating 1 multiplier
30: monBranRatingMultAdd2 100.00 // Additional Rating 2 multiplier
31: LoadingCutOff 0.00 // Loading cutoff in percent for displaying cont analysis flow results
32: showAllHighPreSCD 0 // Show SCD result if pre-SCD above cutoff but post-SCD below
33: N11MODE 1 // Run in N-1+Application Mode
34: multiCoreN1 0 // Run in N-1 ACCont in multi-core mode? [0-No, 1-Yes]
35: numLowestLoading 5 // Max number of lowest loading results to report
36: VoltLimAdder 0.00000 // Add this to voltage limit to expand or limit hi/low voltage viol results
37: StudyFiles 0 // Show Names of Input Files on all reports
38: MonConMode 1 // Select Mon/Con mode (1:Regular, 2:Flowgate, 3:Voltgate, 4:Flowgate & Voltgate
39: MaxMonConMode 100000 // Maximum Number of mon/con mode entries
40: keepDuplicates 1 // Keep contingency even if exact duplicate? [0=no, 1=yes]
41: correctiveSwitchingMode 0 // Run in corrective switching mode? [0=no, 1=yes]
42: lodfCutoff 0.01000 // Cutoff for LODF report (absolute value)
43: lodfImpCutoff 1.00 // MW cutoff for LODF Impact report (lodf*(event rating))
44: maxFgEventTotal 30000 // Max number of all branches and events for all flowgatesflowgate
45: maxEvPerCont 60 // Max number of events (events) per contingency
46: maxSPSLogic 10000 // Max number of SPS logic elements
47: maxInjGroups 500 // Max number of SPS AUX Injections Groups
48: maxSPSInterfaces 1000 // Max number of SPS AUX Interfaces
49: co_mode 0 // Cascading mode, 0=no, 1=yes
50: co_branchoutage 1 // Trip Overloaded Branches in Cascading Outage, 0=no, 1=yes
51: co_genoutage 1 // Trip Generators in Cascading Outage, 0=no, 1=yes
52: co_genterminalbus 0 // Trip Generators with low voltage violation at generator terminal bus, 0=no, 1=yes
53: co_loadoutage 1 // Trip Loads in Cascading Outage, 0=no, 1=yes
54: co_maxlevel 10 // Maximum cascading outage test level
55: saveCOCases 0 // Save a case for each cascading step case
56: COSaveDirectory [] // Folder to save each cascading outage case
57: kVLayer12_Volt 100.0 // Voltage between Layer 1 and Layer 2
58: kVLayer23_Volt 230.0 // Voltage between Layer 2 and Layer 3
59: kVLayer34_Volt 345.0 // Voltage between Layer 3 and Layer 4
60: kVLayer45_Volt 500.0 // Voltage between Layer 4 and Layer 5
61: kVLayer1_LDCutoff 115.0 // Layer 1 RelayLoadability Percent
62: kVLayer2_LDCutoff 115.0 // Layer 2 RelayLoadability Percent
63: kVLayer3_LDCutoff 115.0 // Layer 3 RelayLoadability Percent
64: kVLayer4_LDCutoff 115.0 // Layer 4 RelayLoadability Percent
65: kVLayer5_LDCutoff 115.0 // Layer 5 RelayLoadability Percent
66: zeroRatingCutoff 0.000100 // If rating is below this, set rating to 9999
67: saveN11Cases 0 // Save a case for each N-1-1 first-level case
68: N11SaveDirectory [] // Folder to save each N-1-1 first-level case
69: acVerifyFgate 0 // Enable flowgate AC verification (0-No;1-Yes)
70: useContingencyComments 0 // Use Comments in contingency file in contingency reporting
71: ignoreEnd2Exit 0 // Ignore END statement to exit reading sub mon con exc files (0-No, 1-Yes)
72: nearSyskVLayer1 5 // Subsystem proximity screen 1st kV Layer
73: nearSyskVLayer2 5 // Subsystem proximity screen 2nd kV Layer
74: nearSyskVLayer3 5 // Subsystem proximity screen 3rd kV Layer
75: nearSyskVLayer4 5 // Subsystem proximity screen 4rd kV Layer
76: nearSyskVLayer5 5 // Subsystem proximity screen 5th kV Layer
77: nearSyskVLayer12_Volt 100.0 // Subsystem proximity screen Voltage between Layer 1 and Layer 2
78: nearSyskVLayer23_Volt 230.0 // Subsystem proximity screen Voltage between Layer 2 and Layer 3
79: nearSyskVLayer34_Volt 345.0 // Subsystem proximity screen Voltage between Layer 3 and Layer 4
80: nearSyskVLayer45_Volt 500.0 // Subsystem proximity screen Voltage between Layer 4 and Layer 5
81: nearSysScrnMod 0 // Subsystem Screening for nearby contingencies (1st and 2nd)
82: nearSyskVCutoff 0.00 // Subsystem proximity Specify kV Cutoff
83: nearSysApplykVCutoffOption 0 // Subsystem proximity [0-one side only, 1-both sides]
84: nearByLayerSubSysName [Undefined] // - Subsystem Name for proximity contingency layer screen
Specify option name (or number) and value : [ ignoreEnd2Exit][ 0]
Specify option name (or number) and value : [ 0]
**** New **** Contingency analysis options:
1: monBranRatingBase 1 // Base case rating (1-A;2-B;3-C;4-D)
2: monBranRatingCont 2 // Contingency rating (1-A;2-B;3-C;4-D)
3: monBranRatingMultBase 100.00 // Base case rating multipliers
4: monBranRatingMultCont 100.00 // Contingency rating multipliers
5: contChanCutOffMW 5.0 // MW cutoff to ignore constraints if cont.flow doesn't changes from the base case more than
6: contChanCutOffPercent 2.0 // Rating %% cutoff to ignore if cont.flow changes from the base case is less than
7: PAR_AdjEnabledContAnal 1 // Phase shifter model for the base case (0-fixed angle;1-control flow), always fixed in contingency
8: adjustRatingMVA 0 // Adjust branch MW rating based on MVAR flow (DC analysis)
9: limitTypeLine 0 // Use AMP (=0) or MVA (1) limit to check lines violation in AC mode
10: limitTypeTran 1 // Use AMP (=0) or MVA (1) limit to check transformer violation in AC mode
11: voltMinChange 0.0050 // Voltage change cutoff in PU to ignore voltage violations with change from the base case is smaller
12: numContMaxAlloc 15000 // Max number of contingencies
13: numEventsAlloc 35000 // Max number of contingency events
14: numDispEventAlloc 60000 // Max number of generation redispatch events
15: numLFgatesMaxAlloc 10000 // Max number of flowgates
16: maxFgateBranches 100 // Max number of branches (events) per flowgate
17: mulSecPrintMode 0 // Multi-section line modeling (0-ignore;1-honor)
18: smartCutOff 0 // Use Smart cutoff based on Max conting impact using base case and conting rating difference (0-no;1-yes)
19: maxExcludesAlloc 10000 // Max number of exclude records
20: showConAnalLFLog 0 // Show LF convergence during ACCONT
21: MAXOUTAGES 15000 // Maximum number of outages
22: maxORAFlowResults 2000000 // Maximum number of ORA or N-1-1 results to report
23: ACCONTRepeatSolution 0 // If first AC solution failed, repeat with alternative Flat/Hot start(0-no,1-yes),2-limit to the best iteration
24: showNotMappedContEvents 1 // When generating contingency file, show not mapped event(0-no,1-yes)
25: monBranRatingEnAdd1 0 // Enable first additional rating reporting (0-no,1-yes)
26: monBranRatingEnAdd2 0 // Enable second additional rating reporting (0-no,1-yes)
27: monBranRatingAdd1 3 // Additional Rating 1 (1-A;2-B;3-C;4-D)
28: monBranRatingAdd2 3 // Additional Rating 2 (1-A;2-B;3-C;4-D)
29: monBranRatingMultAdd1 100.00 // Additional Rating 1 multiplier
30: monBranRatingMultAdd2 100.00 // Additional Rating 2 multiplier
31: LoadingCutOff 0.00 // Loading cutoff in percent for displaying cont analysis flow results
32: showAllHighPreSCD 0 // Show SCD result if pre-SCD above cutoff but post-SCD below
33: N11MODE 1 // Run in N-1+Application Mode
34: multiCoreN1 0 // Run in N-1 ACCont in multi-core mode? [0-No, 1-Yes]
35: numLowestLoading 5 // Max number of lowest loading results to report
36: VoltLimAdder 0.00000 // Add this to voltage limit to expand or limit hi/low voltage viol results
37: StudyFiles 0 // Show Names of Input Files on all reports
38: MonConMode 1 // Select Mon/Con mode (1:Regular, 2:Flowgate, 3:Voltgate, 4:Flowgate & Voltgate
39: MaxMonConMode 100000 // Maximum Number of mon/con mode entries
40: keepDuplicates 1 // Keep contingency even if exact duplicate? [0=no, 1=yes]
41: correctiveSwitchingMode 0 // Run in corrective switching mode? [0=no, 1=yes]
42: lodfCutoff 0.01000 // Cutoff for LODF report (absolute value)
43: lodfImpCutoff 1.00 // MW cutoff for LODF Impact report (lodf*(event rating))
44: maxFgEventTotal 30000 // Max number of all branches and events for all flowgatesflowgate
45: maxEvPerCont 60 // Max number of events (events) per contingency
46: maxSPSLogic 10000 // Max number of SPS logic elements
47: maxInjGroups 500 // Max number of SPS AUX Injections Groups
48: maxSPSInterfaces 1000 // Max number of SPS AUX Interfaces
49: co_mode 0 // Cascading mode, 0=no, 1=yes
50: co_branchoutage 1 // Trip Overloaded Branches in Cascading Outage, 0=no, 1=yes
51: co_genoutage 1 // Trip Generators in Cascading Outage, 0=no, 1=yes
52: co_genterminalbus 0 // Trip Generators with low voltage violation at generator terminal bus, 0=no, 1=yes
53: co_loadoutage 1 // Trip Loads in Cascading Outage, 0=no, 1=yes
54: co_maxlevel 10 // Maximum cascading outage test level
55: saveCOCases 0 // Save a case for each cascading step case
56: COSaveDirectory [] // Folder to save each cascading outage case
57: kVLayer12_Volt 100.0 // Voltage between Layer 1 and Layer 2
58: kVLayer23_Volt 230.0 // Voltage between Layer 2 and Layer 3
59: kVLayer34_Volt 345.0 // Voltage between Layer 3 and Layer 4
60: kVLayer45_Volt 500.0 // Voltage between Layer 4 and Layer 5
61: kVLayer1_LDCutoff 115.0 // Layer 1 RelayLoadability Percent
62: kVLayer2_LDCutoff 115.0 // Layer 2 RelayLoadability Percent
63: kVLayer3_LDCutoff 115.0 // Layer 3 RelayLoadability Percent
64: kVLayer4_LDCutoff 115.0 // Layer 4 RelayLoadability Percent
65: kVLayer5_LDCutoff 115.0 // Layer 5 RelayLoadability Percent
66: zeroRatingCutoff 0.000100 // If rating is below this, set rating to 9999
67: saveN11Cases 0 // Save a case for each N-1-1 first-level case
68: N11SaveDirectory [] // Folder to save each N-1-1 first-level case
69: acVerifyFgate 0 // Enable flowgate AC verification (0-No;1-Yes)
70: useContingencyComments 0 // Use Comments in contingency file in contingency reporting
71: ignoreEnd2Exit 0 // Ignore END statement to exit reading sub mon con exc files (0-No, 1-Yes)
72: nearSyskVLayer1 5 // Subsystem proximity screen 1st kV Layer
73: nearSyskVLayer2 5 // Subsystem proximity screen 2nd kV Layer
74: nearSyskVLayer3 5 // Subsystem proximity screen 3rd kV Layer
75: nearSyskVLayer4 5 // Subsystem proximity screen 4rd kV Layer
76: nearSyskVLayer5 5 // Subsystem proximity screen 5th kV Layer
77: nearSyskVLayer12_Volt 100.0 // Subsystem proximity screen Voltage between Layer 1 and Layer 2
78: nearSyskVLayer23_Volt 230.0 // Subsystem proximity screen Voltage between Layer 2 and Layer 3
79: nearSyskVLayer34_Volt 345.0 // Subsystem proximity screen Voltage between Layer 3 and Layer 4
80: nearSyskVLayer45_Volt 500.0 // Subsystem proximity screen Voltage between Layer 4 and Layer 5
81: nearSysScrnMod 0 // Subsystem Screening for nearby contingencies (1st and 2nd)
82: nearSyskVCutoff 0.00 // Subsystem proximity Specify kV Cutoff
83: nearSysApplykVCutoffOption 0 // Subsystem proximity [0-one side only, 1-both sides]
84: nearByLayerSubSysName [Undefined] // - Subsystem Name for proximity contingency layer screen
Select data category:(L2): [ 0]
Select main menu function(L1): [ opt] = Selected Function 10 - Options - TARA analysis options
Select data category:(L2): [ screen] = Selected Function 2 - SCREEN - Worst dispatch screening options
**** Current **** TARA worst dispatch screening options
1: maxWdTest 5000.0 // Maximum redispatch test level
2: maxWdTestRefDn 1000.0 // Maximum allowed decrease in the reference subsystem
3: maxWdTestRefUp 1000.0 // Maximum allowed increase in the reference subsystem
4: maxViolPerCons 10 // Maximum times (by MW redispatch required) to consider the same monitored element during screening
5: maxWdUnits 2 // Maximum number of Downstream Units that can be turned off
6: maxWdTestStrategy 1 // Redispatch strategy: 1- minimize MW redispatch, 2-number of plants, 3 - number of plants and check MW redispatch, 4 - harmers to ref, 5 - helpers to ref
7: wdScalingFactor 100.0 // Screening rating scaling factor in %% [0-9999]
8: wdPumpMode 0 // Allow unit to pump? [0=no, 1=yes]
9: RampingRule 0 // Apply ramping rules [0=no rules, 1=PJM Winter,2=PJM Light Load]
10: limitFgateName40 0 // Limit flowgate name to 40 characters? 1=yes, 0=no
11: uselimitFgateName100 0 // Use 100 characters for flowgate name? 1=yes, 0=no
12: wdSaveOneDirection 0 // Save flowgate for only one direction for mon/con (Probe usage)
13: wdProbeFgates 0 // Add TARA_FORMAT statement and remove default dispatch from fgate file
14: partitionMode 0 // Screening Partition Mode?
15: partitionsTotal 20 // Total partiions to create
16: partitionSelected 1 // Which partition to run?
17: nearStudykVLayer1 0 // Study buses proximity screen 1st kV Layer
18: nearStudykVLayer2 0 // Study buses proximity screen 2nd kV Layer
19: nearStudykVLayer3 0 // Study buses proximity screen 3rd kV Layer
20: nearStudykVLayer4 0 // Study buses proximity screen 4rd kV Layer
21: nearStudykVLayer5 0 // Study buses proximity screen 5th kV Layer
22: nearStudykVLayer12_Volt 0.0 // Study buses proximity screen Voltage between Layer 1 and Layer 2
23: nearStudykVLayer23_Volt 0.0 // Study buses proximity screen Voltage between Layer 2 and Layer 3
24: nearStudykVLayer34_Volt 0.0 // Study buses proximity screen Voltage between Layer 3 and Layer 4
25: nearStudykVLayer45_Volt 0.0 // Study buses proximity screen Voltage between Layer 4 and Layer 5
26: nearStudyScrnMode 0 // Subsystem Screening for nearby contingencies (1st and 2nd)
27: nearStudykVCutoff 0.00 // Study buses proximity Specify kV Cutoff
28: nearStudyApplykVCutoffOption 0 // Study buses proximity [0-one side only, 1-both sides]
29: wdMultiCoreNoHeader 0 // Remove default dispatch from fgate file and header from ViolScreenSum
Specify option name (or number) and value : [ limitFgateName40][ 0]
Specify option name (or number) and value : [ 0]
**** New **** TARA worst dispatch screening options
1: maxWdTest 5000.0 // Maximum redispatch test level
2: maxWdTestRefDn 1000.0 // Maximum allowed decrease in the reference subsystem
3: maxWdTestRefUp 1000.0 // Maximum allowed increase in the reference subsystem
4: maxViolPerCons 10 // Maximum times (by MW redispatch required) to consider the same monitored element during screening
5: maxWdUnits 2 // Maximum number of Downstream Units that can be turned off
6: maxWdTestStrategy 1 // Redispatch strategy: 1- minimize MW redispatch, 2-number of plants, 3 - number of plants and check MW redispatch, 4 - harmers to ref, 5 - helpers to ref
7: wdScalingFactor 100.0 // Screening rating scaling factor in %% [0-9999]
8: wdPumpMode 0 // Allow unit to pump? [0=no, 1=yes]
9: RampingRule 0 // Apply ramping rules [0=no rules, 1=PJM Winter,2=PJM Light Load]
10: limitFgateName40 0 // Limit flowgate name to 40 characters? 1=yes, 0=no
11: uselimitFgateName100 0 // Use 100 characters for flowgate name? 1=yes, 0=no
12: wdSaveOneDirection 0 // Save flowgate for only one direction for mon/con (Probe usage)
13: wdProbeFgates 0 // Add TARA_FORMAT statement and remove default dispatch from fgate file
14: partitionMode 0 // Screening Partition Mode?
15: partitionsTotal 20 // Total partiions to create
16: partitionSelected 1 // Which partition to run?
17: nearStudykVLayer1 0 // Study buses proximity screen 1st kV Layer
18: nearStudykVLayer2 0 // Study buses proximity screen 2nd kV Layer
19: nearStudykVLayer3 0 // Study buses proximity screen 3rd kV Layer
20: nearStudykVLayer4 0 // Study buses proximity screen 4rd kV Layer
21: nearStudykVLayer5 0 // Study buses proximity screen 5th kV Layer
22: nearStudykVLayer12_Volt 0.0 // Study buses proximity screen Voltage between Layer 1 and Layer 2
23: nearStudykVLayer23_Volt 0.0 // Study buses proximity screen Voltage between Layer 2 and Layer 3
24: nearStudykVLayer34_Volt 0.0 // Study buses proximity screen Voltage between Layer 3 and Layer 4
25: nearStudykVLayer45_Volt 0.0 // Study buses proximity screen Voltage between Layer 4 and Layer 5
26: nearStudyScrnMode 0 // Subsystem Screening for nearby contingencies (1st and 2nd)
27: nearStudykVCutoff 0.00 // Study buses proximity Specify kV Cutoff
28: nearStudyApplykVCutoffOption 0 // Study buses proximity [0-one side only, 1-both sides]
29: wdMultiCoreNoHeader 0 // Remove default dispatch from fgate file and header from ViolScreenSum
Select data category:(L2): [ 0]
Select main menu function(L1): [ opt] = Selected Function 10 - Options - TARA analysis options
Select data category:(L2): [ cont] = Selected Function 1 - CONTING - Contingency analysis option
**** Current **** Contingency analysis options:
1: monBranRatingBase 1 // Base case rating (1-A;2-B;3-C;4-D)
2: monBranRatingCont 2 // Contingency rating (1-A;2-B;3-C;4-D)
3: monBranRatingMultBase 100.00 // Base case rating multipliers
4: monBranRatingMultCont 100.00 // Contingency rating multipliers
5: contChanCutOffMW 5.0 // MW cutoff to ignore constraints if cont.flow doesn't changes from the base case more than
6: contChanCutOffPercent 2.0 // Rating %% cutoff to ignore if cont.flow changes from the base case is less than
7: PAR_AdjEnabledContAnal 1 // Phase shifter model for the base case (0-fixed angle;1-control flow), always fixed in contingency
8: adjustRatingMVA 0 // Adjust branch MW rating based on MVAR flow (DC analysis)
9: limitTypeLine 0 // Use AMP (=0) or MVA (1) limit to check lines violation in AC mode
10: limitTypeTran 1 // Use AMP (=0) or MVA (1) limit to check transformer violation in AC mode
11: voltMinChange 0.0050 // Voltage change cutoff in PU to ignore voltage violations with change from the base case is smaller
12: numContMaxAlloc 15000 // Max number of contingencies
13: numEventsAlloc 35000 // Max number of contingency events
14: numDispEventAlloc 60000 // Max number of generation redispatch events
15: numLFgatesMaxAlloc 10000 // Max number of flowgates
16: maxFgateBranches 100 // Max number of branches (events) per flowgate
17: mulSecPrintMode 0 // Multi-section line modeling (0-ignore;1-honor)
18: smartCutOff 0 // Use Smart cutoff based on Max conting impact using base case and conting rating difference (0-no;1-yes)
19: maxExcludesAlloc 10000 // Max number of exclude records
20: showConAnalLFLog 0 // Show LF convergence during ACCONT
21: MAXOUTAGES 15000 // Maximum number of outages
22: maxORAFlowResults 2000000 // Maximum number of ORA or N-1-1 results to report
23: ACCONTRepeatSolution 0 // If first AC solution failed, repeat with alternative Flat/Hot start(0-no,1-yes),2-limit to the best iteration
24: showNotMappedContEvents 1 // When generating contingency file, show not mapped event(0-no,1-yes)
25: monBranRatingEnAdd1 0 // Enable first additional rating reporting (0-no,1-yes)
26: monBranRatingEnAdd2 0 // Enable second additional rating reporting (0-no,1-yes)
27: monBranRatingAdd1 3 // Additional Rating 1 (1-A;2-B;3-C;4-D)
28: monBranRatingAdd2 3 // Additional Rating 2 (1-A;2-B;3-C;4-D)
29: monBranRatingMultAdd1 100.00 // Additional Rating 1 multiplier
30: monBranRatingMultAdd2 100.00 // Additional Rating 2 multiplier
31: LoadingCutOff 0.00 // Loading cutoff in percent for displaying cont analysis flow results
32: showAllHighPreSCD 0 // Show SCD result if pre-SCD above cutoff but post-SCD below
33: N11MODE 1 // Run in N-1+Application Mode
34: multiCoreN1 0 // Run in N-1 ACCont in multi-core mode? [0-No, 1-Yes]
35: numLowestLoading 5 // Max number of lowest loading results to report
36: VoltLimAdder 0.00000 // Add this to voltage limit to expand or limit hi/low voltage viol results
37: StudyFiles 0 // Show Names of Input Files on all reports
38: MonConMode 1 // Select Mon/Con mode (1:Regular, 2:Flowgate, 3:Voltgate, 4:Flowgate & Voltgate
39: MaxMonConMode 100000 // Maximum Number of mon/con mode entries
40: keepDuplicates 1 // Keep contingency even if exact duplicate? [0=no, 1=yes]
41: correctiveSwitchingMode 0 // Run in corrective switching mode? [0=no, 1=yes]
42: lodfCutoff 0.01000 // Cutoff for LODF report (absolute value)
43: lodfImpCutoff 1.00 // MW cutoff for LODF Impact report (lodf*(event rating))
44: maxFgEventTotal 30000 // Max number of all branches and events for all flowgatesflowgate
45: maxEvPerCont 60 // Max number of events (events) per contingency
46: maxSPSLogic 10000 // Max number of SPS logic elements
47: maxInjGroups 500 // Max number of SPS AUX Injections Groups
48: maxSPSInterfaces 1000 // Max number of SPS AUX Interfaces
49: co_mode 0 // Cascading mode, 0=no, 1=yes
50: co_branchoutage 1 // Trip Overloaded Branches in Cascading Outage, 0=no, 1=yes
51: co_genoutage 1 // Trip Generators in Cascading Outage, 0=no, 1=yes
52: co_genterminalbus 0 // Trip Generators with low voltage violation at generator terminal bus, 0=no, 1=yes
53: co_loadoutage 1 // Trip Loads in Cascading Outage, 0=no, 1=yes
54: co_maxlevel 10 // Maximum cascading outage test level
55: saveCOCases 0 // Save a case for each cascading step case
56: COSaveDirectory [] // Folder to save each cascading outage case
57: kVLayer12_Volt 100.0 // Voltage between Layer 1 and Layer 2
58: kVLayer23_Volt 230.0 // Voltage between Layer 2 and Layer 3
59: kVLayer34_Volt 345.0 // Voltage between Layer 3 and Layer 4
60: kVLayer45_Volt 500.0 // Voltage between Layer 4 and Layer 5
61: kVLayer1_LDCutoff 115.0 // Layer 1 RelayLoadability Percent
62: kVLayer2_LDCutoff 115.0 // Layer 2 RelayLoadability Percent
63: kVLayer3_LDCutoff 115.0 // Layer 3 RelayLoadability Percent
64: kVLayer4_LDCutoff 115.0 // Layer 4 RelayLoadability Percent
65: kVLayer5_LDCutoff 115.0 // Layer 5 RelayLoadability Percent
66: zeroRatingCutoff 0.000100 // If rating is below this, set rating to 9999
67: saveN11Cases 0 // Save a case for each N-1-1 first-level case
68: N11SaveDirectory [] // Folder to save each N-1-1 first-level case
69: acVerifyFgate 0 // Enable flowgate AC verification (0-No;1-Yes)
70: useContingencyComments 0 // Use Comments in contingency file in contingency reporting
71: ignoreEnd2Exit 0 // Ignore END statement to exit reading sub mon con exc files (0-No, 1-Yes)
72: nearSyskVLayer1 5 // Subsystem proximity screen 1st kV Layer
73: nearSyskVLayer2 5 // Subsystem proximity screen 2nd kV Layer
74: nearSyskVLayer3 5 // Subsystem proximity screen 3rd kV Layer
75: nearSyskVLayer4 5 // Subsystem proximity screen 4rd kV Layer
76: nearSyskVLayer5 5 // Subsystem proximity screen 5th kV Layer
77: nearSyskVLayer12_Volt 100.0 // Subsystem proximity screen Voltage between Layer 1 and Layer 2
78: nearSyskVLayer23_Volt 230.0 // Subsystem proximity screen Voltage between Layer 2 and Layer 3
79: nearSyskVLayer34_Volt 345.0 // Subsystem proximity screen Voltage between Layer 3 and Layer 4
80: nearSyskVLayer45_Volt 500.0 // Subsystem proximity screen Voltage between Layer 4 and Layer 5
81: nearSysScrnMod 0 // Subsystem Screening for nearby contingencies (1st and 2nd)
82: nearSyskVCutoff 0.00 // Subsystem proximity Specify kV Cutoff
83: nearSysApplykVCutoffOption 0 // Subsystem proximity [0-one side only, 1-both sides]
84: nearByLayerSubSysName [Undefined] // - Subsystem Name for proximity contingency layer screen
Specify option name (or number) and value : [ StudyFiles][ 1]
Specify option name (or number) and value : [ 0]
**** New **** Contingency analysis options:
1: monBranRatingBase 1 // Base case rating (1-A;2-B;3-C;4-D)
2: monBranRatingCont 2 // Contingency rating (1-A;2-B;3-C;4-D)
3: monBranRatingMultBase 100.00 // Base case rating multipliers
4: monBranRatingMultCont 100.00 // Contingency rating multipliers
5: contChanCutOffMW 5.0 // MW cutoff to ignore constraints if cont.flow doesn't changes from the base case more than
6: contChanCutOffPercent 2.0 // Rating %% cutoff to ignore if cont.flow changes from the base case is less than
7: PAR_AdjEnabledContAnal 1 // Phase shifter model for the base case (0-fixed angle;1-control flow), always fixed in contingency
8: adjustRatingMVA 0 // Adjust branch MW rating based on MVAR flow (DC analysis)
9: limitTypeLine 0 // Use AMP (=0) or MVA (1) limit to check lines violation in AC mode
10: limitTypeTran 1 // Use AMP (=0) or MVA (1) limit to check transformer violation in AC mode
11: voltMinChange 0.0050 // Voltage change cutoff in PU to ignore voltage violations with change from the base case is smaller
12: numContMaxAlloc 15000 // Max number of contingencies
13: numEventsAlloc 35000 // Max number of contingency events
14: numDispEventAlloc 60000 // Max number of generation redispatch events
15: numLFgatesMaxAlloc 10000 // Max number of flowgates
16: maxFgateBranches 100 // Max number of branches (events) per flowgate
17: mulSecPrintMode 0 // Multi-section line modeling (0-ignore;1-honor)
18: smartCutOff 0 // Use Smart cutoff based on Max conting impact using base case and conting rating difference (0-no;1-yes)
19: maxExcludesAlloc 10000 // Max number of exclude records
20: showConAnalLFLog 0 // Show LF convergence during ACCONT
21: MAXOUTAGES 15000 // Maximum number of outages
22: maxORAFlowResults 2000000 // Maximum number of ORA or N-1-1 results to report
23: ACCONTRepeatSolution 0 // If first AC solution failed, repeat with alternative Flat/Hot start(0-no,1-yes),2-limit to the best iteration
24: showNotMappedContEvents 1 // When generating contingency file, show not mapped event(0-no,1-yes)
25: monBranRatingEnAdd1 0 // Enable first additional rating reporting (0-no,1-yes)
26: monBranRatingEnAdd2 0 // Enable second additional rating reporting (0-no,1-yes)
27: monBranRatingAdd1 3 // Additional Rating 1 (1-A;2-B;3-C;4-D)
28: monBranRatingAdd2 3 // Additional Rating 2 (1-A;2-B;3-C;4-D)
29: monBranRatingMultAdd1 100.00 // Additional Rating 1 multiplier
30: monBranRatingMultAdd2 100.00 // Additional Rating 2 multiplier
31: LoadingCutOff 0.00 // Loading cutoff in percent for displaying cont analysis flow results
32: showAllHighPreSCD 0 // Show SCD result if pre-SCD above cutoff but post-SCD below
33: N11MODE 1 // Run in N-1+Application Mode
34: multiCoreN1 0 // Run in N-1 ACCont in multi-core mode? [0-No, 1-Yes]
35: numLowestLoading 5 // Max number of lowest loading results to report
36: VoltLimAdder 0.00000 // Add this to voltage limit to expand or limit hi/low voltage viol results
37: StudyFiles 1 // Show Names of Input Files on all reports
38: MonConMode 1 // Select Mon/Con mode (1:Regular, 2:Flowgate, 3:Voltgate, 4:Flowgate & Voltgate
39: MaxMonConMode 100000 // Maximum Number of mon/con mode entries
40: keepDuplicates 1 // Keep contingency even if exact duplicate? [0=no, 1=yes]
41: correctiveSwitchingMode 0 // Run in corrective switching mode? [0=no, 1=yes]
42: lodfCutoff 0.01000 // Cutoff for LODF report (absolute value)
43: lodfImpCutoff 1.00 // MW cutoff for LODF Impact report (lodf*(event rating))
44: maxFgEventTotal 30000 // Max number of all branches and events for all flowgatesflowgate
45: maxEvPerCont 60 // Max number of events (events) per contingency
46: maxSPSLogic 10000 // Max number of SPS logic elements
47: maxInjGroups 500 // Max number of SPS AUX Injections Groups
48: maxSPSInterfaces 1000 // Max number of SPS AUX Interfaces
49: co_mode 0 // Cascading mode, 0=no, 1=yes
50: co_branchoutage 1 // Trip Overloaded Branches in Cascading Outage, 0=no, 1=yes
51: co_genoutage 1 // Trip Generators in Cascading Outage, 0=no, 1=yes
52: co_genterminalbus 0 // Trip Generators with low voltage violation at generator terminal bus, 0=no, 1=yes
53: co_loadoutage 1 // Trip Loads in Cascading Outage, 0=no, 1=yes
54: co_maxlevel 10 // Maximum cascading outage test level
55: saveCOCases 0 // Save a case for each cascading step case
56: COSaveDirectory [] // Folder to save each cascading outage case
57: kVLayer12_Volt 100.0 // Voltage between Layer 1 and Layer 2
58: kVLayer23_Volt 230.0 // Voltage between Layer 2 and Layer 3
59: kVLayer34_Volt 345.0 // Voltage between Layer 3 and Layer 4
60: kVLayer45_Volt 500.0 // Voltage between Layer 4 and Layer 5
61: kVLayer1_LDCutoff 115.0 // Layer 1 RelayLoadability Percent
62: kVLayer2_LDCutoff 115.0 // Layer 2 RelayLoadability Percent
63: kVLayer3_LDCutoff 115.0 // Layer 3 RelayLoadability Percent
64: kVLayer4_LDCutoff 115.0 // Layer 4 RelayLoadability Percent
65: kVLayer5_LDCutoff 115.0 // Layer 5 RelayLoadability Percent
66: zeroRatingCutoff 0.000100 // If rating is below this, set rating to 9999
67: saveN11Cases 0 // Save a case for each N-1-1 first-level case
68: N11SaveDirectory [] // Folder to save each N-1-1 first-level case
69: acVerifyFgate 0 // Enable flowgate AC verification (0-No;1-Yes)
70: useContingencyComments 0 // Use Comments in contingency file in contingency reporting
71: ignoreEnd2Exit 0 // Ignore END statement to exit reading sub mon con exc files (0-No, 1-Yes)
72: nearSyskVLayer1 5 // Subsystem proximity screen 1st kV Layer
73: nearSyskVLayer2 5 // Subsystem proximity screen 2nd kV Layer
74: nearSyskVLayer3 5 // Subsystem proximity screen 3rd kV Layer
75: nearSyskVLayer4 5 // Subsystem proximity screen 4rd kV Layer
76: nearSyskVLayer5 5 // Subsystem proximity screen 5th kV Layer
77: nearSyskVLayer12_Volt 100.0 // Subsystem proximity screen Voltage between Layer 1 and Layer 2
78: nearSyskVLayer23_Volt 230.0 // Subsystem proximity screen Voltage between Layer 2 and Layer 3
79: nearSyskVLayer34_Volt 345.0 // Subsystem proximity screen Voltage between Layer 3 and Layer 4
80: nearSyskVLayer45_Volt 500.0 // Subsystem proximity screen Voltage between Layer 4 and Layer 5
81: nearSysScrnMod 0 // Subsystem Screening for nearby contingencies (1st and 2nd)
82: nearSyskVCutoff 0.00 // Subsystem proximity Specify kV Cutoff
83: nearSysApplykVCutoffOption 0 // Subsystem proximity [0-one side only, 1-both sides]
84: nearByLayerSubSysName [Undefined] // - Subsystem Name for proximity contingency layer screen
Select data category:(L2): [ 0]
Select main menu function(L1): [ 0]
Select main menu function(L1): [ READ] = Selected Function 1 - READ - Read TARA input files
Select function(L2): [ PSSE] = Selected Function 1 - PSSE - Read PSS/E RAW DATA File
Specify PSS/E version number (24-26; 28; 29, 30, 31, 32, 33, 34, 35) or AUX or EPC)==>: [ 34]
Specify PSS/E RAW data file mask [ "C:\Users\03419\Desktop\2022 Gas Study\Alt 3A\2032S_gas_alt#3a_212mw.raw"]
Current Data SubDirectory - [C:\Users\03419\Desktop\2022 Gas Study\Alt 3A]
ReadFiles - Found 1 files matching mask [C:\Users\03419\Desktop\2022 Gas Study\Alt 3A\2032S_gas_alt#3a_212mw.raw]
Total found 1 LF models with date defined within LF file name
1 2032S_gas_alt#3a_212mw.raw
*** Opened [2032S_gas_alt#3a_212mw.raw]-(Lev=1). Current directory - [C:\Users\03419\Desktop\2022 Gas Study\Alt 3A]
Reading PSS/E-34 raw data file 2032S_gas_alt#3a_212mw.raw
92210 Buses Load 82376 Gen 8935 Swing 9 ShutDown 890
52162 Loads
2445 Fixed shunts defined
10839 Machines
WarnID-6159-1-1 Branch [135527 SANTR404 34.5 102 145 135536 SANBORN3 34.5 102 145 ] has high suspicious R/X ratio [ 20.00] > 10.00. R= 0.00020 X= 0.00001 Suggested R= 0.00010
File [2032S_gas_alt#3a_212mw.raw]. Line 164189: 135527,135536,'1 ', 2.00000E-04, 1.00000E-05, 0.00000,' ', 43.00, 47.00, 57.00, 0.00, 0.00, 0.00, 0.00, 0.00, 0.00, 0.00, 0.00, 0.00, 0.00000, 0.00000, 0.00000, 0.00000,1,2, 0.00, 145,1.0000
WarnID-6159-2-2 Branch [135536 SANBORN3 34.5 102 145 135539 SANTR403 34.5 102 145 ] has high suspicious R/X ratio [ 20.00] > 10.00. R= 0.00020 X= 0.00001 Suggested R= 0.00010
File [2032S_gas_alt#3a_212mw.raw]. Line 164199: 135536,135539,'1 ', 2.00000E-04, 1.00000E-05, 0.00000,' ', 43.00, 47.00, 57.00, 0.00, 0.00, 0.00, 0.00, 0.00, 0.00, 0.00, 0.00, 0.00, 0.00000, 0.00000, 0.00000, 0.00000,1,2, 0.00, 145,1.0000
WarnID-6159-3-3 Branch [318409 MS SLR4 COL 34.5 349 1398 318410 MS SLR4 PAD 34.5 349 1398 ] has high suspicious R/X ratio [ 10.01] > 10.00. R= 0.02670 X= 0.00267 Suggested R= 0.02667
File [2032S_gas_alt#3a_212mw.raw]. Line 206815: 318409,318410,'1 ', 2.67000E-02, 2.66700E-03, 0.00585,' ', 888.00, 888.00, 0.00, 0.00, 0.00, 0.00, 0.00, 0.00, 0.00, 0.00, 0.00, 0.00, 0.00000, 0.00000, 0.00000, 0.00000,1,1, 0.00, 1,1.0000
WarnID-6159-4-4 Branch [336007 6VACHRE! 230 351 387 336029 J1142J1158 230 351 387 ] has high suspicious R/X ratio [ 12.20] > 10.00. R= 0.00024 X= 0.00002 Suggested R= 0.00020
File [2032S_gas_alt#3a_212mw.raw]. Line 209188: 336007,336029,'1 ', 2.44100E-04, 2.00000E-05, 0.00031,' ', 396.78, 396.78, 0.00, 0.00, 0.00, 0.00, 0.00, 0.00, 0.00, 0.00, 0.00, 0.00, 0.00000, 0.00000, 0.00000, 0.00000,1,2, 0.00, 1,1.0000
WarnID-6159-5-5 Branch [337038 3INDIANOLATP 115 326 390 337039 3INDIANOLALD 115 326 390 ] has high suspicious R/X ratio [ 30.00] > 10.00. R= 0.00009 X= 0.00000 Suggested R= 0.00003
File [2032S_gas_alt#3a_212mw.raw]. Line 209700: 337038,337039,'ZO', 9.00000E-05, 3.00000E-06, 0.00000,' ', 231.00, 231.00, 0.00, 0.00, 0.00, 0.00, 0.00, 0.00, 0.00, 0.00, 0.00, 0.00, 0.00000, 0.00000, 0.00000, 0.00000,0,1, 0.00, 1,1.0000
WarnID-6159-6-6 Branch [400503 MELROSTP 115 401 401 406698 MELROSE 115 401 412 ] has high suspicious R/X ratio [ 10.53] > 10.00. R= 0.00200 X= 0.00019 Suggested R= 0.00190
File [2032S_gas_alt#3a_212mw.raw]. Line 223012: 400503,406698,'1 ', 2.00100E-03, 1.90000E-04, 0.00000,' ', 48.00, 48.00, 62.00, 0.00, 0.00, 0.00, 0.00, 0.00, 0.00, 0.00, 0.00, 0.00, 0.00000, 0.00000, 0.00000, 0.00000,1,2, 0.03, 401,1.0000
WarnID-6159-7-7 Branch [539810 BUS-0421 34.5 534 1541 539811 SUB34.5KVB 34.5 534 1541 ] has high suspicious R/X ratio [ 22.76] > 10.00. R= 0.00382 X= 0.00017 Suggested R= 0.00168
File [2032S_gas_alt#3a_212mw.raw]. Line 231258: 539810,539811,'1 ', 3.82300E-03, 1.68000E-04, 0.00012,' ', 239.00, 239.00, 239.00, 0.00, 0.00, 0.00, 0.00, 0.00, 0.00, 0.00, 0.00, 0.00, 0.00000, 0.00000, 0.00000, 0.00000,1,1, 1.00, 599,1.0000
WarnID-6159-8-8 Branch [629602 VINING REC 8 69.0 627 665 629604 VINING TAP 8 69.0 627 665 ] has high suspicious R/X ratio [ 43.59] > 10.00. R= 0.00667 X= 0.00015 Suggested R= 0.00153
File [2032S_gas_alt#3a_212mw.raw]. Line 235135: 629602,629604,'1 ', 6.67000E-03, 1.53000E-04, 0.00030,' ', 91.00, 91.00, 91.00, 0.00, 0.00, 0.00, 0.00, 0.00, 0.00, 0.00, 0.00, 0.00, 0.00000, 0.00000, 0.00000, 0.00000,1,2, 1.00, 627,1.0000
WarnID-6159-9-9 Branch [658129 LUVERNEMNS19 25.0 652 1624 658131 LUVERNEMNS29 25.0 652 1624 ] has high suspicious R/X ratio [ 13.06] > 10.00. R= 0.38800 X= 0.02970 Suggested R= 0.29700
File [2032S_gas_alt#3a_212mw.raw]. Line 239227: 658129,658131,'1 ', 3.88000E-01, 2.97000E-02, 0.00057,' ', 9.00, 9.00, 0.00, 0.00, 0.00, 0.00, 0.00, 0.00, 0.00, 0.00, 0.00, 0.00, 0.00000, 0.00000, 0.00000, 0.00000,1,1, 3.57, 658,1.0000
85226 Nontransformer branches
85260 Nontransformer branches
26515 Transformers Two-winding 22770 Three-winding 3745
3745 Star Buses added for three-winding transformers (real 92210 buses)
WarnID-1878-1-9 Transformer [100439 NEWPAGE BUS7 13.8 101 100 100211 NEWPAGEPAPER 115 ] remotely controlled bus {100416 NEWPAGE BUS3 13.8 ] connected to fromBus via ZIL - changed to control fromBus
WarnID-6155-1-10 Suspicious PAR [100780 OXFORD 12.5 101 100 102193 OXFORD 34.5 101 100 ] has R=0 and small X=0.00050 with Phase angle =30.000 Check data. Winding=1 Increased X to improve flat start
WarnID-1878-2-11 Transformer [110822 WALTHAM A 115 101 110 110987 WALT PS-D 115 ] remotely controlled bus {110809 WALTHAM B 115 ] connected to fromBus via ZIL - changed to control fromBus
WarnID-6160-1-13 3W Transformer [121839 NUTMEG 34.5 101 116 999974 NUTMEG-MAIN 34.5 101 116 ] Wind=1 has high suspicious R/X ratio [ -17.51] > 10.00. R= 0.00876 X= -0.00050 Suggested R= -0.00500
File [2032S_gas_alt#3a_212mw.raw]. Line 352762: 0 / END OF TRANSFORMER DATA, BEGIN AREA DATA
WarnID-6160-2-14 2W Transformer [121766 WILLIMANTIC 27.6 101 116 121764 WILLIMANTCM1 99.0 101 116 ] has high suspicious R/X ratio [ 11.55] > 10.00. R= 0.00578 X= 0.00050 Suggested R= 0.00500
File [2032S_gas_alt#3a_212mw.raw]. Line 352762: 0 / END OF TRANSFORMER DATA, BEGIN AREA DATA
WarnID-1878-3-14 Transformer [128835 SHORE RD 345 102 156 129294 SHORE RD2 138 ] remotely controlled bus {129293 SHORE RD 138 ] connected to ToBus via ZIL - changed to control toBus
WarnID-1878-4-15 Transformer [129685 PILGRM1 69.0 102 156 129355 PILGRIM 138 ] remotely controlled bus {129686 PILGRM2 69.0 ] connected to fromBus via ZIL - changed to control fromBus
WarnID-1878-5-16 Transformer [129361 RULND RD 138 102 156 129693 RULAND RD2 69.0 ] remotely controlled bus {129692 RULND RD 69.0 ] connected to ToBus via ZIL - changed to control toBus
WarnID-1878-6-17 Transformer [129791 BRKHAVEN2 69.0 102 156 129416 BRKHVEN4 138 ] remotely controlled bus {129790 BRKHAVEN1 69.0 ] connected to fromBus via ZIL - changed to control fromBus
WarnID-6160-3-19 3W Transformer [130664 Q678_COLL 34.5 102 156 999925 Q678_POI 34.5 102 156 ] Wind=1 has high suspicious R/X ratio [ -20.40] > 10.00. R= 0.01020 X= -0.00050 Suggested R= -0.00500
File [2032S_gas_alt#3a_212mw.raw]. Line 352762: 0 / END OF TRANSFORMER DATA, BEGIN AREA DATA
WarnID-1878-7-19 Transformer [147481 LOVETT_2 138 102 155 999902 BANK 192 138 ] remotely controlled bus {146766 LOVET138 138 ] connected to fromBus via ZIL - changed to control fromBus
WarnID-6160-4-21 3W Transformer [151664 MOOSE_LK_B2 44.0 103 1101 999881 103:MOOSE L 44.0 103 1101 ] Wind=1 has high suspicious R/X ratio [ -26.85] > 10.00. R= 0.03693 X= -0.00137 Suggested R= -0.01375
File [2032S_gas_alt#3a_212mw.raw]. Line 352762: 0 / END OF TRANSFORMER DATA, BEGIN AREA DATA
WarnID-6160-5-22 2W Transformer [151789 LOWER_WHITER 4.16 103 1101 151790 LOWER_WHITEG 0.60 103 1101 ] has high suspicious R/X ratio [ 16.67] > 10.00. R=200.00000 X= 12.00000 Suggested R=120.00000
File [2032S_gas_alt#3a_212mw.raw]. Line 352762: 0 / END OF TRANSFORMER DATA, BEGIN AREA DATA
WarnID-1878-8-22 Transformer [160658 NOVA_MOORE_A 13.8 103 1110 160152 N_MOORE_L27V 220 ] remotely controlled bus {160656 NOVA_MOORE_B 13.8 ] connected to fromBus via ZIL - changed to control fromBus
WarnID-1878-9-23 Transformer [184165 MANIWA 120 104 1143 184401 MANI69 A 69.0 ] remotely controlled bus {184400 MANI69 69.0 ] connected to ToBus via ZIL - changed to control toBus
WarnID-1878-10-24 Transformer [185430 ORFORA 120 104 1153 185445 ORFORD-25B 26.4 ] remotely controlled bus {185444 ORFORD-25A 26.4 ] connected to ToBus via ZIL - changed to control toBus
!!!! Reached the maximum number (10) of messages of this type=(1878). See full warning list for more info
WarnID-6155-2-26 Suspicious PAR [406869 SRNGBNKTR_2 13.2 412 412 997988 SPRNGBNK 2 115 412 412 ] has R=0 and small X=0.00010 with Phase angle =13.200 Check data. Winding=3 Increased X to improve flat start
WarnID-6160-6-28 3W Transformer [531505 CIMWD2 1 34.5 534 1541 997283 CIMRNWND2 MP 34.5 534 1541 ] Wind=1 has high suspicious R/X ratio [ -11.01] > 10.00. R= -0.00551 X= 0.00050 Suggested R= 0.00500
File [2032S_gas_alt#3a_212mw.raw]. Line 352762: 0 / END OF TRANSFORMER DATA, BEGIN AREA DATA
WarnID-6160-7-29 3W Transformer [539724 PHLBURG1 34.5 534 1524 997118 PHLBURG3 34.5 534 1529 ] Wind=0 has high suspicious R/X ratio [ 31.54] > 10.00. R= 0.01577 X= 0.00050 Suggested R= 0.00500
File [2032S_gas_alt#3a_212mw.raw]. Line 352762: 0 / END OF TRANSFORMER DATA, BEGIN AREA DATA
WarnID-6160-8-30 3W Transformer [543154 WHGNSVL1 12.5 541 1552 997029 WEST HIGGI1 12.5 541 1552 ] Wind=1 has high suspicious R/X ratio [ 43.42] > 10.00. R= -0.12113 X= -0.00279 Suggested R= -0.02790
File [2032S_gas_alt#3a_212mw.raw]. Line 352762: 0 / END OF TRANSFORMER DATA, BEGIN AREA DATA
WarnID-6160-9-31 3W Transformer [640202 GR ISLD9 34.5 640 686 996700 GRAND.ISD T1 34.5 640 686 ] Wind=0 has high suspicious R/X ratio [ -12.80] > 10.00. R= 0.01280 X= -0.00100 Suggested R= -0.01000
File [2032S_gas_alt#3a_212mw.raw]. Line 352762: 0 / END OF TRANSFORMER DATA, BEGIN AREA DATA
WarnID-6160-10-32 3W Transformer [647976 S976 8 69.0 645 691 996534 FREMONT T4 69.0 640 686 ] Wind=0 has high suspicious R/X ratio [ -12.40] > 10.00. R= 0.00620 X= -0.00050 Suggested R= -0.00500
File [2032S_gas_alt#3a_212mw.raw]. Line 352762: 0 / END OF TRANSFORMER DATA, BEGIN AREA DATA
WarnID-6160-11-33 3W Transformer [648610 NC2HS 5 161 645 694 996518 NC2HST2 4.20 645 694 ] Wind=2 has high suspicious R/X ratio [ -15.12] > 10.00. R= -0.00756 X= 0.00050 Suggested R= 0.00500
File [2032S_gas_alt#3a_212mw.raw]. Line 352762: 0 / END OF TRANSFORMER DATA, BEGIN AREA DATA
40 Two-terminal DC Lines (online 28 lines)
2 Voltage Source Converters
50 Transformer impedance correction table entries defined
WarnID-1830-1-33 PAR table 2 range [-70.00:70.00] used for LTC 403223 FIGUR SL_COL 34.5 998077 FIGUR SL_COL 34.5 30 with regul range [0.03:0.03]. change table# to zero
0 Multi-terminal DC Networks
40 Multisection lines
0 Interarea Transfer Data
46 FACTS control devices
WarnID-1436-1-35 FACTS Device has mode online but no capability or it is unsupported mode or it has a data error. [29 GROTON_DVAR ] Series link operating as a SSSC and shunt link is disabled by SHMX=0 and TRMX=0. Mode=1
File [2032S_gas_alt#3a_212mw.raw]. Line 354164: 0 / END OF FACTS DEVICE DATA, BEGIN SWITCHED SHUNT DATA
WarnID-1436-2-36 FACTS Device has mode online but no capability or it is unsupported mode or it has a data error. [33 KIBBY_DVAR ] Series link operating as a SSSC and shunt link is disabled by SHMX=0 and TRMX=0. Mode=1
File [2032S_gas_alt#3a_212mw.raw]. Line 354164: 0 / END OF FACTS DEVICE DATA, BEGIN SWITCHED SHUNT DATA
WarnID-1436-3-37 FACTS Device has mode online but no capability or it is unsupported mode or it has a data error. [43 WEAVERDVAR ] Series link operating as a SSSC and shunt link is disabled by SHMX=0 and TRMX=0. Mode=1
File [2032S_gas_alt#3a_212mw.raw]. Line 354164: 0 / END OF FACTS DEVICE DATA, BEGIN SWITCHED SHUNT DATA
Num Device Type VoltMagKV VsetKV QMVAR (negative means generating VARs) Qmin Qmax SendBus# Bus Name Volt TermBus# Bus Name Volt Mode PDES QDES VSET SHMX TRMX VTMN VTMX VSMX IMX LINX RMPCT OWNER SET1 SET2 VSREF CtlBs# CtlBsNam NomV MonBusVlt
29 Series link operating as a SSSC and shunt link is disabled by SHMX=0 and TRMX=0. Mode=1 Not supported kind of device operation 105291 GROTON DVAR 0.48 0 1 0.0 0.0 1.0261 0.0 9999.0 0.9000 1.1000 1.0000 0.0 0.05000 100.0 101 0.00000 0.00000 0 104378 HUCKINS HILL 115 1.0261
Series link operating as a SSSC and shunt link is disabled by SHMX=0 and TRMX=0. Mode=1 -> Not supported kind of device operation
33 Series link operating as a SSSC and shunt link is disabled by SHMX=0 and TRMX=0. Mode=1 Not supported kind of device operation 100355 KIBBY W DVAR 34.5 0 1 0.0 0.0 1.0435 0.0 9999.0 0.9000 1.1000 1.0000 0.0 0.05000 100.0 101 0.00000 0.00000 0 100188 KIBBY WIND 115 0.9933
Series link operating as a SSSC and shunt link is disabled by SHMX=0 and TRMX=0. Mode=1 -> Not supported kind of device operation
43 Series link operating as a SSSC and shunt link is disabled by SHMX=0 and TRMX=0. Mode=1 Not supported kind of device operation 103206 WEAVER_DVAR 0.48 0 1 0.0 0.0 1.0435 0.0 9999.0 0.9000 1.1000 1.0000 0.0 0.05000 100.0 101 0.00000 0.00000 0 103091 BULL HILL 115 1.0403
Series link operating as a SSSC and shunt link is disabled by SHMX=0 and TRMX=0. Mode=1 -> Not supported kind of device operation
WarnID-1417-1-38 Initial switched shunt [180326 OUT315 315 104 1143 ] value [ 700.00] cannot be reached by following block order (possibly has adjustment mode 1). New value is [ 710.33]
File [2032S_gas_alt#3a_212mw.raw]. Line 355360: 180326, 1, 1, 1,1.10000,0.90000,180326, 100.0,' ', 700.00, 2, -140.00, 2, 150.33, 6, 140.00
8106 Switched shunts defined
Skipped empty group of INDUCTION MACHINE DATA
95955 Buses Load 86086 Gen 8939 Swing 9 ShutDown 921
95955 Buses Load 86086 Gen 8939 Swing 9 ShutDown 921
*** Closed [2032S_gas_alt#3a_212mw.raw] - 362281 records (Lev=1)
95955 Buses Load 86086 Gen 8939 Swing 9 ShutDown 921
Select function(L2): [ 0]
Select main menu function(L1): [ 0]
Select main menu function(L1): [ opt] = Selected Function 10 - Options - TARA analysis options
Select data category:(L2): [ cont] = Selected Function 1 - CONTING - Contingency analysis option
**** Current **** Contingency analysis options:
1: monBranRatingBase 1 // Base case rating (1-A;2-B;3-C;4-D)
2: monBranRatingCont 2 // Contingency rating (1-A;2-B;3-C;4-D)
3: monBranRatingMultBase 100.00 // Base case rating multipliers
4: monBranRatingMultCont 100.00 // Contingency rating multipliers
5: contChanCutOffMW 5.0 // MW cutoff to ignore constraints if cont.flow doesn't changes from the base case more than
6: contChanCutOffPercent 2.0 // Rating %% cutoff to ignore if cont.flow changes from the base case is less than
7: PAR_AdjEnabledContAnal 1 // Phase shifter model for the base case (0-fixed angle;1-control flow), always fixed in contingency
8: adjustRatingMVA 0 // Adjust branch MW rating based on MVAR flow (DC analysis)
9: limitTypeLine 0 // Use AMP (=0) or MVA (1) limit to check lines violation in AC mode
10: limitTypeTran 1 // Use AMP (=0) or MVA (1) limit to check transformer violation in AC mode
11: voltMinChange 0.0050 // Voltage change cutoff in PU to ignore voltage violations with change from the base case is smaller
12: numContMaxAlloc 15000 // Max number of contingencies
13: numEventsAlloc 35000 // Max number of contingency events
14: numDispEventAlloc 60000 // Max number of generation redispatch events
15: numLFgatesMaxAlloc 10000 // Max number of flowgates
16: maxFgateBranches 100 // Max number of branches (events) per flowgate
17: mulSecPrintMode 0 // Multi-section line modeling (0-ignore;1-honor)
18: smartCutOff 0 // Use Smart cutoff based on Max conting impact using base case and conting rating difference (0-no;1-yes)
19: maxExcludesAlloc 10000 // Max number of exclude records
20: showConAnalLFLog 0 // Show LF convergence during ACCONT
21: MAXOUTAGES 15000 // Maximum number of outages
22: maxORAFlowResults 2000000 // Maximum number of ORA or N-1-1 results to report
23: ACCONTRepeatSolution 0 // If first AC solution failed, repeat with alternative Flat/Hot start(0-no,1-yes),2-limit to the best iteration
24: showNotMappedContEvents 1 // When generating contingency file, show not mapped event(0-no,1-yes)
25: monBranRatingEnAdd1 0 // Enable first additional rating reporting (0-no,1-yes)
26: monBranRatingEnAdd2 0 // Enable second additional rating reporting (0-no,1-yes)
27: monBranRatingAdd1 3 // Additional Rating 1 (1-A;2-B;3-C;4-D)
28: monBranRatingAdd2 3 // Additional Rating 2 (1-A;2-B;3-C;4-D)
29: monBranRatingMultAdd1 100.00 // Additional Rating 1 multiplier
30: monBranRatingMultAdd2 100.00 // Additional Rating 2 multiplier
31: LoadingCutOff 0.00 // Loading cutoff in percent for displaying cont analysis flow results
32: showAllHighPreSCD 0 // Show SCD result if pre-SCD above cutoff but post-SCD below
33: N11MODE 1 // Run in N-1+Application Mode
34: multiCoreN1 0 // Run in N-1 ACCont in multi-core mode? [0-No, 1-Yes]
35: numLowestLoading 5 // Max number of lowest loading results to report
36: VoltLimAdder 0.00000 // Add this to voltage limit to expand or limit hi/low voltage viol results
37: StudyFiles 1 // Show Names of Input Files on all reports
38: MonConMode 1 // Select Mon/Con mode (1:Regular, 2:Flowgate, 3:Voltgate, 4:Flowgate & Voltgate
39: MaxMonConMode 100000 // Maximum Number of mon/con mode entries
40: keepDuplicates 1 // Keep contingency even if exact duplicate? [0=no, 1=yes]
41: correctiveSwitchingMode 0 // Run in corrective switching mode? [0=no, 1=yes]
42: lodfCutoff 0.01000 // Cutoff for LODF report (absolute value)
43: lodfImpCutoff 1.00 // MW cutoff for LODF Impact report (lodf*(event rating))
44: maxFgEventTotal 30000 // Max number of all branches and events for all flowgatesflowgate
45: maxEvPerCont 60 // Max number of events (events) per contingency
46: maxSPSLogic 10000 // Max number of SPS logic elements
47: maxInjGroups 500 // Max number of SPS AUX Injections Groups
48: maxSPSInterfaces 1000 // Max number of SPS AUX Interfaces
49: co_mode 0 // Cascading mode, 0=no, 1=yes
50: co_branchoutage 1 // Trip Overloaded Branches in Cascading Outage, 0=no, 1=yes
51: co_genoutage 1 // Trip Generators in Cascading Outage, 0=no, 1=yes
52: co_genterminalbus 0 // Trip Generators with low voltage violation at generator terminal bus, 0=no, 1=yes
53: co_loadoutage 1 // Trip Loads in Cascading Outage, 0=no, 1=yes
54: co_maxlevel 10 // Maximum cascading outage test level
55: saveCOCases 0 // Save a case for each cascading step case
56: COSaveDirectory [] // Folder to save each cascading outage case
57: kVLayer12_Volt 100.0 // Voltage between Layer 1 and Layer 2
58: kVLayer23_Volt 230.0 // Voltage between Layer 2 and Layer 3
59: kVLayer34_Volt 345.0 // Voltage between Layer 3 and Layer 4
60: kVLayer45_Volt 500.0 // Voltage between Layer 4 and Layer 5
61: kVLayer1_LDCutoff 115.0 // Layer 1 RelayLoadability Percent
62: kVLayer2_LDCutoff 115.0 // Layer 2 RelayLoadability Percent
63: kVLayer3_LDCutoff 115.0 // Layer 3 RelayLoadability Percent
64: kVLayer4_LDCutoff 115.0 // Layer 4 RelayLoadability Percent
65: kVLayer5_LDCutoff 115.0 // Layer 5 RelayLoadability Percent
66: zeroRatingCutoff 0.000100 // If rating is below this, set rating to 9999
67: saveN11Cases 0 // Save a case for each N-1-1 first-level case
68: N11SaveDirectory [] // Folder to save each N-1-1 first-level case
69: acVerifyFgate 0 // Enable flowgate AC verification (0-No;1-Yes)
70: useContingencyComments 0 // Use Comments in contingency file in contingency reporting
71: ignoreEnd2Exit 0 // Ignore END statement to exit reading sub mon con exc files (0-No, 1-Yes)
72: nearSyskVLayer1 5 // Subsystem proximity screen 1st kV Layer
73: nearSyskVLayer2 5 // Subsystem proximity screen 2nd kV Layer
74: nearSyskVLayer3 5 // Subsystem proximity screen 3rd kV Layer
75: nearSyskVLayer4 5 // Subsystem proximity screen 4rd kV Layer
76: nearSyskVLayer5 5 // Subsystem proximity screen 5th kV Layer
77: nearSyskVLayer12_Volt 100.0 // Subsystem proximity screen Voltage between Layer 1 and Layer 2
78: nearSyskVLayer23_Volt 230.0 // Subsystem proximity screen Voltage between Layer 2 and Layer 3
79: nearSyskVLayer34_Volt 345.0 // Subsystem proximity screen Voltage between Layer 3 and Layer 4
80: nearSyskVLayer45_Volt 500.0 // Subsystem proximity screen Voltage between Layer 4 and Layer 5
81: nearSysScrnMod 0 // Subsystem Screening for nearby contingencies (1st and 2nd)
82: nearSyskVCutoff 0.00 // Subsystem proximity Specify kV Cutoff
83: nearSysApplykVCutoffOption 0 // Subsystem proximity [0-one side only, 1-both sides]
84: nearByLayerSubSysName [Undefined] // - Subsystem Name for proximity contingency layer screen
Specify option name (or number) and value : [ StudyFiles][ 1]
Specify option name (or number) and value : [ 0]
**** New **** Contingency analysis options:
1: monBranRatingBase 1 // Base case rating (1-A;2-B;3-C;4-D)
2: monBranRatingCont 2 // Contingency rating (1-A;2-B;3-C;4-D)
3: monBranRatingMultBase 100.00 // Base case rating multipliers
4: monBranRatingMultCont 100.00 // Contingency rating multipliers
5: contChanCutOffMW 5.0 // MW cutoff to ignore constraints if cont.flow doesn't changes from the base case more than
6: contChanCutOffPercent 2.0 // Rating %% cutoff to ignore if cont.flow changes from the base case is less than
7: PAR_AdjEnabledContAnal 1 // Phase shifter model for the base case (0-fixed angle;1-control flow), always fixed in contingency
8: adjustRatingMVA 0 // Adjust branch MW rating based on MVAR flow (DC analysis)
9: limitTypeLine 0 // Use AMP (=0) or MVA (1) limit to check lines violation in AC mode
10: limitTypeTran 1 // Use AMP (=0) or MVA (1) limit to check transformer violation in AC mode
11: voltMinChange 0.0050 // Voltage change cutoff in PU to ignore voltage violations with change from the base case is smaller
12: numContMaxAlloc 15000 // Max number of contingencies
13: numEventsAlloc 35000 // Max number of contingency events
14: numDispEventAlloc 60000 // Max number of generation redispatch events
15: numLFgatesMaxAlloc 10000 // Max number of flowgates
16: maxFgateBranches 100 // Max number of branches (events) per flowgate
17: mulSecPrintMode 0 // Multi-section line modeling (0-ignore;1-honor)
18: smartCutOff 0 // Use Smart cutoff based on Max conting impact using base case and conting rating difference (0-no;1-yes)
19: maxExcludesAlloc 10000 // Max number of exclude records
20: showConAnalLFLog 0 // Show LF convergence during ACCONT
21: MAXOUTAGES 15000 // Maximum number of outages
22: maxORAFlowResults 2000000 // Maximum number of ORA or N-1-1 results to report
23: ACCONTRepeatSolution 0 // If first AC solution failed, repeat with alternative Flat/Hot start(0-no,1-yes),2-limit to the best iteration
24: showNotMappedContEvents 1 // When generating contingency file, show not mapped event(0-no,1-yes)
25: monBranRatingEnAdd1 0 // Enable first additional rating reporting (0-no,1-yes)
26: monBranRatingEnAdd2 0 // Enable second additional rating reporting (0-no,1-yes)
27: monBranRatingAdd1 3 // Additional Rating 1 (1-A;2-B;3-C;4-D)
28: monBranRatingAdd2 3 // Additional Rating 2 (1-A;2-B;3-C;4-D)
29: monBranRatingMultAdd1 100.00 // Additional Rating 1 multiplier
30: monBranRatingMultAdd2 100.00 // Additional Rating 2 multiplier
31: LoadingCutOff 0.00 // Loading cutoff in percent for displaying cont analysis flow results
32: showAllHighPreSCD 0 // Show SCD result if pre-SCD above cutoff but post-SCD below
33: N11MODE 1 // Run in N-1+Application Mode
34: multiCoreN1 0 // Run in N-1 ACCont in multi-core mode? [0-No, 1-Yes]
35: numLowestLoading 5 // Max number of lowest loading results to report
36: VoltLimAdder 0.00000 // Add this to voltage limit to expand or limit hi/low voltage viol results
37: StudyFiles 1 // Show Names of Input Files on all reports
38: MonConMode 1 // Select Mon/Con mode (1:Regular, 2:Flowgate, 3:Voltgate, 4:Flowgate & Voltgate
39: MaxMonConMode 100000 // Maximum Number of mon/con mode entries
40: keepDuplicates 1 // Keep contingency even if exact duplicate? [0=no, 1=yes]
41: correctiveSwitchingMode 0 // Run in corrective switching mode? [0=no, 1=yes]
42: lodfCutoff 0.01000 // Cutoff for LODF report (absolute value)
43: lodfImpCutoff 1.00 // MW cutoff for LODF Impact report (lodf*(event rating))
44: maxFgEventTotal 30000 // Max number of all branches and events for all flowgatesflowgate
45: maxEvPerCont 60 // Max number of events (events) per contingency
46: maxSPSLogic 10000 // Max number of SPS logic elements
47: maxInjGroups 500 // Max number of SPS AUX Injections Groups
48: maxSPSInterfaces 1000 // Max number of SPS AUX Interfaces
49: co_mode 0 // Cascading mode, 0=no, 1=yes
50: co_branchoutage 1 // Trip Overloaded Branches in Cascading Outage, 0=no, 1=yes
51: co_genoutage 1 // Trip Generators in Cascading Outage, 0=no, 1=yes
52: co_genterminalbus 0 // Trip Generators with low voltage violation at generator terminal bus, 0=no, 1=yes
53: co_loadoutage 1 // Trip Loads in Cascading Outage, 0=no, 1=yes
54: co_maxlevel 10 // Maximum cascading outage test level
55: saveCOCases 0 // Save a case for each cascading step case
56: COSaveDirectory [] // Folder to save each cascading outage case
57: kVLayer12_Volt 100.0 // Voltage between Layer 1 and Layer 2
58: kVLayer23_Volt 230.0 // Voltage between Layer 2 and Layer 3
59: kVLayer34_Volt 345.0 // Voltage between Layer 3 and Layer 4
60: kVLayer45_Volt 500.0 // Voltage between Layer 4 and Layer 5
61: kVLayer1_LDCutoff 115.0 // Layer 1 RelayLoadability Percent
62: kVLayer2_LDCutoff 115.0 // Layer 2 RelayLoadability Percent
63: kVLayer3_LDCutoff 115.0 // Layer 3 RelayLoadability Percent
64: kVLayer4_LDCutoff 115.0 // Layer 4 RelayLoadability Percent
65: kVLayer5_LDCutoff 115.0 // Layer 5 RelayLoadability Percent
66: zeroRatingCutoff 0.000100 // If rating is below this, set rating to 9999
67: saveN11Cases 0 // Save a case for each N-1-1 first-level case
68: N11SaveDirectory [] // Folder to save each N-1-1 first-level case
69: acVerifyFgate 0 // Enable flowgate AC verification (0-No;1-Yes)
70: useContingencyComments 0 // Use Comments in contingency file in contingency reporting
71: ignoreEnd2Exit 0 // Ignore END statement to exit reading sub mon con exc files (0-No, 1-Yes)
72: nearSyskVLayer1 5 // Subsystem proximity screen 1st kV Layer
73: nearSyskVLayer2 5 // Subsystem proximity screen 2nd kV Layer
74: nearSyskVLayer3 5 // Subsystem proximity screen 3rd kV Layer
75: nearSyskVLayer4 5 // Subsystem proximity screen 4rd kV Layer
76: nearSyskVLayer5 5 // Subsystem proximity screen 5th kV Layer
77: nearSyskVLayer12_Volt 100.0 // Subsystem proximity screen Voltage between Layer 1 and Layer 2
78: nearSyskVLayer23_Volt 230.0 // Subsystem proximity screen Voltage between Layer 2 and Layer 3
79: nearSyskVLayer34_Volt 345.0 // Subsystem proximity screen Voltage between Layer 3 and Layer 4
80: nearSyskVLayer45_Volt 500.0 // Subsystem proximity screen Voltage between Layer 4 and Layer 5
81: nearSysScrnMod 0 // Subsystem Screening for nearby contingencies (1st and 2nd)
82: nearSyskVCutoff 0.00 // Subsystem proximity Specify kV Cutoff
83: nearSysApplykVCutoffOption 0 // Subsystem proximity [0-one side only, 1-both sides]
84: nearByLayerSubSysName [Undefined] // - Subsystem Name for proximity contingency layer screen
Select data category:(L2): [ 0]
Select main menu function(L1): [ 0]
Select main menu function(L1): [ lfopt] = Selected Function 11 - LFOPTIONS - LF options
Select data category:(L2): [ misc] = Selected Function 3 - MISC - Miscellaneous options
**** Current **** Select Miscellaneous LF options
1: ZeroImpThr 0.000100 // Zero impedance threshold in PU
2: MemFactor 5 // Sparse methods fill in allocation factor
3: busRepMode 2 // Bus Output Order (1-by names; 2- by numbers)
4: busInputMode 2 // Default Bus input mode (1-names; 2-numbers; 3-branchnames)
5: busOutputMode 2 // Default Bus output mode (1-names; 2-numbers; 3-branchnames)
6: ShowContWarn 1 // Report contingency input warnings during input
7: branNamePrefix [/* [] // Branchname prefix
8: branNameSuffix []] // Branchname suffix
9: maxRXRatio 10.00 // Max allowed R/X ratio
10: useCaseNameFullPath 0 // Use LF case name (0) or full path as scenario name(1)
11: readBranchNamesFromRAW 0 // Read branch names from RAW file? (1=yes, 0=no)
12: readEquipNamesFromRAW 0 // Read equipment names (bus, gen,load,branches, shunts) from RAW file (1=yes, 0=no)
13: reportBusAreaName 0 // Add area names to LF data reports(bus, gen,load,branches, shunts)(1=yes, 0=no)
14: reportBusZoneName 0 // Add zone names to LF data reports(bus, gen,load,branches, shunts)(1=yes, 0=no)
15: scaleFactorR 1.000 // Factor to scale down branch resistances (default 1.00 - do not adjust)
16: scaleFactorX 1.000 // Factor to scale down branch impedance (default 1.00 - do not adjust)
17: scaleFactorRLowVolt 1.000 // Factor to scale down branch resistances for low voltage branches
18: scaleFactorXLowVolt 1.000 // Factor to scale down branch impedance for low voltage branches
19: maxBuses 110000 // Maximum number of buses(default 95000)
20: maxBranches 190000 // Maximum number of branches(default 19000), includes 2 and 3 W transf
21: maxGenerators 25000 // Maximum number of generators and plants (default 25000)
22: maxLoads 190000 // Maximum number of loads
23: maxTransfor 40000 // Maximum number of 2W and 3W transformers total
24: maxShunts 15000 // Maximum number of shunts
25: maxStations 110000 // Maximum number of substations
26: rawIDMethod 0 // Remove PTI prefix from RAW number in report header? (1=yes, 0=no)
27: contFormatOut 0 // Contingency file format when creating cont file (0-PTI, 1-AUX,2-GE)
28: applyGenLocal 0 // Set generators to local voltage regulation (1=yes, 0=no)
29: LockSWShunt 0 // Set discrete switched shunt to a fixed mode (1=yes, 0=no)
30: maxEnodes 300000 // Maximum number of enodes for EMS apps
31: shuntMinVoltBand 0.0000 // Minimum voltage bands for shunts (default 0.00 - do not apply)
32: DCLFTapMode 0 // Branch flow model (0-include TAP ratio, 1-ignore TAP) for DC load flow
33: busNameQuotes 0 // DO NOT USE UNLESS YOU HAVE UNUSUAL BUS NAMES. Add single quote character around bus names in reports
34: NoStarBusNumbers 0 // Don't print bus numbers of 3-wind star buses in mon branch reports
35: autoDimensions 1 // Automatically increase case max dimensions if initial are too small [0-no, 1-yes]
Specify option name (or number) and value : [ busOutputMode][ 2]
Specify option name (or number) and value : [ 0]
**** New **** Select Miscellaneous LF options
1: ZeroImpThr 0.000100 // Zero impedance threshold in PU
2: MemFactor 5 // Sparse methods fill in allocation factor
3: busRepMode 2 // Bus Output Order (1-by names; 2- by numbers)
4: busInputMode 2 // Default Bus input mode (1-names; 2-numbers; 3-branchnames)
5: busOutputMode 2 // Default Bus output mode (1-names; 2-numbers; 3-branchnames)
6: ShowContWarn 1 // Report contingency input warnings during input
7: branNamePrefix [/* [] // Branchname prefix
8: branNameSuffix []] // Branchname suffix
9: maxRXRatio 10.00 // Max allowed R/X ratio
10: useCaseNameFullPath 0 // Use LF case name (0) or full path as scenario name(1)
11: readBranchNamesFromRAW 0 // Read branch names from RAW file? (1=yes, 0=no)
12: readEquipNamesFromRAW 0 // Read equipment names (bus, gen,load,branches, shunts) from RAW file (1=yes, 0=no)
13: reportBusAreaName 0 // Add area names to LF data reports(bus, gen,load,branches, shunts)(1=yes, 0=no)
14: reportBusZoneName 0 // Add zone names to LF data reports(bus, gen,load,branches, shunts)(1=yes, 0=no)
15: scaleFactorR 1.000 // Factor to scale down branch resistances (default 1.00 - do not adjust)
16: scaleFactorX 1.000 // Factor to scale down branch impedance (default 1.00 - do not adjust)
17: scaleFactorRLowVolt 1.000 // Factor to scale down branch resistances for low voltage branches
18: scaleFactorXLowVolt 1.000 // Factor to scale down branch impedance for low voltage branches
19: maxBuses 110000 // Maximum number of buses(default 95000)
20: maxBranches 190000 // Maximum number of branches(default 19000), includes 2 and 3 W transf
21: maxGenerators 25000 // Maximum number of generators and plants (default 25000)
22: maxLoads 190000 // Maximum number of loads
23: maxTransfor 40000 // Maximum number of 2W and 3W transformers total
24: maxShunts 15000 // Maximum number of shunts
25: maxStations 110000 // Maximum number of substations
26: rawIDMethod 0 // Remove PTI prefix from RAW number in report header? (1=yes, 0=no)
27: contFormatOut 0 // Contingency file format when creating cont file (0-PTI, 1-AUX,2-GE)
28: applyGenLocal 0 // Set generators to local voltage regulation (1=yes, 0=no)
29: LockSWShunt 0 // Set discrete switched shunt to a fixed mode (1=yes, 0=no)
30: maxEnodes 300000 // Maximum number of enodes for EMS apps
31: shuntMinVoltBand 0.0000 // Minimum voltage bands for shunts (default 0.00 - do not apply)
32: DCLFTapMode 0 // Branch flow model (0-include TAP ratio, 1-ignore TAP) for DC load flow
33: busNameQuotes 0 // DO NOT USE UNLESS YOU HAVE UNUSUAL BUS NAMES. Add single quote character around bus names in reports
34: NoStarBusNumbers 0 // Don't print bus numbers of 3-wind star buses in mon branch reports
35: autoDimensions 1 // Automatically increase case max dimensions if initial are too small [0-no, 1-yes]
Select data category:(L2): [ 0]
Select main menu function(L1): [ solve] = Selected Function 3 - SOLVE - Solve LF and Review flows
Select load flow solution or report function: (L2): [ fdec] = Selected Function 2 - FDEC - Fast Decoupled Load Flow
Solving AC Load Flow
LFOptions: Toln= 1.0000 MxIt=50 HotStrt ZILIm=0.00010 lowVCtOf=0.8000 mxVChn:In=0.2000 Res=0.1500 mxAngChn:In=3.0000 Res=0.1500
Adjustm: ItrVarChk=0 PAR-ON TAP-ON Shunt-ON-All DC_TAP-ON
Total 113286 closed branches out of 119265
Bus ordering. Diag= 95025. Offd =244794 Max.size 250480. #Swing=9 Offline=921. IgnoreOpen=0
WarnID-1850-1-38 PAR Max angle 180.1 is too big. Set Max= 180.0 for 668090 WHITESH7 110 668091 WHSL1PH7 110 7
WarnID-1851-1-39 PAR Min angle -180.1 is too big (negative). Set Min= -180.0 for 668090 WHITESH7 110 668091 WHSL1PH7 110 7
WarnID-1850-2-40 PAR Max angle 180.1 is too big. Set Max= 180.0 for 668090 WHITESH7 110 668092 WHSL2PH7 110 8
WarnID-1851-2-41 PAR Min angle -180.1 is too big (negative). Set Min= -180.0 for 668090 WHITESH7 110 668092 WHSL2PH7 110 8
Total 95 regulating PARs
WarnID-1867-1-42 Transformer 100565 MERRILL RD 345 100566 CONV_ME 382 1 is radial. LTC control is disabled.
WarnID-1867-2-43 Transformer 109277 NEWPORT HY 12.5 108121 NEWPORT_T2LS 46.0 1 is radial. LTC control is disabled.
WarnID-1867-3-44 Transformer 109002 MORRISVIL2_D 12.0 108623 MORRISVILL 2 34.5 1 is radial. LTC control is disabled.
WarnID-1867-4-45 Transformer 116541 N-CANAL 3 13.8 116228 N-CANAL 115 3 is radial. LTC control is disabled.
WarnID-1867-5-46 Transformer 122526 NOERA STREET 4.80 122527 NOERA STREET 13.8 1 is radial. LTC control is disabled.
WarnID-1867-6-47 Transformer 125011 EFISH115 115 126281 E FISHKILL 345 2 is radial. LTC control is disabled.
WarnID-1867-7-48 Transformer 126139 HURLEY_13._A 13.8 125104 HURLEY 6 69.0 5 is radial. LTC control is disabled.
WarnID-1867-8-49 Transformer 131129 AMENIA46 46.0 131121 AMENIA69 69.0 1 is radial. LTC control is disabled.
WarnID-1867-9-50 Transformer 135383 S219-182 115 135846 PARKCLUB 13.2 1 is radial. LTC control is disabled.
WarnID-1867-10-51 Transformer 151664 MOOSE_LK_B2 44.0 999881 103:MOOSE L 44.0 T2 is radial. LTC control is disabled.
WarnID-1867-11-52 Transformer 151673 PERRAU_FLS_B 12.5 151303 PERRAULT_FLS 118 T1 is radial. LTC control is disabled.
WarnID-1867-12-53 Transformer 152096 TEMBEC_SP_FL 220 152726 TEMB_SP_FLT6 6.60 T6 is radial. LTC control is disabled.
WarnID-1867-13-54 Transformer 152604 HOLLOW_#3TR2 4.16 152608 HOLLOWAY_#3 4.16 R2 is radial. LTC control is disabled.
WarnID-1867-14-55 Transformer 152679 MASSEY_DS_B 12.5 152678 MASSEY_DS_R1 12.5 R1 is radial. LTC control is disabled.
WarnID-1867-15-56 Transformer 153099 BRACEBRIDGE 220 153650 BRACEBRIDGE 44.0 T1 is radial. LTC control is disabled.
WarnID-1867-16-57 Transformer 154626 LIMEBANK_B1 27.6 154228 LIMEBANK_H1 118 T1 is radial. LTC control is disabled.
WarnID-1867-17-58 Transformer 154639 NAVAN_DS_B1 8.32 154240 NAVAN_DS 118 T1 is radial. LTC control is disabled.
WarnID-1867-18-59 Transformer 154644 NAVAN_DS_NL2 27.6 154240 NAVAN_DS 118 T2 is radial. LTC control is disabled.
WarnID-1867-19-60 Transformer 154654 RICHMOND_DSB 27.6 154248 RCHMND_S_MTS 118 T1 is radial. LTC control is disabled.
WarnID-1867-20-61 Transformer 154610 CUMBRLD_DSB2 8.32 154291 CUMBRLD_DS_B 118 T2 is radial. LTC control is disabled.
WarnID-1867-21-62 Transformer 154608 CUMBRLD_DSB1 8.32 154609 CUMBRLD_DSR1 8.32 R1 is radial. LTC control is disabled.
WarnID-1867-22-63 Transformer 154661 RUSSELL_DS 8.32 154662 RUSSELL_DSR1 8.32 R1 is radial. LTC control is disabled.
WarnID-1867-23-64 Transformer 155607 COBDEN_DS 13.4 155213 COBDEN_TSX2Y 118 T3 is radial. LTC control is disabled.
WarnID-1867-24-65 Transformer 155610 MT_CHUTE_DS 12.5 155218 MT_CHUTE_DS 118 T1 is radial. LTC control is disabled.
WarnID-1867-25-66 Transformer 155699 NORTHBROOK_B 12.5 155262 NORTHBROOK 118 T1 is radial. LTC control is disabled.
WarnID-1867-26-67 Transformer 155672 DOBBIN_DS_B1 27.6 155279 DOBBIN_DS 118 T1 is radial. LTC control is disabled.
WarnID-1867-27-68 Transformer 156625 GERDAU_AW_B 44.0 156089 GERDAU_T24C 220 T2 is radial. LTC control is disabled.
WarnID-1867-28-69 Transformer 156623 GERDAU_AW_L1 44.0 156090 GERDAU_T26C 220 T4 is radial. LTC control is disabled.
WarnID-1867-29-70 Transformer 160676 TILBURY_TS 27.6 160247 TILBURY_TS 118 T1 is radial. LTC control is disabled.
WarnID-1867-30-71 Transformer 160750 EWCC_LD1 0.60 160748 EAST_WIBD_G2 13.8 T1 is radial. LTC control is disabled.
WarnID-1867-31-72 Transformer 160751 EWCC_LD2 0.60 160749 EAST_WIND_G1 13.8 T1 is radial. LTC control is disabled.
WarnID-1867-32-73 Transformer 214293 LIMERICK7 230 213741 LIM10 13.8 1 is radial. LTC control is disabled.
WarnID-1867-33-74 Transformer 213771 LMSAFEGD 13.8 213745 LIMRICK8 69.0 1 is radial. LTC control is disabled.
WarnID-1867-34-75 Transformer 213771 LMSAFEGD 13.8 213745 LIMRICK8 69.0 2 is radial. LTC control is disabled.
WarnID-1867-35-76 Transformer 213871 PCHSU343 13.8 213868 PCHBTM2 230 1 is radial. LTC control is disabled.
WarnID-1867-36-77 Transformer 221357 NEWGT030 34.5 221771 NEWGT -7 13.8 1 is radial. LTC control is disabled.
WarnID-1867-37-78 Transformer 221365 NEWGT032 34.5 221773 NEWGT -9 13.8 1 is radial. LTC control is disabled.
WarnID-1867-38-79 Transformer 221365 NEWGT032 34.5 221777 NEWGT -6 13.8 1 is radial. LTC control is disabled.
WarnID-1867-39-80 Transformer 224072 BUZZ 1W 13.8 224014 BUZZ 138 138 1 is radial. LTC control is disabled.
WarnID-1867-40-81 Transformer 224073 BUZZ 2W 13.8 224014 BUZZ 138 138 1 is radial. LTC control is disabled.
WarnID-1867-41-82 Transformer 224074 BUZZ 3W 13.8 224014 BUZZ 138 138 1 is radial. LTC control is disabled.
WarnID-1867-42-83 Transformer 224075 BUZZ 1E 13.8 224014 BUZZ 138 138 1 is radial. LTC control is disabled.
WarnID-1867-43-84 Transformer 224076 BUZZ 2E 13.8 224014 BUZZ 138 138 1 is radial. LTC control is disabled.
WarnID-1867-44-85 Transformer 224077 BUZZ 3E 13.8 224014 BUZZ 138 138 1 is radial. LTC control is disabled.
WarnID-1867-45-86 Transformer 227115 MT VICTORIA 69.0 227202 LOWMTVICTOR2 12.5 1 is radial. LTC control is disabled.
WarnID-1867-46-87 Transformer 232508 LYNCH 2 24.9 232200 LYNCH 69.0 1 is radial. LTC control is disabled.
WarnID-1867-47-88 Transformer 232610 VIENNAL1 12.5 232242 VIENNALC 69.0 1 is radial. LTC control is disabled.
WarnID-1867-48-89 Transformer 243481 05CANAL 138 246576 05CANAL L 13.8 1 is radial. LTC control is disabled.
WarnID-1867-49-90 Transformer 243491 05CORRID 138 246644 05CORRIDR 34.5 4 is radial. LTC control is disabled.
WarnID-1867-50-91 Transformer 243507 05FIFTH 138 246655 05FIFTH L 13.8 1 is radial. LTC control is disabled.
WarnID-1867-51-92 Transformer 243511 05GAY 138 246577 05GAY L 13.8 1 is radial. LTC control is disabled.
WarnID-1867-52-93 Transformer 243524 05HESS NORTH 138 246659 05HESS L 13.8 1 is radial. LTC control is disabled.
WarnID-1867-53-94 Transformer 243532 05KIRK 138 246717 05KIRK L 34.5 1 is radial. LTC control is disabled.
WarnID-1867-54-95 Transformer 243551 05OSU 138 246667 05OSU L 13.8 1 is radial. LTC control is disabled.
WarnID-1867-55-96 Transformer 243553 05POLARS 138 246641 05POLARISL 34.5 1 is radial. LTC control is disabled.
WarnID-1867-56-97 Transformer 243575 05ST.CLR 138 246619 05ST.CLR L 13.8 1 is radial. LTC control is disabled.
WarnID-1867-57-98 Transformer 243581 05TAYLOR 138 246721 05TAYLOR L 34.5 1 is radial. LTC control is disabled.
WarnID-1867-58-99 Transformer 243584 05VINE 138 246579 05VINE L 13.8 1 is radial. LTC control is disabled.
WarnID-1867-59-100 Transformer 252193 HOPPLE P 12.5 251343 08HOPPLP 69.0 1 is radial. LTC control is disabled.
WarnID-1867-60-101 Transformer 251807 EVENDL 1 34.5 251794 08EVNDL1 34.5 1 is radial. LTC control is disabled.
WarnID-1867-61-102 Transformer 312845 3WINYAH 115 311600 1WINYAH 34.5 1 is radial. LTC control is disabled.
WarnID-1867-62-103 Transformer 312845 3WINYAH 115 311600 1WINYAH 34.5 2 is radial. LTC control is disabled.
WarnID-1867-63-104 Transformer 314552 3WINDSORDP 115 313857 6WINDSORDP 230 1 is radial. LTC control is disabled.
WarnID-1867-64-105 Transformer 314115 3GAINSV1 115 314037 6GAINSVL 230 1 is radial. LTC control is disabled.
WarnID-1867-65-106 Transformer 314789 2BEARSKN 69.0 314671 4BEARSKN 138 1 is radial. LTC control is disabled.
WarnID-1867-66-107 Transformer 338472 2FRAZIER! 69.0 337358 3FRAZIER 115 1 is radial. LTC control is disabled.
WarnID-1867-67-108 Transformer 338472 2FRAZIER! 69.0 337358 3FRAZIER 115 2 is radial. LTC control is disabled.
WarnID-1867-68-109 Transformer 346072 1BLANCHET2 34.5 344147 4BLANCHET2 138 1 is radial. LTC control is disabled.
WarnID-1867-69-110 Transformer 344556 1FNLK 2 12.5 344555 4FNLK 2 138 1 is radial. LTC control is disabled.
WarnID-1867-70-111 Transformer 346075 1JC FAIR 13.8 344805 2JC FAIR 69.0 1 is radial. LTC control is disabled.
WarnID-1867-71-112 Transformer 346075 1JC FAIR 13.8 344805 2JC FAIR 69.0 2 is radial. LTC control is disabled.
WarnID-1867-72-113 Transformer 345032 2OAKWOOD 34.5 345033 5FINN 161 1 is radial. LTC control is disabled.
WarnID-1867-73-114 Transformer 345121 1VESSEL1 34.5 345120 4VESSEL 138 1 is radial. LTC control is disabled.
WarnID-1867-74-115 Transformer 345122 1VESSEL2 34.4 345120 4VESSEL 138 1 is radial. LTC control is disabled.
WarnID-1867-75-116 Transformer 348995 1CLINTN_RATA 6.90 348846 7CLINTON 345 1 is radial. LTC control is disabled.
WarnID-1867-76-117 Transformer 348997 1CLINTN_RATC 4.16 348846 7CLINTON 345 1 is radial. LTC control is disabled.
WarnID-1867-77-118 Transformer 349180 1CENTRAL 4.16 349284 2CENTRAL_AM 69.0 1 is radial. LTC control is disabled.
WarnID-1867-78-119 Transformer 372421 2SANTEE115 46.0 370390 3SANTEE! 115 3 is radial. LTC control is disabled.
WarnID-1867-79-120 Transformer 400019 NORMANDY 1 69.0 998369 49-1007 69.0 1 is radial. LTC control is disabled.
WarnID-1867-80-121 Transformer 533900 WCGS_TX1_1 13.8 997234 WOLF CREEK T 13.8 1 is radial. LTC control is disabled.
WarnID-1867-81-122 Transformer 533905 WCGS_TX7_1 13.8 997232 WOLF CREEK T 13.8 1 is radial. LTC control is disabled.
WarnID-1867-82-123 Transformer 532940 EDWRDVL1 12.5 997212 EDWARDSVIL1 115 1 is radial. LTC control is disabled.
WarnID-1867-83-124 Transformer 532948 SPRINGH1 12.5 997210 SPRNGHL TX-4 115 1 is radial. LTC control is disabled.
WarnID-1867-84-125 Transformer 533113 64TH 1 13.8 997171 64TH TX-5 69.0 1 is radial. LTC control is disabled.
WarnID-1867-85-126 Transformer 533890 NTHLAND1 12.5 997166 NORTHLAND TX 12.5 3 is radial. LTC control is disabled.
WarnID-1867-86-127 Transformer 533891 NTHLAND_TER1 4.16 997166 NORTHLAND TX 12.5 3 is radial. LTC control is disabled.
WarnID-1867-87-128 Transformer 541178 LAKERD1_TER1 7.27 997078 LAKE ROAD 1 36.0 1 is radial. LTC control is disabled.
WarnID-1867-88-129 Transformer 541179 LAKERD2_TER1 7.27 997077 LAKE ROAD 2 36.0 2 is radial. LTC control is disabled.
WarnID-1867-89-130 Transformer 541374 POSTOAK_TER1 2.40 997076 POST OAK11 34.5 11 is radial. LTC control is disabled.
WarnID-1867-90-131 Transformer 541326 APCITY_TER1 2.40 997074 APPLETON C11 34.5 11 is radial. LTC control is disabled.
WarnID-1867-91-132 Transformer 541357 METZ_TER1 2.40 997073 METZ11 34.5 11 is radial. LTC control is disabled.
WarnID-1867-92-133 Transformer 541330 GRDNCTY_TER1 4.80 997072 GARDEN CIT11 34.5 11 is radial. LTC control is disabled.
WarnID-1867-93-134 Transformer 541353 MRVL77_TER1 13.1 997069 MARYVILLE77 34.5 77 is radial. LTC control is disabled.
WarnID-1867-94-135 Transformer 541328 BRWNCRV_TER1 13.1 997068 BROWNS CU22 34.5 22 is radial. LTC control is disabled.
WarnID-1867-95-136 Transformer 541195 MRVL44_TER1 13.1 997064 MARYVILLE44 34.5 44 is radial. LTC control is disabled.
WarnID-1867-96-137 Transformer 543660 LACYGN7_TER1 6.90 997045 LACYGNE 7 69.0 7 is radial. LTC control is disabled.
WarnID-1867-97-138 Transformer 543119 BRNSW_TER1 12.5 997039 BRUNSWICK1 34.5 1 is radial. LTC control is disabled.
WarnID-1867-98-139 Transformer 543124 NORTON_TER1 12.5 997038 NORTON1 34.5 1 is radial. LTC control is disabled.
WarnID-1867-99-140 Transformer 543125 S.OTWA1_TER1 12.5 997037 SOUTH OTTA1 34.5 1 is radial. LTC control is disabled.
WarnID-1867-100-141 Transformer 543122 S.OTTWA_TER1 12.5 997036 SOUTH OTTA4 34.5 4 is radial. LTC control is disabled.
!!!! Reached the maximum number (100) of messages of this type=(1867). See full warning list for more info
WarnID-1863-1-143 TAP 100230 LARRABEE RD 115 999992 LARRABEE T1 115 1 Desired voltage range=0.0080 [1.0390:1.0470] is too small comparing to step=0.0062. Expanded to [1.0383:1.0477]
WarnID-1863-2-144 TAP 108902 INDSTRL PK_D 12.5 108550 INDSTRL PARK 34.5 1 Desired voltage range=0.0400 [1.0000:1.0400] is too small comparing to step=0.0333. Expanded to [0.9950:1.0450]
WarnID-1863-3-145 TAP 109290 PUDDNG HIL_D 12.5 108554 PUDDING HILL 34.5 1 Desired voltage range=0.0400 [1.0000:1.0400] is too small comparing to step=0.0333. Expanded to [0.9950:1.0450]
WarnID-1863-4-146 TAP 108911 BURKE_DIST 12.5 108556 BURKE MOUNTN 34.5 1 Desired voltage range=0.0400 [1.0000:1.0400] is too small comparing to step=0.0333. Expanded to [0.9950:1.0450]
WarnID-1863-5-147 TAP 108937 VIL HYDE PRK 12.5 108559 V OF HYDE PK 34.5 1 Desired voltage range=0.0400 [1.0000:1.0400] is too small comparing to step=0.0333. Expanded to [0.9950:1.0450]
WarnID-1863-6-148 TAP 109100 PLAINFIELD_D 12.5 108634 PLAINFIELD 34.5 1 Desired voltage range=0.0400 [1.0000:1.0400] is too small comparing to step=0.0333. Expanded to [0.9950:1.0450]
WarnID-1863-7-149 TAP 109022 HOUSTON1 12.5 108702 HOUSTON 34.5 1 Desired voltage range=0.0400 [1.0000:1.0400] is too small comparing to step=0.0333. Expanded to [0.9950:1.0450]
WarnID-1863-8-150 TAP 109024 HOUSTON2 12.5 108702 HOUSTON 34.5 1 Desired voltage range=0.0400 [1.0000:1.0400] is too small comparing to step=0.0333. Expanded to [0.9950:1.0450]
WarnID-1863-9-151 TAP 109036 LODGE_D 12.5 108703 LODGE 34.5 1 Desired voltage range=0.0400 [1.0000:1.0400] is too small comparing to step=0.0333. Expanded to [0.9950:1.0450]
WarnID-1863-10-152 TAP 109026 WILKINS_D1 12.5 108708 STOWE35 34.5 1 Desired voltage range=0.0400 [1.0000:1.0400] is too small comparing to step=0.0333. Expanded to [0.9950:1.0450]
WarnID-1863-11-153 TAP 109032 WILKINS_D2 12.5 108708 STOWE35 34.5 1 Desired voltage range=0.0400 [1.0000:1.0400] is too small comparing to step=0.0333. Expanded to [0.9950:1.0450]
WarnID-1863-12-154 TAP 111313 WING LANE T2 13.2 111273 WING LANE 115 1 Desired voltage range=0.0126 [1.0287:1.0413] is too small comparing to step=0.0102. Expanded to [1.0273:1.0427]
WarnID-1863-13-155 TAP 122228 CAMPVILLE 27.6 120398 CAMPVILLE 115 1 Desired voltage range=0.0070 [1.0350:1.0420] is too small comparing to step=0.0063. Expanded to [1.0338:1.0432]
WarnID-1863-14-156 TAP 122228 CAMPVILLE 27.6 120398 CAMPVILLE 115 2 Desired voltage range=0.0070 [1.0350:1.0420] is too small comparing to step=0.0052. Expanded to [1.0346:1.0424]
Total 8651 voltage controlling TAPs
WarnID-1938-1-157 Reg bus is not a generator for Switch Shunt Mode 3 - discrete shunt at bus [135081 Q644_COL1 34.5 102 NYISO 165 NYSEG ME ] control MVAR output at remote plant [135081 Q644_COL1 34.5 ]. Ffixed
WarnID-1945-1-158 Reg plant Q range too small for Switch Shunt Mode 3 - discrete shunt at bus [152860 PRINCE2_CTS 34.5 103 IESO 1102 NORTH-EAST ] control MVAR output at remote plant [152860 PRINCE2_CTS 34.5 ]. Ffixed
WarnID-1945-2-159 Reg plant Q range too small for Switch Shunt Mode 3 - discrete shunt at bus [158865 SUMERHA_345 34.5 103 IESO 1108 SOUTH-WEST ] control MVAR output at remote plant [158865 SUMERHA_345 34.5 ]. Ffixed
WarnID-1945-3-160 Reg plant Q range too small for Switch Shunt Mode 3 - discrete shunt at bus [160611 PBURWELL_345 34.5 103 IESO 1110 WEST ] control MVAR output at remote plant [160611 PBURWELL_345 34.5 ]. Ffixed
WarnID-1945-4-161 Reg plant Q range too small for Switch Shunt Mode 3 - discrete shunt at bus [160785 GOSFIELD_345 34.5 103 IESO 1110 WEST ] control MVAR output at remote plant [160785 GOSFIELD_345 34.5 ]. Ffixed
Total Shunts: Continuous=602 Discrete=6177
Total 1 discrete shunts modeled as continuous during solution placed to the nearest step
Nit P_Mism #bus VoltMgn VltAngl Q_Mism #bus VoltMgn VltAngl AngChn #bus VoltMgn VltAngl VM_Chan #bus VoltMgn VltAngl DeAccFc
1p 1708.378 401140 1.0505 -0.380 540.539 615600 1.0371 0.145 0.04605 403222 1.0037 -0.156
1q -2243.526 631164 1.0069 -0.336-56763.897 348126 1.0017 -0.282 0.08519 528220 0.9751 -0.530
2p 274.411 180749 1.0165 0.640 -16.243 274676 1.0072 -0.465 0.01336 608898 1.0000 0.271
2q 125.494 180749 1.0165 0.640 -8815.042 270169 1.0021 -0.830 -0.09321 528220 1.0683 -0.524
3p -67.746 316291 1.1043 -1.056 20.809 274676 1.0399 -0.458 0.02020 255494 0.9917 -0.745
3q 33.280 316293 1.1073 -1.060 153.986 998971 1.0270 -0.575 -0.07179 255494 1.0635 -0.745
4p 36.013 637083 0.9988 -0.146 4.806 637081 0.9698 -0.129 -0.02661 255494 1.0635 -0.771
4q 19.468 255493 1.0356 -0.360 74.525 316290 1.0518 -1.109 -0.03460 693687 1.0035 -0.613
5p -20.963 255517 1.0046 -0.360 -1.440 109181 1.0547 -1.188 -0.00601 693687 1.0035 -0.619
TAPS summary: Total 56 TAP Adjusted #LowVolt=50 #HighVolt=95
5q -4.744 255517 1.0046 -0.361 44.634 316294 1.1231 -1.573 0.03153 316294 1.0915 -1.573
6p 60.291 316291 1.0791 -1.062 -1.384 316294 1.0915 -1.573 0.00391 316294 1.0915 -1.569
TAPS summary: Total 33 TAP Adjusted #LowVolt=50 #HighVolt=73
Discr Shunts summary: Total 1 Adjusted
6q -29.780 316293 1.0803 -1.060 -27.147 316293 1.0803 -1.060 0.02331 102068 1.0686 -1.125
7p -4.185 101760 1.0214 -1.615 -0.518 102071 1.6254 -1.338 -0.00993 102071 1.6254 -1.348
TAPS summary: Total 16 TAP Adjusted #LowVolt=51 #HighVolt=56
7q -1.974 101760 1.0214 -1.614 22.144 539708 1.0364 -0.425 0.02552 115483 0.9991 -1.444
8p -2.981 101760 1.0169 -1.614 -0.491 115483 0.9991 -1.444 -0.00618 102072 1.5444 -1.328
TAPS summary: Total 5 TAP Adjusted #LowVolt=51 #HighVolt=46
8q -1.449 101760 1.0169 -1.614 22.572 539708 1.0174 -0.425 0.01895 539708 0.9985 -0.425
9p -3.029 101760 1.0122 -1.614 0.250 101760 1.0122 -1.614 0.00122 217181 1.0300 -1.988
TAPS summary: Total 5 TAP Adjusted #LowVolt=53 #HighVolt=45
9q -1.376 101760 1.0122 -1.613 23.017 539708 0.9985 -0.426 0.01895 539708 0.9795 -0.426
10p -0.980 101760 1.0119 -1.613 -0.749 101380 1.0347 -1.597 -0.00128 100483 1.4984 -1.785
TAPS summary: Total 3 TAP Adjusted #LowVolt=53 #HighVolt=44
10q -1.868 128825 1.0038 -1.580 15.463 539708 0.9795 -0.426 0.01270 539708 0.9668 -0.426
11p -1.884 128825 1.0037 -1.580 -0.256 101740 1.0209 -1.617 0.00118 217181 1.0300 -1.986
TAPS summary: Total 2 TAP Adjusted #LowVolt=51 #HighVolt=44
11q 2.136 272500 1.0371 -0.685 7.738 539708 0.9668 -0.426 0.01511 217181 1.0149 -1.986
12p -2.230 239073 1.0018 -0.934 0.154 217181 1.0149 -1.986 0.00036 217146 0.9107 -1.626
TAPS summary: Total 1 TAP Adjusted #LowVolt=51 #HighVolt=43
12q 0.267 129343 1.0512 -1.403 4.284 217181 1.0149 -1.986 0.02285 217181 0.9920 -1.986
13p 0.115 999229 0.9946 -1.826 0.235 217181 0.9920 -1.986 -0.00017 217181 0.9920 -1.986
TAPS summary: Total 1 TAP Adjusted #LowVolt=51 #HighVolt=43
13q 0.253 217055 1.0227 -1.885 4.422 217181 0.9920 -1.986 0.02312 217181 0.9689 -1.986
14p -0.140 217055 1.0227 -1.885 0.245 217181 0.9689 -1.986 -0.00034 217181 0.9689 -1.986
TAPS summary: Total 1 TAP Adjusted #LowVolt=51 #HighVolt=43
14q 0.275 217055 1.0227 -1.885 4.479 217181 0.9689 -1.986 0.02293 217181 0.9460 -1.986
15p -0.115 999229 0.9947 -1.826 0.248 217181 0.9460 -1.986 -0.00025 217181 0.9460 -1.987
TAPS summary: Total 1 TAP Adjusted #LowVolt=51 #HighVolt=43
15q 0.186 217055 1.0226 -1.885 3.063 217181 0.9460 -1.987 0.01559 217181 0.9304 -1.987
16p -0.083 999229 0.9948 -1.826 0.173 217181 0.9304 -1.987 -0.00018 217181 0.9304 -1.987
16q 0.037 345989 1.0400 -0.093 0.178 217181 0.9304 -1.987
2032S_gas_alt#3a_212mw.raw. Fast Dec LF solved in 16 iterations. LargMism(MW) P=0.0371 Q=0.1780 Toln=1.0000
Swing bus dispatch summary
Bus# Bus Name Volt Area AreaName Zon ZoneName DispChan curPGen PrevPGen MinPGen MaxPGen curQGen MinQGen MaxQGen VltSched
669732 KETTLE3G 13.8 667 MH 1649 MHRURALN 0.02 100.40 100.38 6.00 102.00 34.18 -63.00 63.00 1.0100
652585 NB WEST4 230 997 WBDC-WECC 1603 WAPA_1603 -0.00 173.56 173.56 -250.00 250.00 -13.00 -250.00 250.00 1.0300
599956 PNM-DC7 345 999 WECC 999 WECC 0.00 451.20 451.20 -1000.00 1000.00 -133.04 -500.00 500.00 1.0000
590012 MOSES3 G 24.0 998 ERCOT 998 Zon_998 -0.00 762.16 762.16 463.00 765.00 216.63 -200.00 275.00 1.0320
590002 OKLAUN1G 24.0 998 ERCOT 998 Zon_998 -0.00 401.61 401.61 175.00 670.00 87.82 -280.00 400.00 1.0350
364003 1BR FERRY N3 22.0 347 TVA 1360 MUSCLE SHOAL 3.20 1287.33 1284.14 1256.00 1302.50 139.28 50.00 278.90 1.0400
195205 BBK B1 230 108 NF 185 Zon_185 0.00 376.86 376.86 -1000.00 1000.00 -66.41 -600.00 600.00 1.0000
181436 OTTOHD 120 104 TE 1151 INTERLG 0.00 -69.02 -69.02 -100.00 100.00 75.03 -61.97 75.00 1.0235
180700 EQUILIBRE 735 104 TE 1144 STLAUREN 0.03 1.41 1.38 -50.00 50.00 0.00 -5.00 5.00 1.0000
Total Swing Dispatch change = 3.25
********************************************************************************************
The following shunts could not satisfy their voltage target (possibly oscillating). Consder enabling mode lockOscShuntACCont to prevent movement during N-1
********************************************************************************************
WarnID-1826-1-162 Switched shunt at bus [121456 GLENBROOK_C1 115 101 116 ] could not reach target during initial solution (possibly oscillating).
WarnID-1826-2-163 Switched shunt at bus [121458 GLENBROOK_C2 115 101 116 ] could not reach target during initial solution (possibly oscillating).
Select load flow solution or report function: (L2): [ 0]
Select main menu function(L1): [ 0]
Select main menu function(L1): [ read] = Selected Function 1 - READ - Read TARA input files
Select function(L2): [ alldef] = Selected Function 19 - ALLDEF - Read sub/con/mon/exc data
Define subsystem,conting, monit and exclude files
Select subsystem File:[ "C:\Users\03419\Desktop\2022 Gas Study\2022 series_sub_EKPC-LGEE.sub"]
Define Contingency File:[ "C:\Users\03419\Desktop\2022 Gas Study\Option 3A N-1-1 con file.con"]
Define First-Level Scenarios definition File Name:[ "C:\Users\03419\Desktop\2022 Gas Study\Option 3A N-1-1 con file.con"]
Select Monitored constraints File:[ "C:\Users\03419\Desktop\2022 Gas Study\2022 series_mon_EKPC-LGEE.mon"]
Define Exclude File :[ nofile.nofile]
*** Opened [C:\Users\03419\Desktop\2022 Gas Study\2022 series_sub_EKPC-LGEE.sub]-(Lev=1). Current directory - [C:\Users\03419\Desktop\2022 Gas Study\temp]
WarnID-1009-1-165 Bus number [243760] not found
File [C:\Users\03419\Desktop\2022 Gas Study\2022 series_sub_EKPC-LGEE.sub]. Line 6: BUS 243760
WarnID-4040-1-165 Subsystem EKPC_EXT has total zero participation factor.
WarnID-5702-1-166 No participating buses can be scaled for EKPC_EXT . Using uniform distr - Found 1 online buses
WarnID-4040-2-167 Subsystem EKPC has total zero participation factor.
WarnID-5702-2-168 No participating buses can be scaled for EKPC . Using uniform distr - Found 579 online buses
WarnID-4040-3-169 Subsystem LGEE has total zero participation factor.
WarnID-5702-3-170 No participating buses can be scaled for LGEE . Using uniform distr - Found 999 online buses
WarnID-1009-2-172 Bus number [243003] not found
File [C:\Users\03419\Desktop\2022 Gas Study\2022 series_sub_EKPC-LGEE.sub]. Line 37: BUS 243003
WarnID-1009-3-173 Bus number [243746] not found
File [C:\Users\03419\Desktop\2022 Gas Study\2022 series_sub_EKPC-LGEE.sub]. Line 84: BUS 243746
WarnID-1009-4-174 Bus number [243755] not found
File [C:\Users\03419\Desktop\2022 Gas Study\2022 series_sub_EKPC-LGEE.sub]. Line 86: BUS 243755
WarnID-1009-5-175 Bus number [243757] not found
File [C:\Users\03419\Desktop\2022 Gas Study\2022 series_sub_EKPC-LGEE.sub]. Line 87: BUS 243757
WarnID-1009-6-176 Bus number [243760] not found
File [C:\Users\03419\Desktop\2022 Gas Study\2022 series_sub_EKPC-LGEE.sub]. Line 90: BUS 243760
WarnID-1009-7-177 Bus number [243761] not found
File [C:\Users\03419\Desktop\2022 Gas Study\2022 series_sub_EKPC-LGEE.sub]. Line 91: BUS 243761
WarnID-1009-8-178 Bus number [244603] not found
File [C:\Users\03419\Desktop\2022 Gas Study\2022 series_sub_EKPC-LGEE.sub]. Line 99: BUS 244603
WarnID-1009-9-179 Bus number [244629] not found
File [C:\Users\03419\Desktop\2022 Gas Study\2022 series_sub_EKPC-LGEE.sub]. Line 101: BUS 244629
WarnID-1009-10-180 Bus number [247414] not found
File [C:\Users\03419\Desktop\2022 Gas Study\2022 series_sub_EKPC-LGEE.sub]. Line 112: BUS 247414
WarnID-4040-4-180 Subsystem AEP has total zero participation factor.
WarnID-5702-4-181 No participating buses can be scaled for AEP . Using uniform distr - Found 75 online buses
WarnID-1009-11-183 Bus number [248003] not found
File [C:\Users\03419\Desktop\2022 Gas Study\2022 series_sub_EKPC-LGEE.sub]. Line 121: BUS 248003
WarnID-4040-5-183 Subsystem OVEC has total zero participation factor.
WarnID-5702-5-184 No participating buses can be scaled for OVEC . Using uniform distr - Found 4 online buses
WarnID-1009-12-186 Bus number [253038] not found
File [C:\Users\03419\Desktop\2022 Gas Study\2022 series_sub_EKPC-LGEE.sub]. Line 138: BUS 253038
WarnID-1009-13-187 Bus number [253110] not found
File [C:\Users\03419\Desktop\2022 Gas Study\2022 series_sub_EKPC-LGEE.sub]. Line 145: BUS 253110
WarnID-4040-6-187 Subsystem DPL has total zero participation factor.
WarnID-5702-6-188 No participating buses can be scaled for DPL . Using uniform distr - Found 12 online buses
WarnID-1009-14-190 Bus number [250035] not found
File [C:\Users\03419\Desktop\2022 Gas Study\2022 series_sub_EKPC-LGEE.sub]. Line 173: BUS 250035
WarnID-1009-15-191 Bus number [251814] not found
File [C:\Users\03419\Desktop\2022 Gas Study\2022 series_sub_EKPC-LGEE.sub]. Line 209: BUS 251814
WarnID-1009-16-192 Bus number [252089] not found
File [C:\Users\03419\Desktop\2022 Gas Study\2022 series_sub_EKPC-LGEE.sub]. Line 215: BUS 252089
WarnID-1009-17-193 Bus number [252090] not found
File [C:\Users\03419\Desktop\2022 Gas Study\2022 series_sub_EKPC-LGEE.sub]. Line 216: BUS 252090
WarnID-1009-18-194 Bus number [252091] not found
File [C:\Users\03419\Desktop\2022 Gas Study\2022 series_sub_EKPC-LGEE.sub]. Line 217: BUS 252091
WarnID-1009-19-195 Bus number [252114] not found
File [C:\Users\03419\Desktop\2022 Gas Study\2022 series_sub_EKPC-LGEE.sub]. Line 218: BUS 252114
WarnID-1009-20-196 Bus number [252115] not found
File [C:\Users\03419\Desktop\2022 Gas Study\2022 series_sub_EKPC-LGEE.sub]. Line 219: BUS 252115
WarnID-1009-21-197 Bus number [252189] not found
File [C:\Users\03419\Desktop\2022 Gas Study\2022 series_sub_EKPC-LGEE.sub]. Line 220: BUS 252189
WarnID-1009-22-198 Bus number [252229] not found
File [C:\Users\03419\Desktop\2022 Gas Study\2022 series_sub_EKPC-LGEE.sub]. Line 221: BUS 252229
WarnID-1009-23-199 Bus number [252271] not found
File [C:\Users\03419\Desktop\2022 Gas Study\2022 series_sub_EKPC-LGEE.sub]. Line 222: BUS 252271
WarnID-4040-7-199 Subsystem DEOK has total zero participation factor.
WarnID-5702-7-200 No participating buses can be scaled for DEOK . Using uniform distr - Found 59 online buses
WarnID-4040-8-201 Subsystem TVA has total zero participation factor.
WarnID-5702-8-202 No participating buses can be scaled for TVA . Using uniform distr - Found 49 online buses
WarnID-3168-1-204 END statement may cause portions of the file to be skipped
File [C:\Users\03419\Desktop\2022 Gas Study\2022 series_sub_EKPC-LGEE.sub]. Line 283: END
*** Closed [C:\Users\03419\Desktop\2022 Gas Study\2022 series_sub_EKPC-LGEE.sub] - 283 records (Lev=1)
Total defined 8 subsystems
*** Study Data File (sub file) Input Summary
LFCaseName: 2032S_gas_alt#3a_212mw.raw
******* Study Data Input warnings Summary ****
Severity Level: 1-info; 2-error; 3-potentially critical; 4-critical error
Warning- 1009 Total- 23 Level- ! 2 Bus number not found
Warning- 1100 Total- 2 Level- 0 Number of completed input files. See warnings details for # of lines read in
Warning- 1417 Total- 1 Level- 1 Initial switched shunt value cannot be reached by following block order (possibly has adjustment mode 1)
Warning- 1436 Total- 3 Level- 1 FACTS Device has mode online but no capability or it is unsupported mode or it has a data error.
Warning- 1826 Total- 2 Level- ! 2 Oscilating switched shunt could not reach its voltage target. Consider changing target range or locking.
Warning- 1830 Total- 1 Level- 1 PAR table used for LTC. Transformer impedance will not be adjusted with Tap ratio adjustments
Warning- 1850 Total- 2 Level- 1 PAR Max angle is too big. Set to Max
Warning- 1851 Total- 2 Level- 1 PAR Min angle is too small. Set to Min
Warning- 1863 Total- 14 Level- 1 TAP Desired voltage range is too small comparing to step. Expanded
Warning- 1867 Total- 119 Level- 1 Transformer is radial. Disabling tap adjustments
Warning- 1878 Total- 88 Level- 0 Transformer remote control bus is connected to its terminal via low impedance line - controlling terminal instead
Warning- 1938 Total- 1 Level- 1 Reg bus is not a generator for discrete shunt controlling reactive power output of the plant at remote bus-fixed
Warning- 1945 Total- 4 Level- 1 Reg plant Q range too small for discrete shunt controlling reactive power output of the plant at remote bus-fixed
Warning- 3168 Total- 1 Level- ! 2 END statement may cause portions of the file to be skipped
Warning- 4040 Total- 8 Level- 1 Subsystem has total zero participation factor
Warning- 5702 Total- 8 Level- 1 No participating buses can be scaled. Using uniform distr
Warning- 6155 Total- 2 Level- 1 Suspicious PAR has R=0 and small X=0.00000. Increased X to improve flat start
Warning- 6159 Total- 9 Level- 1 Branch has high suspicious R/X ratio - make R smaller and X bigger to improve case convergence
Warning- 6160 Total- 11 Level- 1 Transformer has high suspicious R/X ratio - make R smaller and X bigger to improve case convergence
================== Total 301 warnings
*** Opened [C:\Users\03419\Desktop\2022 Gas Study\Option 3A N-1-1 con file.con]-(Lev=1). Current directory - [C:\Users\03419\Desktop\2022 Gas Study\temp]
WarnID-3083-1-205 Duplicate Contingency Names are defined. Modifying name of duplicate - adding _DupX to name to make unique. Duplicate name was changed to EXT_324271 4LEBANON 138 325121 4LOGAN TP 138 1 _SRT-A_Dup1
File [C:\Users\03419\Desktop\2022 Gas Study\Option 3A N-1-1 con file.con]. Line 200: END
WarnID-3168-1-206 END statement may cause portions of the file to be skipped
File [C:\Users\03419\Desktop\2022 Gas Study\Option 3A N-1-1 con file.con]. Line 285: END
*** Closed [C:\Users\03419\Desktop\2022 Gas Study\Option 3A N-1-1 con file.con] - 285 records (Lev=1)
Added 0 single shunt contingencies
37 contingencies, 80 total events, 0 redispatch events
*** Opened [C:\Users\03419\Desktop\2022 Gas Study\Option 3A N-1-1 con file.con]-(Lev=1). Current directory - [C:\Users\03419\Desktop\2022 Gas Study\temp]
WarnID-3168-2-207 END statement may cause portions of the file to be skipped
File [C:\Users\03419\Desktop\2022 Gas Study\Option 3A N-1-1 con file.con]. Line 285: END
*** Closed [C:\Users\03419\Desktop\2022 Gas Study\Option 3A N-1-1 con file.con] - 285 records (Lev=1)
Added 0 single shunt contingencies
Total defined 37 contingencies. Cont.Events 80. Redispatch events 0
Total defined 37 outages. Events 80, Redispatch events 0
Selected All 37 outages
*** Contingency Input warnings Summary ***
Severity Level: 1-info; 2-error; 3-potentially critical; 4-critical error
Warning- 1100 Total- 2 Level- 0 Number of completed input files. See warnings details for # of lines read in
Warning- 3083 Total- 1 Level- ! 2 Duplicate Contingency Names are defined. Modifying name of duplicate - adding _DupX where X is number of duplicate instances at this point.
Warning- 3168 Total- 2 Level- ! 2 END statement may cause portions of the file to be skipped
================== Total 5 warnings
Applying ACCont Must-Run Contingency Names
*** Opened [C:\Users\03419\Desktop\2022 Gas Study\2022 series_mon_EKPC-LGEE.mon]-(Lev=1). Current directory - [C:\Users\03419\Desktop\2022 Gas Study\temp]
WarnID-3168-1-208 END statement may cause portions of the file to be skipped
File [C:\Users\03419\Desktop\2022 Gas Study\2022 series_mon_EKPC-LGEE.mon]. Line 17: END
*** Closed [C:\Users\03419\Desktop\2022 Gas Study\2022 series_mon_EKPC-LGEE.mon] - 17 records (Lev=1)
Total defined: 1977 monit branches; 0 flowgates; 1580 Monit voltage buses
LFCaseName: 2032S_gas_alt#3a_212mw.raw
*** Mon Data File Input warnings Summary
Severity Level: 1-info; 2-error; 3-potentially critical; 4-critical error
Warning- 1100 Total- 1 Level- 0 Number of completed input files. See warnings details for # of lines read in
Warning- 3168 Total- 1 Level- ! 2 END statement may cause portions of the file to be skipped
================== Total 2 warnings
Select function(L2): [ 0]
Select main menu function(L1): [ opt] = Selected Function 10 - Options - TARA analysis options
Select data category:(L2): [ cont] = Selected Function 1 - CONTING - Contingency analysis option
**** Current **** Contingency analysis options:
1: monBranRatingBase 1 // Base case rating (1-A;2-B;3-C;4-D)
2: monBranRatingCont 2 // Contingency rating (1-A;2-B;3-C;4-D)
3: monBranRatingMultBase 100.00 // Base case rating multipliers
4: monBranRatingMultCont 100.00 // Contingency rating multipliers
5: contChanCutOffMW 5.0 // MW cutoff to ignore constraints if cont.flow doesn't changes from the base case more than
6: contChanCutOffPercent 2.0 // Rating %% cutoff to ignore if cont.flow changes from the base case is less than
7: PAR_AdjEnabledContAnal 1 // Phase shifter model for the base case (0-fixed angle;1-control flow), always fixed in contingency
8: adjustRatingMVA 0 // Adjust branch MW rating based on MVAR flow (DC analysis)
9: limitTypeLine 0 // Use AMP (=0) or MVA (1) limit to check lines violation in AC mode
10: limitTypeTran 1 // Use AMP (=0) or MVA (1) limit to check transformer violation in AC mode
11: voltMinChange 0.0050 // Voltage change cutoff in PU to ignore voltage violations with change from the base case is smaller
12: numContMaxAlloc 15000 // Max number of contingencies
13: numEventsAlloc 35000 // Max number of contingency events
14: numDispEventAlloc 60000 // Max number of generation redispatch events
15: numLFgatesMaxAlloc 10000 // Max number of flowgates
16: maxFgateBranches 100 // Max number of branches (events) per flowgate
17: mulSecPrintMode 0 // Multi-section line modeling (0-ignore;1-honor)
18: smartCutOff 0 // Use Smart cutoff based on Max conting impact using base case and conting rating difference (0-no;1-yes)
19: maxExcludesAlloc 10000 // Max number of exclude records
20: showConAnalLFLog 0 // Show LF convergence during ACCONT
21: MAXOUTAGES 15000 // Maximum number of outages
22: maxORAFlowResults 2000000 // Maximum number of ORA or N-1-1 results to report
23: ACCONTRepeatSolution 0 // If first AC solution failed, repeat with alternative Flat/Hot start(0-no,1-yes),2-limit to the best iteration
24: showNotMappedContEvents 1 // When generating contingency file, show not mapped event(0-no,1-yes)
25: monBranRatingEnAdd1 0 // Enable first additional rating reporting (0-no,1-yes)
26: monBranRatingEnAdd2 0 // Enable second additional rating reporting (0-no,1-yes)
27: monBranRatingAdd1 3 // Additional Rating 1 (1-A;2-B;3-C;4-D)
28: monBranRatingAdd2 3 // Additional Rating 2 (1-A;2-B;3-C;4-D)
29: monBranRatingMultAdd1 100.00 // Additional Rating 1 multiplier
30: monBranRatingMultAdd2 100.00 // Additional Rating 2 multiplier
31: LoadingCutOff 0.00 // Loading cutoff in percent for displaying cont analysis flow results
32: showAllHighPreSCD 0 // Show SCD result if pre-SCD above cutoff but post-SCD below
33: N11MODE 1 // Run in N-1+Application Mode
34: multiCoreN1 0 // Run in N-1 ACCont in multi-core mode? [0-No, 1-Yes]
35: numLowestLoading 5 // Max number of lowest loading results to report
36: VoltLimAdder 0.00000 // Add this to voltage limit to expand or limit hi/low voltage viol results
37: StudyFiles 1 // Show Names of Input Files on all reports
38: MonConMode 1 // Select Mon/Con mode (1:Regular, 2:Flowgate, 3:Voltgate, 4:Flowgate & Voltgate
39: MaxMonConMode 100000 // Maximum Number of mon/con mode entries
40: keepDuplicates 1 // Keep contingency even if exact duplicate? [0=no, 1=yes]
41: correctiveSwitchingMode 0 // Run in corrective switching mode? [0=no, 1=yes]
42: lodfCutoff 0.01000 // Cutoff for LODF report (absolute value)
43: lodfImpCutoff 1.00 // MW cutoff for LODF Impact report (lodf*(event rating))
44: maxFgEventTotal 30000 // Max number of all branches and events for all flowgatesflowgate
45: maxEvPerCont 60 // Max number of events (events) per contingency
46: maxSPSLogic 10000 // Max number of SPS logic elements
47: maxInjGroups 500 // Max number of SPS AUX Injections Groups
48: maxSPSInterfaces 1000 // Max number of SPS AUX Interfaces
49: co_mode 0 // Cascading mode, 0=no, 1=yes
50: co_branchoutage 1 // Trip Overloaded Branches in Cascading Outage, 0=no, 1=yes
51: co_genoutage 1 // Trip Generators in Cascading Outage, 0=no, 1=yes
52: co_genterminalbus 0 // Trip Generators with low voltage violation at generator terminal bus, 0=no, 1=yes
53: co_loadoutage 1 // Trip Loads in Cascading Outage, 0=no, 1=yes
54: co_maxlevel 10 // Maximum cascading outage test level
55: saveCOCases 0 // Save a case for each cascading step case
56: COSaveDirectory [] // Folder to save each cascading outage case
57: kVLayer12_Volt 100.0 // Voltage between Layer 1 and Layer 2
58: kVLayer23_Volt 230.0 // Voltage between Layer 2 and Layer 3
59: kVLayer34_Volt 345.0 // Voltage between Layer 3 and Layer 4
60: kVLayer45_Volt 500.0 // Voltage between Layer 4 and Layer 5
61: kVLayer1_LDCutoff 115.0 // Layer 1 RelayLoadability Percent
62: kVLayer2_LDCutoff 115.0 // Layer 2 RelayLoadability Percent
63: kVLayer3_LDCutoff 115.0 // Layer 3 RelayLoadability Percent
64: kVLayer4_LDCutoff 115.0 // Layer 4 RelayLoadability Percent
65: kVLayer5_LDCutoff 115.0 // Layer 5 RelayLoadability Percent
66: zeroRatingCutoff 0.000100 // If rating is below this, set rating to 9999
67: saveN11Cases 0 // Save a case for each N-1-1 first-level case
68: N11SaveDirectory [] // Folder to save each N-1-1 first-level case
69: acVerifyFgate 0 // Enable flowgate AC verification (0-No;1-Yes)
70: useContingencyComments 0 // Use Comments in contingency file in contingency reporting
71: ignoreEnd2Exit 0 // Ignore END statement to exit reading sub mon con exc files (0-No, 1-Yes)
72: nearSyskVLayer1 5 // Subsystem proximity screen 1st kV Layer
73: nearSyskVLayer2 5 // Subsystem proximity screen 2nd kV Layer
74: nearSyskVLayer3 5 // Subsystem proximity screen 3rd kV Layer
75: nearSyskVLayer4 5 // Subsystem proximity screen 4rd kV Layer
76: nearSyskVLayer5 5 // Subsystem proximity screen 5th kV Layer
77: nearSyskVLayer12_Volt 100.0 // Subsystem proximity screen Voltage between Layer 1 and Layer 2
78: nearSyskVLayer23_Volt 230.0 // Subsystem proximity screen Voltage between Layer 2 and Layer 3
79: nearSyskVLayer34_Volt 345.0 // Subsystem proximity screen Voltage between Layer 3 and Layer 4
80: nearSyskVLayer45_Volt 500.0 // Subsystem proximity screen Voltage between Layer 4 and Layer 5
81: nearSysScrnMod 0 // Subsystem Screening for nearby contingencies (1st and 2nd)
82: nearSyskVCutoff 0.00 // Subsystem proximity Specify kV Cutoff
83: nearSysApplykVCutoffOption 0 // Subsystem proximity [0-one side only, 1-both sides]
84: nearByLayerSubSysName [Undefined] // - Subsystem Name for proximity contingency layer screen
Specify option name (or number) and value : [ StudyFiles][ 0]
Specify option name (or number) and value : [ 0]
**** New **** Contingency analysis options:
1: monBranRatingBase 1 // Base case rating (1-A;2-B;3-C;4-D)
2: monBranRatingCont 2 // Contingency rating (1-A;2-B;3-C;4-D)
3: monBranRatingMultBase 100.00 // Base case rating multipliers
4: monBranRatingMultCont 100.00 // Contingency rating multipliers
5: contChanCutOffMW 5.0 // MW cutoff to ignore constraints if cont.flow doesn't changes from the base case more than
6: contChanCutOffPercent 2.0 // Rating %% cutoff to ignore if cont.flow changes from the base case is less than
7: PAR_AdjEnabledContAnal 1 // Phase shifter model for the base case (0-fixed angle;1-control flow), always fixed in contingency
8: adjustRatingMVA 0 // Adjust branch MW rating based on MVAR flow (DC analysis)
9: limitTypeLine 0 // Use AMP (=0) or MVA (1) limit to check lines violation in AC mode
10: limitTypeTran 1 // Use AMP (=0) or MVA (1) limit to check transformer violation in AC mode
11: voltMinChange 0.0050 // Voltage change cutoff in PU to ignore voltage violations with change from the base case is smaller
12: numContMaxAlloc 15000 // Max number of contingencies
13: numEventsAlloc 35000 // Max number of contingency events
14: numDispEventAlloc 60000 // Max number of generation redispatch events
15: numLFgatesMaxAlloc 10000 // Max number of flowgates
16: maxFgateBranches 100 // Max number of branches (events) per flowgate
17: mulSecPrintMode 0 // Multi-section line modeling (0-ignore;1-honor)
18: smartCutOff 0 // Use Smart cutoff based on Max conting impact using base case and conting rating difference (0-no;1-yes)
19: maxExcludesAlloc 10000 // Max number of exclude records
20: showConAnalLFLog 0 // Show LF convergence during ACCONT
21: MAXOUTAGES 15000 // Maximum number of outages
22: maxORAFlowResults 2000000 // Maximum number of ORA or N-1-1 results to report
23: ACCONTRepeatSolution 0 // If first AC solution failed, repeat with alternative Flat/Hot start(0-no,1-yes),2-limit to the best iteration
24: showNotMappedContEvents 1 // When generating contingency file, show not mapped event(0-no,1-yes)
25: monBranRatingEnAdd1 0 // Enable first additional rating reporting (0-no,1-yes)
26: monBranRatingEnAdd2 0 // Enable second additional rating reporting (0-no,1-yes)
27: monBranRatingAdd1 3 // Additional Rating 1 (1-A;2-B;3-C;4-D)
28: monBranRatingAdd2 3 // Additional Rating 2 (1-A;2-B;3-C;4-D)
29: monBranRatingMultAdd1 100.00 // Additional Rating 1 multiplier
30: monBranRatingMultAdd2 100.00 // Additional Rating 2 multiplier
31: LoadingCutOff 0.00 // Loading cutoff in percent for displaying cont analysis flow results
32: showAllHighPreSCD 0 // Show SCD result if pre-SCD above cutoff but post-SCD below
33: N11MODE 1 // Run in N-1+Application Mode
34: multiCoreN1 0 // Run in N-1 ACCont in multi-core mode? [0-No, 1-Yes]
35: numLowestLoading 5 // Max number of lowest loading results to report
36: VoltLimAdder 0.00000 // Add this to voltage limit to expand or limit hi/low voltage viol results
37: StudyFiles 0 // Show Names of Input Files on all reports
38: MonConMode 1 // Select Mon/Con mode (1:Regular, 2:Flowgate, 3:Voltgate, 4:Flowgate & Voltgate
39: MaxMonConMode 100000 // Maximum Number of mon/con mode entries
40: keepDuplicates 1 // Keep contingency even if exact duplicate? [0=no, 1=yes]
41: correctiveSwitchingMode 0 // Run in corrective switching mode? [0=no, 1=yes]
42: lodfCutoff 0.01000 // Cutoff for LODF report (absolute value)
43: lodfImpCutoff 1.00 // MW cutoff for LODF Impact report (lodf*(event rating))
44: maxFgEventTotal 30000 // Max number of all branches and events for all flowgatesflowgate
45: maxEvPerCont 60 // Max number of events (events) per contingency
46: maxSPSLogic 10000 // Max number of SPS logic elements
47: maxInjGroups 500 // Max number of SPS AUX Injections Groups
48: maxSPSInterfaces 1000 // Max number of SPS AUX Interfaces
49: co_mode 0 // Cascading mode, 0=no, 1=yes
50: co_branchoutage 1 // Trip Overloaded Branches in Cascading Outage, 0=no, 1=yes
51: co_genoutage 1 // Trip Generators in Cascading Outage, 0=no, 1=yes
52: co_genterminalbus 0 // Trip Generators with low voltage violation at generator terminal bus, 0=no, 1=yes
53: co_loadoutage 1 // Trip Loads in Cascading Outage, 0=no, 1=yes
54: co_maxlevel 10 // Maximum cascading outage test level
55: saveCOCases 0 // Save a case for each cascading step case
56: COSaveDirectory [] // Folder to save each cascading outage case
57: kVLayer12_Volt 100.0 // Voltage between Layer 1 and Layer 2
58: kVLayer23_Volt 230.0 // Voltage between Layer 2 and Layer 3
59: kVLayer34_Volt 345.0 // Voltage between Layer 3 and Layer 4
60: kVLayer45_Volt 500.0 // Voltage between Layer 4 and Layer 5
61: kVLayer1_LDCutoff 115.0 // Layer 1 RelayLoadability Percent
62: kVLayer2_LDCutoff 115.0 // Layer 2 RelayLoadability Percent
63: kVLayer3_LDCutoff 115.0 // Layer 3 RelayLoadability Percent
64: kVLayer4_LDCutoff 115.0 // Layer 4 RelayLoadability Percent
65: kVLayer5_LDCutoff 115.0 // Layer 5 RelayLoadability Percent
66: zeroRatingCutoff 0.000100 // If rating is below this, set rating to 9999
67: saveN11Cases 0 // Save a case for each N-1-1 first-level case
68: N11SaveDirectory [] // Folder to save each N-1-1 first-level case
69: acVerifyFgate 0 // Enable flowgate AC verification (0-No;1-Yes)
70: useContingencyComments 0 // Use Comments in contingency file in contingency reporting
71: ignoreEnd2Exit 0 // Ignore END statement to exit reading sub mon con exc files (0-No, 1-Yes)
72: nearSyskVLayer1 5 // Subsystem proximity screen 1st kV Layer
73: nearSyskVLayer2 5 // Subsystem proximity screen 2nd kV Layer
74: nearSyskVLayer3 5 // Subsystem proximity screen 3rd kV Layer
75: nearSyskVLayer4 5 // Subsystem proximity screen 4rd kV Layer
76: nearSyskVLayer5 5 // Subsystem proximity screen 5th kV Layer
77: nearSyskVLayer12_Volt 100.0 // Subsystem proximity screen Voltage between Layer 1 and Layer 2
78: nearSyskVLayer23_Volt 230.0 // Subsystem proximity screen Voltage between Layer 2 and Layer 3
79: nearSyskVLayer34_Volt 345.0 // Subsystem proximity screen Voltage between Layer 3 and Layer 4
80: nearSyskVLayer45_Volt 500.0 // Subsystem proximity screen Voltage between Layer 4 and Layer 5
81: nearSysScrnMod 0 // Subsystem Screening for nearby contingencies (1st and 2nd)
82: nearSyskVCutoff 0.00 // Subsystem proximity Specify kV Cutoff
83: nearSysApplykVCutoffOption 0 // Subsystem proximity [0-one side only, 1-both sides]
84: nearByLayerSubSysName [Undefined] // - Subsystem Name for proximity contingency layer screen
Select data category:(L2): [ 0]
Select main menu function(L1): [ 0]
Select main menu function(L1): [ lfreview] = Selected Function 2 - LFREVIEW - Report LF case data(sub-menu)
Select LF data category: (L2): [ %save][ "C:\Users\03419\Desktop\2022 Gas Study\temp\temp_report3.txt"] --> Output to C:\Users\03419\Desktop\2022 Gas Study\temp\temp_report3.txt
Select LF data category: (L2): [ %csv] Using CSV format
[ subsys] = Selected Function 43 - SUBSYS - Report defined subsystem
Updating Subsystem Participation Factors
WarnID-5702-1-208 No participating buses can be scaled for EKPC_EXT ,. Using uniform distr - Found 1 online buses
WarnID-5702-2-209 No participating buses can be scaled for OVEC ,. Using uniform distr - Found 4 online buses
WarnID-5702-3-210 No participating buses can be scaled for DPL ,. Using uniform distr - Found 12 online buses
*** Created [C:\Users\03419\Desktop\2022 Gas Study\temp\temp_report3.txt] Current directory - [C:\Users\03419\Desktop\2022 Gas Study\temp]
Select LF data category: (L2): [ 0]
Select main menu function(L1): [ lfreview] = Selected Function 2 - LFREVIEW - Report LF case data(sub-menu)
Select LF data category: (L2): [ %save][ "C:\Users\03419\Desktop\2022 Gas Study\temp\temp_report1.txt"] --> Output to C:\Users\03419\Desktop\2022 Gas Study\temp\temp_report1.txt
Select LF data category: (L2): [ %csv] Using CSV format
[ larea] = Selected Function 4 - LAREA - Area List
*** Created [C:\Users\03419\Desktop\2022 Gas Study\temp\temp_report1.txt] Current directory - [C:\Users\03419\Desktop\2022 Gas Study\temp]
Select LF data category: (L2): [ 0]
Select main menu function(L1): [ lfreview] = Selected Function 2 - LFREVIEW - Report LF case data(sub-menu)
Select LF data category: (L2): [ %save][ "C:\Users\03419\Desktop\2022 Gas Study\temp\temp_report5.txt"] --> Output to C:\Users\03419\Desktop\2022 Gas Study\temp\temp_report5.txt
Select LF data category: (L2): [ %csv] Using CSV format
[ tzone] = Selected Function 5 - TZONE - Zone summary
Do you need header(1-yes, 0- no : [ 1]
*** Created [C:\Users\03419\Desktop\2022 Gas Study\temp\temp_report5.txt] Current directory - [C:\Users\03419\Desktop\2022 Gas Study\temp]
Select LF data category: (L2): [ 0]
Select main menu function(L1): [ opt] = Selected Function 10 - Options - TARA analysis options
Select data category:(L2): [ cont] = Selected Function 1 - CONTING - Contingency analysis option
**** Current **** Contingency analysis options:
1: monBranRatingBase 1 // Base case rating (1-A;2-B;3-C;4-D)
2: monBranRatingCont 2 // Contingency rating (1-A;2-B;3-C;4-D)
3: monBranRatingMultBase 100.00 // Base case rating multipliers
4: monBranRatingMultCont 100.00 // Contingency rating multipliers
5: contChanCutOffMW 5.0 // MW cutoff to ignore constraints if cont.flow doesn't changes from the base case more than
6: contChanCutOffPercent 2.0 // Rating %% cutoff to ignore if cont.flow changes from the base case is less than
7: PAR_AdjEnabledContAnal 1 // Phase shifter model for the base case (0-fixed angle;1-control flow), always fixed in contingency
8: adjustRatingMVA 0 // Adjust branch MW rating based on MVAR flow (DC analysis)
9: limitTypeLine 0 // Use AMP (=0) or MVA (1) limit to check lines violation in AC mode
10: limitTypeTran 1 // Use AMP (=0) or MVA (1) limit to check transformer violation in AC mode
11: voltMinChange 0.0050 // Voltage change cutoff in PU to ignore voltage violations with change from the base case is smaller
12: numContMaxAlloc 15000 // Max number of contingencies
13: numEventsAlloc 35000 // Max number of contingency events
14: numDispEventAlloc 60000 // Max number of generation redispatch events
15: numLFgatesMaxAlloc 10000 // Max number of flowgates
16: maxFgateBranches 100 // Max number of branches (events) per flowgate
17: mulSecPrintMode 0 // Multi-section line modeling (0-ignore;1-honor)
18: smartCutOff 0 // Use Smart cutoff based on Max conting impact using base case and conting rating difference (0-no;1-yes)
19: maxExcludesAlloc 10000 // Max number of exclude records
20: showConAnalLFLog 0 // Show LF convergence during ACCONT
21: MAXOUTAGES 15000 // Maximum number of outages
22: maxORAFlowResults 2000000 // Maximum number of ORA or N-1-1 results to report
23: ACCONTRepeatSolution 0 // If first AC solution failed, repeat with alternative Flat/Hot start(0-no,1-yes),2-limit to the best iteration
24: showNotMappedContEvents 1 // When generating contingency file, show not mapped event(0-no,1-yes)
25: monBranRatingEnAdd1 0 // Enable first additional rating reporting (0-no,1-yes)
26: monBranRatingEnAdd2 0 // Enable second additional rating reporting (0-no,1-yes)
27: monBranRatingAdd1 3 // Additional Rating 1 (1-A;2-B;3-C;4-D)
28: monBranRatingAdd2 3 // Additional Rating 2 (1-A;2-B;3-C;4-D)
29: monBranRatingMultAdd1 100.00 // Additional Rating 1 multiplier
30: monBranRatingMultAdd2 100.00 // Additional Rating 2 multiplier
31: LoadingCutOff 0.00 // Loading cutoff in percent for displaying cont analysis flow results
32: showAllHighPreSCD 0 // Show SCD result if pre-SCD above cutoff but post-SCD below
33: N11MODE 1 // Run in N-1+Application Mode
34: multiCoreN1 0 // Run in N-1 ACCont in multi-core mode? [0-No, 1-Yes]
35: numLowestLoading 5 // Max number of lowest loading results to report
36: VoltLimAdder 0.00000 // Add this to voltage limit to expand or limit hi/low voltage viol results
37: StudyFiles 0 // Show Names of Input Files on all reports
38: MonConMode 1 // Select Mon/Con mode (1:Regular, 2:Flowgate, 3:Voltgate, 4:Flowgate & Voltgate
39: MaxMonConMode 100000 // Maximum Number of mon/con mode entries
40: keepDuplicates 1 // Keep contingency even if exact duplicate? [0=no, 1=yes]
41: correctiveSwitchingMode 0 // Run in corrective switching mode? [0=no, 1=yes]
42: lodfCutoff 0.01000 // Cutoff for LODF report (absolute value)
43: lodfImpCutoff 1.00 // MW cutoff for LODF Impact report (lodf*(event rating))
44: maxFgEventTotal 30000 // Max number of all branches and events for all flowgatesflowgate
45: maxEvPerCont 60 // Max number of events (events) per contingency
46: maxSPSLogic 10000 // Max number of SPS logic elements
47: maxInjGroups 500 // Max number of SPS AUX Injections Groups
48: maxSPSInterfaces 1000 // Max number of SPS AUX Interfaces
49: co_mode 0 // Cascading mode, 0=no, 1=yes
50: co_branchoutage 1 // Trip Overloaded Branches in Cascading Outage, 0=no, 1=yes
51: co_genoutage 1 // Trip Generators in Cascading Outage, 0=no, 1=yes
52: co_genterminalbus 0 // Trip Generators with low voltage violation at generator terminal bus, 0=no, 1=yes
53: co_loadoutage 1 // Trip Loads in Cascading Outage, 0=no, 1=yes
54: co_maxlevel 10 // Maximum cascading outage test level
55: saveCOCases 0 // Save a case for each cascading step case
56: COSaveDirectory [] // Folder to save each cascading outage case
57: kVLayer12_Volt 100.0 // Voltage between Layer 1 and Layer 2
58: kVLayer23_Volt 230.0 // Voltage between Layer 2 and Layer 3
59: kVLayer34_Volt 345.0 // Voltage between Layer 3 and Layer 4
60: kVLayer45_Volt 500.0 // Voltage between Layer 4 and Layer 5
61: kVLayer1_LDCutoff 115.0 // Layer 1 RelayLoadability Percent
62: kVLayer2_LDCutoff 115.0 // Layer 2 RelayLoadability Percent
63: kVLayer3_LDCutoff 115.0 // Layer 3 RelayLoadability Percent
64: kVLayer4_LDCutoff 115.0 // Layer 4 RelayLoadability Percent
65: kVLayer5_LDCutoff 115.0 // Layer 5 RelayLoadability Percent
66: zeroRatingCutoff 0.000100 // If rating is below this, set rating to 9999
67: saveN11Cases 0 // Save a case for each N-1-1 first-level case
68: N11SaveDirectory [] // Folder to save each N-1-1 first-level case
69: acVerifyFgate 0 // Enable flowgate AC verification (0-No;1-Yes)
70: useContingencyComments 0 // Use Comments in contingency file in contingency reporting
71: ignoreEnd2Exit 0 // Ignore END statement to exit reading sub mon con exc files (0-No, 1-Yes)
72: nearSyskVLayer1 5 // Subsystem proximity screen 1st kV Layer
73: nearSyskVLayer2 5 // Subsystem proximity screen 2nd kV Layer
74: nearSyskVLayer3 5 // Subsystem proximity screen 3rd kV Layer
75: nearSyskVLayer4 5 // Subsystem proximity screen 4rd kV Layer
76: nearSyskVLayer5 5 // Subsystem proximity screen 5th kV Layer
77: nearSyskVLayer12_Volt 100.0 // Subsystem proximity screen Voltage between Layer 1 and Layer 2
78: nearSyskVLayer23_Volt 230.0 // Subsystem proximity screen Voltage between Layer 2 and Layer 3
79: nearSyskVLayer34_Volt 345.0 // Subsystem proximity screen Voltage between Layer 3 and Layer 4
80: nearSyskVLayer45_Volt 500.0 // Subsystem proximity screen Voltage between Layer 4 and Layer 5
81: nearSysScrnMod 0 // Subsystem Screening for nearby contingencies (1st and 2nd)
82: nearSyskVCutoff 0.00 // Subsystem proximity Specify kV Cutoff
83: nearSysApplykVCutoffOption 0 // Subsystem proximity [0-one side only, 1-both sides]
84: nearByLayerSubSysName [Undefined] // - Subsystem Name for proximity contingency layer screen
Specify option name (or number) and value : [ StudyFiles][ 1]
Specify option name (or number) and value : [ 0]
**** New **** Contingency analysis options:
1: monBranRatingBase 1 // Base case rating (1-A;2-B;3-C;4-D)
2: monBranRatingCont 2 // Contingency rating (1-A;2-B;3-C;4-D)
3: monBranRatingMultBase 100.00 // Base case rating multipliers
4: monBranRatingMultCont 100.00 // Contingency rating multipliers
5: contChanCutOffMW 5.0 // MW cutoff to ignore constraints if cont.flow doesn't changes from the base case more than
6: contChanCutOffPercent 2.0 // Rating %% cutoff to ignore if cont.flow changes from the base case is less than
7: PAR_AdjEnabledContAnal 1 // Phase shifter model for the base case (0-fixed angle;1-control flow), always fixed in contingency
8: adjustRatingMVA 0 // Adjust branch MW rating based on MVAR flow (DC analysis)
9: limitTypeLine 0 // Use AMP (=0) or MVA (1) limit to check lines violation in AC mode
10: limitTypeTran 1 // Use AMP (=0) or MVA (1) limit to check transformer violation in AC mode
11: voltMinChange 0.0050 // Voltage change cutoff in PU to ignore voltage violations with change from the base case is smaller
12: numContMaxAlloc 15000 // Max number of contingencies
13: numEventsAlloc 35000 // Max number of contingency events
14: numDispEventAlloc 60000 // Max number of generation redispatch events
15: numLFgatesMaxAlloc 10000 // Max number of flowgates
16: maxFgateBranches 100 // Max number of branches (events) per flowgate
17: mulSecPrintMode 0 // Multi-section line modeling (0-ignore;1-honor)
18: smartCutOff 0 // Use Smart cutoff based on Max conting impact using base case and conting rating difference (0-no;1-yes)
19: maxExcludesAlloc 10000 // Max number of exclude records
20: showConAnalLFLog 0 // Show LF convergence during ACCONT
21: MAXOUTAGES 15000 // Maximum number of outages
22: maxORAFlowResults 2000000 // Maximum number of ORA or N-1-1 results to report
23: ACCONTRepeatSolution 0 // If first AC solution failed, repeat with alternative Flat/Hot start(0-no,1-yes),2-limit to the best iteration
24: showNotMappedContEvents 1 // When generating contingency file, show not mapped event(0-no,1-yes)
25: monBranRatingEnAdd1 0 // Enable first additional rating reporting (0-no,1-yes)
26: monBranRatingEnAdd2 0 // Enable second additional rating reporting (0-no,1-yes)
27: monBranRatingAdd1 3 // Additional Rating 1 (1-A;2-B;3-C;4-D)
28: monBranRatingAdd2 3 // Additional Rating 2 (1-A;2-B;3-C;4-D)
29: monBranRatingMultAdd1 100.00 // Additional Rating 1 multiplier
30: monBranRatingMultAdd2 100.00 // Additional Rating 2 multiplier
31: LoadingCutOff 0.00 // Loading cutoff in percent for displaying cont analysis flow results
32: showAllHighPreSCD 0 // Show SCD result if pre-SCD above cutoff but post-SCD below
33: N11MODE 1 // Run in N-1+Application Mode
34: multiCoreN1 0 // Run in N-1 ACCont in multi-core mode? [0-No, 1-Yes]
35: numLowestLoading 5 // Max number of lowest loading results to report
36: VoltLimAdder 0.00000 // Add this to voltage limit to expand or limit hi/low voltage viol results
37: StudyFiles 1 // Show Names of Input Files on all reports
38: MonConMode 1 // Select Mon/Con mode (1:Regular, 2:Flowgate, 3:Voltgate, 4:Flowgate & Voltgate
39: MaxMonConMode 100000 // Maximum Number of mon/con mode entries
40: keepDuplicates 1 // Keep contingency even if exact duplicate? [0=no, 1=yes]
41: correctiveSwitchingMode 0 // Run in corrective switching mode? [0=no, 1=yes]
42: lodfCutoff 0.01000 // Cutoff for LODF report (absolute value)
43: lodfImpCutoff 1.00 // MW cutoff for LODF Impact report (lodf*(event rating))
44: maxFgEventTotal 30000 // Max number of all branches and events for all flowgatesflowgate
45: maxEvPerCont 60 // Max number of events (events) per contingency
46: maxSPSLogic 10000 // Max number of SPS logic elements
47: maxInjGroups 500 // Max number of SPS AUX Injections Groups
48: maxSPSInterfaces 1000 // Max number of SPS AUX Interfaces
49: co_mode 0 // Cascading mode, 0=no, 1=yes
50: co_branchoutage 1 // Trip Overloaded Branches in Cascading Outage, 0=no, 1=yes
51: co_genoutage 1 // Trip Generators in Cascading Outage, 0=no, 1=yes
52: co_genterminalbus 0 // Trip Generators with low voltage violation at generator terminal bus, 0=no, 1=yes
53: co_loadoutage 1 // Trip Loads in Cascading Outage, 0=no, 1=yes
54: co_maxlevel 10 // Maximum cascading outage test level
55: saveCOCases 0 // Save a case for each cascading step case
56: COSaveDirectory [] // Folder to save each cascading outage case
57: kVLayer12_Volt 100.0 // Voltage between Layer 1 and Layer 2
58: kVLayer23_Volt 230.0 // Voltage between Layer 2 and Layer 3
59: kVLayer34_Volt 345.0 // Voltage between Layer 3 and Layer 4
60: kVLayer45_Volt 500.0 // Voltage between Layer 4 and Layer 5
61: kVLayer1_LDCutoff 115.0 // Layer 1 RelayLoadability Percent
62: kVLayer2_LDCutoff 115.0 // Layer 2 RelayLoadability Percent
63: kVLayer3_LDCutoff 115.0 // Layer 3 RelayLoadability Percent
64: kVLayer4_LDCutoff 115.0 // Layer 4 RelayLoadability Percent
65: kVLayer5_LDCutoff 115.0 // Layer 5 RelayLoadability Percent
66: zeroRatingCutoff 0.000100 // If rating is below this, set rating to 9999
67: saveN11Cases 0 // Save a case for each N-1-1 first-level case
68: N11SaveDirectory [] // Folder to save each N-1-1 first-level case
69: acVerifyFgate 0 // Enable flowgate AC verification (0-No;1-Yes)
70: useContingencyComments 0 // Use Comments in contingency file in contingency reporting
71: ignoreEnd2Exit 0 // Ignore END statement to exit reading sub mon con exc files (0-No, 1-Yes)
72: nearSyskVLayer1 5 // Subsystem proximity screen 1st kV Layer
73: nearSyskVLayer2 5 // Subsystem proximity screen 2nd kV Layer
74: nearSyskVLayer3 5 // Subsystem proximity screen 3rd kV Layer
75: nearSyskVLayer4 5 // Subsystem proximity screen 4rd kV Layer
76: nearSyskVLayer5 5 // Subsystem proximity screen 5th kV Layer
77: nearSyskVLayer12_Volt 100.0 // Subsystem proximity screen Voltage between Layer 1 and Layer 2
78: nearSyskVLayer23_Volt 230.0 // Subsystem proximity screen Voltage between Layer 2 and Layer 3
79: nearSyskVLayer34_Volt 345.0 // Subsystem proximity screen Voltage between Layer 3 and Layer 4
80: nearSyskVLayer45_Volt 500.0 // Subsystem proximity screen Voltage between Layer 4 and Layer 5
81: nearSysScrnMod 0 // Subsystem Screening for nearby contingencies (1st and 2nd)
82: nearSyskVCutoff 0.00 // Subsystem proximity Specify kV Cutoff
83: nearSysApplykVCutoffOption 0 // Subsystem proximity [0-one side only, 1-both sides]
84: nearByLayerSubSysName [Undefined] // - Subsystem Name for proximity contingency layer screen
Select data category:(L2): [ 0]
Select main menu function(L1): [ 0]
Select main menu function(L1): [ lfreview] = Selected Function 2 - LFREVIEW - Report LF case data(sub-menu)
Select LF data category: (L2): [ %save][ "C:\Users\03419\Desktop\2022 Gas Study\temp\CaseSum.csv"] --> Output to C:\Users\03419\Desktop\2022 Gas Study\temp\CaseSum.csv
Select LF data category: (L2): [ %csv] Using CSV format
[ sum] = Selected Function 1 - SUM - LF case summary
*** Created [C:\Users\03419\Desktop\2022 Gas Study\temp\CaseSum.csv] Current directory - [C:\Users\03419\Desktop\2022 Gas Study\temp]
Select LF data category: (L2): [ 0]
Select main menu function(L1): [ 0]
Select main menu function(L1): [ opt] = Selected Function 10 - Options - TARA analysis options
Select data category:(L2): [ misc] = Selected Function 5 - MISC - Miscelaneous options
**** Current **** TARA Miscelaneous options
1: loadEscalationNYDeliv 0.159 // Load Escalation for NY deliverability
2: loadEscalationNYDeliv1 0.159 // Load Escalation for NY deliverability
3: needReportHeader 1 // Report headers (0-no, 1-report headers)
4: preApproveMethod 1 // Method for defining pre-approved outages (0-As read, 1-Date of first case, 2-User-defined date)
5: cutoffDatePreApproved [2008-01-01 00:00] // Cutoff date for auto-marking pre-approved (method 2 above)
6: logfile2 [0] // File name for second log file.
7: logAddWarn 1 // Add warnings to progress log file (0-no, 1-yes)
Specify option name (or number) and value : [ needReportHeader][ 0]
Specify option name (or number) and value : [ 0]
**** New **** TARA Miscelaneous options
1: loadEscalationNYDeliv 0.159 // Load Escalation for NY deliverability
2: loadEscalationNYDeliv1 0.159 // Load Escalation for NY deliverability
3: needReportHeader 0 // Report headers (0-no, 1-report headers)
4: preApproveMethod 1 // Method for defining pre-approved outages (0-As read, 1-Date of first case, 2-User-defined date)
5: cutoffDatePreApproved [2008-01-01 00:00] // Cutoff date for auto-marking pre-approved (method 2 above)
6: logfile2 [0] // File name for second log file.
7: logAddWarn 1 // Add warnings to progress log file (0-no, 1-yes)
Select data category:(L2): [ 0]
Select main menu function(L1): [ 0]
Select main menu function(L1): [ warn] = Selected Function 20 - Warnings - Input Warnings sub menu
Select function(L2): [ %save][ "C:\Users\03419\Desktop\2022 Gas Study\temp\Warn_Sum_Term.csv"] --> Output to C:\Users\03419\Desktop\2022 Gas Study\temp\Warn_Sum_Term.csv
Select function(L2): [ %csv] Using CSV format
[ term] = Selected Function 4 - Terminal - Severe/terminal errors list (Warnings Level 3 only)
*** Created [C:\Users\03419\Desktop\2022 Gas Study\temp\Warn_Sum_Term.csv] Current directory - [C:\Users\03419\Desktop\2022 Gas Study\temp]
Select function(L2): [ 0]
Select main menu function(L1): [ 0]
Select main menu function(L1): [ opt] = Selected Function 10 - Options - TARA analysis options
Select data category:(L2): [ misc] = Selected Function 5 - MISC - Miscelaneous options
**** Current **** TARA Miscelaneous options
1: loadEscalationNYDeliv 0.159 // Load Escalation for NY deliverability
2: loadEscalationNYDeliv1 0.159 // Load Escalation for NY deliverability
3: needReportHeader 0 // Report headers (0-no, 1-report headers)
4: preApproveMethod 1 // Method for defining pre-approved outages (0-As read, 1-Date of first case, 2-User-defined date)
5: cutoffDatePreApproved [2008-01-01 00:00] // Cutoff date for auto-marking pre-approved (method 2 above)
6: logfile2 [0] // File name for second log file.
7: logAddWarn 1 // Add warnings to progress log file (0-no, 1-yes)
Specify option name (or number) and value : [ needReportHeader][ 1]
Specify option name (or number) and value : [ 0]
**** New **** TARA Miscelaneous options
1: loadEscalationNYDeliv 0.159 // Load Escalation for NY deliverability
2: loadEscalationNYDeliv1 0.159 // Load Escalation for NY deliverability
3: needReportHeader 1 // Report headers (0-no, 1-report headers)
4: preApproveMethod 1 // Method for defining pre-approved outages (0-As read, 1-Date of first case, 2-User-defined date)
5: cutoffDatePreApproved [2008-01-01 00:00] // Cutoff date for auto-marking pre-approved (method 2 above)
6: logfile2 [0] // File name for second log file.
7: logAddWarn 1 // Add warnings to progress log file (0-no, 1-yes)
Select data category:(L2): [ 0]
Select main menu function(L1): [ 0]
Select main menu function(L1): [ warn] = Selected Function 20 - Warnings - Input Warnings sub menu
Select function(L2): [ %save][ "C:\Users\03419\Desktop\2022 Gas Study\temp\Warn_Sum.csv"] --> Output to C:\Users\03419\Desktop\2022 Gas Study\temp\Warn_Sum.csv
Select function(L2): [ %csv] Using CSV format
[ sum] = Selected Function 1 - Summary - Warnings Summary
*** Created [C:\Users\03419\Desktop\2022 Gas Study\temp\Warn_Sum.csv] Current directory - [C:\Users\03419\Desktop\2022 Gas Study\temp]
Select function(L2): [ 0]
Select main menu function(L1): [ 0]
Select main menu function(L1): [ warn] = Selected Function 20 - Warnings - Input Warnings sub menu
Select function(L2): [ %save][ "C:\Users\03419\Desktop\2022 Gas Study\temp\Warn_List.csv"] --> Output to C:\Users\03419\Desktop\2022 Gas Study\temp\Warn_List.csv
Select function(L2): [ %csv] Using CSV format
[ list] = Selected Function 2 - List - All Warnings and Errors List
*** Created [C:\Users\03419\Desktop\2022 Gas Study\temp\Warn_List.csv] Current directory - [C:\Users\03419\Desktop\2022 Gas Study\temp]
Select function(L2): [ 0]
Select main menu function(L1): [ 0]
Select main menu function(L1): [ chdir]
Current directory - [C:\Users\03419\Desktop\2022 Gas Study\temp]
Type new path (CR to exit)==>[ "C:\Users\03419\Desktop\2022 Gas Study\temp"]
New Current directory - [C:\Users\03419\Desktop\2022 Gas Study\temp]
Select main menu function(L1): [ _excel]
Engine ready:
*** Closed command file [C:\Users\03419\Desktop\2022 Gas Study\temp\_comm.txt] - 152 records (Lev=1)

## BatchProcessN1_DD3
Do NOT change B3,B4,B5 cells manually. Use right mouse click menu or Ribbon tab TARA Tools/Batch Automation Set up
Use FULL path for all files. Do NOT change any columns names. Do NOT remove first 6 columns.
Application | AC Contingency Analysis Reports |  |  | N-1 mode | RAS/CS is OFF
Reports | BranchViol,0
Reports Root Directory | C:\TARA_main\batch
Scenario Name(required) | LF Case File(required) | Study Data File(required) | Monitor File(required) | Contingency File | Exclude File | Data Directory
Base | sample2014_gen1.raw | sample.sub | Sample.mon | Sample.con |  | C:\TARA_main\SampleData2015 | Completed
Scenario 1 | sample2014_gen2.raw | sample.sub | Sample.mon | Sample.con |  | C:\TARA_main\SampleData2015 | Completed
Scenario 2 | sample2014_gen3.raw | sample.sub | Sample.mon | Sample.con |  | C:\TARA_main\SampleData2015 | Completed
Scenario 3 | sample2014_gen4.raw | sample.sub | Sample.mon | Sample.con |  | C:\TARA_main\SampleData2015 | Completed
`

## BatchProcessN11_DD1
Do NOT change B3,B4,B5 cells manually. Use right mouse click menu or Ribbon tab TARA Tools/Batch Automation Set up
Use FULL path for all files. Do NOT change any columns names. Do NOT remove first 6 columns.
Application | AC Contingency Analysis Reports |  |  | N-1-1 mode | RAS/CS is OFF
Reports | BranchViol,0
Reports Root Directory | C:\TARA_main\batchCases
Scenario Name(required) | LF Case File(required) | Study Data File(required) | Monitor File(required) | Contingency File | Exclude File | First-level Contingency File | Data Directory
Base | sample2014_gen1.raw | sample.sub | Sample.mon | Sample.con |  | Sample.con | C:\TARA_main\SampleData2015
Scenario1 | sample2014_gen2.raw | sample.sub | Sample.mon | Sample.con |  | Sample.con | C:\TARA_main\SampleData2015
Scenario2 | sample2014_gen3.raw | sample.sub | Sample.mon | Sample.con |  | Sample.con | C:\TARA_main\SampleData2015
Scenario3 | sample2014_gen4.raw | sample.sub | Sample.mon | Sample.con |  | Sample.con | C:\TARA_main\SampleData2015
`

## BatchProcess_PV
Do NOT change B3,B4,B5 cells manually. Use right mouse click menu or Ribbon tab TARA Tools/Batch Automation Set up
Use FULL path for all files. Do NOT change any columns names. Do NOT remove first 6 columns.
Application | PV Analysis |  |  | N-1 mode | RAS/CS is OFF
Reports | PVSummary,PVVoltage,0
Reports Root Directory | C:\TARA_main\batch
Scenario Name(required) | LF Case File(required) | Study Data File(required) | Monitor File(required) | Contingency File | Exclude File | Incremental Changes File | Options File | Data Directory | Sending (or Study Gen) Subsystem | Receiving (or Reference) Subsystem | Range of Contingencies (start with double quote, such as "1 -25) | PV Max Test | PV Init Test | PV Step Size
Base | training.epc | training.sub | training.mon | training.otg |  |  |  | C:\TARA_main\trainingQV | SOURCE_SCIT | SINK_SCIT | "1 -2 | 5000 | 400 | 300 | Completed
Scenario 1 | training.epc | training.sub | training.mon | training.otg |  |  |  | C:\TARA_main\trainingQV | SOURCE_SCIT | SINK_SCIT | "1,2,3" | 5500 | 450 | 350 | Completed
Scenario 2 | training.epc | training.sub | training.mon | training.otg |  |  |  | C:\TARA_main\trainingQV | SOURCE_SCIT | SINK_SCIT | "4" | 5500 | 450 | 350 | Completed
Scenario 3 | training.epc | training.sub | training.mon | training.otg |  |  |  | C:\TARA_main\trainingQV | SOURCE_SCIT | SINK_SCIT | "1 -3" | 5500 | 450 | 350 | Completed
Scenario 4 | training.epc | training.sub | training.mon | training.otg |  |  |  | C:\TARA_main\trainingQV | SOURCE_SCIT | SINK_SCIT | 1,2,3 | 5500 | 450 | 350 | Completed
Scenario 5 | training.epc | training.sub | training.mon | training.otg |  |  |  | C:\TARA_main\trainingQV | SOURCE_SCIT | SINK_SCIT | 7 | 5500 | 450 | 350 | Completed
`

## REPORTS (hidden)
TARAReports | [5 empty] | DO NOT DELETE OR EDIT THIS SHEET !
Page # | Page Caption | Report | Value | Prefix | Sheet | Suffix | Ext | Header | FileName | CompareSheet | CompareFile | Criteria | Descriptors | Compare | PivotTableParams | Compare to | ChartOne Y | ChartYOneValue | ChartYValue | ChartParam | ChartX | ChartLegend | HELP | Reserved
1 | lstViewRep1 | Constraints List | TRUE | det | AllViolations | %csv viol |  | 3 | [6 empty] | 4;0;22,23 | C:\TARA_main\TARAviewer_v1902_0_0_12.xlsb | [6 empty] | 1900
1 | lstViewRep1 | Summary Statistics | TRUE | sum | sumStat | %csv stat |  | 0 | [14 empty] | 1900
1 | lstViewRep1 | Details Report for All Snapgates | FALSE | det | AllDet | %txt adet |  | 0 | [14 empty] | 1900
1 | lstViewRep1 | Monitors Summary | FALSE | sum | MonitElem | %csv monit |  | 3 | [14 empty] | 1900
2 | lstViewRep2 | Study Generators | FALSE | sum | StudyGens | %csv gener |  | 3 | [14 empty] | 2000
2 | lstViewRep2 | Study Load and Generator Buses | FALSE | sum | StudyBuses | %csv buses |  | 3 | [14 empty] | 2000
2 | lstViewRep2 | All Harmers for All Constraints | FALSE | sum | Harmers | %csv Dharmer |  | 3 | [14 empty] | 2000
2 | lstViewRep2 | All Helpers for All Constraints | FALSE | sum | Helpers | %csv Dhelpers |  | 3 | [14 empty] | 2000
2 | lstViewRep2 | Combined All Harmers and Helpers | FALSE | sum | HarmHelpers | %csv DGEN |  | 3 | [14 empty] | 2000
2 | lstViewRep2 | DownStream Loads | FALSE | sum | DownStrLoad | %csv Dload |  | 3 | [14 empty] | 2000
2 | lstViewRep2 | Study Generator Worst Disp FCITC | FALSE | sum | StudyWrstFCITC | %csv GenReser |  | 0 | [14 empty] | 2000
3 | lstViewRep3 | Case Summary | TRUE | lfreview | CaseSum | %csv sum |  | 0 | [14 empty] | 1100
3 | lstViewRep3 | Area Summary | TRUE | lfreview | AreaSum | %csv tarea 1 |  | 3 | [14 empty] | 1100
3 | lstViewRep3 | Zone Summary | FALSE | lfreview | ZoneSum | %csv tzone 1 |  | 3 | [14 empty] | 1100
3 | lstViewRep3 | Owners List | FALSE | lfreview | OwnerList | %csv owner |  | 3 | [14 empty] | 1100
3 | lstViewRep3 | Bus Data | FALSE | lfreview | BusData | %csv bus |  | 3 |  |  |  | 1 | 2 | 10,11 | [8 empty] | 1100
3 | lstViewRep3 | Bus mismatches | FALSE | lfreview | BusMism | %csv mism |  | 3 | [14 empty] | 1100
3 | lstViewRep3 | Generator Data | FALSE | lfreview | GenData | %csv gener |  | 3 |  |  |  | 2,3,4,5,6,8 |  | 13,14 | 1;2;23 | [7 empty] | 1100
3 | lstViewRep3 | Plant Data | FALSE | lfreview | PlantData | %csv plant |  | 3 | [14 empty] | 1100
3 | lstViewRep3 | Load Data | FALSE | lfreview | LoadData | %csv load |  | 3 |  |  |  | 2,7 |  | 8 | [8 empty] | 1100
3 | lstViewRep3 | Switchable and Fixed Shunt Data | FALSE | lfreview | ShuntData | %csv shunt |  | 3 | [14 empty] | 1100
3 | lstViewRep3 | Switched Shunt Adjustments Base Solution | FALSE | lfreview | BaseShuntAdj | %csv AdjShuntBase |  | 3 | [14 empty] | 1100
3 | lstViewRep3 | Branch Data | FALSE | lfreview | BranchData | %csv branch |  | 3 |  |  |  | 1,2,3,4,5,6,7,8,9,10,11,13,19,20 | 12 | 14,15 | [8 empty] | 1100
3 | lstViewRep3 | Branch Double List Data | FALSE | lfreview | BranchDbData | %csv dbran |  | 3 |  |  |  | 1,6,11 |  | 14,15,16 | [8 empty] | 1100
3 | lstViewRep3 | Area Tie Data | FALSE | lfreview | TieData | %csv tie |  | 3 | [14 empty] | 1100
3 | lstViewRep3 | Area Tie Double List Data | FALSE | lfreview | TieDbData | %csv dtie |  | 3 | [14 empty] | 1100
3 | lstViewRep3 | TAP Voltage Control Adjust Data | FALSE | lfreview | TransfmrData | %csv tbran |  | 3 | [14 empty] | 1100
3 | lstViewRep3 | PARs Data | FALSE | lfreview | PARsData | %csv par |  | 3 | [14 empty] | 1100
3 | lstViewRep3 | Impedance Correction Data | FALSE | lfreview | ImpedCorr | %csv ImpedCorr |  | 3 | [14 empty] | 1100
3 | lstViewRep3 | Multisection Line Grouping Data | FALSE | lfreview | MultiSectLn | %csv MSECLN |  | 3 | [14 empty] | 1100
3 | lstViewRep3 | Two-term DC line Input Data | FALSE | lfreview 2term | DC2TData | %csv dc_2T 0 |  | 0 | [14 empty] | 1100
3 | lstViewRep3 | Two-term DC line Results | FALSE | lfreview 2term | DC2TFlows | %csv dc2res 0 |  | 0 | [14 empty] | 1100
3 | lstViewRep3 | DC Line Bus Flows | FALSE | lfreview 2term | DCLineBusFlows | %csv termflow 0 |  | 0 | [14 empty] | 1100
3 | lstViewRep3 | FACTS devices | FALSE | lfreview | FACTS | %csv facts |  | 3 | [14 empty] | 1100
3 | lstViewRep3 | Substation node and terminal data | FALSE | lfreview | SubstationNodeTerminalData | %csv NodeTerminal |  | 3 | [14 empty] | 1100
3 | lstViewRep3 | Substation Breaker Data | FALSE | lfreview | SubstationBreakerData | %csv Breaker |  | 3 | [14 empty] | 1100
3 | lstViewRep3 | Inter Area Transfer Data | FALSE | lfreview | InterAreaTran | %csv iartrn |  | 3 | [14 empty] | 1100
3 | lstViewRep3 | List of Defined Subsystems | FALSE | lfreview | Subsys | %csv subsys |  | 3 | [14 empty] | 1100
3 | lstViewRep3 | Input Warnings Summary | FALSE | warn | Warn_Sum | %csv sum |  | 4 |  |  |  | 1,2 |  | 3 | [8 empty] | 7300
3 | lstViewRep3 | Input Warning List | FALSE | warn | Warn_List | %csv list |  | 3 | [14 empty] | 7300
3 | lstViewRep3 | Case/Mon/Con Dimensions | FALSE | lfreview | Dimensions | %csv dimensions |  | 0 | [14 empty] | 1100
4 | lstViewRep4 | Contigency Summary | FALSE | cont | ConStat | %csv stat |  | 0 | [14 empty] | 1600
4 | lstViewRep4 | Contingency List | TRUE | cont | ConList | %csv list |  | 3 | [14 empty] | 1600
4 | lstViewRep4 | Contingency Details | FALSE | cont | ConDetail | %txt det |  | 0 | [14 empty] | 1600
4 | lstViewRep4 | Combined List of Contingency Events | FALSE | cont | ConEvents | %csv event |  | 3 | [14 empty] | 1600
4 | lstViewRep4 | Monitored Branches Base Case Flows | TRUE | cont | BranchFlows | %csv branch |  | 3 | [14 empty] | 1600
4 | lstViewRep4 | Excluded Contingencies and Constraints | FALSE | cont | ExcludeReport | %txt exclude |  | 0 | [14 empty] | 1600
4 | lstViewRep4 | Monitored Voltage Buses | FALSE | cont | VoltMonit | %csv voltage |  | 3 | [14 empty] | 1600
4 | lstViewRep4 | Duplicate Contingencies | FALSE | cont | ConDupl | %txt dupl |  | 0 | [14 empty] | 1600
4 | lstViewRep4 | Max cont event LODF for each mon | FALSE | cont | MaxLODFCon | %csv LODF |  | 3 | [14 empty] | 1600
4 | lstViewRep4 | Max cont event potential impact for each mon | FALSE | cont | MaxLODFImpCon | %csv LODFImpact |  | 3 | [14 empty] | 1600
4 | lstViewRep4 | Contingency Island Buses | FALSE | cont | ConIslandBuses | %csv IslandBuses |  | 3 | [14 empty] | 1600
4 | lstViewRep4 | Warnings List - Contingencies | FALSE | warn | Warn_Cont | %csv cont |  | 3 | [14 empty] | 1600
4 | lstViewRep4 | RAS/SPS Input Data | FALSE | cont | RAS_Input_Data | %csv RasInputReport |  | 0 | [14 empty] | 1600
5 | lstViewRep5 | List Clustered buses with DFAX | TRUE | cluster | ClustBuses | %csv list |  | 4 | [14 empty] | 2200
5 | lstViewRep5 | Area compostion in clusters | TRUE | cluster | ClustArea | %csv areas |  | 4 | [14 empty] | 2200
5 | lstViewRep5 | Summary Distance between clusters | TRUE | cluster | ClustDistSum | %csv chart |  | 0 | [14 empty] | 2200
5 | lstViewRep5 | Detailed Distance between clusters | TRUE | cluster | ClustDistDet | %csv det |  | 0 | [14 empty] | 2200
5 | lstViewRep5 | Create Subsystem per cluster | TRUE | cluster | ClustSubsys | %csv subsys |  | 0 | [14 empty] | 2200
5 | lstViewRep5 | Reserve Requirement Summary | TRUE | cluster | ClusterReserveSummary | %csv reserve |  | 5 | [14 empty] | 2200
6 | lstViewRep6 | Screening Summary (non-optimal mode only) - MIS | FALSE | nemis mis | NE_Screen_MIS | %csv screen |  | 5 | [14 empty] | 2300
6 | lstViewRep6 | Flowgate Loadings - MIS | TRUE | nemis mis | NE_FgLoad_MIS | %csv FgLoad |  | 5 | [14 empty] | 2300
6 | lstViewRep6 | Reference Dispatch Binding Flowgates – MIS | TRUE | nemis mis | NE_Binding_MIS | %csv binding |  | 5 | [14 empty] | 2300
6 | lstViewRep6 | Violation Summary (optimal mode only) - MIS | TRUE | nemis mis | NE_VioSum_MIS | %csv overloads |  | 5 | [14 empty] | 2300
7 | lstViewRep7 | Flowgate Loadings - Overlapping Impacts | TRUE | nemis overlap | NE_FgLoad_Overlap | %csv FgLoad |  | 5 | [14 empty] | 2300
7 | lstViewRep7 | Reference Dispatch Binding Flowgates – Overlapping Impacts | TRUE | nemis overlap | NE_Binding_Overlap | %csv binding |  | 5 | [14 empty] | 2300
7 | lstViewRep7 | Violation Summary - Overlapping Impacts | TRUE | nemis overlap | NE_VioSum_Overlap | %csv overloads |  | 5 | [14 empty] | 2300
8 | lstViewRep8 | Previously Approved for De-list | TRUE | nemis delist | NE_Approved_Delist | %csv approved |  | 5 | [14 empty] | 2300
8 | lstViewRep8 | Screening Summary – De-list | TRUE | nemis delist | NE_Screen_Delist | %csv screen |  | 5 | [14 empty] | 2300
8 | lstViewRep8 | Flowgate Loadings - De-list | TRUE | nemis delist | NE_FgLoad_Delist | %csv FgLoad |  | 5 | [14 empty] | 2300
8 | lstViewRep8 | Reference Dispatch Binding Flowgates – De-list | TRUE | nemis delist | NE_Binding_Delist | %csv binding |  | 5 | [14 empty] | 2300
8 | lstViewRep8 | Violation Summary - De-list | TRUE | nemis delist | NE_VioSum_Delist | %csv overloads |  | 5 | [14 empty] | 2300
9 | lstViewRep9 | Outage Summary | TRUE | outage | ORA_OutStat | %csv statis |  | 3 | [14 empty] | 1000
9 | lstViewRep9 | Outage List | TRUE | outage | ORA_OutList | %csv list |  | 3 | [14 empty] | 1000
9 | lstViewRep9 | Outage Schedule | TRUE | outage | ORA_OutSched | %csv sched |  | 3 | [14 empty] | 1000
9 | lstViewRep9 | Outage Errors | TRUE | outage | ORA_OutErrors | %csv outerrors |  | 3 | [14 empty] | 1000
9 | lstViewRep9 | Outage Details | TRUE | outage | ORA_OutDetail | %csv detail |  | 0 | [14 empty] | 1000
10 | lstViewRep10 | Flowgate Loadings | TRUE | det pjm gendeliv | GenDelivFgLoad | %csv run |  | 4 | [14 empty] | 1000
11 | lstViewRep11 | Reserve Zone Summary | TRUE | misoasm | ReserveZoneSummary | %csv resreq |  | 5 | [14 empty] | 2400
11 | lstViewRep11 | Reserve Zone Flowgates | TRUE | misoasm | ReserveZoneFgates | %csv fgates |  | 5 | [14 empty] | 2400
11 | lstViewRep11 | CP Nodes Assigned to Multiple Zones | FALSE | misoasm | CPNodeMultipleZones | %csv multcp |  | 5 | [14 empty] | 2400
11 | lstViewRep11 | Complete CP Node Assignment List | FALSE | misoasm | CPNodeAssignments | %csv cplist |  | 5 | [14 empty] | 2400
11 | lstViewRep11 | Future ASM Report 1 | FALSE | misoasm | ASM_Rep1 | %csv rep1 |  | 5 | [14 empty] | 2400
11 | lstViewRep11 | Future ASM Report 2 | FALSE | misoasm | ASM_Rep2 | %csv rep2 |  | 5 | [14 empty] | 2400
12 | lstViewRep12 | Load Forecast | TRUE | amb data | AMB_LoadFCast | %csv load |  | 3 | [14 empty] | 1000
13 | lstViewRep13 | Branch Flows Report | TRUE | sced | SCD_BranLoadings | %csv dccont {[SCED]} |  | 3 |  |  |  | 1,11,12 |  | 13,14 | [8 empty] | 1700
13 | lstViewRep13 | Binding constraints and shadow prices | TRUE | sced | SCD_Binding | %csv binding |  | 3 | [14 empty] | 1700
13 | lstViewRep13 | Adjusted Bidders | TRUE | sced | SCD_Adjusted | %csv adjusted |  | 3 | [14 empty] | 1700
13 | lstViewRep13 | Complete dispatch for all bidders | FALSE | sced | SCD_Dispatch | %csv dispatch |  | 3 | [14 empty] | 1700
13 | lstViewRep13 | SCD Redispatch Summary | TRUE | sced | SCD_Sum | %csv Sum |  | 3 | [14 empty] | 1700
13 | lstViewRep13 | Phase Shifters | FALSE | sced | SCD_PARs | %csv pars |  | 3 | [14 empty] | 1700
13 | lstViewRep13 | Bidders LMP Impact Analysis | FALSE | sced | SCD_BidderImpact | %csv bidImpact |  | 3 | [14 empty] | 1700
13 | lstViewRep13 | Pnodes LMP Impact Analysis | FALSE | sced | SCD_LMPImpact | %csv lmpImp |  | 4 | [14 empty] | 1700
13 | lstViewRep13 | Phase Shifter Impact Analysis | FALSE | sced | SCD_ParImpact | %csv parImpact |  | 3 | [14 empty] | 1700
13 | lstViewRep13 | List of Flowgates and Flows | FALSE | sced | SCD_ContFGates | %csv Lfgate |  | 3 | [14 empty] | 1700
13 | lstViewRep13 | Defined Pricing Nodes (pnodes) (for SCED data only) | FALSE | sced | SCD_Pnodes | %csv pnodes |  | 3 | [14 empty] | 1700
13 | lstViewRep13 | Defined Generator and Load Bids (for SCED data only) | FALSE | sced | SCD_Bids | %csv bids |  | 3 | [14 empty] | 1700
13 | lstViewRep13 | Generators to bids mapping (for SCED data only) | FALSE | sced | SCD_GenMap | %csv genmap |  | 3 | [14 empty] | 1700
13 | lstViewRep13 | Aggregate factors analysis | FALSE | sced | SCD_AggFact | %csv aggrFact |  | 3 | [14 empty] | 1700
13 | lstViewRep13 | Voltage Violation Results on case with new SCD dispatch | FALSE | cont | VoltViolRes | %csv acvolt |  | 3 | [14 empty] | 1500
13 | lstViewRep13 | Voltage Analysis Summary (all contingencies that were run by ACCont) | FALSE | cont | VoltViolSum | %csv acsum |  | 3 | [14 empty] | 1500
13 | lstViewRep13 | Voltage Analysis Not Converged Summary | FALSE | cont | VoltViolSumNotCnv | %csv NotConvLog |  | 3 | [14 empty] | 1500
13 | lstViewRep13 | Voltage Analysis Summary (list of contingencies with violation) | FALSE | cont | VoltViolSumViol | %csv ViolLog |  | 3 | [14 empty] | 1500
13 | lstViewRep13 | Voltage Analysis ACCont Bus Mismatch | FALSE | cont | ACContBusMism | %csv accontbusmism |  | 3 | [14 empty] | 1500
13 | lstViewRep13 | Switched Shunt Adjustments Post-Contingency | FALSE | cont | PostContShuntAdj | %csv adjshunt |  | 3 | [14 empty] | 1500
13 | lstViewRep13 | Bidder Impact on new First-Level Constraints (N-1-1 Only) | FALSE | sced | N11BidImpact | %csv N11BidImpact |  | 3 | [14 empty] | 1500
13 | lstViewRep13 | N-1-1 Isolated Gen/Load Buses (N-1-1 Only) | FALSE | cont | N11DetIslands | %csv IslDet |  | 3 | [14 empty] | 1500
14 | lstViewRep14 | Monitored branches AC violations | TRUE | cont | BranchViol | %csv acbranch {[ACC]} |  | 3 |  |  |  | 1,12 |  | 16,17 | [8 empty] | 1500
14 | lstViewRep14 | Monitored voltages violations | TRUE | cont | VoltViol | %csv acvolt |  | 3 |  |  |  | 2,16 |  | 18 | [8 empty] | 1500
14 | lstViewRep14 | ACCONT Summary for all contingencies | TRUE | cont | ACContSumAll | %csv acsum |  | 3 | [14 empty] | 1500
14 | lstViewRep14 | ACCONT Summary - not converged contingencies | TRUE | cont | ACContSumNotCnv | %csv NotConvLog |  | 3 | [14 empty] | 1500
14 | lstViewRep14 | ACCONT Summary - violations only | FALSE | cont | ACContSumViol | %csv ViolLog |  | 3 | [14 empty] | 1500
14 | lstViewRep14 | ACCONT Summary – Bus Mismatch | FALSE | cont | ACContBusMism | %csv accontbusmism |  | 3 | [14 empty] | 1500
14 | lstViewRep14 | Switched Shunt Adjustments Post-Contingency | FALSE | cont | PostContShuntAdj | %csv adjshunt |  | 3 | [14 empty] | 1500
14 | lstViewRep14 | N-1-1 Isolated Gen/Load Buses (N-1-1 Only) | FALSE | cont | N11DetIslands | %csv IslDet |  | 3 | [14 empty] | 1500
14 | lstViewRep14 | Worst case branch loading (obsolete) | FALSE | cont | BranWorstLoad | %csv acwbr {[ACC]} |  | 3 | [14 empty] | 1500
14 | lstViewRep14 | Worst case voltages violations (obsolete) | FALSE | cont | VoltWorstViol | %csv acwvolt |  | 3 | [14 empty] | 1500
14 | lstViewRep14 | Branch violations as Flowgates Monitor File | FALSE | cont | BranVioDefin | %txt flowgate |  | 0 | [14 empty] | 1500
14 | lstViewRep14 | Voltage violations as Voltage Monitor File | FALSE | cont | VoltVioDefin | %txt voltgate |  | 0 | [14 empty] | 1500
15 | lstViewRep15 | Optimal Transfer Summary | TRUE | trlim | MaxMWSum | %csv sum |  | 4 | [14 empty] | 5000
15 | lstViewRep15 | Binding Constraints | TRUE | trlim | MaxMWBinding | %csv binding |  | 3 | [14 empty] | 5000
15 | lstViewRep15 | Adjusted Generators | TRUE | trlim | MaxMWGens | %csv adjust |  | 3 | [14 empty] | 5000
15 | lstViewRep15 | Complete Generator Dispatch | FALSE | trlim | MaxMWDispatch | %csv dispatch |  | 3 | [14 empty] | 5000
15 | lstViewRep15 | PAR Adjustments | FALSE | trlim | MaxMWPARs | %csv pars |  | 3 | [14 empty] | 5000
15 | lstViewRep15 | DC Cont Analysis | TRUE | sced | MaxMWDCCont | %csv dccont {[TRL]} |  | 3 | [14 empty] | 5000
15 | lstViewRep15 | Flowgate Flows | FALSE | sced | MaxMWFgates | %csv lfgate |  | 3 | [14 empty] | 5000
15 | lstViewRep15 | Generator Impact Analysis | FALSE | sced | MaxMWGenImpact | %csv bidImpact |  | 4 | [14 empty] | 5000
15 | lstViewRep15 | Phase Shifter Impact Analysis | FALSE | sced | MaxMWParImpact | %csv parImpact |  | 3 | [14 empty] | 5000
16 | lstViewRep16 | PV Summary | TRUE | trlim | PVSummary | %csv PVSummary |  | 3 | [14 empty] | 8000
16 | lstViewRep16 | PV Voltages | TRUE | trlim | PVVoltage | %csv PVVoltage |  | 3 | [14 empty] | 8000
16 | lstViewRep16 | PV Branch Flows | TRUE | trlim | PVBranchFlow | %csv PVBranchFlow |  | 3 | [14 empty] | 8000
16 | lstViewRep16 | PV Flowgates | TRUE | trlim | PVFlowgate | %csv PVFlowgate |  | 3 | [14 empty] | 8000
16 | lstViewRep16 | PV Shunts | TRUE | trlim | PVShunt | %csv PVShunt |  | 3 | [14 empty] | 8000
16 | lstViewRep16 | Bus Dfax (created if Add Dfax is ON) | FALSE | trlim | BusDfax | %csv BusDfax |  | 3 | [14 empty] | 8000
17 | lstViewRep17 | Impact of Transaction on Area Tie Branches | FALSE | trlim | TieLinesImpact | %csv tieLinesImpact |  | 3 | [14 empty] | 5200
17 | lstViewRep17 | Area-to-Area Impact of Transaction | FALSE | trlim | AreaToAreaImpact | %csv areaToAreaImpact |  | 3 | [14 empty] | 5200
17 | lstViewRep17 | Impact of Transaction on each Area | FALSE | trlim | AreaImpact | %csv areaImpact |  | 3 | [14 empty] | 5200
18 | lstViewRep18 | List of All Available Bus Numbers | FALSE | lfreview | BusAvailNN | %csv UnusedBuse {[UNBUS]} |  | 3 | [14 empty] | 1100
18 | lstViewRep18 | Distance from Generators to remotely controlled buses | FALSE | lfreview | GenRemDist | %csv remdist |  | 3 | [14 empty] | 1100
18 | lstViewRep18 | Area Connectivity Report | FALSE | lfreview | AreaTies | %csv AreaTieDiag |  | 3 | [14 empty] | 1100
18 | lstViewRep18 | Zone Connectivity Report | FALSE | lfreview | ZoneTies | %csv ZoneTieDiag |  | 3 | [14 empty] | 1100
18 | lstViewRep18 | Area Details Summary | FALSE | lfreview | AreasData | %csv AreaDiag |  | 4 | [14 empty] | 1100
18 | lstViewRep18 | Zone Details Summary | FALSE | lfreview | ZonesData | %csv ZoneDiag |  | 4 | [14 empty] | 1100
18 | lstViewRep18 | Area-Zone Cross-mapping | FALSE | lfreview | AreaZoneCrossMap | %csv AREAZONE |  | 3 | [14 empty] | 1100
19 | lstViewRep19 | QV Summary | TRUE | trlim qvanalysis | QVBusBasedSummary | %csv Summary |  | 3 | [14 empty] | 9070
19 | lstViewRep19 | QV Study Buses | TRUE | trlim qvanalysis | QVStudyBusReport | %csv StudyBusReport |  | 3 | [14 empty] | 9070
20 | lstViewRep20 | List of Flowgates/Interfaces | TRUE | cont | ContFGates | %csv Lfgate |  | 3 | [14 empty] | 1600
20 | lstViewRep20 | Flowgate/Interface Details | FALSE | cont | FgateDet | %csv fgate |  | 0 | [14 empty] | 1600
|  | Details | TRUE |  | Details |  |  | 0 | [14 empty] | 1000
|  | Charts | TRUE |  | Charts |  |  | 0 | [14 empty] | 1000
|  | Deliver | TRUE |  | Deliver |  |  | 3 | [14 empty] | 1000
|  | DFAX | TRUE |  | DFAX |  |  | 9 | [14 empty] | 1000
|  | Compet | TRUE |  | Compet |  |  | 5 | [14 empty] | 1000
|  | Gdfax | TRUE |  | Gdfax |  |  | 5 | [14 empty] | 1000
|  | GRDcalc | TRUE |  | GRDcalcTemp |  |  | 4 | [14 empty] | 4300
|  | GRDref | TRUE |  | GRDrefTemp |  |  | 4 | [14 empty] | 4300
|  | GRDstudy | TRUE |  | GRDstudyTemp |  |  | 4 | [14 empty] | 4300
|  | GRDMax | TRUE |  | GRDMaxTemp |  |  | 4 | [14 empty] | 4300
|  | GRDredisp1 | TRUE |  | GRDredisp1Temp |  |  | 4 | [14 empty] | 4300
|  | GRDredisp2 | TRUE |  | GRDredisp2Temp |  |  | 4 | [14 empty] | 4300
|  | ViolationScreenSum | TRUE |  | ViolationScreenSum |  |  | 4 | [14 empty] | 2100
|  | ViolationScreenSumNE | TRUE |  | ViolationScreenSumNE |  |  | 4 | [14 empty] | 2100
|  | ScreeningDispatchDetails | TRUE |  | ScreeningDispatchDetails |  |  | 4 | [14 empty] | 2100
|  | tempFlgFile | TRUE |  | tempFlgFile |  |  | 8 | [14 empty] | 2100
|  | genScreen | TRUE |  | genScreen |  |  | 3 | [14 empty] | 1000
|  | tdfScreen | TRUE |  | tdfScreen |  |  | 3 | [14 empty] | 1000
|  | TrLim | TRUE |  | TRLProp |  |  | 0 | [14 empty] | 5100
|  | TrLimFgDetail | TRUE |  | TrLimFgDetail |  |  | 0 | [14 empty] | 5100
|  | TrLimSubSysDetail | TRUE |  | TrLimSubSysDetail |  |  | 0 | [14 empty] | 5100
|  | TrLimMultiPath | TRUE |  | TrLimMultiPath |  |  | 0 | [14 empty] | 5100
|  | ACTrLim | TRUE |  | TLCvdet |  |  | 3 | [14 empty] | 5200
|  | TrLimPS | TRUE |  | pathTrLim |  |  | 0 | [14 empty] | 5200
|  | PVScrSum | TRUE |  | PVScrSum |  |  | 3 | [14 empty] | 8100
|  | PVBranchFlow | TRUE |  | PVBranchFlow |  |  | 3 | [14 empty] | 8000
|  | PVVoltage | TRUE |  | PVVoltage |  |  | 3 | [14 empty] | 8000
|  | PVFlowgate | TRUE |  | PVFlowgate |  |  | 3 | [14 empty] | 8000
|  | PVShunt | TRUE |  | PVShunt |  |  | 3 | [14 empty] | 8000
|  | PVSummary | TRUE |  | PVSummary |  |  | 3 | [14 empty] | 8000
|  | BusDfax | TRUE |  | BusDfax |  |  | 3 | [14 empty] | 8000
| ACContReports | Monitored branches AC violations (BranchViol sheet) | TRUE | cont | BranchViol | %csv acbranch {[ACC]} |  | 3 | [14 empty] | 1500
| ACContReports | Monitored voltages violations (VoltViol sheet) | TRUE | cont | VoltViol | %csv acvolt |  | 3 | [14 empty] | 1500
| ACContReports | ACCONT Summary for all contingencies (ACContSumAll sheet) | FALSE | cont | ACContSumAll | %csv acsum |  | 3 | [14 empty] | 1500
| ACContReports | ACCONT Summary - not converged cont (ACContSumNotCnv sheet) | TRUE | cont | ACContSumNotCnv | %csv NotConvLog |  | 3 | [14 empty] | 1500
| ACContReports | ACCONT Summary - violations only (ACContSumViol sheet) | FALSE | cont | ACContSumViol | %csv ViolLog |  | 3 | [14 empty] | 1500
| ACContReports | ACCONT Summary – Bus Mismatch | FALSE | cont | ACContBusMism | %csv accontbusmism |  | 3 | [14 empty] | 1500
| ACContReports | Switched Shunt Adjustments Post-Contingency | FALSE | cont | PostContShuntAdj | %csv adjshunt |  | 3 | [14 empty] | 1500
| ACContReports | ALL monitored branches (BranchFlows sheet) | FALSE | cont | BranchFlows | %csv branch |  | 3 | [14 empty] | 1500
| ACContReports | ALL voltages monitored buses (VoltMonit sheet) | FALSE | cont | VoltMonit | %csv voltage |  | 3 | [14 empty] | 1500
| ACContReports | N-1-1 Isolated Gen/Load Buses (N-1-1 Only) | FALSE | cont | N11DetIslands | %csv IslDet |  | 3 | [14 empty] | 1500
| ACContReports | Worst case branch loading (obsolete) | FALSE | cont | BranWorstLoad | %csv acwbr {[ACC]} |  | 3 | [14 empty] | 1500
| ACContReports | Worst case voltages violations (obsolete) | FALSE | cont | VoltWorstViol | %csv acwvolt |  | 3 | [14 empty] | 1500
|  | bus | TRUE |  | BusData |  |  | 3 | [14 empty] | 1100
|  | gener | TRUE |  | GenData |  |  | 3 | [14 empty] | 1100
|  | plant | TRUE |  | PlantData |  |  | 3 | [14 empty] | 1100
|  | load | TRUE |  | LoadData |  |  | 3 | [14 empty] | 1100
|  | shunt | TRUE |  | ShuntData |  |  | 3 | [14 empty] | 1100
|  | bran | TRUE |  | BranchData |  |  | 3 | [14 empty] | 1100
|  | dbran | TRUE |  | BranchDbData |  |  | 3 | [14 empty] | 1100
|  | tie | TRUE |  | TieData |  |  | 3 | [14 empty] | 1100
|  | dtie | TRUE |  | TieDbData |  |  | 3 | [14 empty] | 1100
|  | ztie | TRUE |  | ZTieData |  |  | 3 | [14 empty] | 1100
|  | zdtie | TRUE |  | ZTieDbData |  |  | 3 | [14 empty] | 1100
|  | tbran | TRUE |  | TransfmrData |  |  | 3 | [14 empty] | 1100
|  | par | TRUE |  | PARsData |  |  | 3 | [14 empty] | 1100
|  | conts | TRUE |  | ConstrDetails |  |  | 0 | [14 empty] | 2100
|  | dsubsys | TRUE |  | SubSysDetails |  |  | 3 | [14 empty] | 1000
|  | SubSysBusesCI | TRUE |  | SubBusConIsl |  |  | 3 | [14 empty] | 1000
|  | retrieve | TRUE |  | ssROdata |  |  | 0 | [14 empty] | 1000
|  | BusFlows | TRUE |  | BusFlows |  |  | 0 | [14 empty] | 1000
| NEDemandBilatReps | List of Reconfig/Bilateral Bids | TRUE | nemis demand | NE_BidsList | %csv bids |  | 3 | [14 empty] | 2300
| NEDemandBilatReps | Overload Summary | TRUE | nemis demand | NE_OverloadSum | %csv over |  | 3 | [14 empty] | 2300
| NEDemandBilatReps | Flowgate Stress Summary | TRUE | nemis demand | NE_FgateStressSum | %csv combined |  | 3 | [14 empty] | 2300
| NEDemandBilatReps | Interface Flows | TRUE | nemis demand | NE_InterfaceFlows | %csv Interfaces |  | 3 | [14 empty] | 2300
| NEDemandBilatReps | Subsystem Load and Excess Generation | TRUE | nemis demand | NE_SysLoadExcessGen | %csv SysExcess |  | 3 | [14 empty] | 2300
| NEDemandBilatMReps | Flowgate Stress Summary | TRUE | nemis monthly | NE_MonthlyDet | %csv DemandRun |  | 3 | [14 empty] | 2300
| NEDemandBilatMReps | List of Reconfig/Bilateral Bids | TRUE | nemis monthly | NE_BidsList | %csv bids |  | 3 | [14 empty] | 2300
| NEDemandBilatMReps | Overload Summary | TRUE | nemis monthly | NE_MonthlySum | %csv over |  | 3 | [14 empty] | 2300
| NEDemandBilatSCRD | Binding constraints and shadow prices | FALSE | sced | SCD_Binding | %csv binding |  | 3 | [14 empty] | 1700
| NEDemandBilatSCRD | Adjusted generators | FALSE | sced | SCD_Adjusted | %csv adjusted |  | 3 | [14 empty] | 1700
| NEDemandBilatSCRD | Complete dispatch for all generators | FALSE | sced | SCD_Dispatch | %csv dispatch |  | 3 | [14 empty] | 1700
| NEDemandBilatSCRD | SCED Redispatch summary | FALSE | sced | SCD_Sum | %csv Sum |  | 0 | [14 empty] | 1700
| NEDemandBilatSCRD | Phase Shifters | FALSE | sced | SCD_PARs | %csv pars |  | 3 | [14 empty] | 1700
| NEDemandBilatSCRD | List of Flowgates and Flows | TRUE | nemis demand | SCD_ContFGates | %csv Lfgate |  | 3 | [14 empty] | 1700
| NEDemandBilatMSCRD | Binding constraints and shadow prices | TRUE | sced | SCD_Binding | %csv binding |  | 3 | [14 empty] | 1700
| NEDemandBilatMSCRD | Adjusted generators | FALSE | sced | SCD_Adjusted | %csv adjusted |  | 3 | [14 empty] | 1700
| NEDemandBilatMSCRD | Complete dispatch for all generators | FALSE | sced | SCD_Dispatch | %csv dispatch |  | 3 | [14 empty] | 1700
| NEDemandBilatMSCRD | SCED Redispatch summary | FALSE | sced | SCD_Sum | %csv Sum |  | 0 | [14 empty] | 1700
| NEDemandBilatMSCRD | Phase Shifters | FALSE | sced | SCD_PARs | %csv pars |  | 3 | [14 empty] | 1700
| NEDemandBilatMSCRD | List of Flowgates and Flows | FALSE | sced | SCD_ContFGates | %csv Lfgate |  | 3 | [14 empty] | 1700
| NEDemandBilatMSCRD | Branch Flows Report | FALSE | sced | SCD_BranLoadings | %csv dccont {[SCEDNE]} |  | 3 | [14 empty] | 1700
| StressReview | StressReview | TRUE | nemis demand | StressReview | %csv ReviewInfo |  | 0 | [14 empty] | 1700
|  | BusDiagData | TRUE |  | BusDiagData |  |  | 0 | [14 empty] | 1000
|  | AreaDiagAreaData | TRUE |  | AreaDiagAreaData |  |  | 4 | [14 empty] | 1000
|  | AreaDiagConnectData | TRUE |  | AreaDiagConnectData |  |  | 3 | [14 empty] | 1000
|  | ZoneDiagZoneData | TRUE |  | ZoneDiagZoneData |  |  | 4 | [14 empty] | 1000
|  | ZoneDiagConnectData | TRUE |  | ZoneDiagConnectData |  |  | 3 | [14 empty] | 1000
| NEACContReports | Monitored branches AC violations | TRUE | cont | NE_BranchViol | %csv acbranch {[ACC]} |  | 3 | [14 empty] | 1500
| NEACContReports | Monitored voltages violations | TRUE | cont | NE_VoltViol | %csv acvolt |  | 3 | [14 empty] | 1500
| NEACContReports | ACCONT Summary for all contingencies | TRUE | cont | NE_ACContSumAll | %csv acsum |  | 3 | [14 empty] | 1500
| NEACContReports | ACCONT Summary - not converged cont | TRUE | cont | NE_ACContSumNotCnv | %csv NotConvLog |  | 3 | [14 empty] | 1500
| NEACContReports | ACCONT Summary - violations only | TRUE | cont | NE_ACContSumViol | %csv ViolLog |  | 3 | [14 empty] | 1500
| NEACContReports | ACCONT Summary – Bus Mismatch | TRUE | cont | NE_ACContBusMism | %csv accontbusmism |  | 3 | [14 empty] | 1500
| NEACContReports | Switched Shunt Adjustments Post-Contingency | TRUE | cont | NE_PostContShuntAdj | %csv adjshunt |  | 3 | [14 empty] | 1500
|  | BusDist | TRUE | lfreview | BusDist | %csv bdist | {[BDIST]} | 3 | [14 empty] | 1000
|  | BusMonFile | TRUE | lfreview | BusMonFile | %csv bmon | {[BDIST]} | 0 | [14 empty] | 1000
|  | BusPath | TRUE | lfreview | BusPath | %csv b2dist | {[BPATH]} | 3 | [14 empty] | 1000
|  | BusAvailNN | TRUE | lfreview | BusAvailNN | %csv UnusedBuse |  | 3 | [14 empty] | 1000
|  | BusDFAX | TRUE |  | BusDFAX |  |  | 0 | [14 empty] | 1000
|  | BusContFIle | TRUE | lfreview | BusContFIle | %txt bcont | {[BDIST]} | 0 | [14 empty] | 1000
|  | DCCONT | TRUE | cont | DCCONT | %csv dccont | {[CONT]} | 3 |  |  |  | 1,12 |  | 15 | [8 empty] | 1400
|  | DCACVer | TRUE | cont | DCACVer | %csv acscre | {[CONT]} | 3 | [14 empty] | 1400
|  | ACContSumAll | TRUE | cont | ACContSumAll | %csv acsum |  | 3 | [14 empty] | 1500
|  | ACContSumNotCnv | TRUE | cont | ACContSumNotCnv | %csv NotConvLog |  | 3 | [14 empty] | 1500
|  | ACContSumViol | TRUE | cont | ACContSumViol | %csv ViolLog |  | 3 | [14 empty] | 1500
|  | ACContBusMism | TRUE | cont | ACContBusMism | %csv accontbusmism |  | 3 | [14 empty] | 1500
|  | VoltViol | TRUE | cont | VoltViol | %csv acvolt |  | 3 | [14 empty] | 1500
|  | PostContShuntAdj | TRUE | cont | PostContShuntAdj | %csv adjshunt |  | 3 | [14 empty] | 1500
|  | N11DetIslands | TRUE | cont | N11DetIslands | %csv IslDet |  | 3 | [14 empty] | 1500
|  | N-1-1_Summary | TRUE | cont | N-1-1_Summary | %csv sumN11 |  | 3 | [14 empty] | 1500
|  | N-1-1_Islands | TRUE | cont | N-1-1_Islands | %csv NewIslands |  | 3 | [14 empty] | 1500
|  | CorrSwFlows | TRUE | cont | CorrSwFlows | %csv CorrSw |  | 3 | [14 empty] | 9060
|  | CorrSwVoltages | TRUE | cont | CorrSwVoltages | %csv VoltCorrSw |  | 3 | [14 empty] | 9060
|  | CorrSwSummary | TRUE | cont | CorrSwSummary | %csv SumCorrSw |  | 3 | [14 empty] | 9060
|  | RAS_Flows | TRUE | cont | RAS_Flows | %csv CorrSw |  | 3 | [14 empty] | 8360
|  | RAS_Voltages | TRUE | cont | RAS_Voltages | %csv VoltCorrSw |  | 3 | [14 empty] | 8360
|  | RAS_Summary | TRUE | cont | RAS_Summary | %csv SumCorrSw |  | 3 | [14 empty] | 8360
|  | CascadeSummary | TRUE | cont | CascadeSummary | %csv CascadeSummary |  | 3 | [14 empty] | 1500
|  | CascadeGenTripSum | TRUE | cont | CascadeGenTripSum | %csv CascadeGenTripSummary |  | 3 | [14 empty] | 1500
|  | CascadeGenLdIslandSum | TRUE | cont | CascadeGenLdIslandSum | %csv CascadeGenLdIslandSummary |  | 3 | [14 empty] | 1500
|  | CascadeLoadTripSum | TRUE | cont | CascadeLoadTripSum | %csv CascadeLoadTripSummary |  | 3 | [14 empty] | 1500
|  | ContDetails | TRUE |  | ContDetails |  |  | 0 | [14 empty] | 1500
|  | ContEvents | TRUE |  | ContEvents |  |  | 3 | [14 empty] | 1500
|  | ContLog | TRUE |  | ContLog |  |  | 0 | [14 empty] | 1500
|  | ContDefin | TRUE |  | ContDefin |  |  | 0 | [14 empty] | 1500
|  | ContDoubleDefin | TRUE |  | ContDoubleDefin |  |  | 0 | [14 empty] | 1500
|  | CombinedCont | TRUE |  | CombinedCont |  |  | 0 | [14 empty] | 1500
|  | FgateDefin | TRUE |  | FgateDefin |  |  | 0 | [14 empty] | 1500
|  | FgateDet | TRUE |  | FgateDet |  |  | 0 | [14 empty] | 1500
|  | GDDetail_FG | TRUE |  | GDDetail_FG |  |  | 7 | [14 empty] | 1000
|  | PJM_GDPlant | TRUE |  | PJM_GDPlant |  |  | 7 | [14 empty] | 1000
|  | MISO_GDPlant | TRUE |  | MISO_GDPlant |  |  | 7 | [14 empty] | 1000
|  | FG_Dispatch_FG | TRUE |  | FG_Dispatch_FG |  |  | 9 | [14 empty] | 1000
|  | GenParticipation | TRUE |  | GenParticipation |  |  | 3 | [14 empty] | 1000
|  | NIPSCOGenDelivFgDetails | TRUE |  | NIPSCOGenDelivFgDetails |  |  | 7 | [14 empty] | 1000
|  | NIPSCOGenDelivFgLoad | TRUE |  | NIPSCOGenDelivFgLoad |  |  | 3 | [14 empty] | 1000
|  | AreaSumSnSh | TRUE |  | SnapshotAreaSum |  |  | 3 | [14 empty] | 1100
| GenDeliverability | Flowgate Loadings | TRUE | deliv | GenDelivFgLoad | %csv GDSummary |  | 4 | [14 empty] | 1000
| GenDeliverability | Generation Summary | TRUE | deliv | GenDelivGenSummary | %csv GDGenSummary |  | 3 | [14 empty] | 1000
| GenDeliverability | Create GD Flowgates | TRUE | deliv | GDViolFGateDefinition | %txt CreateGDFlowgates |  | 0 | [14 empty] | 1000
|  | ORA_DCCONT | TRUE |  | ORA_DCCONT |  |  | 3 | [14 empty] | 6500
|  | ORA_OutDetail | TRUE |  | ORA_OutDetail |  |  | 0 | [14 empty] | 6500
|  | ORA_OutDef | TRUE |  | ORA_OutDef |  |  | 0 | [14 empty] | 6500
| MISOGenOutReports | Capacity Outage Analysis Summary | TRUE | capacityout | GenOutSummary | %csv Summary |  | 3 | [14 empty] | 1000
| MISOGenOutReports | List of Generator Outage Combinations | TRUE | capacityout | OutageCombos | %csv OutageCombos |  | 3 | [14 empty] | 1000
| MISOGenOutReports | Binding Constraints | TRUE | sced | SCD_Binding | %csv binding |  | 3 | [14 empty] | 1000
| MISOGenOutReports | All Participating Generators Dispatch | TRUE | sced | SCD_Dispatch | %csv dispatch |  | 3 | [14 empty] | 1000
| MISOGenOutReports | Adjusted Generators Dispatch | TRUE | sced | SCD_Adjusted | %csv adjusted |  | 3 | [14 empty] | 1000
|  | OutLog | TRUE |  | OutLog |  |  | 0 | [14 empty] | 6500
| GenMDeliverability | Flowgate Loadings | TRUE | deliv | MISOGenDelivFgLoad | %csv GDSummary |  | 4 | [14 empty] | 1000
| GenMDeliverability | NR Units Summary | TRUE | deliv | NRUnitsSummary | %csv NRGENSummary |  | 3 | [14 empty] | 1000
| GenMDeliverability | Top 30/Adder Breakdown | TRUE | deliv | Top30AdderBreakDown | %csv Top30AdderBreakdown |  | 4 | [14 empty] | 1000
| GenMDeliverability | Partial NR List | TRUE | deliv | PartialNRList | %csv PNRList |  | 3 | [14 empty] | 1000
| GenMDeliverability | Top 30/Adder Generation Summary | TRUE | deliv | Top30AdderGenSummary | %csv Top30AdderGenSummary |  | 3 | [14 empty] | 1000
| GenMDeliverability | Study Generator Participation Summary | TRUE | deliv | GenPartSummary | %csv GDGenSummary |  | 3 | [14 empty] | 1000
|  | ConstrDefin | TRUE |  | ConstrDefin |  |  | 0 | [14 empty] | 1000
| MISOTSRReports | Branch Violation Summary | TRUE | customApps MISO TSR | MISOTSRSummary_MonBran | %csv TSRSum_MonBran 0 0 |  | 3 | [14 empty] | 1000
| MISOTSRReports | Flowgate Violation Summary | TRUE | customApps MISO TSR | MISOTSRSummary_Fgate | %csv TSRSum_Fgate 0 0 |  | 3 | [14 empty] | 1000
| MISOTSRReports | Bus Voltage Violation Summary | TRUE | customApps MISO TSR | MISOTSRSummary_BusVolt | %csv TSRSum_BusVolt 0 0 |  | 3 | [14 empty] | 1000
|  | ConstrDet | TRUE |  | ConstrDet |  |  | 0 | [14 empty] | 1000
| StudyOutsReports | Branch Flows | FALSE | outage | StudyFlows | %csv branflows | %csv branflows | 3 | %csv branflows | [13 empty] | 6500
| StudyOutsReports | Branch Flows - Report Manager | TRUE | outage | CustomStudyFlows | %csv custBranFlows | %csv custBranFlows | 3 | %csv custBranFlows | [13 empty] | 6500
| StudyOutsReports | Summary of STUDY Outages Analysis Results | TRUE | outage | StudySum | %csv sumstudy | %csv sumORIstudy | 3 | %csv sumstudy | [13 empty] | 6500
| StudyOutsReportsA | Automated STUDY Outages Evaluation | TRUE | outage | AutoSum | %csv sumstudy | %csv sumORIstudy | 3 | %csv sumauto | [13 empty] | 6500
| StudyOutsReportsA | PJM eDART Report | FALSE | outage | eDART | %csv eDART | %csv eDART | 1 | %csv eDART | [13 empty] | 6500
| StudyOutsReports | Outage Convergence Report | FALSE | outage | OutConv | %csv outConvSum | %csv outConvSum | 3 | %csv outConvSum | [13 empty] | 6500
| StudyOutsReports | Generation Complete Dispatch | FALSE | outage | SCD_Disp | %csv disp | %csv disp | 3 | %csv disp | [13 empty] | 1700
| StudyOutsReports | Generation Adjustment Redispatch | FALSE | outage | SCD_Adjust | %csv adjust | %csv adjust | 3 | %csv adjust | [13 empty] | 1700
| StudyOutsReports | Phase Shifters | FALSE | outage | SCD_PARs | %csv pars | %csv pars | 3 | %csv pars | [13 empty] | 1700
| StudyOutsReports | Interfaces/Flowgates | FALSE | outage | SCD_Fgates | %csv FgateFlows | %csv FgateFlows | 3 | %csv FgateFlows | [13 empty] | 1700
| StudyOutsReports | Binding Constraints | FALSE | outage | SCD_Binding | %csv BindingConstraints | %csv BindingConstraints | 3 | %csv BindingConstraints | [13 empty] | 1700
| StudyOutsReports | Bidder Impact on new Outage Constraints | FALSE | outage | BidImpact | %csv BidImpact | %csv BidImpact | 3 | %csv BidImpact | [13 empty] | 1700
| StudyOutsReports | Not Converged Contingencies | FALSE | outage | NotConvCont | %csv converged | %csv converged | 3 | %csv converged | [13 empty] | 1700
| StudyOutsReports | Voltage Violations (AC Mode only) | FALSE | outage | VoltViol | %csv voltviol | %csv voltviol | 3 | %csv voltviol | [13 empty] | 1700
| StudyOutsReports | Voltage Violations - Report Manager (AC Mode only) | FALSE | outage | CustomVoltViol | %csv custVoltViol | %csv custVoltViol | 3 | %csv custVoltViol | [13 empty] | 1700
| StudyOutsReports | Generator Harmer Sensitivities | FALSE | outage | GenSensHarm | %csv HarmGenSens | %csv HarmGenSens | 3 | %csv HarmGenSens | [13 empty] | 1700
| StudyOutsReports | Generator Helper Sensitivities | FALSE | outage | GenSensHelp | %csv HelpGenSens | %csv HelpGenSens | 3 | %csv HelpGenSens | [13 empty] | 1700
| StudyOutsReports | Transfer Sensitivities | FALSE | outage | TrLimSens | %csv TrLim | %csv TrLim | 3 | %csv TrLim | [13 empty] | 1700
| StudyOutsReports | ORA Isolated Gen/Load Summary | FALSE | outage | IslandSummary | %csv IslSummary | %csv IslSummary | 3 | %csv IslSummary | [13 empty] | 1700
| StudyOutsReports | ORA Post-Cont Isolated Gen/Load MW | FALSE | outage | 2ndLevelIslands | %csv NewIslands | %csv NewIslands | 3 | %csv NewIslands | [13 empty] | 1700
| StudyOutsReports | ORA Isolated Gen/Load Buses | FALSE | outage | DetIslands | %csv IslDet | %csv IslDet | 3 | %csv IslDet | [13 empty] | 1700
| StudyOutsReports | Switched Shunt Adjustments | FALSE | outage | ShuntAdj | %csv adjshunt | %csv adjshunt | 3 | %csv adjshunt | [13 empty] | 1700
|  | ORA_CommonImpactSum | TRUE |  | ORA_CommonImpactSum |  |  | 3 | [14 empty] | 1700
| ERISReports | Branch Violation Summary | TRUE | customApps MISO ERIS | ERIS_Summary | %csv ERISSum_MonBran 0 0 |  | 3 | [14 empty] | 1000
| ERISReports | ERIS Report Table | TRUE | customApps MISO ERIS | ERIS_ReportTable | %csv ERIS_ReportTable 0 0 |  | 4 | [14 empty] | 1000
| ERISReports | ERIS Violation Projects Summary | TRUE | customApps MISO ERIS | ERIS_Generator | %csv ERISSum_Generator 0 0 |  | 3 | [14 empty] | 1000
| ERISReports | ERIS Violation Contingency List | TRUE | customApps MISO ERIS | ERIS_Contingency | %txt ERIS_Contingency 0 0 |  | 0 | [14 empty] | 1000
| ERISReports | ERIS CUU Cost Allocation – Detail | TRUE | customApps MISO ERIS | ERIS_CUUCostAllocation_Det | %csv ERIS_CUUCostAllocation_Detail 0 0 |  | 3 | [14 empty] | 1000
| ERISReports | ERIS CUU Cost Allocation - Worst | TRUE | customApps MISO ERIS | ERIS_CUUCostAllocation_Worst | %csv ERIS_CUUCostAllocation_Worst 0 0 |  | 3 | [14 empty] | 1000
|  | PARcalc | TRUE |  | PARcalcTemp |  |  | 0 | [14 empty] | 4200
| SNUReports | SNUReport 1 | TRUE | customApps MISO ERIS | ERIS_SNUCostAlloc_Detail | %csv ERIS_SNUCostAllocation_Detail 0 0 |  | 3 | [14 empty] | 1000
| SNUReports | SNUReport 2 | TRUE | customApps MISO ERIS | ERIS_SNUCostAlloc_Sum | %csv ERIS_SNUCostAllocation_Summary 0 0 |  | 3 | [14 empty] | 1000
|  | ERIS_Detail | TRUE |  | ERIS_Detail |  |  | 8 | [14 empty] | 1000
| ConflContOuts | List of Conflicts | TRUE | outage | ConflictConts | %csv ConflConts |  | 3 | [14 empty] | 6500
| ConflContOuts | Branch Flows | FALSE | outage | StudyFlows | %csv branflows |  | 3 | [14 empty] | 6500
| ConflContOuts | Branch Flows - Report Manager | TRUE | outage | CustomStudyFlows | %csv custBranFlows |  | 3 | [14 empty] | 6500
| ConflContOuts | Summary of STUDY Outages Analysis Results | FALSE | outage | StudySum | %csv sumstudy |  | 3 | [14 empty] | 6500
| ConflContOuts | Generation Complete Dispatch | FALSE | outage | SCD_Disp | %csv disp |  | 3 | [14 empty] | 1700
| ConflContOuts | Generation Adjustment Redispatch | FALSE | outage | SCD_Adjust | %csv adjust |  | 3 | [14 empty] | 1700
| ConflContOuts | Phase Shifters | FALSE | outage | SCD_PARs | %csv pars |  | 3 | [14 empty] | 1700
| ConflContOuts | Interfaces/Flowgates | FALSE | outage | SCD_Fgates | %csv FgateFlows |  | 3 | [14 empty] | 1700
| ConflContOuts | Binding Constraints | FALSE | outage | SCD_Binding | %csv BindingConstraints |  | 3 | [14 empty] | 1700
| ConflContOuts | Bidder Impact on new Outage Constraints | FALSE | outage | BidImpact | %csv BidImpact |  | 3 | [14 empty] | 1700
| ConflContOuts | Not Converged Contingencies | FALSE | outage | NotConvCont | %csv converged |  | 3 | [14 empty] | 1700
| ConflContOuts | Voltage Violations (AC Mode only) | FALSE | outage | VoltViol | %csv voltviol |  | 3 | [14 empty] | 1700
| ConflContOuts | Voltage Violations - Report Manager (AC Mode only) | FALSE | outage | CustomVoltViol | %csv custVoltViol |  | 3 | [14 empty] | 1700
|  | SRDcalc | TRUE |  | GRDcalcTemp |  |  | 0 | [14 empty] | 4300
| EvalConflCont | Branch Flows | FALSE | outage | StudyFlows | %csv branflows |  | 3 | [14 empty] | 6500
| EvalConflCont | Branch Flows - Report Manager | TRUE | outage | CustomStudyFlows | %csv custBranFlows |  | 3 | [14 empty] | 6500
| EvalConflCont | Summary of Conflicting Contingencies | TRUE | outage | Summary | %csv SumConflict |  | 3 | [14 empty] | 6500
| EvalConflCont | Generation Complete Dispatch | FALSE | outage | SCD_Disp | %csv disp |  | 3 | [14 empty] | 1700
| EvalConflCont | Generation Adjustment Redispatch | FALSE | outage | SCD_Adjust | %csv adjust |  | 3 | [14 empty] | 1700
| EvalConflCont | Phase Shifters | FALSE | outage | SCD_PARs | %csv pars |  | 3 | [14 empty] | 1700
| EvalConflCont | Interfaces/Flowgates | FALSE | outage | SCD_Fgates | %csv FgateFlows |  | 3 | [14 empty] | 1700
| EvalConflCont | Binding Constraints | FALSE | outage | SCD_Binding | %csv BindingConstraints |  | 3 | [14 empty] | 1700
| EvalConflCont | Bidder Impact on new Outage Constraints | FALSE | outage | BidImpact | %csv BidImpact |  | 3 | [14 empty] | 1700
| EvalConflCont | Not Converged Contingencies | TRUE | outage | NotConvCont | %csv converged |  | 3 | [14 empty] | 1700
| EvalConflCont | Voltage Violations (AC Mode only) | FALSE | outage | VoltViol | %csv voltviol |  | 3 | [14 empty] | 1700
| EvalConflCont | Voltage Violations - Report Manager (AC Mode only) | FALSE | outage | CustomVoltViol | %csv custVoltViol |  | 3 | [14 empty] | 1700
|  | GRD_Dfax | TRUE |  | GRDcalcTemp |  |  | 0 | [14 empty] | 4300
|  | PRD_Dfax | TRUE |  | GRDcalcTemp |  |  | 0 | [14 empty] | 4300
| GenCADeliverability | CAISO GD Loading Summary | TRUE | customApps CAISO CAISO_GD | CAISOGenDelivFgLoad | %csv GDSummary |  | 3 | [14 empty] | 1000
| GenCADeliverability | Generator Summary inside 5% Dfax Circle | TRUE | customApps CAISO CAISO_GD | 5PcntDfaxCircle | %csv show5PcntDfaxCircle |  | 3 | [14 empty] | 1000
|  | SCDcalc | TRUE |  | GRDcalcTemp |  |  | 0 | [14 empty] | 4300
|  | SCD_Dfax | TRUE |  | GRDcalcTemp |  |  | 0 | [14 empty] | 4300
| ConvScrOuts | Outage Convergence Summary | TRUE | outage | ORA_OutConv | %csv outConvSum |  | 3 | [14 empty] | 6500
|  | AMB_Unfixable | TRUE |  | AMB_Unfixable |  |  | 3 | [14 empty] | 1000
|  | NE_MonthlyConstraints | TRUE |  | NE_MonthlyConstraints |  |  | 0 | [14 empty] | 1700
| NEOptOverlapReps | Flowgate Loadings - Overlapping Impacts | TRUE | nemis optoverlap | NE_FgLoadOpt_Olap | %csv optFgates |  | 4 | [14 empty] | 2300
| NEOptOverlapReps | Reference Dispatch Binding Flowgates – Overlapping Impacts | TRUE | nemis optoverlap | NE_FgBindOpt_Olap | %csv optBind |  | 4 | [14 empty] | 2300
| NEOptOverlapReps | Violation Summary - Overlapping Impacts | TRUE | nemis optoverlap | NE_FgOverOpt_Olap | %csv optOver |  | 4 | [14 empty] | 2300
|  | ConWizardResuls | TRUE |  | ConWizardResuls |  |  | 0 | [14 empty] | 3500
|  | MonSingleBranch | TRUE |  | MonSingleBranch |  |  | 0 | [14 empty] | 3500
| NEOptMISReps | Screening Summary (non-optimal mode only) - MIS | FALSE | nemis mis | NE_Screen_MIS | %csv screen |  | 5 | [14 empty] | 2300
| NEOptMISReps | Flowgate Loadings - MIS | TRUE | nemis optmis | NE_FgLoadOpt_MIS | %csv optFgates |  | 4 | [14 empty] | 2300
| NEOptMISReps | Reference Dispatch Binding Flowgates – MIS | TRUE | nemis optmis | NE_FgBindOpt_MIS | %csv optBind |  | 4 | [14 empty] | 2300
| NEOptMISReps | Violation Summary (optimal mode only) - MIS | TRUE | nemis optmis | NE_FgOverOpt_MIS | %csv optOver |  | 4 | [14 empty] | 2300
|  | ConSingleBranch | TRUE |  | ConSingleBranch |  |  | 0 | [14 empty] | 3500
| NESCDdetails | List of Flowgates and Flows | TRUE | sced | SCD_ContFGates | %csv Lfgate |  | 3 | [14 empty] | 1700
| NESCDdetails | Binding Constraints and Shadow Prices | TRUE | sced | SCD_Binding | %csv binding |  | 3 | [14 empty] | 1700
| NESCDdetails | Adjusted Bidders | TRUE | sced | SCD_Adjusted | %csv adjusted |  | 3 | [14 empty] | 1700
| NESCDdetails | Complete dispatch for all bidders | TRUE | sced | SCD_Dispatch | %csv dispatch |  | 3 | [14 empty] | 1700
| NESCDdetails | Phase Shifters | TRUE | sced | SCD_PARs | %csv pars |  | 3 | [14 empty] | 1700
|  | equip | TRUE |  | AuxEquip |  |  | 2 | [14 empty] | 1000
|  | ACThermal | TRUE |  | ACThermal |  |  | 3 | [14 empty] | 5200
|  | INCH_Log | TRUE |  | INCH_Log |  |  | 0 | [14 empty] | 8390
|  | PROGRESS_Log | TRUE |  | PROGRESS_Log |  |  | 0 | [14 empty] | 8390
| CaseMergeReports | Merge Summary | TRUE | CaseMergeTools | MergeSummary | %csv MergeSummary |  | 0 | [14 empty] | 1300
| CaseMergeReports | Conflicting Buses | TRUE | CaseMergeTools | ConfltBuses | %csv ConfltBuses |  | 0 | [14 empty] | 1300
| CaseMergeReports | Conflicting Ties | TRUE | CaseMergeTools | ConfltTies | %csv ConfltTies |  | 0 | [14 empty] | 1300
| CaseMergeReports | External Ties | TRUE | CaseMergeTools | ExternalTies | %csv ExternalTies |  | 0 | [14 empty] | 1300
|  | ModProjectEquip | TRUE |  | ModProjectEquip |  |  | 3 | [14 empty] | 8380
|  | Project_Log | TRUE |  | Project_Log |  |  | 0 | [14 empty] | 8380
| MonConWzrd | Report Filtered Contingencies | TRUE |  | Report Filtered Contingencies |  |  | 3 | [14 empty] | 8380
| MonConWzrd | Create Single Branch Contingencies | FALSE |  | Create Single Branch Contingencies |  |  | 3 | [14 empty] | 8380
| MonConWzrd | Create Generator Outage Contingencies | FALSE |  | Create Generator Outage Contingencies |  |  | 3 | [14 empty] | 8380
| MonConWzrd | Create Single Branch Monitor File | FALSE |  | Create Single Branch Monitor File |  |  | 3 | [14 empty] | 8380
| MonConWzrd | Create Open End Branch (P21) Contingencies | FALSE |  | Create Open End Branch (P21)Contingencies |  |  | 3 | [14 empty] | 8380
| MonConWzrd | Create Shunt Outage (P14) Contingencies | FALSE |  | Crease Shunt Outage (P14) Contingencies |  |  | 3 | [14 empty] | 8380
|  | crossCompareVoltViol | TRUE |  | crossCompareVoltViol |  |  | 5 | [14 empty] | 6150
|  | crossCompareBranchViol | TRUE |  | crossCompareBranchViol |  |  | 5 | [14 empty] | 6150
|  | crossCompareVoltViolPivot | TRUE |  | crossCompareVoltViolPivot |  |  | 5 | [14 empty] | 6150
|  | crossCompareBranchViolPivot | TRUE |  | crossCompareBranchViolPivot |  |  | 6 | [14 empty] | 6150
|  | retrScensCC | TRUE |  | retrScensCC |  |  | 5 | [14 empty] | 1000
|  | ssERISgen | TRUE |  | ssERISgen |  |  | 3 | [14 empty] | 1000
|  | Bind | TRUE |  | Bind |  |  | 0 | [14 empty] | 1000
|  | LoadsInDifferentAreas | TRUE |  | LoadsInDifferentAreas |  |  | 0 | [14 empty] | 1000
| AMBReps | Load Forecast | TRUE | amb data | AMB_LoadFCast | %csv load |  | 3 | [14 empty] | 1000
| AMBReps | Control Area Dispatch Blocks | TRUE | amb data | AMB_Block | %csv block |  | 3 | [14 empty] | 1000
| AMBReps | Detailed report for generators participation in Dispatch Block | TRUE | amb data | AMB_Generat | %csv generat |  | 3 | [14 empty] | 1000
| AMBReps | Generator SDX events summary | TRUE | amb data | AMB_SDXGenSum | %csv gensum |  | 3 | [14 empty] | 1000
| AMBReps | Generator SDX events schedule by snapshot | TRUE | amb data | AMB_SDXGenSched | %csv gensched |  | 3 | [14 empty] | 1000
| AMBReps | Branch SDX events summary | TRUE | amb data | AMB_SDXBranSum | %csv bransum |  | 3 | [14 empty] | 1000
| AMBReps | Branch SDX events schedule by snapshot | TRUE | amb data | AMB_SDXBranSched | %csv bransched |  | 3 | [14 empty] | 1000
| AMBReps | 3W Transformers SDX events summary | TRUE | amb data | AMB_SDX3WSum | %csv 3Wsum |  | 3 | [14 empty] | 1000
| AMBReps | 3W Transformers SDX events schedule by snapshot | TRUE | amb data | AMB_SDX3WSched | %csv 3Wsched |  | 3 | [14 empty] | 1000
| AMBReps | Transactions summary | TRUE | amb data | AMB_TranSum | %csv transum |  | 3 | [14 empty] | 1000
| AMBReps | Transaction schedule by snapshot | TRUE | amb data | AMB_TranSched | %csv transched |  | 3 | [14 empty] | 1000
| AMBReps | Financial Obligation Schedule by Snapshot | TRUE | amb data | AMB_CapResSched | %csv capres |  | 3 | [14 empty] | 1000
| AMBReps | Subsystem Financial Obligation Summary by Snapshot | TRUE | amb data | AMB_CapResSummary | %csv crsum |  | 3 | [14 empty] | 1000
| AMBReps | Subsystem Financial Obligation Details by Snapshot | TRUE | amb data | AMB_CapResDetails | %csv crdet |  | 3 | [14 empty] | 1000
| AMBReps | Subsystem Generator SDX Events by Snapshot | TRUE | amb data | AMB_GenOutSubsystem | %csv gensub |  | 3 | [14 empty] | 1000
| AMBReps | EMS flows and flow bias (once AMB model created) | TRUE | amb data | AMB_EMS | %csv emsflow |  | 3 | [14 empty] | 1000
| AMBReps | Warnings List - SDX Load | TRUE | warn | Warn_SDXLoad | %csv loadSDX |  | 3 | [14 empty] | 1000
| AMBReps | Warnings List - SDX Generators | TRUE | warn | Warn_SDXGen | %csv genSDX |  | 3 | [14 empty] | 1000
| AMBReps | Warnings List - SDX Branches | TRUE | warn | Warn_SDXBran | %csv branSDX |  | 3 | [14 empty] | 1000
| AMBReps | Warnings List - SDX 3-Winding | TRUE | warn | Warn_SDX3Wind | %csv 3windSDX |  | 3 | [14 empty] | 1000

## Main (hidden)
EnginePID/HWnd | InputBox | DefaultValue | Page | InputBox/txtFlgFile | CVParam/Parameters | FindRepParam | frmSelectArea | frmSelectArea | frmSelectArea | frmSheetListMulti/AddHistory/FindBuses/frmWorstVio |  | frmRedsptCalc_NE_rev |  |  |  | DetChaSS | frmNEMIS |  | Def_names_numb/frmConINCH |  | frmEvalStudyOuts | frmContN11/_new | frmContN11/_new | Compare | DataEditorSelectedRows | GenDataEditor | GenDataEditorSel | LoadDataEditor | LoadDataEditorSel | BusDataEditor | BusDataEditorSel | BranchDataEditor | BranchDataEditorSel | PARsDataEditor | PARsDataEditorSel | TieDataEditor | TieDataEditorSel | AreaSumEditor | AreaSumEditorSel | TransfmrDataEditor | TransfmrDataEditorSel | TieDbDataEditor | TieDbDataEditorSel | BranchDbDataEditor | BranchDbDataEditorSel | InputINCHfiles | InputINCHfiles | InputINCHfiles | CHANGEFiles | frmDESaveNew | frmExlude | frmACCont | LFCaseSelected(BusUtilitiesReports) |  | frmFgateOptions | DefaultValue | Details/Chart parameters | frmOptions | DefaultValue | frmOptCont | frmOptContTrL | frmOptSolve | reserved | frmDiagram | frmDiagram(colmn nn) | frmDiagram | frmDiagram | frmDiagram(colmn nn) | frmDiagram | frmDiagram (options) | frmDiagram (options) | frmAMBOpts/frmCaskAnOpts | DefaultValue |  | StartDay | StartTime | EndMonth | EndDay | EndTime | StartYear | EndYear | MonthNN | MonthDays | frmOptSCED | DefaultValue | Scenario1 | CompSum | ImportOptions | ImportOptions | ImportOptions | ImportOptions | InputLFfiles | InputLFfiles | LastScenarioSettings | LastScenarioSettings(reserved) | frmNE_revOpts | DefaultValue | NE_revDoneflag | frmNE/frmOptPP/frmDfaxRepUpd/frmSelectPaths | DefaultValue | frmGenDelOpts | DefaultValue | frmTrLimOpts/TrLimACOpts/frmPVSA | DefaultValue | frmAnCutoffs/frmAZdiagram/frmAnCutoffs2 | DefaultValue | frmCreateWorkbook/MonConWzrd | DefaultValue | frmNE_revMOpts/frmScale2 | DefaultValue | frmPVcurves | DefaultValue | frmAnCutoffs1/RepManager | DefaultValue | frmOutEditor/Add | DefaultValue | frmOptN11 | DefaultValue | frmSelectAreaNew | frmSelectAreaNew | frmSelectAreaNew | frmSelectPaths | frmSelectPaths | frmSelectPaths | frmSelectPaths | frmSelectPaths | frmSelectPaths | MultiCoreN11 | frmMultiCaseCreate | (area - no impact) | frmAZdiagram | frmAZdiagram | (connect - no impact) | frmAZdiagram | (area - impact) | frmAZdiagram | (connect - impact) | frmAZdiagram | (zone - no impact) | frmAZdiagram | frmMISO_ERIS1 | frmMISO_ERIS1 | ERIS1 sta | ERIS1 pgen_org | ERIS1 pgen | ERIS1 pmin | ERIS1 pmax | ERIS1 qmax | ERIS1 ID | MulticoreQV | MulticoreQV | frmBatch_DB_upd | frmBatch_DB_upd | YAML
0 | optCAmode2 | TRUE | 1 |  |  | TRUE |  | 101,102,103,104,105,106,107,108,201,202,205,206,207,208,209,210,212,215,216,217,218,219,222,225,226,227,228,229,230,231,232,233,234,235,236,237,238,295,296,314,315,320,326,327,330,332,333,340,341,342,343,344,345,346,347,348,349,350,351,352,353,354,355,356,357,360,361,362,363,364,365,401,402,403,404,405,406,407,409,411,412,415,416,419,421,426,427,438,502,503,504,506,515,520,523,524,525,526,527,531,534,536,541,542,544,545,546,600,608,613,615,620,627,633,635,640,641,642,645,650,652,659,661,663,667,672,680,694,696,697,698,997,998,999,0 | ALL | txtAdd | _1 | STUDY_REGION |  |  |  | 277 | 0.1 |  | bus_names |  | 1 | 1 |  | BranchViol_split | 1,0 | Sta | 8 | Area | 4 | Volt | 3 | Section | 0 | RegSt | 14 | Section | 12 | AreaName | 2 | #tap | 13 | St | 13 | St | 13 |  |  | TRUE |  | C:\TARA_main\temp\INCH_temp1.inch | C:\TARA_main\temp\test1.exc | FALSE |  |  | optIgnSfgNo | TRUE |  | optBr1 | TRUE | TRUE | TRUE | TRUE |  | Bus# | 1 | TRUE | CKT | 6 | FALSE | 450 | position of the first bus | optSStype1 | TRUE | [10 empty] | optSCED | FALSE | Scenario2 | FALSE | [8 empty] | txtOpt1 | 0.03 | FALSE | optSCRDdis1 | TRUE | frmGenDeliv_txtss3 | ISO_NE_GENs | txtss3 | EAST_GEN | txORACut1 | 90 | opt1 | FALSE | txtLP1 | 10000 | optX1 | TRUE | txORACut1 | 90 | NM_EST |  | txORACut1 | 90 | [6 empty] | chkDupls | FALSE | C:\TARA_main\PathsSet3w12.csv | -1 | C:\TARA_main\SampleData\sample2014.raw | Gener | TRUE |  | MW Flow | TRUE | TDF | FALSE | TDF | FALSE | Gener | TRUE | [9 empty] | 20 | 2 | FALSE | Base | lfopt | solve
0 | txtSubFile | C:\Users\03419\Desktop\2022 Gas Study\2022 series_sub_EKPC-LGEE.sub | bStart | C:\Users\03419\Desktop\2022 Gas Study\2022 series_mon_EKPC-LGEE.mon | BusParam | BatchMode and Editor |  | 101_ISO-NE,102_NYISO,103_IESO,104_TE,105_NB,106_NS,107_CORNWALL,108_NF,201_APS,202_ATSI,205_AEP,206_OVEC,207_HE,208_DEI,209_DAY,210_SIGE,212_DEO&K,215_DLCO,216_IPL,217_NIPS,218_METC,219_ITCT,222_CE,225_PJM,226_PENELEC,227_ME,228_JCPL,229_PL,230_PECO,231_PSEG,232_BGE,233_PEPCO,234_AE,235_DP&L,236_UGI,237_RECO,238_SMECO,295_WEC,296_MIUP,314_BREC,315_HMPL,320_EKPC,326_EES-EMI,327_EES-EAI,330_AECI,332_LAGN,333_CWLD,340_CPLE,341_CPLW,342_DUK,343_SCEG,344_SC,345_DVP,346_SOCO,347_TVA,348_GULF,349_SMEPA,350_PS,351_EES,352_YAD,353_SEHA,354_SERU,355_SETH,356_AMMO,357_AMIL,360_CWLP,361_SIPC,362_GLH,363_LGEE,364_OMUA,365_SMT,401_FPL,402_DEF,403_FTP,404_GVL,405_HST,406_JEA,407_KEY,409_LWU,411_FMPP,412_SEC,415_TAL,416_TECO,419_RCU,421_TCEC,426_OSC,427_OLEANDER,438_IPP-REL,502_CLEC,503_LAFA,504_LEPA,506_MJMEUC,515_SWPA,520_AEPW,523_GRDA,524_OKGE,525_WFEC,526_SPS,527_OMPA,531_MIDW,534_SUNC,536_WERE,541_KCPL,542_KACY,544_EMDE,545_INDN,546_SPRM,600_XEL,608_MP,613_SMMPA,615_GRE,620_OTP,627_ALTW,633_MPW,635_MEC,640_NPPD,641_HAST,642_GRIS,645_OPPD,650_LES,652_WAPA,659_BEPC-SPP,661_MDU,663_BEPC-MISO,667_MH,672_SPC,680_DPC,694_ALTE,696_WPS,697_MGE,698_UPPC,997_WBDC-WECC,998_ERCOT,999_WECC,0 | ALL | optSuf | TRUE |  |  |  |  | 2 | 10 |  | FALSE |  | 1 | 1 |  |  | 14,15,16,17,18,19,20,21,0 | PGen | 9 | Zone | 5 | Area | 0 | St | 14 | TAPRat | 15 | St | 14 | DesInter | 17 | CurTarV | 14 | R | 19 | R | 19 | [5 empty] | 2 | FALSE | LFCasesSelected(BusAnalysisReports) | LFCasesBusesSelected(BusAnalysisReports) | optIgnSfgYes | FALSE |  | optBr2 | FALSE | FALSE | FALSE | FALSE |  | BusName | 2 | TRUE | MW | 32 | TRUE | TRUE | UpdDoneFlag | optSStype2 | FALSE | FALSE | [9 empty] | optSCED1 | FALSE | Scenario1 | FALSE | [8 empty] | txtOpt2 | 3 | GenDevDoneflag | optSCRDdis2 | FALSE | frmGenDeliv_txtss4 | ISO_NE_Load | txtss4 | CENTRAL_LOAD | txORACut2 | 5 | opt2 | TRUE | txtLP2 | 0.05 | optX2 | FALSE | txORACut2 | 5 | ALPS |  | txORACut2 | 5 | [6 empty] | enACVer | TRUE | 4 | -1 |  | Load | TRUE |  | MVar Flow | TRUE | MW_Impact | FALSE | FlowChn(MW) | FALSE | Load | TRUE | [9 empty] | 22 | K20 | TRUE | Scenario1 | 1 | busMismToler | txtLF1 |  |  |  | # Bus Mismatch tolerance
SCED Done Flag | txtMonFile | C:\Users\03419\Desktop\2022 Gas Study\2022 series_mon_EKPC-LGEE.mon | FALSE |  | 1,0 | 6 | shapshots |  |  | optPre | FALSE | [7 empty] | number |  | FALSE | FALSE |  |  | 14,15,16,17,0 | QGen | 11 | St | 7 | Zone | 0 | R | 20 | PSAngleDeg | 16 | R | 20 | Slack Bus# | 18 | voltMin | 15 | X | 20 | X | 20 |  |  |  |  | 30 | FALSE | TRUE | 0 |  | txtMax1 | 10 |  | optBr3 | FALSE | FALSE | FALSE | FALSE |  | Volt | 3 | TRUE | MVAR | 33 | FALSE | TRUE | HideBrDataFlag | optSStype3 | FALSE | [10 empty] | optSCED2 | TRUE | two | [9 empty] | txtOpt3 | 1 | FALSE | SelBid | 5 | frmGenDeliv_txtLoadCOff | 85 | txtPen1 | 10000 | txORACut3 | 2 | chkFlows | TRUE | txtLP3 | 0.05 | optX11 | FALSE | txORACut3 | 2 | 345 |  | txORACut3 | 2 | [6 empty] | txtTrlTestLev | 10000 | 3 | -1 | C:\TARA_main\SampleData\sample2014_test.raw | Losses | FALSE |  | numTies | FALSE |  |  | FlowRes(MW) | FALSE | Losses | TRUE | [10 empty] | K22 | TRUE |  | 1 | MaxIterLF | txtLF2 |  |  |  | # Max N of iterations in DC
FALSE | txtConFile | C:\Users\03419\Desktop\2022 Gas Study\Option 3A N-1-1 con file.con | bControlChanged | Misc Flags | mCreateLFcont | 13 |  |  |  | optMove | TRUE | [7 empty] | FALSE |  | 1 | FALSE |  |  | 26951,26952,26953,26954,26955,26956,0 | Pmin | 12 | Pconst | 12 | CodeBTyp | 0 | X | 21 | PSAngleMin | 20 | X | 21 |  |  | voltMax | 16 | Charg | 21 | Charg | 21 | C:\TARA_main\solution_analysis_1\pre_cont_lock.inch |  |  |  | FALSE | FALSE | FALSE | sample2014 Redispatched WITH PARs | 5 , | txtMax2 | 50 |  | optBr4 | FALSE | FALSE | FALSE | FALSE |  | Ar | 4 | FALSE | MVA | 34 | FALSE | Courier New | BusFont | optSStype4 | FALSE | [10 empty] | optSCED3 | FALSE | FALSE | [9 empty] | txtOpt4 | 0 | TrLimDoneflag | SelFG | 929 | optPJM | TRUE | txtPen2 | 1000 | txORACut11 | 70 | chkVolt | TRUE | txtLP4 | 3 | optY1 | FALSE | txORAVolt1 | 0.002 | NYPP |  | txORACut11 | 60 | [6 empty] | txtTrlPSCons | 1 | 4 |  |  | IntTies | TRUE |  | TieKV | FALSE |  |  |  |  | IntTies | FALSE | [9 empty] | 33 |  | TRUE | Scenario21 | 2 | useFlatStart | optLFflat2 | optLFflat1 |  |  | # Use flat start during LF
CommandRecord | txtExcFile | Please define the correct path here | FALSE | 2 | 69,80,7,96,70,66,43,96,0 | 2 |  |  |  | optCopy | FALSE | [7 empty] | C:\Results\conINCH1 |  |  | 1 |  |  | 4,0 | Pmax | 13 | Qconst | 13 | Ownr | 0 | Charg | 0 | PsAngleMax | 21 | Charg | 22 |  |  | Ratio | 17 | ShuntGFrom | 24 | ShuntGFrom | 24 |  |  |  |  | FALSE | TRUE | FALSE | sample_new-split-shunts1.raw | 102 105 108 110 , | txtMax3 | 20 |  | txtBrM | 100 | 100 | 100 | 100 |  | Zn | 5 | FALSE | MW_loss | 35 | FALSE | 8 | BusSize | optInc1 | FALSE | [10 empty] | optSCRD | TRUE | 0 | [9 empty] | txtss1 | ISO_NE_Load | FALSE | SelLF |  | optPJM1 | TRUE | txtPen3 | 0.0001 | txORACut22 | 5 | chkNotCC | TRUE | txtLP5 | 2000 | optY2 | TRUE | txORAVolt2 | 0.002 | txtTicketNN | 1-08000075 | txORACut22 | 5 | [6 empty] | txtTrlPS1 | 0.03 | 5 |  |  | IntExtLd | FALSE | [7 empty] | IntExtLd | FALSE | [9 empty] | 35 | K10,11,12 | \\DESKTOP-1J8ML0V\EnfTest\batch11\TARA.db | Scenario23 | 1 | ZeroImpThr | txtLF6 |  |  |  | # Zero impedance threshhold in PU
FALSE | txtFlgFile | C:\Users\03419\Desktop\2022 Gas Study\2022 series_mon_EKPC-LGEE.mon | bAreaZone | PJMGD available | 30 | TRUE |  |  |  | txtWorkName | C:\TARA_main\ERIS.xlsb | [9 empty] | TRUE | 50 |  |  | 19,20,21,22,23,0 | Qmin | 15 | Pcurrt | 0 |  |  | ShuntGFrom | 0 | PSRegMinMW | 22 | ShuntGFrom | 25 |  |  | RatioTo | 18 | ShuntBFrom | 25 | ShuntBFrom | 25 |  |  |  |  | C:\TARA_main\temp\INCH_temp1.inch | 1 | 95 | sample_new-split-shunts.raw | 137451, | txtMax4 | 5000 |  | optCr1 | FALSE | FALSE | FALSE | FALSE |  | PU | 11 | TRUE | MVAR_loss | 36 | FALSE | TRUE | BusBold | optInc2 | TRUE | [10 empty] | optSCRD1 | FALSE | [10 empty] | txtHarm | 0.01 | NE_revMDoneflag | txtLoadCOffSCED | 90 | optPJM2 | FALSE | txtPen4 | 3 | txORACut33 | 2 | chkFg | TRUE | txtMulti1 | 100 | txtSheetName | PVcurves142 | txORAShaP | 30 | txtOutName | 1-110011433403C-32M-0 | txORACut33 | 2 | [6 empty] | txtTrlPS2 | 5 | 5 |  |  | DesInter | FALSE | [7 empty] | genMaxOnl | FALSE | [9 empty] | 8 |  | C:\TARA_main\temp |  | 1 | lowVoltCutOffLoad | txtLF7 |  |  |  | # Scale load down if voltage becomes
C:\TARA_main\test.dir | txtRawData | C:\Users\03419\Desktop\2022 Gas Study\Alt 3A\2032S_gas_alt#3a_212mw.raw | FALSE | FALSE | C:\TARA_main\temp\test.raw | TRUE | shapshots for Fgate analysis |  |  | txtSScen | test | [9 empty] | FALSE | optBr1 | TRUE |  | 11,0 | Qmax | 16 | Qcurrt | 0 |  |  | ShuntBFrom | 0 | PSRegMaxMW | 23 | ShuntBFrom | 26 |  |  | Rat_Min | 19 | ShuntGTo | 26 | ShuntGTo | 26 |  |  |  |  | FALSE | 1 | FALSE | sample_new-split-shunts1.raw | 137451, | optCust1 | TRUE |  | optCr2 | TRUE | TRUE | TRUE | TRUE |  | KV | 12 | FALSE | R | 20 | FALSE | Courier New | BrFont | txtPar1 | 8760 | [10 empty] | optSCRD2 | TRUE | [10 empty] | optHaIn1 | FALSE | FALSE | optSCRDdis3 | TRUE | optMISO | FALSE | chkPen1 | TRUE | txORAVolt1 | 0.002 | optCase | FALSE | txtMulti2 | 100 | chkBaseCase | FALSE | txORAShaP2 | 1000 | optON | TRUE | txORAVolt1 | 0.002 | [6 empty] | chkTrlPS1 | FALSE |  |  |  | genMaxOnl | FALSE | [7 empty] | genMaxInOffl | FALSE | [9 empty] | 545 |  | TRUE | Scenario6 | 1 | maxVoltChangeInit | txtLF10 |  |  |  | # Max volt magnit change in PU iteration - init stage
FALSE | optAppl1 | FALSE | nnTARAapp | MISOGD available | FALSE | BatchProcessMultiTRL_1 |  |  |  | optNsave | TRUE | [9 empty] | TRUE | optBr2 | FALSE |  | 3,0 | %Share | 17 | PAdmit | 0 |  |  | ShuntGTo | 0 |  |  | ShuntGTo | 27 |  |  | Rat_Max | 20 | ShuntBTo | 27 | ShuntBTo | 27 |  |  |  |  | TRUE |  | TRUE | sample_new-split-shunts.raw | 137455, | optCust2 | FALSE |  | optCr3 | FALSE | FALSE | FALSE | FALSE |  | An | 13 | FALSE | X | 21 | FALSE | 8 | BrSize | txtPar2 | 1096 | [10 empty] | txtss | AllGen | [10 empty] | optHaIn2 | FALSE | TrLimACDoneflag | chkEnSeqEval | FALSE | chkAC | FALSE | txtLP1 | 10000 | txORAVolt2 | 0.002 | optOutage | TRUE | chkPen3 | FALSE | optY4 | FALSE | txORACut222 | 100 | optOFF | FALSE | txORAVolt2 | 0.002 | [6 empty] | txtTrlTestLevNew | 2000 |  |  |  | genMaxInOffl | FALSE | [7 empty] | #Buses | FALSE | [9 empty] | 546 |  |  | Scenario7 | 1 | maxAngleChangeInit | txtLF11 |  |  |  | # Max volt angle change in radians iteration - init stage
AC Done Flag | optAppl2 | FALSE | 0 | FALSE |  | PV Analysis |  |  |  | optSave | FALSE | [9 empty] | TRUE | optBr3 | FALSE |  | 20,0 | CtrlB# | 18 | QAdmit | 0 |  |  | ShuntBTo | 0 |  |  | ShuntBTo | 28 |  |  | Step | 21 | RateA | 28 | RateA | 28 |  |  |  |  | FALSE |  | FALSE | day_09_2007_03_31_00.raw | 10009, | optCust3 | FALSE |  | optCr4 | FALSE | FALSE | FALSE | FALSE |  |  |  |  | Chr | 22 | FALSE | TRUE | BrBold | txtPar3 | 104 | [10 empty] | chkPhSh | FALSE | [10 empty] | optHaIn3 | TRUE | FALSE | chkEnEnf | FALSE | txtAC | 85 | txtLP2 | 0.05 | txORAShaP | 30 | txtWorkName | C:\TARA_main\testBook9.xlsb | chkPen1 | TRUE | optY3 | FALSE | txORACut333 | 20 | optS1 | FALSE | txORAShaP | 30 | [6 empty] | chkTrl_lim | FALSE |  |  |  | #Buses | FALSE | [7 empty] | #Ties | FALSE | [9 empty] | 537 |  |  |  | 1 | maxVoltChangeFinal | txtLF12 |  |  |  | # Max volt magnit change in PU iteration - final stage
TRUE | optAppl3 | TRUE | NE available | Latest Export File | C:\TARA_main\temp | PVSummary,PVVoltage,0 |  |  |  | txtSSFile | C:\TARA_main\TARAviewer_v700c_Options3.csv | [9 empty] | FALSE | txtBrM | 100 |  | 1,0 | VoltTarg | 21 |  |  |  |  | RateA | 29 |  |  | RateA | 29 |  |  | LinDropR | 22 | RateB | 29 | RateB | 29 |  |  |  |  | FALSE |  | FALSE | day_01_2007_03_23_00.raw | 3,4, | optN1No | TRUE |  | txtCrM | 100 | 100 | 100 | 100 |  | Equipment |  | TRUE | A | 23 | FALSE | FALSE | BusFontCnangeFlag | txtPar4 | 120 | [10 empty] | txtPen1 | 10000 | [10 empty] | optHaIn4 | FALSE | TrLimPrDoneflag | optEnf | TRUE | txtRTEP1 | 0 | txtLP3 | 0.05 | txORAShaP2 | 1000 | txtDir | C:\files\TARA_v510test\MISO_ORA_Feb17_2011\Ellendale_trans_outage_issues\results_520_05272011 | chkPen2 | FALSE | optY1 | FALSE | txtMonOpt1 | 10000 | optS2 | TRUE | txORAShaP2 | 1000 | [6 empty] | optLF11 | FALSE |  |  |  | #Ties | FALSE | [7 empty] | LoadNom | FALSE | [9 empty] | 567 |  |  |  | 1 | maxAngleChangeFinal | txtLF13 |  |  |  | # Max volt angle change in radians iteration - final stage
SCED/SCRD Save Flag | txtss1 | ALLGEN | FALSE |  | C:\TARA_main\PJMGD_StudyFiles\test11.raw | 6 |  |  |  | txtName | VIC* | [9 empty] | FALSE | optBr11 | TRUE |  |  | MBase | 32 |  |  |  |  | RateB | 30 |  |  | RateB | 30 |  |  | LinDropX | 23 | RateC | 30 | RateC | 30 |  |  |  |  | TRUE |  | FALSE | day_02_2007_03_24_00.raw | 3,4, | optN1Yes | FALSE |  | chkEmRat | FALSE | FALSE | FALSE | FALSE |  | BrThick |  | FALSE | B | 24 | FALSE | FALSE | BrFontCnangeFlag | txtPar5 | 200000 | [10 empty] | txtPen2 | 1000 | [10 empty] | optHaO1 | TRUE | FALSE | optMulti | FALSE | txtRTEP2 | 0 | txtLP4 | 3 | txORACut222 | 100 | optOneBook | FALSE | txtPen1 | 10000 | optInt | FALSE | txtMonOpt2 | 10000 | optS3 | FALSE | txORACut222 | 100 | [6 empty] | optLF22 | TRUE |  |  |  | LoadNom | FALSE | [7 empty] | LdInDifZone | FALSE | [9 empty] | 565 |  |  |  | 1 | numIterInit | txtLF14 |  |  |  | # Max iteration for initial stage
0 | txtss2 | ALLLOAD | TORA available | BusPathOptions | TRUE | FALSE |  |  |  | txtNum1 | 100000 | [9 empty] | FALSE | optBr21 | FALSE |  |  | RSource | 33 |  |  |  |  | RateC | 31 |  |  | RateC | 31 |  |  | MonitBus | 26 | Length | 31 | Length | 31 |  |  |  |  | FALSE |  |  | day_09_2007_03_31_00.raw | 10015 , | txtDfactcut | 0.05 | 0.05 | optConvYes | FALSE | FALSE | FALSE | FALSE |  | Rate |  | A | C | 25 | FALSE | TRUE | Equipment | txtPar6 | 10000 | [10 empty] | txtPen3 | 1 | [10 empty] | optHaO2 | FALSE | N11EnabParallel | txtMulti | 4 | txtAdLm1 | 0.071 | txtLP5 | 2000 | txORACut333 | 20 | optManyBooks | TRUE | txtPen2 | 1000 | optBran | TRUE | chkT1 | TRUE | optS4 | FALSE | txORACut333 | 20 | [6 empty] | optLF33 | FALSE |  |  |  | LdInDifAr | FALSE | [7 empty] | LdFrDifZone | FALSE | [9 empty] | 571 |  |  |  | 1 | MemFactor | txtMaxCont5 |  |  |  | # Sparse methods fill in allocation factor
Workbook path | txtss3 | EXPORT | FALSE | 0 | area 1,2,3,4 | FALSE |  |  |  | txtNum2 | 100006 |  |  |  |  | frmAdvFilter | headers | filters | filters | filters | TRUE | optBr31 | FALSE |  |  | XSource | 34 |  |  |  |  | RateD | 32 |  |  | RateD | 32 | [7 empty] | 37 |  |  |  |  | TRUE |  |  | day_01_2007_03_23_00.raw | 12013 | txtMWimpcut | 2 | 2 | optConvNo | TRUE | TRUE | TRUE | TRUE |  | MaxBrThick |  | 100 | TAPR | 17 | FALSE | TRUE | BrThick | txtPar7 | 10000 | [10 empty] | txtPen4 | 20 | [10 empty] | optHaO3 | FALSE | FALSE | txtEnf1 | localhost | txtAdLm2 | 465 | txtPen5 | 0.1 | txtMonOpt1 | 5 | optNoBook | FALSE | txtPen3 | 0.0001 | nContinue | 1 | chkT2 | TRUE | txtStartDate | 2012-07-07 16:00 | chkN11Compare | TRUE | [6 empty] | txtRawData | C:\TARA_main\SampleData2015\sample_Trlim2.raw |  |  |  | LdFrDifAr | FALSE | [7 empty] | shuntLoss | FALSE | [9 empty] | 572 |  |  |  | 1 | voltTolnUser | txtLF19 |  |  |  | # Voltage magnitude tolerance for volt. contr. 0 will be computed automat.
C:\Users\03599\Documents | txtss4 | REF | CAGenDel available | 300 |  | FALSE |  |  |  | optShow1 | FALSE |  |  |  |  | 64079 MT ROSE 120 64104 STEAMBT 120 1 1 | Cont ID |  |  |  | TRUE | txtBrM1 | 100 |  |  | RTran | 35 |  |  |  |  | Length | 0 |  |  | Length | 33 | [12 empty] | 59 |  |  | day_01_2007_03_23_00.raw | 12014 | txtRepcut | 1 | 1 | txtMaxCont1 | 15000 | 4000 | 4000 | 15000 |  |  |  |  | PSAng | 18 | FALSE | None | Rate | txtPar8 | 0.01 | [10 empty] | chkPen1 | TRUE | [10 empty] | optHaO4 | FALSE | AddCoresNumber | txtEnf2 | 10102 | txtAdLm3 | 1549 | txtPen9 | 200000 | txtMonOpt2 | 5 | txtDir1 | C:\TARA_main\temp | txtPen4 | 70 | txtSheetNameQV | QVcurve12 | chkT3 | TRUE | txtEndDate | 2012-07-07 17:00 | chkN11Speed | FALSE | [11 empty] | Slack Bus# | FALSE | [18 empty] | 601 |  |  |  | 0 | lowVoltAddQGen | chkQR1 |  |  |  | # Add Q at generator buses with voltage(0-no,1-yes)
Help | txtOutDef | C:\Users\03419\Desktop\2022 Gas Study\Option 3A N-1-1 con file.con | FALSE | TARAStudio |  | FALSE |  |  |  | optShow2 | TRUE | [5 empty] | Cont Name |  |  |  | 4 | optBr12 | TRUE |  |  | XTran | 36 | [5 empty] | 0 | [16 empty] | Test Project 1 |  |  | day_01_2007_03_23_00.raw | 12015 | txtGenNum | 20 | 20 | txtMaxCont1e | 60 | 60 | 60 | 60 | [7 empty] | 100 | MaxBrThick | chkPar1 | TRUE | [10 empty] | txtLP1 | 10000 | [10 empty] | txtHelp | -0.03 | 4 | txtEnf3 | c:\EnFuzion | txtAdLm4 | 3500 | optSR | TRUE | chkACcut0 | FALSE | txtDir2 | C:\TARA_main\temp | txtPen5 | 10000 | chkAddSh | TRUE | chkT4 | TRUE | txtEqStartDate | 2012-07-07 16:00 | optEvAll | TRUE | [11 empty] | SlackName | FALSE | [18 empty] | 602 |  |  |  | 1 | lowVoltCutOffQGen | txtQR1 |  |  |  | # Low voltage cutoff to add Qgen voltage becomes low
TRUE | txtDFc | 0.02 | MISO available | C:\TARA_main\TaraStudio2002_0_0_13\TaraStudio.exe | 35 | FALSE |  |  |  | chkIgn | FALSE |  |  |  |  | Crys | Monitored Facility |  |  |  | FALSE | optBr22 | FALSE |  |  | GenTap | 37 |  |  |  |  | Length | 0 | [16 empty] | Test Project 1 Phase 1 |  |  | day_01_2007_03_23_00.raw | 12016 | txtStrlev | 100 | 100 | optPhS1 | FALSE | FALSE | FALSE | FALSE |  |  |  |  | Status | 7 |  | FALSE | DoNotUseColorFlag | chkPar2 | TRUE | [10 empty] | txtLP2 | 0.05 | [10 empty] | optHeIn1 | TRUE | MultipleCaseCreator | chkShowRefe | TRUE | txtAdLm7 | 5 | optS | FALSE | optACcut0 | FALSE | chkEach | TRUE | txtPen6 | 50000 | chkAdj | TRUE | chkT5 | FALSE | txtEqEndDate | 2012-07-07 17:00 | optEvRan | FALSE | [11 empty] | Volt | FALSE | [18 empty] | 603 |  |  |  | 0 | highVoltReduceQGen | chkQR2 |  |  |  | # Reduce Q at generator buses with voltage below Qmin (0-no,1-yes)
TARA2201help.chm | txtMaxTotalChange | 10000 | FALSE | 0 | C:\TARA_main\temp\test.raw | TRUE |  |  |  | txtNameC | * |  |  |  |  | Crys | Fr Bus |  |  |  | TRUE | optBr32 | FALSE | [26 empty] | K2016-09-30 |  |  | day_01_2007_03_23_00.raw | 12017 | txtSysload | 85 | 85 | optPhS2 | TRUE | TRUE | TRUE | TRUE |  |  |  |  | MW_arrow | 8 |  | 345 | ColorRed | chkPar3 | FALSE | [10 empty] | txtLP3 | 0.05 | [10 empty] | optHeIn2 | FALSE | C:\TARA_main\cases | chkShowRegi | TRUE | txtAdLm8 | AB2 | optR | FALSE | optACcut1 | TRUE | chkAll | TRUE | txtPen7 | 10000 | txtSh1 | 100 | chkT6 | FALSE | txtTrOutNew | C:\TARA_main\Trans_Outage_new3.csv | txtRan1 | 24 | [11 empty] | SlackPGen | FALSE | [18 empty] | 604 |  |  |  | 1 | highVoltCutOffQGen | txtQR2 |  |  |  | # High Voltage cutoff to reduce Q for high voltage
no | txtMdsp1 | 1 | AMB available | 21824 | 16 | FALSE |  |  |  | txtNum1C | 100 |  |  |  |  | 49730 | Fr Name |  |  |  | FALSE | txtBrM2 | 100 | [26 empty] | Planned |  |  | day_01_2007_03_23_00.raw | 12018 | txtMaxchange | 10000 | 10000 | txtMaxCont2 | 35000 | 35000 | 35000 | 35000 | [7 empty] | 230 | ColorBlue | optTimeZone1 | TRUE | [10 empty] | txtLP4 | 3 | [10 empty] | optHeIn3 | FALSE | _inch | chkShowLoc | TRUE | chkIgnVio | TRUE | optNE | FALSE | optACcut2 | FALSE | optSubSys | FALSE | txtPen11 | 1000 | txtSh2 | 200 | chkT7 | FALSE | txtTrOutOld | C:\TARA_main\Trans_Outage_org - Copy.csv | txtRan2 | 24 | [11 empty] | SlackPmin | FALSE | [18 empty] | 569 |  |  |  | 0 | fixedQGenRelax | chkQR5 |  |  |  | # Relax Q at generators with Qmin=Qmax (0-no,1-yes)
not used | chkMdsp | FALSE | FALSE |  |  | TRUE |  |  |  | txtNum2C | 100 |  |  |  |  | 49730 | To Bus |  |  |  | FALSE | [28 empty] | Project Comment |  |  | day_01_2007_03_23_00.raw | 12019 | txtMinchange | 1000 | 1000 | txtMaxCont3 | 60000 | 40000 | 40000 | 60000 | [7 empty] | 115 | ColorGreen | optTimeZone2 | FALSE | [10 empty] | txtLP5 | 2000 | [10 empty] | optHeIn4 | FALSE | TRUE | txtPmax | 0 | txtssQ1 | QUEUEEXPORT | txtSend | 1 | optACcut3 | FALSE | optArea | FALSE | txtPen8 | 1 | txtSh3 | 300 | chkT8 | TRUE | optTrOutNew | TRUE | chkEnabParallel | FALSE | [11 empty] | SlackPmax | FALSE | [18 empty] | 570 |  |  |  | 0 | lowVoltAddShunt | chkQR3 |  |  |  | # Add Shunts at buses with low voltage(0-no,1-yes)
Corrective Switching | txtMdsp2 | 1 | SCED available |  |  | TRUE |  |  |  | optFg1 | FALSE |  |  |  |  | Cr | To Name |  |  |  | FALSE | [28 empty] | Phase Comment |  |  | day_01_2007_03_23_00.raw | 12020 | txtLoadcut | 0.15 | 0.15 | txtMaxCont4 | 10000 | 10000 | 10000 | 10000 | [7 empty] | FALSE | SetBusColorCnangeFlag | optTDFSave1 | TRUE | [10 empty] | txtPen5 | 10 | [10 empty] | optHeO1 | FALSE | TRUE | chkShowOpt | TRUE | txtssQ2 | QUEUEIMPORT | chkSend | FALSE | optAdd | FALSE | optZone | TRUE | txtPen9 | 1000000 | txtSh4 | 400 | chkT9 | TRUE | optTrOutOld | FALSE | txtMulti | 7 | [11 empty] | shuntLoss | FALSE | [18 empty] | 717 |  |  |  | 1 | lowVoltCutOffShunt | txtQR3 |  |  |  | # Low voltage cutoff to add shunts voltage becomes low
0 | txtMtimes | 5 | FALSE |  |  | TRUE |  |  |  | optFg2 | TRUE |  |  |  |  | Cr | CKT |  |  |  | FALSE | [28 empty] | QueueName |  |  | day_01_2007_03_23_00.raw | 12101 | optLoadDfactNo | TRUE | TRUE | txtMaxCont5 | 5 | 5 | 5 | 5 | [7 empty] | FALSE | SetDiagChecked | optTDFSave2 | FALSE | [10 empty] | txtPen9 | 200000 | [10 empty] | optHeO2 | FALSE | 32 | optZ | TRUE | optPJM_DS1 | FALSE | chkSendIgn | FALSE | optNew | TRUE | optBus | FALSE | optArea | TRUE |  |  | chkT10 | TRUE |  |  | txtScr1 | 0.05 | [31 empty] | 718 |  |  |  | 0 | highVoltReduceShunt | chkQR4 |  |  |  | # Remove fixed Shunt with high voltage(0-no,1-yes)
C:\TARA_main\temp\test.con | txtMaxHelp | 3 | bInpFileModified |  |  | FALSE |  |  |  | chkCSVs | FALSE |  |  |  |  | Cr | Section |  |  |  | <---> | [28 empty] | TRUE |  |  | day_01_2007_03_23_00.raw | 12103 | optLoadDfactYes | FALSE | FALSE | txtMaxCont6 | 15000 | 1000 | 1000 | 15000 | [7 empty] | TRUE |  | optTDFMet1 | TRUE | [10 empty] | optSCEDgen1 | FALSE | [10 empty] | optHeO3 | TRUE | N1 EnabParallel | optR | FALSE | optPJM_DS2 | TRUE | txtRec | 100 | chkShowImp | TRUE | txtSubSys | allgen | optZone | FALSE |  |  | chkT11 | TRUE |  |  | txtScr2 | 0.05 | [31 empty] | 752 |  |  |  | 1 | highVoltCutOffShunt | txtQR4 |  |  |  | # High Voltage cutoff to limit fixed injection
TARAviewer version | optMinMW | TRUE | FALSE |  |  | FALSE | [9 empty] | Crys | kVs | [32 empty] | FALSE |  |  |  |  | txtImploadcut | 2 | 2 | txtMaxCont7 | 2000000 | 2000000 | 2000000 | 2000000 | [7 empty] | FALSE |  | optTDFMet2 | FALSE | [10 empty] | optSCEDgen2 | TRUE | [10 empty] | optHeO4 | FALSE | FALSE | optSCRDdis1s | FALSE | optPJM_DS3 | FALSE | chkRec | FALSE | txtTrlTie1 | 3000 | txtArea | ,0 | optBus | FALSE |  |  | chkT12 | TRUE |  |  | txtScr3 | 5 | [31 empty] | 842
v2201 | optMinNumHelp | FALSE | FALSE |  |  | FALSE | [9 empty] | Crystal | Areas | [37 empty] | optStrlevNo | TRUE | TRUE | txtMaxCont8 | 100 | 60 | 60 | 100 | [7 empty] | FALSE |  | optTDFMet3 | FALSE | [10 empty] | optPnode | FALSE | [10 empty] | chkPhSh | FALSE | QVDoneflag | optSCRDdis2s | TRUE | chkAdLm | TRUE | chkSendDerate | FALSE | txtss33 | West | txtZone | 231,263,264,276,277,351,432,433,58,71,75,82,0 | optSubSys | FALSE |  |  | chkT111 | TRUE |  |  | optScr1 | FALSE | [31 empty] | 844 |  |  |  | lfopt | adj
INCH log | optMinMWHar | FALSE | FALSE |  |  | 0 | [9 empty] | Crystal | Rate Base (MVA) | [37 empty] | optStrlevYes | FALSE | FALSE | txtMaxCont9 | 30000 | 30000 | 30000 | 30000 | [9 empty] | txtHour1 | 1 | [10 empty] | optSubsys | TRUE | [10 empty] | chkPhSh1 | FALSE | FALSE | optSCRDdis3s | FALSE | txtACM1 | 95 | txtSendDerate | 0.05 | txtss44 | East | txtBus | ,0 | optNone1 | TRUE |  |  | chkT122 | TRUE |  |  | optScr2 | FALSE | [31 empty] | 869 |  |  |  | 1 | iterCheckVarLimitHotStart | txtLF3 |  |  |  | # Iteration to start generator VAR limit - hot start
FALSE | optMinMWHel | FALSE | FALSE |  |  | 4 | [9 empty] | Cedar Grove - Clifton | Rate Cont (MVA) | [37 empty] | optSortImp | FALSE | FALSE | optIgn | TRUE | TRUE | TRUE | TRUE | [9 empty] | txtHour2 | 1 | [10 empty] | chkPSD | FALSE | [10 empty] | chkPhSh2 | FALSE | LoadPrDoneflag | optSCRDdis4s | TRUE | txtACM2 | 110 | chkReport1 | FALSE | optColBr0 | FALSE | chkKV1 | TRUE | optArea1 | FALSE |  |  | chkT13 | TRUE |  |  | optScr3 | TRUE | [35 empty] | 1 | iterCheckVarLimitFlat | txtLF4 |  |  |  | # Iteration to start generator VAR limit - flat start
| txtRawData1 | Please define the correct path here | FALSE |  |  | ,3,4,5,6,5,6,7,8,3,4,3,4,3,4,3,4,3,4,3,4,3,4,3,4,3,4,3,4,3,4,3,4,3,4,3,4,3,4 | [9 empty] | Cedar | Base Flow (MVA) | [37 empty] | optSortSens | TRUE | TRUE | optHon | FALSE | FALSE | FALSE | FALSE | [9 empty] | txtHour3 | 10 | [10 empty] | chkDSR | FALSE | [10 empty] | txtPen1 | 10000 | FALSE | optDFRep1 | TRUE | txtMaxUnits | 30 | chkReport2 | FALSE | optColBr1 | FALSE | chkMW1 | TRUE | optZone1 | FALSE |  |  | chkT14 | TRUE |  |  | txtFlgFileName | Please define the correct path here | [35 empty] | 0 | PAR_AdjEnabledLF | chkLFPA |  |  |  | # Enable Phase Shifter Adjustment
| cboOptVersion | PTI RAW 34 | FALSE |  |  | 38 | [9 empty] | Cedar | Step 0 Cont Flow (MVA) | [37 empty] | txtss3 |  |  | optLF1 | FALSE | FALSE | FALSE | FALSE | [9 empty] | chkHour1 | TRUE | [10 empty] | optSCUnit1 | FALSE | [10 empty] | txtPen2 | 10000 | MISOTSRDoneflag | optDFRep2 | FALSE | txtss | PJM_MISO_EXPORT | txtssRep1 | allgen | optColBr2 | TRUE | chkMW2 | TRUE | optBus1 | FALSE |  |  | chkT15 | TRUE |  |  | chkIncl | FALSE | [35 empty] | 4 | areaInterAdjustEnabled | optLFarea1 | optLFarea2 | optLFarea3 | optLFarea4 | # Area interchange control
LF case formats (hard-coded!) | cboOptVersion1 | PTI RAW 34 | FALSE |  |  | FALSE | [9 empty] | Cedar Grov | Step 0 DC %Loading | [37 empty] | txtss4 |  |  | optLF2 | TRUE | TRUE | TRUE | TRUE | [9 empty] | optLong1 | FALSE | [10 empty] | optSCUnit2 | TRUE | [10 empty] | txtPen3 | 0.0001 | FALSE | optDFRep3 | FALSE | txtss1 | Swing | txtssRep2 | allload | optColAr0 | FALSE | txtKV1 | 100 | optSubSys1 | FALSE | 130750 COOPC345 345 148060 MARCCSC2 345 1 |  | chkT16 | TRUE |  |  | chkINCH | TRUE | [35 empty] | 0 | TAP_AdjEnabledLF | chkLFTA |  |  |  | # Enable TAP adjustment
PTI RAW 24-26 | chkConFile | FALSE | reserved |  |  | TRUE | [9 empty] | Cedar Grove - Clifton | Step 0 AC %Loading | [37 empty] | <---> |  |  | optLF3 | FALSE | FALSE | FALSE | FALSE | [9 empty] | optLong2 | TRUE | [10 empty] | optSCUnit3 | FALSE | [10 empty] | txtPen4 | 3 | FALSE | optDFRep4 | FALSE | txtss3 | PJMEXPORT | txtssRep3 | allgen | optColAr1 | FALSE | txtKV2 | 230 | optNone2 | FALSE | P1_F_L_ED-HA_P1: (Future) Eldorado - Harry Allen 525kV | 137562 | chkT17 | TRUE |  |  | chkOpt | FALSE | [35 empty] | 3 | shuntAdjEnabled | optLFSEn1 | optLFSEn2 | optLFSEn3 |  | # Enable shunt adjustment
PTI RAW 28 | chkExcFile | TRUE | reserved |  |  | FALSE | [9 empty] | 8797_Battlefield_SouthwestPowerPlant 161kV | Cascade Step | [40 empty] | optLF4 | FALSE | FALSE | FALSE | FALSE | [9 empty] | optLong3 | FALSE | [10 empty] | optIter1 | TRUE | [10 empty] | txtPen5 | 1000 | FALSE | txtEnteredBus | 6 | txtss4 | PJMIMPORT | chkPhSh | FALSE | optColAr2 | TRUE | txtKV3 | 345 | optArea2 | FALSE |  | 137730 | chkT18 | TRUE |  |  | chkRange | FALSE | [35 empty] | 0 | fixedToSwitched | chkConvShunts |  |  |  | # Convert all fixed shunts to discrete switched shunts
PTI RAW 29 | optN1ScNo | TRUE | TRUE |  |  | TRUE | [9 empty] | - | Cascade Flow (MVA) | [40 empty] | optLFP1 | FALSE | FALSE | FALSE | FALSE | [9 empty] | txtLong1 | 0.85 | [10 empty] | optIter2 | FALSE | [10 empty] | chkPen1 | TRUE |  | txtss_DR1 | East | txtss33 | MISOEXPORT | optSCUnit1 | FALSE | chkColAr1 | TRUE | txtKV4 | 500 | optZone2 | FALSE | DUVAL 230 |  | chkT21 | FALSE |  |  | chkRAS | FALSE | [35 empty] | 0 | DCLineAdjEnabled | chkLFDA |  |  |  | # Enable DC lines adjustment
PTI RAW 30 | optN1ScYes | FALSE | 1 |  |  | FALSE | [9 empty] | - | Cascade AC %Loading | [40 empty] | optLFP2 | TRUE | TRUE | TRUE | TRUE | [9 empty] | txtLong2 | 3 | [10 empty] | optIter3 | FALSE | [10 empty] | txtPen6 | 10000 |  | txtss_DR2 | West | txtss44 | MISOIMPORT | optSCUnit2 | TRUE | txtCon1 | 115 | txtLa1 | 1 | optBus2 | TRUE | FPL-FLA-0040-067_40 FLA CITY 138 5 FLACITY 230 1 |  | chkT22 | FALSE |  |  | chkExtra | FALSE | [35 empty] | 3 | showParAdj | optLFP1 | optLFP2 | optLFP3 |  | # Report PAR adjustments per iteration
PTI RAW 31 | optN1ScYes2 | FALSE | 2 |  |  | FALSE | [9 empty] | bedi | Radial Index | [40 empty] | optLFP3 | FALSE | FALSE | FALSE | FALSE | [9 empty] | txtLong3 | 3 | [10 empty] | txtIter1 | 20 | [10 empty] | txtPen7 | 10000 |  | txtss_DR3 | West | chkGD1AC | FALSE | optSCUnit3 | FALSE | txtCon2 | 230 | txtLa2 | 1 | optSubSys2 | FALSE | FPL-FLA-0040-128_119 TURKEY P 230 732 MCGREGOR 230 1 | 1658 | chkT23 | FALSE |  |  | txtNextra | 2 | [35 empty] | 3 | showTapAdj | optLFT1 | optLFT2 | optLFT3 |  | # Report TAP adjustments per iteration
PTI RAW 32 | optN1ScYes3 | FALSE | BatchProcessN1_DD3 |  | frmRedsptCalc (additional) | [10 empty] | bedi | Base MW Flow | [40 empty] | optLFT1 | FALSE | FALSE | FALSE | FALSE | [9 empty] | txtPeakF | 11 | [10 empty] | txtIter2 | 1 | [10 empty] | txtPen11 | 10000 |  | txtRawData_SCED | C:\TARA_main\NE\2021-22_FCA_Dynamic_Delist_final_corr\2021-22_FCA_Dynamic_Delist_final_corr_test1.raw | txtGD1LoadCOff | 80 | txtMulti1 | 100 | txtCon3 | 345 | txtLa3 | 1 | txtBus | 1,2,3,4,0 | FlaCity_TkyPt_230kV_40 FLA CITY 138 5 FLACITY 230 1 |  | chkT24 | FALSE |  |  | chkIntOpt | FALSE | [35 empty] | 3 | showShuntAdj | optLFS1 | optLFS2 | optLFS3 |  | # Report shunt adjustments per iteration
PTI RAW 33 | chkLayer | FALSE | 12 |  | frmRedsptCalc | frmRedsptCalc | frmRedsptCalc | frmRedsptCalc | frmRedsptCalc | frmRedsptCalc | frmRedsptCalc | frmRedsptCalc | frmRedsptCalc | frmRedsptCalc | frmRedsptCalc | bed | Cascade MW Flow | [40 empty] | optLFT2 | TRUE | TRUE | TRUE | TRUE | [9 empty] | txtPeakL | 21 | [10 empty] | txtMulti1 | 100 | [10 empty] | txtPen8 | 1000 |  | txtSubFile | C:\TARA_main\NE\2021-22_FCA_Dynamic_Delist_final_corr\2021-22_FCA_Dynamic_Delist_Subsystems_Round4_TeamID3.sub | optGD1PJM1 | TRUE | txtMulti2 | 100 | txtCon11 | 0.05 | txtLa4 | 1 | txtBus1 | 25,0 | 5 FLACITY 230 732 MCGREGOR 230 1_40 FLA CITY 138 5 FLACITY 230 1 |  | chkV1 | TRUE |  |  | chkAnOpt | FALSE | [35 empty] | 4 | showAreaInterAdj | optLFrepa1 | optLFrepa2 | optLFrepa3 | optLFrepa4 | # Area interchange reporting level
PTI RAW 34 | chkScrRepBaseVio | TRUE |  |  | 9 | 24087 MAGUNDEN 230 24153 VESTAL 230 2 1 _Line-9_ 24087 MAGUNDEN 230 24153 VESTAL 230 1 | 417.6 | 373 | 111.94 |  | 24087 MAGUNDEN 230 24153 VESTAL 230 2 1 | Line-9_ 24087 MAGUNDEN 230 24153 VESTAL 230 1 | 200 | 0 | 27 | bed | Base MVAR Flow | [40 empty] | optLFT3 | FALSE | FALSE | FALSE | FALSE | [9 empty] | txtOffPeakF | 3 | [10 empty] | txtMulti2 | 100 | [10 empty] | txtPen9 | 1000000 |  | txtMonFile | C:\TARA_main\NE\2021-22_FCA_Dynamic_Delist_final_corr\2021-22_FCA_Dynamic_Delist_Interfaces_only.mon | optGD1PJM2 | FALSE | txtACtrl5 | 0.03 | txtCon22 | 0.2 | txtLa5 | 1 | txtBus2 | 20112,20115,0 | 119 TURKEY P 230 732 MCGREGOR 230 1_40 FLA CITY 138 5 FLACITY 230 1 |  | chkV2 | TRUE |  |  | chkDD | FALSE | [35 empty] | 1 | busMismTolerAreaInter | txtLF17 |  |  |  | # Bus Mismatch tolerance to start area
PTI RAW 35 | chkCrScrReport | TRUE | 1 |  | 0 | 22771 BAY BLVD 230 22466 MLMS3TAP 230 1 1 _Base Case | 948.6 | 912 | 102.19 |  | 22771 BAY BLVD 230 22466 MLMS3TAP 230 1 1 | Base Case | 3 | 0 | 27 | bed | Cascade MVAR Flow | [40 empty] | optLFSEn1 | FALSE | FALSE | FALSE | FALSE | [9 empty] | txtOffPeakL | 5 | [10 empty] | txtMulti3 | 0 | [10 empty] | chkPen2 | FALSE |  | txtConFile | C:\TARA_main\NE\2021-22_FCA_Dynamic_Delist_final_corr\2021-22_FCA_Dynamic_Delist_Contigencies.con | optMISO1 | TRUE | txtACtrl6 | 100 | txtArea1 | -100 | chkMWAll | FALSE | chkSL1 | FALSE |  |  | chkV3 | FALSE |  |  | chkN11 | FALSE | [35 empty] | 1 | maxVarLimitsBusTypeChanges | txtLF9 |  |  |  | # Max times voltage controlled bus can type
PowerWorld AUX | txtScrMulti | 90 | Data Directory |  | 0 | 24087 MAGUNDEN 230 24101 OMAR 230 1 1 _Base Case | 589 | 598 | 96.97 |  | 24087 MAGUNDEN 230 24101 OMAR 230 1 1 | Base Case | 4 |  |  | wyl | Fr Base Volt | [40 empty] | optLFSEn2 | FALSE | FALSE | FALSE | FALSE | [9 empty] | chkLong1 | FALSE | [10 empty] | chkSCRD_dis | FALSE | [10 empty] | txtLP1 | 10000 |  | txtExcFile | C:\TARA_main\NE\2021-22_FCA_Dynamic_Delist_final_corr\CP2021-22_DDB_exclude_ACCONT.exc | optMISO2 | FALSE | txtACtrl7 | 10 | txtArea2 | 1000 | chkKVAll | FALSE | chkSL2 | FALSE |  |  | chkV4 | FALSE |  |  | optRAS | TRUE | [35 empty] | 1 | iterCheckVarLimitLast | txtLF8 |  |  |  | # Iteration to stop checking var limits
PSLF EPC 18 | txtNEMIS1 | 0.05 | 0 |  | 0 | 14355 PRESCOTT 115 14351 BAGDAD 115 1 1 _Base Case | 88.2 | 90 | 98.45 |  | 14355 PRESCOTT 115 14351 BAGDAD 115 1 1 | Base Case | 5 |  |  |  | Fr Cascade Volt | [40 empty] | optLFSEn3 | TRUE | TRUE | TRUE | TRUE | [9 empty] | optDur1 | FALSE | [10 empty] | txtSCRD_dis | 1200 | [10 empty] | txtLP2 | 0.05 |  | chkConFile | FALSE | optMISOst1 | FALSE | chkACtrl1 | FALSE | txtArea11 | 0.05 | txtKVCut | 200 | chkSL3 | FALSE |  |  | chkV5 | FALSE |  |  | optCS | FALSE | [35 empty] | 1 | maxAdjustIterVolt | txtLF18 |  |  |  | # Iteration to stop TAP and Shunt
PSLF EPC 19 | txtNEMIS2 | 5 |  |  | 0 | [6 empty] | Line-5_ 24301 BIG CRK1 230 24235 RECTOR 230 1 | 6 |  |  |  | To Base Volt | [40 empty] | chkConvShunts | FALSE | FALSE | FALSE | FALSE | [9 empty] | optDur2 | TRUE | [10 empty] | chkSCRD_count | FALSE | [10 empty] | txtLP3 | 0.05 |  | chkExcFile | TRUE | optMISOst2 | TRUE | chkACtrl2 | TRUE | txtArea22 | 0.2 | chkKVless | FALSE | optSE1 | FALSE |  |  | chkV6 | TRUE |  |  | txtKV1 | 100 | [35 empty] | 1 | deacFactRTap | txtLFS1 |  |  |  | # Voltage adjustment deacceleration factor
PSLF EPC 21 | txtNEMIS3 | 0 |  |  | 0 | 24151 VALLEYSC 500 24160 VALLEYSC 115 2 1 _Base Case | 509.8 | 560 | 90.1 |  | 24151 VALLEYSC 500 24160 VALLEYSC 115 2 1 | Base Case | 7 |  |  |  | To Cascade Volt | [40 empty] | optLFS1 | FALSE | FALSE | FALSE | FALSE | [9 empty] | txtDur | 50 | [10 empty] | txtLoadCut | 85 | [10 empty] | txtLP4 | 3 |  | txtVoltLimAdd_NE | 0 | chkMISOstBus | FALSE | txtACtrl2Num | 0.95 | chkBrThick | TRUE | txtMWCut | 100 | optSE2 | FALSE |  |  | chkV7 | TRUE |  |  | txtKV2 | 230 | [35 empty] | 1 | maxTapChange | txtLFT2 |  |  |  | # Max tap ratio change per iteration
EMS File | txtNEMIS4 | 0 |  |  | 0 | [6 empty] | 20101 BED 500 20103 OAK 500 1 | 8 |  |  |  | Base dAngle [deg] | [40 empty] | optLFS2 | TRUE | TRUE | TRUE | TRUE | [9 empty] | optSttime1 | TRUE | [10 empty] | optVVC1 | TRUE | [10 empty] | txtLP5 | 2000 |  | txtss_DR11 | East | txtTSR1 | 0.025 | txtACtrl2Num2 | 100 | txtMaxBrThick | 1000 | chkSaveFile | TRUE | optSE3 | TRUE |  |  | chkV8 | TRUE |  |  | txtKV3 | 345 | [35 empty] | 1 | voltAdjTrigger | txtLF15 |  |  |  | # Max voltage magnitude change to activate and Shunt adjustments
| txtNEMIS5 | 0.05 |  |  | 74 | 14917 RAINY 500 20105 DOOMS 500 1 _20103 OAK 500 20108 MCCOY 500 1 | 2292.6 | 1864 |  |  | 14917 RAINY 500 20105 DOOMS 500 1 | 20103 OAK 500 20108 MCCOY 500 1 | 9 |  |  |  | Cascade dAngle [deg] | [40 empty] | optLFS3 | FALSE | FALSE | FALSE | FALSE | [9 empty] | optSttime2 | FALSE | [10 empty] | optVVC2 | FALSE | [10 empty] | txtMulti1 | 100 |  | txtss_DR22 | West | txtTSR2 | 200 | optACtrl2Num | TRUE | chkN11ClosePr | FALSE | txtSaveFile | Please define the correct path here | optG1 | TRUE |  |  | chkV9 | TRUE |  |  | txtKV4 | 500 | [35 empty] | 1 | angleAdjTrigger | txtLF16 |  |  |  | # Max voltage angle change (in degrees) activate PAR and area interchange adjustments
| txtNEMIS6 | 0.05 |  |  | 66 | 20103 OAK 500 20108 MCCOY 500 1 _14917 RAINY 500 20105 DOOMS 500 1 | 2482.7 | 2226.4 |  |  | 20103 OAK 500 20108 MCCOY 500 1 | 14917 RAINY 500 20105 DOOMS 500 1 | 10 | [44 empty] | optLFrepa1 | FALSE | TRUE | TRUE | FALSE | [9 empty] | optSttime3 | FALSE | [10 empty] | optVVC3 | FALSE | [10 empty] | txtMulti2 | 100 |  | chkSubSys | FALSE | txtLoadCOff | 85 | optACtrl2Num2 | FALSE | chkUpscr | FALSE | chkExcIns | FALSE | optG2 | FALSE |  |  | chkV10 | TRUE |  |  | txtLa1 | 2 | [35 empty] | 3 | showBusTypeChan | optSh1 | optSh2 | optSh3 |  | # Show voltage controlled buses type changes
| txtNEMIS7 | 1 |  |  | 68 | 20101 BED 500 20103 OAK 500 1 _14917 RAINY 500 20112 POINTY 500 1 | 2998.8 | 2700 |  |  | 20101 BED 500 20103 OAK 500 1 | 14917 RAINY 500 20112 POINTY 500 1 | 11 |  |  |  | RSource | [40 empty] | optLFrepa2 | TRUE | FALSE | FALSE | TRUE | [9 empty] | txtAMBStartDate | 2007-03-02 01 | [10 empty] | txtVoltLimAdd | 0 | [10 empty] | chkScren | FALSE |  | chkPVDfax | FALSE | txtTSR3 | 95 | txtLFdir | C:\TARA_main\test1 | txtUpscr | 15 | chkSaveDB | FALSE | optG3 | FALSE |  |  | chkV11 | TRUE |  |  | txtLa2 | 3 | [35 empty] | 1 | deOscilFactor | txtDeOs |  |  |  | # De-oscillation factor (if 1.0-not activated)
| txtNEMIS8 | 95 |  |  | 0 | [11 empty] | XSource | [40 empty] | optLFrepa3 | FALSE | FALSE | FALSE | FALSE | [9 empty] | chkAMBRT11 | TRUE | [10 empty] | chkEnfP | FALSE | [10 empty] | txtScren1 | 3000 |  | txtPV_DF1 | 345 | txtTSR4 | 0.03 | chkACtrlSave | FALSE | txORACutGenTr | 90 | txtDirDB | C:\TARA_main\temp | optG4 | FALSE |  |  | chkV12 | TRUE |  |  | txtLa3 | 3
| txtNEMIS9 | 0 | [14 empty] | RTran | [40 empty] | optLFrepa4 | FALSE | FALSE | FALSE | FALSE | [9 empty] | chkAMBRT12 | TRUE | [10 empty] | txtPen1A | 100000 | [10 empty] | txtScren2 | 0.0005 |  | txtPV_DF2 | 0.05 | txtTSR5 | 100 | chkACtrlRun1 | TRUE | chkORAgen | FALSE | optSaveDBNo | TRUE | chkG1 | TRUE |  |  | chkV13 | TRUE |  |  | txtLa4 | 4
Rating 1 | chkNEMIS9 | TRUE | [14 empty] | XTran | [40 empty] | chkLFPA | TRUE | FALSE | TRUE | TRUE | [9 empty] | chkAMBRT13 | TRUE | [10 empty] | txtPen2A | 1000 | [10 empty] | txtScren3 | 90 |  | txtPV_DF3 | 0.02 | txtTSR6 | 1 | chkACtrlRun2 | TRUE | chkORAtr | FALSE | optSaveDB1 | FALSE | chkL1 | TRUE |  |  | chkV14 | TRUE |  |  | txtLa5 | 4
Rating 2 | chkNEMIS10 | FALSE | [14 empty] | GenTap | [40 empty] | optLFarea1 | TRUE | TRUE | TRUE | TRUE | [9 empty] | chkAMBRT14 | TRUE | [10 empty] | txtPen3A | 100000 | [13 empty] | chkDupls | FALSE | txtTSR7 | 0.01 | chkACtrlRun3 | FALSE | txtss3 | allgen | optSaveDB2 | FALSE | optInc | FALSE |  |  | chkV15 | TRUE |  |  | txtKVCut | 100
Rating 3 | chkNEMIS11 | FALSE | [14 empty] | BusName Volt | [40 empty] | optLFarea2 | FALSE | FALSE | FALSE | FALSE | [9 empty] | chkAMBRT15 | TRUE | [10 empty] | optBasPen | TRUE | [13 empty] | enACVer | TRUE | txtLFdir | C:\TARA_main\test | chkACtrlRun4 | TRUE | txtss4 | allload | txtDBfileName | C:\TARA_main\temp\ORA.db | optPC | TRUE |  |  | chkV16 | TRUE |  |  | chkKVAll | FALSE
Rating 4 | chkNEMIS12 | TRUE | [14 empty] | AvailStat | [40 empty] | optLFarea3 | FALSE | FALSE | FALSE | FALSE | [9 empty] | chkAMBRT21 | TRUE | [10 empty] | optAdvPen | FALSE | [13 empty] | txtTrlTestLev | 10000 | chkIncAdd | TRUE | chkACtrlRun5 | FALSE | txtORAGen1 | 3000 | txtss3 | STUDY_BES | optTN | FALSE |  |  | chkV17 | FALSE |  |  | chkKV1 | TRUE
Rating 5 | txtRTEP1 | 0 | [55 empty] | optLFarea4 | FALSE | FALSE | FALSE | FALSE | [9 empty] | chkAMBRT22 | TRUE | [10 empty] | txtBIcut | 0.05 | [13 empty] | txtTrlPSCons | 1 | txtERIS1 | 90 | txtACtrlRun6 | 1 | txtORAGen2 | 3000 | txtDisCut | 0.0001 | txtPen1SCD | 500 |  |  | chkV18 | TRUE |  |  | chkN11ClosePr | FALSE
Rating 6 | txtRTEP2 | 0 | [14 empty] | ZnBus[1] | [40 empty] | chkLFTA | TRUE | TRUE | TRUE | TRUE | [9 empty] | chkAMBRT23 | TRUE | [10 empty] | optBI1 | TRUE | [13 empty] | txtTrlPS1 | 0.03 | txtERIS2 | 0.05 | txtACtrlRun7 | 0.05 | txtORAGen3 | 0.05 | txtSaveFile1 | Please define the correct path here | txtPen2SCD | 10000 |  |  | chkV19 | TRUE |  |  | chkACtrlSave | FALSE
Rating 7 | optRTEP1 | TRUE | [14 empty] | ZnBus[2] | [40 empty] | chkLFDA | TRUE | TRUE | TRUE | TRUE | [9 empty] | chkAMBRT24 | TRUE | [10 empty] | optBI2 | FALSE | [13 empty] | txtTrlPS2 | 5 | txtERIS3 | 0.2 | chkACtrlRun6 | TRUE | txtORATr1 | 50000 |  |  | txtPen3SCD | 1 |  |  | chkV20 | TRUE |  |  | txtLFdir | C:\TARA_main\cases
Rating 8 | optRTEP2 | FALSE | [14 empty] | ZnBus[Dif] | [40 empty] | txtLF1 | 1 | 1 | 1 | 1 | [9 empty] | chkAMBRT25 | TRUE | [10 empty] | txtBIss | allload | [13 empty] | chkTrlPS1 | FALSE | txtERIS4 | 0.2 | optIter1 | TRUE | txtORATr2 | 0.02 |  |  | txtPen4SCD | 100 |  |  | chkV21 | FALSE |  |  | chkN11_ACscr2 | FALSE
Rating 9 | txtFlgFileName | Please define the correct path here | [55 empty] | txtLF2 | 50 | 50 | 50 | 50 | [9 empty] | chkEMS | FALSE | [10 empty] | optSCEDp1 | TRUE | [13 empty] | txtTrlTestLevNew | 2000 | txtERIS5 | 0.2 | optIter2 | FALSE | txtVoltLimAdd | 0 |  |  | txtPen5SCD | 200000 |  |  | chkV22 | FALSE |  |  | optN11_ACscr1 | TRUE
Rating 10 | txtEntered | 9004 | [55 empty] | txtLF3 | 0 | 0 | 0 | 0 | [9 empty] | txtEMS1 | 4 | [10 empty] | optSCEDp2 | FALSE | [13 empty] | chkTrl_lim | FALSE | txtERIS6 | 0.05 | optIter3 | FALSE |  |  |  |  | txtLP1SCD | 100000 |  |  | chkV23 | FALSE |  |  | optN11_ACscr2 | FALSE
Rating 11 | optClust1 | FALSE | [55 empty] | txtLF4 | 3 | 3 | 3 | 3 | [9 empty] | txtEMS2 | 8 | [10 empty] | txtLSadd | -400 | [13 empty] | optLF11 | FALSE | txtERIS7 | 0.05 | txtIter1 | 5 |  |  |  |  | txtLP2SCD | 0.001 |  |  | chkV24 | FALSE |  |  | optN11_ACscr3 | FALSE
Rating 12 | optClust2 | FALSE | [55 empty] | txtLF6 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | [9 empty] | optEMS1 | FALSE | [10 empty] | txtRSadd | 300 | [13 empty] | optLF22 | TRUE | txtERIS8 | 5 | txtIter2 | 1 |  |  |  |  | txtLP3SCD | 0.001 |  |  | chkA2 | TRUE |  |  | txtKV1_1 | 100
| optClust3 | FALSE | [55 empty] | txtLF7 | 0.8 | 0.8 | 0.8 | 0.8 | [9 empty] | optEMS2 | FALSE | [10 empty] | txtEMSch | 50 | [13 empty] | optLF33 | FALSE | txtERIS44 | 0.03 | txtLoadCut | 85 |  |  |  |  | txtLP4SCD | 3 |  |  | chkA3 | TRUE |  |  | txtKV2_1 | 300
| optClust4 | FALSE | [55 empty] | txtLF8 | 40 | 40 | 40 | 40 | [9 empty] | optEMS3 | TRUE | [10 empty] | txtBIcut1 | 20 | [13 empty] | txtRawData | C:\TARA_main\SampleData2015\sample_Trlim2.raw | txtERIS55 | 0.2 | optACtrlRun1 | FALSE |  |  |  |  | txtLP5SCD | 2000 |  |  | chkA4 | TRUE |  |  | txtKV3_1 | 400
| optClust5 | TRUE | [55 empty] | txtLF9 | 6 | 6 | 6 | 6 | [9 empty] | optEMSNo | TRUE | [10 empty] | txtBIcut2 | 5 | [13 empty] | optDFVolt1 | TRUE | txtSNU1 | 5 | optACtrlRun2 | TRUE | [8 empty] | chkA5 | FALSE |  |  | txtKV4_1 | 600
| txtClust1 | 0.2 | [55 empty] | txtLF10 | 0.2 | 0.2 | 0.2 | 0.2 | [9 empty] | optEMSYes | FALSE | [10 empty] | txtBIcut3 | 2 | [13 empty] | optDFVolt2 | FALSE | txtSNU2 | 0.01 | optACtrl1 | FALSE | [8 empty] | chkA6 | FALSE |  |  | txtLa1_1 | 10
| txtClust2 | 0.01 | [55 empty] | txtLF11 | 3 | 3 | 3 | 3 | [9 empty] | chkBuildMod | FALSE | [10 empty] | chkEnPost | FALSE | [13 empty] | optDFVolt3 | FALSE | txtSNU3 | 0.2 | optACtrl2 | TRUE | [8 empty] | chkA7 | FALSE |  |  | txtLa2_1 | 10
| txtClust3 | 0.05 | [55 empty] | txtLF12 | 0.15 | 0.15 | 0.15 | 0.15 | [9 empty] | chkEnEnf | FALSE | [10 empty] | chkEnGLSO | TRUE | [13 empty] | optDFVoltRep1 | FALSE | txtSNU4 | 0.05 | txtACtrlTop | 5 | [8 empty] | chkA8 | TRUE |  |  | txtLa3_1 | 10
| chkClust1 | FALSE | [55 empty] | txtLF13 | 1 | 1 | 1 | 1 | [9 empty] | chkCasBr | TRUE | [10 empty] | optGL1 | TRUE | [13 empty] | optDFVoltRep2 | FALSE | txtRawData | C:\ProjectTest\ERIS\test.raw | txtPen1A | 100000 | [8 empty] | chkA9 | TRUE |  |  | txtLa4_1 | 10
| chkClust2 | TRUE | [55 empty] | txtLF14 | 3 | 3 | 3 | 3 | [9 empty] | chkCasGen | TRUE | [10 empty] | optGL2 | FALSE | [13 empty] | optDFVoltRep3 | FALSE | txtINCH1 | C:\ProjectTest\ERIS\test.inch | txtPen2A | 1000 | [8 empty] | chkA10 | TRUE |  |  | txtLa5_1 | 10
| txtClustXMLfile1 | C:\TARA_MISO\ClusterReserveDefinition.xml | [55 empty] | txtLF15 | 0.05 | 0.05 | 0.05 | 0.05 | [9 empty] | chkCasGen1 | FALSE | [10 empty] | optGL3 | TRUE | [13 empty] | optDFVoltRep4 | TRUE | chkApp1 | TRUE | txtPen3A | 100000 | [8 empty] | chkA11 | TRUE |  |  | txtKVCut_1 | 0
| txtClustXMLfile2 | C:\TARA_MISO\ClusterReserveRequirements.xml | [55 empty] | txtLF16 | 0.2 | 0.2 | 0.2 | 0.2 | [9 empty] | chkCasLd | TRUE | [10 empty] | optGL4 | FALSE | [13 empty] | txtEnteredBus11 | K6 | chkOpenReps | TRUE | optBasPen | TRUE | [8 empty] | chkA111 | TRUE |  |  | chkKVAll_1 | TRUE
| txtClustXMLfile3 | C:\TARA_MISO\ClusterReserveConstraints.xml | [55 empty] | txtLF17 | 5 | 5 | 5 | 5 | [9 empty] | txtCPar1 | 100 | [10 empty] | optGL5 | TRUE | [15 empty] | chkSaveReps | TRUE | optAdvPen | FALSE | [8 empty] | chkA122 | TRUE |  |  | chkKV1_1 | TRUE
| chkMultiCases | FALSE | [55 empty] | txtLF18 | 30 | 30 | 30 | 30 | [9 empty] | txtCPar2 | 200 | [10 empty] | optGL6 | FALSE | [15 empty] | txtWorkName | C:\TARA_main\TARA_all_reports.xlsx | txtPV1 | 8000 | [8 empty] | chkA12 | TRUE |  |  | txtKV1_2 | 100
| chkCreateLFlist | FALSE | [55 empty] | txtLF19 | 0 | 0 | 0 | 0 | [9 empty] | txtCPar3 | 300 | [10 empty] | optGL7 | FALSE | [15 empty] | txtCA_GD1 | 90 | txtPV1a | 2000 | [8 empty] | chkA13 | TRUE |  |  | txtKV2_2 | 300
| txtMISO1 | 0.05 | [55 empty] | txtLF20 | 1.25 | 1.25 | 1.25 | 1.25 | [9 empty] | txtCPar4 | 400 | [10 empty] | optGL8 | FALSE | [15 empty] | txtCA_GD2 | 0.05 | txtPV2 | 1000 | [8 empty] | chkA14 | TRUE |  |  | txtKV3_2 | 400
| txtMISO2 | 0 | [55 empty] | txtLFT2 | 0.02 | 0.02 | 0.02 | 0.02 | [9 empty] | txtCPar11 | 115 | [10 empty] | optGL9 | TRUE | [15 empty] | txtCA_GD3 | 0.02 | txtPV3 | 0.5 | [8 empty] | chkA15 | TRUE |  |  | txtKV4_2 | 600
| chkMISO1 | TRUE | [55 empty] | txtLFS1 | 1 | 1 | 1 | 1 | [9 empty] | txtCPar12 | 115 | [10 empty] | optGL10 | FALSE | [15 empty] | txtCA_GD4 | 0.05 | txtEntered | K1 | [8 empty] | chkA16 | TRUE |  |  | txtLa1_2 | 10
| chkMISO2 | TRUE | [55 empty] | chkTraceBuses | FALSE | FALSE | FALSE | FALSE | [9 empty] | txtCPar13 | 115 | [10 empty] | optGL11 | TRUE | [15 empty] | txtCA_GD5 | 1500 | txtPVBack1 | 0.95 | [8 empty] | chkA17 | TRUE |  |  | txtLa2_2 | 10
| txtLoadCOff | 90 | [55 empty] | txtTraceBuses | K98937 |  |  | K98937 | [9 empty] | txtCPar14 | 115 | [10 empty] | optGL12 | FALSE | [15 empty] | txtCA_GD55 | 20 | txtPVBack2 | 100 | [8 empty] | chkA18 | TRUE |  |  | txtLa3_2 | 10
| txtLoadCOffAC | 90 | [55 empty] | optLFflat1 | TRUE | TRUE | TRUE | TRUE | [9 empty] | txtCPar15 | 115 | [10 empty] | optGL13 | FALSE | [15 empty] | chkCA_GD1 | TRUE | optPVBack1 | TRUE | [8 empty] | chkA21 | FALSE |  |  | txtLa4_2 | 10
| chkAddCaskAn | FALSE | [55 empty] | optLFflat2 | FALSE | FALSE | FALSE | FALSE | [9 empty] | txtCMax | 5 | [10 empty] | optGL14 | FALSE | [15 empty] | txtCA_GD6 | 99 | optPVBack2 | FALSE | [8 empty] | chkA22 | FALSE |  |  | txtLa5_2 | 10
| chkAddACfg | FALSE | [55 empty] | txtGenOpt1 | 5 | 5 | 5 | 5 | [9 empty] | chkACtrlSave | FALSE | [10 empty] | optGL21 | TRUE | [15 empty] | chkSolveSave | FALSE | optPVBack0 | FALSE | [8 empty] | chkA23 | FALSE |  |  | txtKVCut_2 | 0
| txtLoadCOffOut | 90 | [55 empty] | txtGenOpt2 | 2 | 2 | 2 | 2 | [9 empty] | txtLFdir | C:\TARA_main\cases\test | [10 empty] | optGL22 | FALSE | [15 empty] | chkCA_GD2 | TRUE | chkACTAQV | TRUE | [8 empty] | chkA24 | FALSE |  |  | chkKVAll_2 | TRUE
| txtLoadCOffSCED | 90 | [55 empty] | txtGenOpt3 | 0.005 | 2 | 2 | 0.005 | [21 empty] | optGL23 | FALSE | [15 empty] | txtCA_GD7 | 8 | chkACPAQV | FALSE | [8 empty] | chkPVP1 | TRUE |  |  | chkKV1_2 | TRUE
| chkOutPreAppr | FALSE | [55 empty] | optFlgFile1 | FALSE | FALSE | FALSE | FALSE | [21 empty] | optGL24 | FALSE | [15 empty] | optStudio1 | TRUE | chkLFDAQV | TRUE | [8 empty] | chkPVA1 | TRUE |  |  | txtKV1_4 | 100
| txtAMBStartDate | 2020-04-30 21 | [55 empty] | optFlgFile2 | TRUE | TRUE | TRUE | TRUE | [21 empty] | chkGL1 | FALSE | [15 empty] | optStudio2 | FALSE | optLACEn1QV | FALSE | [8 empty] | chkPVA2 | FALSE |  |  | txtKV2_4 | 300
| txtAMBdir | C:\TARA_main\temp | [55 empty] | chkLogFileSave | TRUE | FALSE | FALSE | TRUE | [21 empty] | chkGL2 | FALSE | [15 empty] | optStudio3 | FALSE | optLACEn3QV | FALSE | [8 empty] | chkPVA3 | FALSE |  |  | txtKV3_4 | 400
| txtAMBnn | 3 | [55 empty] | chkUseTrace | TRUE | FALSE | FALSE | TRUE | [21 empty] | txtGL1 | 500 | [15 empty] | chkRunContSubsys | FALSE | optLACEn2QV | TRUE | [8 empty] | chkPVA4 | FALSE |  |  | txtKV4_4 | 600
| chkAMBSkip | FALSE | [55 empty] | chkShowProgress | FALSE | FALSE | FALSE | FALSE | [21 empty] | txtGL2 | 500 | [15 empty] | optSubSys | FALSE | optACarea1QV | TRUE | [8 empty] | chkPV1 | TRUE |  |  | txtLa1_4 | 5
| txtAMBSkip | 3 | [55 empty] | txtLogFile | C:\Users\03419\Desktop\2022 Gas Study\temp\taralog.txt |  |  | C:\TARA_main\temp\taralog.txt | [21 empty] | txtGL3 | 10 | [15 empty] | optAreaGr | TRUE | optACarea2QV | FALSE | [8 empty] | chkPV2 | TRUE |  |  | txtLa2_4 | 5
| chkAMBsolve | TRUE | [55 empty] | txtScriptFile | C:\TARA_main\temp\taraScript1.txt |  |  | C:\TARA_main\temp\taraScript1.txt | [21 empty] | optDF1 | TRUE | [15 empty] | txtSubSys | PJM | optACarea3QV | FALSE | [8 empty] | chkPV3 | TRUE |  |  | txtLa3_4 | 5
| chkAMBRAWD | TRUE | [55 empty] | chkUseRecord | FALSE | FALSE | FALSE | FALSE | [21 empty] | optDF2 | FALSE | [15 empty] | txtAreaGr | 201 202 205 206 209 212 215 222 225 -238 320 345 | chkACVRQV | FALSE | [8 empty] | chkPV4 | TRUE |  |  | txtLa4_4 | 5
| chkAMBTDF | FALSE | [55 empty] | optScrApnd | FALSE | FALSE | FALSE | FALSE | [21 empty] | optDF3 | FALSE | [15 empty] | txtINCH | C:\TARA_main\MergeTestInputFiles\test.inch | txtLF1QV | 0.1 | [8 empty] | chkPV5 | TRUE |  |  | txtLa5_4 | 5
| txtAMBTDF | C:\TARA_main\tdf.bin | [55 empty] | optScrOver | TRUE | TRUE | TRUE | TRUE | [21 empty] | txtDFss | AllGen | [15 empty] | optTie1 | TRUE | txtLF7QV | 0.1 | [8 empty] | chkPV6 | TRUE |  |  | txtKVCut_4 | 0
| chkAMBsolveSCED | FALSE | [55 empty] | chkUseContComm | FALSE | FALSE | FALSE | FALSE | [21 empty] | txtDFss1 | allgen | [15 empty] | optTie2 | FALSE | txtEnteredQV | K5,6,7,8,9 | [8 empty] | chkPV7 | TRUE |  |  | chkKVAll_4 | TRUE
| optSStype1 | FALSE | [55 empty] | chkRecordStop | FALSE | FALSE | FALSE | FALSE | [21 empty] | txtDFss2 | allload | [15 empty] | optTie3 | FALSE | txtEntered1QV | K11027,11036,11040,11050 | [8 empty] | chkPV8 | TRUE |  |  | chkKV1_4 | TRUE
| optSStype2 | TRUE | [55 empty] | chkShowLFconv | FALSE | FALSE | FALSE | FALSE | [21 empty] | txtDF1 | 0.03 | [15 empty] | optOff1 | TRUE | txtPV66 | 0.05 | [8 empty] | chkPV9 | TRUE |  |  | txtssRun | allgen
| optSStype3 | FALSE | [55 empty] | optSh1 | TRUE | TRUE | TRUE | TRUE | [21 empty] | txtDF2 | -0.03 | [15 empty] | optOff2 | FALSE | txtPV33 | 1 | [8 empty] | chkPVAV1 | TRUE |  |  | txtKV1_3 | 100
| optSStype4 | FALSE | [55 empty] | optSh2 | FALSE | FALSE | FALSE | FALSE | [21 empty] | N11ContScrnVolt | TRUE | [15 empty] | txtSaveINCH | C:\TARA_main\MergeTestInputFiles\test1.inch | chkPV33 | FALSE | [8 empty] | chkPVAV2 | FALSE |  |  | txtKV2_3 | 300
| optInc1 | FALSE | [55 empty] | optSh3 | FALSE | FALSE | FALSE | FALSE | [21 empty] | chkPostCor | FALSE | [17 empty] | chkPV22 | FALSE | [8 empty] | chkPVAV3 | FALSE |  |  | txtKV3_3 | 400
| optInc2 | TRUE | [55 empty] | txtDeOs | 0.7 | 0.7 | 0.7 | 0.7 | [40 empty] | chkPV_lb | TRUE | [8 empty] | chkPVAV4 | FALSE |  |  | txtKV4_3 | 600
| optABM1 | FALSE | [55 empty] | chkLFflat1 | FALSE | FALSE | FALSE | FALSE | [40 empty] | chkPV_db | FALSE | [8 empty] | chkPVV1 | TRUE |  |  | txtLa1_3 | 10
| optABM2 | FALSE | [55 empty] | optACflat1 | TRUE | TRUE | TRUE | TRUE | [40 empty] | chkPV_bt | TRUE | [8 empty] | chkPVV2 | TRUE |  |  | txtLa2_3 | 10
| optABM3 | TRUE | [55 empty] | optACflat2 | FALSE | FALSE | FALSE | FALSE | [40 empty] | chkPV_ft | FALSE | [8 empty] | chkPVV3 | TRUE |  |  | txtLa3_3 | 10
| txtRawData_SCED | Please define the correct path here | [55 empty] | optACflat3 | FALSE | FALSE | FALSE | FALSE | [40 empty] | chkPV77 | TRUE | [8 empty] | chkPVV4 | TRUE |  |  | txtLa4_3 | 10
| txtLFdir_SCED | C:\TARA_main\temp | [55 empty] | chkQR1 | FALSE | FALSE | FALSE | FALSE | [40 empty] | chkClosePr | TRUE | [8 empty] | chkPVV5 | TRUE |  |  | txtLa5_3 | 10
| txtLFdir_OUT | C:\TARA_main\temp22 | [55 empty] | chkQR2 | FALSE | FALSE | FALSE | FALSE | [40 empty] | chkPVDfax | FALSE | [8 empty] | chkPVV6 | TRUE |  |  | txtKVCut_3 | 1
| optAMBsolve1 | FALSE | [55 empty] | chkQR3 | FALSE | FALSE | FALSE | FALSE | [40 empty] | txtss3DF | SCD_AllGens | [8 empty] | chkPVV7 | TRUE |  |  | chkKVAll_3 | TRUE
| optAMBsolve2 | FALSE | [55 empty] | chkQR4 | FALSE | FALSE | FALSE | FALSE | [40 empty] | txtss4DF | NWEST | [8 empty] | chkPVV8 | FALSE |  |  | chkKV1_3 | TRUE
| optAMBsolve3 | TRUE | [55 empty] | chkQR5 | FALSE | FALSE | FALSE | FALSE | [40 empty] | txtPV_DF1 | 345 | [8 empty] | chkPVV9 | FALSE
| chkAMBSCCons | TRUE | [55 empty] | txtQR1 | 0.7 | 0.7 | 0.7 | 0.7 | [40 empty] | txtPV_DF2 | 0.05 | [8 empty] | chkPVV10 | TRUE
| chkUseDataDir | TRUE | [55 empty] | txtQR2 | 1.3 | 1.3 | 1.3 | 1.3 | [40 empty] | txtPV_DF3 | 0.02 | [8 empty] | chkPVV11 | TRUE
| txtss33 | West | [55 empty] | txtQR3 | 0.7 | 0.7 | 0.7 | 0.7 | [50 empty] | chkPVV12 | TRUE
| txtss44 | East | [55 empty] | txtQR4 | 1.25 | 1.25 | 1.25 | 1.25 | [50 empty] | chkPVV13 | TRUE
| txtTrlTestLev | 2000 | [55 empty] | chkAdjInternal | FALSE | FALSE | FALSE | FALSE | [50 empty] | chkPVV14 | TRUE
| optTrl11 | TRUE | [55 empty] | txtAdjInternal | K3,4 | 3,4 | 3,4 | K3,4 | [50 empty] | chkPVV15 | TRUE
| optTrl12 | FALSE | [55 empty] | txtBrNamPre | /* [ | /* [ | /* [ | /* [ | [50 empty] | chkTRL1 | TRUE
| optTrl13 | FALSE | [55 empty] | txtBrNamSuf | ] | ] | ] | ] | [50 empty] | chkTRL2 | FALSE
| optTrl14 | FALSE | [55 empty] | chkBrNam | FALSE | FALSE | FALSE | FALSE | [50 empty] | chkTRL3 | FALSE
| optTrl21 | TRUE | [55 empty] | chkAddAreaNam | FALSE | FALSE | FALSE | FALSE | [50 empty] | optTRL1 | TRUE
| optTrl22 | FALSE | [55 empty] | chkAddZoneNam | FALSE | FALSE | FALSE | FALSE | [50 empty] | optTRL2 | TRUE
| optTrl23 | FALSE | [55 empty] | txtSCED1 | 10000 | 10000 | 10000 | 10000 | [50 empty] | chkTRLaz1 | TRUE
| optTrl24 | FALSE | [55 empty] | txtSCED2 | 100000 | 100000 | 100000 | 100000 | [50 empty] | chkTRLaz2 | TRUE
| txtTrl11 | TRUE | [55 empty] | txtSCED3 | 40000 | 40000 | 40000 | 40000 | [50 empty] | chkTRLaz3 | TRUE
| txtTrl21 | TRUE | [55 empty] | txtMaxASM1 | 10 |  |  | 10 | [50 empty] | chkTRLaz4 | TRUE
| txtTrl1 | 0.03 | [55 empty] | txtMaxASM2 | 10 |  |  | 10 | [50 empty] | chkTRL4 | TRUE
| txtTrl2 | 5 | [55 empty] | chkFGNamLimit | FALSE | FALSE | FALSE | FALSE | [50 empty] | chkPVRepSS | TRUE
| txtLoadCOffTRL | 90 | [55 empty] | chkAddQuotes | FALSE | FALSE | FALSE | FALSE | [50 empty] | txtVoltLimAdd | TRUE
| chkTrlScale | FALSE | [55 empty] | chkNo3wnd | FALSE | FALSE | FALSE | FALSE | [50 empty] | chkT6O | FALSE
| chkTrl1 | TRUE | [55 empty] | chkMiscEnd | FALSE | FALSE | FALSE | FALSE | [50 empty] | chkT7O | FALSE
| txtTrl3 | 10 | [55 empty] | chkMiscFont | FALSE | FALSE | FALSE | TRUE | [50 empty] | chkA6O | FALSE
| txtTrl4 | K300,400 | [55 empty] | txtPar1 | 110000 | 110000 | 110000 | 110000 | [50 empty] | chkA7O | FALSE
| optTrl2_1 | TRUE | [55 empty] | txtPar2 | 190000 | 190000 | 190000 | 190000 | [50 empty] | chkV4O | FALSE
| optTrl2_2 | FALSE | [55 empty] | txtPar3 | 190000 | 190000 | 190000 | 190000 | [50 empty] | chkV5O | FALSE
| chkTrl2 | FALSE | [55 empty] | txtPar4 | 15000 | 15000 | 15000 | 15000
| chkTrl_bus | FALSE | [55 empty] | txtPar5 | 40000 | 30000 | 30000 | 40000
| txtTrl_bus | 20 | [55 empty] | txtPar6 | 25000 | 25000 | 25000 | 25000
| optTrl_bus1 | TRUE | [55 empty] | optEMS1 | TRUE | TRUE | TRUE | TRUE
| optTrl_bus2 | FALSE | [55 empty] | optEMS2 | FALSE | FALSE | FALSE | FALSE
| chkTrl2ac | FALSE | [55 empty] | optEMS3 | FALSE | FALSE | FALSE | FALSE
| chkTrl_lim | FALSE | [55 empty] | chkEMS1 | FALSE | FALSE | FALSE | FALSE
| txtACtrl1 | East | [55 empty] | chkEMSsd | FALSE | FALSE | FALSE | FALSE
| txtTrlPSCons | 5 | [55 empty] | txtEMSsd | 1e-06 | 1e-06 | 1e-06 | 1e-06
| txtTrlPSTestLev | 10000 | [55 empty] | chkShowLoadRes | TRUE | TRUE | TRUE | TRUE
| txtTrlPS1 | 0.05 | [55 empty] | chkShowCaseSum | TRUE | FALSE | FALSE | TRUE
| txtTrlPS2 | 3 | [55 empty] | chkShowListRes | TRUE | TRUE | TRUE | TRUE
| chkTrlPS1 | FALSE | [55 empty] | optRed1 | TRUE | TRUE | TRUE | TRUE
| txtPSFileName | Please define the correct path here | [55 empty] | optRed2 | FALSE | FALSE | FALSE | FALSE
| txtFileN11 | Please define the correct path here | [55 empty] | optAUX | TRUE | TRUE | TRUE | TRUE
| optEvAll | TRUE | [55 empty] | optCSV | FALSE | FALSE | FALSE | FALSE
| optEvRan | FALSE | [55 empty] | chkACTA | FALSE | FALSE | FALSE | FALSE
| optEvFile | FALSE | [55 empty] | chkACPA | FALSE | FALSE | FALSE | FALSE
| txtRan1 | 1 | [55 empty] | chkACVR | TRUE | FALSE | TRUE | TRUE
| txtRan2 | 50 | [55 empty] | chkACDC | FALSE | FALSE | TRUE | FALSE
| txtTrlTie1 | 2000 | [55 empty] | optLACEn1 | TRUE | TRUE | TRUE | TRUE
| txtTrlTie2 | 0.005 | [55 empty] | optLACEn3 | FALSE | FALSE | FALSE | FALSE
| optCAmode1 | FALSE | [55 empty] | optLACEn2 | FALSE | FALSE | FALSE | FALSE
| optCAmode3 | FALSE | [55 empty] | optACarea1 | TRUE | TRUE | TRUE | TRUE
| chkAddDCReps | TRUE | [55 empty] | optACarea2 | FALSE | FALSE | FALSE | FALSE
| chkAddN11DetIsl | FALSE | [55 empty] | optACarea3 | FALSE | FALSE | FALSE | FALSE
| txtVoltLimAdd | 0 | [55 empty] | chkVR | FALSE | FALSE | FALSE | FALSE
| txtVoltLimAdd1 | 0 | [55 empty] | optLFT1na | TRUE | TRUE | TRUE | TRUE
| enACVer | FALSE | [55 empty] | optLFT2na | FALSE | FALSE | FALSE | FALSE
| txtFGfile_noDupl | C:\TARA_main\UGM2011\data\Sample_test.fgt | [55 empty] | optLFT3na | FALSE | FALSE | FALSE | FALSE
| chkAddInchFlist | FALSE | [55 empty] | optLFP1na | TRUE | TRUE | TRUE | TRUE
| txtLOAF | 0.01 | [55 empty] | optLFP2na | FALSE | FALSE | FALSE | FALSE
| txtLOAI | 1 | [55 empty] | optLFP3na | FALSE | FALSE | FALSE | FALSE
| txtPV44 | 10 | [55 empty] | optLFS1na | TRUE | TRUE | TRUE | TRUE
| txtPV55 | 60 | [55 empty] | optLFS2na | FALSE | FALSE | FALSE | FALSE
| txtPV33 | 1 | [55 empty] | optLFS3na | FALSE | FALSE | FALSE | FALSE
| txtPV1 | 8000 | [55 empty] | optLFrepa1na | TRUE | TRUE | TRUE | TRUE
| txtPV1a | 0 | [55 empty] | optLFrepa2na | FALSE | FALSE | FALSE | FALSE
| txtPV2 | 500 | [55 empty] | optLFrepa3na | FALSE | FALSE | FALSE | FALSE
| txtPV11 | 8000 | [55 empty] | optLFrepa4na | FALSE | FALSE | FALSE | FALSE
| txtPV11a | 0 | [55 empty] | optLVio1 | TRUE | TRUE | TRUE | TRUE
| txtPV22 | 100 | [55 empty] | optLVio2 | FALSE | FALSE | FALSE | FALSE
| txtPV3 | 1 | [55 empty] | optTVio1 | FALSE | FALSE | FALSE | FALSE
| txtPV66 | 0.05 | [55 empty] | optTVio2 | TRUE | TRUE | TRUE | TRUE
| txtss333 | EXPORT | [55 empty] | chkAdd1 | FALSE | FALSE | FALSE | FALSE
| chkPV22 | TRUE | [55 empty] | chkAdd2 | FALSE | FALSE | FALSE | FALSE
| txtss3_NE | EXPORT | [55 empty] | txtAdd1 | 90 | 100 | 100 | 90
| txtss4_NE | REF | [55 empty] | txtAdd2 | 90 | 100 | 100 | 90
| txtQV1 | 0.7 | [55 empty] | optAdd11 | FALSE | FALSE | FALSE | FALSE
| txtQV2 | 1.05 | [55 empty] | optAdd12 | TRUE | TRUE | TRUE | TRUE
| txtQV3 | 0.01 | [55 empty] | optAdd13 | FALSE | FALSE | FALSE | FALSE
| txtQV4 | 3 | [55 empty] | optAdd14 | FALSE | FALSE | FALSE | FALSE
| txtQV5 | 0.925 | [55 empty] | optAdd21 | FALSE | FALSE | FALSE | FALSE
| chkQV1 | TRUE | [55 empty] | optAdd22 | FALSE | TRUE | TRUE | FALSE
| chkQV2 | TRUE | [55 empty] | optAdd23 | TRUE | FALSE | FALSE | TRUE
| txtQV6 | 100 | [55 empty] | optAdd24 | FALSE | FALSE | FALSE | FALSE
| txtQV7 | 70 | [55 empty] | cboOptRatingsBr | Rating 1 | Rating 1 | Rating 1 | Rating 1
| chkPV33 | FALSE | [55 empty] | cboOptRatingsCr | Rating 1 | Rating 1 | Rating 1 | Rating 1
| chkINCH_apply | TRUE | [55 empty] | cboOptRatingsAdd1 | Rating 1 | Rating 1 | Rating 1 | Rating 1
| optRest1 | TRUE | [55 empty] | cboOptRatingsAdd2 | Rating 1 | Rating 1 | Rating 1 | Rating 1
| optRest2 | FALSE | [55 empty] | chkOptRatingsBr | FALSE | FALSE | FALSE | FALSE
| chkAddTRLRep1 | FALSE | [55 empty] | chkOptRatingsCr | FALSE | FALSE | FALSE | FALSE
| chkAddTRLRep2 | FALSE | [55 empty] | chkOptRatingsAdd1 | FALSE | FALSE | FALSE | FALSE
| txtLFdir | C:\TARA_main\inch_project_files | [55 empty] | chkOptRatingsAdd2 | FALSE | FALSE | FALSE | FALSE
| txtApplyDate | K2016-08-01 | [55 empty] | cboOptRatingsBr1 | Rating 1 | Rating 1 | Rating 1 | Rating 1
| chkSolvePr | TRUE | [55 empty] | cboOptRatingsCr1 | Rating 1 | Rating 1 | Rating 1 | Rating 1
| chkLockShs | FALSE | [55 empty] | cboOptRatingsAdd11 | Rating 1 | Rating 1 | Rating 1 | Rating 1
| chkLockShs1 | FALSE | [55 empty] | cboOptRatingsAdd22 | Rating 1 | Rating 1 | Rating 1 | Rating 1
| chkWD | TRUE | [55 empty] | chkOptRatingsBr1 | FALSE | FALSE | FALSE | FALSE
| chkProbe1 | FALSE | [55 empty] | chkOptRatingsCr1 | FALSE | FALSE | FALSE | FALSE
| chkProbe2 | FALSE | [55 empty] | chkOptRatingsAdd11 | FALSE | FALSE | FALSE | FALSE
| chkIncAdd | TRUE | [55 empty] | chkOptRatingsAdd22 | FALSE | FALSE | FALSE | FALSE
| bDummy860a | FALSE | [55 empty] | chkT1 | TRUE | FALSE | FALSE | TRUE
| chkRunContSubsys | FALSE | [55 empty] | txtMonOpt1 | 5 | 10000 | 10000 | 5
| chkRunContSubsys1 | FALSE | [55 empty] | txtMonOpt2 | 5 | 10000 | 10000 | 5
| chkRunContSubsys2 | FALSE | [55 empty] | chkrReadRT | FALSE | FALSE | FALSE | FALSE
txtReadRT
[58 empty] | chkEnabParallel | FALSE | FALSE | FALSE | FALSE
[58 empty] | txtMulti | 4 | 4 | 4 | 4
[58 empty] | chkMisc1 | FALSE | FALSE | FALSE | FALSE
[58 empty] | optMisc1 | FALSE | TRUE | TRUE | FALSE
[58 empty] | optMisc2 | TRUE | FALSE | FALSE | TRUE
[58 empty] | optMisc3 | FALSE | FALSE | FALSE | FALSE
[58 empty] | optMiscSc1 | TRUE | TRUE | TRUE | TRUE
[58 empty] | optMiscSc2 | FALSE | FALSE | FALSE | FALSE
[58 empty] | chkLFlockSh | FALSE | FALSE | FALSE | FALSE
[58 empty] | txtLF7trl | 0.8 | 0.8 | 0.8 | 0.8
[58 empty] | txtLF7pv | 0.8 | 0.8 | 0.7 | 0.8
<--->

## ColumnsComments (hidden)
<--------> | <-------->
Application | Report | Column | Description
TARA | PVScrSum | Cont ID | Contingency ID
TARA | PVScrSum | Cont Name | Contingency Name
TARA | PVScrSum | Blown Up MW Transfer | MW transfer creating non-convergence
TARA | PVScrSum | MW Transfer at FG Overload | MW transfer at the first flowgate thermal violation
TARA | PVScrSum | FGID | Flowgate ID
TARA | PVScrSum | FG Name | Flowgate name
TARA | PVScrSum | Rating | Flowgate Rating
TARA | PVScrSum | Final AC %Loading | Final AC % loading at the first flowgate thermal violaiton
TARA | PVScrSum | MW Transfer at Vlow Limit | from bus voltage in basecase or contingency in QV test
TARA | PVScrSum | Bus # (Vmag Vio) | Bus Number with the first low voltage violation
TARA | PVScrSum | Bus Name | Bus Name
TARA | PVScrSum | Base kV | Bus Base kV
TARA | PVScrSum | Area | Bus Area Number
TARA | PVScrSum | Vmin | Low voltage limit
TARA | PVScrSum | Base Volt | Pre-contingency bus voltage
TARA | PVScrSum | Cont Volt | Post-contingency bus voltage
TARA | PVScrSum | MW Transfer at Vdrop Limit | MW transfer at the first voltage drop violation
TARA | PVScrSum | Bus # (Vdrop Vio) Limit | Bus Number with the first voltage drop violation
TARA | PVScrSum | Bus Name | Bus Name
TARA | PVScrSum | Base kV | Bus Base kV
TARA | PVScrSum | Area | Bus Area Number
TARA | PVScrSum | %Vdrop Limit | Maximum % voltage drop limit for bus
TARA | PVScrSum | Base Volt | Bus pre-contingency voltage
TARA | PVScrSum | Cont Volt | Bus post-contingency voltage
TARA | PVScrSum | %Vdrop | % voltage drop
TARA | PVScrSum | MW Transfer at FGBranch Overload | MW transfer at the first branch thermal violation
TARA | PVScrSum | Fr Bus | FROM bus number
TARA | PVScrSum | Fr Name | FROM bus name
TARA | PVScrSum | To Bus | TO bus number
TARA | PVScrSum | To Name | TO bus name
TARA | PVScrSum | CKT | Branch circuit identifier
TARA | PVScrSum | kVs | kV level(s)
TARA | PVScrSum | Areas | Area Number(s)
TARA | PVScrSum | Zones | Zone Number(s)
TARA | PVScrSum | Rating | Monitored facility rating (MVA)
TARA | PVScrSum | Dfax | Subsystem TDF (from sending to receiving subsystems)
TARA | PVScrSum | Final DC %Loading | Final % loading – linear (DC) solution
TARA | PVScrSum | Final AC %Loading | Final % loading – nonlinear (AC) solution
TARA | PVSummary | Sending System | Sending subsystem name
TARA | PVSummary | Receiving System | Receiving subsystem name
TARA | PVSummary | Worst Limit Flag | Identify contingencies with lowest transfer limits (NC, Vmag, Vdrop, BranOL, and FGOL). See TARA Manual for detail
TARA | PVSummary | Cont ID | Contingency ID
TARA | PVSummary | Cont Name | Contingency Name
TARA | PVSummary | Last Converged MW Transfer | MW transfer with the last post-contingency convergence
TARA | PVSummary | FG Name (Last Converge) | Flowgate name
TARA | PVSummary | Rating | Flowgate rating
TARA | PVSummary | Base MW | Pre-contingency MW flow
TARA | PVSummary | Base MW after Backing Off | Base MW flow adjusted by MW Backoff for Non-Convergent Limit
TARA | PVSummary | Cont MW | Post-contingency MW flow
TARA | PVSummary | Knee Flag | Knee if a post-contingency interface flow reversal occurs while transfer is increased
TARA | PVSummary | MW Transfer at 100% Loading | MW transfer when flowgate loading reaches 100%
TARA | PVSummary | Actual AC %Loading | Actual AC %Loading when flowgate reaches thermal limit (should be close to 100%)
TARA | PVSummary | Limit Info | Indicate whether or not MW transfer with the exact flowgate thermal violation found. See TARA Manual for detail
TARA | PVSummary | MW Transfer at Vlow Limit | MW transfer at the first low voltage violation
TARA | PVSummary | Bus # (Vmag Vio) | Bus Number with the first low voltage violation
TARA | PVSummary | Bus Name | Bus Name
TARA | PVSummary | Base kV | Bus Base kV
TARA | PVSummary | Area | Bus Area Number
TARA | PVSummary | Vmin | Low voltage limit
TARA | PVSummary | Base Volt | Pre-contingency bus voltage
TARA | PVSummary | Cont Volt | Post-contingency bus voltage
TARA | PVSummary | Limit Info | Indicate whether or not MW transfer with the exact low voltage violation found. See TARA Manual for detail
TARA | PVSummary | FG Baseflow at Vmag Violation | Flowgate base flow when the first low voltage violation occurs
TARA | PVSummary | FG Contflow at Vmag Violation | Flowgate conf flow when the first low voltage violation occurs
TARA | PVSummary | Limit Info | Indicate whether or not MW transfer with the exact low voltage violation found. See TARA Manual for detail
TARA | PVSummary | MW Transfer at Vdrop Limit | MW transfer at the first voltage drop violation
TARA | PVSummary | Bus # (Vdrop Vio) | Bus Number with the first voltage drop violation
TARA | PVSummary | Bus Name | Bus Name
TARA | PVSummary | Base kV | Bus Base kV
TARA | PVSummary | Area | Bus Area Number
TARA | PVSummary | Vmin | Percent voltage drop limit
TARA | PVSummary | Base Volt | Pre-contingency bus voltage
TARA | PVSummary | Cont Volt | Post-contingency bus voltage
TARA | PVSummary | Cont Volt | Percent voltage drop (Base Volt - Cont Volt)
TARA | PVSummary | Limit Info | Indicate whether or not MW transfer with the exact low voltage violation found. See TARA Manual for detail
TARA | PVSummary | FG Baseflow at Vdrop Violation | Flowgate base flow when the first voltage drop violation occurs
TARA | PVSummary | FG Contflow at Vdrop Violation | Flowgate conf flow when the first voltage drop violation occurs
TARA | PVSummary | Limit Info | Indicate whether or not MW transfer with the exact voltage drop violation found. See TARA Manual for detail
TARA | PVSummary | MW Transfer at 100% Branch Loading | MW transfer when branch loading reaches 100%
TARA | PVSummary | Fr Bus | FROM bus number
TARA | PVSummary | Fr Name | FROM bus name
TARA | PVSummary | To Bus | TO bus number
TARA | PVSummary | To Name | TO bus name
TARA | PVSummary | CKT | Branch circuit identifier
TARA | PVSummary | kVs | kV level(s)
TARA | PVSummary | Areas | Area Number(s)
TARA | PVSummary | Zones | Zone Number(s)
TARA | PVSummary | Rating | Monitored facility rating (MVA)
TARA | PVSummary | Actual AC %Loading | Actual branch percent loading when the first thermal branch limit is found
TARA | PVSummary | Limit Info | Indicate whether or not MW transfer with the exact branch thermal violation found. See TARA Manual for detail
TARA | PVShunt | Sending System | Sending subsystem name
TARA | PVShunt | Receiving System | Receiving subsystem name
TARA | PVShunt | MW Transfer | MW transfer
TARA | PVShunt | Bus # | Bus Number
TARA | PVShunt | Bus Name | Bus Name
TARA | PVShunt | Base kV | Bus Base kV
TARA | PVShunt | Area | Bus Area Number
TARA | PVShunt | Zone | Bus Zone Number
TARA | PVShunt | Shunt Min | Minimum MVAR shunt installed
TARA | PVShunt | Shunt Max | Maximum MVAR shunt installed
TARA | PVShunt | Control Mode | Shunt control mode
TARA | PVShunt | Vlower Limit | Controlled Voltage Upper Limit
TARA | PVShunt | Vupper Limit | Controlled voltage Lower Limit
TARA | PVShunt | Cont Name | Contingency Name
TARA | PVShunt | Cont ID | Contingency ID
TARA | PVShunt | Base Volt | Pre-contingency bus voltage
TARA | PVShunt | Cont Volt | Post-contingency bus voltage
TARA | PVShunt | Base Shunt MVAR | Nominal shunt MVAR output in basecase
TARA | PVShunt | Cont Shunt MVAR | Nominal shunt MVAR output in contingency
TARA | PVShunt | Shunt Flag | Mark "Changed" if shunt output is changed while MW transfer is increased
TARA | PVFlowgate | Sending System | Sending subsystem name
TARA | PVFlowgate | Receiving System | Receiving subsystem name
TARA | PVFlowgate | Worst Limit Flag | Identify contingencies with lowest transfer limits (NC, Vmag, Vdrop, BranOL, and FGOL). See TARA Manual for detail
TARA | PVFlowgate | MW Transfer | Test MW transfer
TARA | PVFlowgate | Index | Flowgate index
TARA | PVFlowgate | Flowgate Name | Flowgate name
TARA | PVFlowgate | Cont Name | Contingency Name
TARA | PVFlowgate | Cont ID | Contingency ID
TARA | PVFlowgate | Rating | Flowgate rating
TARA | PVFlowgate | Base MW | Pre-contingency MW flow
TARA | PVFlowgate | Cont MW | Post-contingency MW flow
TARA | PVFlowgate | Knee Flag | Knee if a post-contingency interface flow reversal occurs while transfer is increased
TARA | PVFlowgate | Base MVAR Flow | Pre-contingency MVAR flow
TARA | PVFlowgate | Cont MVAR Flow | Post-contingency MVAR flow
TARA | PVFlowgate | Base MW Loss | Pre-contingency MW loss
TARA | PVFlowgate | Cont MW Loss | Post-contingency MW loss
TARA | PVFlowgate | Base MVAR Loss | Pre-contingency MVAR loss
TARA | PVFlowgate | Cont MVAR Loss | Post-contingency MVAR loss
TARA | PVFlowgate | dMW Loss | MW loss difference between pre- and post-contingencies
TARA | PVFlowgate | dMVAR Loss | MVAR loss difference between pre- and post-contingencies
TARA | PVFlowgate | Final DC %Loading | Final % loading – linear (DC) solution
TARA | PVFlowgate | Final AC %Loading | Final % loading – nonlinear (AC) solution
TARA | PVVoltage | Sending System | Sending subsystem name
TARA | PVVoltage | Receiving System | Receiving subsystem name
TARA | PVVoltage | Worst Limit Flag | Identify contingencies with lowest transfer limits (NC, Vmag, Vdrop, BranOL, and FGOL). See TARA Manual for detail
TARA | PVVoltage | MW Transfer | Test MW transfer
TARA | PVVoltage | Bus # | Bus Number
TARA | PVVoltage | Bus Name | Bus Name
TARA | PVVoltage | Base kV | Bus Base kV
TARA | PVVoltage | Area | Bus Area Number
TARA | PVVoltage | Area Name | Bus Area Name
TARA | PVVoltage | Zone | Bus Zone Number
TARA | PVVoltage | Zone Name | Bus Zone Name
TARA | PVVoltage | Bus Type | Bus type
TARA | PVVoltage | Pgen | MW generation
TARA | PVVoltage | Pload | MW load
TARA | PVVoltage | G Shunt | Active component of shunt admittance
TARA | PVVoltage | B Shunt | Reactive component of shunt admittance
TARA | PVVoltage | Min Volt Limit | Low voltage limit
TARA | PVVoltage | Max Volt Limit | High voltage limit
TARA | PVVoltage | %Vdrop Limit | Post-contingency voltage drop limit
TARA | PVVoltage | %Vrise Limit | Post-contingency voltage rise limit
TARA | PVVoltage | Cont Name | Contingency Name
TARA | PVVoltage | Cont ID | Contingency ID
TARA | PVVoltage | Base Volt | Pre-contingency bus voltage
TARA | PVVoltage | Cont Volt | Post-contingency bus voltage
TARA | PVVoltage | %Vdrop | % voltage drop
TARA | PVVoltage | Vmag Violation | Low, Worst Low, High, and Worst High voltage magnitude violation
TARA | PVVoltage | Vchng Violation | Drop, Worst Drop, Rise, Worst Rise voltage violation
TARA | PVVoltage | # of Branches | # of branches connected after contingency events
TARA | PVVoltage | Radial Index | Radial index (= 1.0, 1.0 = radial). See TARA Manual for details.
TARA | PVVoltage | Max MW Flow | Max MW bus injection or withdrawal
TARA | PVBranchFlow | Sending System | Sending subsystem name
TARA | PVBranchFlow | Receiving System | Receiving subsystem name
TARA | PVBranchFlow | Worst Limit Flag | Identify contingencies with lowest transfer limits (NC, Vmag, Vdrop, BranOL, and FGOL). See TARA Manual for detail
TARA | PVBranchFlow | MW Transfer | Test MW transfer
TARA | PVBranchFlow | Monitored Facility | Monitored facility
TARA | PVBranchFlow | Fr Bus | FROM bus number
TARA | PVBranchFlow | Fr Name | FROM bus name
TARA | PVBranchFlow | To Bus | TO bus number
TARA | PVBranchFlow | To Name | TO bus name
TARA | PVBranchFlow | CKT | Branch circuit identifier
TARA | PVBranchFlow | kVs | kV level(s)
TARA | PVBranchFlow | Areas | Area Number(s)
TARA | PVBranchFlow | Area Names | Area Name(s)
TARA | PVBranchFlow | Zones | Zone Numbers(s)
TARA | PVBranchFlow | Zone Names | Zone Name(s)
TARA | PVBranchFlow | Rate Base (MVA) | Monitored facility normal rating (MVA)
TARA | PVBranchFlow | Rate Cont (MVA) | Monitored facility contingency rating (MVA)
TARA | PVBranchFlow | Cont Name | Contingency Name
TARA | PVBranchFlow | Cont ID | Contingency ID
TARA | PVBranchFlow | Base MW Flow | Pre-contingency MW flow
TARA | PVBranchFlow | Cont MW Flow | Post-contingency MW flow
TARA | PVBranchFlow | Knee Flag | Knee if a post-contingency monitored facility flow reversal occurs while transfer is increased
TARA | PVBranchFlow | Dfax (pu) | Subsystem OTDF from the sending subsystem to the receiving subsystem
TARA | PVBranchFlow | Cont MVAR Flow | Post-contingency MVAR flow
TARA | PVBranchFlow | Cont MW Loss | Post-contingency MW loss
TARA | PVBranchFlow | Cont MVAR Loss | Post-contingency MVAR loss
TARA | PVBranchFlow | Base MVAR Flow | Pre-contingency MVAR flow
TARA | PVBranchFlow | Base MW Loss | Pre-contingency MW loss
TARA | PVBranchFlow | Base MVAR Loss | Pre-contingency MVAR loss
TARA | PVBranchFlow | dMW Loss | MW loss difference between pre- and post-contingencies
TARA | PVBranchFlow | dMVAR Loss | MVAR loss difference between pre- and post-contingencies
TARA | PVBranchFlow | Base dSen [deg] | Pre-contingency branch bus angle difference between the current transfer case and the previous transfer case divided by the incremental MW transfer
TARA | PVBranchFlow | Cont dSen [deg] | Post-contingency branch bus angle difference between the current transfer case and the previous transfer case divided by the incremental MW transfer
TARA | PVBranchFlow | Final DC %Loading | Final % loading – linear (DC) solution
TARA | PVBranchFlow | Final AC %Loading | Final % loading – nonlinear (AC) solution
TARA | PVBranchFlow | Fr Base Volt | Pre-contingency From bus voltage
TARA | PVBranchFlow | Fr Cont Volt | Post-contingency From bus voltage
TARA | PVBranchFlow | To Base Volt | Pre-contingency To bus voltage
TARA | PVBranchFlow | To Cont Volt | Post-contingency To bus voltage
TARA | PVBranchFlow | Radial Index | Radial index (= 1.0, 1.0 = radial). See TARA Manual for details.
N-1 AC SCD | SCD_BranLoadings | Monitored Facility | FROM bus TO bus circuit ID
N-1 AC SCD | SCD_BranLoadings | Fr Bus | FROM bus number
N-1 AC SCD | SCD_BranLoadings | Fr Name | FROM bus name
N-1 AC SCD | SCD_BranLoadings | To Bus | TO bus number
N-1 AC SCD | SCD_BranLoadings | To Name | TO bus name
N-1 AC SCD | SCD_BranLoadings | CKT | Circuit ID
N-1 AC SCD | SCD_BranLoadings | kVs | kV level(s) of From bus and To bus
N-1 AC SCD | SCD_BranLoadings | Areas | Area number(s) of From bus and To bus
N-1 AC SCD | SCD_BranLoadings | Rate Base (MVA) | Monitored facility normal rating (MVA)
N-1 AC SCD | SCD_BranLoadings | Rate Cont (MVA) | Monitored facility contingency rating (MVA)
N-1 AC SCD | SCD_BranLoadings | Cont Name | Contingency name
N-1 AC SCD | SCD_BranLoadings | Cont ID | Contingency index
N-1 AC SCD | SCD_BranLoadings | Initial Base Flow (Signed MVA) | The maximum MVA/Amp base case flow of the From and To ends of the branch, but with no SCD. Opposite MW flow direction for negative sign
N-1 AC SCD | SCD_BranLoadings | Initial Cont Flow (Signed MVA) | The maximum MVA/Amp contingency flow of the From and To ends of the branch, but with no SCD. Opposite MW flow direction for negative sign
N-1 AC SCD | SCD_BranLoadings | SCD Base Flow (Signed MVA) | The maximum MVA/Amp base case flow of the From and To ends of the branch, but with SCD. Opposite MW flow direction for negative sign
N-1 AC SCD | SCD_BranLoadings | SCD Cont Flow (Signed MVA) | The maximum MVA/Amp contingency flow of the From and To ends of the branch, but with SCD. Opposite MW flow direction for negative sign
N-1 AC SCD | SCD_BranLoadings | Flow Change (MVA) | For contingency: Initial Cont Flow – SCD Cont Flow, For basecase: Initial Base Flow – SCD Base Flow
N-1 AC SCD | SCD_BranLoadings | Initial AC %Loading | Percent loading of the maximum MVA/Amp flow of the From and To ends of the branch with no SCD.
N-1 AC SCD | SCD_BranLoadings | SCD AC %Loading | Percent loading of the maximum MVA/Amp flow of the From and To ends of the branch with SCD.
N-1 AC SCD | SCD_BranLoadings | Shadow Price ($/MW) | Amount that objective function would improve if constraint limit was relaxed by 1 MW
N-1 AC SCD | SCD_BranLoadings | Soft Exclude | Facility defined as soft excluded facility
N-1 AC SCD | SCD_BranLoadings | Severity Rank | Severity rank for monitored facility
N-1 AC SCD | SCD_BranLoadings | Radial Index | Radial index (≤ 1.0, 1.0 = radial)
N-1 AC SCD | SCD_BranLoadings | Base MW Flow | Base case MW flow from From bus - nonlinear (AC) solution. Opposite flow direction for negative sign
N-1 AC SCD | SCD_BranLoadings | Cont MW Flow | Contingency MW flow from From bus - nonlinear (AC) solution. Opposite flow direction for negative sign
N-1 AC SCD | SCD_BranLoadings | Base MVAR Flow | Base case MVAR flow, AC solution. Opposite flow direction for negative sign
N-1 AC SCD | SCD_BranLoadings | Cont MVAR Flow | Contingency MVAR flow from From bus. Opposite flow direction for negative sign
N-1 AC SCD | SCD_BranLoadings | Fr Base Volt | FROM bus base case voltage
N-1 AC SCD | SCD_BranLoadings | Fr Cont Volt | FROM bus contingency voltage
N-1 AC SCD | SCD_BranLoadings | To Base Volt | TO bus base case voltage
N-1 AC SCD | SCD_BranLoadings | To Cont Volt | TO bus contingency voltage
N-1 AC SCD | SCD_BranLoadings | Base dAngle [deg] | Base case branch bus angle difference
N-1 AC SCD | SCD_BranLoadings | Cont dAngle [deg] | Post-contingency branch bus angle difference
N-1 AC SCD | SCD_BranLoadings | Pre-RAS %Loading | %Loading after the contingency but before RAS is applied
N-1 AC SCD | SCD_BranLoadings | RAS Name | Name of RAS
N-1 AC SCD | SCD_BranLoadings | RAS Index | Index of RAS (numbered in order of input)
N-1 AC SCD | SCD_BranLoadings | RAS resolves all overloads? | Yes if all branches are below 100% after RAS is applied
N-1 AC SCD | SCD_BranLoadings | Number of Overloads After RAS | Number of branches over 100% after RAS is applied
N-1 AC SCD | SCD_BranLoadings | Overload Index After RAS | Sum of (%Loading-100) for all branches over 100% after RAS is applied
N-1 AC SCD | SCD_BranLoadings | Worst %Overload After RAS | Highest %Loading among overloaded branches after RAS is applied
N-1 AC SCD | SCD_BranLoadings | RAS Islanded Load | Consequentially islanded load due to RAS application
N-1 AC SCD | SCD_BranLoadings | RAS Islanded Gen | Consequentially islanded generation due to RAS application
N-1-1 AC SCD | SCD_BranLoadings | First Level Scenario Index | First Level Contingency index
N-1-1 AC SCD | SCD_BranLoadings | First Level Scenario | First Level Contingency name
N-1-1 AC SCD | SCD_BranLoadings | Monitored Facility | FROM bus TO bus circuit ID
N-1-1 AC SCD | SCD_BranLoadings | Fr Bus | FROM bus number
N-1-1 AC SCD | SCD_BranLoadings | Fr Name | FROM bus name
N-1-1 AC SCD | SCD_BranLoadings | To Bus | TO bus number
N-1-1 AC SCD | SCD_BranLoadings | To Name | TO bus name
N-1-1 AC SCD | SCD_BranLoadings | CKT | Circuit ID
N-1-1 AC SCD | SCD_BranLoadings | kVs | kV level(s) of From bus and To bus
N-1-1 AC SCD | SCD_BranLoadings | Areas | Area number(s) of From bus and To bus
N-1-1 AC SCD | SCD_BranLoadings | Rate Base (MVA) | Monitored facility normal rating (MVA)
N-1-1 AC SCD | SCD_BranLoadings | Rate Cont (MVA) | Monitored facility contingency rating (MVA)
N-1-1 AC SCD | SCD_BranLoadings | Cont Name | Contingency name
N-1-1 AC SCD | SCD_BranLoadings | Cont ID | Contingency index
N-1-1 AC SCD | SCD_BranLoadings | Initial Base Flow (Signed MVA) | The maximum MVA/Amp base case (N-1-0) flow of the From and To ends of the branch after the first-level contingency applied, but with no SCD. Opposite MW flow direction for negative sign
N-1-1 AC SCD | SCD_BranLoadings | Initial Cont Flow (Signed MVA) | The maximum MVA/Amp contingency (N-1-1) of the From and To ends of the branch after both the first- and second-level contingencies applied, but with no SCD. Opposite MW flow direction for negative sign
N-1-1 AC SCD | SCD_BranLoadings | SCD Base Flow (Signed MVA) | The maximum MVA/Amp basecase (N-1-0) flow of the From and To ends of the branch after the first-level contingency applied, but with SCD. Opposite MW flow direction for negative sign
N-1-1 AC SCD | SCD_BranLoadings | SCD Cont Flow (Signed MVA) | The maximum MVA/Amp contingency (N-1-1) flow of the From and To ends of the branch after applying both the first-and second-level contingencies, but with SCD. Opposite MW flow direction for negative sign
N-1-1 AC SCD | SCD_BranLoadings | Orig Case Cont AC %Loading | Percent loading of the maximum MVA/Amp N-0-1 flow of the From and To ends of the branch after applying only second-level contingency
N-1-1 AC SCD | SCD_BranLoadings | Initial AC %Loading | Percent loading of the maximum MVA/Amp flow of the From and To ends of the branch after applying both the first- and second-level contingencies with no SCD. (i.e. N-1-0 for base case and N-1-1 for contingency AC %Loading with no SCD).
N-1-1 AC SCD | SCD_BranLoadings | SCD AC %Loading | Percent loading of the maximum MVA/Amp flow of the From and To ends of the branch after applying both the first- and second-level contingencies with SCD (i.e. N-1-1 AC %Loading with SCD).
N-1-1 AC SCD | SCD_BranLoadings | Shadow Price ($/MW) | Amount that objective function would improve if constraint limit was relaxed by 1 MW
N-1-1 AC SCD | SCD_BranLoadings | Soft Exclude | Facility defined as soft excluded facility
N-1-1 AC SCD | SCD_BranLoadings | Severity Rank | Severity rank for monitored facility
N-1-1 AC SCD | SCD_BranLoadings | Radial Index | Radial index (≤ 1.0, 1.0 = radial)
N-1-1 AC SCD | SCD_BranLoadings | Base MW Flow | Base case (N-1-0) MW flow from From bus - nonlinear (AC) solution. Opposite flow direction for negative sign
N-1-1 AC SCD | SCD_BranLoadings | Cont MW Flow | Contingency (N-1-1) MW flow from From bus - nonlinear (AC) solution. Opposite flow direction for negative sign
N-1-1 AC SCD | SCD_BranLoadings | Base MVAR Flow | Base case (N-1-0) MVAR flow, AC solution. Opposite flow direction for negative sign
N-1-1 AC SCD | SCD_BranLoadings | Cont MVAR Flow | Contingency (N-1-1) MVAR flow from From bus. Opposite flow direction for negative sign
N-1-1 AC SCD | SCD_BranLoadings | Fr Base Volt | FROM bus base case (N-1-0) voltage
N-1-1 AC SCD | SCD_BranLoadings | Fr Cont Volt | FROM bus contingency (N-1-1) voltage
N-1-1 AC SCD | SCD_BranLoadings | To Base Volt | TO bus base case (N-1-0) voltage
N-1-1 AC SCD | SCD_BranLoadings | To Cont Volt | TO bus contingency (N-1-0) voltage
N-1-1 AC SCD | SCD_BranLoadings | Base dAngle [deg] | Base case (N-1-0) branch bus angle difference
N-1-1 AC SCD | SCD_BranLoadings | Pre-RAS %Loading | %Loading after the contingency but before RAS is applied
N-1-1 AC SCD | SCD_BranLoadings | RAS Name | Name of RAS
N-1-1 AC SCD | SCD_BranLoadings | RAS Index | Index of RAS (numbered in order of input)
N-1-1 AC SCD | SCD_BranLoadings | RAS resolves all overloads? | Yes if all branches are below 100% after RAS is applied
N-1-1 AC SCD | SCD_BranLoadings | Number of Overloads After RAS | Number of branches over 100% after RAS is applied
N-1-1 AC SCD | SCD_BranLoadings | Overload Index After RAS | Sum of (%Loading-100) for all branches over 100% after RAS is applied
N-1-1 AC SCD | SCD_BranLoadings | Worst %Overload After RAS | Highest %Loading among overloaded branches after RAS is applied
N-1-1 AC SCD | SCD_BranLoadings | RAS Islanded Load | Consequentially islanded load due to RAS application
N-1-1 AC SCD | SCD_BranLoadings | RAS Islanded Gen | Consequentially islanded generation due to RAS application
N-1-1 AC SCD | SCD_BranLoadings | Cont dAngle [deg] | Post-contingency (N-1-1) branch bus angle difference
N-1 DC SCD | SCD_BranLoadings | Monitored Facility | FROM bus TO bus circuit ID
N-1 DC SCD | SCD_BranLoadings | Fr Bus | FROM bus number
N-1 DC SCD | SCD_BranLoadings | Fr Name | FROM bus name
N-1 DC SCD | SCD_BranLoadings | To Bus | TO bus number
N-1 DC SCD | SCD_BranLoadings | To Name | TO bus name
N-1 DC SCD | SCD_BranLoadings | CKT | Circuit ID
N-1 DC SCD | SCD_BranLoadings | kVs | kV level(s) of From bus and To bus
N-1 DC SCD | SCD_BranLoadings | Areas | Area number(s) of From bus and To bus
N-1 DC SCD | SCD_BranLoadings | Rate Base (MVA) | Monitored facility normal rating (MVA)
N-1 DC SCD | SCD_BranLoadings | Rate Cont (MVA) | Monitored facility contingency rating (MVA)
N-1 DC SCD | SCD_BranLoadings | Cont Name | Contingency name
N-1 DC SCD | SCD_BranLoadings | Cont ID | Contingency index
N-1 DC SCD | SCD_BranLoadings | Initial Base Flow (MW) | Pre-contingency AC-solved MW flow on metered end of the branch with no SCD. Opposite MW flow direction for negative sign
N-1 DC SCD | SCD_BranLoadings | Initial Cont Flow (MW) | Post-contingency estimated MW flow on monitored branch with no SCD. Opposite MW flow direction for negative sign
N-1 DC SCD | SCD_BranLoadings | SCD Base Flow (MW) | Pre-contingency AC-solved MW flow on metered end of the branch with SCD. Opposite MW flow direction for negative sign
N-1 DC SCD | SCD_BranLoadings | SCD Cont Flow (MW) | Post-contingency estimated MW flow on monitored branch with SCD. Opposite MW flow direction for negative sign
N-1 DC SCD | SCD_BranLoadings | Flow Change (MW) | For contingency: Initial Cont Flow – SCD Cont Flow, For basecase: Initial Base Flow – SCD Base Flow
N-1 DC SCD | SCD_BranLoadings | Initial DC %Loading | Percent DC loading with no SCD.
N-1 DC SCD | SCD_BranLoadings | SCD DC %Loading | Percent DC loading with SCD.
N-1 DC SCD | SCD_BranLoadings | Shadow Price ($/MW) | Amount that objective function would improve if constraint limit was relaxed by 1 MW
N-1 DC SCD | SCD_BranLoadings | Severity Rank | Severity rank for monitored facility (See TARA Manual for detail)
N-1-1 DC SCD | SCD_BranLoadings | First Level Scenario Index | First Level Contingency index
N-1-1 DC SCD | SCD_BranLoadings | First Level Scenario | First Level Contingency name
N-1-1 DC SCD | SCD_BranLoadings | Monitored Facility | FROM bus TO bus circuit ID
N-1-1 DC SCD | SCD_BranLoadings | Fr Bus | FROM bus number
N-1-1 DC SCD | SCD_BranLoadings | Fr Name | FROM bus name
N-1-1 DC SCD | SCD_BranLoadings | To Bus | TO bus number
N-1-1 DC SCD | SCD_BranLoadings | To Name | TO bus name
N-1-1 DC SCD | SCD_BranLoadings | CKT | Circuit ID
N-1-1 DC SCD | SCD_BranLoadings | kVs | kV level(s) of From bus and To bus
N-1-1 DC SCD | SCD_BranLoadings | Areas | Area number(s) of From bus and To bus
N-1-1 DC SCD | SCD_BranLoadings | Rate Base (MVA) | Monitored facility normal rating (MVA)
N-1-1 DC SCD | SCD_BranLoadings | Rate Cont (MVA) | Monitored facility contingency rating (MVA)
N-1-1 DC SCD | SCD_BranLoadings | Cont Name | Contingency name
N-1-1 DC SCD | SCD_BranLoadings | Cont ID | Contingency index
N-1-1 DC SCD | SCD_BranLoadings | Initial Base Flow (MW) | N-1-0 base case AC-solved MW flow on metered end of the branch with no SCD. Opposite MW flow direction for negative sign
N-1-1 DC SCD | SCD_BranLoadings | Initial Cont Flow (MW) | N-1-1 post-contingency estimated MW flow on monitored branch with no SCD. Opposite MW flow direction for negative sign
N-1-1 DC SCD | SCD_BranLoadings | SCD Base Flow (MW) | N-1-0 base case AC-solved MW flow on metered end of the branch with SCD. Opposite MW flow direction for negative sign
N-1-1 DC SCD | SCD_BranLoadings | SCD Cont Flow (MW) | N-1-1 post-contingency estimated MW flow on monitored branch with SCD. Opposite MW flow direction for negative sign
N-1-1 DC SCD | SCD_BranLoadings | Flow Change (MW) | For contingency: Initial Cont Flow – SCD Cont Flow, For basecase: Initial Base Flow – SCD Base Flow
N-1-1 DC SCD | SCD_BranLoadings | Orig Case Cont %Loading | DC Percent loading after applying only second-level contingency
N-1-1 DC SCD | SCD_BranLoadings | Initial DC %Loading | Percent DC loading with no SCD.
N-1-1 DC SCD | SCD_BranLoadings | SCD DC %Loading | Percent DC loading with SCD.
N-1-1 DC SCD | SCD_BranLoadings | Shadow Price ($/MW) | Amount that objective function would improve if constraint limit was relaxed by 1 MW
N-1-1 DC SCD | SCD_BranLoadings | Severity Rank | Severity rank for monitored facility (See TARA Manual for detail)
N-1-1 DC SCD ACVerify | SCD_BranLoadings | First Level Scenario Index | First Level Contingency index
N-1-1 DC SCD ACVerify | SCD_BranLoadings | First Level Scenario | First Level Contingency name
N-1-1 DC SCD ACVerify | SCD_BranLoadings | Monitored Facility | FROM bus TO bus circuit ID
N-1-1 DC SCD ACVerify | SCD_BranLoadings | Fr Bus | FROM bus number
N-1-1 DC SCD ACVerify | SCD_BranLoadings | Fr Name | FROM bus name
N-1-1 DC SCD ACVerify | SCD_BranLoadings | To Bus | TO bus number
N-1-1 DC SCD ACVerify | SCD_BranLoadings | To Name | TO bus name
N-1-1 DC SCD ACVerify | SCD_BranLoadings | CKT | Circuit ID
N-1-1 DC SCD ACVerify | SCD_BranLoadings | kVs | kV level(s) of From bus and To bus
N-1-1 DC SCD ACVerify | SCD_BranLoadings | Areas | Area number(s) of From bus and To bus
N-1-1 DC SCD ACVerify | SCD_BranLoadings | Rate Base (MVA) | Monitored facility normal rating (MVA)
N-1-1 DC SCD ACVerify | SCD_BranLoadings | Rate Cont (MVA) | Monitored facility contingency rating (MVA)
N-1-1 DC SCD ACVerify | SCD_BranLoadings | Cont Name | Contingency name
N-1-1 DC SCD ACVerify | SCD_BranLoadings | Cont ID | Contingency index
N-1-1 DC SCD ACVerify | SCD_BranLoadings | Initial Base Flow (MW) | N-1-0 base case AC-solved MW flow on metered end of the branch with no SCD. Opposite MW flow direction for negative sign
N-1-1 DC SCD ACVerify | SCD_BranLoadings | Initial Cont Flow (MW) | N-1-1 post-contingency estimated MW flow on monitored branch with no SCD. Opposite MW flow direction for negative sign
N-1-1 DC SCD ACVerify | SCD_BranLoadings | SCD Base Flow (MW) | N-1-0 base case AC-solved MW flow on metered end of the branch with SCD. Opposite MW flow direction for negative sign
N-1-1 DC SCD ACVerify | SCD_BranLoadings | SCD Cont Flow (MW) | N-1-1 post-contingency estimated MW flow on monitored branch with SCD. Opposite MW flow direction for negative sign
N-1-1 DC SCD ACVerify | SCD_BranLoadings | Flow Change (MW) | For contingency: Initial Cont Flow – SCD Cont Flow, For basecase: Initial Base Flow – SCD Base Flow
N-1-1 DC SCD ACVerify | SCD_BranLoadings | Orig Case Cont AC %Loading | DC Percent loading after applying only second-level contingency
N-1-1 DC SCD ACVerify | SCD_BranLoadings | Initial DC %Loading | Percent DC loading with no SCD.
N-1-1 DC SCD ACVerify | SCD_BranLoadings | SCD DC %Loading | Percent DC loading with SCD.
N-1-1 DC SCD ACVerify | SCD_BranLoadings | Shadow Price ($/MW) | Amount that objective function would improve if constraint limit was relaxed by 1 MW
N-1-1 DC SCD ACVerify | SCD_BranLoadings | AC Verify %Loading | Percent AC loading with SCD.
N-1-1 DC SCD ACVerify | SCD_BranLoadings | Severity Rank | Severity rank for monitored facility (See TARA Manual for detail)
N-1-1 DC SCD ACVerify | SCD_BranLoadings | Radial Index | Radial index (≤ 1.0, 1.0 = radial)
N-1-1 DC SCD ACVerify | SCD_BranLoadings | Base MW Flow | Base case (N-1-0) MW flow from From bus - nonlinear (AC) solution. Opposite flow direction for negative sign
N-1-1 DC SCD ACVerify | SCD_BranLoadings | Cont MW Flow | Contingency (N-1-1) MW flow from From bus - nonlinear (AC) solution. Opposite flow direction for negative sign
N-1-1 DC SCD ACVerify | SCD_BranLoadings | Base MVAR Flow | Base case (N-1-0) MVAR flow, AC solution. Opposite flow direction for negative sign
N-1-1 DC SCD ACVerify | SCD_BranLoadings | Cont MVAR Flow | Contingency (N-1-1) MVAR flow from From bus. Opposite flow direction for negative sign
N-1-1 DC SCD ACVerify | SCD_BranLoadings | Fr Base Volt | FROM bus base case (N-1-0) voltage
N-1-1 DC SCD ACVerify | SCD_BranLoadings | Fr Cont Volt | FROM bus contingency (N-1-1) voltage
N-1-1 DC SCD ACVerify | SCD_BranLoadings | To Base Volt | TO bus base case (N-1-0) voltage
N-1-1 DC SCD ACVerify | SCD_BranLoadings | To Cont Volt | TO bus contingency (N-1-0) voltage
N-1-1 DC SCD ACVerify | SCD_BranLoadings | Base dAngle [deg] | Base case (N-1-0) branch bus angle difference
N-1-1 DC SCD ACVerify | SCD_BranLoadings | Cont dAngle [deg] | Post-contingency (N-1-1) branch bus angle difference
N-1 DC SCD ACVerify | SCD_BranLoadings | Monitored Facility | FROM bus TO bus circuit ID
N-1 DC SCD ACVerify | SCD_BranLoadings | Fr Bus | FROM bus number
N-1 DC SCD ACVerify | SCD_BranLoadings | Fr Name | FROM bus name
N-1 DC SCD ACVerify | SCD_BranLoadings | To Bus | TO bus number
N-1 DC SCD ACVerify | SCD_BranLoadings | To Name | TO bus name
N-1 DC SCD ACVerify | SCD_BranLoadings | CKT | Circuit ID
N-1 DC SCD ACVerify | SCD_BranLoadings | kVs | kV level(s) of From bus and To bus
N-1 DC SCD ACVerify | SCD_BranLoadings | Areas | Area number(s) of From bus and To bus
N-1 DC SCD ACVerify | SCD_BranLoadings | Rate Base (MVA) | Monitored facility normal rating (MVA)
N-1 DC SCD ACVerify | SCD_BranLoadings | Rate Cont (MVA) | Monitored facility contingency rating (MVA)
N-1 DC SCD ACVerify | SCD_BranLoadings | Cont Name | Contingency name
N-1 DC SCD ACVerify | SCD_BranLoadings | Cont ID | Contingency index
N-1 DC SCD ACVerify | SCD_BranLoadings | Initial Base Flow (MW) | Pre-contingency AC-solved MW flow on metered end of the branch with no SCD. Opposite MW flow direction for negative sign
N-1 DC SCD ACVerify | SCD_BranLoadings | Initial Cont Flow (MW) | Post-contingency estimated MW flow on monitored branch with no SCD. Opposite MW flow direction for negative sign
N-1 DC SCD ACVerify | SCD_BranLoadings | SCD Base Flow (MW) | Pre-contingency AC-solved MW flow on metered end of the branch with SCD. Opposite MW flow direction for negative sign
N-1 DC SCD ACVerify | SCD_BranLoadings | SCD Cont Flow (MW) | Post-contingency estimated MW flow on monitored branch with SCD. Opposite MW flow direction for negative sign
N-1 DC SCD ACVerify | SCD_BranLoadings | Flow Change (MW) | For contingency: Initial Cont Flow – SCD Cont Flow, For basecase: Initial Base Flow – SCD Base Flow
N-1 DC SCD ACVerify | SCD_BranLoadings | Initial DC %Loading | Percent DC loading with no SCD.
N-1 DC SCD ACVerify | SCD_BranLoadings | SCD DC %Loading | Percent DC loading with SCD.
N-1 DC SCD ACVerify | SCD_BranLoadings | Shadow Price ($/MW) | Amount that objective function would improve if constraint limit was relaxed by 1 MW
N-1 DC SCD ACVerify | SCD_BranLoadings | AC Verify %Loading | Percent AC loading with SCD.
N-1 DC SCD ACVerify | SCD_BranLoadings | Severity Rank | Severity rank for monitored facility (See TARA Manual for detail)
N-1 DC SCD ACVerify | SCD_BranLoadings | Radial Index | Radial index (≤ 1.0, 1.0 = radial)
N-1 DC SCD ACVerify | SCD_BranLoadings | Base MW Flow | Base case (N-1-0) MW flow from From bus - nonlinear (AC) solution. Opposite flow direction for negative sign
N-1 DC SCD ACVerify | SCD_BranLoadings | Cont MW Flow | Contingency (N-1-1) MW flow from From bus - nonlinear (AC) solution. Opposite flow direction for negative sign
N-1 DC SCD ACVerify | SCD_BranLoadings | Base MVAR Flow | Base case (N-1-0) MVAR flow, AC solution. Opposite flow direction for negative sign
N-1 DC SCD ACVerify | SCD_BranLoadings | Cont MVAR Flow | Contingency (N-1-1) MVAR flow from From bus. Opposite flow direction for negative sign
N-1 DC SCD ACVerify | SCD_BranLoadings | Fr Base Volt | FROM bus base case (N-1-0) voltage
N-1 DC SCD ACVerify | SCD_BranLoadings | Fr Cont Volt | FROM bus contingency (N-1-1) voltage
N-1 DC SCD ACVerify | SCD_BranLoadings | To Base Volt | TO bus base case (N-1-0) voltage
N-1 DC SCD ACVerify | SCD_BranLoadings | To Cont Volt | TO bus contingency (N-1-0) voltage
N-1 DC SCD ACVerify | SCD_BranLoadings | Base dAngle [deg] | Base case (N-1-0) branch bus angle difference
N-1 DC SCD ACVerify | SCD_BranLoadings | Cont dAngle [deg] | Post-contingency (N-1-1) branch bus angle difference
N-1 DCCONT | DCCONT | Monitored Facility | Complete branch information
N-1 DCCONT | DCCONT | Fr Bus | FROM bus number
N-1 DCCONT | DCCONT | Fr Name | FROM bus name
N-1 DCCONT | DCCONT | To Bus | TO bus number
N-1 DCCONT | DCCONT | To Name | TO bus name
N-1 DCCONT | DCCONT | CKT | Circuit ID
N-1 DCCONT | DCCONT | kVs | kV level(s)
N-1 DCCONT | DCCONT | Areas Name | Area name(s)
N-1 DCCONT | DCCONT | Zones Name | Zone name(s)
N-1 DCCONT | DCCONT | Rate Base (MVA) | Monitored facility normal rating (MVA)
N-1 DCCONT | DCCONT | Rate Cont (MVA) | Monitored facility contingency rating (MVA)
N-1 DCCONT | DCCONT | Cont Name | Contingency name
N-1 DCCONT | DCCONT | Cont ID | Contingency index
N-1 DCCONT | DCCONT | Base Flow (MW) | Pre-contingency AC-solved MW flow on metered end of the branch. Opposite MW flow direction for negative sign
N-1 DCCONT | DCCONT | Cont Flow (MW) | Post-contingency estimated MW flow on monitored branch. Opposite MW flow direction for negative sign
N-1 DCCONT | DCCONT | Final DC %Loading | Percent loading for applicable rating
N-1 DCCONT | DCCONT | Soft Exclude | Facility defined as soft excluded facility
N-1 DCCONT | DCCONT | Severity Rank | Severity rank for monitored facility
N-1 DCCONT | DCCONT | Pre-RAS %Loading | %Loading after the contingency but before RAS is applied
N-1 DCCONT | DCCONT | RAS Name | Name of RAS
N-1 DCCONT | DCCONT | RAS Index | Index of RAS (numbered in order of input)
N-1 DCCONT | DCCONT | RAS resolves all overloads? | Yes if all branches are below 100% after RAS is applied
N-1 DCCONT | DCCONT | Number of Overloads After RAS | Number of branches over 100% after RAS is applied
N-1 DCCONT | DCCONT | Overload Index After RAS | Sum of (%Loading-100) for all branches over 100% after RAS is applied
N-1 DCCONT | DCCONT | Worst %Overload After RAS | Highest %Loading among overloaded branches after RAS is applied
N-1 DCCONT | DCCONT | RAS Islanded Load | Consequentially islanded load due to RAS application
N-1 DCCONT | DCCONT | RAS Islanded Gen | Consequentially islanded generation due to RAS application
N-1-1 DCCONT | DCCONT | First Level Scenario Index | First Level Contingency index
N-1-1 DCCONT | DCCONT | First Level Scenario | First Level Contingency name
N-1-1 DCCONT | DCCONT | Monitored Facility | Complete branch information
N-1-1 DCCONT | DCCONT | Fr Bus | FROM bus number
N-1-1 DCCONT | DCCONT | Fr Name | FROM bus name
N-1-1 DCCONT | DCCONT | To Bus | TO bus number
N-1-1 DCCONT | DCCONT | To Name | TO bus name
N-1-1 DCCONT | DCCONT | CKT | Circuit ID
N-1-1 DCCONT | DCCONT | kVs | kV level(s)
N-1-1 DCCONT | DCCONT | Areas Name | Area name(s)
N-1-1 DCCONT | DCCONT | Zones Name | Zone name(s)
N-1-1 DCCONT | DCCONT | Rate Base (MVA) | Monitored facility normal rating (MVA)
N-1-1 DCCONT | DCCONT | Rate Cont (MVA) | Monitored facility contingency rating (MVA)
N-1-1 DCCONT | DCCONT | Cont Name | Contingency name
N-1-1 DCCONT | DCCONT | Cont ID | Contingency index
N-1-1 DCCONT | DCCONT | Base Flow (MW) | Pre-contingency AC-solved MW flow on metered end of the branch after the first-level contingency applied. Opposite MW flow direction for negative sign
N-1-1 DCCONT | DCCONT | Cont Flow (MW) | Post-contingency estimated MW flow on monitored branch after the first-level contingency applied. Opposite MW flow direction for negative sign
N-1-1 DCCONT | DCCONT | Orig Case Cont %Loading | Percent loading after applying only second-level contingency (i.e. N-0-1 percent loading)
N-1-1 DCCONT | DCCONT | Final DC %Loading | Percent DC loading for applicable rating
N-1-1 DCCONT | DCCONT | Soft Exclude | Facility defined as soft excluded facility
N-1-1 DCCONT | DCCONT | Severity Rank | Severity rank for monitored facility
N-1-1 DCCONT | DCCONT | Pre-RAS %Loading | %Loading after the contingency but before RAS is applied
N-1-1 DCCONT | DCCONT | RAS Name | Name of RAS
N-1-1 DCCONT | DCCONT | RAS Index | Index of RAS (numbered in order of input)
N-1-1 DCCONT | DCCONT | RAS resolves all overloads? | Yes if all branches are below 100% after RAS is applied
N-1-1 DCCONT | DCCONT | Number of Overloads After RAS | Number of branches over 100% after RAS is applied
N-1-1 DCCONT | DCCONT | Overload Index After RAS | Sum of (%Loading-100) for all branches over 100% after RAS is applied
N-1-1 DCCONT | DCCONT | Worst %Overload After RAS | Highest %Loading among overloaded branches after RAS is applied
N-1-1 DCCONT | DCCONT | RAS Islanded Load | Consequentially islanded load due to RAS application
N-1-1 DCCONT | DCCONT | RAS Islanded Gen | Consequentially islanded generation due to RAS application
N-1 DC ACVerify | DCACVer | Monitored Facility | Complete branch information
N-1 DC ACVerify | DCACVer | Fr Bus | FROM bus number
N-1 DC ACVerify | DCACVer | Fr Name | FROM bus name
N-1 DC ACVerify | DCACVer | To Bus | TO bus number
N-1 DC ACVerify | DCACVer | To Name | TO bus name
N-1 DC ACVerify | DCACVer | CKT | Circuit ID
N-1 DC ACVerify | DCACVer | kVs | kV level(s)
N-1 DC ACVerify | DCACVer | Areas | Area name(s)
N-1 DC ACVerify | DCACVer | Rate Base (MVA) | Monitored facility normal rating (MVA)
N-1 DC ACVerify | DCACVer | Rate Cont (MVA) | Monitored facility contingency rating (MVA)
N-1 DC ACVerify | DCACVer | Cont Name | Contingency name
N-1 DC ACVerify | DCACVer | Cont ID | Contingency index
N-1 DC ACVerify | DCACVer | DC Base Flow (MW) | Pre-contingency AC-solved MW flow on metered end of the branch. Opposite MW flow direction for negative sign
N-1 DC ACVerify | DCACVer | AC Base Flow (MVA) | The maximum MVA/Amp base case flow of the From and To ends of the branch after the first-level contingency applied. Opposite MW flow direction for negative sign
N-1 DC ACVerify | DCACVer | DC Cont Flow (MW) | Post-contingency estimated MW flow on monitored branch. Opposite MW flow direction for negative sign
N-1 DC ACVerify | DCACVer | AC Cont Flow (MVA) | The maximum MVA/Amp contingency flow of the From and To ends of the branch. Opposite MW flow direction for negative sign
N-1 DC ACVerify | DCACVer | Final DC %Loading | Percent DC loading for applicable rating
N-1 DC ACVerify | DCACVer | Final AC %Loading | Percent loading of the maximum MVA/Amp flow of the From and To ends of the branch
N-1 DC ACVerify | DCACVer | Severity Rank | Severity rank for monitored facility (See TARA Manual for detail)
N-1 DC ACVerify | DCACVer | Radial Index | Radial index (≤ 1.0, 1.0 = radial)
N-1 DC ACVerify | DCACVer | Base MW Flow | Base case MW flow from From bus - nonlinear (AC) solution. Opposite flow direction for negative sign
N-1 DC ACVerify | DCACVer | Cont MW Flow | Contingency MW flow from From bus - nonlinear (AC) solution. Opposite flow direction for negative sign
N-1 DC ACVerify | DCACVer | Base MVAR Flow | Base case MVAR flow, AC solution. Opposite flow direction for negative sign
N-1 DC ACVerify | DCACVer | Cont MVAR Flow | Contingency MVAR flow from From bus. Opposite flow direction for negative sign
N-1 DC ACVerify | DCACVer | Fr Base Volt | FROM bus base case voltage
N-1 DC ACVerify | DCACVer | Fr Cont Volt | FROM bus contingency voltage
N-1 DC ACVerify | DCACVer | To Base Volt | TO bus base case voltage
N-1 DC ACVerify | DCACVer | To Cont Volt | TO bus contingency voltage
N-1 DC ACVerify | DCACVer | Base dAngle [deg] | Base case branch bus angle difference
N-1 DC ACVerify | DCACVer | Cont dAngle [deg] | Post-contingency branch bus angle difference
N-1 DC ACVerify | DCACVer | Pre-RAS %Loading | %Loading after the contingency but before RAS is applied
N-1 DC ACVerify | DCACVer | RAS Name | Name of RAS
N-1 DC ACVerify | DCACVer | RAS Index | Index of RAS (numbered in order of input)
N-1 DC ACVerify | DCACVer | RAS resolves all overloads? | Yes if all branches are below 100% after RAS is applied
N-1 DC ACVerify | DCACVer | Number of Overloads After RAS | Number of branches over 100% after RAS is applied
N-1 DC ACVerify | DCACVer | Overload Index After RAS | Sum of (%Loading-100) for all branches over 100% after RAS is applied
N-1 DC ACVerify | DCACVer | Worst %Overload After RAS | Highest %Loading among overloaded branches after RAS is applied
N-1 DC ACVerify | DCACVer | RAS Islanded Load | Consequentially islanded load due to RAS application
N-1 DC ACVerify | DCACVer | RAS Islanded Gen | Consequentially islanded generation due to RAS application
N-1-1 DC ACVerify | DCACVer | First Level Scenario Index | First Level Contingency index
N-1-1 DC ACVerify | DCACVer | First Level Scenario | First Level Contingency name
N-1-1 DC ACVerify | DCACVer | Monitored Facility | Complete branch information
N-1-1 DC ACVerify | DCACVer | Fr Bus | FROM bus number
N-1-1 DC ACVerify | DCACVer | Fr Name | FROM bus name
N-1-1 DC ACVerify | DCACVer | To Bus | TO bus number
N-1-1 DC ACVerify | DCACVer | To Name | TO bus name
N-1-1 DC ACVerify | DCACVer | CKT | Circuit ID
N-1-1 DC ACVerify | DCACVer | kVs | kV level(s)
N-1-1 DC ACVerify | DCACVer | Areas | Area name(s)
N-1-1 DC ACVerify | DCACVer | Rate Base (MVA) | Monitored facility normal rating (MVA)
N-1-1 DC ACVerify | DCACVer | Rate Cont (MVA) | Monitored facility contingency rating (MVA)
N-1-1 DC ACVerify | DCACVer | Cont Name | Contingency name
N-1-1 DC ACVerify | DCACVer | Cont ID | Contingency index
N-1-1 DC ACVerify | DCACVer | DC Base Flow (MW) | Pre-contingency AC-solved MW flow on metered end of the branch. Opposite MW flow direction for negative sign
N-1-1 DC ACVerify | DCACVer | AC Base Flow (MVA) | The maximum MVA/Amp base case flow of the From and To ends of the branch after the first-level contingency applied. Opposite MW flow direction for negative sign
N-1-1 DC ACVerify | DCACVer | DC Cont Flow (MW) | Post-contingency estimated MW flow on monitored branch. Opposite MW flow direction for negative sign
N-1-1 DC ACVerify | DCACVer | AC Cont Flow (MVA) | The maximum MVA/Amp contingency flow of the From and To ends of the branch. Opposite MW flow direction for negative sign
N-1-1 DC ACVerify | DCACVer | Orig Case Cont AC %Loading | Percent loading of the maximum MVA/Amp N-0-1 flow of the From and To ends of the branch after applying only second-level contingency
N-1-1 DC ACVerify | DCACVer | Final DC %Loading | Percent DC loading for applicable rating
N-1-1 DC ACVerify | DCACVer | Final AC %Loading | Percent loading of the maximum MVA/Amp flow of the From and To ends of the branch
N-1-1 DC ACVerify | DCACVer | Severity Rank | Severity rank for monitored facility (See TARA Manual for detail)
N-1-1 DC ACVerify | DCACVer | Radial Index | Radial index (≤ 1.0, 1.0 = radial)
N-1-1 DC ACVerify | DCACVer | Base MW Flow | Base case (N-1-0) MW flow from From bus - nonlinear (AC) solution. Opposite flow direction for negative sign
N-1-1 DC ACVerify | DCACVer | Cont MW Flow | Contingency (N-1-1) MW flow from From bus - nonlinear (AC) solution. Opposite flow direction for negative sign
N-1-1 DC ACVerify | DCACVer | Base MVAR Flow | Base case (N-1-0) MVAR flow, AC solution. Opposite flow direction for negative sign
N-1-1 DC ACVerify | DCACVer | Cont MVAR Flow | Contingency (N-1-1) MVAR flow from From bus. Opposite flow direction for negative sign
N-1-1 DC ACVerify | DCACVer | Fr Base Volt | FROM bus base case (N-1-0) voltage
N-1-1 DC ACVerify | DCACVer | Fr Cont Volt | FROM bus contingency (N-1-1) voltage
N-1-1 DC ACVerify | DCACVer | To Base Volt | TO bus base case (N-1-0) voltage
N-1-1 DC ACVerify | DCACVer | To Cont Volt | TO bus contingency (N-1-0) voltage
N-1-1 DC ACVerify | DCACVer | Base dAngle [deg] | Base case (N-1-0) branch bus angle difference
N-1-1 DC ACVerify | DCACVer | Cont dAngle [deg] | Post-contingency (N-1-1) branch bus angle difference
N-1-1 DC ACVerify | DCACVer | Pre-RAS %Loading | %Loading after the contingency but before RAS is applied
N-1-1 DC ACVerify | DCACVer | RAS Name | Name of RAS
N-1-1 DC ACVerify | DCACVer | RAS Index | Index of RAS (numbered in order of input)
N-1-1 DC ACVerify | DCACVer | RAS resolves all overloads? | Yes if all branches are below 100% after RAS is applied
N-1-1 DC ACVerify | DCACVer | Number of Overloads After RAS | Number of branches over 100% after RAS is applied
N-1-1 DC ACVerify | DCACVer | Overload Index After RAS | Sum of (%Loading-100) for all branches over 100% after RAS is applied
N-1-1 DC ACVerify | DCACVer | Worst %Overload After RAS | Highest %Loading among overloaded branches after RAS is applied
N-1-1 DC ACVerify | DCACVer | RAS Islanded Load | Consequentially islanded load due to RAS application
N-1-1 DC ACVerify | DCACVer | RAS Islanded Gen | Consequentially islanded generation due to RAS application
N-1 AC | BranchViol | Monitored Facility | FROM bus TO bus circuit ID
N-1 AC | BranchViol | Fr Bus | FROM bus number
N-1 AC | BranchViol | Fr Name | FROM bus name
N-1 AC | BranchViol | To Bus | TO bus number
N-1 AC | BranchViol | To Name | TO bus name
N-1 AC | BranchViol | CKT | Circuit ID
N-1 AC | BranchViol | kVs | kV level(s)
N-1 AC | BranchViol | Areas Name | Area name(s)
N-1 AC | BranchViol | Zones Name | Zone name(s)
N-1 AC | BranchViol | Rate Base (MVA) | Monitored facility normal rating (MVA)
N-1 AC | BranchViol | Rate Cont (MVA) | Monitored facility contingency rating (MVA)
N-1 AC | BranchViol | Cont Name | Contingency name
N-1 AC | BranchViol | Cont ID | Contingency index
N-1 AC | BranchViol | Base Flow (MVA) | The maximum MVA/Amp base case flow of the From and To ends of the branch. Opposite MW flow direction for negative sign
N-1 AC | BranchViol | Cont Flow (MVA) | The maximum MVA/Amp contingency flow of the From and To ends of the branch. Opposite MW flow direction for negative sign
N-1 AC | BranchViol | Final DC %Loading | Contingency % loading - linear (DC) solution
N-1 AC | BranchViol | Final AC %Loading | Contingency % loading of the maximum MVA/Amp flow of the From and To ends of the branch
N-1 AC | BranchViol | Soft Exclude | Facility defined as soft excluded facility
N-1 AC | BranchViol | Severity Rank | Severity rank for monitored facility
N-1 AC | BranchViol | Radial Index | Radial index (≤ 1.0, 1.0 = radial)
N-1 AC | BranchViol | Base MW Flow | Base case MW flow from From bus - nonlinear (AC) solution. Opposite flow direction for negative sign
N-1 AC | BranchViol | Cont MW Flow | Contingency MW flow from From bus - nonlinear (AC) solution. Opposite flow direction for negative sign
N-1 AC | BranchViol | Base MVAR Flow | Base case MVAR flow, AC solution. Opposite flow direction for negative sign
N-1 AC | BranchViol | Cont MVAR Flow | Contingency MVAR flow from From bus. Opposite flow direction for negative sign
N-1 AC | BranchViol | Fr Base Volt | FROM bus base case voltage
N-1 AC | BranchViol | Fr Cont Volt | FROM bus contingency voltage
N-1 AC | BranchViol | To Base Volt | TO bus base case voltage
N-1 AC | BranchViol | To Cont Volt | TO bus contingency voltage
N-1 AC | BranchViol | Base dAngle [deg] | Base case branch bus angle difference
N-1 AC | BranchViol | Cont dAngle [deg] | Post-contingency branch bus angle difference
N-1 AC | BranchViol | Pre-RAS %Loading | %Loading after the contingency but before RAS is applied
N-1 AC | BranchViol | RAS Name | Name of RAS
N-1 AC | BranchViol | RAS Index | Index of RAS (numbered in order of input)
N-1 AC | BranchViol | RAS resolves all overloads? | Yes if all branches are below 100% after RAS is applied
N-1 AC | BranchViol | Number of Overloads After RAS | Number of branches over 100% after RAS is applied
N-1 AC | BranchViol | Overload Index After RAS | Sum of (%Loading-100) for all branches over 100% after RAS is applied
N-1 AC | BranchViol | Worst %Overload After RAS | Highest %Loading among overloaded branches after RAS is applied
N-1 AC | BranchViol | RAS Islanded Load | Consequentially islanded load due to RAS application
N-1 AC | BranchViol | RAS Islanded Gen | Consequentially islanded generation due to RAS application
N-1-1 AC | BranchViol | First Level Scenario Index | First Level Contingency index
N-1-1 AC | BranchViol | First Level Scenario | First Level Contingency name
N-1-1 AC | BranchViol | Monitored Facility | FROM bus TO bus circuit ID
N-1-1 AC | BranchViol | Fr Bus | FROM bus number
N-1-1 AC | BranchViol | Fr Name | FROM bus name
N-1-1 AC | BranchViol | To Bus | TO bus number
N-1-1 AC | BranchViol | To Name | TO bus name
N-1-1 AC | BranchViol | CKT | Circuit ID
N-1-1 AC | BranchViol | kVs | kV level(s)
N-1-1 AC | BranchViol | Areas Name | Area name(s)
N-1-1 AC | BranchViol | Zones Name | Zone name(s)
N-1-1 AC | BranchViol | Rate Base (MVA) | Monitored facility normal rating (MVA)
N-1-1 AC | BranchViol | Rate Cont (MVA) | Monitored facility contingency rating (MVA)
N-1-1 AC | BranchViol | Cont Name | Contingency name
N-1-1 AC | BranchViol | Cont ID | Contingency index
N-1-1 AC | BranchViol | Base Flow (MVA) | The maximum MVA/Amp base case (N-1-0) flow of the From and To ends of the branch after the first-level contingency applied. Opposite MW flow direction for negative sign
N-1-1 AC | BranchViol | Cont Flow (MVA) | The maximum MVA/Amp contingency (N-1-1) flow of the From and To ends of the branch after both the first- and second-level contingencies applied. Opposite MW flow direction for negative sign
N-1-1 AC | BranchViol | Final DC %Loading | Contingency (N-1-1) % loading - linear (DC) solution
N-1-1 AC | BranchViol | Final AC %Loading | Percent loading of the maximum MVA/Amp flow of the From and To ends of the branch after applying both the first- and second-level contingencies (i.e. N-1-1 AC %Loading).
N-1-1 AC | BranchViol | Soft Exclude | Facility defined as soft excluded facility
N-1-1 AC | BranchViol | Severity Rank | Severity rank for monitored facility
N-1-1 AC | BranchViol | Radial Index | Radial index (≤ 1.0, 1.0 = radial)
N-1-1 AC | BranchViol | Base MW Flow | Base case (N-1-0) MW flow from From bus - nonlinear (AC) solution. Opposite flow direction for negative sign
N-1-1 AC | BranchViol | Cont MW Flow | Contingency (N-1-1) MW flow from From bus - nonlinear (AC) solution. Opposite flow direction for negative sign
N-1-1 AC | BranchViol | Base MVAR Flow | Base case (N-1-0) MVAR flow, AC solution. Opposite flow direction for negative sign
N-1-1 AC | BranchViol | Cont MVAR Flow | Contingency (N-1-1) MVAR flow from From bus. Opposite flow direction for negative sign
N-1-1 AC | BranchViol | Fr Base Volt | FROM bus base case (N-1-0) voltage
N-1-1 AC | BranchViol | Fr Cont Volt | FROM bus contingency (N-1-1) voltage
N-1-1 AC | BranchViol | To Base Volt | TO bus base case (N-1-0) voltage
N-1-1 AC | BranchViol | To Cont Volt | TO bus contingency (N-1-0) voltage
N-1-1 AC | BranchViol | Base dAngle [deg] | Base case (N-1-0) branch bus angle difference
N-1-1 AC | BranchViol | Cont dAngle [deg] | Post-contingency (N-1-1) branch bus angle difference
N-1-1 AC | BranchViol | Pre-RAS %Loading | %Loading after the contingency but before RAS is applied
N-1-1 AC | BranchViol | RAS Name | Name of RAS
N-1-1 AC | BranchViol | RAS Index | Index of RAS (numbered in order of input)
N-1-1 AC | BranchViol | RAS resolves all overloads? | Yes if all branches are below 100% after RAS is applied
N-1-1 AC | BranchViol | Number of Overloads After RAS | Number of branches over 100% after RAS is applied
N-1-1 AC | BranchViol | Overload Index After RAS | Sum of (%Loading-100) for all branches over 100% after RAS is applied
N-1-1 AC | BranchViol | Worst %Overload After RAS | Highest %Loading among overloaded branches after RAS is applied
N-1-1 AC | BranchViol | RAS Islanded Load | Consequentially islanded load due to RAS application
N-1-1 AC | BranchViol | RAS Islanded Gen | Consequentially islanded generation due to RAS application
Cascading Outage N-1 | BranchViol | Cont ID | Contingency index
Cascading Outage N-1 | BranchViol | Cont Name | Contingency name
Cascading Outage N-1 | BranchViol | Monitored Facility | FROM bus TO bus circuit ID
Cascading Outage N-1 | BranchViol | Fr Bus | FROM bus number
Cascading Outage N-1 | BranchViol | Fr Name | FROM bus name
Cascading Outage N-1 | BranchViol | To Bus | TO bus number
Cascading Outage N-1 | BranchViol | To Name | TO bus name
Cascading Outage N-1 | BranchViol | CKT | Circuit ID
Cascading Outage N-1 | BranchViol | kVs | kV level(s)
Cascading Outage N-1 | BranchViol | Areas Name | Area name(s)
Cascading Outage N-1 | BranchViol | Zones Name | Zone name(s)
Cascading Outage N-1 | BranchViol | Rate Base (MVA) | Monitored facility normal rating (MVA)
Cascading Outage N-1 | BranchViol | Rate Cont (MVA) | Monitored facility contingency rating (MVA)
Cascading Outage N-1 | BranchViol | Base Flow (MVA) | The maximum MVA/Amp base case flow of the From and To ends of the branch.
Cascading Outage N-1 | BranchViol | Step 0 Cont Flow (MVA) | The maximum MVA/Amp contingency flow of the From and To ends of the branch. No cascading outage applied.
Cascading Outage N-1 | BranchViol | Step 0 DC %Loading | Contingency (N-1) % loading - linear (DC) solution. No cascading outage applied.
Cascading Outage N-1 | BranchViol | Cascade Step | Casecase step. 0 means no cascading events have been applied.
Cascading Outage N-1 | BranchViol | Casecase Flow (MVA) | The maximum MVA/Amp flow of the From and To ends of the branch after applying cascading events
Cascading Outage N-1 | BranchViol | Cascade AC %Loading | Percent loading of the maximum MVA/Amp flow of the From and To ends of the branch after applying cascading events
Cascading Outage N-1 | BranchViol | Radial Index | Radial index (≤ 1.0, 1.0 = radial)
Cascading Outage N-1 | BranchViol | Base MW Flow | Base case MW flow from From bus - nonlinear (AC) solution. Opposite flow direction for negative sign
Cascading Outage N-1 | BranchViol | Cascade MW Flow | MW flow from From bus after applying cascading events - nonlinear (AC) solution. Opposite flow direction for negative sign
Cascading Outage N-1 | BranchViol | Base MVAR Flow | Base case MVAR flow, AC solution. Opposite flow direction for negative sign
Cascading Outage N-1 | BranchViol | Cascade MVAR Flow | MVAR flow from From bus after applying cascading events. Opposite flow direction for negative sign
Cascading Outage N-1 | BranchViol | Fr Base Volt | FROM bus base case voltage
Cascading Outage N-1 | BranchViol | Fr Cascade Volt | FROM bus voltage after applying cascade events
Cascading Outage N-1 | BranchViol | To Base Volt | TO bus base case voltage
Cascading Outage N-1 | BranchViol | To Cascade Volt | TO bus voltage after applying cascade events
Cascading Outage N-1 | BranchViol | Base dAngle [deg] | Base case branch bus angle difference
Cascading Outage N-1 | BranchViol | Cascade dAngle [deg] | Branch bus angle difference after applying cascading events
Cascading Outage N-1-1 | BranchViol | First Level Scenario Index | First Level Contingency index
Cascading Outage N-1-1 | BranchViol | First Level Scenario | First Level Contingency name
Cascading Outage N-1-1 | BranchViol | Cont ID | Contingency index
Cascading Outage N-1-1 | BranchViol | Cont Name | Contingency name
Cascading Outage N-1-1 | BranchViol | Monitored Facility | FROM bus TO bus circuit ID
Cascading Outage N-1-1 | BranchViol | Fr Bus | FROM bus number
Cascading Outage N-1-1 | BranchViol | Fr Name | FROM bus name
Cascading Outage N-1-1 | BranchViol | To Bus | TO bus number
Cascading Outage N-1-1 | BranchViol | To Name | TO bus name
Cascading Outage N-1-1 | BranchViol | CKT | Circuit ID
Cascading Outage N-1-1 | BranchViol | kVs | kV level(s)
Cascading Outage N-1-1 | BranchViol | Areas Name | Area name(s)
Cascading Outage N-1-1 | BranchViol | Zones Name | Zone name(s)
Cascading Outage N-1-1 | BranchViol | Rate Base (MVA) | Monitored facility normal rating (MVA)
Cascading Outage N-1-1 | BranchViol | Rate Cont (MVA) | Monitored facility contingency rating (MVA)
Cascading Outage N-1-1 | BranchViol | Base Flow (MVA) | The maximum MVA/Amp base case flow of the From and To ends of the branch.
Cascading Outage N-1-1 | BranchViol | Step 0 Cont Flow (MVA) | The maximum MVA/Amp contingency flow of the From and To ends of the branch. No cascading outage applied.
Cascading Outage N-1-1 | BranchViol | Step 0 DC %Loading | Contingency (N-1) % loading - linear (DC) solution. No cascading outage applied.
Cascading Outage N-1-1 | BranchViol | Cascade Step | Casecase step. 0 means no cascading events have been applied.
Cascading Outage N-1-1 | BranchViol | Casecase Flow (MVA) | The maximum MVA/Amp flow of the From and To ends of the branch after applying cascading events
Cascading Outage N-1-1 | BranchViol | Cascade AC %Loading | Percent loading of the maximum MVA/Amp flow of the From and To ends of the branch after applying cascading events
Cascading Outage N-1-1 | BranchViol | Radial Index | Radial index (≤ 1.0, 1.0 = radial)
Cascading Outage N-1-1 | BranchViol | Base MW Flow | Base case MW flow from From bus - nonlinear (AC) solution. Opposite flow direction for negative sign
Cascading Outage N-1-1 | BranchViol | Cascade MW Flow | MW flow from From bus after applying cascading events - nonlinear (AC) solution. Opposite flow direction for negative sign
Cascading Outage N-1-1 | BranchViol | Base MVAR Flow | Base case MVAR flow, AC solution. Opposite flow direction for negative sign
Cascading Outage N-1-1 | BranchViol | Cascade MVAR Flow | MVAR flow from From bus after applying cascading events. Opposite flow direction for negative sign
Cascading Outage N-1-1 | BranchViol | Fr Base Volt | FROM bus base case voltage
Cascading Outage N-1-1 | BranchViol | Fr Cascade Volt | FROM bus voltage after applying cascade events
Cascading Outage N-1-1 | BranchViol | To Base Volt | TO bus base case voltage
Cascading Outage N-1-1 | BranchViol | To Cascade Volt | TO bus voltage after applying cascade events
Cascading Outage N-1-1 | BranchViol | Base dAngle [deg] | Base case branch bus angle difference
Cascading Outage N-1-1 | BranchViol | Cascade dAngle [deg] | Branch bus angle difference after applying cascading events
N-1 VoltViol | VoltViol | Bus # | Bus number
N-1 VoltViol | VoltViol | Bus Name | Bus name
N-1 VoltViol | VoltViol | Base kV | Bus base kV
N-1 VoltViol | VoltViol | Area | Bus area number
N-1 VoltViol | VoltViol | Zone | Bus zone number
N-1 VoltViol | VoltViol | Pgen | Real power generation at bus
N-1 VoltViol | VoltViol | Pload | Real power load at bus
N-1 VoltViol | VoltViol | G Shunt | Real power shunt at bus
N-1 VoltViol | VoltViol | B Shunt | Reactive power shunt at bus
N-1 VoltViol | VoltViol | Min Volt Limit | Low voltage criteria for bus
N-1 VoltViol | VoltViol | Max Volt Limit | High voltage criteria for bus
N-1 VoltViol | VoltViol | %Vdrop Limit | Maximum voltage drop criteria for bus
N-1 VoltViol | VoltViol | %Vrise Limit | Maximum voltage rise criteria for bus
N-1 VoltViol | VoltViol | Cont Name | Contingency name
N-1 VoltViol | VoltViol | Cont ID | Contingency ID
N-1 VoltViol | VoltViol | Base Volt | Base case bus voltage
N-1 VoltViol | VoltViol | Cont Volt | Contingency voltage
N-1 VoltViol | VoltViol | %Vdrop | % voltage drop (negative for voltage rise)
N-1 VoltViol | VoltViol | Vmag Violation | Low, Worst Low, High, and Worst High voltage magnitude violation
N-1 VoltViol | VoltViol | Vchng Violation | Drop, Worst Drop, Rise, Worst Rise voltage violation
N-1 VoltViol | VoltViol | # of Branches | # of branches connected after continency events
N-1 VoltViol | VoltViol | Radial Index | Radial index (≤ 1.0, 1.0 = radial)
N-1 VoltViol | VoltViol | Max MW Flow | Max MW bus injection or withdrawal
N-1-1 VoltViol | VoltViol | First Level Scenario Index | First Level Contingency index
N-1-1 VoltViol | VoltViol | First Level Scenario | First Level Contingency name
N-1-1 VoltViol | VoltViol | Bus # | Bus number
N-1-1 VoltViol | VoltViol | Bus Name | Bus name
N-1-1 VoltViol | VoltViol | Base kV | Bus base kV
N-1-1 VoltViol | VoltViol | Area | Bus area number
N-1-1 VoltViol | VoltViol | Zone | Bus zone number
N-1-1 VoltViol | VoltViol | Pgen | Real power generation at bus
N-1-1 VoltViol | VoltViol | Pload | Real power load at bus
N-1-1 VoltViol | VoltViol | G Shunt | Real power shunt at bus
N-1-1 VoltViol | VoltViol | B Shunt | Reactive power shunt at bus
N-1-1 VoltViol | VoltViol | Min Volt Limit | Low voltage criteria for bus
N-1-1 VoltViol | VoltViol | Max Volt Limit | High voltage criteria for bus
N-1-1 VoltViol | VoltViol | %Vdrop Limit | Maximum voltage drop criteria for bus
N-1-1 VoltViol | VoltViol | %Vrise Limit | Maximum voltage rise criteria for bus
N-1-1 VoltViol | VoltViol | Cont Name | Contingency name
N-1-1 VoltViol | VoltViol | Cont ID | Contingency ID
N-1-1 VoltViol | VoltViol | Orig Case Cont Volt | Bus post-contingency voltage after applying only second-level contingency (i.e. N-0-1 bus voltage)
N-1-1 VoltViol | VoltViol | Base Volt | Bus base case voltage after applying only first-level contingency (i.e. N-1-0 bus voltage)
N-1-1 VoltViol | VoltViol | Cont Volt | Contingency voltage applying both the first-and second-level contingencies (i.e. N-1-1 bus voltage)
N-1-1 VoltViol | VoltViol | %Vdrop | % voltage drop (negative for voltage rise)
N-1-1 VoltViol | VoltViol | Vmag Violation | Low, Worst Low, High, and Worst High voltage magnitude violation
N-1-1 VoltViol | VoltViol | Vchng Violation | Drop, Worst Drop, Rise, Worst Rise voltage violation
N-1-1 VoltViol | VoltViol | # of Branches | # of branches connected after continency events
N-1-1 VoltViol | VoltViol | Radial Index | Radial index (≤ 1.0, 1.0 = radial)
N-1-1 VoltViol | VoltViol | Max MW Flow | Max MW bus injection or withdrawal
Cascading Outage N-1 | VoltViol | Cont ID | Contingency index
Cascading Outage N-1 | VoltViol | Cont Name | Contingency name
Cascading Outage N-1 | VoltViol | Bus # | Bus number
Cascading Outage N-1 | VoltViol | Bus Name | Bus name
Cascading Outage N-1 | VoltViol | Base kV | Bus base kV
Cascading Outage N-1 | VoltViol | Area | Bus area number
Cascading Outage N-1 | VoltViol | Zone | Bus zone number
Cascading Outage N-1 | VoltViol | Bus Type | Bus type
Cascading Outage N-1 | VoltViol | Pgen | Real power generation at bus
Cascading Outage N-1 | VoltViol | Pload | Real power load at bus
Cascading Outage N-1 | VoltViol | G Shunt | Real power shunt at bus
Cascading Outage N-1 | VoltViol | B Shunt | Reactive power shunt at bus
Cascading Outage N-1 | VoltViol | Min Volt Limit | Low voltage criteria for bus
Cascading Outage N-1 | VoltViol | Max Volt Limit | High voltage criteria for bus
Cascading Outage N-1 | VoltViol | %Vdrop Limit | Maximum voltage drop criteria for bus
Cascading Outage N-1 | VoltViol | %Vrise Limit | Maximum voltage rise criteria for bus
Cascading Outage N-1 | VoltViol | Base Volt | Base case bus voltage
Cascading Outage N-1 | VoltViol | Step 0 Cont Volt | Contingency voltage before applying cascading events
Cascading Outage N-1 | VoltViol | Cascade Step | Cascade step. 0 means no cascading events have been applied.
Cascading Outage N-1 | VoltViol | MW Tripped | MW generation tripped as cascading events
Cascading Outage N-1 | VoltViol | MVAR Tripped | MVAR generation tripped as cascading events
Cascading Outage N-1 | VoltViol | Cascade Volt | Bus voltage after applying cascading events
Cascading Outage N-1 | VoltViol | %Vdrop | % voltage drop (negative for voltage rise)
Cascading Outage N-1 | VoltViol | Vmag Violation | Low and High voltage magnitude violation
Cascading Outage N-1 | VoltViol | Vchng Violation | Drop and Rise voltage violation
Cascading Outage N-1 | VoltViol | # of Branches | # of branches connected after applying cascading events
Cascading Outage N-1 | VoltViol | Radial Index | Radial index (≤ 1.0, 1.0 = radial) after applying cascading events
Cascading Outage N-1 | VoltViol | Max MW Flow | Max MW bus injection or withdrawal after applying cascading events
Cascading Outage N-1-1 | VoltViol | First Level Scenario Index | First Level Contingency index
Cascading Outage N-1-1 | VoltViol | First Level Scenario | First Level Contingency name
Cascading Outage N-1-1 | VoltViol | Cont ID | Contingency index
Cascading Outage N-1-1 | VoltViol | Cont Name | Contingency name
Cascading Outage N-1-1 | VoltViol | Bus # | Bus number
Cascading Outage N-1-1 | VoltViol | Bus Name | Bus name
Cascading Outage N-1-1 | VoltViol | Base kV | Bus base kV
Cascading Outage N-1-1 | VoltViol | Area | Bus area number
Cascading Outage N-1-1 | VoltViol | Zone | Bus zone number
Cascading Outage N-1-1 | VoltViol | Bus Type | Bus type
Cascading Outage N-1-1 | VoltViol | Pgen | Real power generation at bus
Cascading Outage N-1-1 | VoltViol | Pload | Real power load at bus
Cascading Outage N-1-1 | VoltViol | G Shunt | Real power shunt at bus
Cascading Outage N-1-1 | VoltViol | B Shunt | Reactive power shunt at bus
Cascading Outage N-1-1 | VoltViol | Min Volt Limit | Low voltage criteria for bus
Cascading Outage N-1-1 | VoltViol | Max Volt Limit | High voltage criteria for bus
Cascading Outage N-1-1 | VoltViol | %Vdrop Limit | Maximum voltage drop criteria for bus
Cascading Outage N-1-1 | VoltViol | %Vrise Limit | Maximum voltage rise criteria for bus
Cascading Outage N-1-1 | VoltViol | Base Volt | Base case bus voltage
Cascading Outage N-1-1 | VoltViol | Step 0 Cont Volt | Contingency voltage before applying cascading events
Cascading Outage N-1-1 | VoltViol | Cascade Step | Cascade step. 0 means no cascading events have been applied.
Cascading Outage N-1-1 | VoltViol | MW Tripped | MW generation tripped as cascading events
Cascading Outage N-1-1 | VoltViol | MVAR Tripped | MVAR generation tripped as cascading events
Cascading Outage N-1-1 | VoltViol | Cascade Volt | Bus voltage after applying cascading events
Cascading Outage N-1-1 | VoltViol | %Vdrop | % voltage drop (negative for voltage rise)
Cascading Outage N-1-1 | VoltViol | Vmag Violation | Low and High voltage magnitude violation
Cascading Outage N-1-1 | VoltViol | Vchng Violation | Drop and Rise voltage violation
Cascading Outage N-1-1 | VoltViol | # of Branches | # of branches connected after applying cascading events
Cascading Outage N-1-1 | VoltViol | Radial Index | Radial index (≤ 1.0, 1.0 = radial) after applying cascading events
Cascading Outage N-1-1 | VoltViol | Max MW Flow | Max MW bus injection or withdrawal after applying cascading events
TARA | AllViolations | LikeHd | Likelihood of overload occurrence: An integer, between 1 and 8, that denotes the 'likelihood that the overload (violation) may occur. It is based on the congestion exposure (CE) parameter. Values are as follows: 1 NoGens - initial overload, no helpers and harmers exist, 2 NoFix - overload cannot be removed (CE=1.0), 3 Vhigh – 0.8<CE<1.0, 4 High-0.6<CE<0.8, 5 Medium - 0.4<CE<0.6, 6 LMedium - 0.2<CE<0.4, 7 Unlikely - 0.1<CE<0.2, 8 VUnlikely - 0.0<CE<0.1
TARA | AllViolations | NAre | Number of areas involved
TARA | AllViolations | PrbType | Problem type (qualitative description): NoGens – initial overload, no helpers and harmers exist; LdPock_NoHarm – load pocket, no harmers; GenPock_NoHelp - generator pocket, no helpers; Local500 – local problem, more than 500 MW of generation involved; Local1000 – local problem, more than 1000 MW of generation involved; Global5000 – global problem, more than 5000 MW involved; General – general problem–none of the above
TARA | AllViolations | Type | Violation type (primary or secondary)
TARA | AllViolations | PInd | Primary constraint index -constraint which is is more limiting and has the same harmers and helpers
TARA | AllViolations | Ind | Reported constraint index
TARA | AllViolations | Snapshot | Snapshot (case) name
TARA | AllViolations | FgID | Flowgate (monitored element/contingency pair) index
TARA | AllViolations | Monit Param | Monitored parameter (element)
TARA | AllViolations | Contingency | Contingency name (description)
TARA | AllViolations | Flow | Branch flow (in MW)
TARA | AllViolations | Rating | Branch rating
TARA | AllViolations | Loading% | Branch loading (in %). If less than zero, initial flow is in opposite direction than potential violation
TARA | AllViolations | CongExpo | Congestion exposure parameter
TARA | AllViolations | DwnStLoad | Total downstream (helping) load impacted (in MW)
TARA | AllViolations | LdDfaxAver | Average distribution factor of impacted (downstreakm) load
TARA | AllViolations | LdTotlImp | Total (helping) impact from affected load (in MW)
TARA | AllViolations | HarmMax | Maximum upstream (harmer) generation (in MW)
TARA | AllViolations | HelpMax | Maximum downstream (helper) generation (in MW)
TARA | AllViolations | TotalGen | Total (helper + harmer) maximum generation (in MW)
TARA | AllViolations | NGens | Number of generating units (helpers or harmers) involved
TARA | AllViolations | MinFlow | Minimum possible branch flow (in MW). Assumes all helper generation turned on and all harmer generation turned off.
TARA | AllViolations | MaxFlow | Maximum possible branch flow (in MW). Assumes all helper generation turned off and all harmer generation turned on.
TARA | AllViolations | Areas | List of areas involved
TARA | AllViolations | Zones | List of zones involved
TARA | CascadeSummary | First Level Scenario Index | First Level Contingency index
TARA | CascadeSummary | First Level Scenario | First Level Contingency name
TARA | CascadeSummary | Cont ID | Contingency index
TARA | CascadeSummary | Cont Name | Contingency name
TARA | CascadeSummary | Cascade Step | Casecase step. 0 means no cascading events have been applied.
TARA | CascadeSummary | Cascade Status | Stopped-No additional cascading events identified. Collapsed-case not converged after applying cascading events.
TARA | CascadeSummary | # of Branches Tripped | # of branches tripped
TARA | CascadeSummary | # of Gens Tripped | # of generators tripped
TARA | CascadeSummary | Pgen Tripped | Amount of Pgen tripped
TARA | CascadeSummary | # of Loads Tripped | # of loads tripped
TARA | CascadeSummary | Pload Tripped | Amount of Pload tripped
TARA | CascadeSummary | # of Buses Isolated | # of buses isolated
TARA | CascadeSummary | Islanded Pload | Consequentially islanded Pload due to cascading events
TARA | CascadeSummary | Islanded Pgen | Consequentially islanded Pgen due to cascading events
TARA | CascadeSummary | # of Branches above Tripping %Loading Cutoff | # of branches loaded above tripping %Loading cutoff
TARA | CascadeSummary | # of Reg. Buses with Low Voltage | # of low voltage bus - Regulating generators will be tripped.
TARA | CascadeSummary | # of Load Buses with Low Voltage | # of low voltage bus - Loads will be dropped.
TARA | CascadeSummary | # of Buses with Low Voltage | # of low voltage bus
TARA | CascadeGenTripSum | First Level Scenario Index | First Level Contingency index
TARA | CascadeGenTripSum | First Level Scenario | First Level Contingency name
TARA | CascadeGenTripSum | Cont ID | Contingency index
TARA | CascadeGenTripSum | Cont Name | Contingency name
TARA | CascadeGenTripSum | Cascade Step | Casecase step. 0 means no cascading events have been applied.
TARA | CascadeGenTripSum | Bus # | Bus number
TARA | CascadeGenTripSum | Bus Name | Bus name
TARA | CascadeGenTripSum | Base kV | Bus base kV
TARA | CascadeGenTripSum | Area | Bus area number
TARA | CascadeGenTripSum | Zone | Bus zone number
TARA | CascadeGenTripSum | ID | Machine Identifier
TARA | CascadeGenTripSum | Gen Trip Volt Limit | Low voltage limit to trip generators
TARA | CascadeGenTripSum | Pon | Unit power output accounting for status and bus type (in MW)
TARA | CascadeGenTripSum | Qgen | Reactive power output iff status = 1 and Btyp = Gen or Swing (in MVAr)
TARA | CascadeGenTripSum | Pmin | Plant minimum generating power output (in MW)
TARA | CascadeGenTripSum | Pmax | Plant maximum generating power output (in MW)
TARA | CascadeGenTripSum | Qmin | Minimum reactive power limit (in MVAr)
TARA | CascadeGenTripSum | Qmax | Maximum reactive power limit (in MVAr)
TARA | CascadeGenTripSum | Reg. Bus # | Remote controlled bus number
TARA | CascadeGenTripSum | Reg. Volt | Remote controlled bus voltage target (in pu)
TARA | CascadeGenTripSum | Reg. Base Volt | Remote bus base case voltage (in pu)
TARA | CascadeGenTripSum | Reg. Cont Volt | Remote bus contingency voltage (in pu)
TARA | CascadeGenLdIslandSum | Reg. Cascade Volt | Remote bus voltage after applying cascading events
TARA | CascadeGenLdIslandSum | First Level Scenario Index | First Level Contingency index
TARA | CascadeGenLdIslandSum | First Level Scenario | First Level Contingency name
TARA | CascadeGenLdIslandSum | Cont ID | Contingency index
TARA | CascadeGenLdIslandSum | Cont Name | Contingency name
TARA | CascadeGenLdIslandSum | Cascade Step | Casecase step. 0 means no cascading events have been applied.
TARA | CascadeGenLdIslandSum | Bus # | Bus number
TARA | CascadeGenLdIslandSum | Bus Name | Bus name
TARA | CascadeGenLdIslandSum | Base kV | Bus base kV
TARA | CascadeGenLdIslandSum | Area | Bus area number
TARA | CascadeGenLdIslandSum | Zone | Bus zone number
TARA | CascadeGenLdIslandSum | Bus Type | Bus type
TARA | CascadeGenLdIslandSum | Islanded Pload | Consequentially islanded Pload due to cascading events
TARA | CascadeGenLdIslandSum | Islanded Pgen | Consequentially islanded Pgen due to cascading events
TARA | CascadeLoadTripSum | First Level Scenario Index | First Level Contingency index
TARA | CascadeLoadTripSum | First Level Scenario | First Level Contingency name
TARA | CascadeLoadTripSum | Cont ID | Contingency index
TARA | CascadeLoadTripSum | Cont Name | Contingency name
TARA | CascadeLoadTripSum | Cascade Step | Casecase step. 0 means no cascading events have been applied.
TARA | CascadeLoadTripSum | Bus # | Bus number
TARA | CascadeLoadTripSum | Bus Name | Bus name
TARA | CascadeLoadTripSum | Volt | Nominal voltage level (in kV)
TARA | CascadeLoadTripSum | Area | Bus area number
TARA | CascadeLoadTripSum | Zone | Bus zone number
TARA | CascadeLoadTripSum | ID | Load Identifier
TARA | CascadeLoadTripSum | Pload | Real power load at bus
TARA | CascadeLoadTripSum | Qload | Reactive power load at bus
TARA | CascadeLoadTripSum | Load Trip Volt Limit | Low voltage limit to drop loads
TARA | CascadeLoadTripSum | Base Volt | Base case voltage (in pu)
TARA | CascadeLoadTripSum | Cont Volt | Contingency voltage (in pu)
TARA | CascadeLoadTripSum | Cascade Volt | Bus voltage after applying cascading events
TARA | AreaSum | Area | Area number
TARA | AreaSum | AreaName | Area name
TARA | AreaSum | Buses | Number of buses in Area
TARA | AreaSum | NTies | Number of ties from Area
TARA | AreaSum | TotGen | Generation output (in MW -- sum of Pgen of units online)
TARA | AreaSum | MaxGenOnl | Maximum generation output (in MW -- sum of Pmax of units online)
TARA | AreaSum | MaxGenOff | Maximum generation output (in MW -- sum of Pmax of all units -- on- and off-line)
TARA | AreaSum | LoadAct | Load at actual bus voltages (MW)
TARA | AreaSum | LoadNom | Load at flat, 1.0 p.u., bus voltages (MW)
TARA | AreaSum | LdInDifAr | Load assigned to this Area but located in different Area (MW)
TARA | AreaSum | LdFrDifAr | Load assigned to different Area but located in this Area (MW)
TARA | AreaSum | shuntLoss | Losses from real power bus shunts (MW)
TARA | AreaSum | TotLosses | Total Area Losses
TARA | AreaSum | AreaInterTies | Total flow on Area ties (MW, positive is export)
TARA | AreaSum | AreaInterExtLd
TARA | AreaSum | DesInter | Desired Area Interchange
TARA | AreaSum | Bus# | Area slack generator bus number
TARA | AreaSum | AreaSlack | Area slack generator bus name
TARA | AreaSum | Volt | Area slack generator bus base voltage (kV)
TARA | AreaSum | curPGen | Area slack generator bus power (MW)
TARA | AreaSum | MinPGen | Area slack generator bus minimum power (MW)
TARA | AreaSum | MaxPGen | Area slack generator bus maximum power (MW)
TARA | AreaSum | Stat | Area slack generator limit status ("High" if Pgen>Pmax, "Low" if Pgen<Pmin)
TARA | BranchData | busFrm | FROM bus number
TARA | BranchData | busNamFr | FROM bus name
TARA | BranchData | Volt | FROM nominal voltage level (in kV)
TARA | BranchData | ArFr | FROM area number
TARA | BranchData | ZnFr | FROM zone number
TARA | BranchData | busTo | TO bus number
TARA | BranchData | busNamTo | TO bus name
TARA | BranchData | Volt | TO nominal voltage level (in kV)
TARA | BranchData | ArTo | TO area number
TARA | BranchData | ZnTo | TO zone number
TARA | BranchData | CKT | Circuit identifier
TARA | BranchData | Mt | Branch metered end (From, To)
TARA | BranchData | St | Branch status (0-off,1-on)
TARA | BranchData | MW_Flow | Power flow (in MW)
TARA | BranchData | MVAr_flow | Reactive power flow (in MVAr)
TARA | BranchData | MVA_flow | Total power flow (in MVA)
TARA | BranchData | LossesMW | Real power losses (in MW)
TARA | BranchData | LssesMVAr | Reactive power losses (in MVAr)
TARA | BranchData | RateA | Branch rating A (normal)
TARA | BranchData | RateB | Branch rating B (LTE)
TARA | BranchData | RateC | Branch rating C (STE)
TARA | BranchData | R | Branch resistance (in pu)
TARA | BranchData | X | Branch reactance (in pu)
TARA | BranchData | Charg | Branch charging (in pu)
TARA | BranchData | TranRat | transformer off nominal turns ratio
TARA | BranchData | PhsShftGrd | Phase shifter Angle in degree
TARA | BranchData | ShuntGFrom | Branch shunt susceptance, FROM bus (in pu)
TARA | BranchData | ShuntBFrom | Branch shunt admittance, FROM bus (in pu)
TARA | BranchData | ShuntGTo | Branch shunt susceptance, TO bus (in pu)
TARA | BranchData | ShuntBTo | Branch shunt admittance, TO bus (in pu)
TARA | BranchData | Length | Branch length
TARA | BranchData | Ow1 | Owner 1
TARA | BranchData | Own1% | Owner 1 share
TARA | BranchData | Ow2 | Owner 2
TARA | BranchData | Own2% | Owner 2 share
TARA | BranchData | Ow3 | Owner 3
TARA | BranchData | Own3% | Owner 3 share
TARA | BranchData | Ow4 | Owner 4
TARA | BranchData | Own4% | Owner 4 share
TARA | BranchDbData | busFrm | FROM bus number
TARA | BranchDbData | busNamFr | FROM bus name
TARA | BranchDbData | Volt | FROM nominal voltage level (in kV)
TARA | BranchDbData | ArFr | FROM area number
TARA | BranchDbData | ZnFr | FROM zone number
TARA | BranchDbData | busTo | TO bus number
TARA | BranchDbData | busNamTo | TO bus name
TARA | BranchDbData | Volt | TO nominal voltage level (in kV)
TARA | BranchDbData | ArTo | TO area number
TARA | BranchDbData | ZnTo | TO zone number
TARA | BranchDbData | CKT | Circuit identifier
TARA | BranchDbData | Mt | Branch metered end (From, To)
TARA | BranchDbData | St | Branch status (0-off,1-on)
TARA | BranchDbData | MW_Flow | Power flow (in MW)
TARA | BranchDbData | MVAr_flow | Reactive power flow (in MVAr)
TARA | BranchDbData | MVA_flow | Total power flow (in MVA)
TARA | BranchDbData | LossesMW | Real power losses (in MW)
TARA | BranchDbData | LssesMVAr | Reactive power losses (in MVAr)
TARA | BranchDbData | RateA | Branch rating A (normal)
TARA | BranchDbData | RateB | Branch rating B (LTE)
TARA | BranchDbData | RateC | Branch rating C (STE)
TARA | BranchDbData | R | Branch resistance (in pu)
TARA | BranchDbData | X | Branch reactance (in pu)
TARA | BranchDbData | Charg | Branch charging (in pu)
TARA | BranchDbData | TranRat | transformer off nominal turns ratio
TARA | BranchDbData | PhsShftGrd | Phase shifter Angle in degree
TARA | BranchDbData | ShuntGFrom | Branch shunt susceptance, FROM bus (in pu)
TARA | BranchDbData | ShuntBFrom | Branch shunt admittance, FROM bus (in pu)
TARA | BranchDbData | ShuntGTo | Branch shunt susceptance, TO bus (in pu)
TARA | BranchDbData | ShuntBTo | Branch shunt admittance, TO bus (in pu)
TARA | BranchDbData | Length | Branch length
TARA | BranchDbData | Ow1 | Owner 1
TARA | BranchDbData | Own1% | Owner 1 share
TARA | BranchDbData | Ow2 | Owner 2
TARA | BranchDbData | Own2% | Owner 2 share
TARA | BranchDbData | Ow3 | Owner 3
TARA | BranchDbData | Own3% | Owner 3 share
TARA | BranchDbData | Ow4 | Owner 4
TARA | BranchDbData | Own4% | Owner 4 share
TARA | BusData | Bus# | Bus number
TARA | BusData | BusName | Bus name
TARA | BusData | Volt | Nominal voltage level (in kV)
TARA | BusData | Area | Area number
TARA | BusData | Zone | Zone number
TARA | BusData | BTyp | Bus type (generator, load, disconnected, or swing)
TARA | BusData | CodeBTyp | 1=load, 2=generator, 3=swing, 4=disconnected
TARA | BusData | Vmag [PU] | Voltage magnitude (in PU)
TARA | BusData | Vmag [KV] | Voltage magnitude (in kV)
TARA | BusData | Vangle | Voltage angle (in degrees)
TARA | BusData | PGen | Bus (generating) power output (in MW)
TARA | BusData | PloadNom | Bus load (in MW)
TARA | BusData | GShuntOn | Bus shunt conductance (in MW, at 1.0 per unit voltage)
TARA | BusData | BShuntOn | Bus shunt susceptance (in MVAr, at 1.0 per unit voltage)
TARA | BusData | Ownr | Bus owner code
TARA | BusData | PMism | Real power mismatch (MW)
TARA | BusData | QMism | Reactive power mismatch (MVAr)
TARA | BusData | MVAMism | Apparent power mismatch (MVAr)
TARA | CaseSum | no formal columns | no help exists for this report at this time -- content self-explanatory, or not fully developed yet
TARA | ConDetail | no formal columns | no help exists for this report at this time -- content self-explanatory, or not fully developed yet
TARA | ConDupl | no formal columns | no help exists for this report at this time -- content self-explanatory, or not fully developed yet
TARA | ConList | CntInd | Contingency index
TARA | ConList | Contingency | Contingency name (description)
TARA | ConList | OpenBr | Number of branches opened (tripped) events
TARA | ConList | ClosBr | Number of branches close event
TARA | ConList | GenrEv | Nubmer of generation change events (drop, change, increase…)
TARA | ConList | LoadEv | Number of Load change event dropped (lost -- in MW)
TARA | ConList | #Isl | Number of isolated islands
TARA | ConList | #BsIsl | Number of bused in isolated islands
TARA | ConList | IsoltLoad | Load on isolated islands (in MW)
TARA | ConList | IsolatGen | Generation in isolated islands (in MW)
TARA | ConList | IgnrEv | Number of branch events inside islands
TARA | ConList | StatEr | Status errors such as branch already opened or generation already offline
TARA | ConList | #InpErr | Number of events with input errors
TARA | ConList | ContSta | Contingency status - enabled or disabled
TARA | ConList | Area | Contingency event facilities belong to these areas
TARA | ConList | Zone | Contingency event facilities belong to these zones
TARA | ConStat | no formal columns | no help exists for this report at this time -- content self-explanatory, or not fully developed yet
TARA | ContFGates | FGate ID | Flowgate ID
TARA | ContFGates | Fgate Name | Flowgate Name
TARA | ContFGates | Contingency | Contingency name (description)
TARA | ContFGates | Min Rating | Flowgate minimum rating (in MVA) -- It may reflect rate A, B, or C (depending on user selection) and normal or contingency conditions (depending on flowgate definition)
TARA | ContFGates | Max Rating | Flowgate maximum rating (in MVA) -- It may reflect rate A, B, or C (depending on user selection) and normal or contingency conditions (depending on flowgate definition)
TARA | ContFGates | Base MW Flow | Flowgate base case MW flow. Measured at the metered end. Opposite flow direction for negative sign
TARA | ContFGates | Base MVA Flow (Signed) | The maximum MVA/Amp base case flow of the From and To ends of the branch. Opposite MW flow direction for negative sign
TARA | ContFGates | Cont MW Flow | Flowgate post-contingency MW flow. Measured at the metered end. Opposite flow direction for negative sign
TARA | ContFGates | Cont MVA Flow (Signed) | The maximum MVA/Amp post-contingency flow of the From and To ends of the branch. Opposite MW flow direction for negative sign
TARA | ContFGates | Final DC %Loading | Final % loading – linear (DC) solution
TARA | ContFGates | Final AC %Loading | Final AC % loading
TARA | ContFGates | AFC | Available Flowgate Capability. A measure of the flow capability remaining on a flowgate for further commercial activity over and above already committed uses
TARA | ContFGates | LODF | Sensitivity measure of how a change in a branch's status impacts the flows on the monitored facilityother lines in the system. Report only first four contingency events.
TARA | DC2TermData | no formal columns | no help exists for this report at this time -- content self-explanatory, or not fully developed yet
TARA | Deliver | LikeHd | Likelihood of overload occurrence: An integer, between 1 and 8, that denotes the 'likelihood that the overload (violation) may occur. It is based on the congestion exposure (CE) parameter. Values are as follows: 1 NoGens - initial overload, no helpers and harmers exist, 2 NoFix - overload cannot be removed (CE=1.0), 3 Vhigh – 0.8<CE<1.0, 4 High-0.6<CE<0.8, 5 Medium - 0.4<CE<0.6, 6 LMedium - 0.2<CE<0.4, 7 Unlikely - 0.1<CE<0.2, 8 VUnlikely - 0.0<CE<0.1
TARA | Deliver | NAre | Number of areas involved
TARA | Deliver | PrbType | Problem type (qualitative description): NoGens – initial overload, no helpers and harmers exist; LdPock_NoHarm – load pocket, no harmers; GenPock_NoHelp - generator pocket, no helpers; Local500 – local problem, more than 500 MW of generation involved; Local1000 – local problem, more than 1000 MW of generation involved; Global5000 – global problem, more than 5000 MW involved; General – general problem–none of the above
TARA | Deliver | Type | Violation type (primary or secondary)
TARA | Deliver | PInd | Primary violation index
TARA | Deliver | Ind | Secondary violation index (same as flowgate index)
TARA | Deliver | SnapShot | Snapshot (case) name
TARA | Deliver | Monitored Element | Monitored parameter (element)
TARA | Deliver | Contingency | Contingency name (description)
TARA | Deliver | Flow | Branch flow (in MW)
TARA | Deliver | Limit | Branch rating
TARA | Deliver | Load% | Branch loading (in %). If less than zero, initial flow in opposite direction than potential violation
TARA | Deliver | CongExpo | Congestion exposure
TARA | Deliver | TotLoad | Total downstream (helping) load impacted (in MW)
TARA | Deliver | AvrLDDfax | Average distribution factor of impacted (downstreakm) load
TARA | Deliver | TotImpact | Total (helping) impact from affected load (in MW)
TARA | Deliver | Areas | List of areas involved
TARA | Deliver | Zones | List of zones involved
TARA | Deliver | M1_HarmerImp | Method 1 Harmers Impact when scheduled upto EFORD with Dfax > DfaxCutOff
TARA | Deliver | M1_HelperImp | Method 1 Helpers Impact when scheduled upto EFORD with Dfax > DfaxCutOff
TARA | Deliver | M1_Headroom | Headoom= Limit – Flow - UpStreamImpact - DnStreamImpact, If positve, it is not a problem
TARA | Deliver | M2_HarmerImp | M2 upstream helpers impact using 80/20 rule
TARA | Deliver | M2_HelperImp | M2 down stream harmers impact using 100% impact
TARA | Deliver | M2_Headroom | Headoom= Limit – Flow - UpStreamImpact - DnStreamImpact
TARA | Deliver | M3_LoadGrowthMW | LoadGrowthMW=loadEscalation*UpStreamLoadTotal
TARA | Deliver | M3_LoadGrowthImpact | LoadGrowthImpact=LoadGrowthMW*UpStreamDfax
TARA | Deliver | M3_GenLeft | CutOffGenLeft=totalGenCutOff-LoadGrowthMW, 0 if negative
TARA | Deliver | M3_GenLeftImpact | CutOffImpactLeft = CutOffGenLeft * DfaxGen
TARA | Deliver | M3_Headroom | HeadRoom = Limit – Flow - LoadGrowthImpact - CutOffImpactLeft
TARA | Deliver | M4_UpStreamLoad | UpStreamLoadTotalEscal=UpStreamLoadTotal * (1+loadEscalation)
TARA | Deliver | M4_UpStreamGen | UpStreamGenTotal = Sum(genMax), no DFAX cutoff
TARA | Deliver | M4_UpStreamExcess | UpStreamGenAvail = max(0, UpStreamGenTotal -UpStreamLoadTotalEscal)
TARA | Deliver | M4_UpStreamLeakage | UpStreamLeakage=(UpStreamDfaxGen-UpStreamDfaxLoad)*UpStreamGenToUse
TARA | Deliver | M4_DwnStrmLoad | DnStreamLoadTotalEscal=DnStreamLoadTotal * (1+loadEscalation)
TARA | Deliver | M4_DwnStrmGen | DnStreamGenTotal =sum(genMax[igen]), no DFAX cutoff
TARA | Deliver | M4_DwnStrmDeficit | DnStreamGenNeeded= max(0, DnStreamLoadTotalEscal-DnStreamGenTotal)
TARA | Deliver | M4_DwnStrmLeakage | DnStreamLeakage=(DnStreamDfaxGen -DnStreamDfaxLoad)*DnStreamGenToUse
TARA | Deliver | InadvFlow | inAdvertFlow=Flow-UpStreamGenImpactDisp-DnStreamGenImpactDisp, no cutoff, it is the flow due to PARs, external transactions, losses
TARA | Deliver | M4_UpStreamImpc | UpStreamTotalImpact=UpStreamLeakage+DnStreamLeakage+UpStreamGenAvailImpac
TARA | Deliver | M4_AdjHeadRoom | AdjHeadRoom(Upstream Gen Excess) =Limit - UpStreamTotalImpact-inAdvertFlow
TARA | Deliver | M4_NeedDnStreamImpc | DnStreamTotalImpact=UpStreamLeakage+DnStreamLeakage+DnStreamGenNeededImpact
TARA | Deliver | M4_AdjHeadroom | AdjHeadroom(DnStreamDeficit) = Limit – DnStreamTotalImpact - inAdvertFlow
TARA | DownStrLoad | Bus# | Bus number
TARA | DownStrLoad | BusName | Bus name
TARA | DownStrLoad | Volt | Nominal voltage level (in kV)
TARA | DownStrLoad | Area | Area number
TARA | DownStrLoad | Zone | Zone number
TARA | DownStrLoad | Pgen | Bus (generating) power output (in MW)
TARA | DownStrLoad | Pmax | Bus maximum (generating) power output (in MW)
TARA | DownStrLoad | PLoad | Bus load (in MW)
TARA | DownStrLoad | Dfact | Bus load distribution factor (calculated with respect to reference subsystem, selected by user)
TARA | DownStrLoad | Impact | Load Impact=Dfax*Pload
TARA | DownStrLoad | HelpMax | Maximum downstream (helper) generation (in MW)
TARA | DownStrLoad | HelpMaxIm | Maximum potential impact from downstream (helper) generation (in MW). Assumes all helper generation turned on at maximum output.
TARA | DownStrLoad | HarmMax | Maximum upstream (harmer) generation (in MW)
TARA | DownStrLoad | HarmMaxImp | Maximum potential impact from upstream (harmer) generation (in MW). Assumes all harmer generation turned on at maximum output.
TARA | DownStrLoad | Hl/Hr | Helper MW/Harmer MW ratio
TARA | DownStrLoad | LikeHd | Likelihood of overload occurrence: An integer, between 1 and 8, that denotes the 'likelihood that the overload (violation) may occur. It is based on the congestion exposure (CE) parameter. Values are as follows: 1 NoGens - initial overload, no helpers and harmers exist, 2 NoFix - overload cannot be removed (CE=1.0), 3 Vhigh – 0.8<CE<1.0, 4 High-0.6<CE<0.8, 5 Medium - 0.4<CE<0.6, 6 LMedium - 0.2<CE<0.4, 7 Unlikely - 0.1<CE<0.2, 8 VUnlikely - 0.0<CE<0.1
TARA | DownStrLoad | NAre | Number of areas involved
TARA | DownStrLoad | PrbType | Problem type (qualitative description): NoGens – initial overload, no helpers and harmers exist; LdPock_NoHarm – load pocket, no harmers; GenPock_NoHelp - generator pocket, no helpers; Local500 – local problem, more than 500 MW of generation involved; Local1000 – local problem, more than 1000 MW of generation involved; Global5000 – global problem, more than 5000 MW involved; General – general problem–none of the above
TARA | DownStrLoad | STyp | Type of snapshot (primary or secondary)
TARA | DownStrLoad | Pind | Primary violation index
TARA | DownStrLoad | Ind | Secondary violation index (same as flowgate index)
TARA | DownStrLoad | Snapshot | Snapshot (case) name
TARA | DownStrLoad | FgID | Flowgate ID
TARA | DownStrLoad | Monit Param | Monitored parameter (element)
TARA | DownStrLoad | Contingency | Contingency name (description)
TARA | DownStrLoad | Flow | Branch flow (in MW)
TARA | DownStrLoad | Rating | Branch rating
TARA | DownStrLoad | Loading% | Branch loading (in %). If less than zero, initial flow in opposite direction than potential violation
TARA | DownStrLoad | CongExpo | Congestion exposure parameter
TARA | DownStrLoad | MinFlow | Minimum possible branch flow (in MW). Assumes all helper generation turned on and all harmer generation turned off.
TARA | DownStrLoad | MaxFlow | Maximum possible branch flow (in MW). Assumes all helper generation turned off and all harmer generation turned on.
TARA | ExcludeReport | no formal columns | no help exists for this report at this time -- content self-explanatory, or not fully developed yet
TARA | FgateDet | no formal columns | no help exists for this report at this time -- content self-explanatory, or not fully developed yet
TARA | GenData | Bus# | Bus number
TARA | GenData | BusName | Bus name
TARA | GenData | Volt | Nominal voltage level (in kV)
TARA | GenData | Area | Area number
TARA | GenData | Zone | Zone number
TARA | GenData | ID | unit ID
TARA | GenData | Sta | unit status
TARA | GenData | PGen | Unit power output iff status = 1 and Btyp = Gen or Swing (in MW)
TARA | GenData | Pon | Unit power output, accounting for status and bus type (in MW)
TARA | GenData | QGen | Reactive power output iff status = 1 and Btyp = Gen or Swing (in MVAr)
TARA | GenData | Pmin | Unit minimum power output (in MW)
TARA | GenData | Pmax | Unit maximum power output (in MW)
TARA | GenData | Pavail | Pmax - Pgen (in MW)
TARA | GenData | Qmin | Minimum reactive power limit (in MVAr)
TARA | GenData | Qmax | Maximum reactive power limit (in MVAr)
TARA | GenData | %Share | Qgen share when several generators control voltage at the same bus (in %)
TARA | GenData | CtrlB# | Remote controlled bus number (0 to control terminal bus)
TARA | GenData | ContBusNme | Remote controlled bus name
TARA | GenData | Volt | Remote controlled bus nominal voltage level (in kV)
TARA | GenData | VoltTarg | Remote controlled bus voltage target (in pu)
TARA | GenData | Ow1 | Owner 1
TARA | GenData | Own1% | Owner 1 share
TARA | GenData | Ow2 | Owner 2
TARA | GenData | Own2% | Owner 2 share
TARA | GenData | Ow3 | Owner 3
TARA | GenData | Own3% | Owner 3 share
TARA | GenData | Ow4 | Owner 4
TARA | GenData | Own4% | Owner 4 share
TARA | GenData | MBase | total machine MVA base
TARA | GenData | RSource | Machine impedance (resistance -- in p.u. on MBASE)
TARA | GenData | XSource | Machine impedance (reactance -- in p.u. on MBASE)
TARA | GenData | RTran | Step-up transformer impedance (resistance -- in p.u. on MBASE)
TARA | GenData | XTran | Step-up transformer impedance (reactance -- in p.u. on MBASE)
TARA | GenData | GenTap | generator step-up transformer off-nominal turns ratio
TARA | Harmers | Bus# | Bus number
TARA | Harmers | BusName | Bus name
TARA | Harmers | Volt | Nominal voltage level (in kV)
TARA | Harmers | Area | Area number
TARA | Harmers | Zone | Zone number
TARA | Harmers | Pgen | Unit power output (in MW)
TARA | Harmers | Pmax | Unit maximum power output (in MW)
TARA | Harmers | Share | Unit share within total pool of harmers
TARA | Harmers | Dfact | Unit distribution factor (calculated with respect to reference subsystem, selected by user)
TARA | Harmers | Impact | Pgen*Dfax
TARA | Harmers | HelpMax | Maximum downstream (helper) generation (in MW)
TARA | Harmers | HelpMaxIm | Maximum potential impact from downstream (helper) generation (in MW). Assumes all helper generation turned on at maximum output.
TARA | Harmers | HarmMax | Maximum upstream (harmer) generation (in MW)
TARA | Harmers | HarmMaxImp | Maximum potential impact from upstream (harmer) generation (in MW). Assumes all harmer generation turned on at maximum output.
TARA | Harmers | Hl/Hr | Helper MW/Harmer MW ratio
TARA | Harmers | LikeHd | Likelihood of overload occurrence: An integer, between 1 and 8, that denotes the 'likelihood that the overload (violation) may occur. It is based on the congestion exposure (CE) parameter. Values are as follows: 1 NoGens - initial overload, no helpers and harmers exist, 2 NoFix - overload cannot be removed (CE=1.0), 3 Vhigh – 0.8<CE<1.0, 4 High-0.6<CE<0.8, 5 Medium - 0.4<CE<0.6, 6 LMedium - 0.2<CE<0.4, 7 Unlikely - 0.1<CE<0.2, 8 VUnlikely - 0.0<CE<0.1
TARA | Harmers | NAre | Number of areas involved
TARA | Harmers | PrbType | Problem type (qualitative description): NoGens – initial overload, no helpers and harmers exist; LdPock_NoHarm – load pocket, no harmers; GenPock_NoHelp - generator pocket, no helpers; Local500 – local problem, more than 500 MW of generation involved; Local1000 – local problem, more than 1000 MW of generation involved; Global5000 – global problem, more than 5000 MW involved; General – general problem–none of the above
TARA | Harmers | STyp | Type of snapshot (primary or secondary)
TARA | Harmers | Pind | Primary violation index
TARA | Harmers | Ind | Secondary violation index (same as flowgate index)
TARA | Harmers | Snapshot | Snapshot (case) name
TARA | Harmers | FgID | Flowgate ID
TARA | Harmers | Monit Param | Monitored parameter (element)
TARA | Harmers | Contingency | Contingency name (description)
TARA | Harmers | Flow | Branch flow (in MW)
TARA | Harmers | Rating | Branch rating
TARA | Harmers | Loading% | Branch loading (in %). If less than zero, initial flow in opposite direction than potential violation
TARA | Harmers | CongExpo | Congestion exposure parameter
TARA | Harmers | MinFlow | Minimum possible branch flow (in MW). Assumes all helper generation turned on and all harmer generation turned off.
TARA | Harmers | MaxFlow | Maximum possible branch flow (in MW). Assumes all helper generation turned off and all harmer generation turned on.
TARA | HarmHelpers | Bus# | Bus number
TARA | HarmHelpers | BusName | Bus name
TARA | HarmHelpers | Volt | Nominal voltage level (in kV)
TARA | HarmHelpers | Area | Area number
TARA | HarmHelpers | Zone | Zone number
TARA | HarmHelpers | Pgen | Unit power output (in MW)
TARA | HarmHelpers | Pmax | Unit maximum power output (in MW)
TARA | HarmHelpers | Help/Harm | Impact type (helper or harmer)
TARA | HarmHelpers | Share | Unit share within corresponding (helper or harmer) pool
TARA | HarmHelpers | Dfact | Unit distribution factor (calculated with respect to reference subsystem, selected by user)
TARA | HarmHelpers | Impact | Pgen*Dfax
TARA | HarmHelpers | HelpMax | Maximum downstream (helper) generation (in MW)
TARA | HarmHelpers | HelpMaxIm | Maximum potential impact from downstream (helper) generation (in MW). Assumes all helper generation turned on at maximum output.
TARA | HarmHelpers | HarmMax | Maximum upstream (harmer) generation (in MW)
TARA | HarmHelpers | HarmMaxImp | Maximum potential impact from upstream (harmer) generation (in MW). Assumes all harmer generation turned on at maximum output.
TARA | HarmHelpers | Hl/Hr | Helper MW/Harmer MW ratio
TARA | HarmHelpers | LikeHd | Likelihood of overload occurrence: An integer, between 1 and 8, that denotes the 'likelihood that the overload (violation) may occur. It is based on the congestion exposure (CE) parameter. Values are as follows: 1 NoGens - initial overload, no helpers and harmers exist, 2 NoFix - overload cannot be removed (CE=1.0), 3 Vhigh – 0.8<CE<1.0, 4 High-0.6<CE<0.8, 5 Medium - 0.4<CE<0.6, 6 LMedium - 0.2<CE<0.4, 7 Unlikely - 0.1<CE<0.2, 8 VUnlikely - 0.0<CE<0.1
TARA | HarmHelpers | NAre | Number of areas involved
TARA | HarmHelpers | PrbType | Problem type (qualitative description): NoGens – initial overload, no helpers and harmers exist; LdPock_NoHarm – load pocket, no harmers; GenPock_NoHelp - generator pocket, no helpers; Local500 – local problem, more than 500 MW of generation involved; Local1000 – local problem, more than 1000 MW of generation involved; Global5000 – global problem, more than 5000 MW involved; General – general problem–none of the above
TARA | HarmHelpers | STyp | Type of snapshot (primary or secondary)
TARA | HarmHelpers | Pind | Primary violation index
TARA | HarmHelpers | Ind | Secondary violation index (same as flowgate index)
TARA | HarmHelpers | Snapshot | Snapshot (case) name
TARA | HarmHelpers | FgID | Flowgate ID
TARA | HarmHelpers | Monit Param | Monitored parameter (element)
TARA | HarmHelpers | Contingency | Contingency name (description)
TARA | HarmHelpers | Flow | Branch flow (in MW)
TARA | HarmHelpers | Rating | Branch rating
TARA | HarmHelpers | Loading% | Branch loading (in %). If less than zero, initial flow in opposite direction than potential violation
TARA | HarmHelpers | CongExpo | Congestion exposure parameter
TARA | HarmHelpers | MinFlow | Minimum possible branch flow (in MW). Assumes all helper generation turned on and all harmer generation turned off.
TARA | HarmHelpers | MaxFlow | Maximum possible branch flow (in MW). Assumes all helper generation turned off and all harmer generation turned on.
TARA | Helpers | Bus# | Bus number
TARA | Helpers | BusName | Bus name
TARA | Helpers | Volt | Nominal voltage level (in kV)
TARA | Helpers | Area | Area number
TARA | Helpers | Zone | Zone number
TARA | Helpers | Pgen | Unit power output (in MW)
TARA | Helpers | Pmax | Unit maximum power output (in MW)
TARA | Helpers | Share | Impact type (helper or harmer)
TARA | Helpers | Dfact | Unit share within total pool of helpers
TARA | Helpers | Impact | Unit distribution factor (calculated with respect to reference subsystem, selected by user)
TARA | Helpers | HelpMax | Maximum downstream (helper) generation (in MW)
TARA | Helpers | HelpMaxIm | Maximum potential impact from downstream (helper) generation (in MW). Assumes all helper generation turned on at maximum output.
TARA | Helpers | HarmMax | Maximum upstream (harmer) generation (in MW)
TARA | Helpers | HarmMaxImp | Maximum potential impact from upstream (harmer) generation (in MW). Assumes all harmer generation turned on at maximum output.
TARA | Helpers | Hl/Hr | Helper MW/Harmer MW ratio
TARA | Helpers | LikeHd | Likelihood of overload occurrence: An integer, between 1 and 8, that denotes the 'likelihood that the overload (violation) may occur. It is based on the congestion exposure (CE) parameter. Values are as follows: 1 NoGens - initial overload, no helpers and harmers exist, 2 NoFix - overload cannot be removed (CE=1.0), 3 Vhigh – 0.8<CE<1.0, 4 High-0.6<CE<0.8, 5 Medium - 0.4<CE<0.6, 6 LMedium - 0.2<CE<0.4, 7 Unlikely - 0.1<CE<0.2, 8 VUnlikely - 0.0<CE<0.1
TARA | Helpers | NAre | Number of areas involved
TARA | Helpers | PrbType | Problem type (qualitative description): NoGens – initial overload, no helpers and harmers exist; LdPock_NoHarm – load pocket, no harmers; GenPock_NoHelp - generator pocket, no helpers; Local500 – local problem, more than 500 MW of generation involved; Local1000 – local problem, more than 1000 MW of generation involved; Global5000 – global problem, more than 5000 MW involved; General – general problem–none of the above
TARA | Helpers | STyp | Type of snapshot (primary or secondary)
TARA | Helpers | Pind | Primary violation index
TARA | Helpers | Ind | Secondary violation index (same as flowgate index)
TARA | Helpers | Snapshot | Snapshot (case) name
TARA | Helpers | FgID | Flowgate ID
TARA | Helpers | Monit Param | Monitored parameter (element)
TARA | Helpers | Contingency | Contingency name (description)
TARA | Helpers | Flow | Branch flow (in MW)
TARA | Helpers | Rating | Branch rating
TARA | Helpers | Loading% | Branch loading (in %). If less than zero, initial flow in opposite direction than potential violation
TARA | Helpers | CongExpo | Congestion exposure parameter
TARA | Helpers | MinFlow | Minimum possible branch flow (in MW). Assumes all helper generation turned on and all harmer generation turned off.
TARA | Helpers | MaxFlow | Maximum possible branch flow (in MW). Assumes all helper generation turned off and all harmer generation turned on.
TARA | LoadData | Bus# | Bus number
TARA | LoadData | BusName | Bus name
TARA | LoadData | Volt | Nominal voltage level (in kV)
TARA | LoadData | Area | Load Area number
TARA | LoadData | Zone | Load Zone number
TARA | LoadData | ID | Load ID
TARA | LoadData | St | Load status (0-off,1-on)
TARA | LoadData | BsSt | Bus code at load bus
TARA | LoadData | VoltMagPU | Voltage at load (p.u.)
TARA | LoadData | Ownr | Owner
TARA | LoadData | Pconst | Constant MW Load
TARA | LoadData | Qconst | Contant MVAr Load
TARA | LoadData | Pcurrt | Constat Current MW Load
TARA | LoadData | Qcurrt | Constat Current MVAr Load
TARA | LoadData | PAdmit | Constant admitance MW load
TARA | LoadData | QAdmit | Constant admitance MVAr load
TARA | LoadData | ArLoad | Bus Area number - defined only if bus area differs from load area
TARA | LoadData | ArLoadNm | Bus Area name - defined only if bus area differs from load area
TARA | LoadData | ZnLoad | Bus Zone number - defined only if bus zone differs from load zone
TARA | MonitElem | Monitored | Monitored parameter (element)
TARA | MonitElem | #FGates | Number of constraints involving reported monitored branch is involved
TARA | MonitElem | #CongExpo>0 | Number of snapgates with reported monitored branch and non-zero congestion exposure
TARA | MonitElem | WorstCongExpo | Worst Congestion exposure
TARA | MonitElem | MaxContFlow | Maximum contingency flow
TARA | MonitElem | FgIndMaxFlow | Constraint index
TARA | MultiSectLn | Bus# | FROM bus number
TARA | MultiSectLn | BusName | FROM bus name
TARA | MultiSectLn | Volt | FROM nominal voltage level (in kV)
TARA | MultiSectLn | Bus# | TO bus number
TARA | MultiSectLn | BusName | TO bus name
TARA | MultiSectLn | Volt | TO nominal voltage level (in kV)
TARA | MultiSectLn | CKT | Circuit identifier
TARA | MultiSectLn | DUM1 | Dummy bus # 1
TARA | MultiSectLn | DUM2 | Dummy bus # 2
TARA | MultiSectLn | DUM3 | Dummy bus # 3
TARA | MultiSectLn | DUM4 | Dummy bus # 4
TARA | MultiSectLn | DUM5 | Dummy bus # 5
TARA | MultiSectLn | DUM6 | Dummy bus # 6
TARA | MultiSectLn | DUM7 | Dummy bus # 7
TARA | MultiSectLn | DUM8 | Dummy bus # 8
TARA | MultiSectLn | DUM9 | Dummy bus # 9
TARA | PARsData | busFrm | FROM bus number
TARA | PARsData | busNamFr | FROM bus name
TARA | PARsData | Volt | FROM nominal voltage level (in kV)
TARA | PARsData | ArFr | FROM area number
TARA | PARsData | ZnFr | FROM zone number
TARA | PARsData | busTo | TO bus number
TARA | PARsData | busNamTo | TO bus name
TARA | PARsData | Volt | TO nominal voltage level (in kV)
TARA | PARsData | ArTo | TO area number
TARA | PARsData | ZnTo | TO zone number
TARA | PARsData | CKT | Circuit identifier
TARA | PARsData | Mt | Transformer metered end (From, To)
TARA | PARsData | BrSt | PAR branch status (0-off,1-on)
TARA | PARsData | RegSt | PAR transformer regulating status (0-off,1-on)
TARA | PARsData | TAPRat | Tap ratio (p.u.)
TARA | PARsData | PSAngleDeg | Phase angle (degrees)
TARA | PARsData | MW_Flow | Power flow (in MW)
TARA | PARsData | MVAr_flow | Reactive power flow (in MVAr)
TARA | PARsData | MVA_flow | Total power flow (in MVA)
TARA | PARsData | PSAngleMin | Lower angle limit (phase shift)
TARA | PARsData | PsAngleMax | Upper angle limit (phase shift)
TARA | PARsData | PSRegMinMW | Lower limit of controlled V, MW or MVAr
TARA | PARsData | PSRegMaxMW | Upper limit of controlled V, MW or MVAr
TARA | PARsData | ImpedanceCorrectTable | Reference to impedance correction table
TARA | PlantData | Bus# | Bus number
TARA | PlantData | BusName | Bus name
TARA | PlantData | Volt | Nominal voltage level (in kV)
TARA | PlantData | Area | Area number
TARA | PlantData | Zone | Zone number
TARA | PlantData | BTyp | Bus type (generator, load or swing)
TARA | PlantData | Nm | Number of plant units
TARA | PlantData | #On | Number of plant units online
TARA | PlantData | #Of | Number of plant units offline
TARA | PlantData | Pgen | Plant power output (in MW)
TARA | PlantData | Pmax | Plant maximum generating power output (in MW)
TARA | PlantData | PmaxOff | Plant maximum generating power output (in MW -- sum of Pmax of all units -- on- and off-line)
TARA | PlantData | PAvail | Plant Pmax -Pgen
TARA | PlantData | Pmin | Plant minimum generating power output (in MW)
TARA | ShuntData | Bus# | Bus number
TARA | ShuntData | BusName | Bus name
TARA | ShuntData | Volt | Nominal voltage level (in kV)
TARA | ShuntData | Area | Area number
TARA | ShuntData | Zone | Zone number
TARA | ShuntData | Area | Area number
TARA | ShuntData | Zone | Zone number
TARA | ShuntData | BTyp | Bus type (generator, load or swing)
TARA | ShuntData | Vmag [PU] | Bus voltage magnitude (per-unit)
TARA | ShuntData | Vmag [kV] | Bus voltage magnitude (kV)
TARA | ShuntData | Vangle | Bus voltage angle (degrees)
TARA | ShuntData | ShuntMW | Shunt MW flow
TARA | ShuntData | ShuntMVar | Shunt Mvar flow (+ capacitive, - inductive)
TARA | ShuntData | Mod | Mode (0-fixed, 1-discrete, 2-continuous)
TARA | ShuntData | ModDiscr | Mode description
TARA | ShuntData | CtlBs# | Remote controlled bus number (0 to control own bus)
TARA | ShuntData | CtlBsNam | Name of controlled bus
TARA | ShuntData | NomV | Nominal voltage of controlled bus, if remote (kV)
TARA | ShuntData | Vmin | Desired (or target) voltage minmum level (in pu)
TARA | ShuntData | Vmax | Desired (or target) voltage maxmum level (in pu)
TARA | ShuntData | MonBusVlt | Monitored bus voltage (per-unit)
TARA | ShuntData | VoltViol | Voltage violation of desired range (per-unit)
TARA | ShuntData | ShSt | Shunt status when in automatic control (maximum, minimum, regulating)
TARA | ShuntData | GShunt | Shunt MW consumption
TARA | ShuntData | Bshunt | Initial shunt admittance (in MVAr, at 1.0 pu)
TARA | ShuntData | AdmitMin | Shunt minimum reactive admittance (MVAr)
TARA | ShuntData | AdmitMax | Shunt maximum reactive admittance (MVAr)
TARA | ShuntData | RmPct | Percentage shunt contrubutes to control of voltage
TARA | ShuntData | St#1 | number of steps, block 1
TARA | ShuntData | BlkAdm1 | Admittance, block 1 (in MVAr, at 1.0 pu)
TARA | ShuntData | St#2 | number of steps, block 2
TARA | ShuntData | BlkAdm2 | Admittance, block 2 (in MVAr, at 1.0 pu)
TARA | ShuntData | St#3 | number of steps, block 3
TARA | ShuntData | BlkAdm3 | Admittance, block 3 (in MVAr, at 1.0 pu)
TARA | ShuntData | St#4 | number of steps, block 4
TARA | ShuntData | BlkAdm4 | Admittance, block 4 (in MVAr, at 1.0 pu)
TARA | ShuntData | St#5 | number of steps, block 5
TARA | ShuntData | BlkAdm5 | Admittance, block 5 (in MVAr, at 1.0 pu)
TARA | ShuntData | St#6 | number of steps, block 6
TARA | ShuntData | BlkAdm6 | Admittance, block 6 (in MVAr, at 1.0 pu)
TARA | ShuntData | St#7 | number of steps, block 7
TARA | ShuntData | BlkAdm7 | Admittance, block 7 (in MVAr, at 1.0 pu)
TARA | ShuntData | St#8 | number of steps, block 8
TARA | ShuntData | BlkAdm8 | Admittance, block 8 (in MVAr, at 1.0 pu)
TARA | ShuntData | St#9 | number of steps, block 9
TARA | ShuntData | BlkAdm9 | Admittance, block 9 (in MVAr, at 1.0 pu)
TARA | ShuntData | St#10 | number of steps, block 10
TARA | ShuntData | BlkAdm10 | Admittance, block 10 (in MVAr, at 1.0 pu)
TARA | ShuntData | St#11 | number of steps, block 11
TARA | ShuntData | BlkAdm11 | Admittance, block 11 (in MVAr, at 1.0 pu)
TARA | ShuntData | St#12 | number of steps, block 12
TARA | ShuntData | BlkAdm12 | Admittance, block 12 (in MVAr, at 1.0 pu)
TARA | StudyBuses | Snapshot | Snapshot (case) name
TARA | StudyBuses | Bus# | Bus number
TARA | StudyBuses | BusName | Bus name
TARA | StudyBuses | Volt | Nominal voltage level (in kV)
TARA | StudyBuses | Area | Area number
TARA | StudyBuses | Zone | Zone number
TARA | StudyBuses | Pgen | Bus (generating) power output (in MW)
TARA | StudyBuses | Pmax | Bus maximum (generating) power output (in MW)
TARA | StudyBuses | Pload | Bus load (in MW)
TARA | StudyGens | Snapshot | Snapshot (case) name
TARA | StudyGens | Bus# | Bus number
TARA | StudyGens | BusName | Bus name
TARA | StudyGens | Volt | Nominal voltage level (in kV)
TARA | StudyGens | Area | Area number
TARA | StudyGens | Zone | Zone number
TARA | StudyGens | Pgen | Unit power output (in MW)
TARA | StudyGens | Pmax | Unit maximum power output (in MW)
TARA | StudyGens | Pload | Bus load (in MW)
TARA | Subsys | SubSysName | subsystem name
TARA | Subsys | Buses | buses selected within subsystem
TARA | Subsys | ParBs | Participating buses with non zero scaling factor
TARA | Subsys | ScaleMethod | scaling method
TARA | Subsys | TotalLoad | total load
TARA | Subsys | TotalGen | Generation output (in MW -- sum of Pgen of units online)
TARA | Subsys | MaxGenOn | Maximum generation output (in MW -- sum of Pmax of units online)
TARA | Subsys | MaxGenOff | Maximum generation output (in MW -- sum of Pmax of all units -- on- and off-line)
TARA | sumStat | no formal columns | no help exists for this report at this time -- content self-explanatory, or not fully developed yet
TARA | AllDet | no formal columns | no help exists for this report at this time -- content self-explanatory, or not fully developed yet
TARA | TieData | busFrm | FROM bus number
TARA | TieData | busNamFr | FROM bus name
TARA | TieData | Volt | FROM nominal voltage level (in kV)
TARA | TieData | ArFr | FROM area number
TARA | TieData | ZnFr | FROM zone number
TARA | TieData | busTo | TO bus number
TARA | TieData | busNamTo | TO bus name
TARA | TieData | Volt | TO nominal voltage level (in kV)
TARA | TieData | ArTo | TO area number
TARA | TieData | ZnTo | TO zone number
TARA | TieData | CKT | Circuit identifier
TARA | TieData | Mt | Branch metered end (From, To)
TARA | TieData | St | Branch status (0-off,1-on)
TARA | TieData | MW_Flow | Power flow (in MW)
TARA | TieData | MVAr_flow | Reactive power flow (in MVAr)
TARA | TieData | MVA_flow | Total power flow (in MVA)
TARA | TieData | LossesMW | Power losses (in MW)
TARA | TieData | RateA | Branch rating A (normal)
TARA | TieData | RateB | Branch rating B (LTE)
TARA | TieData | RateC | Branch rating C (STE)
TARA | TieData | R | Branch resistance (in pu)
TARA | TieData | X | Branch reactance (in pu)
TARA | TieData | Charg | Branch charging (in pu)
TARA | TieData | TranRat | transformer off nominal turns ratio
TARA | TieData | PhsShftGrd | Phase shifter Angle in degree
TARA | TieData | ShuntGFrom | Branch shunt susceptance, FROM bus (in pu)
TARA | TieData | ShuntBFrom | Branch shunt admittance, FROM bus (in pu)
TARA | TieData | ShuntGTo | Branch shunt susceptance, TO bus (in pu)
TARA | TieData | ShuntBTo | Branch shunt admittance, TO bus (in pu)
TARA | TieData | Length | Branch length
TARA | TieData | Ow1 | Owner 1
TARA | TieData | Own1% | Owner 1 share
TARA | TieData | Ow2 | Owner 2
TARA | TieData | Own2% | Owner 2 share
TARA | TieData | Ow3 | Owner 3
TARA | TieData | Own3% | Owner 3 share
TARA | TieData | Ow4 | Owner 4
TARA | TieData | Own4% | Owner 4 share
TARA | TieDbData | busFrm | FROM bus number
TARA | TieDbData | busNamFr | FROM bus name
TARA | TieDbData | Volt | FROM nominal voltage level (in kV)
TARA | TieDbData | ArFr | FROM area number
TARA | TieDbData | ZnFr | FROM zone number
TARA | TieDbData | busTo | TO bus number
TARA | TieDbData | busNamTo | TO bus name
TARA | TieDbData | Volt | TO nominal voltage level (in kV)
TARA | TieDbData | ArTo | TO area number
TARA | TieDbData | ZnTo | TO zone number
TARA | TieDbData | CKT | Circuit identifier
TARA | TieDbData | Mt | Branch metered end (From, To)
TARA | TieDbData | St | Branch status (0-off,1-on)
TARA | TieDbData | MW_Flow | Power flow (in MW)
TARA | TieDbData | MVAr_flow | Reactive power flow (in MVAr)
TARA | TieDbData | MVA_flow | Total power flow (in MVA)
TARA | TieDbData | LossesMW | Power losses (in MW)
TARA | TieDbData | RateA | Branch rating A (normal)
TARA | TieDbData | RateB | Branch rating B (LTE)
TARA | TieDbData | RateC | Branch rating C (STE)
TARA | TieDbData | R | Branch resistance (in pu)
TARA | TieDbData | X | Branch reactance (in pu)
TARA | TieDbData | Charg | Branch charging (in pu)
TARA | TieDbData | TranRat | transformer off nominal turns ratio
TARA | TieDbData | PhsShftGrd | Phase shifter Angle in degree
TARA | TieDbData | ShuntGFrom | Branch shunt susceptance, FROM bus (in pu)
TARA | TieDbData | ShuntBFrom | Branch shunt admittance, FROM bus (in pu)
TARA | TieDbData | ShuntGTo | Branch shunt susceptance, TO bus (in pu)
TARA | TieDbData | ShuntBTo | Branch shunt admittance, TO bus (in pu)
TARA | TieDbData | Length | Branch length
TARA | TieDbData | Ow1 | Owner 1
TARA | TieDbData | Own1% | Owner 1 share
TARA | TieDbData | Ow2 | Owner 2
TARA | TieDbData | Own2% | Owner 2 share
TARA | TieDbData | Ow3 | Owner 3
TARA | TieDbData | Own3% | Owner 3 share
TARA | TieDbData | Ow4 | Owner 4
TARA | TieDbData | Own4% | Owner 4 share
TARA | TransfmrData | Bus# | FROM bus number
TARA | TransfmrData | BusName | FROM bus name
TARA | TransfmrData | Volt | FROM bus base voltage (kV)
TARA | TransfmrData | Bus# | TO bus number
TARA | TransfmrData | BusName | TO bus name
TARA | TransfmrData | Volt | TO bus base voltage (kV)
TARA | TransfmrData | CKT | Circuit ID
TARA | TransfmrData | Area | From Bus Area number
TARA | TransfmrData | AreaName | From bus Area name
TARA | TransfmrData | voltViol | Voltage magnitude outside regulation voltage limits
TARA | TransfmrData | Status | Transformer tap adjust status
TARA | TransfmrData | tap | Current tap position
TARA | TransfmrData | #tap | Total tap position
TARA | TransfmrData | CurTarV | Current controlled voltage
TARA | TransfmrData | voltMin | Lower limit of voltage at controled bus
TARA | TransfmrData | voltMax | Upper limit of voltage at controled bus
TARA | TransfmrData | Ratio | Primary winding tap ratio
TARA | TransfmrData | AngleDegrees | Phase angle
TARA | TransfmrData | RatioTo | Secondary winding tap ratio
TARA | TransfmrData | Rat_Min | Minimum tap ratio
TARA | TransfmrData | Rat_Max | Maximum tap ratio
TARA | TransfmrData | Step | Tap step size
TARA | TransfmrData | LinDropR | Line drop compensation resistance
TARA | TransfmrData | LinDropX | Line drop compensation reactance
TARA | TransfmrData | Tabl | Impedance correction table ID
TARA | TransfmrData | Mon | Monitored bus, F = from, or T = to
TARA | TransfmrData | Bus# | Regulated bus number
TARA | TransfmrData | MonitBus | Regulated bus name
TARA | TransfmrData | Volt | Regulated bus base kV
TARA | ViolationScreenSum | Bus# | FROM bus number
TARA | ViolationScreenSum | BusName | Monitored branch FROM bus name
TARA | ViolationScreenSum | Volt | FROM nominal voltage level (in kV)
TARA | ViolationScreenSum | Bus# | Monitored branch TO bus number
TARA | ViolationScreenSum | BusName | Monitored branch TO bus name
TARA | ViolationScreenSum | Volt | TO nominal voltage level (in kV)
TARA | ViolationScreenSum | CKT | Circuit identifier
TARA | ViolationScreenSum | #Cnt | Contingency index
TARA | ViolationScreenSum | Contingency | Contingency name (description)
TARA | ViolationScreenSum | Rating | Branch (line or transformer) rating. In general, reflects rate A for base case violation, or rate B for contingency violation. Different ratings may be selected by user.
TARA | ViolationScreenSum | FlowMW | Branch flow (in MW)
TARA | ViolationScreenSum | Loading% | Branch loading (in %). If less than zero, initial flow in opposite direction than potential violation
TARA | ViolationScreenSum | HeadRoom | HeadRoom = Limit – Flow - LoadGrowthImpact - CutOffImpactLeft
TARA | ViolationScreenSum | TotRedis | Minimum possible redispatch required to overload report branch. 0 - if it is N-1 violation as defined in the LF case
TARA | ZoneSum | Zone | Zone number
TARA | ZoneSum | ZoneName | Zone name
TARA | ZoneSum | Buses | Number of buses
TARA | ZoneSum | NTies | Number of ties from Zone
TARA | ZoneSum | TotGen | Generation output (in MW -- sum of Pgen of units online)
TARA | ZoneSum | MaxGenOnl | Maximum generation output (in MW -- sum of Pmax of units online)
TARA | ZoneSum | MaxGenOff | Maximum generation output (in MW -- sum of Pmax of all units -- on- and off-line)
TARA | ZoneSum | LoadAct | Load at actual bus voltages (MW)
TARA | ZoneSum | LoadNom | Load at flat, 1.0 p.u., bus voltages (MW)
TARA | ZoneSum | LdInDifZone | Load assigned to this Zone but located in different Zone (MW)
TARA | ZoneSum | LdFrDifZone | Load assigned to different Zone but located in this Zone (MW)
TARA | ZoneSum | shuntLoss | Losses from real power bus shunts (MW)
TARA | ZoneSum | TotLosses | Total Zone Losses
TARA | ZoneSum | ZoneInterTies | Total flow on Zone ties (MW, positive is export)
TARA | ZoneSum | ZoneInterExtLd
TARA | OwnerList | Owner | Owner number
TARA | OwnerList | OwnName | Owner name
TARA | OwnerList | Buses | Number of buses for Owner
TARA | BusPath | Level | Bus path index. Each row shows one path branch; second bus in a row, becomes first bus in following row. Last row only shows one bus (target bus).
TARA | BusPath | Distn | Bus path distance (reverse of path index), indicating remaining buses until target bus is reached
TARA | BusPath | ElecDistn | Sum of the impedances of the shortest path (in pu)
TARA | BusPath | busFrm | FROM bus number
TARA | BusPath | busNamFr | FROM bus name
TARA | BusPath | Volt | FROM nominal voltage level (in kV)
TARA | BusPath | ArFr | FROM area number
TARA | BusPath | ZnFr | FROM zone number
TARA | BusPath | Btyp | Bus type (generator, load or swing)
TARA | BusPath | VoltMagPU | Voltage maginitude (in PU)
TARA | BusPath | VoltMagKV | Voltage maginitude (in kV)
TARA | BusPath | VoltAngl | Voltage angle (in degrees)
TARA | BusPath | busTo | TO bus number
TARA | BusPath | busNamTo | TO bus name
TARA | BusPath | Volt | TO nominal voltage level (in kV)
TARA | BusPath | ArTo | TO area number
TARA | BusPath | ZnTo | TO zone number
TARA | BusPath | CKT | Circuit identifier
TARA | BusPath | Resistanc | Branch resistance (in pu)
TARA | BusPath | Reactance | Branch reactance (in pu)
TARA | NE_FgLoad_Overlap | Dispatch Ind | List of generators was sorted according to DFAX with respect to this flowgate (unique flowgate Index number)
TARA | NE_FgLoad_Overlap | Mon Ind | Unique Index number of monitored flowgate
TARA | NE_FgLoad_Overlap | Monit Param | Flowgate name as specified in first line of flowgate definition inside flowgate file. This is the monitored branch name if flowgate file was created from TARA screen.
TARA | NE_FgLoad_Overlap | Contingency | Contingency name as specified in flowgate definition.
TARA | NE_FgLoad_Overlap | Rating | Flowgate rating.
TARA | NE_FgLoad_Overlap | FlowMW | Flowgate MW flow in base case
TARA | NE_FgLoad_Overlap | RefLoading% | Flowgate % loading resulting from Reference Dispatch.
TARA | NE_FgLoad_Overlap | StudyLoading% | Flowgate % loading resulting from Study Dispatch (create Reference Dispatch then remove Study Generator)
TARA | NE_FgLoad_Overlap | Failed? | 1 if StudyLoading is over 100%. 0 otherwise.
TARA | NE_FgLoad_Overlap | PassedScreen? | 1 if flowgate passed both initial TARA Screen and Overlapping Impact Screen. 0 if flowgate passed only initial TARA Screen.
TARA | NE_FgLoad_Overlap | BindingRefInd | Mon Ind of flowgate loaded at 100% for reference dispatch.
TARA | NE_FgLoad_Overlap | BigHelper Bus# BusName Volt Pgen StudyPMax | Bus Number, Bus Name, Bus Voltage, and Bus Pgen of largest impact helper for dispatch flowgate
TARA | NE_FgLoad_Overlap | StudyPMax | Study Generator PMAX
TARA | NE_FgLoad_Overlap | Bus# | Study Generator Bus #
TARA | NE_FgLoad_Overlap | BusName | Study Generator Bus Name
TARA | NE_FgLoad_Overlap | Volt | Study Generator Bus kV
TARA | NE_FgLoad_Overlap | Area | Study Generator Bus Area
TARA | NE_FgLoad_Overlap | Zone | Study Generator Bus Zone
TARA | NE_FgLoad_Overlap | Dispatch FgID | List of generators was sorted according to DFAX with respect to this flowgate (flowgate ID number found in fgt file)
TARA | NE_FgLoad_Overlap | STyp | Primary or Secondary flowgate?
TARA | NE_FgLoad_Overlap | PrimaryInd | Index of Primary flowgate.
TARA | NE_FgLoad_Overlap | Snapshot | Not used
TARA | NE_FgLoad_Overlap | FgID | Flowgate ID number of monitored flowgate specified in fgt file
TARA | NE_FgLoad_MIS | Dispatch Ind | List of generators was sorted according to DFAX with respect to this flowgate (unique flowgate Index number)
TARA | NE_FgLoad_MIS | Mon Ind | Unique Index number of monitored flowgate
TARA | NE_FgLoad_MIS | Monit Param | Flowgate name as specified in first line of flowgate definition inside flowgate file. This is the monitored branch name if flowgate file was created from TARA screen.
TARA | NE_FgLoad_MIS | Contingency | Contingency name as specified in flowgate definition.
TARA | NE_FgLoad_MIS | Rating | Flowgate rating.
TARA | NE_FgLoad_MIS | FlowInitMW | Flowgate MW flow in base case
TARA | NE_FgLoad_MIS | RefLoading% | Flowgate % loading resulting from Reference Dispatch.
TARA | NE_FgLoad_MIS | StudyLoading% | Flowgate % loading resulting from Study Dispatch (create Reference Dispatch then add Study Generator)
TARA | NE_FgLoad_MIS | RedispatchLoading1% | Flowgate % loading resulting from Study Dispatch after attempting to alleviate overloads by redispatch (method 1)
TARA | NE_FgLoad_MIS | RedispatchLoading2% | Flowgate % loading resulting from Study Dispatch after attempting to alleviate overloads by redispatch (method 2)
TARA | NE_FgLoad_MIS | TotalRedispatch1MW | Total MW amount of redispatch attempted (method 1)
TARA | NE_FgLoad_MIS | TotalRedispatch2MW | Total MW amount of redispatch attempted (method 2)
TARA | NE_FgLoad_MIS | FailedRedispatch1? | 1 if RedispatchLoading1% is over 100% or Total MW amount of redispatch attempted is over PMAX of study generator. 0 otherwise.
TARA | NE_FgLoad_MIS | FailedRedispatch2? | 1 if RedispatchLoading2% is over 100%. 0 otherwise.
TARA | NE_FgLoad_MIS | PassedScreen? | 1 if flowgate passed both initial TARA Screen and Overlapping Impact Screen. 0 if flowgate passed only initial TARA Screen.
TARA | NE_FgLoad_MIS | BindingRefInd | Mon Ind of flowgate loaded at 100% for reference dispatch.
TARA | NE_FgLoad_MIS | StudyPMax | Study Generator PMAX
TARA | NE_FgLoad_MIS | Bus# | Study Generator Bus #
TARA | NE_FgLoad_MIS | BusName | Study Generator Bus Name
TARA | NE_FgLoad_MIS | Volt | Study Generator Bus kV
TARA | NE_FgLoad_MIS | Area | Study Generator Bus Area
TARA | NE_FgLoad_MIS | Zone | Study Generator Bus Zone
TARA | NE_FgLoad_MIS | Dispatch FgID | List of generators was sorted according to DFAX with respect to this flowgate (flowgate ID number found in fgt file)
TARA | NE_FgLoad_MIS | STyp | Primary or Secondary flowgate?
TARA | NE_FgLoad_MIS | PrimaryInd | Index of Primary flowgate.
TARA | NE_FgLoad_MIS | Snapshot | Not used
TARA | NE_FgLoad_MIS | FgID | Flowgate ID number of monitored flowgate specified in fgt file
TARA | NE_Screen_MIS | STyp | Primary or Secondary flowgate?
TARA | NE_Screen_MIS | Blank | Index of Primary flowgate.
TARA | NE_Screen_MIS | Ind | Unique Index number of monitored flowgate
TARA | NE_Screen_MIS | FgID | Flowgate ID number of monitored flowgate specified in fgt file in first line of flowgate definition
TARA | NE_Screen_MIS | Monit Param | Flowgate name as specified in first line of flowgate definition inside flowgate file. This is the monitored branch name if flowgate file was created from TARA screen.
TARA | NE_Screen_MIS | Contingency | Contingency name as specified in flowgate definition
TARA | NE_Screen_MIS | Rating | Flowgate rating
TARA | NE_Screen_MIS | FlowMW | Flowgate MW flow in base case
TARA | NE_Screen_MIS | Dfax | Dfax of study generator with respect to flowgate
TARA | NE_Screen_MIS | MWImpact | Dfax*Pmax of study generator
TARA | NE_Screen_MIS | PctRatingImpact | MWImpact divided by Rating expressed as fraction
TARA | NE_Screen_MIS | DfaxRankCutoff | If study generator Dfax is greater than this, it is in the top x % harmers based on Dfax
TARA | NE_Screen_MIS | ImpactRankCutoff | If study generator MWImpact is greater than this, it is in the top x % harmers based on Dfax
TARA | NE_Screen_MIS | NumHarmers | Number of harmers (plants with Dfax greater than zero)
TARA | NE_Screen_MIS | DfaxFlag | 1 if study generator Dfax greater than Dfax cutoff. 0 otherwise.
TARA | NE_Screen_MIS | ImpactFlag | 1 if study generator MWImpact greater than MWImpact cutoff. 0 otherwise.
TARA | NE_Screen_MIS | DfaxRankFlag | 1 if study generator Dfax rank in top x % of harmers. 0 otherwise.
TARA | NE_Screen_MIS | ImpactRankFlag | 1 if study generator Impact rank in top x % of harmers. 0 otherwise.
TARA | NE_Screen_MIS | PercentWithSameDfaxAsStudy | Number of generators that have same dfax as study generator (within 0.0001 of study gen dfax value) expressed as fraction of total number of plants
TARA | NE_Screen_MIS | PercentWithSameDfaxAsStudy2 | Number of generators that have same dfax as study generator (within 0.005 of study gen dfax value) expressed as fraction of total number of plants
TARA | NE_Screen_MIS | TotPGenHarm | Sum of Pgen of all harmers
TARA | NE_Screen_MIS | TotPMaxHarm | Sum of Pmax of all harmers
TARA | NE_Screen_MIS | ActHarmerImpact | Sum of Pgen*Dfax of all harmers
TARA | NE_Screen_MIS | MaxHarmerImpact | Sum of Pmax*Dfax of all harmers
TARA | NE_Screen_MIS | TotPGenHelp | Sum of Pgen of all helpers
TARA | NE_Screen_MIS | TotPMaxHelp | Sum of Pmax of all helpers
TARA | NE_Screen_MIS | ActHelperImpact | Sum of Pgen*Dfax of all helpers
TARA | NE_Screen_MIS | MaxHelperImpact | Sum of Pmax*Dfax of all helpers
TARA | NE_Screen_MIS | StudyPMaxHarmerRatio | Pmax of study generator divided by TotPMaxHarm
TARA | NE_Screen_MIS | StudyImpactHarmerRatio | Impact of study generator divided by MaxHarmerImpact
TARA | NE_Screen_MIS | Blank | Study Generator PMAX
TARA | NE_Screen_MIS | Blank | Study Generator Bus #
TARA | NE_Screen_MIS | Blank | Study Generator Bus Name
TARA | NE_Screen_MIS | Blank | Study Generator Bus kV
TARA | NE_Screen_MIS | Blank | Study Generator Bus Area
TARA | NE_Screen_MIS | Blank | Study Generator Bus Zone
TARA | NE_Screen_Overlap | STyp | Primary or Secondary flowgate?
TARA | NE_Screen_Overlap | Blank | Index of Primary flowgate.
TARA | NE_Screen_Overlap | Ind | Unique Index number of monitored flowgate
TARA | NE_Screen_Overlap | FgID | Flowgate ID number of monitored flowgate specified in fgt file in first line of flowgate definition
TARA | NE_Screen_Overlap | Monit Param | Flowgate name as specified in first line of flowgate definition inside flowgate file. This is the monitored branch name if flowgate file was created from TARA screen.
TARA | NE_Screen_Overlap | Contingency | Contingency name as specified in flowgate definition
TARA | NE_Screen_Overlap | Rating | Flowgate rating
TARA | NE_Screen_Overlap | FlowMW | Flowgate MW flow in base case
TARA | NE_Screen_Overlap | Dfax | Dfax of study generator with respect to flowgate
TARA | NE_Screen_Overlap | MWImpact | Dfax*Pmax of study generator
TARA | NE_Screen_Overlap | PctRatingImpact | MWImpact divided by Rating expressed as fraction
TARA | NE_Screen_Overlap | DfaxRankCutoff | If study generator Dfax is greater than this, it is in the top x % harmers based on Dfax
TARA | NE_Screen_Overlap | ImpactRankCutoff | If study generator MWImpact is greater than this, it is in the top x % harmers based on Dfax
TARA | NE_Screen_Overlap | NumHarmers | Number of harmers (plants with Dfax greater than zero)
TARA | NE_Screen_Overlap | DfaxFlag | 1 if study generator Dfax greater than Dfax cutoff. 0 otherwise.
TARA | NE_Screen_Overlap | ImpactFlag | 1 if study generator MWImpact greater than MWImpact cutoff. 0 otherwise.
TARA | NE_Screen_Overlap | DfaxRankFlag | 1 if study generator Dfax rank in top x % of harmers. 0 otherwise.
TARA | NE_Screen_Overlap | ImpactRankFlag | 1 if study generator Impact rank in top x % of harmers. 0 otherwise.
TARA | NE_Screen_Overlap | PercentWithSameDfaxAsStudy | Number of generators that have same dfax as study generator (within 0.0001 of study gen dfax value) expressed as fraction of total number of plants
TARA | NE_Screen_Overlap | PercentWithSameDfaxAsStudy2 | Number of generators that have same dfax as study generator (within 0.005 of study gen dfax value) expressed as fraction of total number of plants
TARA | NE_Screen_Overlap | TotPGenHarm | Sum of Pgen of all harmers
TARA | NE_Screen_Overlap | TotPMaxHarm | Sum of Pmax of all harmers
TARA | NE_Screen_Overlap | ActHarmerImpact | Sum of Pgen*Dfax of all harmers
TARA | NE_Screen_Overlap | MaxHarmerImpact | Sum of Pmax*Dfax of all harmers
TARA | NE_Screen_Overlap | TotPGenHelp | Sum of Pgen of all helpers
TARA | NE_Screen_Overlap | TotPMaxHelp | Sum of Pmax of all helpers
TARA | NE_Screen_Overlap | ActHelperImpact | Sum of Pgen*Dfax of all helpers
TARA | NE_Screen_Overlap | MaxHelperImpact | Sum of Pmax*Dfax of all helpers
TARA | NE_Screen_Overlap | StudyPMaxHarmerRatio | Pmax of study generator divided by TotPMaxHarm
TARA | NE_Screen_Overlap | StudyImpactHarmerRatio | Impact of study generator divided by MaxHarmerImpact
TARA | NE_Screen_Overlap | Blank | Study Generator PMAX
TARA | NE_Screen_Overlap | Blank | Study Generator Bus #
TARA | NE_Screen_Overlap | Blank | Study Generator Bus Name
TARA | NE_Screen_Overlap | Blank | Study Generator Bus kV
TARA | NE_Screen_Overlap | Blank | Study Generator Bus Area
TARA | NE_Screen_Overlap | Blank | Study Generator Bus Zone
TARA | NE_Binding_MIS | Mon Ind | Unique Index number of monitored flowgate
TARA | NE_Binding_MIS | Monit Param | Flowgate name as specified in first line of flowgate definition inside flowgate file. This is the monitored branch name if flowgate file was created from TARA screen.
TARA | NE_Binding_MIS | Contingency | Contingency name as specified in flowgate definition
TARA | NE_Binding_MIS | Rating | Flowgate rating
TARA | NE_Binding_MIS | FlowMW | Flowgate MW flow in base case
TARA | NE_Binding_MIS | PctLoadingInit | Flowgate % loading in base case
TARA | NE_Binding_MIS | NumTimesBinding | Number of dispatches for which the flowgate limited the harmer-helper transfer
TARA | NE_Binding_MIS | Dfax-StudyGen | Dfax of study generator with respect to flowgate
TARA | NE_Binding_MIS | ImpactMW | Dfax*Pmax of study generator
TARA | NE_Binding_MIS | PctRating | MWImpact divided by Rating expressed as fraction
TARA | NE_Binding_MIS | PassedScreen? | 1 if flowgate passed MIS screen. 0 otherwise
TARA | NE_Binding_MIS | StudyPMax | Study Generator PMAX
TARA | NE_Binding_MIS | Bus# | Study Generator Bus #
TARA | NE_Binding_MIS | BusName | Study Generator Bus Name
TARA | NE_Binding_MIS | Volt | Study Generator Bus kV
TARA | NE_Binding_MIS | Area | Study Generator Bus Area
TARA | NE_Binding_MIS | Zone | Study Generator Bus Zone
TARA | NE_Binding_MIS | FgID | Flowgate ID number of monitored flowgate specified in fgt file
TARA | NE_Binding_Overlap | Mon Ind | Unique Index number of monitored flowgate
TARA | NE_Binding_Overlap | Monit Param | Flowgate name as specified in first line of flowgate definition inside flowgate file. This is the monitored branch name if flowgate file was created from TARA screen.
TARA | NE_Binding_Overlap | Contingency | Contingency name as specified in flowgate definition
TARA | NE_Binding_Overlap | Rating | Flowgate rating
TARA | NE_Binding_Overlap | FlowMW | Flowgate MW flow in base case
TARA | NE_Binding_Overlap | PctLoadingInit | Flowgate % loading in base case
TARA | NE_Binding_Overlap | NumTimesBinding | Number of dispatches for which the flowgate limited the harmer-helper transfer
TARA | NE_Binding_Overlap | Dfax-StudyGen | Dfax of study generator with respect to flowgate
TARA | NE_Binding_Overlap | ImpactMW | Dfax*Pmax of study generator
TARA | NE_Binding_Overlap | PctRating | MWImpact divided by Rating expressed as fraction
TARA | NE_Binding_Overlap | PassedScreen? | 1 if flowgate passed Overlap screen. 0 otherwise
TARA | NE_Binding_Overlap | StudyPMax | Study Generator PMAX
TARA | NE_Binding_Overlap | Bus# | Study Generator Bus #
TARA | NE_Binding_Overlap | BusName | Study Generator Bus Name
TARA | NE_Binding_Overlap | Volt | Study Generator Bus kV
TARA | NE_Binding_Overlap | Area | Study Generator Bus Area
TARA | NE_Binding_Overlap | Zone | Study Generator Bus Zone
TARA | NE_Binding_Overlap | FgID | Flowgate ID number of monitored flowgate specified in fgt file
TARA | NE_VioSum_Overlap | Dispatch Ind | List of generators was sorted according to DFAX with respect to this flowgate (unique flowgate Index number)
TARA | NE_VioSum_Overlap | Mon Ind | Unique Index number of monitored flowgate
TARA | NE_VioSum_Overlap | Monit Param | Flowgate name as specified in first line of flowgate definition inside flowgate file. This is the monitored branch name if flowgate file was created from TARA screen.
TARA | NE_VioSum_Overlap | Contingency | Contingency name as specified in flowgate definition.
TARA | NE_VioSum_Overlap | Rating | Flowgate rating.
TARA | NE_VioSum_Overlap | FlowMW | Flowgate MW flow in base case
TARA | NE_VioSum_Overlap | RefLoading% | Flowgate % loading resulting from Reference Dispatch.
TARA | NE_VioSum_Overlap | StudyLoading% | Flowgate % loading resulting from Study Dispatch (create Reference Dispatch then add Study Generator)
TARA | NE_VioSum_Overlap | NumOverloads | Number of dispatches for which the flowgate was overloaded
TARA | NE_VioSum_Overlap | Dfax-StudyGen | Dfax of study generator with respect to flowgate
TARA | NE_VioSum_Overlap | ImpactMW | Dfax*Pmax of study generator
TARA | NE_VioSum_Overlap | PctRating | MWImpact divided by Rating expressed as percentage
TARA | NE_VioSum_Overlap | Failed? | 1 if StudyLoading is over 100%. 0 otherwise.
TARA | NE_VioSum_Overlap | PassedScreen? | 1 if flowgate passed both initial TARA Screen and Overlapping Impact Screen. 0 if flowgate passed only initial TARA Screen.
TARA | NE_VioSum_Overlap | BindingRefInd | Mon Ind of flowgate loaded at 100% for reference dispatch.
TARA | NE_VioSum_Overlap | BigHelper Bus# BusName Volt Pgen StudyPMax | Bus Number, Bus Name, Bus Voltage, and Bus Pgen of largest impact helper for dispatch flowgate
TARA | NE_VioSum_Overlap | StudyPMax | Study Generator PMAX
TARA | NE_VioSum_Overlap | Bus# | Study Generator Bus #
TARA | NE_VioSum_Overlap | BusName | Study Generator Bus Name
TARA | NE_VioSum_Overlap | Volt | Study Generator Bus kV
TARA | NE_VioSum_Overlap | Area | Study Generator Bus Area
TARA | NE_VioSum_Overlap | Zone | Study Generator Bus Zone
TARA | NE_VioSum_Overlap | Dispatch FgID | List of generators was sorted according to DFAX with respect to this flowgate (flowgate ID number found in fgt file)
TARA | NE_VioSum_Overlap | STyp | Primary or Secondary flowgate?
TARA | NE_VioSum_Overlap | PrimaryInd | Index of Primary flowgate.
TARA | NE_VioSum_Overlap | Snapshot | Not used
TARA | NE_VioSum_Overlap | FgID | Flowgate ID number of monitored flowgate specified in fgt file
TARA | PRDstudy | Index | Unique Index number of monitored flowgate
TARA | PRDstudy | Dfax | Identifies the column to which DFAX values in the Dispatch section correspond. If Dfax_1, see column labeled Dfax_1 to find DFAX of each generator with respect to this flowgate.
TARA | PRDstudy | Monitored Element | Flowgate name as specified in first line of flowgate definition inside flowgate file. This is the monitored branch name if flowgate file was created from TARA screen.
TARA | PRDstudy | Contingency | Contingency name as specified in flowgate definition.
TARA | PRDstudy | Limit | Flowgate rating.
TARA | PRDstudy | FlowInit | Flowgate MW flow in base case
TARA | PRDstudy | FlowRes | Flowgate MW after making dispatch changes specified in column Pnew
TARA | PRDstudy | FlowChange | Change in flowgate MW flow after making dispatch changes specified in column Pnew
TARA | PRDstudy | Loading | Flowgate % loading resulting from dispatch changes specified in column Pnew
TARA | PRDstudy | PassedScreen? | 1 if flowgate passed both initial TARA Screen and De-list Screen. 0 if flowgate passed only initial TARA Screen.
TARA | PRDstudy | DispatchIndex | Dispatch Index from FgLoad sheet. List of generators was sorted according to DFAX with respect to this flowgate (unique flowgate Index number)
TARA | PRDstudy | Bus# | Bus number
TARA | PRDstudy | BusName | Bus name
TARA | PRDstudy | Volt | Nominal voltage level (in kV)
TARA | PRDstudy | Area | Area number
TARA | PRDstudy | Zone | Zone number
TARA | PRDstudy | Pgen | Bus (generating) power output (in MW) in the base case
TARA | PRDstudy | PMin | Bus minimum (generating) power output (in MW)
TARA | PRDstudy | PMax | Bus maximum (generating) power output (in MW)
TARA | PRDstudy | Pnew | Bus (generating) power output (in MW) for study dispatch. User can modify and see how flow changes on selected flowgates
TARA | PRDstudy | Pdelta | Pnew-Pgen
TARA | PRDstudy | Pavail | Pmax-Pnew
TARA | PRDstudy | Dfax_i | Dfax of generator with respect to flowgate i
TARA | PRDstudy | Impact_i | Dfax*Pdelta of study generator with respect to flowgate i
TARA | PRDref | Index | Unique Index number of monitored flowgate
TARA | PRDref | Dfax | Identifies the column to which DFAX values in the Dispatch section correspond. If Dfax_1, see column labeled Dfax_1 to find DFAX of each generator with respect to this flowgate.
TARA | PRDref | Monitored Element | Flowgate name as specified in first line of flowgate definition inside flowgate file. This is the monitored branch name if flowgate file was created from TARA screen.
TARA | PRDref | Contingency | Contingency name as specified in flowgate definition.
TARA | PRDref | Limit | Flowgate rating.
TARA | PRDref | FlowInit | Flowgate MW flow in base case
TARA | PRDref | FlowRes | Flowgate MW after making dispatch changes specified in column Pnew
TARA | PRDref | FlowChange | Change in flowgate MW flow after making dispatch changes specified in column Pnew
TARA | PRDref | Loading | Flowgate % loading resulting from dispatch changes specified in column Pnew
TARA | PRDref | PassedScreen? | 1 if flowgate passed both initial TARA Screen and De-list Screen. 0 if flowgate passed only initial TARA Screen.
TARA | PRDref | DispatchIndex | Dispatch Index from FgLoad sheet. List of generators was sorted according to DFAX with respect to this flowgate (unique flowgate Index number)
TARA | PRDref | Bus# | Bus number
TARA | PRDref | BusName | Bus name
TARA | PRDref | Volt | Nominal voltage level (in kV)
TARA | PRDref | Area | Area number
TARA | PRDref | Zone | Zone number
TARA | PRDref | Pgen | Bus (generating) power output (in MW) in the base case
TARA | PRDref | PMin | Bus minimum (generating) power output (in MW)
TARA | PRDref | PMax | Bus maximum (generating) power output (in MW)
TARA | PRDref | Pnew | Bus (generating) power output (in MW) for reference dispatch. User can modify and see how flow changes on selected flowgates
TARA | PRDref | Pdelta | Pnew-Pgen
TARA | PRDref | Pavail | Pmax-Pnew
TARA | PRDref | Dfax_i | Dfax of generator with respect to flowgate i
TARA | PRDref | Impact_i | Dfax*Pdelta of study generator with respect to flowgate i
TARA | PRDredisp1 | Index | Unique Index number of monitored flowgate
TARA | PRDredisp1 | Dfax | Identifies the column to which DFAX values in the Dispatch section correspond. If Dfax_1, see column labeled Dfax_1 to find DFAX of each generator with respect to this flowgate.
TARA | PRDredisp1 | Monitored Element | Flowgate name as specified in first line of flowgate definition inside flowgate file. This is the monitored branch name if flowgate file was created from TARA screen.
TARA | PRDredisp1 | Contingency | Contingency name as specified in flowgate definition.
TARA | PRDredisp1 | Limit | Flowgate rating.
TARA | PRDredisp1 | FlowInit | Flowgate MW flow in base case
TARA | PRDredisp1 | FlowRes | Flowgate MW after making dispatch changes specified in column Pnew
TARA | PRDredisp1 | FlowChange | Change in flowgate MW flow after making dispatch changes specified in column Pnew
TARA | PRDredisp1 | Loading | Flowgate % loading resulting from dispatch changes specified in column Pnew
TARA | PRDredisp1 | PassedScreen? | 1 if flowgate passed both initial TARA Screen and De-list Screen. 0 if flowgate passed only initial TARA Screen.
TARA | PRDredisp1 | DispatchIndex | Dispatch Index from FgLoad sheet. List of generators was sorted according to DFAX with respect to this flowgate (unique flowgate Index number)
TARA | PRDredisp1 | Bus# | Bus number
TARA | PRDredisp1 | BusName | Bus name
TARA | PRDredisp1 | Volt | Nominal voltage level (in kV)
TARA | PRDredisp1 | Area | Area number
TARA | PRDredisp1 | Zone | Zone number
TARA | PRDredisp1 | Pgen | Bus (generating) power output (in MW) in the base case
TARA | PRDredisp1 | PMin | Bus minimum (generating) power output (in MW)
TARA | PRDredisp1 | PMax | Bus maximum (generating) power output (in MW)
TARA | PRDredisp1 | Pnew | Bus (generating) power output (in MW) for redispatch method 1. User can modify and see how flow changes on selected flowgates
TARA | PRDredisp1 | Pdelta | Pnew-Pgen
TARA | PRDredisp1 | Pavail | Pmax-Pnew
TARA | PRDredisp1 | Dfax_i | Dfax of generator with respect to flowgate i
TARA | PRDredisp1 | Impact_i | Dfax*Pdelta of study generator with respect to flowgate i
TARA | PRDredisp2 | Index | Unique Index number of monitored flowgate
TARA | PRDredisp2 | Dfax | Identifies the column to which DFAX values in the Dispatch section correspond. If Dfax_1, see column labeled Dfax_1 to find DFAX of each generator with respect to this flowgate.
TARA | PRDredisp2 | Monitored Element | Flowgate name as specified in first line of flowgate definition inside flowgate file. This is the monitored branch name if flowgate file was created from TARA screen.
TARA | PRDredisp2 | Contingency | Contingency name as specified in flowgate definition.
TARA | PRDredisp2 | Limit | Flowgate rating.
TARA | PRDredisp2 | FlowInit | Flowgate MW flow in base case
TARA | PRDredisp2 | FlowRes | Flowgate MW after making dispatch changes specified in column Pnew
TARA | PRDredisp2 | FlowChange | Change in flowgate MW flow after making dispatch changes specified in column Pnew
TARA | PRDredisp2 | Loading | Flowgate % loading resulting from dispatch changes specified in column Pnew
TARA | PRDredisp2 | PassedScreen? | 1 if flowgate passed both initial TARA Screen and De-list Screen. 0 if flowgate passed only initial TARA Screen.
TARA | PRDredisp2 | DispatchIndex | Dispatch Index from FgLoad sheet. List of generators was sorted according to DFAX with respect to this flowgate (unique flowgate Index number)
TARA | PRDredisp2 | Bus# | Bus number
TARA | PRDredisp2 | BusName | Bus name
TARA | PRDredisp2 | Volt | Nominal voltage level (in kV)
TARA | PRDredisp2 | Area | Area number
TARA | PRDredisp2 | Zone | Zone number
TARA | PRDredisp2 | Pgen | Bus (generating) power output (in MW) in the base case
TARA | PRDredisp2 | PMin | Bus minimum (generating) power output (in MW)
TARA | PRDredisp2 | PMax | Bus maximum (generating) power output (in MW)
TARA | PRDredisp2 | Pnew | Bus (generating) power output (in MW) for redispatch method 2. User can modify and see how flow changes on selected flowgates
TARA | PRDredisp2 | Pdelta | Pnew-Pgen
TARA | PRDredisp2 | Pavail | Pmax-Pnew
TARA | PRDredisp2 | Dfax_i | Dfax of generator with respect to flowgate i
TARA | PRDredisp2 | Impact_i | Dfax*Pdelta of study generator with respect to flowgate i
TARA | GRDstudy | Index | Unique Index number of monitored flowgate
TARA | GRDstudy | Dfax | Identifies the column to which DFAX values in the Dispatch section correspond. If Dfax_1, see column labeled Dfax_1 to find DFAX of each generator with respect to this flowgate.
TARA | GRDstudy | Monitored Element | Flowgate name as specified in first line of flowgate definition inside flowgate file. This is the monitored branch name if flowgate file was created from TARA screen.
TARA | GRDstudy | Contingency | Contingency name as specified in flowgate definition.
TARA | GRDstudy | Limit | Flowgate rating.
TARA | GRDstudy | FlowInit | Flowgate MW flow in base case
TARA | GRDstudy | FlowRes | Flowgate MW after making dispatch changes specified in column Pnew
TARA | GRDstudy | FlowChange | Change in flowgate MW flow after making dispatch changes specified in column Pnew
TARA | GRDstudy | Loading | Flowgate % loading resulting from dispatch changes specified in column Pnew
TARA | GRDstudy | PassedScreen? | 1 if flowgate passed both initial TARA Screen and De-list Screen. 0 if flowgate passed only initial TARA Screen.
TARA | GRDstudy | DispatchIndex | Dispatch Index from FgLoad sheet. List of generators was sorted according to DFAX with respect to this flowgate (unique flowgate Index number)
TARA | GRDstudy | Bus# | Bus number
TARA | GRDstudy | BusName | Bus name
TARA | GRDstudy | Volt | Nominal voltage level (in kV)
TARA | GRDstudy | ID | Unit ID
TARA | GRDstudy | Sta | Unit Status. 1=on 0=off
TARA | GRDstudy | Area | Area number
TARA | GRDstudy | Zone | Zone number
TARA | GRDstudy | Pgen | Unit (generating) power output (in MW) in the base case
TARA | GRDstudy | PMin | Unit minimum (generating) power output (in MW)
TARA | GRDstudy | PMax | Unit maximum (generating) power output (in MW)
TARA | GRDstudy | StaNew | Status of unit for study dispatch. User can modify and see how flow changes on selected flowgates.
TARA | GRDstudy | Pnew | Unit (generating) power output (in MW) for study dispatch. User can modify and see how flow changes on selected flowgates
TARA | GRDstudy | Pdelta | Pnew-Pgen
TARA | GRDstudy | Pavail | Pmax-Pnew
TARA | GRDstudy | Dfax_i | Dfax of generator with respect to flowgate i
TARA | GRDstudy | Impact_i | Dfax*Pdelta of study generator with respect to flowgate i
TARA | GRDref | Index | Unique Index number of monitored flowgate
TARA | GRDref | Dfax | Identifies the column to which DFAX values in the Dispatch section correspond. If Dfax_1, see column labeled Dfax_1 to find DFAX of each generator with respect to this flowgate.
TARA | GRDref | Monitored Element | Flowgate name as specified in first line of flowgate definition inside flowgate file. This is the monitored branch name if flowgate file was created from TARA screen.
TARA | GRDref | Contingency | Contingency name as specified in flowgate definition.
TARA | GRDref | Limit | Flowgate rating.
TARA | GRDref | FlowInit | Flowgate MW flow in base case
TARA | GRDref | FlowRes | Flowgate MW after making dispatch changes specified in column Pnew
TARA | GRDref | FlowChange | Change in flowgate MW flow after making dispatch changes specified in column Pnew
TARA | GRDref | Loading | Flowgate % loading resulting from dispatch changes specified in column Pnew
TARA | GRDref | PassedScreen? | 1 if flowgate passed both initial TARA Screen and De-list Screen. 0 if flowgate passed only initial TARA Screen.
TARA | GRDref | DispatchIndex | Dispatch Index from FgLoad sheet. List of generators was sorted according to DFAX with respect to this flowgate (unique flowgate Index number)
TARA | GRDref | Bus# | Bus number
TARA | GRDref | BusName | Bus name
TARA | GRDref | Volt | Nominal voltage level (in kV)
TARA | GRDref | ID | Unit ID
TARA | GRDref | Sta | Unit Status. 1=on 0=off. Remember, if units status is 0 but Pgen or Pnew is nonzero, the unit output will actually be zero.
TARA | GRDref | Area | Area number
TARA | GRDref | Zone | Zone number
TARA | GRDref | Pgen | Unit (generating) power output (in MW) in the base case
TARA | GRDref | PMin | Unit minimum (generating) power output (in MW)
TARA | GRDref | PMax | Unit maximum (generating) power output (in MW)
TARA | GRDref | StaNew | Status of unit for reference dispatch. User can modify and see how flow changes on selected flowgates.
TARA | GRDref | Pnew | Unit (generating) power output (in MW) for reference dispatch. User can modify and see how flow changes on selected flowgates
TARA | GRDref | Pdelta | Pnew-Pgen
TARA | GRDref | Pavail | Pmax-Pnew
TARA | GRDref | Dfax_i | Dfax of generator with respect to flowgate i
TARA | GRDref | Impact_i | Dfax*Pdelta of study generator with respect to flowgate i
TARA | GRDredisp1 | Index | Unique Index number of monitored flowgate
TARA | GRDredisp1 | Dfax | Identifies the column to which DFAX values in the Dispatch section correspond. If Dfax_1, see column labeled Dfax_1 to find DFAX of each generator with respect to this flowgate.
TARA | GRDredisp1 | Monitored Element | Flowgate name as specified in first line of flowgate definition inside flowgate file. This is the monitored branch name if flowgate file was created from TARA screen.
TARA | GRDredisp1 | Contingency | Contingency name as specified in flowgate definition.
TARA | GRDredisp1 | Limit | Flowgate rating.
TARA | GRDredisp1 | FlowInit | Flowgate MW flow in base case
TARA | GRDredisp1 | FlowRes | Flowgate MW after making dispatch changes specified in column Pnew
TARA | GRDredisp1 | FlowChange | Change in flowgate MW flow after making dispatch changes specified in column Pnew
TARA | GRDredisp1 | Loading | Flowgate % loading resulting from dispatch changes specified in column Pnew
TARA | GRDredisp1 | PassedScreen? | 1 if flowgate passed both initial TARA Screen and De-list Screen. 0 if flowgate passed only initial TARA Screen.
TARA | GRDredisp1 | DispatchIndex | Dispatch Index from FgLoad sheet. List of generators was sorted according to DFAX with respect to this flowgate (unique flowgate Index number)
TARA | GRDredisp1 | Bus# | Bus number
TARA | GRDredisp1 | BusName | Bus name
TARA | GRDredisp1 | Volt | Nominal voltage level (in kV)
TARA | GRDredisp1 | ID | Unit ID
TARA | GRDredisp1 | Sta | Unit Status. 1=on 0=off. Remember, if units status is 0 but Pgen or Pnew is nonzero, the unit output will actually be zero.
TARA | GRDredisp1 | Area | Area number
TARA | GRDredisp1 | Zone | Zone number
TARA | GRDredisp1 | Pgen | Unit (generating) power output (in MW) in the base case
TARA | GRDredisp1 | PMin | Unit minimum (generating) power output (in MW)
TARA | GRDredisp1 | PMax | Unit maximum (generating) power output (in MW)
TARA | GRDredisp1 | StaNew | Status of unit for reference dispatch. User can modify and see how flow changes on selected flowgates.
TARA | GRDredisp1 | Pnew | Unit (generating) power output (in MW) for redispatch method 1. User can modify and see how flow changes on selected flowgates
TARA | GRDredisp1 | Pdelta | Pnew-Pgen
TARA | GRDredisp1 | Pavail | Pmax-Pnew
TARA | GRDredisp1 | Dfax_i | Dfax of generator with respect to flowgate i
TARA | GRDredisp1 | Impact_i | Dfax*Pdelta of study generator with respect to flowgate i
TARA | GRDredisp2 | Index | Unique Index number of monitored flowgate
TARA | GRDredisp2 | Dfax | Identifies the column to which DFAX values in the Dispatch section correspond. If Dfax_1, see column labeled Dfax_1 to find DFAX of each generator with respect to this flowgate.
TARA | GRDredisp2 | Monitored Element | Flowgate name as specified in first line of flowgate definition inside flowgate file. This is the monitored branch name if flowgate file was created from TARA screen.
TARA | GRDredisp2 | Contingency | Contingency name as specified in flowgate definition.
TARA | GRDredisp2 | Limit | Flowgate rating.
TARA | GRDredisp2 | FlowInit | Flowgate MW flow in base case
TARA | GRDredisp2 | FlowRes | Flowgate MW after making dispatch changes specified in column Pnew
TARA | GRDredisp2 | FlowChange | Change in flowgate MW flow after making dispatch changes specified in column Pnew
TARA | GRDredisp2 | Loading | Flowgate % loading resulting from dispatch changes specified in column Pnew
TARA | GRDredisp2 | PassedScreen? | 1 if flowgate passed both initial TARA Screen and De-list Screen. 0 if flowgate passed only initial TARA Screen.
TARA | GRDredisp2 | DispatchIndex | Dispatch Index from FgLoad sheet. List of generators was sorted according to DFAX with respect to this flowgate (unique flowgate Index number)
TARA | GRDredisp2 | Bus# | Bus number
TARA | GRDredisp2 | BusName | Bus name
TARA | GRDredisp2 | Volt | Nominal voltage level (in kV)
TARA | GRDredisp2 | ID | Unit ID
TARA | GRDredisp2 | Sta | Unit Status. 1=on 0=off. Remember, if units status is 0 but Pgen or Pnew is nonzero, the unit output will actually be zero.
TARA | GRDredisp2 | Area | Area number
TARA | GRDredisp2 | Zone | Zone number
TARA | GRDredisp2 | Pgen | Unit (generating) power output (in MW) in the base case
TARA | GRDredisp2 | PMin | Unit minimum (generating) power output (in MW)
TARA | GRDredisp2 | PMax | Unit maximum (generating) power output (in MW)
TARA | GRDredisp2 | StaNew | Status of unit for reference dispatch. User can modify and see how flow changes on selected flowgates.
TARA | GRDredisp2 | Pnew | Unit (generating) power output (in MW) for redispatch method 2. User can modify and see how flow changes on selected flowgates
TARA | GRDredisp2 | Pdelta | Pnew-Pgen
TARA | GRDredisp2 | Pavail | Pmax-Pnew
TARA | GRDredisp2 | Dfax_i | Dfax of generator with respect to flowgate i
TARA | GRDredisp2 | Impact_i | Dfax*Pdelta of study generator with respect to flowgate i
TARA | GRDcalc | NN | Identifies the column to which DFAX values in the Dispatch section correspond. If 1, see column labeled Dfax_1 to find DFAX of each generator with respect to this flowgate.
TARA | GRDcalc | LFCaseName | Name of RAW data file to which report data corresponds. Blank if only one case was loaded into TARA
TARA | GRDcalc | Monitored Element | Flowgate name as specified in first line of flowgate definition inside flowgate file. This is the monitored branch name if flowgate file was created from TARA screen.
TARA | GRDcalc | Contingency | Contingency name as specified in flowgate definition.
TARA | GRDcalc | Limit | Flowgate rating.
TARA | GRDcalc | FlowInit | Flowgate MW flow in base case
TARA | GRDcalc | FlowRes | Flowgate MW after making dispatch changes specified in column Pnew
TARA | GRDcalc | FlowChange | Change in flowgate MW flow after making dispatch changes specified in column Pnew
TARA | GRDcalc | Loading | Flowgate % loading resulting from dispatch changes specified in column Pnew
TARA | GRDcalc | Bus# | Bus number
TARA | GRDcalc | BusName | Bus name
TARA | GRDcalc | Volt | Nominal voltage level (in kV)
TARA | GRDcalc | ID | Unit ID
TARA | GRDcalc | Sta | Unit Status. 1=on 0=off
TARA | GRDcalc | Area | Area number
TARA | GRDcalc | Zone | Zone number
TARA | GRDcalc | Pgen | Unit (generating) power output (in MW) in the base case
TARA | GRDcalc | PMin | Unit minimum (generating) power output (in MW)
TARA | GRDcalc | PMax | Unit maximum (generating) power output (in MW)
TARA | GRDcalc | StaNew | New status of unit. User can modify and see how flow changes on selected flowgates.
TARA | GRDcalc | Pnew | New unit (generating) power output (in MW). User can modify and see how flow changes on selected flowgates
TARA | GRDcalc | Pdelta | Pnew-Pgen
TARA | GRDcalc | Pavail | Pmax-Pnew
TARA | GRDcalc | Dfax_i | Dfax of generator with respect to flowgate i
TARA | GRDcalc | Impact_i | Dfax*Pdelta of study generator with respect to flowgate i
TARA | PRDcalc | NN | Identifies the column to which DFAX values in the Dispatch section correspond. If 1, see column labeled Dfax_1 to find DFAX of each generator with respect to this flowgate.
TARA | PRDcalc | LFCaseName | Name of RAW data file to which report data corresponds. Blank if only one case was loaded into TARA
TARA | PRDcalc | Monitored Element | Flowgate name as specified in first line of flowgate definition inside flowgate file. This is the monitored branch name if flowgate file was created from TARA screen.
TARA | PRDcalc | Contingency | Contingency name as specified in flowgate definition.
TARA | PRDcalc | Limit | Flowgate rating.
TARA | PRDcalc | FlowInit | Flowgate MW flow in base case
TARA | PRDcalc | FlowRes | Flowgate MW after making dispatch changes specified in column Pnew
TARA | PRDcalc | FlowChange | Change in flowgate MW flow after making dispatch changes specified in column Pnew
TARA | PRDcalc | Loading | Flowgate % loading resulting from dispatch changes specified in column Pnew
TARA | PRDcalc | Bus# | Bus number
TARA | PRDcalc | BusName | Bus name
TARA | PRDcalc | Volt | Nominal voltage level (in kV)
TARA | PRDcalc | Area | Area number
TARA | PRDcalc | Zone | Zone number
TARA | PRDcalc | Pgen | Bus (generating) power output (in MW) in the base case
TARA | PRDcalc | PMin | Bus minimum (generating) power output (in MW)
TARA | PRDcalc | PMax | Bus maximum (generating) power output (in MW)
TARA | PRDcalc | Pnew | New bus (generating) power output (in MW). User can modify and see how flow changes on selected flowgates
TARA | PRDcalc | Pdelta | Pnew-Pgen
TARA | PRDcalc | Pavail | Pmax-Pnew
TARA | PRDcalc | Dfax_i | Dfax of generator with respect to flowgate i
TARA | PRDcalc | Impact_i | Dfax*Pdelta of study generator with respect to flowgate i
TARA | NE_FgateStressSum | BidIndex | FCM Bid Index (assigned by TARA according to order in FCM bid file)
TARA | NE_FgateStressSum | BidID | FCM Bid ID as read from bid file
TARA | NE_FgateStressSum | Type | Demand or Offer
TARA | NE_FgateStressSum | PnodeID | Pnode ID read from bid file
TARA | NE_FgateStressSum | PnodeNam | Pnode name read from bid file
TARA | NE_FgateStressSum | MW | Pmax reduction to test (will be subtracted from base case Pmax)
TARA | NE_FgateStressSum | StressFgIndex | Unique Index number of stressed flowgate
TARA | NE_FgateStressSum | StressFgID | Flowgate ID number of stressed flowgate. Same value as found in fgt file and may not be unique.
TARA | NE_FgateStressSum | Stress Monit Param | Flowgate name as specified in first line of flowgate definition inside flowgate file. This is the monitored branch name if flowgate file was created from TARA screen.
TARA | NE_FgateStressSum | Stress Contingency | Contingency name as specified in flowgate definition.
TARA | NE_FgateStressSum | StressFgtRating | Flowgate rating.
TARA | NE_FgateStressSum | Base%Loading | Flowgate % loading in base case
TARA | NE_FgateStressSum | Ref%Loading | Flowgate % loading resulting from Reference Dispatch.
TARA | NE_FgateStressSum | Study%Loading | Flowgate % loading resulting from Study Dispatch (create Reference Dispatch then add Study Generator)
TARA | NE_FgateStressSum | DfaxDemand | Dfax of study generator with respect to flowgate
TARA | NE_FgateStressSum | DemandMWRef | MW redispatch by SCRD in Reference dispatch. (MW Up + MW Down)/2
TARA | NE_FgateStressSum | DemandMWStudyMW | MW redispatch by SCRD in Study dispatch. (MW Up + MW Down)/2
TARA | NE_FgateStressSum | DispPassFail | Did FCM bid pass or fail reliability review for this stressed flowgate?
TARA | NE_FgateStressSum | RefMWRedispatch | Pgen of study bid in reference dispatch
TARA | NE_FgateStressSum | StudyMWRedispatchMW | Pgen of study bid in study dispatch
TARA | NE_FgateStressSum | NumPenRef | Number of SCRD penalties applied in reference dispatch.
TARA | NE_FgateStressSum | NumPenStudy | Number of SCRD penalties applied in study dispatch.
TARA | NE_FgateStressSum | HelperMWBase | Biggest helper Pgen in base case
TARA | NE_FgateStressSum | HelperMWRef | Biggest helper Pgen in reference dispatch
TARA | NE_FgateStressSum | HelperMWStudy | Biggest helper Pgen in study dispatch
TARA | NE_FgateStressSum | BidderName | Biggest helper name
TARA | NE_FgateStressSum | unitType | Biggest helper unit type
TARA | NE_FgateStressSum | Fuel/Schd | Biggest helper fuel type
TARA | NE_FgateStressSum | OrgName | Biggest helper organization name
TARA | NE_FgateStressSum | BTyp | Biggest helper bidder type
TARA | NE_FgateStressSum | InHarmerMWDownStudy | Total in-circle harmer MW turned down
TARA | NE_FgateStressSum | InHarmerImpactDownStudy | Total impact (dfax*MW) of in-circle harmers turned down
TARA | NE_FgateStressSum | InHarmerPnodesDownStudy | Number of in-circle harmers turned down
TARA | NE_FgateStressSum | OutHelperMWUpStudy | Total out-circle helper MW turned down
TARA | NE_FgateStressSum | OutHelperImpactUpStudy | Total impact (dfax*MW) of out-circle helpers turned down
TARA | NE_FgateStressSum | OutHelperPnodesUpStudy | Number of out-circle helpers turned down
TARA | NE_BindingFgates | BidIndex | FCM Bid Index (assigned by TARA according to order in FCM bid file)
TARA | NE_BindingFgates | BidID | FCM Bid ID as read from bid file
TARA | NE_BindingFgates | Type | Demand or Offer
TARA | NE_BindingFgates | PnodeID | Pnode ID read from bid file
TARA | NE_BindingFgates | PnodeNam | Pnode name read from bid file
TARA | NE_BindingFgates | MW | Pmax reduction to test (will be subtracted from base case Pmax)
TARA | NE_BindingFgates | BidStatus | ACCEPTED or REJECTED based on reliability review criteria
TARA | NE_BindingFgates | StressFgIndex | Unique Index number of stressed flowgate
TARA | NE_BindingFgates | StressFgID | Flowgate ID number of stressed flowgate. Same value as found in fgt file and may not be unique.
TARA | NE_BindingFgates | Stress Monit Param | Flowgate name as specified in first line of stressed flowgate definition inside flowgate file. This is the monitored branch name if flowgate file was created from TARA screen.
TARA | NE_BindingFgates | Stress Contingency | Contingency name as specified in stressed flowgate definition.
TARA | NE_BindingFgates | StressFgtRatingStudy | Stressed Flowgate rating.
TARA | NE_BindingFgates | BindingFgIndexStudy | Unique Index number of binding flowgate
TARA | NE_BindingFgates | BindingFgID | Flowgate ID number of binding flowgate. Same value as found in fgt file and may not be unique.
TARA | NE_BindingFgates | Binding Monit Param | Flowgate name as specified in first line of binding flowgate definition inside flowgate file. This is the monitored branch name if flowgate file was created from TARA screen.
TARA | NE_BindingFgates | Binding Contingency | Contingency name as specified in binding flowgate definition.
TARA | NE_BindingFgates | BindingFgtRatingStudy | Binding Flowgate rating.
TARA | NE_BindingFgates | DfaxDemand | Dfax of study generator with respect to flowgate
TARA | NE_BindingFgates | RefOrStudyBinding | Ref or Study tells which dispatch the Binding Fgate was binding for
TARA | NE_BindingFgates | DispPassFail | Did FCM bid pass or fail reliability review for this stressed flowgate?
TARA | TRLProp | Monitored Facility | Monitored Facility
TARA | TRLProp | CntInd | Contingency Index
TARA | TRLProp | Contingency | Contingency Name
TARA | TRLProp | TrLim | Transfer MW at which mon/con pair reaches 100% loading
TARA | TRLProp | Dfax | Transfer distribution factor for mon/con pair
TARA | TRLProp | Rating | Rating
TARA | TRLProp | Flow | MW flow at 0 MW transfer
TARA | TRLProp | Loading% | %Loading at 0 MW transfer
TARA | TRLProp | HeadRoom | Rating-Flow
TARA | TRLProp | Fg_1_MW | #1 Interface flow at transfer level corresponding to TrLim value
TARA | TRLProp | Fg_2_MW | #2 Interface flow at transfer level corresponding to TrLim value
TARA | TRLProp | Fg_3_MW | #3 Interface flow at transfer level corresponding to TrLim value
TARA | MaxMWSum | TransLimit | Sending generation increased by this much and Receiving generation decreased by this much
TARA | MaxMWSum | SendSubsys | Name of sending system
TARA | MaxMWSum | SendInitMW | Total Pgen of sending system in base case
TARA | MaxMWSum | SendMaxMW | SendInitMW+TransLimit
TARA | MaxMWSum | SendMaxGenOn | Total Pmax of all online units in sending system
TARA | MaxMWSum | SendMaxGenOff | Total Pmax of all online and offline units in sending system
TARA | MaxMWSum | RecSubsys | Name of receiving system
TARA | MaxMWSum | RecInitMW | Total Pgen of receiving system in base case
TARA | MaxMWSum | RecMinMW | RecInitMW-TransLimit
TARA | MaxMWSum | RecMaxGenOn | Total Pmax of all online units in receiving system
TARA | MaxMWSum | RecMaxGenOff | Total Pmax of all online and offline units in receiving system
TARA | GenRemDist | nBus | number of buses between generator and regulated bus
TARA | GenRemDist | ElectDist | minumum impedance between generator and regulated bus
TARA | GenRemDist | Typ | Rem = remote, RFx = ???, Rof = ???
TARA | GenRemDist | Bus# | Generator bus number
TARA | GenRemDist | BusName | Generator bus name
TARA | GenRemDist | Volt | Generator bus base voltage
TARA | GenRemDist | Area # | Generator area number
TARA | GenRemDist | AreaName | Generator area name
TARA | GenRemDist | Bus# | Regulated bus number
TARA | GenRemDist | BusName | Regulated bus name
TARA | GenRemDist | Volt | Regulated bus base voltage
TARA | GenRemDist | Area # | Regulated bus area number
TARA | GenRemDist | AreaName | Regulated bus area name
TARA | GenRemDist | Vgen | Generator terminal voltage
TARA | GenRemDist | Vrem | Regulated bus voltage
TARA | GenRemDist | Vtarg | Regulated bus voltage target
TARA | GenRemDist | Verror | Regulated bus voltage minus target
TARA | GenRemDist | Qgen | Generator MVAr output
TARA | GenRemDist | Qmin | Generator MVAr minimum limit
TARA | GenRemDist | Qmax | Generator MVAr maximum limit
TARA | GenRemDist | QRange | Generator Qmax minus Qmin
TARA | GenRemDist | Pgen | Generator MW output
TARA | GenRemDist | Pmax | Generator maximum MW
TARA | BusMism | Bus# | Bus number
TARA | BusMism | BusName | Bus name
TARA | BusMism | Volt | Bus base voltage
TARA | BusMism | Area | Bus area number
TARA | BusMism | Zone | Bus zone numbe
TARA | BusMism | BTyp | Bus type
TARA | BusMism | CodeBTyp | Bus type code (1 load, 2 generator, 3 swing)
TARA | BusMism | PMism | Real power mismatch (MW)
TARA | BusMism | QMism | Reactive power mismatch (MVAr)
TARA | BusMism | MVAMism | Apparent power mismatch (MVA)
TARA | BusMism | Vmag [PU] | Bus voltage (per-unit)
TARA | BusMism | Vmag [kV] | Bus voltage (kV)
TARA | BusMism | Vangle | Bus voltage angle
TARA | BusMism | PGen | Generation at bus (MW)
TARA | BusMism | PloadNom | Load at bus (MW)
TARA | BusMism | GShntOn | Real power shunt (MW)
TARA | BusMism | BShntOn | Reactive power shunt (MVAr)
TARA | BusMism | Ownr | Bus owner number
TARA | ConEvents | Cont ID | Contingency index
TARA | ConEvents | Contingency | Contingency name
TARA | ConEvents | Disabled? | Contingency disabled
TARA | ConEvents | Excluded? | Contingency excluded
TARA | ConEvents | PrimEventType | Equipment for this facility
TARA | ConEvents | SecEventType | Action for this equipment
TARA | ConEvents | EventFacility | Facility description in this contingency
TARA | ConEvents | MW | Pre-contingency MW flow for this facility
TARA | VoltMonit | Bus# | Bus number of voltage monitored bus
TARA | VoltMonit | BusName | Bus name of voltage monitored bus
TARA | VoltMonit | Volt | Base voltage of voltage monitored bus
TARA | VoltMonit | Area | Area number of voltage monitored bus
TARA | VoltMonit | Zone | Zone number of voltage monitored bus
TARA | VoltMonit | Cont ID | Contingency index
TARA | VoltMonit | Cont Name | Basecase (no contingency applied)
TARA | VoltMonit | Radial Index | Radial index (≤ 1.0, 1.0 = radial)
TARA | VoltMonit | # of Branches | # of branches connected to the bus
TARA | VoltMonit | Max MW Flow | Max MW bus injection or withdrawal
TARA | VoltMonit | MinVoltBase | Low voltage criteria for pre-contingency case
TARA | VoltMonit | MaxVoltBase | High voltage criteria for pre-contingency case
TARA | VoltMonit | VDropLim | Post-contingency voltage drop criteria
TARA | VoltMonit | VRiseLim | Post-contingency voltage rise criteria
TARA | VoltMonit | MinVoltCont | Low voltage criteria for post-contingency case
TARA | VoltMonit | MaxVoltCont | High voltage criteria for post-contingency case
TARA | VoltMonit | BaseVolt | Pre-contingency voltage (pu)
TARA | BranchFlows | Monitored Facility | Monitored facility
TARA | BranchFlows | St | Monitored equipment status
TARA | BranchFlows | Base MW Flow | Real power flow (MW)
TARA | BranchFlows | Base MVAR FLow | Reactive power flow (MVAr)
TARA | BranchFlows | MVA¦AMP Flow | MVA flow or Voltage Adjusted MVA flow
TARA | BranchFlows | MVA¦AMP | Either MVA or AMP
TARA | BranchFlows | Radial Index | Radial index (≤ 1.0, 1.0 = radial)
TARA | BranchFlows | Rate Base (MVA) | Monitored facility base case rating
TARA | BranchFlows | Rate Cont (MVA) | Monitored facility base case loading (%)
TARA | BranchFlows | DC %Loading | Contingency % loading - linear (DC) solution
TARA | BranchFlows | AC %Loading | Contingency % loading - nonlinear (AC) solution
TARA | BranchFlows | Number of Appearances in Cont File | Number of times referenced in contingency file
TARA | BranchFlows | Fr_Vmag [PU] | FROM bus voltage magnitude (pu)
TARA | BranchFlows | Vmag [kV] | FROM bus voltage magnitude (kV)
TARA | BranchFlows | Vangle | FROM bus voltage angle (deg)
TARA | BranchFlows | To_Vmag [PU] | TO bus voltage magnitude (pu)
TARA | BranchFlows | Vmag [kV] | TO bus voltage magnitude (kV)
TARA | BranchFlows | Vangle | TO bus voltage angle (deg)
TARA | BranchFlows | ExcludeStatus | Indicate a facility to be exlcuded in basecase or/and contingency
TARA | BranchFlows | NumExcludeConts | Number of contingencies for which this branch is excluded
TARA | ACContSum | Cont ID | Contingency index
TARA | ACContSum | Contingency | Contingency name
TARA | ACContSum | Status | Ovl for thermal violation, Vlt for voltage violation
TARA | ACContSum | #Itr | Number of iterations needed for solution
TARA | ACContSum | #Pms | # of buses whose MW mismatch is greater than bus mismatch tolerance defined in LF Solution Option
TARA | ACContSum | #Qms | # of buses whose MVAR mismatch is greater than bus mismatch tolerance defined in LF Solution Option
TARA | ACContSum | PmaxMism | Maximum real power mismatch (MW)
TARA | ACContSum | Bus# | Bus number of maximum real power mismatch
TARA | ACContSum | BusName | Bus name of maximum real power mismatch
TARA | ACContSum | Volt | Base kV of bus with maximum real power mismatch
TARA | ACContSum | VoltMagPU | Voltage (pu) at bus with maximum real power mismatch
TARA | ACContSum | QmaxMism | Maximum reactive power mismatch (MVAr)
TARA | ACContSum | Bus# | Bus number of maximum reactive power mismatch
TARA | ACContSum | BusName | Bus name of maximum reactive power mismatch
TARA | ACContSum | Volt | Base kV of bus with maximum reactive power mismatch
TARA | ACContSum | VoltMagPU | Voltage (pu) at bus with maximum reactive power mismatch
TARA | ACContSum | OvlSever | Summation of square of each overloaded percentage above 100%
TARA | ACContSum | #Ovl | Number of overloads for this contingency
TARA | ACContSum | Worst | Highest overload
TARA | ACContSum | VltSevrInd | Summation of (Vmag-Vmin)^2 for all voltage violations
TARA | ACContSum | VLow | Lowest voltage
TARA | ACContSum | VHi | Highest voltage
TARA | ACContSum | Drop | Lowest drop in voltage
TARA | ACContSum | Rise | Highest rise in voltage
TARA | VoltWorstViol | Bus # | Bus number
TARA | VoltWorstViol | Bus Name | Bus name
TARA | VoltWorstViol | Base kV | Bus base kV
TARA | VoltWorstViol | Area Name | Bus area name
TARA | VoltWorstViol | Zone Name | Bus zone name
TARA | VoltWorstViol | Bus Type | Bus type
TARA | VoltWorstViol | Pgen | Real power generation at bus
TARA | VoltWorstViol | Pload | Real power load at bus
TARA | VoltWorstViol | G Shunt | Real power shunt at bus
TARA | VoltWorstViol | B Shunt | Reactive power shunt at bus
TARA | VoltWorstViol | Min Volt Limit | Low voltage criteria for bus
TARA | VoltWorstViol | Max Volt Limit | High voltage criteria for bus
TARA | VoltWorstViol | %Vdrop Limit | Maximum voltage drop criteria for bus
TARA | VoltWorstViol | %Vrise Limit | Maximum voltage rise criteria for bus
TARA | VoltWorstViol | Cont Name | Contingency name
TARA | VoltWorstViol | Cont ID | Contingency ID
TARA | VoltWorstViol | Base Volt | Bus pre-contingency voltage
TARA | VoltWorstViol | Cont Volt | Bus post-contingency voltage
TARA | VoltWorstViol | %Vdrop | % voltage drop (negative for voltage rise)
TARA | VoltWorstViol | Vmag Violation | Low, Worst Low, High, and Worst High voltage magnitude violation
TARA | VoltWorstViol | Vchng Violation | Drop, Worst Drop, Rise, Worst Rise voltage violation
TARA | VoltWorstViol | # of Branches | # of branches connected after continency events
TARA | VoltWorstViol | Radial Index | Radial index (≤ 1.0, 1.0 = radial)
TARA | VoltWorstViol | Max MW Flow | Max MW bus injection or withdrawal
TARA | BranWorstLoad | Monitored Facility | FROM bus TO bus circuit ID
TARA | BranWorstLoad | Fr Bus | FROM bus number
TARA | BranWorstLoad | Fr Name | FROM bus name
TARA | BranWorstLoad | To Bus | TO bus number
TARA | BranWorstLoad | To Name | TO bus name
TARA | BranWorstLoad | CKT | Circuit ID
TARA | BranWorstLoad | kVs | kV level(s)
TARA | BranWorstLoad | Areas Name | Area name(s)
TARA | BranWorstLoad | Zones Name | Zone name(s)
TARA | BranWorstLoad | Rate Base (MVA) | Monitored facility normal rating (MVA)
TARA | BranWorstLoad | Rate Cont (MVA) | Monitored facility contingency rating (MVA)
TARA | BranWorstLoad | Cont Name | Contingency name
TARA | BranWorstLoad | Cont ID | Contingency index
TARA | BranWorstLoad | Base Flow (MVA) | Flow before contingency (MVA)
TARA | BranWorstLoad | Cont Flow (MVA) | Flow after contingency (MVA)
TARA | BranWorstLoad | Final DC %Loading | Contingency % loading - linear (DC) solution
TARA | BranWorstLoad | Final AC %Loading | Contingency % loading - nonlinear (AC) solution
TARA | BranWorstLoad | Soft Exclude | Facility defined as soft excluded facility
TARA | BranWorstLoad | Severity Rank | Severity rank for monitored facility
TARA | BranWorstLoad | Radial Index | Radial index (≤ 1.0, 1.0 = radial)
TARA | BranWorstLoad | Base MW Flow | Base MW flow - nonlinear (AC) solution. Opposite flow direction for negative sign
TARA | BranWorstLoad | Cont MW Flow | Contingency MW flow- nonlinear (AC) solution. Opposite flow direction for negative sign
TARA | BranWorstLoad | Base MVAR Flow | Base case MVAR flow, AC solution
TARA | BranWorstLoad | Cont MVAR Flow | Contingency MVAR flow
TARA | BranWorstLoad | Fr Base Volt | FROM bus base voltage
TARA | BranWorstLoad | Fr Cont Volt | FROM bus contingency voltage
TARA | BranWorstLoad | To Base Volt | TO bus base voltage
TARA | BranWorstLoad | To Cont Volt | TO bus contingency voltage
TARA | QVBusBasedSummary | Bus # | Bus number
TARA | QVBusBasedSummary | Bus Name | Bus name
TARA | QVBusBasedSummary | Base kV | Bus base kV
TARA | QVBusBasedSummary | Area | Bus area number
TARA | QVBusBasedSummary | Zone | Bus zone number
TARA | QVBusBasedSummary | Cont Name | Contingency Name
TARA | QVBusBasedSummary | Cont ID | Contingency index
TARA | QVBusBasedSummary | Maximum Reactive Margin (MVAR) | Maximum amount of reactive power at study bus that can be increased until reaching non-convergent solution. If the maximum reactive margin is negative, the case is non-convergent in N-1 AC test
TARA | QVBusBasedSummary | Volt at Reactive Margin | Study bus voltage at the maximum reactive margin
TARA | QVBusBasedSummary | Reactive Margin Rank | Sort maximum reactive margin in ascending order for each study bus. Rank 1 is the worst contingency with the lowest reactive margin for the study bus
TARA | QVBusBasedSummary | Base¦Cont Volt W/O QV | Study bus voltage in basecase or contingency (No QV test)
TARA | QVBusBasedSummary | Reactive Margin at VLimit (MVAR) | Reactive margin at the voltage cutoff (or operational low voltage limit)
TARA | QVBusBasedSummary | Low Volt Limit | Voltage cutoff. If QV test creates a non-convergence before reaching this limit, it will be written “Not Reached.”
TARA | QVBusBasedSummary | Test Range Vlow | Lowest study bus voltage tested
TARA | QVBusBasedSummary | Test Range Vhigh | Highest study bus voltage tested
TARA | QVStudyBusReport | Bus # | Bus number
TARA | QVStudyBusReport | Bus Name | Bus name
TARA | QVStudyBusReport | Base kV | Bus base kV
TARA | QVStudyBusReport | Area | Bus area number
TARA | QVStudyBusReport | Zone | Bus zone number
TARA | QVStudyBusReport | Cont Name | Contingency Name
TARA | QVStudyBusReport | Cont ID | Contingency index
TARA | QVStudyBusReport | Base¦Cont Volt | Study bus voltage in basecase or contingency (No QV test)
TARA | QVStudyBusReport | Reg. Volt | Study bus voltage in basecase or contingency in QV test
TARA | QVStudyBusReport | Bus Angle [deg] | Study bus angle in basecase or contingency in QV test
TARA | QVStudyBusReport | Qgen [MVAR] | Reactive power injection or withdrawal from the study bus for each QV test
TARA | QVStudyBusReport | Flag | The smallest reactive power injection or withdrawal from each study bus and contingency in QV test
TARA | QVBusVolt | Bus # | Bus number
TARA | QVBusVolt | Bus Name | Bus name
TARA | QVBusVolt | Base kV | Bus base kV
TARA | QVBusVolt | Area | Bus area number
TARA | QVBusVolt | Zone | Bus zone number
TARA | QVBusVolt | Cont Name | Contingency Name
TARA | QVBusVolt | Cont ID | Contingency index
TARA | QVBusVolt | Orig. Volt | Bus voltage in the original case with no contingency (No QV test)
TARA | QVBusVolt | Base¦Cont Volt | Bus voltage in basecase or contingency (No QV test)
TARA | QVBusVolt | Q Base¦Cont Volt | Bus voltage in basecase or contingency in QV test
TARA | QVBusVolt | Study Bus | QV Study bus
TARA | QVBusVolt | Study Bus Name | QV Study Bus
TARA | QVBusVolt | Study Bus Volt | QV Study Bus Base kV
TARA | QVBusVolt | Bus Distance | # of the shorted buses (stations) from the study bus
TARA | QVShunt | Bus # | Bus number
TARA | QVShunt | Bus Name | Bus name
TARA | QVShunt | Base kV | Bus base kV
TARA | QVShunt | Area | Bus area number
TARA | QVShunt | Zone | Bus zone number
TARA | QVShunt | Shunt Min | Minimum MVAR shunt installed
TARA | QVShunt | Shunt Max | Maximum MVAR shunt installed
TARA | QVShunt | Control Mode | Shunt control mode
TARA | QVShunt | Vlower Limit | Controlled Voltage Upper Limit
TARA | QVShunt | Vupper Limit | Controlled voltage Lower Limit
TARA | QVShunt | Cont Name | Contingency Name
TARA | QVShunt | Cont ID | Contingency index
TARA | QVShunt | Study Bus | QV Study bus
TARA | QVShunt | Study Bus Name | QV Study Bus
TARA | QVShunt | Study Bus Volt | QV Study Bus Base kV
TARA | QVShunt | Bus Distance | # of the shorted buses (stations) from the study bus
TARA | QVShunt | Base¦Cont Volt | Shunt bus voltage in basecase or contingency (No QV test)
TARA | QVShunt | Q Base¦Cont Volt | Shunt bus voltage in basecase or contingency in QV test
TARA | QVShunt | Base¦Cont Shunt MVAR | Nominal shunt MVAR output in basecase or contingency (No QV test)
TARA | QVShunt | Q Base¦Cont Shunt MVAR | Nominal shunt MVAR output in basecase or contingency in QV test
TARA | QVGen | Bus # | Bus number
TARA | QVGen | Bus Name | Bus name
TARA | QVGen | Base kV | Bus base kV
TARA | QVGen | Area | Bus area number
TARA | QVGen | Zone | Bus zone number
TARA | QVGen | ID | Machine Identifier
TARA | QVGen | Status | Machine Status
TARA | QVGen | Pon | Machine MW Power Output
TARA | QVGen | Qgen | Machine MVAR Power Output
TARA | QVGen | Pmin | Minimum machine real power out
TARA | QVGen | Pmax | Maximum machine real power output
TARA | QVGen | Qmin | Minimum generator reactive power output
TARA | QVGen | Qmax | Maximum generator reactive power output
TARA | QVGen | Cont Name | Contingency Name
TARA | QVGen | Cont ID | Contingency index
TARA | QVGen | Study Bus | QV Study bus
TARA | QVGen | Study Bus Name | QV Study Bus
TARA | QVGen | Study Bus Volt | QV Study Bus Base kV
TARA | QVGen | Bus Distance | # of the shorted buses (stations) from the study bus
TARA | QVBranch | Monitored Facility: | Monitored parameter
TARA | QVBranch | kVs | kV level(s)
TARA | QVBranch | Areas | Area Number(s)
TARA | QVBranch | Zones | Zone Numbers(s)
TARA | QVBranch | Rate Base (MVA) | Monitored facility normal rating (MVA)
TARA | QVBranch | Rate Cont (MVA) | Monitored facility contingency rating (MVA)
TARA | QVBranch | Cont Name | Contingency Name
TARA | QVBranch | Cont ID | Contingency index
TARA | QVBranch | Base¦Cont Flow (MVA) | Branch MVA flow in basecase or contingency (No QV test)
TARA | QVBranch | Q Base¦Cont Flow (MVA) | Branch MVA flow in basecase or contingency in QV test
TARA | QVBranch | Base¦Cont MW Flow | Branch MW flow in basecase or contingency (No QV test)
TARA | QVBranch | Q Base¦Cont MW Flow | Branch MW flow in basecase or contingency in QV test
TARA | QVBranch | Base¦Cont MVAR Flow | Branch MVAR flow in basecase or contingency (No QV test)
TARA | QVBranch | Q Base¦Cont MVAR Flow | Branch MVAR flow in basecase or contingency in QV test
TARA | QVBranch | Q Base¦Cont MVAR Loss | Branch MVAR loss in basecase or contingency in QV test
TARA | QVBranch | Q Base¦Cont From Bus Volt | From bus voltage in basecase or contingency in QV test
TARA | QVBranch | Q Base¦Cont To Bus Volt | To bus voltage in basecase or contingency in QV test
TARA | QVBranch | Base¦Cont dAngle [deg] | Branch bus angle difference in basecase or contingency (No QV test)
TARA | QVBranch | Q Base¦Cont dAngle [deg] | Branch bus angle difference in basecase or contingency in QV test
TARA | QVBranch | Branch Layer | # of buses to reach the study bus
TARA | QVBranch | Study Bus | QV Study bus
TARA | QVBranch | Study Bus Name | QV Study Bus
TARA | QVBranch | Study Bus Volt | QV Study Bus Base kV
TARA | RAS_Summary | Cont ID | Contingency Index for which RAS was applied
TARA | RAS_Summary | Contingency Name | Contingency Name for which RAS was applied
TARA | RAS_Summary | Pre-RAS %Loading | %Loading after the contingency but before RAS is applied
TARA | RAS_Summary | Post-RAS %Loading | %Loading after the contingency and after RAS is applied
TARA | RAS_Summary | RAS Name | Name of RAS
TARA | RAS_Summary | RAS Index | Index of RAS (numbered in order of input)
TARA | RAS_Summary | RAS resolves all overloads? | Yes if all branches are below 100% after RAS is applied
TARA | RAS_Summary | Num Overloads Before | Number of branches over 100% after contingency but before RAS is applied
TARA | RAS_Summary | Num Overloads After | Number of branches over 100% after RAS is applied
TARA | RAS_Summary | Overload Severity Index Before | Sum of (%Loading-100) for all branches over 100% after contingency but before RAS is applied
TARA | RAS_Summary | Overload Severity Index After | Sum of (%Loading-100) for all branches over 100% after RAS is applied
TARA | RAS_Summary | Worst %Loading Before | Highest %Loading among overloaded branches after contingency but before RAS is applied
TARA | RAS_Summary | Worst %Loading After | Highest %Loading among overloaded branches after RAS is applied
TARA | RAS_Summary | Isolated Load | Consequentially islanded load due to RAS application
TARA | RAS_Summary | Isolated Generation | Consequentially islanded generation due to RAS application
TARA | RAS_Flows | Cont ID | Contingency Index for which RAS was applied
TARA | RAS_Flows | Contingency Name | Contingency Name for which RAS was applied
TARA | RAS_Flows | Before RAS %Loading | %Loading after the contingency but before RAS is applied
TARA | RAS_Flows | After RAS %Loading | %Loading after the contingency and after RAS is applied
TARA | RAS_Flows | RAS Name | Name of RAS
TARA | RAS_Flows | RAS Index | Index of RAS (numbered in order of input)
TARA | RAS_Flows | RAS resolves all overloads? | Yes if all branches are below 100% after RAS is applied
TARA | RAS_Flows | Num Overloads Before | Number of branches over 100% after contingency but before RAS is applied
TARA | RAS_Flows | Num Overloads After | Number of branches over 100% after RAS is applied
TARA | RAS_Flows | Overload Severity Index Before | Sum of (%Loading-100) for all branches over 100% after contingency but before RAS is applied
TARA | RAS_Flows | Overload Severity Index After | Sum of (%Loading-100) for all branches over 100% after RAS is applied
TARA | RAS_Flows | Worst %Loading Before | Highest %Loading among overloaded branches after contingency but before RAS is applied
TARA | RAS_Flows | Worst %Loading After | Highest %Loading among overloaded branches after RAS is applied
TARA | RAS_Flows | Isolated Load | Consequentially islanded load due to RAS application
TARA | RAS_Flows | Isolated Generation | Consequentially islanded generation due to RAS application
TARA | RAS_Voltages | Cont ID | Contingency Index for which RAS was applied
TARA | RAS_Voltages | Contingency Name | Contingency Name for which RAS was applied
TARA | RAS_Voltages | RAS Name | Name of RAS
TARA | RAS_Voltages | RAS Index | Index of RAS (numbered in order of input)
TARA | RAS_Voltages | Cont Volt Before RAS | Bus voltage after the contingency but before RAS is applied
TARA | RAS_Voltages | Cont Volt After RAS | Bus voltage after the contingency and after RAS is applied
TARA | RAS_Voltages | %Vdrop due to RAS | Difference between bus voltage before and after RAS (multiplied by 100)
TARA | RAS_Voltages | Vmag Violation Before | Type of voltage violation at the bus after the contingency but before RAS is applied
TARA | RAS_Voltages | Vmag Violation After | Type of voltage violation at the bus after the contingency and after RAS is applied
TARA | LogFile | no formal columns | no help exists for this report at this time -- content self-explanatory, or not fully developed yet
TARA | TLCvdet | LimitTyp | Criteria for judging a voltage problem
TARA | TLCvdet | Interface | Interface or Flowgate under study
TARA | TLCvdet | MWFlowPreContNoTransfer | Pre-contingency Interface flow before any transfer increment is applied
TARA | TLCvdet | ContingencyThatCausesViolation | Most Limiting Critical contingency
TARA | TLCvdet | MWFlowPostContNoTransfer | Critical Interface Post-Contingency flow before any transfer increment is applied
TARA | TLCvdet | MonElement | Limiting factor: Critical Bus with lowest voltage or Voltage Drop or Branch Overloaded for Thermal Problem
TARA | TLCvdet | PreContValuAtLimit | Monitored factor pre-contingency value (KV or MW/MVA)
TARA | TLCvdet | PostContValuAtLimit | Monitored factor post-critical contingency value (KV or MW) at the limiting transfer level
TARA | TLCvdet | FinalValueAtLimit | Limiting value
TARA | TLCvdet | TrnsfrLvlAtLimit | Transfer Level at the Limiting value
TARA | TLCvdet | MWFlowPreContAtLimit | Interface transfer Limit MW pre-contingency
TARA | TLCvdet | IntrfcBackOff | Interface Transfer Limit adjustment MW
TARA | TLCvdet | MWLimitPreContAtLimit | Interface transfer limit MW pre-contingency flow with adjustment factor
TARA | TLCvdet | MWFlowPostContAtLimit | Interface transfer limit MW post critical contingency
TARA | TLCvdet | IntrfcBackOffAtLimit | Interface Transfer Limit adjustment MW
TARA | TLCvdet | MWLimitPreContAtLimit | Interface transfer limit MW post- critical contingency with adjustment factor
TARA | NE_FgLoadOpt_Olap | ProjIndex | Index assigned to study project by TARA (based on order read from file)
TARA | NE_FgLoadOpt_Olap | ID | User-assigned ID of study project (read from file column ResourceID)
TARA | NE_FgLoadOpt_Olap | ProjName | User-assigned name of study project (read from file column ProjectName)
TARA | NE_FgLoadOpt_Olap | ProjMW | Study project maximum MW to be evaluated (read from file column MW)
TARA | NE_FgLoadOpt_Olap | Bus# | Bus Number of study unit
TARA | NE_FgLoadOpt_Olap | BusName | Bus Name of study unit
TARA | NE_FgLoadOpt_Olap | Volt | Bus nominal KV of study unit
TARA | NE_FgLoadOpt_Olap | Area | Bus Area of study unit
TARA | NE_FgLoadOpt_Olap | Zone | Bus Zone of study unit
TARA | NE_FgLoadOpt_Olap | Dispatch Ind | Index of stressed flowgate (index is assigned to flowgates based on order read by TARA)
TARA | NE_FgLoadOpt_Olap | Mon Ind | Index of flowgate reported for this row. Flows and Loadings for this specific Dispatch stress condition
TARA | NE_FgLoadOpt_Olap | Monit Param | Flowgate monitored branch corresponding to reported flowgate flows for this row.
TARA | NE_FgLoadOpt_Olap | Contingency | Flowgate contingency corresponding to reported flowgate flows for this row.
TARA | NE_FgLoadOpt_Olap | Rating | Rating of flowgate reported on this row
TARA | NE_FgLoadOpt_Olap | FlowMW | Original case flowgate flow (post-contingency if flowgate has contingency). This is before stress occurs.
TARA | NE_FgLoadOpt_Olap | RefFlowMW | Reference Dispatch flow on monitored flowgate (for this row Mon Ind) after performing stress on the base case
TARA | NE_FgLoadOpt_Olap | StudyFlowMW | Study Dispatch flow on monitored flowgate (for this row Mon Ind) after adding Study unit at Project-Rated MW to the Reference Dispatch case. SCD does not redispatch for overloads.
TARA | NE_FgLoadOpt_Olap | PARFlowMW | PARs are optimized for Study Dispatch case to see if PAR adjustments can resolve overloads. Value in this cell is flow on monitored flowgate (for this row Mon Ind) after optimizing PARs
TARA | NE_FgLoadOpt_Olap | PmaxRestricted FlowMW | Use SCD to maximize output of Study Unit (see column Pmax Restricted Gen MW). At maximum Study Unit output, this is flow on monitored flowgate (for this row Mon Ind)
TARA | NE_FgLoadOpt_Olap | RefLoading% | RefFlowMW divided by Flowgate Rating expressed as percentage
TARA | NE_FgLoadOpt_Olap | StudyLoading% | StudyFlowMW divided by Flowgate Rating expressed as percentage
TARA | NE_FgLoadOpt_Olap | PARLoading% | PARFlowMW divided by Flowgate Rating expressed as percentage
TARA | NE_FgLoadOpt_Olap | PmaxRestricted Loading% | PmaxRestricted FlowMW divided by Flowgate Rating expressed as percentage
TARA | NE_FgLoadOpt_Olap | Pmax Restricted Gen MW | Maximum output of Study Unit such that no overloads are caused. Use SCD to maximize output of Study Unit.
TARA | NE_FgLoadOpt_Olap | Monitored Ref Dispatch? | Was this flowgate monitored for the Reference Dispatch stress? If so, then it can restrict the applied stress. If not, then its loading can go over 100%. See option "Restrict Ref Disp Mon Fgates". If enabled, then only flowgates that meet Study Unit impact thresholds are monitored for reference dispatch.
TARA | NE_FgLoadOpt_Olap | Binding Ref Dispatch? | Was this flowgate binding for the Reference Dispatch stress? If so, then it is restricting the applied stress. User question - does it make sense that this flowgate should restrict the stress?
TARA | NE_FgLoadOpt_Olap | Passed Screen Study Unit? | See "Screening Options" on Viewer menu. If value is 1, then the Study Unit satisfied the screening options conditions for this flowgate. It will be monitored for overloads.
TARA | NE_FgLoadOpt_Olap | Failed Flowgate? | Can only be 1 if the flowgate passed the "Screening Options" conditions AND the flowgate went over 100% loading when the Study Unit was added (Study Dispatch)
TARA | NE_FgLoadOpt_Olap | RedispatchMW | For the initial Reference Dispatch (stress) condition, how many MW were moved to cause the stress (this much went up and the same amount went down to maintain energy balance)
TARA | NE_FgLoadOpt_Olap | PGenBase Big Helper MW | In the starting initial base case, what was Pgen of the unit selected as Biggest Helper. For each Reference Dispatch stress, the biggest help is selected as the initial "sink" when turning up units.
TARA | NE_FgLoadOpt_Olap | PGenRef Big Helper MW | In the Reference Dispatch stress condition, what was Pgen of the unit selected as Biggest Helper. For each Reference Dispatch stress, the biggest help is selected as the initial "sink" when turning up units.
TARA | NE_FgLoadOpt_Olap | Dfax Big Helper | For the stressed flowgate (see Dispatch Ind column), this value is the Dfax of the biggest helper that was selected when applying the Reference Dispatch stress. Dfax is with respect to user-selected Dfax reference
TARA | NE_FgLoadOpt_Olap | PGen Avail Ref OutsideRegion MW | After the biggest helper MW are used in creating the Reference Dispatch, additional sink MW are available from aggregate set of units "outside region of influence". How many MW were available in the "outside region". If this is zero, then the stress will stop. See Viewer "Analysis Options" for outside region cutoffs
TARA | NE_FgLoadOpt_Olap | Pdelta Ref OutsideRegion MW | When creating the Reference Dispatch, the amount scaled down from aggregate set of units "outside region of influence". If this is zero, then the biggest helper MW were not reduced to zero before a monitored flowgate hit the limit. See Viewer "Analysis Options" for outside region cutoffs
TARA | NE_FgLoadOpt_Olap | PGen Avail Study OutsideRegion MW | After the biggest helper MW are used in creating the Study Dispatch, additional sink MW are available from aggregate set of units "outside region of influence". How many MW were available in the "outside region". If this is zero, then the remaining MW needed will sink to the case swing bus. See Viewer "Analysis Options" for outside region cutoffs and for the subsysem to be used for finding outside region units for the Study Dispatch.
TARA | NE_FgLoadOpt_Olap | Pdelta Study OutsideRegion MW | When creating the Study Dispatch, the amount scaled down from aggregate set of units "outside region of influence". If this is zero, then the biggest helper MW were not reduced to zero before a monitored flowgate hit the limit. See Viewer "Analysis Options" for outside region cutoffs (a different sysem can be selected for Ref than for Study)
TARA | NE_FgLoadOpt_Olap | BigHelper Bus# BusName Volt Pgen Pmax | Bus number and name for biggest helper
TARA | NE_FgLoadOpt_Olap | Dispatch FgID | Flowgate ID for the stressed flowgate. This is not the same as the Flowgate Index. Flowgate ID is found in the flowgate definition in the fgt file.
TARA | NE_FgBindOpt_Olap | ProjIndex | Index assigned to study project by TARA (based on order read from file)
TARA | NE_FgBindOpt_Olap | ID | User-assigned ID of study project (read from file column ResourceID)
TARA | NE_FgBindOpt_Olap | ProjName | User-assigned name of study project (read from file column ProjectName)
TARA | NE_FgBindOpt_Olap | ProjMW | Study project maximum MW to be evaluated (read from file column MW)
TARA | NE_FgBindOpt_Olap | Bus# | Bus Number of study unit
TARA | NE_FgBindOpt_Olap | BusName | Bus Name of study unit
TARA | NE_FgBindOpt_Olap | Volt | Bus nominal KV of study unit
TARA | NE_FgBindOpt_Olap | Area | Bus Area of study unit
TARA | NE_FgBindOpt_Olap | Zone | Bus Zone of study unit
TARA | NE_FgBindOpt_Olap | Dispatch Ind | For the Monitored flowgate, this is an example of a Stress Dispatch for which the Monitored Flowgate was binding in the Reference Dispatch (Index of stressed flowgate (index is assigned to flowgates based on order read by TARA))
TARA | NE_FgBindOpt_Olap | Mon Ind | Monitored flowgate that was binding for Reference stresses - index of flowgate reported for this row. Flows and Loadings for this specific Dispatch stress condition
TARA | NE_FgBindOpt_Olap | Monit Param | Monitored flowgate that was binding for Reference stresses - monitored branch corresponding to reported flowgate flows for this row.
TARA | NE_FgBindOpt_Olap | Contingency | Monitored flowgate that was binding for Reference stresses - Flowgate contingency corresponding to reported flowgate flows for this row.
TARA | NE_FgBindOpt_Olap | Rating | Rating of flowgate reported on this row
TARA | NE_FgBindOpt_Olap | FlowMW | Original case flowgate flow (post-contingency if flowgate has contingency). This is before stress occurs.
TARA | NE_FgBindOpt_Olap | NumTimesBinding | Key component of this report. How many times was this Flowgate (see Mon Ind, Param, Contingency) binding when creating the reference stress. Should this flowgate be restricting stress conditions?
TARA | NE_FgBindOpt_Olap | StudyDfax | Dfax of Study Unit on the Flowgate identified by Mon Ind, Monit Param, Contingency columns
TARA | NE_FgBindOpt_Olap | RefFlowMW | Reference Dispatch flow on monitored flowgate (for this row Mon Ind) after performing stress on the base case
TARA | NE_FgBindOpt_Olap | StudyFlowMW | Study Dispatch flow on monitored flowgate (for this row Mon Ind) after adding Study unit at Project-Rated MW to the Reference Dispatch case. SCD does not redispatch for overloads.
TARA | NE_FgBindOpt_Olap | PARFlowMW | PARs are optimized for Study Dispatch case to see if PAR adjustments can resolve overloads. Value in this cell is flow on monitored flowgate (for this row Mon Ind) after optimizing PARs
TARA | NE_FgBindOpt_Olap | PmaxRestricted FlowMW | Use SCD to maximize output of Study Unit (see column Pmax Restricted Gen MW). At maximum Study Unit output, this is flow on monitored flowgate (for this row Mon Ind)
TARA | NE_FgBindOpt_Olap | RefLoading% | RefFlowMW divided by Flowgate Rating expressed as percentage
TARA | NE_FgBindOpt_Olap | StudyLoading% | StudyFlowMW divided by Flowgate Rating expressed as percentage
TARA | NE_FgBindOpt_Olap | PARLoading% | PARFlowMW divided by Flowgate Rating expressed as percentage
TARA | NE_FgBindOpt_Olap | PmaxRestricted Loading% | PmaxRestricted FlowMW divided by Flowgate Rating expressed as percentage
TARA | NE_FgBindOpt_Olap | Pmax Restricted Gen MW | Maximum output of Study Unit such that no overloads are caused. Use SCD to maximize output of Study Unit.
TARA | NE_FgBindOpt_Olap | Monitored Ref Dispatch? | Was this flowgate monitored for the Reference Dispatch stress? If so, then it can restrict the applied stress. If not, then its loading can go over 100%. See option "Restrict Ref Disp Mon Fgates". If enabled, then only flowgates that meet Study Unit impact thresholds are monitored for reference dispatch.
TARA | NE_FgBindOpt_Olap | Binding Ref Dispatch? | Was this flowgate binding for the Reference Dispatch stress? If so, then it is restricting the applied stress. User question - does it make sense that this flowgate should restrict the stress?
TARA | NE_FgBindOpt_Olap | Passed Screen Study Unit? | See "Screening Options" on Viewer menu. If value is 1, then the Study Unit satisfied the screening options conditions for this flowgate. It will be monitored for overloads.
TARA | NE_FgBindOpt_Olap | Failed Flowgate? | Can only be 1 if the flowgate passed the "Screening Options" conditions AND the flowgate went over 100% loading when the Study Unit was added (Study Dispatch)
TARA | NE_FgBindOpt_Olap | RedispatchMW | For the initial Reference Dispatch (stress) condition, how many MW were moved to cause the stress (this much went up and the same amount went down to maintain energy balance)
TARA | NE_FgBindOpt_Olap | PGenBase Big Helper MW | In the starting initial base case, what was Pgen of the unit selected as Biggest Helper. For each Reference Dispatch stress, the biggest help is selected as the initial "sink" when turning up units.
TARA | NE_FgBindOpt_Olap | PGenRef Big Helper MW | In the Reference Dispatch stress condition, what was Pgen of the unit selected as Biggest Helper. For each Reference Dispatch stress, the biggest help is selected as the initial "sink" when turning up units.
TARA | NE_FgBindOpt_Olap | Dfax Big Helper | For the stressed flowgate (see Dispatch Ind column), this value is the Dfax of the biggest helper that was selected when applying the Reference Dispatch stress. Dfax is with respect to user-selected Dfax reference
TARA | NE_FgBindOpt_Olap | PGen Avail Ref OutsideRegion MW | After the biggest helper MW are used in creating the Reference Dispatch, additional sink MW are available from aggregate set of units "outside region of influence". How many MW were available in the "outside region". If this is zero, then the stress will stop. See Viewer "Analysis Options" for outside region cutoffs
TARA | NE_FgBindOpt_Olap | Pdelta Ref OutsideRegion MW | When creating the Reference Dispatch, the amount scaled down from aggregate set of units "outside region of influence". If this is zero, then the biggest helper MW were not reduced to zero before a monitored flowgate hit the limit. See Viewer "Analysis Options" for outside region cutoffs
TARA | NE_FgBindOpt_Olap | PGen Avail Study OutsideRegion MW | After the biggest helper MW are used in creating the Study Dispatch, additional sink MW are available from aggregate set of units "outside region of influence". How many MW were available in the "outside region". If this is zero, then the remaining MW needed will sink to the case swing bus. See Viewer "Analysis Options" for outside region cutoffs and for the subsysem to be used for finding outside region units for the Study Dispatch.
TARA | NE_FgBindOpt_Olap | Pdelta Study OutsideRegion MW | When creating the Study Dispatch, the amount scaled down from aggregate set of units "outside region of influence". If this is zero, then the biggest helper MW were not reduced to zero before a monitored flowgate hit the limit. See Viewer "Analysis Options" for outside region cutoffs (a different sysem can be selected for Ref than for Study)
TARA | NE_FgBindOpt_Olap | BigHelper Bus# BusName Volt Pgen Pmax | Bus number and name for biggest helper
TARA | NE_FgBindOpt_Olap | Dispatch FgID | Flowgate ID for the stressed flowgate corresponding to Disp Ind column. This is not the same as the Flowgate Index. Flowgate ID is found in the flowgate definition in the fgt file.
TARA | NE_FgOverOpt_Olap | ProjIndex | Index assigned to study project by TARA (based on order read from file)
TARA | NE_FgOverOpt_Olap | ID | User-assigned ID of study project (read from file column ResourceID)
TARA | NE_FgOverOpt_Olap | ProjName | User-assigned name of study project (read from file column ProjectName)
TARA | NE_FgOverOpt_Olap | ProjMW | Study project maximum MW to be evaluated (read from file column MW)
TARA | NE_FgOverOpt_Olap | Bus# | Bus Number of study unit
TARA | NE_FgOverOpt_Olap | BusName | Bus Name of study unit
TARA | NE_FgOverOpt_Olap | Volt | Bus nominal KV of study unit
TARA | NE_FgOverOpt_Olap | Area | Bus Area of study unit
TARA | NE_FgOverOpt_Olap | Zone | Bus Zone of study unit
TARA | NE_FgOverOpt_Olap | Dispatch Ind | For the Monitored flowgate, this Stress Dispatch was the highest overload among all dispatches tested (Index of stressed flowgate (index is assigned to flowgates based on order read by TARA))
TARA | NE_FgOverOpt_Olap | Mon Ind | Monitored flowgate that was overloaded for Study Dispatches - index of flowgate reported for this row. Flows and Loadings for this specific Dispatch stress condition
TARA | NE_FgOverOpt_Olap | Monit Param | Monitored flowgate that was overloaded for Study Dispatches - monitored branch corresponding to reported flowgate flows for this row.
TARA | NE_FgOverOpt_Olap | Contingency | Monitored flowgate that was overloaded for Study Dispatches - Flowgate contingency corresponding to reported flowgate flows for this row.
TARA | NE_FgOverOpt_Olap | Rating | Rating of flowgate reported on this row
TARA | NE_FgOverOpt_Olap | FlowMW | Original case flowgate flow (post-contingency if flowgate has contingency). This is before stress occurs.
TARA | NE_FgOverOpt_Olap | NumOverloads | Number of stress conditions (dispatches) for which this Mon Flowgate was overloaded when turning up Study Unit to Pmax
TARA | NE_FgOverOpt_Olap | StudyDfax | Dfax of Study Unit on the Flowgate identified by Mon Ind, Monit Param, Contingency columns
TARA | NE_FgOverOpt_Olap | RefFlowMW | Reference Dispatch flow on monitored flowgate (for this row Mon Ind) after performing stress on the base case
TARA | NE_FgOverOpt_Olap | StudyFlowMW | Study Dispatch flow on monitored flowgate (for this row Mon Ind) after adding Study unit at Project-Rated MW to the Reference Dispatch case. SCD does not redispatch for overloads.
TARA | NE_FgOverOpt_Olap | PARFlowMW | PARs are optimized for Study Dispatch case to see if PAR adjustments can resolve overloads. Value in this cell is flow on monitored flowgate (for this row Mon Ind) after optimizing PARs
TARA | NE_FgOverOpt_Olap | PmaxRestricted FlowMW | Use SCD to maximize output of Study Unit (see column Pmax Restricted Gen MW). At maximum Study Unit output, this is flow on monitored flowgate (for this row Mon Ind)
TARA | NE_FgOverOpt_Olap | RefLoading% | RefFlowMW divided by Flowgate Rating expressed as percentage
TARA | NE_FgOverOpt_Olap | StudyLoading% | StudyFlowMW divided by Flowgate Rating expressed as percentage
TARA | NE_FgOverOpt_Olap | PARLoading% | PARFlowMW divided by Flowgate Rating expressed as percentage
TARA | NE_FgOverOpt_Olap | PmaxRestricted Loading% | PmaxRestricted FlowMW divided by Flowgate Rating expressed as percentage
TARA | NE_FgOverOpt_Olap | Pmax Restricted Gen MW | Maximum output of Study Unit such that no overloads are caused. Use SCD to maximize output of Study Unit.
TARA | NE_FgOverOpt_Olap | Monitored Ref Dispatch? | Was this flowgate monitored for the Reference Dispatch stress? If so, then it can restrict the applied stress. If not, then its loading can go over 100%. See option "Restrict Ref Disp Mon Fgates". If enabled, then only flowgates that meet Study Unit impact thresholds are monitored for reference dispatch.
TARA | NE_FgOverOpt_Olap | Binding Ref Dispatch? | Was this flowgate binding for the Reference Dispatch stress? If so, then it is restricting the applied stress. User question - does it make sense that this flowgate should restrict the stress?
TARA | NE_FgOverOpt_Olap | Passed Screen Study Unit? | See "Screening Options" on Viewer menu. If value is 1, then the Study Unit satisfied the screening options conditions for this flowgate. It will be monitored for overloads.
TARA | NE_FgOverOpt_Olap | Failed Flowgate? | Can only be 1 if the flowgate passed the "Screening Options" conditions AND the flowgate went over 100% loading when the Study Unit was added (Study Dispatch)
TARA | NE_FgOverOpt_Olap | RedispatchMW | For the initial Reference Dispatch (stress) condition, how many MW were moved to cause the stress (this much went up and the same amount went down to maintain energy balance)
TARA | NE_FgOverOpt_Olap | PGenBase Big Helper MW | In the starting initial base case, what was Pgen of the unit selected as Biggest Helper. For each Reference Dispatch stress, the biggest help is selected as the initial "sink" when turning up units.
TARA | NE_FgOverOpt_Olap | PGenRef Big Helper MW | In the Reference Dispatch stress condition, what was Pgen of the unit selected as Biggest Helper. For each Reference Dispatch stress, the biggest help is selected as the initial "sink" when turning up units.
TARA | NE_FgOverOpt_Olap | Dfax Big Helper | For the stressed flowgate (see Dispatch Ind column), this value is the Dfax of the biggest helper that was selected when applying the Reference Dispatch stress. Dfax is with respect to user-selected Dfax reference
TARA | NE_FgOverOpt_Olap | PGen Avail Ref OutsideRegion MW | After the biggest helper MW are used in creating the Reference Dispatch, additional sink MW are available from aggregate set of units "outside region of influence". How many MW were available in the "outside region". If this is zero, then the stress will stop. See Viewer "Analysis Options" for outside region cutoffs
TARA | NE_FgOverOpt_Olap | Pdelta Ref OutsideRegion MW | When creating the Reference Dispatch, the amount scaled down from aggregate set of units "outside region of influence". If this is zero, then the biggest helper MW were not reduced to zero before a monitored flowgate hit the limit. See Viewer "Analysis Options" for outside region cutoffs
TARA | NE_FgOverOpt_Olap | PGen Avail Study OutsideRegion MW | After the biggest helper MW are used in creating the Study Dispatch, additional sink MW are available from aggregate set of units "outside region of influence". How many MW were available in the "outside region". If this is zero, then the remaining MW needed will sink to the case swing bus. See Viewer "Analysis Options" for outside region cutoffs and for the subsysem to be used for finding outside region units for the Study Dispatch.
TARA | NE_FgOverOpt_Olap | Pdelta Study OutsideRegion MW | When creating the Study Dispatch, the amount scaled down from aggregate set of units "outside region of influence". If this is zero, then the biggest helper MW were not reduced to zero before a monitored flowgate hit the limit. See Viewer "Analysis Options" for outside region cutoffs (a different sysem can be selected for Ref than for Study)
TARA | NE_FgOverOpt_Olap | BigHelper Bus# BusName Volt Pgen Pmax | Bus number and name for biggest helper
TARA | NE_FgOverOpt_Olap | Dispatch FgID | Flowgate ID for the stressed flowgate corresponding to Disp Ind column. This is not the same as the Flowgate Index. Flowgate ID is found in the flowgate definition in the fgt file.
TARA | SCD_ContFgates | Ind | Index of Flowgate (index is assigned to flowgates based on order read by TARA)
TARA | SCD_ContFgates | Flowgate ID | Flowgate ID is found in the flowgate definition in the fgt file.
TARA | SCD_ContFgates | Flowgate Name | Flowgate name from Flowgate Definition. Typially, it is either the monitored branch of the flowgate or the name of an Interface
TARA | SCD_ContFgates | Contingency | Flowgate contingency as found in the flowgate definition in the flowgate file
TARA | SCD_ContFgates | FgtMinRating | Flowgate positive flow direction is defined by From Bus/To Bus order in the flowgate monitor definition. FgtMinRating is the lower limit of allowable flow in the positive oriented direction. Can be positive if using BIRATINGS command in the flowgate definition to specify both lower and upper limits. If BIRATINGS are not specified, it is the negative of the rating of the monitored branch in the flowgate.
TARA | SCD_ContFgates | FgtMaxRating | Flowgate positive flow direction is defined by From Bus/To Bus order in the flowgate monitor definition. FgtMaxRating is the upper limit of allowable flow in the positive oriented direction. Can be negative if using BIRATINGS command in the flowgate definition to specify both lower and upper limits and you desire flow opposite the positive orientation. If BIRATINGS are not specified, it is the the rating of the monitored branch in the flowgate.
TARA | SCD_ContFgates | FgateFlow | Initial, before-SCD MW flow on the Flowgate (positive direction is user-defined from/to in the flowgate definition)
TARA | SCD_ContFgates | FgFlowRes | Final, after-SCD MW flow on the Flowgate (positive direction is user-defined from/to in the flowgate definition)
TARA | SCD_ContFgates | FlowDelt | Difference between FgFlowRes minus FgateFlow
TARA | SCD_ContFgates | LoadInt | FgateFlow divided by FgtMaxRating expressed as percentage
TARA | SCD_ContFgates | LoadRes | FgFlowRes divided by FgtMaxRating expressed as percentage
TARA | SCD_ContFgates | Shadow Price | SCD-determined shadow price for this flowgate. If it equals the overload penalty, then the flowgate was unfixable. If non-zero, then the flowgate was binding (forcing redispatch). Value indicates objective function improvement if flowgate rating is relaxed 1 MW
TARA | SCD_ContFgates | maxShadowPrice | Penalty per MW overload according to user-defined settings (SCD Options> Cont Branch Penalty) or user-defined in the flowgate file (add penalty keyword to definition)
TARA | SCD_ContFgates | Soft Exclude | If=1, then exclude file indicates this flowgate is soft excluded. Overloads will not be enforced during SCD execution
TARA | SCD_Binding | Monitored Facility | Name of monitored facility that was binding. If it is ### Energy, then it is energy balance constraint. See column Cons Type for type of element, e.g. Energy, Mon Branch, Flowgate)
TARA | SCD_Binding | CntInd | If it is a monitored branch post-contingency constraint, the contingency index for the contingency. If flowgate constraint, it is the flowgate index.
TARA | SCD_Binding | Cont Name | Contingency Name for binding constraint. If name is Base Case, then it is a pre-contingency constraint.
TARA | SCD_Binding | ConsType | Type of binding constraint, e.g. Branch (line or transformer), Flowgate/Interface, or Energy (energy balance is enforced so that gen up=gen down)
TARA | SCD_Binding | Rating | Rating enforced for binding constraint. For a flowgate definition that has BIRATINGS, this will show the rating that was enforced. SCD Options> Rating Multiplier is applied before printing rating. If 98% was specified, then actual branch rating times 98% is shown as Rating here. However, SCD_BranchLoadings will show actual branch original rating from case.
TARA | SCD_Binding | Flow | Post-SCD MW or MVA or Amp flow
TARA | SCD_Binding | %Loading | Flow divided by Rating
TARA | SCD_Binding | ShadowPrice | SCD-determined shadow price for this binding constraint. If it equals the overload penalty, then the constraint was unfixable. Value indicates objective function improvement if constraint rating is relaxed 1 MW
TARA | SCD_Adjusted | BidderName | If bidders and costs are defined in the sub file, this is the user-defined name of the bidder from the cost file. For SCRD using subsystems, this is the Bus Number and Name and Machine ID if generator or Load ID if load
TARA | SCD_Adjusted | unitType | If bidders and costs are defined in the sub file, this is the user-defined Unit Type from the cost file. For SCRD using subsystems, this is NA
TARA | SCD_Adjusted | Fuel/Schd | If bidders and costs are defined in the sub file, this is the user-defined Fuel/Schd from the cost file. For SCRD using subsystems, this is the name of the Subsystem
TARA | SCD_Adjusted | OrgName | If bidders and costs are defined in the sub file, this is the user-defined OrgName from the cost file. For SCRD using subsystems, this is the name of the Area it which the machine or load is located
TARA | SCD_Adjusted | BTyp | Type of SCD control. It could be a generator, load shedding, etc.
TARA | SCD_Adjusted | MinMW | Lower dispatch range of SCD control
TARA | SCD_Adjusted | MaxMW | Upper dispatch range of SCD control
TARA | SCD_Adjusted | Init_MW | Initial MW dispatch of SCD control
TARA | SCD_Adjusted | Res_MW | Final, SCD-determined MW dispatch of SCD control
TARA | SCD_Adjusted | MWChang | Res_MW minus Init_MW
TARA | SCD_Adjusted | LMP | Value of additional 1 MW injected by the machine/load (or aggregate set of machines/loads)
TARA | SCD_Adjusted | Status | Was the bidder already on in initial case, turned on by SCD, turned off by SCD
TARA | SCD_Adjusted | DsSt | Was the maximum
TARA | SCD_Adjusted | Bus# | Bus Number of bidder. None provided for subsystem aggregate.
TARA | SCD_Adjusted | BusName | Bus Name of bidder
TARA | SCD_Adjusted | Volt | Nominal KV of bidder Bus
TARA | SCD_Adjusted | Area | Area Number of bidder Bus
TARA | SCD_Adjusted | AreaName | Area Name of bidder Bus
TARA | SCD_Adjusted | Zon | Zone Number of bidder Bus
TARA | SCD_Adjusted | ZoneName | Zone Name of bidder Bus
TARA | SCD_Adjusted | ID | Machine or Load ID of bidder equipment
TARA | SCD_Adjusted | Aggr? | Aggregate or Physical. Aggregate bidders are comprised of multiple machines and loads grouped together to act as a single bidder.
TARA | SCD_Adjusted | LimitViol? | Did bidder hit Max or Min during SCD redispatch?
TARA | SCD_Dispatch | BidderName | If bidders and costs are defined in the sub file, this is the user-defined name of the bidder from the cost file. For SCRD using subsystems, this is the Bus Number and Name and Machine ID if generator or Load ID if load
TARA | SCD_Dispatch | unitType | If bidders and costs are defined in the sub file, this is the user-defined Unit Type from the cost file. For SCRD using subsystems, this is NA
TARA | SCD_Dispatch | Fuel/Schd | If bidders and costs are defined in the sub file, this is the user-defined Fuel/Schd from the cost file. For SCRD using subsystems, this is the name of the Subsystem
TARA | SCD_Dispatch | OrgName | If bidders and costs are defined in the sub file, this is the user-defined OrgName from the cost file. For SCRD using subsystems, this is the name of the Area it which the machine or load is located
TARA | SCD_Dispatch | BTyp | Type of SCD control. It could be a generator, load shedding, etc.
TARA | SCD_Dispatch | MinMW | Lower dispatch range of SCD control
TARA | SCD_Dispatch | MaxMW | Upper dispatch range of SCD control
TARA | SCD_Dispatch | Init_MW | Initial MW dispatch of SCD control
TARA | SCD_Dispatch | Res_MW | Final, SCD-determined MW dispatch of SCD control
TARA | SCD_Dispatch | MWChang | Res_MW minus Init_MW
TARA | SCD_Dispatch | LMP | Value of additional 1 MW injected by the machine/load (or aggregate set of machines/loads)
TARA | SCD_Dispatch | Status | Was the bidder already on in initial case, turned on by SCD, turned off by SCD
TARA | SCD_Dispatch | DsSt | Was the maximum
TARA | SCD_Dispatch | Bus# | Bus Number of bidder. None provided for subsystem aggregate.
TARA | SCD_Dispatch | BusName | Bus Name of bidder
TARA | SCD_Dispatch | Volt | Nominal KV of bidder Bus
TARA | SCD_Dispatch | Area | Area Number of bidder Bus
TARA | SCD_Dispatch | AreaName | Area Name of bidder Bus
TARA | SCD_Dispatch | Zon | Zone Number of bidder Bus
TARA | SCD_Dispatch | ZoneName | Zone Name of bidder Bus
TARA | SCD_Dispatch | ID | Machine or Load ID of bidder equipment
TARA | SCD_Dispatch | Aggr? | Aggregate or Physical. Aggregate bidders are comprised of multiple machines and loads grouped together to act as a single bidder.
TARA | SCD_Dispatch | LimitViol? | Did bidder hit Max or Min during SCD redispatch?
TARA | SCD_PARs | ParName | User-defined name of PAR as defined in the sub file
TARA | SCD_PARs | Bus# | Bus Number of From end of PAR
TARA | SCD_PARs | BusName | Bus Name of From end of PAR
TARA | SCD_PARs | Volt | Bus Nominal KV of From end of PAR
TARA | SCD_PARs | Bus# | Bus Number of To end of PAR
TARA | SCD_PARs | BusName | Bus Name of To end of PAR
TARA | SCD_PARs | Volt | Bus Nominal KV of To end of PAR
TARA | SCD_PARs | CKT | Ckt ID of PAR branch
TARA | SCD_PARs | InitMW | MW flow on PAR before SCD
TARA | SCD_PARs | ResMW | MW flow on PAR after SCD
TARA | SCD_PARs | DeltMW | ResMW minus InitMW
TARA | SCD_PARs | MinMW | Negative of Applicable Rating of PAR obained from LF Case and user-defined set from Initial Loading Options
TARA | SCD_PARs | MaxMW | Applicable Rating of PAR obained from LF Case and user-defined set from Initial Loading Options
TARA | SCD_PARs | IntAnDeg | PAR Angle in Degrees before SCD
TARA | SCD_PARs | ResAnDeg | PAR Angle in Degrees after SCD
TARA | SCD_PARs | DltAnDeg | ResAnDeg minus IntAnDeg
TARA | SCD_PARs | MinAnDeg | PAR minimum allowable angle as obtained from LF case PAR data
TARA | SCD_PARs | MaxAnDeg | PAR maximum allowable angle as obtained from LF case PAR data
TARA | NE_FgLoadOpt_MIS | ProjIndex | Index assigned to study project by TARA (based on order read from file)
TARA | NE_FgLoadOpt_MIS | ID | User-assigned ID of study project (read from file column ResourceID)
TARA | NE_FgLoadOpt_MIS | ProjName | User-assigned name of study project (read from file column ProjectName)
TARA | NE_FgLoadOpt_MIS | ProjMW | Study project maximum MW to be evaluated (read from file column MW)
TARA | NE_FgLoadOpt_MIS | Bus# | Bus Number of study unit
TARA | NE_FgLoadOpt_MIS | BusName | Bus Name of study unit
TARA | NE_FgLoadOpt_MIS | Volt | Bus nominal KV of study unit
TARA | NE_FgLoadOpt_MIS | Area | Bus Area of study unit
TARA | NE_FgLoadOpt_MIS | Zone | Bus Zone of study unit
TARA | NE_FgLoadOpt_MIS | Dispatch Ind | Index of stressed flowgate (index is assigned to flowgates based on order read by TARA)
TARA | NE_FgLoadOpt_MIS | Mon Ind | Index of flowgate reported for this row. Flows and Loadings for this specific Dispatch stress condition
TARA | NE_FgLoadOpt_MIS | Monit Param | Flowgate monitored branch corresponding to reported flowgate flows for this row.
TARA | NE_FgLoadOpt_MIS | Contingency | Flowgate contingency corresponding to reported flowgate flows for this row.
TARA | NE_FgLoadOpt_MIS | Rating | Rating of flowgate reported on this row
TARA | NE_FgLoadOpt_MIS | FlowMW | Original case flowgate flow (post-contingency if flowgate has contingency). This is before stress occurs.
TARA | NE_FgLoadOpt_MIS | RefFlowMW | Reference Dispatch flow on monitored flowgate (for this row Mon Ind) after performing stress on the base case
TARA | NE_FgLoadOpt_MIS | StudyFlowMW | Study Dispatch flow on monitored flowgate (for this row Mon Ind) after adding Study unit at Project-Rated MW to the Reference Dispatch case. SCD does not redispatch for overloads.
TARA | NE_FgLoadOpt_MIS | PARFlowMW | PARs are optimized for Study Dispatch case to see if PAR adjustments can resolve overloads. Value in this cell is flow on monitored flowgate (for this row Mon Ind) after optimizing PARs
TARA | NE_FgLoadOpt_MIS | RefLoading% | RefFlowMW divided by Flowgate Rating expressed as percentage
TARA | NE_FgLoadOpt_MIS | StudyLoading% | StudyFlowMW divided by Flowgate Rating expressed as percentage
TARA | NE_FgLoadOpt_MIS | PARLoading% | PARFlowMW divided by Flowgate Rating expressed as percentage
TARA | NE_FgLoadOpt_MIS | Monitored Ref Dispatch? | Was this flowgate monitored for the Reference Dispatch stress? If so, then it can restrict the applied stress. If not, then its loading can go over 100%. See option "Restrict Ref Disp Mon Fgates". If enabled, then only flowgates that meet Study Unit impact thresholds are monitored for reference dispatch.
TARA | NE_FgLoadOpt_MIS | Binding Ref Dispatch? | Was this flowgate binding for the Reference Dispatch stress? If so, then it is restricting the applied stress. User question - does it make sense that this flowgate should restrict the stress?
TARA | NE_FgLoadOpt_MIS | Passed Screen Study Unit? | See "Screening Options" on Viewer menu. If value is 1, then the Study Unit satisfied the screening options conditions for this flowgate. It will be monitored for overloads.
TARA | NE_FgLoadOpt_MIS | Failed Flowgate? | Can only be 1 if the flowgate passed the "Screening Options" conditions AND the flowgate went over 100% loading when the Study Unit was added (Study Dispatch)
TARA | NE_FgLoadOpt_MIS | RedispatchMW | For the initial Reference Dispatch (stress) condition, how many MW were moved to cause the stress (this much went up and the same amount went down to maintain energy balance)
TARA | NE_FgLoadOpt_MIS | PGenBase Big Helper MW | In the starting initial base case, what was Pgen of the unit selected as Biggest Helper. For each Reference Dispatch stress, the biggest help is selected as the initial "sink" when turning up units.
TARA | NE_FgLoadOpt_MIS | PGenRef Big Helper MW | In the Reference Dispatch stress condition, what was Pgen of the unit selected as Biggest Helper. For each Reference Dispatch stress, the biggest help is selected as the initial "sink" when turning up units.
TARA | NE_FgLoadOpt_MIS | Dfax Big Helper | For the stressed flowgate (see Dispatch Ind column), this value is the Dfax of the biggest helper that was selected when applying the Reference Dispatch stress. Dfax is with respect to user-selected Dfax reference
TARA | NE_FgLoadOpt_MIS | BigHelper Bus# BusName Volt Pgen Pmax | Bus number and name for biggest helper
TARA | NE_FgLoadOpt_MIS | Dispatch FgID | Flowgate ID for the stressed flowgate. This is not the same as the Flowgate Index. Flowgate ID is found in the flowgate definition in the fgt file.
TARA | NE_FgBindOpt_MIS | ProjIndex | Index assigned to study project by TARA (based on order read from file)
TARA | NE_FgBindOpt_MIS | ID | User-assigned ID of study project (read from file column ResourceID)
TARA | NE_FgBindOpt_MIS | ProjName | User-assigned name of study project (read from file column ProjectName)
TARA | NE_FgBindOpt_MIS | ProjMW | Study project maximum MW to be evaluated (read from file column MW)
TARA | NE_FgBindOpt_MIS | Bus# | Bus Number of study unit
TARA | NE_FgBindOpt_MIS | BusName | Bus Name of study unit
TARA | NE_FgBindOpt_MIS | Volt | Bus nominal KV of study unit
TARA | NE_FgBindOpt_MIS | Area | Bus Area of study unit
TARA | NE_FgBindOpt_MIS | Zone | Bus Zone of study unit
TARA | NE_FgBindOpt_MIS | Dispatch Ind | For the Monitored flowgate, this is an example of a Stress Dispatch for which the Monitored Flowgate was binding in the Reference Dispatch (Index of stressed flowgate (index is assigned to flowgates based on order read by TARA))
TARA | NE_FgBindOpt_MIS | Mon Ind | Monitored flowgate that was binding for Reference stresses - index of flowgate reported for this row. Flows and Loadings for this specific Dispatch stress condition
TARA | NE_FgBindOpt_MIS | Monit Param | Monitored flowgate that was binding for Reference stresses - monitored branch corresponding to reported flowgate flows for this row.
TARA | NE_FgBindOpt_MIS | Contingency | Monitored flowgate that was binding for Reference stresses - Flowgate contingency corresponding to reported flowgate flows for this row.
TARA | NE_FgBindOpt_MIS | Rating | Rating of flowgate reported on this row
TARA | NE_FgBindOpt_MIS | FlowMW | Original case flowgate flow (post-contingency if flowgate has contingency). This is before stress occurs.
TARA | NE_FgBindOpt_MIS | NumTimesBinding | Key component of this report. How many times was this Flowgate (see Mon Ind, Param, Contingency) binding when creating the reference stress. Should this flowgate be restricting stress conditions?
TARA | NE_FgBindOpt_MIS | StudyDfax | Dfax of Study Unit on the Flowgate identified by Mon Ind, Monit Param, Contingency columns
TARA | NE_FgBindOpt_MIS | RefFlowMW | Reference Dispatch flow on monitored flowgate (for this row Mon Ind) after performing stress on the base case
TARA | NE_FgBindOpt_MIS | StudyFlowMW | Study Dispatch flow on monitored flowgate (for this row Mon Ind) after adding Study unit at Project-Rated MW to the Reference Dispatch case. SCD does not redispatch for overloads.
TARA | NE_FgBindOpt_MIS | PARFlowMW | PARs are optimized for Study Dispatch case to see if PAR adjustments can resolve overloads. Value in this cell is flow on monitored flowgate (for this row Mon Ind) after optimizing PARs
TARA | NE_FgBindOpt_MIS | RefLoading% | RefFlowMW divided by Flowgate Rating expressed as percentage
TARA | NE_FgBindOpt_MIS | StudyLoading% | StudyFlowMW divided by Flowgate Rating expressed as percentage
TARA | NE_FgBindOpt_MIS | PARLoading% | PARFlowMW divided by Flowgate Rating expressed as percentage
TARA | NE_FgBindOpt_MIS | Monitored Ref Dispatch? | Was this flowgate monitored for the Reference Dispatch stress? If so, then it can restrict the applied stress. If not, then its loading can go over 100%. See option "Restrict Ref Disp Mon Fgates". If enabled, then only flowgates that meet Study Unit impact thresholds are monitored for reference dispatch.
TARA | NE_FgBindOpt_MIS | Binding Ref Dispatch? | Was this flowgate binding for the Reference Dispatch stress? If so, then it is restricting the applied stress. User question - does it make sense that this flowgate should restrict the stress?
TARA | NE_FgBindOpt_MIS | Passed Screen Study Unit? | See "Screening Options" on Viewer menu. If value is 1, then the Study Unit satisfied the screening options conditions for this flowgate. It will be monitored for overloads.
TARA | NE_FgBindOpt_MIS | Failed Flowgate? | Can only be 1 if the flowgate passed the "Screening Options" conditions AND the flowgate went over 100% loading when the Study Unit was added (Study Dispatch)
TARA | NE_FgBindOpt_MIS | RedispatchMW | For the initial Reference Dispatch (stress) condition, how many MW were moved to cause the stress (this much went up and the same amount went down to maintain energy balance)
TARA | NE_FgBindOpt_MIS | PGenBase Big Helper MW | In the starting initial base case, what was Pgen of the unit selected as Biggest Helper. For each Reference Dispatch stress, the biggest help is selected as the initial "sink" when turning up units.
TARA | NE_FgBindOpt_MIS | PGenRef Big Helper MW | In the Reference Dispatch stress condition, what was Pgen of the unit selected as Biggest Helper. For each Reference Dispatch stress, the biggest help is selected as the initial "sink" when turning up units.
TARA | NE_FgBindOpt_MIS | Dfax Big Helper | For the stressed flowgate (see Dispatch Ind column), this value is the Dfax of the biggest helper that was selected when applying the Reference Dispatch stress. Dfax is with respect to user-selected Dfax reference
TARA | NE_FgBindOpt_MIS | BigHelper Bus# BusName Volt Pgen Pmax | Bus number and name for biggest helper
TARA | NE_FgBindOpt_MIS | Dispatch FgID | Flowgate ID for the stressed flowgate corresponding to Disp Ind column. This is not the same as the Flowgate Index. Flowgate ID is found in the flowgate definition in the fgt file.
TARA | NE_FgOverOpt_MIS | ProjIndex | Index assigned to study project by TARA (based on order read from file)
TARA | NE_FgOverOpt_MIS | ID | User-assigned ID of study project (read from file column ResourceID)
TARA | NE_FgOverOpt_MIS | ProjName | User-assigned name of study project (read from file column ProjectName)
TARA | NE_FgOverOpt_MIS | ProjMW | Study project maximum MW to be evaluated (read from file column MW)
TARA | NE_FgOverOpt_MIS | Bus# | Bus Number of study unit
TARA | NE_FgOverOpt_MIS | BusName | Bus Name of study unit
TARA | NE_FgOverOpt_MIS | Volt | Bus nominal KV of study unit
TARA | NE_FgOverOpt_MIS | Area | Bus Area of study unit
TARA | NE_FgOverOpt_MIS | Zone | Bus Zone of study unit
TARA | NE_FgOverOpt_MIS | Dispatch Ind | For the Monitored flowgate, this Stress Dispatch was the highest overload among all dispatches tested (Index of stressed flowgate (index is assigned to flowgates based on order read by TARA))
TARA | NE_FgOverOpt_MIS | Mon Ind | Monitored flowgate that was binding for Reference stresses - index of flowgate reported for this row. Flows and Loadings for this specific Dispatch stress condition
TARA | NE_FgOverOpt_MIS | Monit Param | Monitored flowgate that was binding for Reference stresses - monitored branch corresponding to reported flowgate flows for this row.
TARA | NE_FgOverOpt_MIS | Contingency | Monitored flowgate that was binding for Reference stresses - Flowgate contingency corresponding to reported flowgate flows for this row.
TARA | NE_FgOverOpt_MIS | Rating | Rating of flowgate reported on this row
TARA | NE_FgOverOpt_MIS | FlowMW | Original case flowgate flow (post-contingency if flowgate has contingency). This is before stress occurs.
TARA | NE_FgOverOpt_MIS | NumOverloads | Number of stress conditions (dispatches) for which this Mon Flowgate was overloaded when turning up Study Unit to Pmax
TARA | NE_FgOverOpt_MIS | StudyDfax | Dfax of Study Unit on the Flowgate identified by Mon Ind, Monit Param, Contingency columns
TARA | NE_FgOverOpt_MIS | RefFlowMW | Reference Dispatch flow on monitored flowgate (for this row Mon Ind) after performing stress on the base case
TARA | NE_FgOverOpt_MIS | StudyFlowMW | Study Dispatch flow on monitored flowgate (for this row Mon Ind) after adding Study unit at Project-Rated MW to the Reference Dispatch case. SCD does not redispatch for overloads.
TARA | NE_FgOverOpt_MIS | PARFlowMW | PARs are optimized for Study Dispatch case to see if PAR adjustments can resolve overloads. Value in this cell is flow on monitored flowgate (for this row Mon Ind) after optimizing PARs
TARA | NE_FgOverOpt_MIS | RefLoading% | RefFlowMW divided by Flowgate Rating expressed as percentage
TARA | NE_FgOverOpt_MIS | StudyLoading% | StudyFlowMW divided by Flowgate Rating expressed as percentage
TARA | NE_FgOverOpt_MIS | PARLoading% | PARFlowMW divided by Flowgate Rating expressed as percentage
TARA | NE_FgOverOpt_MIS | Monitored Ref Dispatch? | Was this flowgate monitored for the Reference Dispatch stress? If so, then it can restrict the applied stress. If not, then its loading can go over 100%. See option "Restrict Ref Disp Mon Fgates". If enabled, then only flowgates that meet Study Unit impact thresholds are monitored for reference dispatch.
TARA | NE_FgOverOpt_MIS | Binding Ref Dispatch? | Was this flowgate binding for the Reference Dispatch stress? If so, then it is restricting the applied stress. User question - does it make sense that this flowgate should restrict the stress?
TARA | NE_FgOverOpt_MIS | Passed Screen Study Unit? | See "Screening Options" on Viewer menu. If value is 1, then the Study Unit satisfied the screening options conditions for this flowgate. It will be monitored for overloads.
TARA | NE_FgOverOpt_MIS | Failed Flowgate? | Can only be 1 if the flowgate passed the "Screening Options" conditions AND the flowgate went over 100% loading when the Study Unit was added (Study Dispatch)
TARA | NE_FgOverOpt_MIS | RedispatchMW | For the initial Reference Dispatch (stress) condition, how many MW were moved to cause the stress (this much went up and the same amount went down to maintain energy balance)
TARA | NE_FgOverOpt_MIS | PGenBase Big Helper MW | In the starting initial base case, what was Pgen of the unit selected as Biggest Helper. For each Reference Dispatch stress, the biggest help is selected as the initial "sink" when turning up units.
TARA | NE_FgOverOpt_MIS | PGenRef Big Helper MW | In the Reference Dispatch stress condition, what was Pgen of the unit selected as Biggest Helper. For each Reference Dispatch stress, the biggest help is selected as the initial "sink" when turning up units.
TARA | NE_FgOverOpt_MIS | Dfax Big Helper | For the stressed flowgate (see Dispatch Ind column), this value is the Dfax of the biggest helper that was selected when applying the Reference Dispatch stress. Dfax is with respect to user-selected Dfax reference
TARA | NE_FgOverOpt_MIS | BigHelper Bus# BusName Volt Pgen Pmax | Bus number and name for biggest helper
TARA | NE_FgOverOpt_MIS | Dispatch FgID | Flowgate ID for the stressed flowgate corresponding to Disp Ind column. This is not the same as the Flowgate Index. Flowgate ID is found in the flowgate definition in the fgt file.
TARA | NE_OverloadSum | BidIndex | FCM Bid Index (assigned by TARA according to order in FCM bid file)
TARA | NE_OverloadSum | BidID | FCM Bid ID as read from bid file
TARA | NE_OverloadSum | Type | Demand or Offer
TARA | NE_OverloadSum | PnodeID | Pnode ID read from bid file
TARA | NE_OverloadSum | PnodeNam | Pnode name read from bid file
TARA | NE_OverloadSum | MW | Pmax reduction to test (will be subtracted from base case Pmax)
TARA | NE_OverloadSum | StressFgIndex | Unique Index number of stressed flowgate
TARA | NE_OverloadSum | StressFgID | Flowgate ID number of stressed flowgate. Same value as found in fgt file and may not be unique.
TARA | NE_OverloadSum | Stress Monit Param | Flowgate name as specified in first line of flowgate definition inside flowgate file. This is the monitored branch name if flowgate file was created from TARA screen.
TARA | NE_OverloadSum | Stress Contingency | Contingency name as specified in flowgate definition.
TARA | NE_OverloadSum | StressFgtRating | Flowgate rating.
TARA | NE_OverloadSum | Base%Loading | Flowgate % loading in base case
TARA | NE_OverloadSum | Ref%Loading | Flowgate % loading resulting from Reference Dispatch.
TARA | NE_OverloadSum | Study%Loading | Flowgate % loading resulting from Study Dispatch (create Reference Dispatch then add Study Generator)
TARA | NE_OverloadSum | DfaxDemand | Dfax of study generator with respect to flowgate
TARA | NE_OverloadSum | DemandMWRef | MW redispatch by SCRD in Reference dispatch. (MW Up + MW Down)/2
TARA | NE_OverloadSum | DemandMWStudy | MW redispatch by SCRD in Study dispatch. (MW Up + MW Down)/2
TARA | NE_OverloadSum | DispPassFail | Did FCM bid pass or fail reliability review for this stressed flowgate?
TARA | NE_OverloadSum | NumKeyBindingFgates | For flowgates that were binding for the Study Dispatch SCD, how many satisfied the Study Unit Dfax cutoff (see Options> StudyFgate> Study Gen Impact)
TARA | NE_OverloadSum | RefMWRedispatch | Pgen of study bid in reference dispatch
TARA | NE_OverloadSum | StudyMWRedispatchMW | Pgen of study bid in study dispatch
TARA | NE_OverloadSum | NumPenRef | Number of SCRD penalties applied in reference dispatch.
TARA | NE_OverloadSum | NumPenStudy | Number of SCRD penalties applied in study dispatch.
TARA | NE_OverloadSum | HelperMWBase | Biggest helper Pgen in base case
TARA | NE_OverloadSum | HelperMWRef | Biggest helper Pgen in reference dispatch
TARA | NE_OverloadSum | HelperMWStudy | Biggest helper Pgen in study dispatch
TARA | NE_OverloadSum | BidderName | Biggest helper name
TARA | NE_OverloadSum | unitType | Biggest helper unit type
TARA | NE_OverloadSum | Fuel/Schd | Biggest helper fuel type
TARA | NE_OverloadSum | OrgName | Biggest helper organization name
TARA | NE_OverloadSum | BTyp | Biggest helper bidder type
TARA | NE_OverloadSum | InHarmerMWDownStudy | Total in-circle harmer MW turned down
TARA | NE_OverloadSum | InHarmerImpactDownStudy | Total impact (dfax*MW) of in-circle harmers turned down
TARA | NE_OverloadSum | InHarmerPnodesDownStudy | Number of in-circle harmers turned down
TARA | NE_OverloadSum | OutHelperMWUpStudy | Total out-circle helper MW turned down
TARA | NE_OverloadSum | OutHelperImpactUpStudy | Total impact (dfax*MW) of out-circle helpers turned down
TARA | NE_OverloadSum | OutHelperPnodesUpStudy | Number of out-circle helpers turned down
TARA | NE_BidsList | BidID | Demand/Bilateral Bid ID as read from Demand Bid file
TARA | NE_BidsList | Type | Type of Bid. Could be Demand, Offer, or Restricted. Demand reduce capacity, Offer increase capacity, Restricted are can go down from Ref Dispatch MW but not higher than Ref Dispatc hMW
TARA | NE_BidsList | PnodeID | Typically an integer assigned to the node as read from the Demand Bid file
TARA | NE_BidsList | PnodeName | Name assigned to node as read from the Demand Bid File
TARA | NE_BidsList | MW | MW to study when evaluating the bid
TARA | NE_BidsList | Status | User-defined initial bid status. Accepted, Declined or Study
TARA | MISOGenDelivFgLoad | Base FG Flow | Flowgate MW flow with no dispatch changes (i.e. MISO GD generator dispatches not applied)
TARA | MISOGenDelivFgLoad | Top 30 Impact | Total MW impact of Top30 units ((NR MW - Pgen) X Dfax)
TARA | MISOGenDelivFgLoad | Adder Impact | Total MW impact of Adder units (NR MW X Dfax)
TARA | MISOGenDelivFgLoad | ER Impact | Total MW impact of ER units ((NR MW-Pgen) X Dfax)
TARA | MISOGenDelivFgLoad | DC Final Flow | Base FG Flow + Top 30 Impact + Adder Impact + ER Impact
TARA | MISOGenDelivFgLoad | AC Final Flow | AC post-cont flow with MISO GD dispatches applied. AC Final Flow=DC Final Flow if no AC verification performed
TARA | MISOGenDelivFgLoad | MW Restricted | Sum of shared MW undeliverable
TARA | MISOGenDelivFgLoad | Shared Pmax NR | Sum of total NR MW in Top 30 or Adder list. User options available to select only STUDY units
TARA | MISOGenDelivFgLoad | Severity Rank | Severity rank for a monitored facility. 1 for highest loading. 0 for basecase violation
TARA | CAISOGenDelivFgLoad | Post-FLA %LD | Post-FLA percent loading with no GCR applied. If FLA is not triggered, it is the Post-Shift loading with no GCR applied.
TARA | CAISOGenDelivFgLoad | Post-GCR %LD | Post-GCR percent loading. For no GCR analysis, it is the same as Post-FLA loading.
TARA | CAISOGenDelivFgLoad | DC¦AC | AC if post-shift case converged. DC if post-shift case is not converged, or not AC-tested
TARA | CAISOGenDelivFgLoad | Pre-Shift MW Flow | Estimated MW flow on a monitored facility with a contingency applied
TARA | CAISOGenDelivFgLoad | Top20 MW Impact | Summation of incremental flow impacts of TOP20 post-shift dispatch (Max 20 units and total dispatch less than or equal to 1500 MW)
TARA | CAISOGenDelivFgLoad | GCR MW Impact | Total MW impact after applying GCR
TARA | CAISOGenDelivFgLoad | Post-Shift MW Flow | Estimated MW flow on a monitored facility with a contingency and Top20 dispatches applied. Equal to Pre-Shift MW Flow + Top20 MW Impact + GCR MW Impact
TARA | CAISOGenDelivFgLoad | Post-Shift MVA Flow | MVA flow on a monitored facility with a contignency and Top20 disaptches applied and GCR applied if GCR is performed.
TARA | CAISOGenDelivFgLoad | Post-Shift DC %LD | Post-shift DC percent loading
TARA | CAISOGenDelivFgLoad | Post-Shift AC %LD | Post-shift AC percent loading
TARA | CAISOGenDelivFgLoad | Adder MW Impact | Total MW impact from FLA generation
TARA | CAISOGenDelivFgLoad | Adder Counter MW Impact | Total MW impact from the selected counter generation
TARA | CAISOGenDelivFgLoad | Post-FLA Flow | Post Facility Loading Adder (FLA) flow with no GCR. MVA flow if AC tested. MW flow if AC test is not performed or not converged.
TARA | CAISOGenDelivFgLoad | Post-GCR Flow | Post Facility Loading Adder (FLA) flow with GCR. MVA flow if AC tested. MW flow if AC test is not performed or not converged.
TARA | CAISOGenDelivFgLoad | Severity Rank | Severity rank for monitored facility (order of percent loading. 1 is the highest. 0 is for basecase)
TARA | 5PcntDfaxCircle | Pnew | New dispatch MW
TARA | 5PcntDfaxCircle | Flag | Reason if a unit is dispatched (Top20, Top20 Partial, Top20 GCR, etc.)
TARA | 5PcntDfaxCircle | MW Impact | MW impact after a unit is dispatched up or down
TARA | 5PcntDfaxCircle | GCR Priority | Curtailment priority (OWNER2 field of the GEN table in the study EPC case)
TARA | 5PcntDfaxCircle | Impact Factor | (Pmax-Pold) X Dfax)/Line Rating
TARA | 5PcntDfaxCircle | Full Impact | Pmax X Dfax
TARA | 5PcntDfaxCircle | Study Bus | Study if a generator bus is defined as a study bus
TARA | 5PcntDfaxCircle | Post-FLA %LD | Post Facility Loading Adder (FLA) percent Loading with no GCR. If FLA is not triggered, it is the Post-Shift loading with no GCR applied.
TARA | 5PcntDfaxCircle | Post-GCR %LD | Post Facility Loading Adder (FLA) percent Loading with GCR. For no GCR analysis, it is the same as Post-FLA loading.
TARA | 5PcntDfaxCircle | DC¦AC | AC if post-shift case converged. DC if post-shift case is not converged, or not AC-tested
TARA | FGx_Dispatch | Pre-Shift MW Flow | Estimated MW flow on a monitored facility with a contingency applied
TARA | FGx_Dispatch | Pre-Shift MVA Flow | MVA flow on a monitored facility with a contingency applied
TARA | FGx_Dispatch | Top20 MW Impact | Summation of incremental flow impacts of TOP20 post-shift dispatch (Max 20 units and total dispatch less than or equal to 1500 MW)
TARA | FGx_Dispatch | GCR MW Impact | Total MW impact after applying GCR
TARA | FGx_Dispatch | Post-Shift MW Flow | Estimated MW flow on a monitored facility with a contingency and Top20 dispatches applied. Equal to Pre-Shift MW Flow + Top20 MW Impact + GCR MW Impact
TARA | FGx_Dispatch | Post-Shift MVA Flow | MVA flow on a monitored facility with a contignency and Top20 disaptches applied and GCR applied if GCR is performed.
TARA | FGx_Dispatch | Post-Shift DC %LD | Post-shift DC percent loading
TARA | FGx_Dispatch | Post-Shift AC %LD | Post-shift AC percent loading
TARA | FGx_Dispatch | Adder MW Impact | Total MW impact from FLA generation
TARA | FGx_Dispatch | Adder Counter MW Impact | Total MW impact from the selected counter generation
TARA | FGx_Dispatch | FLA Net Flow | max(0, (Adder MW impact - Adder Counter MW impact))
TARA | FGx_Dispatch | Post-FLA DC %LD | Post-FLA DC percent loading with no GCR applied
TARA | FGx_Dispatch | Post-FLA AC %LD | Post-FLA AC percent loading with no GCR applied
TARA | FGx_Dispatch | Post-GCR DC %LD | Post-FLA DC percent loading
TARA | FGx_Dispatch | Post-GCR AC %LD | Post-FLA AC percent loading
TARA | FGx_Dispatch | Pnew | New dispatch MW
TARA | FGx_Dispatch | Flag | Reason if a unit is dispatched (Top20, Top20 Partial, Top20 GCR, etc.)
TARA | FGx_Dispatch | MW Impact | MW impact after a unit is dispatched up or down
TARA | FGx_Dispatch | Top20 Count | Count if a unit belongs to Top20 or Adder (1 is the highest MW impact, 20 is the last)
TARA | FGx_Dispatch | GCR Priority | Curtailment priority (OWNER2 field of the GEN table in the study EPC case)
TARA | FGx_Dispatch | Impact Factor | (Pmax-Pold) X Dfax)/Line Rating
TARA | FGx_Dispatch | Full Impact | Pmax X Dfax
TARA | FGx_Dispatch | Study Bus | Study if a generator bus is defined as a study bus
<--------> | <--------> | <--------> | <-------->

## RMC_MAP800 (hidden)
TARA Right Mouse Click (RMC) Functions Summary
All Reports
TARA Main Menu
TARA Sort
Ascending
Descending
Ascending Abs
Descending Abs
TARA Filter
Filter
Filter Out
Master Filter
TARA Utilities
Compare Reports
Compare Two Reports
Compare Two LF Cases on Single Report
Create BatchProcess sheet
Find/Rename/Export Sheet
Hide/Unhide Columns
Create Pivot Table
Create TARA Desktop Shortcut
TARA LF Case Editor
Bus Based Editor
Scale Gen/Load
Create Subset Case
Bus Functions
Bus Analysis/Diagram
Bus Utilities
Available Bus Numbers
TARA Help
Column Description
Help Topics
About TARA
Area (Zone) Reports
Area (Zone) Diagram
LF Case Details
Buses
Generators
Plants
Loads
Shunts
Branches
BranchDbl
Transformers
Ties
TiesDbl
PARs
Bus, Branch, Gen, Load, Ties, Area Reports
TARA LF Case Editor
Bus Based Editor
Data Editor (depends data item)
Scale Gen/Load
Create Subset Case
Contingency List Report (or selected contingencies in a report)
Contingency Analysis Functions
ACCont
Details
Definitions
Create Double Contingencies
Exclude
Monitored Branch Report
Exclude
Flowgates/Interfaces Reports
Flowgate Reports
Flowgate Analysis
Flowgate Definitions
Flowgate Details
Flow Impact Calculator
PAR Impact Calculator
Create Flowgate File with No Duplicates
List of Defined Subsystems Report
Subsystem Details
AC or DC Contingency Analysis Branch Reports
Constraint Reports
Flowgate Analysis
Flowgate Definitions
Flowgate Details
Flow Impact Calculator
PAR Impact Calculator
Contingency Analysis Functions
ACCont
Details
Definitions
Create Double Contingencies
Exclude
Add/Create LF Case
Contingency Analysis Bus Reports
Contingency Analysis Functions
ACCont
Details
Definitions
Create Double Contingencies
Exclude
Add/Create LF Case
PV Screening Summary Report
Run PV Analysis
PV Analysis Reports
Create PV Plot for selected contingency
Create PV Plot for selected bus
Any BatchProcess sheet
Select Application
Add Scenario (Specify Input Files)
Edit Scenario (Specify Input Files)
Select Report Directory
Run Batch Automation
Create LF Cases (After INCH File Applied)
Merge Output Reports
Perform Cross-Comparison
Bring up Main Menu with Scenario Input Files
Bus Editor
Create Changed Case and INCH File
Editor Utilities
Add/Duplicate Selected Records
Purge Selected Records
Tap Selected Line
Data Editor Help
Flow Impact Calculator (GRDcalc & EQUIPcalc reports)
Save Data Changes
One Line Diagram
Update Diagram
Diagram Utilities
Select Bus to Grow
Change Diagram Data
Hide/Show Branch Data
Reroute Branch Connections
Add Bus to Diagram
Connect All Buses
Switch Diagram to Run Mode
Apply Changes (run mode)
Apply Changes
Apply Changes and Solve
Area (Zone) Diagram
Update Diagram
Change Diagram Data
Select Area to Grow
Add Area to Diagram
Hide/Show Connection Data
Reroute Connections
Connect All Areas