## Branch Flow
BRANCH | [6 empty] | CONTINGENCY | CONTINGENCY | MVAFLOW | AMPFLOW | RATE RATE1/RATE2 | % FLOW | OWNER | ANALYSIS
341761 | 2LIBERTY J | 69 | 341896 | 2MT OLIVE J | 69 | 1 | EKPC_P1-2_COP-LIBJ-PU161 | EKPC_P1-2_COP-LIBJ-PU161 | 98.9113 | 96.8001 | 63 | 153.651 | EKPC |  | BASE VOLTS is pu base case voltage.
341761 | 2LIBERTY J | 69 | 341767 | 2LIBERTYKU T | 69 | 1 | SING OPN LIN 469 342222-342760(1) | OPEN LINE FROM BUS 342222 [5S CASEY 161.00] TO BUS 342760 [5LIBERTY J 161.00] CKT 1 | -98.4251 | 101.1 | 66 | 153.1819 | EKPC |  | CONT VOLTS is pu contingency case voltage.
341761 | 2LIBERTY J | 69 | 341896 | 2MT OLIVE J | 69 | 1 | SING OPN LIN 603 342760-342790(1) | OPEN LINE FROM BUS 342760 [5LIBERTY J 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 97.8482 | 95.7662 | 63 | 152.0099 | EKPC |  | DEVIATION is difference between contingency case and base case voltage.
341617 | 2HIGHLAND EK | 69 | 341896 | 2MT OLIVE J | 69 | 1 | EKPC_P1-2_COP-LIBJ-PU161 | EKPC_P1-2_COP-LIBJ-PU161 | -90.3191 | 88.9241 | 63 | 141.1494 | EKPC |  | RANGE VIO is range violations calculated as bus voltage - minimum range limit or bus voltage - maximum range limit.
DEV VIO is deviation violations calculated as DEVIATION - minimum deviation limit or DEVIATION - maximum deviation limit.
341617 | 2HIGHLAND EK | 69 | 341896 | 2MT OLIVE J | 69 | 1 | SING OPN LIN 603 342760-342790(1) | OPEN LINE FROM BUS 342760 [5LIBERTY J 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | -89.2693 | 87.8802 | 63 | 139.4925 | EKPC |  | Report Options Used:
Solution type = contingency
341209 | 2BROUGTWN T | 69 | 341617 | 2HIGHLAND EK | 69 | 1 | EKPC_P1-2_COP-LIBJ-PU161 | EKPC_P1-2_COP-LIBJ-PU161 | -84.7009 | 84.3775 | 63 | 133.9325 | EKPC |  | Rating to use to calculate Base Case percentage overload = RATE1
341209 | 2BROUGTWN T | 69 | 341617 | 2HIGHLAND EK | 69 | 1 | SING OPN LIN 603 342760-342790(1) | OPEN LINE FROM BUS 342760 [5LIBERTY J 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | -83.6697 | 83.3307 | 63 | 132.2709 | EKPC |  | Rating to use to calculate Contingency Case percentage overload = RATE2
341209 | 2BROUGTWN T | 69 | 342367 | 2TOMM GOOC T | 69 | 1 | EKPC_P1-2_COP-LIBJ-PU161 | EKPC_P1-2_COP-LIBJ-PU161 | 82.1281 | 81.47 | 63 | 129.3174 | EKPC |  | Exclude elements with base case loading violations from contingency reports = False
341209 | 2BROUGTWN T | 69 | 342367 | 2TOMM GOOC T | 69 | 1 | SING OPN LIN 603 342760-342790(1) | OPEN LINE FROM BUS 342760 [5LIBERTY J 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 81.0791 | 80.4195 | 63 | 127.6499 | EKPC |  | Exclude buses with base case voltage range violations from contingency reports = False
341761 | 2LIBERTY J | 69 | 341896 | 2MT OLIVE J | 69 | 1 | B-69-18 | B-69-18 | 75.9602 | 75.7782 | 63 | 120.2828 | EKPC |  | Exclude elements with base case SWD loading violations from contingency reports = False
Exclude buses with base case node voltage range violations from contingency reports = False
341767 | 2LIBERTYKU T | 69 | 342064 | 2PEYTONS ST | 69 | 1 | SING OPN LIN 469 342222-342760(1) | OPEN LINE FROM BUS 342222 [5S CASEY 161.00] TO BUS 342760 [5LIBERTY J 161.00] CKT 1 | -107.2888 | 108.2143 | 90 | 120.2381 | EKPC |  | Percent of flow rating = 90
341269 | 2CASEY CO | 69 | 342064 | 2PEYTONS ST | 69 | 1 | SING OPN LIN 469 342222-342760(1) | OPEN LINE FROM BUS 342222 [5S CASEY 161.00] TO BUS 342760 [5LIBERTY J 161.00] CKT 1 | 115.8886 | 116.0766 | 98 | 118.4455 | EKPC |  | Minimum contingency case flow change (=contCaseFlow-baseCaseFlow) for overload reports = 1 MVA
Minimum contingency case voltage change (=contCaseV-baseCaseV) for violations = 0.01 pu
342222 | 5S CASEY | 161 | 342760 | 5LIBERTY J | 161 | 1 | B-69-18 | B-69-18 | -590.486 | 608.2081 | 525 | 115.8492 | EKPC |  | Cutoff threshold for branch angle difference = 0.0 pu, filter criteria ignored
324141 | 5ELIHU | 161 | 324130 | 5ALCALDE | 161 | 1 | BASE CASE | BASE CASE | 377.7607 | 385.414 | 342 | 112.6941 | LGEE |  | Exclude islanded buses from contingency reports = True
342222 | 5S CASEY | 161 | 342760 | 5LIBERTY J | 161 | 1 | BASE CASE | BASE CASE | 383.5917 | 383.5917 | 342 | 112.1613 | EKPC |  | Bus mismatch tolerance = 0.5 MVA
341269 | 2CASEY CO | 69 | 342703 | 5CASEY CO | 161 | 1 | SING OPN LIN 469 342222-342760(1) | OPEN LINE FROM BUS 342222 [5S CASEY 161.00] TO BUS 342760 [5LIBERTY J 161.00] CKT 1 | -120.4873 | 120.4873 | 108 | 111.5623 | EKPC |  | System mismatch tolerance = 5 MVA
342760 | 5LIBERTY J | 161 | 342790 | 5PULASK CO J | 161 | 1 | BASE CASE | BASE CASE | 375.5008 | 380.0857 | 342 | 111.1362 | EKPC
Note: RATE column label is Base Case Rating/Contingency case rating.
342760 | 5LIBERTY J | 161 | 342790 | 5PULASK CO J | 161 | 1 | B-69-18 | B-69-18 | 564.6859 | 581.6336 | 525 | 110.7874 | EKPC
342715 | 5COOPER1 | 161 | 342790 | 5PULASK CO J | 161 | 1 | SING OPN TIE 734 342782-342837(1) | OPEN LINE FROM BUS 342782 [5PINEVILL EK161.00] TO BUS 342837 [7PINEVILL EK345.00] CKT 1 | -314.0575 | 321.3725 | 298 | 107.8431 | EKPC
341617 | 2HIGHLAND EK | 69 | 341896 | 2MT OLIVE J | 69 | 1 | B-69-18 | B-69-18 | -67.4394 | 67.2688 | 63 | 106.7759 | EKPC
342715 | 5COOPER1 | 161 | 342790 | 5PULASK CO J | 161 | 1 | SING OPN LIN 619 342787-342790(1) | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | -308.4038 | 316.5779 | 298 | 106.2342 | EKPC
341761 | 2LIBERTY J | 69 | 342760 | 5LIBERTY J | 161 | 1 | SING OPN LIN 603 342760-342790(1) | OPEN LINE FROM BUS 342760 [5LIBERTY J 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 115.5212 | 115.5212 | 109 | 105.9828 | EKPC
341761 | 2LIBERTY J | 69 | 342760 | 5LIBERTY J | 161 | 1 | EKPC_P1-2_COP-LIBJ-PU161 | EKPC_P1-2_COP-LIBJ-PU161 | 115.0528 | 115.0528 | 109 | 105.553 | EKPC
342286 | 2SOMERSET | 69 | 342287 | 2SOMERSET KU | 69 | 1 | SING OPN LIN 583 342715-342718(1) | OPEN LINE FROM BUS 342715 [5COOPER1 161.00] TO BUS 342718 [5COOPER2 161.00] CKT 1 | -227.3194 | 235.9876 | 225 | 104.8834 | EKPC
341392 | 2DENNY | 69 | 342499 | 2WIBORG T | 69 | 1 | SING OPN TIE 742 342823-360486(1) | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 68.7352 | 77.1943 | 76 | 101.5714 | EKPC
341392 | 2DENNY | 69 | 341578 | 2GREGORY R T | 69 | 1 | SING OPN TIE 742 342823-360486(1) | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | -190.8431 | 225.4386 | 225 | 100.1949 | EKPC
341392 | 2DENNY | 69 | 342499 | 2WIBORG T | 69 | 1 | SING OPN TIE 732 342778-360486(1) | OPEN LINE FROM BUS 342778 [5MCCREARY CO161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 73.6172 | 76.0804 | 76 | 100.1058 | EKPC
341209 | 2BROUGTWN T | 69 | 341617 | 2HIGHLAND EK | 69 | 1 | B-69-18 | B-69-18 | -63.0856 | 62.9346 | 63 | 99.8962 | EKPC
342715 | 5COOPER1 | 161 | 342790 | 5PULASK CO J | 161 | 1 | SING OPN LIN 617 342782-342787(1) | OPEN LINE FROM BUS 342782 [5PINEVILL EK161.00] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | -288.9762 | 296.4958 | 298 | 99.4952 | EKPC
342793 | 5RUSSEL CO | 161 | 342178 | 2RUSSEL CO | 69 | 1 | EKPC_P1-2_RUSSOL-RUS-WLF161 | EKPC_P1-2_RUSSOL-RUS-WLF161 | 150.391 | 150.391 | 152 | 98.9415 | EKPC
342793 | 5RUSSEL CO | 161 | 342178 | 2RUSSEL CO | 69 | 1 | SING OPN LIN 621 342793-342796(1) | OPEN LINE FROM BUS 342793 [5RUSSEL CO 161.00] TO BUS 342796 [5RUSSEL CO J161.00] CKT 1 | 150.3764 | 150.3763 | 152 | 98.9318 | EKPC
341761 | 2LIBERTY J | 69 | 341896 | 2MT OLIVE J | 69 | 1 | B-138-111 | B-138-111 | 62.3659 | 61.9486 | 63 | 98.3311 | EKPC
942410 | AE2-254 TAP | 69 | 341515 | 2GARRARD CO | 69 | 1 | BASE CASE | BASE CASE | 144.6651 | 142.5988 | 146 | 97.6704 | EKPC
324141 | 5ELIHU | 161 | 324130 | 5ALCALDE | 161 | 1 | SING OPN TIE 734 342782-342837(1) | OPEN LINE FROM BUS 342782 [5PINEVILL EK161.00] TO BUS 342837 [7PINEVILL EK345.00] CKT 1 | 496.2146 | 510.6698 | 525 | 97.2704 | LGEE
342286 | 2SOMERSET | 69 | 342287 | 2SOMERSET KU | 69 | 1 | SING OPN TIE 724 342718-324141(1) | OPEN LINE FROM BUS 342718 [5COOPER2 161.00] TO BUS 324141 [5ELIHU 161.00] CKT 1 | -209.121 | 217.1422 | 225 | 96.5077 | EKPC
342472 | 2WALNUT GROV | 69 | 342511 | 2WOODSTOCK | 69 | 1 | SING OPN LIN 13 341032-341379(1) | OPEN LINE FROM BUS 341032 [2ASAHI M W T69.000] TO BUS 341379 [2DAHL ROAD 69.000] CKT 1 | -59.1355 | 60.3826 | 63 | 95.8454 | EKPC
341974 | 2NORWOOD T | 69 | 341233 | 2CABIN HOLLW | 69 | 1 | SING OPN TIE 734 342782-342837(1) | OPEN LINE FROM BUS 342782 [5PINEVILL EK161.00] TO BUS 342837 [7PINEVILL EK345.00] CKT 1 | -83.2589 | 86.1676 | 90 | 95.7418 | EKPC
341209 | 2BROUGTWN T | 69 | 342367 | 2TOMM GOOC T | 69 | 1 | B-69-18 | B-69-18 | 60.7187 | 60.2371 | 63 | 95.6144 | EKPC
341761 | 2LIBERTY J | 69 | 342760 | 5LIBERTY J | 161 | 1 | SING OPN LIN 469 342222-342760(1) | OPEN LINE FROM BUS 342222 [5S CASEY 161.00] TO BUS 342760 [5LIBERTY J 161.00] CKT 1 | -103.7318 | 103.7318 | 109 | 95.1668 | EKPC
342222 | 5S CASEY | 161 | 342760 | 5LIBERTY J | 161 | 1 | B-138-111 | B-138-111 | -489.421 | 499.3547 | 525 | 95.1152 | EKPC
341392 | 2DENNY | 69 | 342499 | 2WIBORG T | 69 | 1 | EKPC_P1-2_MCCR-WAYNE161 | EKPC_P1-2_MCCR-WAYNE161 | 70.6722 | 72.2241 | 76 | 95.0317 | EKPC
341761 | 2LIBERTY J | 69 | 341896 | 2MT OLIVE J | 69 | 1 | SING OPN TIE 734 342782-342837(1) | OPEN LINE FROM BUS 342782 [5PINEVILL EK161.00] TO BUS 342837 [7PINEVILL EK345.00] CKT 1 | 59.2198 | 58.5078 | 63 | 92.8696 | EKPC
342760 | 5LIBERTY J | 161 | 342790 | 5PULASK CO J | 161 | 1 | B-138-111 | B-138-111 | 474.3684 | 483.9966 | 525 | 92.1898 | EKPC
342222 | 5S CASEY | 161 | 342760 | 5LIBERTY J | 161 | 1 | SING OPN LIN 626 342814-943820(1) | OPEN LINE FROM BUS 342814 [5SUMM SHADE 161.00] TO BUS 943820 [AF1-050 TAP 161.00] CKT 1 | 476.9379 | 476.9379 | 525 | 90.8453 | EKPC
341344 | 2COOPER | 69 | 342715 | 5COOPER1 | 161 | 1 | SING OPN LIN 583 342715-342718(1) | OPEN LINE FROM BUS 342715 [5COOPER1 161.00] TO BUS 342718 [5COOPER2 161.00] CKT 1 | 129.5038 | 129.5038 | 143 | 90.5621 | EKPC
324141 | 5ELIHU | 161 | 324130 | 5ALCALDE | 161 | 1 | SING OPN LIN 617 342782-342787(1) | OPEN LINE FROM BUS 342782 [5PINEVILL EK161.00] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 460.0994 | 472.5569 | 525 | 90.0108 | LGEE

## Branch Flow Filtered
BRANCH | [6 empty] | CONTINGENCY | CONTINGENCY | MVAFLOW | AMPFLOW | RATE RATE1/RATE2 | % FLOW | OWNER | ANALYSIS
341761 | 2LIBERTY J | 69 | 341896 | 2MT OLIVE J | 69 | 1 | EKPC_P1-2_COP-LIBJ-PU161 | EKPC_P1-2_COP-LIBJ-PU161 | 98.9113 | 96.8001 | 63 | 153.651 | EKPC | rebuild using 795 ACSR (should have been upgraded with initial solar projects)
341761 | 2LIBERTY J | 69 | 341767 | 2LIBERTYKU T | 69 | 1 | SING OPN LIN 469 342222-342760(1) | OPEN LINE FROM BUS 342222 [5S CASEY 161.00] TO BUS 342760 [5LIBERTY J 161.00] CKT 1 | -98.4251 | 101.1 | 66 | 153.1819 | EKPC | rebuild using 795 ACSR (should have been upgraded with initial solar projects)
341617 | 2HIGHLAND EK | 69 | 341896 | 2MT OLIVE J | 69 | 1 | EKPC_P1-2_COP-LIBJ-PU161 | EKPC_P1-2_COP-LIBJ-PU161 | -90.3191 | 88.9241 | 63 | 141.1494 | EKPC | rebuild using 795 ACSR (should have been upgraded with initial solar projects)
341209 | 2BROUGTWN T | 69 | 341617 | 2HIGHLAND EK | 69 | 1 | EKPC_P1-2_COP-LIBJ-PU161 | EKPC_P1-2_COP-LIBJ-PU161 | -84.7009 | 84.3775 | 63 | 133.9325 | EKPC | rebuild using 795 ACSR
341209 | 2BROUGTWN T | 69 | 342367 | 2TOMM GOOC T | 69 | 1 | EKPC_P1-2_COP-LIBJ-PU161 | EKPC_P1-2_COP-LIBJ-PU161 | 82.1281 | 81.47 | 63 | 129.3174 | EKPC | rebuild using 795 ACSR
341767 | 2LIBERTYKU T | 69 | 342064 | 2PEYTONS ST | 69 | 1 | SING OPN LIN 469 342222-342760(1) | OPEN LINE FROM BUS 342222 [5S CASEY 161.00] TO BUS 342760 [5LIBERTY J 161.00] CKT 1 | -107.2888 | 108.2143 | 90 | 120.2381 | EKPC | rebuild using 795 ACSR
341269 | 2CASEY CO | 69 | 342064 | 2PEYTONS ST | 69 | 1 | SING OPN LIN 469 342222-342760(1) | OPEN LINE FROM BUS 342222 [5S CASEY 161.00] TO BUS 342760 [5LIBERTY J 161.00] CKT 1 | 115.8886 | 116.0766 | 98 | 118.4455 | EKPC | rebuild using 795 ACSR
342222 | 5S CASEY | 161 | 342760 | 5LIBERTY J | 161 | 1 | B-69-18 | B-69-18 | -590.486 | 608.2081 | 525 | 115.8492 | EKPC | rebuild using bundled 954 ACSS
324141 | 5ELIHU | 161 | 324130 | 5ALCALDE | 161 | 1 | BASE CASE | BASE CASE | 377.7607 | 385.414 | 342 | 112.6941 | LGEE | rebuild using bundled 954 ACSS
341269 | 2CASEY CO | 69 | 342703 | 5CASEY CO | 161 | 1 | SING OPN LIN 469 342222-342760(1) | OPEN LINE FROM BUS 342222 [5S CASEY 161.00] TO BUS 342760 [5LIBERTY J 161.00] CKT 1 | -120.4873 | 120.4873 | 108 | 111.5623 | EKPC | correct ratings to: 107,131,147
342760 | 5LIBERTY J | 161 | 342790 | 5PULASK CO J | 161 | 1 | BASE CASE | BASE CASE | 375.5008 | 380.0857 | 342 | 111.1362 | EKPC | rebuild using bundled 954 ACSS
342715 | 5COOPER1 | 161 | 342790 | 5PULASK CO J | 161 | 1 | SING OPN TIE 734 342782-342837(1) | OPEN LINE FROM BUS 342782 [5PINEVILL EK161.00] TO BUS 342837 [7PINEVILL EK345.00] CKT 1 | -314.0575 | 321.3725 | 298 | 107.8431 | EKPC | rebuild using 954 ACSS
341761 | 2LIBERTY J | 69 | 342760 | 5LIBERTY J | 161 | 1 | SING OPN LIN 603 342760-342790(1) | OPEN LINE FROM BUS 342760 [5LIBERTY J 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 115.5212 | 115.5212 | 109 | 105.9828 | EKPC | upgrade 93MVA transformer to 150MVA: 144,175/198
342286 | 2SOMERSET | 69 | 342287 | 2SOMERSET KU | 69 | 1 | SING OPN LIN 583 342715-342718(1) | OPEN LINE FROM BUS 342715 [5COOPER1 161.00] TO BUS 342718 [5COOPER2 161.00] CKT 1 | -227.3194 | 235.9876 | 225 | 104.8834 | EKPC | rebuild using bundled conductor
341392 | 2DENNY | 69 | 342499 | 2WIBORG T | 69 | 1 | SING OPN TIE 742 342823-360486(1) | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 68.7352 | 77.1943 | 76 | 101.5714 | EKPC | upgrade CT, jumpers, and disconnect switch to get to conductor rating
341392 | 2DENNY | 69 | 341578 | 2GREGORY R T | 69 | 1 | SING OPN TIE 742 342823-360486(1) | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | -190.8431 | 225.4386 | 225 | 100.1949 | EKPC | rebuild

## Bus Voltage
BUS | RECORD | TYPE | MIN | MAX | CONTINGENCY | CONTINGENCY | BASE VOLTS | VOLTAGE | CONT VOLTS | VOLTAGE | DEVIATION | RANGE VIO | DEV VIO | Analysis
No monitored bus voltages specified.

## Contingency Events
CONTINGENCY | EVENTS | CONVERGED | CONVERGENCE STATE | ISLANDS | MVAWORST | MVATOTAL | LOADS SHED | MWs SHED
BASE CASE | BASE CASE | TRUE | Met convergence tolerances | 0 | 0.14437 | 2.0597
SING OPN LIN 1 339206-342769(1) | OPEN LINE FROM BUS 339206 [AE1-143 C 161.00] TO BUS 342769 [5MARION CO 161.00] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.83116 | 19.7308
SING OPN LIN 2 339206-939132(1) | OPEN LINE FROM BUS 339206 [AE1-143 C 161.00] TO BUS 939132 [AE1-143 E 161.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.73376 | 8.2257
SING OPN LIN 3 341002-341443(1) | OPEN LINE FROM BUS 341002 [2AIRPORT RD 69.000] TO BUS 341443 [2ELLIO CO PT69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.25117 | 10.6945
SING OPN LIN 4 341002-341752(1) | OPEN LINE FROM BUS 341002 [2AIRPORT RD 69.000] TO BUS 341752 [2LEON 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.22125 | 10.4372
SING OPN LIN 5 341008-342106(1) | OPEN LINE FROM BUS 341008 [2ALCAN 69.000] TO BUS 342106 [2PPG J 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.7448
SING OPN LIN 6 341008-342430(1) | OPEN LINE FROM BUS 341008 [2ALCAN 69.000] TO BUS 342430 [2W BEREA 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.5452
SING OPN LIN 7 341014-341017(1) | OPEN LINE FROM BUS 341014 [2ANNVILLE 69.000] TO BUS 341017 [2ANNVILLE T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 3.1028 | 1 | 4.3545
SING OPN LIN 8 341017-341428(1) | OPEN LINE FROM BUS 341017 [2ANNVILLE T 69.000] TO BUS 341428 [2EBERLE T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 7.5388
SING OPN LIN 9 341017-342391(1) | OPEN LINE FROM BUS 341017 [2ANNVILLE T 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 8.3553
SING OPN LIN 10 341020-341782(1) | OPEN LINE FROM BUS 341020 [2ARGENTUM 69.000] TO BUS 341782 [2LOW GAP T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 8.2679
SING OPN LIN 11 341020-342538(1) | OPEN LINE FROM BUS 341020 [2ARGENTUM 69.000] TO BUS 342538 [4ARGENTUM 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.9536
SING OPN LIN 12 341029-341032(1) | OPEN LINE FROM BUS 341029 [2ASAHI M W 69.000] TO BUS 341032 [2ASAHI M W T69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 2.1986 | 23.5993 | 1 | 11.9039
SING OPN LIN 13 341032-341379(1) | OPEN LINE FROM BUS 341032 [2ASAHI M W T69.000] TO BUS 341379 [2DAHL ROAD 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.3448 | 7.789
SING OPN LIN 14 341032-342077(1) | OPEN LINE FROM BUS 341032 [2ASAHI M W T69.000] TO BUS 342077 [2PINEVILL EK69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14384 | 5.9274
SING OPN LIN 15 341032-342472(1) | OPEN LINE FROM BUS 341032 [2ASAHI M W T69.000] TO BUS 342472 [2WALNUT GROV69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.25013 | 4.7565
SING OPN LIN 16 341035-341038(1) | OPEN LINE FROM BUS 341035 [2BACON CRK 69.000] TO BUS 341038 [2BACON CRK T69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 2.635 | 1 | 4.3674
SING OPN LIN 17 341038-341755(1) | OPEN LINE FROM BUS 341038 [2BACON CRK T69.000] TO BUS 341755 [2LIBER CH T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.3123
SING OPN LIN 18 341038-342187(1) | OPEN LINE FROM BUS 341038 [2BACON CRK T69.000] TO BUS 342187 [2S CORBIN 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.4471
SING OPN LIN 19 341041-341635(1) | OPEN LINE FROM BUS 341041 [2BAKER LN 69.000] TO BUS 341635 [2HOLLOWAY 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 2.111 | 22.8271 | 1 | 10.8215
SING OPN LIN 20 341041-341638(1) | OPEN LINE FROM BUS 341041 [2BAKER LN 69.000] TO BUS 341638 [2HOLLOWAY J 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.6009
SING OPN LIN 21 341041-342547(1) | OPEN LINE FROM BUS 341041 [2BAKER LN 69.000] TO BUS 342547 [4BAKER LN 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.18903 | 6.0232
SING OPN LIN 22 341044-341671(1) | OPEN LINE FROM BUS 341044 [2BALLARD 69.000] TO BUS 341671 [2HUNT FARM J69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.5619
SING OPN LIN 23 341044-342361(1) | OPEN LINE FROM BUS 341044 [2BALLARD 69.000] TO BUS 342361 [2TODDVILLE T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14435 | 2.8391
SING OPN LIN 24 341047-342424(1) | OPEN LINE FROM BUS 341047 [2BALLTOWN 69.000] TO BUS 342424 [2W BARDST J 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 2.3884 | 25.3607 | 1 | 11.9528
SING OPN LIN 25 341050-342295(1) | OPEN LINE FROM BUS 341050 [2BANK LCK 69.000] TO BUS 342295 [2STANLY P J169.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 2.6853 | 28.0485 | 1 | 13.3486
SING OPN LIN 26 341053-341056(1) | OPEN LINE FROM BUS 341053 [2BARD SHOP 69.000] TO BUS 341056 [2BARD SHOP T69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 2.1802 | 23.3983 | 1 | 11.0844
SING OPN LIN 27 341056-341407(1) | OPEN LINE FROM BUS 341056 [2BARD SHOP T69.000] TO BUS 341407 [2E BARDSTOWN69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.1748 | 9.5532
SING OPN LIN 28 341056-342424(1) | OPEN LINE FROM BUS 341056 [2BARD SHOP T69.000] TO BUS 342424 [2W BARDST J 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.895
SING OPN LIN 29 341059-341275(1) | OPEN LINE FROM BUS 341059 [2BARREN CO 69.000] TO BUS 341275 [2CAVE CITY J69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.5376
SING OPN LIN 30 341059-341542(1) | OPEN LINE FROM BUS 341059 [2BARREN CO 69.000] TO BUS 341542 [2GOODNIGHT 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 4.2467
SING OPN LIN 31 341059-341651(1) | OPEN LINE FROM BUS 341059 [2BARREN CO 69.000] TO BUS 341651 [2HORSECAVE J69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 7.1067
SING OPN LIN 32 341059-342694(1) | OPEN LINE FROM BUS 341059 [2BARREN CO 69.000] TO BUS 342694 [5BARREN CO 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.915
SING OPN LIN 33 341062-341269(1) | OPEN LINE FROM BUS 341062 [2BASS 69.000] TO BUS 341269 [2CASEY CO 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 2.977 | 1 | 4.6051
SING OPN LIN 34 341065-341068(1) | OPEN LINE FROM BUS 341065 [2BEAM 69.000] TO BUS 341068 [2BEAM T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 4.0547 | 1 | 8.1995
SING OPN LIN 35 341068-341215(1) | OPEN LINE FROM BUS 341068 [2BEAM T 69.000] TO BUS 341215 [2BULLITT CO 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.7504
SING OPN LIN 36 341068-342253(1) | OPEN LINE FROM BUS 341068 [2BEAM T 69.000] TO BUS 342253 [2SHEPHEVIL J69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.4905
SING OPN LIN 37 341071-341074(1) | OPEN LINE FROM BUS 341071 [2BEATTYV 69.000] TO BUS 341074 [2BEATTYV D 69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 2.5038 | 26.5091 | 2 | 13.0124
SING OPN LIN 38 341071-341077(1) | OPEN LINE FROM BUS 341071 [2BEATTYV 69.000] TO BUS 341077 [2BEATTYV J 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.8179
SING OPN LIN 39 341071-342520(1) | OPEN LINE FROM BUS 341071 [2BEATTYV 69.000] TO BUS 342520 [2ZACHARIAH 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.9402
SING OPN LIN 40 341074-341992(1) | OPEN LINE FROM BUS 341074 [2BEATTYV D 69.000] TO BUS 341992 [2OAKDALE 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14949 | 7.0093 | 1 | 5.3401
SING OPN LIN 41 341077-341173(1) | OPEN LINE FROM BUS 341077 [2BEATTYV J 69.000] TO BUS 341173 [2BOONEVIL T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.8025
SING OPN LIN 42 341080-341149(1) | OPEN LINE FROM BUS 341080 [2BECKTON 69.000] TO BUS 341149 [2BON AYR 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.6638
SING OPN LIN 43 341080-342445(1) | OPEN LINE FROM BUS 341080 [2BECKTON 69.000] TO BUS 342445 [2W GLASGOW T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.5351
SING OPN LIN 44 341089-342500(1) | OPEN LINE FROM BUS 341089 [2BEKAERT 69.000] TO BUS 342500 [2WIELAND 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.7391
SING OPN LIN 45 341092-341095(1) | OPEN LINE FROM BUS 341092 [2BELLVIEW 69.000] TO BUS 341095 [2BELLVIEW T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.15257 | 7.9358 | 1 | 5.1645
SING OPN LIN 46 341095-341164(1) | OPEN LINE FROM BUS 341095 [2BELLVIEW T 69.000] TO BUS 341164 [2BOONE CO 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.23832 | 9.7496
SING OPN LIN 47 341095-341227(1) | OPEN LINE FROM BUS 341095 [2BELLVIEW T 69.000] TO BUS 341227 [2BURLINGTN T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.20985 | 8.7594
SING OPN LIN 48 341098-342433(1) | OPEN LINE FROM BUS 341098 [2BEREAKU T 69.000] TO BUS 342433 [2W BEREA J 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14437 | 2.2133
SING OPN LIN 49 341104-341107(1) | OPEN LINE FROM BUS 341104 [2BIG BONE 69.000] TO BUS 341107 [2BIG BONE T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 2.5178 | 1 | 3.3535
SING OPN LIN 50 341107-341164(1) | OPEN LINE FROM BUS 341107 [2BIG BONE T 69.000] TO BUS 341164 [2BOONE CO 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.35204 | 13.4779
SING OPN LIN 51 341107-341917(1) | OPEN LINE FROM BUS 341107 [2BIG BONE T 69.000] TO BUS 341917 [2MUNK 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.37552 | 14.69
SING OPN LIN 52 341110-341113(1) | OPEN LINE FROM BUS 341110 [2BIG CREEK 69.000] TO BUS 341113 [2BIG CREEK T69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.15075 | 11.1013 | 2 | 9.4652
SING OPN LIN 53 341110-341439(1) | OPEN LINE FROM BUS 341110 [2BIG CREEK 69.000] TO BUS 341439 [2ELK MT IP 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 3.1273 | 1 | 4.7318
SING OPN LIN 54 341113-341464(1) | OPEN LINE FROM BUS 341113 [2BIG CREEK T69.000] TO BUS 341464 [2FALL ROCK 69.000] CKT 1 | TRUE | Met convergence tolerances | 4 | 2.3419 | 24.9874 | 3 | 11.8301
SING OPN LIN 55 341113-342001(1) | OPEN LINE FROM BUS 341113 [2BIG CREEK T69.000] TO BUS 342001 [2ONEIDA 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14519 | 4.4281 | 1 | 2.365
SING OPN LIN 56 341114-341115(1) | OPEN LINE FROM BUS 341114 [2BIG HILL 69.000] TO BUS 341115 [2BIG HILL T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14416 | 7.3335 | 1 | 5.202
SING OPN LIN 57 341115-342223(1) | OPEN LINE FROM BUS 341115 [2BIG HILL T 69.000] TO BUS 342223 [2SAND GAP T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.6955
SING OPN LIN 58 341115-342346(1) | OPEN LINE FROM BUS 341115 [2BIG HILL T 69.000] TO BUS 342346 [2THREE LINKS69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.9285
SING OPN LIN 59 341116-341119(1) | OPEN LINE FROM BUS 341116 [2BIG WOODS 69.000] TO BUS 341119 [2BIG WOODS J69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.1494 | 9.0737 | 1 | 5.4642
SING OPN LIN 60 341119-341620(1) | OPEN LINE FROM BUS 341119 [2BIG WOODS J69.000] TO BUS 341620 [2HILDA 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.23426 | 8.5536
SING OPN LIN 61 341119-342088(1) | OPEN LINE FROM BUS 341119 [2BIG WOODS J69.000] TO BUS 342088 [2PLUMMR L T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.26496 | 9.9206
SING OPN LIN 62 341122-341125(1) | OPEN LINE FROM BUS 341122 [2BILL WELL T69.000] TO BUS 341125 [2BILL WELLS 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.28272 | 12.7042 | 1 | 7.6338
SING OPN LIN 63 341122-341692(1) | OPEN LINE FROM BUS 341122 [2BILL WELL T69.000] TO BUS 341692 [2JENNY WIL T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.16327 | 6.1067
SING OPN LIN 64 341122-341860(1) | OPEN LINE FROM BUS 341122 [2BILL WELL T69.000] TO BUS 341860 [2MIDDL CRK T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.26169 | 10.2144
SING OPN LIN 65 341131-341134(1) | OPEN LINE FROM BUS 341131 [2BLEVINS V T69.000] TO BUS 341134 [2BLEVINS VAL69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 3.606 | 1 | 2.7272
SING OPN LIN 66 341131-341644(1) | OPEN LINE FROM BUS 341131 [2BLEVINS V T69.000] TO BUS 341644 [2HOPE 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.0298
SING OPN LIN 67 341131-342112(1) | OPEN LINE FROM BUS 341131 [2BLEVINS V T69.000] TO BUS 342112 [2PRESTON T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.8364
SING OPN LIN 68 341137-341296(1) | OPEN LINE FROM BUS 341137 [2BLOOMFLD 69.000] TO BUS 341296 [2CHAPLIN T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.26194 | 11.1778
SING OPN LIN 69 341137-341935(1) | OPEN LINE FROM BUS 341137 [2BLOOMFLD 69.000] TO BUS 341935 [2N SPRINGFLD69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.62576 | 43.2925
SING OPN LIN 70 341140-341143(1) | OPEN LINE FROM BUS 341140 [2BLUE G PW 69.000] TO BUS 341143 [2BLUE G PW T69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 2.1259 | 22.9019 | 1 | 11.2397
SING OPN LIN 71 341143-342019(1) | OPEN LINE FROM BUS 341143 [2BLUE G PW T69.000] TO BUS 342019 [2OWENS IL J 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.2281 | 13.8389
SING OPN LIN 72 341143-342508(1) | OPEN LINE FROM BUS 341143 [2BLUE G PW T69.000] TO BUS 342508 [2WOODLAWN 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.5492 | 16.9483
SING OPN LIN 73 341149-341272(1) | OPEN LINE FROM BUS 341149 [2BON AYR 69.000] TO BUS 341272 [2CAVE CITY 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.8087
SING OPN LIN 74 341152-341155(1) | OPEN LINE FROM BUS 341152 [2BONANZA 69.000] TO BUS 341155 [2BONANZA T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 3.4421 | 1 | 4.0496
SING OPN LIN 75 341155-341803(1) | OPEN LINE FROM BUS 341155 [2BONANZA T 69.000] TO BUS 341803 [2MAGOFFIN CO69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.35493 | 13.8068
SING OPN LIN 76 341155-341860(1) | OPEN LINE FROM BUS 341155 [2BONANZA T 69.000] TO BUS 341860 [2MIDDL CRK T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.31354 | 12.0751
SING OPN LIN 77 341158-341161(1) | OPEN LINE FROM BUS 341158 [2BONNIV DIST69.000] TO BUS 341161 [2BONNIV EK 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.36777 | 16.6896
SING OPN LIN 78 341158-341908(1) | OPEN LINE FROM BUS 341158 [2BONNIV DIST69.000] TO BUS 341908 [2MUNFVIL EK 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.3144 | 17.99
SING OPN LIN 79 341161-342403(1) | OPEN LINE FROM BUS 341161 [2BONNIV EK 69.000] TO BUS 342403 [2UPTON T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 4.1629
SING OPN LIN 80 341164-341167(1) | OPEN LINE FROM BUS 341164 [2BOONE CO 69.000] TO BUS 341167 [2BOONE DIST 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 2.4946 | 26.1415 | 1 | 12.5148
SING OPN LIN 81 341164-342388(1) | OPEN LINE FROM BUS 341164 [2BOONE CO 69.000] TO BUS 342388 [2TURKEY FT J69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.7505
SING OPN LIN 82 341164-342466(1) | OPEN LINE FROM BUS 341164 [2BOONE CO 69.000] TO BUS 342466 [2W R SMOOT 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 2.2648 | 23.8247 | 1 | 23.4435
SING OPN LIN 83 341164-342559(1) | OPEN LINE FROM BUS 341164 [2BOONE CO 69.000] TO BUS 342559 [4BOONE CO 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 6.3181
SING OPN LIN 84 341170-341173(1) | OPEN LINE FROM BUS 341170 [2BOONEVIL 69.000] TO BUS 341173 [2BOONEVIL T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 3.0599 | 1 | 4.449
SING OPN LIN 85 341173-342196(1) | OPEN LINE FROM BUS 341173 [2BOONEVIL T 69.000] TO BUS 342196 [2WHITE OAK 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.0148
SING OPN LIN 86 341179-341746(1) | OPEN LINE FROM BUS 341179 [2BOSTONKU 69.000] TO BUS 341746 [2LEBANON J 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.475
SING OPN LIN 87 341179-342514(1) | OPEN LINE FROM BUS 341179 [2BOSTONKU 69.000] TO BUS 342514 [2WOOSLEY 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.4557
SING OPN LIN 88 341185-341614(1) | OPEN LINE FROM BUS 341185 [2BOWEN 69.000] TO BUS 341614 [2HIGH ROCK 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.44753 | 12.7939
SING OPN LIN 89 341185-342100(1) | OPEN LINE FROM BUS 341185 [2BOWEN 69.000] TO BUS 342100 [2POWELL CO 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.41104 | 9.8646
SING OPN LIN 90 341188-341488(1) | OPEN LINE FROM BUS 341188 [2BRACKEN CO 69.000] TO BUS 341488 [2FOUR OAKS T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.32932 | 8.1914
SING OPN LIN 91 341188-341587(1) | OPEN LINE FROM BUS 341188 [2BRACKEN CO 69.000] TO BUS 341587 [2GRIFFIN J 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 8.5744
SING OPN LIN 92 341194-342385(1) | OPEN LINE FROM BUS 341194 [2BRISTOW 69.000] TO BUS 342385 [2TURKEY FT 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 4.3795
SING OPN LIN 93 341194-342388(1) | OPEN LINE FROM BUS 341194 [2BRISTOW 69.000] TO BUS 342388 [2TURKEY FT J69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 7.8586
SING OPN LIN 94 341197-341818(1) | OPEN LINE FROM BUS 341197 [2BRODHEAD 69.000] TO BUS 341818 [2MARETBURG T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 6.2816
SING OPN LIN 95 341197-342349(1) | OPEN LINE FROM BUS 341197 [2BRODHEAD 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 6.1865
SING OPN LIN 96 341200-341920(1) | OPEN LINE FROM BUS 341200 [2BROMLEYEK 69.000] TO BUS 341920 [2MUNK J 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.1429 | 5.3451
SING OPN LIN 97 341200-342010(1) | OPEN LINE FROM BUS 341200 [2BROMLEYEK 69.000] TO BUS 342010 [2OWEN CO J1 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.17675 | 6.1209
SING OPN LIN 98 341203-341206(1) | OPEN LINE FROM BUS 341203 [2BRONSTON 69.000] TO BUS 341206 [2BRONSTON T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 2.6252 | 27.7795 | 1 | 13.1724
SING OPN LIN 99 341206-341347(1) | OPEN LINE FROM BUS 341206 [2BRONSTON T 69.000] TO BUS 341347 [2COOPER DIST69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.1762
SING OPN LIN 100 341206-341392(1) | OPEN LINE FROM BUS 341206 [2BRONSTON T 69.000] TO BUS 341392 [2DENNY 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.4841
SING OPN LIN 101 341209-341210(1) | OPEN LINE FROM BUS 341209 [2BROUGTWN T 69.000] TO BUS 341210 [2BROUGHT TWN69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 3.0762 | 1 | 4.4578
SING OPN LIN 102 341209-341617(1) | OPEN LINE FROM BUS 341209 [2BROUGTWN T 69.000] TO BUS 341617 [2HIGHLAND EK69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 4.9359
SING OPN LIN 103 341209-342367(1) | OPEN LINE FROM BUS 341209 [2BROUGTWN T 69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 4.6204
SING OPN LIN 104 341212-341774(1) | OPEN LINE FROM BUS 341212 [2BUDD 69.000] TO BUS 341774 [2LOGAN 2 T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.42884 | 33.6067
SING OPN LIN 105 341212-342500(1) | OPEN LINE FROM BUS 341212 [2BUDD 69.000] TO BUS 342500 [2WIELAND 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.18998 | 8.3894
SING OPN LIN 106 341215-341281(1) | OPEN LINE FROM BUS 341215 [2BULLITT CO 69.000] TO BUS 341281 [2CEDAR GR 69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 1.0504 | 9.7887 | 2 | 34.729
SING OPN LIN 107 341215-341389(1) | OPEN LINE FROM BUS 341215 [2BULLITT CO 69.000] TO BUS 341389 [2DEATSVILL T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.0009
SING OPN LIN 108 341215-342700(1) | OPEN LINE FROM BUS 341215 [2BULLITT CO 69.000] TO BUS 342700 [5BULLITT CO 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.96433 | 11.0781
SING OPN LIN 109 341218-341227(1) | OPEN LINE FROM BUS 341218 [2BULLITTSVIL69.000] TO BUS 341227 [2BURLINGTN T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.16929 | 7.6983
SING OPN LIN 110 341218-341605(1) | OPEN LINE FROM BUS 341218 [2BULLITTSVIL69.000] TO BUS 341605 [2HEBRON 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.18013 | 6.8736
SING OPN LIN 111 341224-341227(1) | OPEN LINE FROM BUS 341224 [2BURLINGTN 69.000] TO BUS 341227 [2BURLINGTN T69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.15717 | 10.602 | 1 | 8.1595
SING OPN LIN 112 341233-341974(1) | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 341974 [2NORWOOD T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 4.3007
SING OPN LIN 113 341233-342286(1) | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.3285
SING OPN LIN 114 341248-341608(1) | OPEN LINE FROM BUS 341248 [2CAMPTON 69.000] TO BUS 341608 [2HELECHAW 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 2.2709 | 27.8885
SING OPN LIN 115 341248-342520(1) | OPEN LINE FROM BUS 341248 [2CAMPTON 69.000] TO BUS 342520 [2ZACHARIAH 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 2.2809 | 27.752
SING OPN LIN 116 341251-341254(1) | OPEN LINE FROM BUS 341251 [2CANE RIDG 69.000] TO BUS 341254 [2CANE RIDG T69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14445 | 2.8923 | 1 | 0.37481
SING OPN LIN 117 341254-341872(1) | OPEN LINE FROM BUS 341254 [2CANE RIDG T69.000] TO BUS 341872 [2MILLB-CRL J69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.3988
SING OPN LIN 118 341254-342259(1) | OPEN LINE FROM BUS 341254 [2CANE RIDG T69.000] TO BUS 342259 [2SIDEVIEW 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 2.1897 | 22.4769
SING OPN LIN 119 341260-342013(1) | OPEN LINE FROM BUS 341260 [2CARSON 69.000] TO BUS 342013 [2OWEN CO J2 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.16374 | 8.2944 | 1 | 5.8918
SING OPN LIN 120 341263-341266(1) | OPEN LINE FROM BUS 341263 [2CARTER CTY 69.000] TO BUS 341266 [2CARTER CY T69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 3.2808 | 1 | 3.7198
SING OPN LIN 121 341266-342034(1) | OPEN LINE FROM BUS 341266 [2CARTER CY T69.000] TO BUS 342034 [2PACTOLUS T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.1747 | 10.8584
SING OPN LIN 122 341266-342475(1) | OPEN LINE FROM BUS 341266 [2CARTER CY T69.000] TO BUS 342475 [2WARNOCK 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.15708 | 11.5954
SING OPN LIN 123 341269-342064(1) | OPEN LINE FROM BUS 341269 [2CASEY CO 69.000] TO BUS 342064 [2PEYTONS ST 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.7435
SING OPN LIN 124 341269-342703(1) | OPEN LINE FROM BUS 341269 [2CASEY CO 69.000] TO BUS 342703 [5CASEY CO 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 4.0027
SING OPN LIN 125 341272-341275(1) | OPEN LINE FROM BUS 341272 [2CAVE CITY 69.000] TO BUS 341275 [2CAVE CITY J69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.5804
SING OPN LIN 126 341275-342241(1) | OPEN LINE FROM BUS 341275 [2CAVE CITY J69.000] TO BUS 342241 [2SEYMOUR T 69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.14287 | 2.7972 | 1 | 3.7942
SING OPN LIN 127 341281-342082(1) | OPEN LINE FROM BUS 341281 [2CEDAR GR 69.000] TO BUS 342082 [2PLEAS GRV 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 1.3868 | 14.0997 | 1 | 26.1472
SING OPN LIN 128 341287-341713(1) | OPEN LINE FROM BUS 341287 [2CENT HARDIN69.000] TO BUS 341713 [2KARGLE 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.3817 | 16.258
SING OPN LIN 129 341287-342307(1) | OPEN LINE FROM BUS 341287 [2CENT HARDIN69.000] TO BUS 342307 [2STEPHENSBRG69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.4447 | 8.8383
SING OPN LIN 130 341287-342568(1) | OPEN LINE FROM BUS 341287 [2CENT HARDIN69.000] TO BUS 342568 [4CENT HARDIN138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.1131 | 12.7334
SING OPN LIN 131 341293-341296(1) | OPEN LINE FROM BUS 341293 [2CHAPLIN 69.000] TO BUS 341296 [2CHAPLIN T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14492 | 3.7232 | 1 | 1.4053
SING OPN LIN 132 341296-342262(1) | OPEN LINE FROM BUS 341296 [2CHAPLIN T 69.000] TO BUS 342262 [2SINAI 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.29591 | 11.6351
SING OPN LIN 133 341299-341989(1) | OPEN LINE FROM BUS 341299 [2CHARTERS 69.000] TO BUS 341989 [2OAK RIDGE T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 5.2941
SING OPN LIN 134 341299-342124(1) | OPEN LINE FROM BUS 341299 [2CHARTERS 69.000] TO BUS 342124 [2RECTORVILLE69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 5.1713
SING OPN LIN 135 341302-341305(1) | OPEN LINE FROM BUS 341302 [2CLAY CITY 69.000] TO BUS 341305 [2CLAY CITY T69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.15313 | 12.0632 | 1 | 8.5542
SING OPN LIN 136 341305-341593(1) | OPEN LINE FROM BUS 341305 [2CLAY CITY T69.000] TO BUS 341593 [2HARDWCRK T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 4.0365
SING OPN LIN 137 341305-341599(1) | OPEN LINE FROM BUS 341305 [2CLAY CITY T69.000] TO BUS 341599 [2HARGETT T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 4.5125
SING OPN LIN 138 341308-341314(1) | OPEN LINE FROM BUS 341308 [2CLAY LCK 69.000] TO BUS 341314 [2CLAY LCK SW69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14687 | 8.5717 | 1 | 6.1845
SING OPN LIN 139 341311-341314(1) | OPEN LINE FROM BUS 341311 [2CLAY LCK J 69.000] TO BUS 341314 [2CLAY LCK SW69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.14686 | 8.5723 | 1 | 6.1845
SING OPN LIN 140 341311-342184(1) | OPEN LINE FROM BUS 341311 [2CLAY LCK J 69.000] TO BUS 342184 [2S ANDERSON 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.9088 | 20.9034
SING OPN LIN 141 341311-342406(1) | OPEN LINE FROM BUS 341311 [2CLAY LCK J 69.000] TO BUS 342406 [2VAN ARSDELL69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 2.1302 | 22.8401
SING OPN LIN 142 341317-341390(1) | OPEN LINE FROM BUS 341317 [2CLAY VILLAG69.000] TO BUS 341390 [2DEFOE TAP 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 4.0952
SING OPN LIN 143 341320-341512(1) | OPEN LINE FROM BUS 341320 [2COBURG 69.000] TO BUS 341512 [2GARLIN T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.98272 | 12.3521
SING OPN LIN 144 341323-341335(1) | OPEN LINE FROM BUS 341323 [2COBURG J 69.000] TO BUS 341335 [2COLUMBIA 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.2082
SING OPN LIN 145 341323-341512(1) | OPEN LINE FROM BUS 341323 [2COBURG J 69.000] TO BUS 341512 [2GARLIN T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.50477 | 36.9276
SING OPN LIN 146 341323-342235(1) | OPEN LINE FROM BUS 341323 [2COBURG J 69.000] TO BUS 342235 [2SEWELTN J 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 7.7799
SING OPN LIN 147 341326-341488(1) | OPEN LINE FROM BUS 341326 [2COLEMANSVIL69.000] TO BUS 341488 [2FOUR OAKS T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 6.4511
SING OPN LIN 148 341326-342133(1) | OPEN LINE FROM BUS 341326 [2COLEMANSVIL69.000] TO BUS 342133 [2RENAKER 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.30934 | 7.7015
SING OPN LIN 149 341329-341332(1) | OPEN LINE FROM BUS 341329 [2COLESBURG 69.000] TO BUS 341332 [2COLESBURG J69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14638 | 4.8592 | 1 | 2.9494
SING OPN LIN 150 341332-341944(1) | OPEN LINE FROM BUS 341332 [2COLESBURG J69.000] TO BUS 341944 [2NELSON CO 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.532
SING OPN LIN 151 341332-342155(1) | OPEN LINE FROM BUS 341332 [2COLESBURG J69.000] TO BUS 342155 [2ROANOKE T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.5065
SING OPN LIN 152 341335-341370(1) | OPEN LINE FROM BUS 341335 [2COLUMBIA 69.000] TO BUS 341370 [2COLUMB S KU69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.79845 | 16.8849 | 2 | 10.7
SING OPN LIN 153 341335-342436(1) | OPEN LINE FROM BUS 341335 [2COLUMBIA 69.000] TO BUS 342436 [2W COLUMBI T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 4.1363
SING OPN LIN 154 341338-341341(1) | OPEN LINE FROM BUS 341338 [2CONWAY 69.000] TO BUS 341341 [2CONWAY T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 3.0869 | 1 | 4.2596
SING OPN LIN 155 341341-342346(1) | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342346 [2THREE LINKS69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 4.0782
SING OPN LIN 156 341341-342349(1) | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 4.3078
SING OPN LIN 157 341342-341343(1) | OPEN LINE FROM BUS 341342 [2CONTOWN T 69.000] TO BUS 341343 [2CONTOWN 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14318 | 4.4552 | 1 | 2.2548
SING OPN LIN 158 341342-341761(1) | OPEN LINE FROM BUS 341342 [2CONTOWN T 69.000] TO BUS 341761 [2LIBERTY J 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.9883
SING OPN LIN 159 341342-342067(1) | OPEN LINE FROM BUS 341342 [2CONTOWN T 69.000] TO BUS 342067 [2PHIL 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.0796
SING OPN LIN 160 341344-341347(1) | OPEN LINE FROM BUS 341344 [2COOPER 69.000] TO BUS 341347 [2COOPER DIST69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.1754
SING OPN LIN 161 341344-342286(1) | OPEN LINE FROM BUS 341344 [2COOPER 69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.1629
SING OPN LIN 162 341344-342286(2) | OPEN LINE FROM BUS 341344 [2COOPER 69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 2 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.1629
SING OPN LIN 163 341344-342715(1) | OPEN LINE FROM BUS 341344 [2COOPER 69.000] TO BUS 342715 [5COOPER1 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.3572
SING OPN LIN 164 341350-342067(1) | OPEN LINE FROM BUS 341350 [2CRESTON 69.000] TO BUS 342067 [2PHIL 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14177 | 8.0067 | 1 | 5.7798
SING OPN LIN 165 341353-341356(1) | OPEN LINE FROM BUS 341353 [2CROCKETT 69.000] TO BUS 341356 [2CROCKETT T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 2.7865 | 1 | 3.3314
SING OPN LIN 166 341356-341653(1) | OPEN LINE FROM BUS 341356 [2CROCKETT T 69.000] TO BUS 341653 [2HOT MIX R T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.0977 | 7.8442
SING OPN LIN 167 341356-342265(1) | OPEN LINE FROM BUS 341356 [2CROCKETT T 69.000] TO BUS 342265 [2SKAGGS 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.0909 | 7.7666
SING OPN LIN 168 341359-341362(1) | OPEN LINE FROM BUS 341359 [2CROOKSVIL 69.000] TO BUS 341362 [2CROOKSVIL T69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.81842 | 19.6916 | 2 | 7.195
SING OPN LIN 169 341359-342288(1) | OPEN LINE FROM BUS 341359 [2CROOKSVIL 69.000] TO BUS 342288 [2SPEEDWELL 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14453 | 3.5378 | 1 | 1.3
SING OPN LIN 170 341362-341406(1) | OPEN LINE FROM BUS 341362 [2CROOKSVIL T69.000] TO BUS 341406 [2DUNCAN LN T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.6377
SING OPN LIN 171 341362-341611(1) | OPEN LINE FROM BUS 341362 [2CROOKSVIL T69.000] TO BUS 341611 [2HICKORY PL 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.18305 | 4.227
SING OPN LIN 172 341366-341370(1) | OPEN LINE FROM BUS 341366 [2COLUMB KU 69.000] TO BUS 341370 [2COLUMB S KU69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.53001 | 11.8639 | 1 | 6.29
SING OPN LIN 173 341377-342355(1) | OPEN LINE FROM BUS 341377 [2CYNTHIA TIE69.000] TO BUS 342355 [2THREE M T 69.000] CKT 1 | FALSE | Blown up | 0 | 1011.6628 | 13128.6211
SING OPN LIN 174 341377-936380(1) | OPEN LINE FROM BUS 341377 [2CYNTHIA TIE69.000] TO BUS 936380 [AD2-048 TAP 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.82513 | 9.9629
SING OPN LIN 175 341379-342256(1) | OPEN LINE FROM BUS 341379 [2DAHL ROAD 69.000] TO BUS 342256 [2SHOPVILLE 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.26411 | 6.5384
SING OPN LIN 176 341380-341959(1) | OPEN LINE FROM BUS 341380 [2DALE 69.000] TO BUS 341959 [2NEWBY 1 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14522 | 2.6358
SING OPN LIN 177 341380-341962(1) | OPEN LINE FROM BUS 341380 [2DALE 69.000] TO BUS 341962 [2NEWBY 2 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.5515
SING OPN LIN 178 341380-342574(1) | OPEN LINE FROM BUS 341380 [2DALE 69.000] TO BUS 342574 [4DALE 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.4403
SING OPN LIN 179 341381-341382(1) | OPEN LINE FROM BUS 341381 [2DAV LANE 69.000] TO BUS 341382 [2DAV LANE T 69.000] CKT 1 | TRUE | Met convergence tolerances | 3 | 0.15521 | 9.7136 | 1 | 9.26
SING OPN LIN 180 341381-341930(1) | OPEN LINE FROM BUS 341381 [2DAV LANE 69.000] TO BUS 341930 [2N LONDON T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.7699
SING OPN LIN 181 341381-342452(1) | OPEN LINE FROM BUS 341381 [2DAV LANE 69.000] TO BUS 342452 [2W LONDON T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14708 | 3.0493
SING OPN LIN 182 341382-341734(1) | OPEN LINE FROM BUS 341382 [2DAV LANE T 69.000] TO BUS 341734 [2LAUR C IP T69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.15521 | 9.7207 | 1 | 9.26
SING OPN LIN 183 341383-341467(1) | OPEN LINE FROM BUS 341383 [2DAVIS 69.000] TO BUS 341467 [2FAYETTE 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.6383 | 41.6413
SING OPN LIN 184 341383-341965(1) | OPEN LINE FROM BUS 341383 [2DAVIS 69.000] TO BUS 341965 [2NICHOLASVIL69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 8.0828
SING OPN LIN 185 341386-341389(1) | OPEN LINE FROM BUS 341386 [2DEATSVIL 69.000] TO BUS 341389 [2DEATSVILL T69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.21044 | 9.694 | 1 | 7.9864
SING OPN LIN 186 341389-341707(1) | OPEN LINE FROM BUS 341389 [2DEATSVILL T69.000] TO BUS 341707 [2JOE TICH T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.6847
SING OPN LIN 187 341390-341391(1) | OPEN LINE FROM BUS 341390 [2DEFOE TAP 69.000] TO BUS 341391 [2DEFOE 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 3.537 | 1 | 4.021
SING OPN LIN 188 341390-341950(1) | OPEN LINE FROM BUS 341390 [2DEFOE TAP 69.000] TO BUS 341950 [2NEW CASTLE 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 4.6054
SING OPN LIN 189 341392-341578(1) | OPEN LINE FROM BUS 341392 [2DENNY 69.000] TO BUS 341578 [2GREGORY R T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.19607 | 10.1062
SING OPN LIN 190 341392-342499(1) | OPEN LINE FROM BUS 341392 [2DENNY 69.000] TO BUS 342499 [2WIBORG T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.15756 | 5.8024
SING OPN LIN 191 341392-342727(1) | OPEN LINE FROM BUS 341392 [2DENNY 69.000] TO BUS 342727 [5DENNY 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.5064
SING OPN LIN 192 341394-341479(1) | OPEN LINE FROM BUS 341394 [2PATRIOT PW 69.000] TO BUS 341479 [2S BOUND RD 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.17359 | 7.8269 | 1 | 6.5271
SING OPN LIN 193 341394-342151(1) | OPEN LINE FROM BUS 341394 [2PATRIOT PW 69.000] TO BUS 342151 [2RINEYVILLE 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 1.7295 | 16.1695 | 1 | 5.6071
SING OPN LIN 194 341394-342157(1) | OPEN LINE FROM BUS 341394 [2PATRIOT PW 69.000] TO BUS 342157 [2ROGERSVIL J69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.4124
SING OPN LIN 195 341394-342274(1) | OPEN LINE FROM BUS 341394 [2PATRIOT PW 69.000] TO BUS 342274 [2SMITHRVIL T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.4104
SING OPN LIN 196 341398-341605(1) | OPEN LINE FROM BUS 341398 [2DOWNING 69.000] TO BUS 341605 [2HEBRON 69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 1.1956 | 12.6943 | 2 | 23.5626
SING OPN LIN 197 341398-341880(1) | OPEN LINE FROM BUS 341398 [2DOWNING 69.000] TO BUS 341880 [2MINEOLA PKE69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 2.4643 | 25.8297 | 1 | 12.222
SING OPN LIN 198 341400-342091(1) | OPEN LINE FROM BUS 341400 [2DRAVO 69.000] TO BUS 342091 [2PLUMVILLE 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14711 | 5.2151 | 1 | 2.641
SING OPN LIN 199 341401-341842(1) | OPEN LINE FROM BUS 341401 [2DURO 69.000] TO BUS 341842 [2MBUSA T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.17721 | 11.7922 | 1 | 8.9714
SING OPN LIN 200 341404-341842(1) | OPEN LINE FROM BUS 341404 [2DURO T 69.000] TO BUS 341842 [2MBUSA T 69.000] CKT 1 | TRUE | Met convergence tolerances | 3 | 1.2092 | 12.7612 | 2 | 23.5079
SING OPN LIN 201 341404-342295(1) | OPEN LINE FROM BUS 341404 [2DURO T 69.000] TO BUS 342295 [2STANLY P J169.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 7.1327
SING OPN LIN 202 341404-342388(1) | OPEN LINE FROM BUS 341404 [2DURO T 69.000] TO BUS 342388 [2TURKEY FT J69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 5.2795
SING OPN LIN 203 341405-341406(1) | OPEN LINE FROM BUS 341405 [2DUNCANNO LN69.000] TO BUS 341406 [2DUNCAN LN T69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 2.9805 | 1 | 3.7451
SING OPN LIN 204 341407-342019(1) | OPEN LINE FROM BUS 341407 [2E BARDSTOWN69.000] TO BUS 342019 [2OWENS IL J 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.032 | 11.9015
SING OPN LIN 205 341410-341929(1) | OPEN LINE FROM BUS 341410 [2E BERNSTADT69.000] TO BUS 341929 [2N LONDON 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.15103 | 7.7821 | 1 | 6.944
SING OPN LIN 206 341416-342076(1) | OPEN LINE FROM BUS 341416 [2E PINE KNOT69.000] TO BUS 342076 [2PINE KNOT 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 2.5237 | 1 | 4.2639
SING OPN LIN 207 341419-341422(1) | OPEN LINE FROM BUS 341419 [2E SOMERSE T69.000] TO BUS 341422 [2E SOMERSET 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14231 | 9.5732 | 1 | 8.3699
SING OPN LIN 208 341419-341941(1) | OPEN LINE FROM BUS 341419 [2E SOMERSE T69.000] TO BUS 341941 [2NELSN VAL T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.376
SING OPN LIN 209 341419-341974(1) | OPEN LINE FROM BUS 341419 [2E SOMERSE T69.000] TO BUS 341974 [2NORWOOD T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.6553
SING OPN LIN 210 341425-341428(1) | OPEN LINE FROM BUS 341425 [2EBERLE 69.000] TO BUS 341428 [2EBERLE T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 3.6821 | 1 | 4.738
SING OPN LIN 211 341428-341809(1) | OPEN LINE FROM BUS 341428 [2EBERLE T 69.000] TO BUS 341809 [2MAPLESVIL T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.7366
SING OPN LIN 212 341431-341434(1) | OPEN LINE FROM BUS 341431 [2EDM-JBGAL J69.000] TO BUS 341434 [2EDM-JBGAL T69.000] CKT 1 | TRUE | Met convergence tolerances | 3 | 0.28398 | 14.8764 | 2 | 8.9524
SING OPN LIN 213 341431-341728(1) | OPEN LINE FROM BUS 341431 [2EDM-JBGAL J69.000] TO BUS 341728 [2KNOB LICK 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.8382 | 17.1318
SING OPN LIN 214 341431-342322(1) | OPEN LINE FROM BUS 341431 [2EDM-JBGAL J69.000] TO BUS 342322 [2SUMM SHADE 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.81144 | 8.9924
SING OPN LIN 215 341434-341437(1) | OPEN LINE FROM BUS 341434 [2EDM-JBGAL T69.000] TO BUS 341437 [2EDMON IND P69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14405 | 4.3595 | 1 | 1.5349
SING OPN LIN 216 341434-341680(1) | OPEN LINE FROM BUS 341434 [2EDM-JBGAL T69.000] TO BUS 341680 [2JB GALLOWAY69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.23415 | 12.697 | 1 | 7.4175
SING OPN LIN 217 341443-341446(1) | OPEN LINE FROM BUS 341443 [2ELLIO CO PT69.000] TO BUS 341446 [2ELLIOT CO P69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 2.0734 | 21.9677 | 1 | 10.6457
SING OPN LIN 218 341443-341953(1) | OPEN LINE FROM BUS 341443 [2ELLIO CO PT69.000] TO BUS 341953 [2NEW FOUNDL 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.3487 | 11.836
SING OPN LIN 219 341449-342163(1) | OPEN LINE FROM BUS 341449 [2ELLIOTTVILL69.000] TO BUS 342163 [2ROWAN CO 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.15155 | 9.191 | 1 | 6.2363
SING OPN LIN 220 341455-341458(1) | OPEN LINE FROM BUS 341455 [2ETOWN EK1 69.000] TO BUS 341458 [2ETOWN EK2 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.5561
SING OPN LIN 221 341455-342274(1) | OPEN LINE FROM BUS 341455 [2ETOWN EK1 69.000] TO BUS 342274 [2SMITHRVIL T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.1735
SING OPN LIN 222 341455-342379(1) | OPEN LINE FROM BUS 341455 [2ETOWN EK1 69.000] TO BUS 342379 [2TUNNEL H T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.6453
SING OPN LIN 223 341458-342340(1) | OPEN LINE FROM BUS 341458 [2ETOWN EK2 69.000] TO BUS 342340 [2THARP T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.892
SING OPN LIN 224 341461-341797(1) | OPEN LINE FROM BUS 341461 [2FALCON EK 69.000] TO BUS 341797 [2MAGGARD 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.26403 | 12.1895
SING OPN LIN 225 341461-342310(1) | OPEN LINE FROM BUS 341461 [2FALCON EK 69.000] TO BUS 342310 [2SUBLETT 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 8.7234
SING OPN LIN 226 341464-341569(1) | OPEN LINE FROM BUS 341464 [2FALL ROCK 69.000] TO BUS 341569 [2GREENBRIA T69.000] CKT 1 | TRUE | Met convergence tolerances | 5 | 0.14692 | 9.0486 | 1 | 7.3931
SING OPN LIN 227 341464-342391(1) | OPEN LINE FROM BUS 341464 [2FALL ROCK 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.5249
SING OPN LIN 228 341464-342730(1) | OPEN LINE FROM BUS 341464 [2FALL ROCK 69.000] TO BUS 342730 [5FALL ROCK 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14717 | 3.1866
SING OPN LIN 229 341467-342580(1) | OPEN LINE FROM BUS 341467 [2FAYETTE 69.000] TO BUS 342580 [4FAYETTE 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.8279 | 11.2474
SING OPN LIN 230 341470-341473(1) | OPEN LINE FROM BUS 341470 [2FLOYD EK 69.000] TO BUS 341473 [2FLOYD-SFL T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.6196
SING OPN LIN 231 341470-342511(1) | OPEN LINE FROM BUS 341470 [2FLOYD EK 69.000] TO BUS 342511 [2WOODSTOCK 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.7864
SING OPN LIN 232 341473-342115(1) | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.3541
SING OPN LIN 233 341473-342193(1) | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342193 [2S FLOYD 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14341 | 8.3768 | 1 | 7.0517
SING OPN LIN 234 341476-341899(1) | OPEN LINE FROM BUS 341476 [2FOGG PIKE 69.000] TO BUS 341899 [2MT STERLING69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 3.7828 | 1 | 4.504
SING OPN LIN 235 341476-342130(1) | OPEN LINE FROM BUS 341476 [2FOGG PIKE 69.000] TO BUS 342130 [2REID VILLAG69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 1.1613 | 10.0447 | 1 | 4.504
SING OPN LIN 236 341485-341488(1) | OPEN LINE FROM BUS 341485 [2FOUR OAKS 69.000] TO BUS 341488 [2FOUR OAKS T69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 1.0811 | 12.7434 | 2 | 11.1208
SING OPN LIN 237 341485-341550(1) | OPEN LINE FROM BUS 341485 [2FOUR OAKS 69.000] TO BUS 341550 [2FALMOUTH KU69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.27458 | 9.1196 | 1 | 4.56
SING OPN LIN 238 341491-341548(1) | OPEN LINE FROM BUS 341491 [2FOX HOLLOW 69.000] TO BUS 341548 [2GORIN PRK J69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.8317
SING OPN LIN 239 341491-342037(1) | OPEN LINE FROM BUS 341491 [2FOX HOLLOW 69.000] TO BUS 342037 [2PARKWAY 1 69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 2.4159 | 25.5805 | 2 | 12.671
SING OPN LIN 240 341491-342043(1) | OPEN LINE FROM BUS 341491 [2FOX HOLLOW 69.000] TO BUS 342043 [2PARKWAY 2 T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 4.7264
SING OPN LIN 241 341491-342049(1) | OPEN LINE FROM BUS 341491 [2FOX HOLLOW 69.000] TO BUS 342049 [2PATTON RD J69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.84606 | 10.198
SING OPN LIN 242 341491-342732(1) | OPEN LINE FROM BUS 341491 [2FOX HOLLOW 69.000] TO BUS 342732 [5FOX HOLLOW 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.0135 | 11.8387
SING OPN LIN 243 341494-341497(1) | OPEN LINE FROM BUS 341494 [2FREDRIKBG T69.000] TO BUS 341497 [2FREDRIKBRG 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.66462 | 16.3494 | 1 | 4.135
SING OPN LIN 244 341494-341935(1) | OPEN LINE FROM BUS 341494 [2FREDRIKBG T69.000] TO BUS 341935 [2N SPRINGFLD69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.34683 | 11.6407
SING OPN LIN 245 341494-342508(1) | OPEN LINE FROM BUS 341494 [2FREDRIKBG T69.000] TO BUS 342508 [2WOODLAWN 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.0027 | 11.619
SING OPN LIN 246 341500-341644(1) | OPEN LINE FROM BUS 341500 [2FRENCHBURG 69.000] TO BUS 341644 [2HOPE 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 2.5577 | 26.5305
SING OPN LIN 247 341500-341824(1) | OPEN LINE FROM BUS 341500 [2FRENCHBURG 69.000] TO BUS 341824 [2MARIBA T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 2.1829 | 22.8928
SING OPN LIN 248 341503-341506(1) | OPEN LINE FROM BUS 341503 [2GAP OF RG T69.000] TO BUS 341506 [2GAP OF RIDG69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.1421 | 10.5202 | 1 | 9.8439
SING OPN LIN 249 341503-341578(1) | OPEN LINE FROM BUS 341503 [2GAP OF RG T69.000] TO BUS 341578 [2GREGORY R T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.22568 | 10.4218
SING OPN LIN 250 341503-341887(1) | OPEN LINE FROM BUS 341503 [2GAP OF RG T69.000] TO BUS 341887 [2MONTICELLO 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.15238 | 10.3743
SING OPN LIN 251 341509-341512(1) | OPEN LINE FROM BUS 341509 [2GARLIN 69.000] TO BUS 341512 [2GARLIN T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14195 | 8.6636 | 1 | 5.8713
SING OPN LIN 252 341515-341732(1) | OPEN LINE FROM BUS 341515 [2GARRARD CO 69.000] TO BUS 341732 [2LANCASTER T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.6191
SING OPN LIN 253 341515-942410(1) | OPEN LINE FROM BUS 341515 [2GARRARD CO 69.000] TO BUS 942410 [AE2-254 TAP 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.90413 | 11.1473
SING OPN LIN 254 341518-341521(1) | OPEN LINE FROM BUS 341518 [2GARRARD KU 69.000] TO BUS 341521 [2GARRARDKU T69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14443 | 2.2773
SING OPN LIN 255 341521-341806(1) | OPEN LINE FROM BUS 341521 [2GARRARDKU T69.000] TO BUS 341806 [2MANCHESTER 69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.14435 | 2.2885
SING OPN LIN 256 341530-342043(1) | OPEN LINE FROM BUS 341530 [2GLASGO-CLEV69.000] TO BUS 342043 [2PARKWAY 2 T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 4.7875
SING OPN LIN 257 341530-342445(1) | OPEN LINE FROM BUS 341530 [2GLASGO-CLEV69.000] TO BUS 342445 [2W GLASGOW T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 4.7715
SING OPN LIN 258 341533-341632(1) | OPEN LINE FROM BUS 341533 [2GLENDALE 69.000] TO BUS 341632 [2HODGENVILLE69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.42578 | 14.5046
SING OPN LIN 259 341533-342307(1) | OPEN LINE FROM BUS 341533 [2GLENDALE 69.000] TO BUS 342307 [2STEPHENSBRG69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.1034 | 31.0399
SING OPN LIN 260 341536-341623(1) | OPEN LINE FROM BUS 341536 [2GODDARD 69.000] TO BUS 341623 [2HILLSBORO 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.5945 | 17.2849
SING OPN LIN 261 341536-341989(1) | OPEN LINE FROM BUS 341536 [2GODDARD 69.000] TO BUS 341989 [2OAK RIDGE T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 5.7996
SING OPN LIN 262 341536-342088(1) | OPEN LINE FROM BUS 341536 [2GODDARD 69.000] TO BUS 342088 [2PLUMMR L T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 4.717
SING OPN LIN 263 341536-342589(1) | OPEN LINE FROM BUS 341536 [2GODDARD 69.000] TO BUS 342589 [4GODDARD 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 4.4414
SING OPN LIN 264 341539-341686(1) | OPEN LINE FROM BUS 341539 [2GOLDBUG 69.000] TO BUS 341686 [2JELLICO C T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 4.2415
SING OPN LIN 265 341542-341548(1) | OPEN LINE FROM BUS 341542 [2GOODNIGHT 69.000] TO BUS 341548 [2GORIN PRK J69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.898
SING OPN LIN 266 341551-341587(1) | OPEN LINE FROM BUS 341551 [2GRANTS LICK69.000] TO BUS 341587 [2GRIFFIN J 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 7.0475
SING OPN LIN 267 341551-342298(1) | OPEN LINE FROM BUS 341551 [2GRANTS LICK69.000] TO BUS 342298 [2STANLY P J269.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.15062 | 5.7924
SING OPN LIN 268 341554-341752(1) | OPEN LINE FROM BUS 341554 [2GRAYSON J 69.000] TO BUS 341752 [2LEON 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.28149 | 9.1317
SING OPN LIN 269 341554-342034(1) | OPEN LINE FROM BUS 341554 [2GRAYSON J 69.000] TO BUS 342034 [2PACTOLUS T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.20754 | 7.8311
SING OPN LIN 270 341563-341575(1) | OPEN LINE FROM BUS 341563 [2GREEN CO 69.000] TO BUS 341575 [2GREENSBURG 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.99675 | 16.5564
SING OPN LIN 271 341563-342325(1) | OPEN LINE FROM BUS 341563 [2GREEN CO 69.000] TO BUS 342325 [2SUMMERSVIL 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14228 | 10.2909
SING OPN LIN 272 341563-342733(1) | OPEN LINE FROM BUS 341563 [2GREEN CO 69.000] TO BUS 342733 [5GREEN CO 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.18668 | 6.3719
SING OPN LIN 273 341569-341572(1) | OPEN LINE FROM BUS 341569 [2GREENBRIA T69.000] TO BUS 341572 [2GREENBRIAR 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14712 | 8.9296 | 1 | 7.3931
SING OPN LIN 274 341569-341806(1) | OPEN LINE FROM BUS 341569 [2GREENBRIA T69.000] TO BUS 341806 [2MANCHESTER 69.000] CKT 1 | TRUE | Met convergence tolerances | 3 | 0.14428 | 2.3027
SING OPN LIN 275 341575-341854(1) | OPEN LINE FROM BUS 341575 [2GREENSBURG 69.000] TO BUS 341854 [2MCKINNY T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 2.7139 | 28.1302
SING OPN LIN 276 341578-341581(1) | OPEN LINE FROM BUS 341578 [2GREGORY R T69.000] TO BUS 341581 [2GREGORY RD 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14378 | 3.7808 | 1 | 1.8519
SING OPN LIN 277 341584-341587(1) | OPEN LINE FROM BUS 341584 [2GRIFFIN 69.000] TO BUS 341587 [2GRIFFIN J 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.23744 | 12.3455 | 1 | 7.6275
SING OPN LIN 278 341590-341593(1) | OPEN LINE FROM BUS 341590 [2HARDWCRK 69.000] TO BUS 341593 [2HARDWCRK T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14505 | 4.4041 | 1 | 1.8746
SING OPN LIN 279 341593-342301(1) | OPEN LINE FROM BUS 341593 [2HARDWCRK T 69.000] TO BUS 342301 [2STANTON 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 4.0079
SING OPN LIN 280 341596-341599(1) | OPEN LINE FROM BUS 341596 [2HARGETT 69.000] TO BUS 341599 [2HARGETT T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 4.478 | 1 | 3.9751
SING OPN LIN 281 341599-342370(1) | OPEN LINE FROM BUS 341599 [2HARGETT T 69.000] TO BUS 342370 [2TRAPP 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 5.6906
SING OPN LIN 282 341602-341872(1) | OPEN LINE FROM BUS 341602 [2HEADQTRS 69.000] TO BUS 341872 [2MILLB-CRL J69.000] CKT 1 | FALSE | Blown up | 0 | 20371.7949 | 261129.6719
SING OPN LIN 283 341602-342280(1) | OPEN LINE FROM BUS 341602 [2HEADQTRS 69.000] TO BUS 342280 [2SNOW HILL 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.6213 | 21.2842
SING OPN LIN 284 341602-936380(1) | OPEN LINE FROM BUS 341602 [2HEADQTRS 69.000] TO BUS 936380 [AD2-048 TAP 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 2.0304 | 22.5701
SING OPN LIN 285 341605-342595(1) | OPEN LINE FROM BUS 341605 [2HEBRON 69.000] TO BUS 342595 [4HEBRON 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.0177
SING OPN LIN 286 341608-342313(1) | OPEN LINE FROM BUS 341608 [2HELECHAW 69.000] TO BUS 342313 [2SUBLETT J 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.32021 | 12.2429
SING OPN LIN 287 341611-342103(1) | OPEN LINE FROM BUS 341611 [2HICKORY PL 69.000] TO BUS 342103 [2PPG 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.1142
SING OPN LIN 288 341614-342520(1) | OPEN LINE FROM BUS 341614 [2HIGH ROCK 69.000] TO BUS 342520 [2ZACHARIAH 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.46003 | 12.8555
SING OPN LIN 289 341617-341896(1) | OPEN LINE FROM BUS 341617 [2HIGHLAND EK69.000] TO BUS 341896 [2MT OLIVE J 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 5.3163
SING OPN LIN 290 341620-342163(1) | OPEN LINE FROM BUS 341620 [2HILDA 69.000] TO BUS 342163 [2ROWAN CO 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 4.0648
SING OPN LIN 291 341623-342052(1) | OPEN LINE FROM BUS 341623 [2HILLSBORO 69.000] TO BUS 342052 [2PEASTICKS 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.2993
SING OPN LIN 292 341632-341800(1) | OPEN LINE FROM BUS 341632 [2HODGENVILLE69.000] TO BUS 341800 [2MAGNOLIA 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.60811 | 7.9061
SING OPN LIN 293 341632-342316(1) | OPEN LINE FROM BUS 341632 [2HODGENVILLE69.000] TO BUS 342316 [2SULPHUR CRK69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 2.0497 | 22.4401
SING OPN LIN 294 341638-342199(1) | OPEN LINE FROM BUS 341638 [2HOLLOWAY J 69.000] TO BUS 342199 [2S JESSAM J 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 4.2051
SING OPN LIN 295 341638-342463(1) | OPEN LINE FROM BUS 341638 [2HOLLOWAY J 69.000] TO BUS 342463 [2W NICHVIL T69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 2.1828 | 23.1007 | 1 | 23.1559
SING OPN LIN 296 341641-341887(1) | OPEN LINE FROM BUS 341641 [2HOMESTEAD S69.000] TO BUS 341887 [2MONTICELLO 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 2.7578 | 29.0872 | 1 | 14.1787
SING OPN LIN 297 341644-341683(1) | OPEN LINE FROM BUS 341644 [2HOPE 69.000] TO BUS 341683 [2JEFFERSNVIL69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.4434 | 16.25
SING OPN LIN 298 341647-341650(1) | OPEN LINE FROM BUS 341647 [2HORSE CV KU69.000] TO BUS 341650 [2HORSECAVE T69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 1.3538 | 19.6208 | 1 | 46.06
SING OPN LIN 299 341650-341651(Z1) | OPEN LINE FROM BUS 341650 [2HORSECAVE T69.000] TO BUS 341651 [2HORSECAVE J69.000] CKT Z1 | TRUE | Met convergence tolerances | 2 | 1.3538 | 19.6195 | 1 | 46.06
SING OPN LIN 300 341651-341914(1) | OPEN LINE FROM BUS 341651 [2HORSECAVE J69.000] TO BUS 341914 [2MUNFVILKU T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.1333 | 13.9949
SING OPN LIN 301 341653-341656(1) | OPEN LINE FROM BUS 341653 [2HOT MIX R T69.000] TO BUS 341656 [2HOT MIX RD 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.47649 | 8.646 | 1 | 5.3326
SING OPN LIN 302 341653-341890(1) | OPEN LINE FROM BUS 341653 [2HOT MIX R T69.000] TO BUS 341890 [2MORGAN CO 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.1751 | 9.5283
SING OPN LIN 303 341659-341662(1) | OPEN LINE FROM BUS 341659 [2HT ADAMS 69.000] TO BUS 341662 [2HT ADAMS T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14552 | 2.8193 | 1 | 6.0761
SING OPN LIN 304 341662-341671(1) | OPEN LINE FROM BUS 341662 [2HT ADAMS T 69.000] TO BUS 341671 [2HUNT FARM J69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 4.5288
SING OPN LIN 305 341662-341857(1) | OPEN LINE FROM BUS 341662 [2HT ADAMS T 69.000] TO BUS 341857 [2MERCR IND 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.7705
SING OPN LIN 306 341665-341701(1) | OPEN LINE FROM BUS 341665 [2HUNT 69.000] TO BUS 341701 [2JK SMITH 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 5.5689
SING OPN LIN 307 341665-341869(1) | OPEN LINE FROM BUS 341665 [2HUNT 69.000] TO BUS 341869 [2MILL HUNT T69.000] CKT 1 | FALSE | Blown up | 0 | 727.1511 | 8209.6309
SING OPN LIN 308 341665-342596(1) | OPEN LINE FROM BUS 341665 [2HUNT 69.000] TO BUS 342596 [4HUNT 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.4688 | 18.1806
SING OPN LIN 309 341671-342061(1) | OPEN LINE FROM BUS 341671 [2HUNT FARM J69.000] TO BUS 342061 [2PERRYVILLE 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.0118 | 11.6793
SING OPN LIN 310 341677-341890(1) | OPEN LINE FROM BUS 341677 [2INDEX 69.000] TO BUS 341890 [2MORGAN CO 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14177 | 4.104 | 1 | 6.9677
SING OPN LIN 311 341683-342100(1) | OPEN LINE FROM BUS 341683 [2JEFFERSNVIL69.000] TO BUS 342100 [2POWELL CO 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 2.7999 | 29.395
SING OPN LIN 312 341686-341689(1) | OPEN LINE FROM BUS 341686 [2JELLICO C T69.000] TO BUS 341689 [2JELLICO CRK69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 3.4921 | 1 | 1.9129
SING OPN LIN 313 341686-342076(1) | OPEN LINE FROM BUS 341686 [2JELLICO C T69.000] TO BUS 342076 [2PINE KNOT 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.44965 | 14.0494
SING OPN LIN 314 341692-341695(1) | OPEN LINE FROM BUS 341692 [2JENNY WIL T69.000] TO BUS 341695 [2JENNY WILEY69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.17086 | 9.6624 | 1 | 5.4657
SING OPN LIN 315 341692-342343(1) | OPEN LINE FROM BUS 341692 [2JENNY WIL T69.000] TO BUS 342343 [2THELMA 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 5.4234
SING OPN LIN 316 341701-342370(1) | OPEN LINE FROM BUS 341701 [2JK SMITH 69.000] TO BUS 342370 [2TRAPP 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 5.6191
SING OPN LIN 317 341704-341707(1) | OPEN LINE FROM BUS 341704 [2JOE TICH 69.000] TO BUS 341707 [2JOE TICH T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.20936 | 9.6554 | 1 | 7.9884
SING OPN LIN 318 341707-342427(1) | OPEN LINE FROM BUS 341707 [2JOE TICH T 69.000] TO BUS 342427 [2W BARDSTWN 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.1101
SING OPN LIN 319 341716-341722(1) | OPEN LINE FROM BUS 341716 [2KEAVY 69.000] TO BUS 341722 [2KEAVY 2 T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 2.135 | 22.9544 | 1 | 10.7978
SING OPN LIN 320 341719-341740(1) | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.4888
SING OPN LIN 321 341719-342073(1) | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.4214
SING OPN LIN 322 341722-341740(1) | OPEN LINE FROM BUS 341722 [2KEAVY 2 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.7394
SING OPN LIN 323 341722-342187(1) | OPEN LINE FROM BUS 341722 [2KEAVY 2 T 69.000] TO BUS 342187 [2S CORBIN 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.9682
SING OPN LIN 324 341725-342007(1) | OPEN LINE FROM BUS 341725 [2KEITH 69.000] TO BUS 342007 [2OWEN CO 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.8794
SING OPN LIN 325 341725-342058(1) | OPEN LINE FROM BUS 341725 [2KEITH 69.000] TO BUS 342058 [2PENN 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.3316
SING OPN LIN 326 341728-341854(1) | OPEN LINE FROM BUS 341728 [2KNOB LICK 69.000] TO BUS 341854 [2MCKINNY T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.4141 | 15.9317
SING OPN LIN 327 341731-341732(1) | OPEN LINE FROM BUS 341731 [2LANCASTER 69.000] TO BUS 341732 [2LANCASTER T69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14436 | 7.4579 | 1 | 5.5024
SING OPN LIN 328 341732-341959(1) | OPEN LINE FROM BUS 341732 [2LANCASTER T69.000] TO BUS 341959 [2NEWBY 1 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.326
SING OPN LIN 329 341734-341737(1) | OPEN LINE FROM BUS 341734 [2LAUR C IP T69.000] TO BUS 341737 [2LAUR CO IP 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.15522 | 9.7532 | 1 | 9.26
SING OPN LIN 330 341740-342754(1) | OPEN LINE FROM BUS 341740 [2LAUREL CO 69.000] TO BUS 342754 [5LAUREL CO 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.30554 | 21.9747
SING OPN LIN 331 341746-342253(1) | OPEN LINE FROM BUS 341746 [2LEBANON J 69.000] TO BUS 342253 [2SHEPHEVIL J69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.9715
SING OPN LIN 332 341749-342058(1) | OPEN LINE FROM BUS 341749 [2LEES LICK 69.000] TO BUS 342058 [2PENN 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.9949 | 25.4196
SING OPN LIN 333 341749-342133(1) | OPEN LINE FROM BUS 341749 [2LEES LICK 69.000] TO BUS 342133 [2RENAKER 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.841 | 23.7614
SING OPN LIN 334 341755-341758(1) | OPEN LINE FROM BUS 341755 [2LIBER CH T 69.000] TO BUS 341758 [2LIBERT CHUR69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 5.8166 | 1 | 4.8231
SING OPN LIN 335 341761-341767(1) | OPEN LINE FROM BUS 341761 [2LIBERTY J 69.000] TO BUS 341767 [2LIBERTYKU T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.5685
SING OPN LIN 336 341761-341896(1) | OPEN LINE FROM BUS 341761 [2LIBERTY J 69.000] TO BUS 341896 [2MT OLIVE J 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 7.6189
SING OPN LIN 337 341761-342760(1) | OPEN LINE FROM BUS 341761 [2LIBERTY J 69.000] TO BUS 342760 [5LIBERTY J 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.7108
SING OPN LIN 338 341764-341767(1) | OPEN LINE FROM BUS 341764 [2LIBERTY KU 69.000] TO BUS 341767 [2LIBERTYKU T69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.49544 | 12.6599 | 1 | 7.68
SING OPN LIN 339 341767-342064(1) | OPEN LINE FROM BUS 341767 [2LIBERTYKU T69.000] TO BUS 342064 [2PEYTONS ST 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.9079
SING OPN LIN 340 341772-341774(1) | OPEN LINE FROM BUS 341772 [2LOGAN 69.000] TO BUS 341774 [2LOGAN 2 T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 2.7124 | 28.6615 | 1 | 13.452
SING OPN LIN 341 341774-341775(1) | OPEN LINE FROM BUS 341774 [2LOGAN 2 T 69.000] TO BUS 341775 [2LOGAN TAP 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 4.4103
SING OPN LIN 342 341775-342247(1) | OPEN LINE FROM BUS 341775 [2LOGAN TAP 69.000] TO BUS 342247 [2SHELBY CO 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 4.4172
SING OPN LIN 343 341776-342208(1) | OPEN LINE FROM BUS 341776 [2LORETTO 69.000] TO BUS 342208 [2S SPRINGF T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 2.5676 | 65.8029
SING OPN LIN 344 341776-342316(1) | OPEN LINE FROM BUS 341776 [2LORETTO 69.000] TO BUS 342316 [2SULPHUR CRK69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 2.289 | 24.4632
SING OPN LIN 345 341779-341782(1) | OPEN LINE FROM BUS 341779 [2LOW GAP 69.000] TO BUS 341782 [2LOW GAP T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 3.4182 | 1 | 4.1103
SING OPN LIN 346 341782-342475(1) | OPEN LINE FROM BUS 341782 [2LOW GAP T 69.000] TO BUS 342475 [2WARNOCK 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 7.2839
SING OPN LIN 347 341785-341788(1) | OPEN LINE FROM BUS 341785 [2LYMAN BW 69.000] TO BUS 341788 [2LYMAN BW T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.18714 | 8.4004 | 1 | 7.0814
SING OPN LIN 348 341788-342155(1) | OPEN LINE FROM BUS 341788 [2LYMAN BW T 69.000] TO BUS 342155 [2ROANOKE T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.4918
SING OPN LIN 349 341788-342379(1) | OPEN LINE FROM BUS 341788 [2LYMAN BW T 69.000] TO BUS 342379 [2TUNNEL H T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.4953
SING OPN LIN 350 341791-341794(1) | OPEN LINE FROM BUS 341791 [2MACKVIL KU 69.000] TO BUS 341794 [2MACKVILKU T69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14448 | 2.6992 | 1 | 0.45
SING OPN LIN 351 341794-341935(1) | OPEN LINE FROM BUS 341794 [2MACKVILKU T69.000] TO BUS 341935 [2N SPRINGFLD69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.6099 | 17.9184
SING OPN LIN 352 341794-342061(1) | OPEN LINE FROM BUS 341794 [2MACKVILKU T69.000] TO BUS 342061 [2PERRYVILLE 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.574 | 17.6135
SING OPN LIN 353 341797-342265(1) | OPEN LINE FROM BUS 341797 [2MAGGARD 69.000] TO BUS 342265 [2SKAGGS 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.33209 | 14.6617
SING OPN LIN 354 341800-342325(1) | OPEN LINE FROM BUS 341800 [2MAGNOLIA 69.000] TO BUS 342325 [2SUMMERSVIL 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.0332 | 12.2541
SING OPN LIN 355 341803-342310(1) | OPEN LINE FROM BUS 341803 [2MAGOFFIN CO69.000] TO BUS 342310 [2SUBLETT 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.9346
SING OPN LIN 356 341803-342313(1) | OPEN LINE FROM BUS 341803 [2MAGOFFIN CO69.000] TO BUS 342313 [2SUBLETT J 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.39645 | 12.7651
SING OPN LIN 357 341809-341812(1) | OPEN LINE FROM BUS 341809 [2MAPLESVIL T69.000] TO BUS 341812 [2MAPLESVILLE69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14805 | 7.019 | 1 | 5.784
SING OPN LIN 358 341809-341929(1) | OPEN LINE FROM BUS 341809 [2MAPLESVIL T69.000] TO BUS 341929 [2N LONDON 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 7.3257
SING OPN LIN 359 341815-341818(1) | OPEN LINE FROM BUS 341815 [2MARETBURG 69.000] TO BUS 341818 [2MARETBURG T69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.9914 | 16.7888 | 1 | 6.4511
SING OPN LIN 360 341818-342472(1) | OPEN LINE FROM BUS 341818 [2MARETBURG T69.000] TO BUS 342472 [2WALNUT GROV69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14499 | 2.6519
SING OPN LIN 361 341821-341824(1) | OPEN LINE FROM BUS 341821 [2MARIBA 69.000] TO BUS 341824 [2MARIBA T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 3.2528 | 1 | 4.525
SING OPN LIN 362 341824-341833(1) | OPEN LINE FROM BUS 341824 [2MARIBA T 69.000] TO BUS 341833 [2MAYTOWN T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 2.0104 | 20.6748
SING OPN LIN 363 341827-342343(1) | OPEN LINE FROM BUS 341827 [2MARTIN CO 69.000] TO BUS 342343 [2THELMA 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 4.6875 | 1 | 4.7105
SING OPN LIN 364 341830-341833(1) | OPEN LINE FROM BUS 341830 [2MAYTOWN 69.000] TO BUS 341833 [2MAYTOWN T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 3.2228 | 1 | 3.9033
SING OPN LIN 365 341833-341890(1) | OPEN LINE FROM BUS 341833 [2MAYTOWN T 69.000] TO BUS 341890 [2MORGAN CO 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.72817 | 9.0432
SING OPN LIN 366 341836-341953(1) | OPEN LINE FROM BUS 341836 [2MAZIE 69.000] TO BUS 341953 [2NEW FOUNDL 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.4287 | 14.8197
SING OPN LIN 367 341836-342265(1) | OPEN LINE FROM BUS 341836 [2MAZIE 69.000] TO BUS 342265 [2SKAGGS 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.46428 | 16.0974
SING OPN LIN 368 341839-341842(1) | OPEN LINE FROM BUS 341839 [2MBUSA 69.000] TO BUS 341842 [2MBUSA T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 2.9154 | 30.6038 | 1 | 14.5365
SING OPN LIN 369 341845-342139(1) | OPEN LINE FROM BUS 341845 [2MCCREARY CO69.000] TO BUS 342139 [2REVELO KU T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 7.3857
SING OPN LIN 370 341845-342490(1) | OPEN LINE FROM BUS 341845 [2MCCREARY CO69.000] TO BUS 342490 [2WHITLEY CTY69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.6764
SING OPN LIN 371 341845-342778(1) | OPEN LINE FROM BUS 341845 [2MCCREARY CO69.000] TO BUS 342778 [5MCCREARY CO161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14764 | 5.446
SING OPN LIN 372 341848-342223(1) | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342223 [2SAND GAP T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.6115
SING OPN LIN 373 341848-342391(1) | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.5546
SING OPN LIN 374 341851-341854(1) | OPEN LINE FROM BUS 341851 [2MCKINNEY 69.000] TO BUS 341854 [2MCKINNY T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 2.8835 | 1 | 4.4445
SING OPN LIN 375 341857-342406(1) | OPEN LINE FROM BUS 341857 [2MERCR IND 69.000] TO BUS 342406 [2VAN ARSDELL69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.7677
SING OPN LIN 376 341860-341863(1) | OPEN LINE FROM BUS 341860 [2MIDDL CRK T69.000] TO BUS 341863 [2MIDDLE CRK 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.17029 | 10.0275 | 1 | 5.746
SING OPN LIN 377 341869-341875(1) | OPEN LINE FROM BUS 341869 [2MILL HUNT T69.000] TO BUS 341875 [2MILLER HUNT69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14485 | 5.4052 | 1 | 2.2498
SING OPN LIN 378 341869-342259(1) | OPEN LINE FROM BUS 341869 [2MILL HUNT T69.000] TO BUS 342259 [2SIDEVIEW 69.000] CKT 1 | FALSE | Blown up | 0 | 731.0385 | 8162.5874
SING OPN LIN 379 341872-341878(1) | OPEN LINE FROM BUS 341872 [2MILLB-CRL J69.000] TO BUS 341878 [2MILLERSB EK69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.6337 | 32.2902 | 1 | 3.855
SING OPN LIN 380 341887-342268(1) | OPEN LINE FROM BUS 341887 [2MONTICELLO 69.000] TO BUS 342268 [2SLAT 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.22157 | 13.7895
SING OPN LIN 381 341893-341896(1) | OPEN LINE FROM BUS 341893 [2MT OLIVE 69.000] TO BUS 341896 [2MT OLIVE J 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 3.4493 | 1 | 4.6349
SING OPN LIN 382 341908-341914(1) | OPEN LINE FROM BUS 341908 [2MUNFVIL EK 69.000] TO BUS 341914 [2MUNFVILKU T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 2.3313 | 30.8892
SING OPN LIN 383 341911-341914(1) | OPEN LINE FROM BUS 341911 [2MUNFVIL KU 69.000] TO BUS 341914 [2MUNFVILKU T69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.39172 | 10.8911 | 1 | 6.11
SING OPN LIN 384 341917-341998(1) | OPEN LINE FROM BUS 341917 [2MUNK 69.000] TO BUS 341998 [2OAKLEY NOEL69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.48378 | 19.4479
SING OPN LIN 385 341920-341998(1) | OPEN LINE FROM BUS 341920 [2MUNK J 69.000] TO BUS 341998 [2OAKLEY NOEL69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.61834 | 25.0505
SING OPN LIN 386 341920-342502(1) | OPEN LINE FROM BUS 341920 [2MUNK J 69.000] TO BUS 342502 [2WILLIAMSTWN69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.95767 | 16.2815 | 1 | 12.2435
SING OPN LIN 387 341923-342091(1) | OPEN LINE FROM BUS 341923 [2MURPHYSVIL 69.000] TO BUS 342091 [2PLUMVILLE 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.21489 | 14.1345
SING OPN LIN 388 341923-342280(1) | OPEN LINE FROM BUS 341923 [2MURPHYSVIL 69.000] TO BUS 342280 [2SNOW HILL 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.9235 | 47.5099
SING OPN LIN 389 341926-342181(1) | OPEN LINE FROM BUS 341926 [2N ALBANY 69.000] TO BUS 342181 [2S ALBANY 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.1651 | 10.2083 | 1 | 7.995
SING OPN LIN 390 341926-342283(1) | OPEN LINE FROM BUS 341926 [2N ALBANY 69.000] TO BUS 342283 [2SNOW T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 6.687
SING OPN LIN 391 341926-342397(1) | OPEN LINE FROM BUS 341926 [2N ALBANY 69.000] TO BUS 342397 [2UPCHURCH T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.15011 | 4.375
SING OPN LIN 392 341929-341930(1) | OPEN LINE FROM BUS 341929 [2N LONDON 69.000] TO BUS 341930 [2N LONDON T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.7917
SING OPN LIN 393 341935-342208(1) | OPEN LINE FROM BUS 341935 [2N SPRINGFLD69.000] TO BUS 342208 [2S SPRINGF T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.6617 | 50.162
SING OPN LIN 394 341938-342505(1) | OPEN LINE FROM BUS 341938 [2NANCY 69.000] TO BUS 342505 [2WINDSOR 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.9434 | 22.0077
SING OPN LIN 395 341938-342526(1) | OPEN LINE FROM BUS 341938 [2NANCY 69.000] TO BUS 342526 [2ZOLLICOF T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.5692 | 17.9637
SING OPN LIN 396 341941-341947(1) | OPEN LINE FROM BUS 341941 [2NELSN VAL T69.000] TO BUS 341947 [2NELSON VAL 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14281 | 7.0997 | 1 | 5.5639
SING OPN LIN 397 341941-341971(1) | OPEN LINE FROM BUS 341941 [2NELSN VAL T69.000] TO BUS 341971 [2NORWOOD 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.2414
SING OPN LIN 398 341944-342424(1) | OPEN LINE FROM BUS 341944 [2NELSON CO 69.000] TO BUS 342424 [2W BARDST J 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.6743
SING OPN LIN 399 341944-342514(1) | OPEN LINE FROM BUS 341944 [2NELSON CO 69.000] TO BUS 342514 [2WOOSLEY 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.8537
SING OPN LIN 400 341950-342007(1) | OPEN LINE FROM BUS 341950 [2NEW CASTLE 69.000] TO BUS 342007 [2OWEN CO 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.9053
SING OPN LIN 401 341953-342229(1) | OPEN LINE FROM BUS 341953 [2NEW FOUNDL 69.000] TO BUS 342229 [2SANDY HOOK 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 3.3257 | 1 | 3.5476
SING OPN LIN 402 341962-342361(1) | OPEN LINE FROM BUS 341962 [2NEWBY 2 69.000] TO BUS 342361 [2TODDVILLE T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.5455
SING OPN LIN 403 341965-342199(1) | OPEN LINE FROM BUS 341965 [2NICHOLASVIL69.000] TO BUS 342199 [2S JESSAM J 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.4035 | 8.8343
SING OPN LIN 404 341971-342115(1) | OPEN LINE FROM BUS 341971 [2NORWOOD 69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14484 | 2.5389
SING OPN LIN 405 341974-342256(1) | OPEN LINE FROM BUS 341974 [2NORWOOD T 69.000] TO BUS 342256 [2SHOPVILLE 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.23327 | 6.3622
SING OPN LIN 406 341977-341983(1) | OPEN LINE FROM BUS 341977 [2OAK HILL 69.000] TO BUS 341983 [2OAK HILL T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14427 | 7.7385 | 1 | 6.5887
SING OPN LIN 407 341980-341983(1) | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 341983 [2OAK HILL T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.36159 | 20.4894
SING OPN LIN 408 341980-342286(1) | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.3618 | 20.4909
SING OPN LIN 409 341983-342469(1) | OPEN LINE FROM BUS 341983 [2OAK HILL T 69.000] TO BUS 342469 [2W SOMERSET 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.1561 | 24.345
SING OPN LIN 410 341986-341989(1) | OPEN LINE FROM BUS 341986 [2OAK RIDGE 69.000] TO BUS 341989 [2OAK RIDGE T69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 3.7664 | 1 | 4.6709
SING OPN LIN 411 342007-342008(1) | OPEN LINE FROM BUS 342007 [2OWEN CO 69.000] TO BUS 342008 [4OWEN CO 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.43215 | 7.0158
SING OPN LIN 412 342007-342010(1) | OPEN LINE FROM BUS 342007 [2OWEN CO 69.000] TO BUS 342010 [2OWEN CO J1 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.1767 | 6.12
SING OPN LIN 413 342007-342013(1) | OPEN LINE FROM BUS 342007 [2OWEN CO 69.000] TO BUS 342013 [2OWEN CO J2 69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.16381 | 8.2968 | 1 | 5.8918
SING OPN LIN 414 342016-342019(1) | OPEN LINE FROM BUS 342016 [2OWENS IL 69.000] TO BUS 342019 [2OWENS IL J 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14872 | 2.8715 | 1 | 7.503
SING OPN LIN 415 342022-342025(1) | OPEN LINE FROM BUS 342022 [2OWINGSVIL T69.000] TO BUS 342025 [2OWINGVIL KU69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 1.2473 | 19.4687 | 1 | 9.53
SING OPN LIN 416 342022-342052(1) | OPEN LINE FROM BUS 342022 [2OWINGSVIL T69.000] TO BUS 342052 [2PEASTICKS 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.5878
SING OPN LIN 417 342022-342112(1) | OPEN LINE FROM BUS 342022 [2OWINGSVIL T69.000] TO BUS 342112 [2PRESTON T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.8682
SING OPN LIN 418 342031-342034(1) | OPEN LINE FROM BUS 342031 [2PACTOLUS 69.000] TO BUS 342034 [2PACTOLUS T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.17008 | 16.4296 | 1 | 8.8816
SING OPN LIN 419 342037-342040(1) | OPEN LINE FROM BUS 342037 [2PARKWAY 1 69.000] TO BUS 342040 [2PARKWAY 2 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 2.6496 | 1 | 3.3429
SING OPN LIN 420 342049-342161(1) | OPEN LINE FROM BUS 342049 [2PATTON RD J69.000] TO BUS 342161 [2ROSEVILLE T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.5979 | 17.6055
SING OPN LIN 421 342049-940830(1) | OPEN LINE FROM BUS 342049 [2PATTON RD J69.000] TO BUS 940830 [AE2-071 TAP 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.6213
SING OPN LIN 422 342067-342505(1) | OPEN LINE FROM BUS 342067 [2PHIL 69.000] TO BUS 342505 [2WINDSOR 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.718
SING OPN LIN 423 342070-342073(1) | OPEN LINE FROM BUS 342070 [2PINE GROVE 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.15494 | 9.9897 | 1 | 9.8481
SING OPN LIN 424 342073-342451(1) | OPEN LINE FROM BUS 342073 [2PINE GRV T 69.000] TO BUS 342451 [2W LONDON 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.847
SING OPN LIN 425 342076-342139(1) | OPEN LINE FROM BUS 342076 [2PINE KNOT 69.000] TO BUS 342139 [2REVELO KU T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 7.1002
SING OPN LIN 426 342077-342782(1) | OPEN LINE FROM BUS 342077 [2PINEVILL EK69.000] TO BUS 342782 [5PINEVILL EK161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 5.8402
SING OPN LIN 427 342085-342088(1) | OPEN LINE FROM BUS 342085 [2PLUMMR L 69.000] TO BUS 342088 [2PLUMMR L T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 3.5477 | 1 | 4.0531
SING OPN LIN 428 342091-342124(1) | OPEN LINE FROM BUS 342091 [2PLUMVILLE 69.000] TO BUS 342124 [2RECTORVILLE69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.8214
SING OPN LIN 429 342091-342634(1) | OPEN LINE FROM BUS 342091 [2PLUMVILLE 69.000] TO BUS 342634 [4PLUMVILLE 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 9.0873
SING OPN LIN 430 342097-342184(1) | OPEN LINE FROM BUS 342097 [2POWEL TAYL 69.000] TO BUS 342184 [2S ANDERSON 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14705 | 7.738 | 1 | 5.6222
SING OPN LIN 431 342100-342301(1) | OPEN LINE FROM BUS 342100 [2POWELL CO 69.000] TO BUS 342301 [2STANTON 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.8068
SING OPN LIN 432 342100-342637(1) | OPEN LINE FROM BUS 342100 [2POWELL CO 69.000] TO BUS 342637 [4POWELL CO 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.18871 | 8.0076
SING OPN LIN 433 342103-342106(1) | OPEN LINE FROM BUS 342103 [2PPG 69.000] TO BUS 342106 [2PPG J 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.7444
SING OPN LIN 434 342109-342112(1) | OPEN LINE FROM BUS 342109 [2PRESTON 69.000] TO BUS 342112 [2PRESTON T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.59287 | 14.6121 | 1 | 1.5083
SING OPN LIN 435 342115-342787(1) | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.2544
SING OPN LIN 436 342118-342121(1) | OPEN LINE FROM BUS 342118 [2RADCLIFF 69.000] TO BUS 342121 [2T BROWN L T69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.2053 | 8.8993 | 1 | 7.6513
SING OPN LIN 437 342121-342328(1) | OPEN LINE FROM BUS 342121 [2T BROWN L T69.000] TO BUS 342328 [2T BROWN LOG69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.2023 | 8.808 | 1 | 7.5424
SING OPN LIN 438 342121-342415(1) | OPEN LINE FROM BUS 342121 [2T BROWN L T69.000] TO BUS 342415 [2VINE GROV J69.000] CKT 1 | TRUE | Met convergence tolerances | 3 | 1.4168 | 15.8445 | 2 | 15.1937
SING OPN LIN 439 342127-342265(1) | OPEN LINE FROM BUS 342127 [2REDBUSH 69.000] TO BUS 342265 [2SKAGGS 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.5158 | 15.7816
SING OPN LIN 440 342127-342421(1) | OPEN LINE FROM BUS 342127 [2REDBUSH 69.000] TO BUS 342421 [2VOLGA 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.5361 | 16.0023
SING OPN LIN 441 342130-342259(1) | OPEN LINE FROM BUS 342130 [2REID VILLAG69.000] TO BUS 342259 [2SIDEVIEW 69.000] CKT 1 | TRUE | Met convergence tolerances | 3 | 1.0933 | 9.5803 | 2 | 7.7983
SING OPN LIN 442 342133-342355(1) | OPEN LINE FROM BUS 342133 [2RENAKER 69.000] TO BUS 342355 [2THREE M T 69.000] CKT 1 | FALSE | Blown up | 0 | 991.3359 | 13157.2188
SING OPN LIN 443 342133-342640(1) | OPEN LINE FROM BUS 342133 [2RENAKER 69.000] TO BUS 342640 [4RENAKER 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.24446 | 15.1878
SING OPN LIN 444 342136-342139(1) | OPEN LINE FROM BUS 342136 [2REVELO KU 69.000] TO BUS 342139 [2REVELO KU T69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.92429 | 53.4747 | 1 | 1.8
SING OPN LIN 445 342145-342487(1) | OPEN LINE FROM BUS 342145 [2RICHARDSON 69.000] TO BUS 342487 [2WEBSTER RD 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 2.7475 | 28.6389 | 1 | 13.5187
SING OPN LIN 446 342154-342155(1) | OPEN LINE FROM BUS 342154 [2ROANOKE 69.000] TO BUS 342155 [2ROANOKE T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 2.8388 | 1 | 3.4896
SING OPN LIN 447 342157-342418(1) | OPEN LINE FROM BUS 342157 [2ROGERSVIL J69.000] TO BUS 342418 [2VINE GROVE 69.000] CKT 1 | TRUE | Met convergence tolerances | 5 | 2.2198 | 23.5233 | 3 | 23.3966
SING OPN LIN 448 342160-342161(1) | OPEN LINE FROM BUS 342160 [2ROSEVILLE 69.000] TO BUS 342161 [2ROSEVILLE T69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.25181 | 10.6587 | 1 | 7.0525
SING OPN LIN 449 342161-342334(1) | OPEN LINE FROM BUS 342161 [2ROSEVILLE T69.000] TO BUS 342334 [2TEMPLE HILL69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.766 | 19.2529
SING OPN LIN 450 342163-342649(1) | OPEN LINE FROM BUS 342163 [2ROWAN CO 69.000] TO BUS 342649 [4ROWAN CO 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 4.751
SING OPN LIN 451 342166-342169(1) | OPEN LINE FROM BUS 342166 [2RUSS SPEK T69.000] TO BUS 342169 [2RUSS SPKU T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.20235 | 4.8605
SING OPN LIN 452 342166-342172(1) | OPEN LINE FROM BUS 342166 [2RUSS SPEK T69.000] TO BUS 342172 [2RUSS SPR EK69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 2.0173 | 21.8185 | 1 | 11.0494
SING OPN LIN 453 342166-342235(1) | OPEN LINE FROM BUS 342166 [2RUSS SPEK T69.000] TO BUS 342235 [2SEWELTN J 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.22637 | 5.4961
SING OPN LIN 454 342169-342175(1) | OPEN LINE FROM BUS 342169 [2RUSS SPKU T69.000] TO BUS 342175 [2RUSS SPR KU69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.42589 | 11.2683 | 1 | 6.4
SING OPN LIN 455 342169-342178(1) | OPEN LINE FROM BUS 342169 [2RUSS SPKU T69.000] TO BUS 342178 [2RUSSEL CO 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.18425 | 4.4142
SING OPN LIN 456 342178-342232(1) | OPEN LINE FROM BUS 342178 [2RUSSEL CO 69.000] TO BUS 342232 [2SEWELLTON 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.85609 | 10.2982
SING OPN LIN 457 342178-342793(1) | OPEN LINE FROM BUS 342178 [2RUSSEL CO 69.000] TO BUS 342793 [5RUSSEL CO 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.0318 | 12.5564
SING OPN LIN 458 342184-342262(1) | OPEN LINE FROM BUS 342184 [2S ANDERSON 69.000] TO BUS 342262 [2SINAI 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.1787 | 49.1348
SING OPN LIN 459 342186-342424(1) | OPEN LINE FROM BUS 342186 [2S BARDSTWN 69.000] TO BUS 342424 [2W BARDST J 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.7522
SING OPN LIN 460 342186-342427(1) | OPEN LINE FROM BUS 342186 [2S BARDSTWN 69.000] TO BUS 342427 [2W BARDSTWN 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.6487
SING OPN LIN 461 342196-342391(1) | OPEN LINE FROM BUS 342196 [2WHITE OAK 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.4467
SING OPN LIN 462 342199-342202(1) | OPEN LINE FROM BUS 342199 [2S JESSAM J 69.000] TO BUS 342202 [2S JESSAMINE69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 2.9571 | 31.227 | 1 | 14.9115
SING OPN LIN 463 342208-342211(1) | OPEN LINE FROM BUS 342208 [2S SPRINGF T69.000] TO BUS 342211 [2S SPRINGFLD69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 3.5489 | 1 | 4.6495
SING OPN LIN 464 342214-342217(1) | OPEN LINE FROM BUS 342214 [2SALEM EK 69.000] TO BUS 342217 [2SALEM EK T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.18784 | 13.1645 | 1 | 10.2212
SING OPN LIN 465 342217-342481(1) | OPEN LINE FROM BUS 342217 [2SALEM EK T 69.000] TO BUS 342481 [2WEBB CR R T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.5928
SING OPN LIN 466 342217-342505(1) | OPEN LINE FROM BUS 342217 [2SALEM EK T 69.000] TO BUS 342505 [2WINDSOR 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.16305 | 5.5294
SING OPN LIN 467 342220-342223(1) | OPEN LINE FROM BUS 342220 [2SAND GAP 69.000] TO BUS 342223 [2SAND GAP T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14426 | 4.9624 | 1 | 2.7435
SING OPN LIN 468 342222-342703(1) | OPEN LINE FROM BUS 342222 [5S CASEY 161.00] TO BUS 342703 [5CASEY CO 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 2.1419 | 51.9511
SING OPN LIN 469 342222-342760(1) | OPEN LINE FROM BUS 342222 [5S CASEY 161.00] TO BUS 342760 [5LIBERTY J 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.0521 | 11.4139
SING OPN LIN 470 342235-943700(1) | OPEN LINE FROM BUS 342235 [2SEWELTN J 69.000] TO BUS 943700 [AF1-038 TAP 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.7124
SING OPN LIN 471 342238-342241(1) | OPEN LINE FROM BUS 342238 [2SEYMOUR 69.000] TO BUS 342241 [2SEYMOUR T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 2.7939 | 1 | 3.7942
SING OPN LIN 472 342247-342248(1) | OPEN LINE FROM BUS 342247 [2SHELBY CO 69.000] TO BUS 342248 [2SHELBY TAP 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.5496
SING OPN LIN 473 342247-342410(1) | OPEN LINE FROM BUS 342247 [2SHELBY CO 69.000] TO BUS 342410 [2VEECHDALE 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 2.5846 | 1 | 5.1171
SING OPN LIN 474 342247-342808(1) | OPEN LINE FROM BUS 342247 [2SHELBY CO 69.000] TO BUS 342808 [5SHELBY CO 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.72958 | 16.0104
SING OPN LIN 475 342250-342253(1) | OPEN LINE FROM BUS 342250 [2SHEPHEVIL 69.000] TO BUS 342253 [2SHEPHEVIL J69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 1.0939 | 11.5453 | 1 | 20.8315
SING OPN LIN 476 342265-342658(1) | OPEN LINE FROM BUS 342265 [2SKAGGS 69.000] TO BUS 342658 [4SKAGGS 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.2492 | 45.2239
SING OPN LIN 477 342268-342478(1) | OPEN LINE FROM BUS 342268 [2SLAT 69.000] TO BUS 342478 [2WAYNE CO 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.23168 | 15.1374
SING OPN LIN 478 342271-342274(1) | OPEN LINE FROM BUS 342271 [2SMITHRSVIL 69.000] TO BUS 342274 [2SMITHRVIL T69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 2.7674 | 29.2606 | 1 | 13.9816
SING OPN LIN 479 342277-342283(1) | OPEN LINE FROM BUS 342277 [2SNOW 69.000] TO BUS 342283 [2SNOW T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14177 | 2.6284 | 1 | 9.8435
SING OPN LIN 480 342283-342322(1) | OPEN LINE FROM BUS 342283 [2SNOW T 69.000] TO BUS 342322 [2SUMM SHADE 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.37319 | 9.9816
SING OPN LIN 481 342286-342287(1) | OPEN LINE FROM BUS 342286 [2SOMERSET 69.000] TO BUS 342287 [2SOMERSET KU69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 4.5499
SING OPN LIN 482 342292-342295(1) | OPEN LINE FROM BUS 342292 [2STANLEY PRK69.000] TO BUS 342295 [2STANLY P J169.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.15241 | 9.7113
SING OPN LIN 483 342292-342298(1) | OPEN LINE FROM BUS 342292 [2STANLEY PRK69.000] TO BUS 342298 [2STANLY P J269.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 6.0738
SING OPN LIN 484 342292-342667(1) | OPEN LINE FROM BUS 342292 [2STANLEY PRK69.000] TO BUS 342667 [4STANLEY PRK138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14918 | 9.8906
SING OPN LIN 485 342307-342403(1) | OPEN LINE FROM BUS 342307 [2STEPHENSBRG69.000] TO BUS 342403 [2UPTON T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.9801
SING OPN LIN 486 342307-342412(1) | OPEN LINE FROM BUS 342307 [2STEPHENSBRG69.000] TO BUS 342412 [2VERTREES 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14717 | 7.397 | 1 | 5.8907
SING OPN LIN 487 342319-342322(1) | OPEN LINE FROM BUS 342319 [2SUMM SHAD J69.000] TO BUS 342322 [2SUMM SHADE 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.8239 | 17.1803
SING OPN LIN 488 342319-342334(1) | OPEN LINE FROM BUS 342319 [2SUMM SHAD J69.000] TO BUS 342334 [2TEMPLE HILL69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.9726
SING OPN LIN 489 342319-940830(1) | OPEN LINE FROM BUS 342319 [2SUMM SHAD J69.000] TO BUS 940830 [AE2-071 TAP 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.2746 | 10.6746
SING OPN LIN 490 342322-342436(1) | OPEN LINE FROM BUS 342322 [2SUMM SHADE 69.000] TO BUS 342436 [2W COLUMBI T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 4.3229
SING OPN LIN 491 342322-342814(1) | OPEN LINE FROM BUS 342322 [2SUMM SHADE 69.000] TO BUS 342814 [5SUMM SHADE 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 2.4568 | 74.454
SING OPN LIN 492 342337-342340(1) | OPEN LINE FROM BUS 342337 [2THARP 69.000] TO BUS 342340 [2THARP T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.26353 | 10.9438 | 1 | 10.0175
SING OPN LIN 493 342343-342421(1) | OPEN LINE FROM BUS 342343 [2THELMA 69.000] TO BUS 342421 [2VOLGA 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.51054 | 10.3265
SING OPN LIN 494 342349-342433(1) | OPEN LINE FROM BUS 342349 [2THREE LNK J69.000] TO BUS 342433 [2W BEREA J 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.9143
SING OPN LIN 495 342352-342355(1) | OPEN LINE FROM BUS 342352 [2THREE M 69.000] TO BUS 342355 [2THREE M T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 1.411 | 15.7511 | 1 | 19.4904
SING OPN LIN 496 342358-342361(1) | OPEN LINE FROM BUS 342358 [2TODDVILLE 69.000] TO BUS 342361 [2TODDVILLE T69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 3.1928 | 1 | 4.2681
SING OPN LIN 497 342364-342367(1) | OPEN LINE FROM BUS 342364 [2TOMM GOOC 69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.92273 | 57.3488
SING OPN LIN 498 342364-342821(1) | OPEN LINE FROM BUS 342364 [2TOMM GOOC 69.000] TO BUS 342821 [5TOMMY EK 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.39707 | 9.8083
SING OPN LIN 499 342364-342821(2) | OPEN LINE FROM BUS 342364 [2TOMM GOOC 69.000] TO BUS 342821 [5TOMMY EK 161.00] CKT 2 | TRUE | Met convergence tolerances | 0 | 0.39707 | 9.8083
SING OPN LIN 500 342367-942410(1) | OPEN LINE FROM BUS 342367 [2TOMM GOOC T69.000] TO BUS 942410 [AE2-254 TAP 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 9.3517
SING OPN LIN 501 342379-342382(1) | OPEN LINE FROM BUS 342379 [2TUNNEL H T 69.000] TO BUS 342382 [2TUNNEL HILL69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.85243 | 9.4375 | 1 | 16.3905
SING OPN LIN 502 342385-342487(1) | OPEN LINE FROM BUS 342385 [2TURKEY FT 69.000] TO BUS 342487 [2WEBSTER RD 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.4706
SING OPN LIN 503 342391-342820(1) | OPEN LINE FROM BUS 342391 [2TYNER 69.000] TO BUS 342820 [5TYNER 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 4.7892
SING OPN LIN 504 342394-342397(1) | OPEN LINE FROM BUS 342394 [2UPCHURCH 69.000] TO BUS 342397 [2UPCHURCH T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14177 | 10.2398 | 1 | 8.1682
SING OPN LIN 505 342397-342532(1) | OPEN LINE FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14427 | 3.7639
SING OPN LIN 506 342400-342403(1) | OPEN LINE FROM BUS 342400 [2UPTON 69.000] TO BUS 342403 [2UPTON T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 2.7093 | 1 | 3.4103
SING OPN LIN 507 342415-342418(1) | OPEN LINE FROM BUS 342415 [2VINE GROV J69.000] TO BUS 342418 [2VINE GROVE 69.000] CKT 1 | TRUE | Met convergence tolerances | 4 | 1.4169 | 15.8475 | 2 | 15.1937
SING OPN LIN 508 342430-342433(1) | OPEN LINE FROM BUS 342430 [2W BEREA 69.000] TO BUS 342433 [2W BEREA J 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.9215
SING OPN LIN 509 342430-342691(1) | OPEN LINE FROM BUS 342430 [2W BEREA 69.000] TO BUS 342691 [4W BEREA 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.25213 | 3.9768
SING OPN LIN 510 342436-342439(1) | OPEN LINE FROM BUS 342436 [2W COLUMBI T69.000] TO BUS 342439 [2W COLUMBIA 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14207 | 8.6352 | 1 | 5.8725
SING OPN LIN 511 342442-342445(1) | OPEN LINE FROM BUS 342442 [2W GLASGOW 69.000] TO BUS 342445 [2W GLASGOW T69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 2.3816 | 25.2413 | 1 | 12.7509
SING OPN LIN 512 342451-342452(1) | OPEN LINE FROM BUS 342451 [2W LONDON 69.000] TO BUS 342452 [2W LONDON T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14691 | 2.977
SING OPN LIN 513 342460-342463(1) | OPEN LINE FROM BUS 342460 [2W NICHVIL 69.000] TO BUS 342463 [2W NICHVIL T69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 2.1828 | 23.1005 | 1 | 23.1559
SING OPN LIN 514 342469-342526(1) | OPEN LINE FROM BUS 342469 [2W SOMERSET 69.000] TO BUS 342526 [2ZOLLICOF T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.3552 | 15.6767
SING OPN LIN 515 342472-342511(1) | OPEN LINE FROM BUS 342472 [2WALNUT GROV69.000] TO BUS 342511 [2WOODSTOCK 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.9
SING OPN LIN 516 342478-342532(1) | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.15633 | 4.0131
SING OPN LIN 517 342478-342535(1) | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342535 [2ZULA T 69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.14177 | 10.1487 | 1 | 8.451
SING OPN LIN 518 342478-342823(1) | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 4.2048
SING OPN LIN 519 342481-342484(1) | OPEN LINE FROM BUS 342481 [2WEBB CR R T69.000] TO BUS 342484 [2WEBB CR RDS69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 3.238 | 1 | 5.4721
SING OPN LIN 520 342481-943700(1) | OPEN LINE FROM BUS 342481 [2WEBB CR R T69.000] TO BUS 943700 [AF1-038 TAP 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.6856 | 23.7623
SING OPN LIN 521 342490-342493(1) | OPEN LINE FROM BUS 342490 [2WHITLEY CTY69.000] TO BUS 342493 [2WHITLY C KU69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.23158 | 8.1684 | 1 | 3.81
SING OPN LIN 522 342490-342499(1) | OPEN LINE FROM BUS 342490 [2WHITLEY CTY69.000] TO BUS 342499 [2WIBORG T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 4.7862
SING OPN LIN 523 342496-342499(1) | OPEN LINE FROM BUS 342496 [2WIBORG 69.000] TO BUS 342499 [2WIBORG T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14365 | 7.9364 | 1 | 8.0737
SING OPN LIN 524 342523-342526(1) | OPEN LINE FROM BUS 342523 [2ZOLLICOF 69.000] TO BUS 342526 [2ZOLLICOF T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 2.8214 | 1 | 3.8925
SING OPN LIN 525 342529-342535(1) | OPEN LINE FROM BUS 342529 [2ZULA 69.000] TO BUS 342535 [2ZULA T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14177 | 10.2281 | 1 | 8.451
SING OPN LIN 526 342538-342616(1) | OPEN LINE FROM BUS 342538 [4ARGENTUM 138.00] TO BUS 342616 [4LOVE HYDRO 138.00] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.91319 | 15.5345
SING OPN LIN 527 342541-342544(1) | OPEN LINE FROM BUS 342541 [4AVON 138.00] TO BUS 342544 [4AVON-R 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.7692 | 19.0663
SING OPN LIN 528 342541-342556(1) | OPEN LINE FROM BUS 342541 [4AVON 138.00] TO BUS 342556 [4BECKNERV T 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.1802
SING OPN LIN 529 342541-342580(1) | OPEN LINE FROM BUS 342541 [4AVON 138.00] TO BUS 342580 [4FAYETTE 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.88555 | 11.7084
SING OPN LIN 530 342541-342631(1) | OPEN LINE FROM BUS 342541 [4AVON 138.00] TO BUS 342631 [4PARIS T 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.9597 | 24.0494
SING OPN LIN 531 342541-342829(1) | OPEN LINE FROM BUS 342541 [4AVON 138.00] TO BUS 342829 [7AVON 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.4391 | 15.6196
SING OPN LIN 532 342550-342559(1) | OPEN LINE FROM BUS 342550 [4BAVARIAN LF138.00] TO BUS 342559 [4BOONE CO 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.86205 | 37.7303
SING OPN LIN 533 342550-342640(1) | OPEN LINE FROM BUS 342550 [4BAVARIAN LF138.00] TO BUS 342640 [4RENAKER 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.97145 | 39.561
SING OPN LIN 534 342553-342556(1) | OPEN LINE FROM BUS 342553 [4BECKNERV 138.00] TO BUS 342556 [4BECKNERV T 138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14506 | 3.8631 | 1 | 1.593
SING OPN LIN 535 342556-342565(1) | OPEN LINE FROM BUS 342556 [4BECKNERV T 138.00] TO BUS 342565 [4BOONESBOR T138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.2194
SING OPN LIN 536 342559-342646(1) | OPEN LINE FROM BUS 342559 [4BOONE CO 138.00] TO BUS 342646 [4RICHWOOD T 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 4.8109
SING OPN LIN 537 342559-342673(1) | OPEN LINE FROM BUS 342559 [4BOONE CO 138.00] TO BUS 342673 [4STERLNG T 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.4613 | 20.8104
SING OPN LIN 538 342565-342574(1) | OPEN LINE FROM BUS 342565 [4BOONESBOR T138.00] TO BUS 342574 [4DALE 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 7.0619
SING OPN LIN 539 342571-342589(1) | OPEN LINE FROM BUS 342571 [4CRANSTON 138.00] TO BUS 342589 [4GODDARD 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.7085 | 18.4426
SING OPN LIN 540 342571-342649(1) | OPEN LINE FROM BUS 342571 [4CRANSTON 138.00] TO BUS 342649 [4ROWAN CO 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.3778 | 15.1819
SING OPN LIN 541 342574-342596(1) | OPEN LINE FROM BUS 342574 [4DALE 138.00] TO BUS 342596 [4HUNT 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.79704 | 47.6858
SING OPN LIN 542 342574-342676(1) | OPEN LINE FROM BUS 342574 [4DALE 138.00] TO BUS 342676 [4THREE FK T 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.65118 | 39.5036
SING OPN LIN 543 342577-342607(1) | OPEN LINE FROM BUS 342577 [4FAWKES EK 138.00] TO BUS 342607 [4JK SMITH 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.8502
SING OPN LIN 544 342577-342676(1) | OPEN LINE FROM BUS 342577 [4FAWKES EK 138.00] TO BUS 342676 [4THREE FK T 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.58547 | 8.1846
SING OPN LIN 545 342577-342691(1) | OPEN LINE FROM BUS 342577 [4FAWKES EK 138.00] TO BUS 342691 [4W BEREA 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.25301 | 3.9687
SING OPN LIN 546 342583-342589(1) | OPEN LINE FROM BUS 342583 [4FLEMINGSBRG138.00] TO BUS 342589 [4GODDARD 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.6462 | 17.8763
SING OPN LIN 547 342583-342664(1) | OPEN LINE FROM BUS 342583 [4FLEMINGSBRG138.00] TO BUS 342664 [4SPURLOCK 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.5132 | 16.6097
SING OPN LIN 548 342586-342587(1) | OPEN LINE FROM BUS 342586 [4GALLATIN CO138.00] TO BUS 342587 [1GALLATIN CO34.500] CKT 1 | TRUE | Met convergence tolerances | 1 | 2.2335 | 23.664 | 1 | 23.73
SING OPN LIN 549 342586-342673(1) | OPEN LINE FROM BUS 342586 [4GALLATIN CO138.00] TO BUS 342673 [4STERLNG T 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.4059 | 20.6402
SING OPN LIN 550 342589-342634(1) | OPEN LINE FROM BUS 342589 [4GODDARD 138.00] TO BUS 342634 [4PLUMVILLE 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.5086 | 16.581
SING OPN LIN 551 342596-342607(1) | OPEN LINE FROM BUS 342596 [4HUNT 138.00] TO BUS 342607 [4JK SMITH 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 9.0781
SING OPN LIN 552 342598-342664(1) | OPEN LINE FROM BUS 342598 [4INLAND C T 138.00] TO BUS 342664 [4SPURLOCK 138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 1.5566 | 15.8529 | 1 | 31.2332
SING OPN LIN 553 342601-342604(1) | OPEN LINE FROM BUS 342601 [4JACKSNVIL 138.00] TO BUS 342604 [4JACKSNVIL T138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 2.0156 | 91.4649 | 1 | 3.3691
SING OPN LIN 554 342604-342631(1) | OPEN LINE FROM BUS 342604 [4JACKSNVIL T138.00] TO BUS 342631 [4PARIS T 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.7141
SING OPN LIN 555 342604-925980(1) | OPEN LINE FROM BUS 342604 [4JACKSNVIL T138.00] TO BUS 925980 [AC1-074 TAP 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.1609 | 13.7201
SING OPN LIN 556 342607-342610(1) | OPEN LINE FROM BUS 342607 [4JK SMITH 138.00] TO BUS 342610 [4JK SMITH 21138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.33222 | 18.9588
SING OPN LIN 557 342607-342613(1) | OPEN LINE FROM BUS 342607 [4JK SMITH 138.00] TO BUS 342613 [4JK SMITH 22138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.30912 | 18.2309
SING OPN LIN 558 342607-342637(1) | OPEN LINE FROM BUS 342607 [4JK SMITH 138.00] TO BUS 342637 [4POWELL CO 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.18271 | 8.4059
SING OPN LIN 559 342607-342688(1) | OPEN LINE FROM BUS 342607 [4JK SMITH 138.00] TO BUS 342688 [4UNION CTY T138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.88979 | 44.5733
SING OPN LIN 560 342610-342832(1) | OPEN LINE FROM BUS 342610 [4JK SMITH 21138.00] TO BUS 342832 [7JK SMITH 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.31097 | 18.3448
SING OPN LIN 561 342613-342832(1) | OPEN LINE FROM BUS 342613 [4JK SMITH 22138.00] TO BUS 342832 [7JK SMITH 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.29423 | 18.0454
SING OPN LIN 562 342622-342625(1) | OPEN LINE FROM BUS 342622 [4MAYSVIL I T138.00] TO BUS 342625 [4MAYSVIL IND138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.15445 | 9.3005 | 1 | 8.0269
SING OPN LIN 563 342622-342634(1) | OPEN LINE FROM BUS 342622 [4MAYSVIL I T138.00] TO BUS 342634 [4PLUMVILLE 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.283 | 14.3251
SING OPN LIN 564 342622-342664(1) | OPEN LINE FROM BUS 342622 [4MAYSVIL I T138.00] TO BUS 342664 [4SPURLOCK 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.2025 | 13.549
SING OPN LIN 565 342637-342784(1) | OPEN LINE FROM BUS 342637 [4POWELL CO 138.00] TO BUS 342784 [5POWELL CO 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.40206 | 12.1931
SING OPN LIN 566 342640-342664(1) | OPEN LINE FROM BUS 342640 [4RENAKER 138.00] TO BUS 342664 [4SPURLOCK 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 9.5255
SING OPN LIN 567 342640-925980(1) | OPEN LINE FROM BUS 342640 [4RENAKER 138.00] TO BUS 925980 [AC1-074 TAP 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.8348 | 22.6927
SING OPN LIN 568 342643-342646(1) | OPEN LINE FROM BUS 342643 [4RICHWOOD 138.00] TO BUS 342646 [4RICHWOOD T 138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 2.2823 | 24.2105 | 1 | 11.3427
SING OPN LIN 569 342646-342667(1) | OPEN LINE FROM BUS 342646 [4RICHWOOD T 138.00] TO BUS 342667 [4STANLEY PRK138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 5.0798
SING OPN LIN 570 342649-342658(1) | OPEN LINE FROM BUS 342649 [4ROWAN CO 138.00] TO BUS 342658 [4SKAGGS 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.2434 | 45.3746
SING OPN LIN 571 342661-342664(1) | OPEN LINE FROM BUS 342661 [4SPUR-KENT-R138.00] TO BUS 342664 [4SPURLOCK 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.22841 | 7.5625
SING OPN LIN 572 342664-342667(1) | OPEN LINE FROM BUS 342664 [4SPURLOCK 138.00] TO BUS 342667 [4STANLEY PRK138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.21804 | 5.3657
SING OPN LIN 573 342664-342838(1) | OPEN LINE FROM BUS 342664 [4SPURLOCK 138.00] TO BUS 342838 [7SPURLOCK 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.34301 | 21.6709
SING OPN LIN 574 342664-342838(2) | OPEN LINE FROM BUS 342664 [4SPURLOCK 138.00] TO BUS 342838 [7SPURLOCK 345.00] CKT 2 | TRUE | Met convergence tolerances | 0 | 0.1935 | 12.9157
SING OPN LIN 575 342664-342838(3) | OPEN LINE FROM BUS 342664 [4SPURLOCK 138.00] TO BUS 342838 [7SPURLOCK 345.00] CKT 3 | TRUE | Met convergence tolerances | 0 | 0.30892 | 19.6238
SING OPN LIN 576 342670-342673(1) | OPEN LINE FROM BUS 342670 [4STERLING 138.00] TO BUS 342673 [4STERLNG T 138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.15534 | 7.6125 | 1 | 6.9793
SING OPN LIN 577 342676-342679(1) | OPEN LINE FROM BUS 342676 [4THREE FK T 138.00] TO BUS 342679 [4THREE FORKS138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.19003 | 7.4663 | 1 | 3.0944
SING OPN LIN 578 342685-342688(1) | OPEN LINE FROM BUS 342685 [4UNION CITY 138.00] TO BUS 342688 [4UNION CTY T138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14555 | 2.8116 | 1 | 6.4748
SING OPN LIN 579 342694-342813(1) | OPEN LINE FROM BUS 342694 [5BARREN CO 161.00] TO BUS 342813 [5SUMM SOL 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.9513
SING OPN LIN 580 342697-342780(1) | OPEN LINE FROM BUS 342697 [5BEATTYV J 161.00] TO BUS 342780 [5MILL CRK T 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.39683 | 12.098
SING OPN LIN 581 342700-342819(1) | OPEN LINE FROM BUS 342700 [5BULLITT CO 161.00] TO BUS 342819 [5TAYLORSV T 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.1588 | 24.6891
SING OPN LIN 582 342703-342769(1) | OPEN LINE FROM BUS 342703 [5CASEY CO 161.00] TO BUS 342769 [5MARION CO 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.1502 | 24.3555
SING OPN LIN 583 342715-342718(1) | OPEN LINE FROM BUS 342715 [5COOPER1 161.00] TO BUS 342718 [5COOPER2 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.58511 | 12.4467
SING OPN LIN 584 342715-342790(1) | OPEN LINE FROM BUS 342715 [5COOPER1 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.3654 | 15.2096
SING OPN LIN 585 342715-342799(1) | OPEN LINE FROM BUS 342715 [5COOPER1 161.00] TO BUS 342799 [5S OAKHILL 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.7502 | 34.3329
SING OPN LIN 586 342718-342727(1) | OPEN LINE FROM BUS 342718 [5COOPER2 161.00] TO BUS 342727 [5DENNY 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.6135
SING OPN LIN 587 342718-342757(1) | OPEN LINE FROM BUS 342718 [5COOPER2 161.00] TO BUS 342757 [5LAUREL DAM 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.2347 | 16.1224
SING OPN LIN 588 342721-342724(1) | OPEN LINE FROM BUS 342721 [5DARWIN TH 161.00] TO BUS 342724 [5DARWIN TH T161.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.7959 | 8.9612 | 1 | 15.3905
SING OPN LIN 589 342724-342766(1) | OPEN LINE FROM BUS 342724 [5DARWIN TH T161.00] TO BUS 342766 [5LITTLE MT T161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.93332 | 17.8552
SING OPN LIN 590 342724-342808(1) | OPEN LINE FROM BUS 342724 [5DARWIN TH T161.00] TO BUS 342808 [5SHELBY CO 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.72887 | 15.8542
SING OPN LIN 591 342730-342820(1) | OPEN LINE FROM BUS 342730 [5FALL ROCK 161.00] TO BUS 342820 [5TYNER 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14405 | 2.3602
SING OPN LIN 592 342733-342817(1) | OPEN LINE FROM BUS 342733 [5GREEN CO 161.00] TO BUS 342817 [5TAYLOR CO J161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.99343 | 11.2996
SING OPN LIN 593 342733-943820(1) | OPEN LINE FROM BUS 342733 [5GREEN CO 161.00] TO BUS 943820 [AF1-050 TAP 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.7239 | 18.9959
SING OPN LIN 594 342736-342739(1) | OPEN LINE FROM BUS 342736 [5GREEN HAL T161.00] TO BUS 342739 [5GREEN HALL 161.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14571 | 4.5763 | 1 | 2.6482
SING OPN LIN 595 342736-342820(1) | OPEN LINE FROM BUS 342736 [5GREEN HAL T161.00] TO BUS 342820 [5TYNER 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.4026
SING OPN LIN 596 342742-342745(1) | OPEN LINE FROM BUS 342742 [5JABEZ 161.00] TO BUS 342745 [5JABEZ T 161.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 2.8351 | 1 | 4.1686
SING OPN LIN 597 342745-342751(1) | OPEN LINE FROM BUS 342745 [5JABEZ T 161.00] TO BUS 342751 [5JAMESTOWN T161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.487 | 32.9645
SING OPN LIN 598 342745-342799(1) | OPEN LINE FROM BUS 342745 [5JABEZ T 161.00] TO BUS 342799 [5S OAKHILL 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.416 | 33.1227
SING OPN LIN 599 342748-342751(1) | OPEN LINE FROM BUS 342748 [5JAMESTOWN 161.00] TO BUS 342751 [5JAMESTOWN T161.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14177 | 2.5573 | 1 | 6.8602
SING OPN LIN 600 342751-342792(1) | OPEN LINE FROM BUS 342751 [5JAMESTOWN T161.00] TO BUS 342792 [5RUSS SOL 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.5053 | 32.9515
SING OPN LIN 601 342754-342757(1) | OPEN LINE FROM BUS 342754 [5LAUREL CO 161.00] TO BUS 342757 [5LAUREL DAM 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.94825 | 13.6007
SING OPN LIN 602 342754-342783(1) | OPEN LINE FROM BUS 342754 [5LAUREL CO 161.00] TO BUS 342783 [5PITTSBURG 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 4.5032
SING OPN LIN 603 342760-342790(1) | OPEN LINE FROM BUS 342760 [5LIBERTY J 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.5507 | 16.1832
SING OPN LIN 604 342763-342766(1) | OPEN LINE FROM BUS 342763 [5LITTLE MT 161.00] TO BUS 342766 [5LITTLE MT T161.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 3.248 | 1 | 5.1178
SING OPN LIN 605 342766-342819(1) | OPEN LINE FROM BUS 342766 [5LITTLE MT T161.00] TO BUS 342819 [5TAYLORSV T 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.0073 | 19.5291
SING OPN LIN 606 342769-342770(1) | OPEN LINE FROM BUS 342769 [5MARION CO 161.00] TO BUS 342770 [4MARION CO 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.81954 | 47.1927
SING OPN LIN 607 342769-342770(2) | OPEN LINE FROM BUS 342769 [5MARION CO 161.00] TO BUS 342770 [4MARION CO 138.00] CKT 2 | TRUE | Met convergence tolerances | 0 | 0.81954 | 47.1927
SING OPN LIN 608 342769-342770(3) | OPEN LINE FROM BUS 342769 [5MARION CO 161.00] TO BUS 342770 [4MARION CO 138.00] CKT 3 | TRUE | Met convergence tolerances | 0 | 0.81954 | 47.1927
SING OPN LIN 609 342769-342770(4) | OPEN LINE FROM BUS 342769 [5MARION CO 161.00] TO BUS 342770 [4MARION CO 138.00] CKT 4 | TRUE | Met convergence tolerances | 0 | 0.81954 | 47.1927
SING OPN LIN 610 342769-342781(1) | OPEN LINE FROM BUS 342769 [5MARION CO 161.00] TO BUS 342781 [5N LEBANON 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.6287 | 20.0934
SING OPN LIN 611 342772-342797(1) | OPEN LINE FROM BUS 342772 [5MARION IP 161.00] TO BUS 342797 [5S MARION IT161.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14263 | 9.8045 | 1 | 7.3059
SING OPN LIN 612 342775-342781(1) | OPEN LINE FROM BUS 342775 [5MARION IP T161.00] TO BUS 342781 [5N LEBANON 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 2.0571 | 21.7425
SING OPN LIN 613 342775-342797(1) | OPEN LINE FROM BUS 342775 [5MARION IP T161.00] TO BUS 342797 [5S MARION IT161.00] CKT 1 | TRUE | Met convergence tolerances | 3 | 1.7824 | 17.5297 | 2 | 37.708
SING OPN LIN 614 342775-342805(1) | OPEN LINE FROM BUS 342775 [5MARION IP T161.00] TO BUS 342805 [5SALOMA T 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 2.4741 | 25.8376
SING OPN LIN 615 342779-342780(1) | OPEN LINE FROM BUS 342779 [5MILLER CRK 161.00] TO BUS 342780 [5MILL CRK T 161.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 2.72 | 1 | 3.1325
SING OPN LIN 616 342780-342784(1) | OPEN LINE FROM BUS 342780 [5MILL CRK T 161.00] TO BUS 342784 [5POWELL CO 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.40684 | 12.3923
SING OPN LIN 617 342782-342787(1) | OPEN LINE FROM BUS 342782 [5PINEVILL EK161.00] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.16905 | 6.8169
SING OPN LIN 618 342783-342820(1) | OPEN LINE FROM BUS 342783 [5PITTSBURG 161.00] TO BUS 342820 [5TYNER 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.6642
SING OPN LIN 619 342787-342790(1) | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.52235 | 9.2252
SING OPN LIN 620 342792-342796(1) | OPEN LINE FROM BUS 342792 [5RUSS SOL 161.00] TO BUS 342796 [5RUSSEL CO J161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 2.2647 | 27.8196
SING OPN LIN 621 342793-342796(1) | OPEN LINE FROM BUS 342793 [5RUSSEL CO 161.00] TO BUS 342796 [5RUSSEL CO J161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 2.4977 | 84.1338
SING OPN LIN 622 342797-342798(1) | OPEN LINE FROM BUS 342797 [5S MARION IT161.00] TO BUS 342798 [5S MARION IP161.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 1.4298 | 14.4363 | 1 | 30.4021
SING OPN LIN 623 342802-342805(1) | OPEN LINE FROM BUS 342802 [5SALOMA 161.00] TO BUS 342805 [5SALOMA T 161.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 2.0898 | 22.4981 | 1 | 12.0099
SING OPN LIN 624 342805-944150(1) | OPEN LINE FROM BUS 342805 [5SALOMA T 161.00] TO BUS 944150 [AF1-083 TAP 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.3749 | 17.4758
SING OPN LIN 625 342813-342814(1) | OPEN LINE FROM BUS 342813 [5SUMM SOL 161.00] TO BUS 342814 [5SUMM SHADE 161.00] CKT 1 | FALSE | Blown up | 0 | 1064.5896 | 14663.2031
SING OPN LIN 626 342814-943820(1) | OPEN LINE FROM BUS 342814 [5SUMM SHADE 161.00] TO BUS 943820 [AF1-050 TAP 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.1921 | 57.3257
SING OPN LIN 627 342817-944150(1) | OPEN LINE FROM BUS 342817 [5TAYLOR CO J161.00] TO BUS 944150 [AF1-083 TAP 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 2.3754 | 24.1976
SING OPN LIN 628 342818-342819(1) | OPEN LINE FROM BUS 342818 [5TAYLORSVILL161.00] TO BUS 342819 [5TAYLORSV T 161.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.27167 | 12.1543 | 1 | 10.0637
SING OPN LIN 629 342829-342835(1) | OPEN LINE FROM BUS 342829 [7AVON 345.00] TO BUS 342835 [7N CLARK 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.4944 | 16.1908
SING OPN LIN 630 342832-342835(1) | OPEN LINE FROM BUS 342832 [7JK SMITH 345.00] TO BUS 342835 [7N CLARK 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.4483 | 18.7931
SING OPN LIN 631 342832-342841(1) | OPEN LINE FROM BUS 342832 [7JK SMITH 345.00] TO BUS 342841 [7W GARRARDEK345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.935 | 20.6825
SING OPN LIN 632 342835-342838(1) | OPEN LINE FROM BUS 342835 [7N CLARK 345.00] TO BUS 342838 [7SPURLOCK 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.61714 | 7.4307
SING OPN LIN 633 925980-925981(1) | OPEN LINE FROM BUS 925980 [AC1-074 TAP 138.00] TO BUS 925981 [AC1-074 C O1138.00] CKT 1 | TRUE | Met convergence tolerances | 2 | 1.6733 | 75.8365
SING OPN LIN 634 925980-932551(1) | OPEN LINE FROM BUS 925980 [AC1-074 TAP 138.00] TO BUS 932551 [AC2-075 C 138.00] CKT 1 | TRUE | Met convergence tolerances | 2 | 1.7556 | 19.3579
SING OPN LIN 635 925981-925982(1) | OPEN LINE FROM BUS 925981 [AC1-074 C O1138.00] TO BUS 925982 [AC1-074 E O1138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 2.0919 | 22.7193
SING OPN LIN 636 932551-932552(1) | OPEN LINE FROM BUS 932551 [AC2-075 C 138.00] TO BUS 932552 [AC2-075 E 138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 4.1868
SING OPN LIN 637 936380-936381(1) | OPEN LINE FROM BUS 936380 [AD2-048 TAP 69.000] TO BUS 936381 [AD2-048 C 69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 1.0095 | 17.2677
SING OPN LIN 638 936381-936382(1) | OPEN LINE FROM BUS 936381 [AD2-048 C 69.000] TO BUS 936382 [AD2-048 E 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 1.5604 | 17.4347
SING OPN LIN 639 940830-940831(1) | OPEN LINE FROM BUS 940830 [AE2-071 TAP 69.000] TO BUS 940831 [AE2-071 C 69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 1.535 | 18.8534
SING OPN LIN 640 940831-940832(1) | OPEN LINE FROM BUS 940831 [AE2-071 C 69.000] TO BUS 940832 [AE2-071 E 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 1.1393 | 13.2541
SING OPN LIN 641 942410-942411(1) | OPEN LINE FROM BUS 942410 [AE2-254 TAP 69.000] TO BUS 942411 [AE2-254 C O169.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 1.0098 | 17.0131
SING OPN LIN 642 942411-942412(1) | OPEN LINE FROM BUS 942411 [AE2-254 C O169.000] TO BUS 942412 [AE2-254 E O169.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 1.8458 | 19.8965
SING OPN LIN 643 943700-943701(1) | OPEN LINE FROM BUS 943700 [AF1-038 TAP 69.000] TO BUS 943701 [AF1-038 C 69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 1.1443 | 19.0379
SING OPN LIN 644 943701-943702(1) | OPEN LINE FROM BUS 943701 [AF1-038 C 69.000] TO BUS 943702 [AF1-038 E 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 2.068 | 22.0898
SING OPN LIN 645 943820-943821(1) | OPEN LINE FROM BUS 943820 [AF1-050 TAP 161.00] TO BUS 943821 [AF1-050 C 161.00] CKT 1 | TRUE | Met convergence tolerances | 2 | 1.0432 | 17.4649
SING OPN LIN 646 943821-943822(1) | OPEN LINE FROM BUS 943821 [AF1-050 C 161.00] TO BUS 943822 [AF1-050 E 161.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 1.9163 | 20.5875
SING OPN LIN 647 944150-944151(1) | OPEN LINE FROM BUS 944150 [AF1-083 TAP 161.00] TO BUS 944151 [AF1-083 C O1161.00] CKT 1 | TRUE | Met convergence tolerances | 2 | 1.9433 | 60.897
SING OPN LIN 648 944151-944152(1) | OPEN LINE FROM BUS 944151 [AF1-083 C O1161.00] TO BUS 944152 [AF1-083 E O1161.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 1.8155 | 19.5908
SING OPN TIE 649 341020-243725(1) | OPEN LINE FROM BUS 341020 [2ARGENTUM 69.000] TO BUS 243725 [05GRAYSB 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.2326
SING OPN TIE 650 341071-324430(1) | OPEN LINE FROM BUS 341071 [2BEATTYV 69.000] TO BUS 324430 [2BEATTYVI KU69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.7374
SING OPN TIE 651 341089-325102(1) | OPEN LINE FROM BUS 341089 [2BEKAERT 69.000] TO BUS 325102 [2W SHELBY 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.7689
SING OPN TIE 652 341161-324213(1) | OPEN LINE FROM BUS 341161 [2BONNIV EK 69.000] TO BUS 324213 [4BONNIEVILLE138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14372 | 7.9526
SING OPN TIE 653 341188-324463(1) | OPEN LINE FROM BUS 341188 [2BRACKEN CO 69.000] TO BUS 324463 [2CARNTOWN 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 4.4498
SING OPN TIE 654 341188-324722(1) | OPEN LINE FROM BUS 341188 [2BRACKEN CO 69.000] TO BUS 324722 [2SHARON KU 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.19424 | 10.0493
SING OPN TIE 655 341317-324474(1) | OPEN LINE FROM BUS 341317 [2CLAY VILLAG69.000] TO BUS 324474 [2CLAY VILG T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.89723 | 9.9325
SING OPN TIE 656 341320-324830(1) | OPEN LINE FROM BUS 341320 [2COBURG 69.000] TO BUS 324830 [2CAMPBELV EK69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.2419
SING OPN TIE 657 341406-324530(1) | OPEN LINE FROM BUS 341406 [2DUNCAN LN T69.000] TO BUS 324530 [2FAWKES 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 4.1858
SING OPN TIE 658 341407-324425(1) | OPEN LINE FROM BUS 341407 [2E BARDSTOWN69.000] TO BUS 324425 [2BARDT IND T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.51692 | 12.4546
SING OPN TIE 659 341461-243721(Z1) | OPEN LINE FROM BUS 341461 [2FALCON EK 69.000] TO BUS 243721 [05FALCON 69.000] CKT Z1 | TRUE | Met convergence tolerances | 1 | 0.17593 | 13.761 | 1 | 10.79
SING OPN TIE 660 341515-324600(1) | OPEN LINE FROM BUS 341515 [2GARRARD CO 69.000] TO BUS 324600 [2LANCASTR KU69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.53368 | 7.7006
SING OPN TIE 661 341539-324784(1) | OPEN LINE FROM BUS 341539 [2GOLDBUG 69.000] TO BUS 324784 [2WOFFORD 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.7206
SING OPN TIE 662 341554-243726(1) | OPEN LINE FROM BUS 341554 [2GRAYSON J 69.000] TO BUS 243726 [05GRAYSO 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.17347 | 13.0816 | 1 | 9.905
SING OPN TIE 663 341563-324554(1) | OPEN LINE FROM BUS 341563 [2GREEN CO 69.000] TO BUS 324554 [2GRENSBRG KU69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.2836 | 16.2455
SING OPN TIE 664 341605-251579(1) | OPEN LINE FROM BUS 341605 [2HEBRON 69.000] TO BUS 251579 [08HEBRON 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.0063
SING OPN TIE 665 341608-243812(Z1) | OPEN LINE FROM BUS 341608 [2HELECHAW 69.000] TO BUS 243812 [05LEE C 69.000] CKT Z1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 5.3072
SING OPN TIE 666 341632-324575(1) | OPEN LINE FROM BUS 341632 [2HODGENVILLE69.000] TO BUS 324575 [2HODGENV KU 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 2.9392 | 31.8486
SING OPN TIE 667 341632-324660(1) | OPEN LINE FROM BUS 341632 [2HODGENVILLE69.000] TO BUS 324660 [2NEW HAVEN 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 2.6287
SING OPN TIE 668 341713-324519(1) | OPEN LINE FROM BUS 341713 [2KARGLE 69.000] TO BUS 324519 [2ETOWN KU 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.4258 | 16.632
SING OPN TIE 669 341740-324576(1) | OPEN LINE FROM BUS 341740 [2LAUREL CO 69.000] TO BUS 324576 [2HOPEWELL 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 4.5082
SING OPN TIE 670 341752-243737(Z1) | OPEN LINE FROM BUS 341752 [2LEON 69.000] TO BUS 243737 [05LEONKY 69.000] CKT Z1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.393
SING OPN TIE 671 341755-324527(1) | OPEN LINE FROM BUS 341755 [2LIBER CH T 69.000] TO BUS 324527 [2FARLEY KU 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.4013
SING OPN TIE 672 341890-246973(Z1) | OPEN LINE FROM BUS 341890 [2MORGAN CO 69.000] TO BUS 246973 [05MORGCO 69.000] CKT Z1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.6199
SING OPN TIE 673 341923-324717(1) | OPEN LINE FROM BUS 341923 [2MURPHYSVIL 69.000] TO BUS 324717 [2SARDIS TAP 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 9.3123
SING OPN TIE 674 341923-325019(1) | OPEN LINE FROM BUS 341923 [2MURPHYSVIL 69.000] TO BUS 325019 [2KENTON-6 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 2.0333 | 20.8636
SING OPN TIE 675 341929-324662(1) | OPEN LINE FROM BUS 341929 [2N LONDON 69.000] TO BUS 324662 [2N LONDON KU69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14229 | 2.8291
SING OPN TIE 676 341935-324736(1) | OPEN LINE FROM BUS 341935 [2N SPRINGFLD69.000] TO BUS 324736 [2SPRINGFL KU69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.9411 | 53.2074
SING OPN TIE 677 341944-324288(1) | OPEN LINE FROM BUS 341944 [2NELSON CO 69.000] TO BUS 324288 [4NELSON CO 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.9849
SING OPN TIE 678 342007-324455(1) | OPEN LINE FROM BUS 342007 [2OWEN CO 69.000] TO BUS 324455 [2BROMLEY 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.22151 | 5.7563
SING OPN TIE 679 342008-324290(1) | OPEN LINE FROM BUS 342008 [4OWEN CO 138.00] TO BUS 324290 [4OWEN CO TAP138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.43269 | 7.0053
SING OPN TIE 680 342055-243742(1) | OPEN LINE FROM BUS 342055 [2PELFREY 69.000] TO BUS 243742 [05CORYSS 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 4.2603 | 1 | 3.5497
SING OPN TIE 681 342058-324951(1) | OPEN LINE FROM BUS 342058 [2PENN 69.000] TO BUS 324951 [2SCOTT CO 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.30176 | 5.9155
SING OPN TIE 682 342133-324492(1) | OPEN LINE FROM BUS 342133 [2RENAKER 69.000] TO BUS 324492 [2CYNTHIAN SW69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.5121 | 7.5028
SING OPN TIE 683 342157-324708(1) | OPEN LINE FROM BUS 342157 [2ROGERSVIL J69.000] TO BUS 324708 [2ROGERSVILLE69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.1921
SING OPN TIE 684 342184-324445(1) | OPEN LINE FROM BUS 342184 [2S ANDERSON 69.000] TO BUS 324445 [2BONDS MILL 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.0881
SING OPN TIE 685 342184-324445(2) | OPEN LINE FROM BUS 342184 [2S ANDERSON 69.000] TO BUS 324445 [2BONDS MILL 69.000] CKT 2 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.0881
SING OPN TIE 686 342218-247897(Z1) | OPEN LINE FROM BUS 342218 [2SALT LICK 138.00] TO BUS 247897 [05SNAG FK SS138.00] CKT Z1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 3.8073 | 1 | 4.2393
SING OPN TIE 687 342232-324787(1) | OPEN LINE FROM BUS 342232 [2SEWELLTON 69.000] TO BUS 324787 [2UNION UNDWR69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.6528 | 19.2421
SING OPN TIE 688 342248-324718(1) | OPEN LINE FROM BUS 342248 [2SHELBY TAP 69.000] TO BUS 324718 [2SHELBY CO T69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.5638
SING OPN TIE 689 342287-324531(1) | OPEN LINE FROM BUS 342287 [2SOMERSET KU69.000] TO BUS 324531 [2FERGUSON SO69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.1077 | 14.0494
SING OPN TIE 690 342287-324737(1) | OPEN LINE FROM BUS 342287 [2SOMERSET KU69.000] TO BUS 324737 [2SOMERSET SO69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.87593 | 12.9403
SING OPN TIE 691 342307-324509(1) | OPEN LINE FROM BUS 342307 [2STEPHENSBRG69.000] TO BUS 324509 [2EASTVIEW 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14177 | 3.0168
SING OPN TIE 692 342340-324519(1) | OPEN LINE FROM BUS 342340 [2THARP T 69.000] TO BUS 324519 [2ETOWN KU 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.60787 | 38.221
SING OPN TIE 693 342343-246971(1) | OPEN LINE FROM BUS 342343 [2THELMA 69.000] TO BUS 246971 [05THELM2 69.000] CKT 1 | FALSE | Iteration limit exceeded | 0 | 1.7513 | 25.6598
SING OPN TIE 694 342454-251315(1) | OPEN LINE FROM BUS 342454 [2W M SMITH 69.000] TO BUS 251315 [08EKSMTH 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 3.2656 | 1 | 3.651
SING OPN TIE 695 342487-250148(1) | OPEN LINE FROM BUS 342487 [2WEBSTER RD 69.000] TO BUS 250148 [08EKPWEB 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.8137
SING OPN TIE 696 342538-243688(1) | OPEN LINE FROM BUS 342538 [4ARGENTUM 138.00] TO BUS 243688 [05S.PORT MTR138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 5.123
SING OPN TIE 697 342544-324275(1) | OPEN LINE FROM BUS 342544 [4AVON-R 138.00] TO BUS 324275 [4LOUDON AVE 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.7709 | 19.0807
SING OPN TIE 698 342547-324210(1) | OPEN LINE FROM BUS 342547 [4BAKER LN 138.00] TO BUS 324210 [4BAKER LANE 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.18924 | 6.0148
SING OPN TIE 699 342559-250054(1) | OPEN LINE FROM BUS 342559 [4BOONE CO 138.00] TO BUS 250054 [08LONGBR 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 2.2768 | 24.3869
SING OPN TIE 700 342565-325925(1) | OPEN LINE FROM BUS 342565 [4BOONESBOR T138.00] TO BUS 325925 [4BOONSBORO N138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 4.5134
SING OPN TIE 701 342568-324047(1) | OPEN LINE FROM BUS 342568 [4CENT HARDIN138.00] TO BUS 324047 [4BLACKBRANCH138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.5986
SING OPN TIE 702 342568-324261(1) | OPEN LINE FROM BUS 342568 [4CENT HARDIN138.00] TO BUS 324261 [4HARDIN CO 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.84673 | 9.9888
SING OPN TIE 703 342577-324247(1) | OPEN LINE FROM BUS 342577 [4FAWKES EK 138.00] TO BUS 324247 [4FAWKES TAP 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.1084
SING OPN TIE 704 342577-324248(1) | OPEN LINE FROM BUS 342577 [4FAWKES EK 138.00] TO BUS 324248 [4FAWKES KU 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.1316
SING OPN TIE 705 342586-324253(1) | OPEN LINE FROM BUS 342586 [4GALLATIN CO138.00] TO BUS 324253 [4GHENT 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.76688 | 41.7467
SING OPN TIE 706 342595-250152(1) | OPEN LINE FROM BUS 342595 [4HEBRON 138.00] TO BUS 250152 [08HEBRNG 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 4.4057
SING OPN TIE 707 342607-342918(1) | OPEN LINE FROM BUS 342607 [4JK SMITH 138.00] TO BUS 342918 [1JKCT 1G 13.800] CKT 1 | TRUE | Met convergence tolerances | 1 | 2.1817 | 98.361
SING OPN TIE 708 342607-342921(1) | OPEN LINE FROM BUS 342607 [4JK SMITH 138.00] TO BUS 342921 [1JKCT 2G 13.800] CKT 1 | TRUE | Met convergence tolerances | 1 | 2.1802 | 99.3519
SING OPN TIE 709 342607-342924(1) | OPEN LINE FROM BUS 342607 [4JK SMITH 138.00] TO BUS 342924 [1JKCT 3G 13.800] CKT 1 | TRUE | Met convergence tolerances | 1 | 2.1817 | 98.5546
SING OPN TIE 710 342607-342927(1) | OPEN LINE FROM BUS 342607 [4JK SMITH 138.00] TO BUS 342927 [1JKCT 4G 13.800] CKT 1 | TRUE | Met convergence tolerances | 1 | 1.5287 | 69.8085
SING OPN TIE 711 342607-342930(1) | OPEN LINE FROM BUS 342607 [4JK SMITH 138.00] TO BUS 342930 [1JKCT 5G 13.800] CKT 1 | TRUE | Met convergence tolerances | 1 | 1.5286 | 70.0508
SING OPN TIE 712 342607-342933(1) | OPEN LINE FROM BUS 342607 [4JK SMITH 138.00] TO BUS 342933 [1JKCT 6G 13.800] CKT 1 | TRUE | Met convergence tolerances | 1 | 1.5289 | 69.9037
SING OPN TIE 713 342607-342936(1) | OPEN LINE FROM BUS 342607 [4JK SMITH 138.00] TO BUS 342936 [1JKCT 7G 13.800] CKT 1 | TRUE | Met convergence tolerances | 1 | 1.5291 | 70.0855
SING OPN TIE 714 342616-342948(1) | OPEN LINE FROM BUS 342616 [4LOVE HYDRO 138.00] TO BUS 342948 [1LOVE HYDRO 4.1600] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.91414 | 15.5423
SING OPN TIE 715 342631-324328(1) | OPEN LINE FROM BUS 342631 [4PARIS T 138.00] TO BUS 324328 [4PARIS 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.35497 | 23.6734
SING OPN TIE 716 342649-324302(1) | OPEN LINE FROM BUS 342649 [4ROWAN CO 138.00] TO BUS 324302 [4RODBURN 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 2.3671 | 22.7819
SING OPN TIE 717 342661-324267(1) | OPEN LINE FROM BUS 342661 [4SPUR-KENT-R138.00] TO BUS 324267 [4KENTON 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.23079 | 7.2876
SING OPN TIE 718 342664-342957(1) | OPEN LINE FROM BUS 342664 [4SPURLOCK 138.00] TO BUS 342957 [1SPURLK1G 22.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.32406 | 12.8362 | 1 | 44
SING OPN TIE 719 342688-324276(1) | OPEN LINE FROM BUS 342688 [4UNION CTY T138.00] TO BUS 324276 [4LAKE REBA T138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.51976 | 7.5502
SING OPN TIE 720 342697-324138(1) | OPEN LINE FROM BUS 342697 [5BEATTYV J 161.00] TO BUS 324138 [5DELVINTA 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.28852 | 8.4059
SING OPN TIE 721 342697-324430(1) | OPEN LINE FROM BUS 342697 [5BEATTYV J 161.00] TO BUS 324430 [2BEATTYVI KU69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.3409
SING OPN TIE 722 342700-326975(1) | OPEN LINE FROM BUS 342700 [5BULLITT CO 161.00] TO BUS 326975 [5CEDAR GRV 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.83807 | 9.874
SING OPN TIE 723 342700-326998(1) | OPEN LINE FROM BUS 342700 [5BULLITT CO 161.00] TO BUS 326998 [5BULLITT TAP161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 2.2891 | 23.8483
SING OPN TIE 724 342718-324141(1) | OPEN LINE FROM BUS 342718 [5COOPER2 161.00] TO BUS 324141 [5ELIHU 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.95464 | 22.6584
SING OPN TIE 725 342732-361603(1) | OPEN LINE FROM BUS 342732 [5FOX HOLLOW 161.00] TO BUS 361603 [5E GLASGOW T161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.0163 | 11.8733
SING OPN TIE 726 342736-324138(1) | OPEN LINE FROM BUS 342736 [5GREEN HAL T161.00] TO BUS 324138 [5DELVINTA 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.5001
SING OPN TIE 727 342757-342945(1) | OPEN LINE FROM BUS 342757 [5LAUREL DAM 161.00] TO BUS 342945 [1LAUREL 1G 13.800] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14503 | 2.3345
SING OPN TIE 728 342770-324271(1) | OPEN LINE FROM BUS 342770 [4MARION CO 138.00] TO BUS 324271 [4LEBANON 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.1132
SING OPN TIE 729 342770-324271(2) | OPEN LINE FROM BUS 342770 [4MARION CO 138.00] TO BUS 324271 [4LEBANON 138.00] CKT 2 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.1132
SING OPN TIE 730 342770-324271(3) | OPEN LINE FROM BUS 342770 [4MARION CO 138.00] TO BUS 324271 [4LEBANON 138.00] CKT 3 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.1132
SING OPN TIE 731 342778-360473(1) | OPEN LINE FROM BUS 342778 [5MCCREARY CO161.00] TO BUS 360473 [5JELLICO TN 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 2.2751 | 27.2535
SING OPN TIE 732 342778-360486(1) | OPEN LINE FROM BUS 342778 [5MCCREARY CO161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.6082 | 17.1599
SING OPN TIE 733 342778-361579(1) | OPEN LINE FROM BUS 342778 [5MCCREARY CO161.00] TO BUS 361579 [5WINFIELD TN161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.7516 | 36.8951
SING OPN TIE 734 342782-342837(1) | OPEN LINE FROM BUS 342782 [5PINEVILL EK161.00] TO BUS 342837 [7PINEVILL EK345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.7426 | 8.6118
SING OPN TIE 735 342783-324688(1) | OPEN LINE FROM BUS 342783 [5PITTSBURG 161.00] TO BUS 324688 [2PITTSBRG KU69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.36997 | 33.4736
SING OPN TIE 736 342796-360448(1) | OPEN LINE FROM BUS 342796 [5RUSSEL CO J161.00] TO BUS 360448 [5WOLF CRK HP161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.062 | 45.3416
SING OPN TIE 737 342814-360334(1) | OPEN LINE FROM BUS 342814 [5SUMM SHADE 161.00] TO BUS 360334 [5SUMMER SHAD161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.9446
SING OPN TIE 738 342814-361788(1) | OPEN LINE FROM BUS 342814 [5SUMM SHADE 161.00] TO BUS 361788 [5SUM SHAD TP161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.9096
SING OPN TIE 739 342817-325921(1) | OPEN LINE FROM BUS 342817 [5TAYLOR CO J161.00] TO BUS 325921 [5TAYLOR CO 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 3.0752
SING OPN TIE 740 342821-342839(1) | OPEN LINE FROM BUS 342821 [5TOMMY EK 161.00] TO BUS 342839 [7TOMMY EK 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.3641
SING OPN TIE 741 342821-342839(2) | OPEN LINE FROM BUS 342821 [5TOMMY EK 161.00] TO BUS 342839 [7TOMMY EK 345.00] CKT 2 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.3641
SING OPN TIE 742 342823-360486(1) | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.5666 | 22.7503
SING OPN TIE 743 342832-342939-342942(1) | OPEN LINE FROM BUS 342832 [7JK SMITH 345.00] TO BUS 342939 [1JKCT 9G 13.800] TO BUS 342942 [1JKCT 10G 13.800] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.16251 | 7.1934 | 2 | 6
SING OPN TIE 744 342838-249581(1) | OPEN LINE FROM BUS 342838 [7SPURLOCK 345.00] TO BUS 249581 [08MELDAL 345.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 2.6844 | 67.808
SING OPN TIE 745 342838-253077(1) | OPEN LINE FROM BUS 342838 [7SPURLOCK 345.00] TO BUS 253077 [09STUART 345.00] CKT 1 | FALSE | Iteration limit exceeded | 0 | 57.8265 | 1164.3668
SING OPN TIE 746 342838-342960(1) | OPEN LINE FROM BUS 342838 [7SPURLOCK 345.00] TO BUS 342960 [1SPURLK2G 22.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.95548 | 25.1026 | 1 | 45
SING OPN TIE 747 342838-342963(1) | OPEN LINE FROM BUS 342838 [7SPURLOCK 345.00] TO BUS 342963 [1SPURLK3G 18.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.88445 | 54.9998 | 1 | 20
SING OPN TIE 748 342838-342966(1) | OPEN LINE FROM BUS 342838 [7SPURLOCK 345.00] TO BUS 342966 [1SPURLK4G 18.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.35036 | 13.3144 | 1 | 38
SING OPN TIE 749 342841-325074(Z1) | OPEN LINE FROM BUS 342841 [7W GARRARDEK345.00] TO BUS 325074 [7W GARRARDKU345.00] CKT Z1 | TRUE | Met convergence tolerances | 0 | 1.7018 | 74.3974
SING OPN TIE 750 342844-384157(1) | OPEN LINE FROM BUS 342844 [8SOUTHGEN 500.00] TO BUS 384157 [8MILLER8 500.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14437 | 2.2126
SING OPN TIE 751 342847-243205(1) | OPEN LINE FROM BUS 342847 [9NORTHGEN 765.00] TO BUS 243205 [05COOK 765.00] CKT 1 | FALSE | Blown up | 1 | 1482.1409 | 62510.2695
BARREN CO - HORSECAVE 69 SS | OPEN BRANCH FROM BUS 341059 [2BARREN CO 69.000] TO BUS 341651 [2HORSECAVE J69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.079 | 13.4776
OPEN BRANCH FROM BUS 341651 [2HORSECAVE J69.000] TO BUS 341914 [2MUNFVILKU T69.000] CKT 1
CLOSE BRANCH FROM BUS 341650 [2HORSECAVE T69.000] TO BUS 342241 [2SEYMOUR T 69.000] CKT 1
CAVE CITY J-SEYMOUR T 69 SS | OPEN BRANCH FROM BUS 341275 [2CAVE CITY J69.000] TO BUS 342241 [2SEYMOUR T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 4.2648
CLOSE BRANCH FROM BUS 341650 [2HORSECAVE T69.000] TO BUS 342241 [2SEYMOUR T 69.000] CKT 1
CAVE CITY - CAVE CITY JCT 69 SS | OPEN BRANCH FROM BUS 341272 [2CAVE CITY 69.000] TO BUS 341275 [2CAVE CITY J69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 5.796
OPEN BRANCH FROM BUS 341059 [2BARREN CO 69.000] TO BUS 341275 [2CAVE CITY J69.000] CKT 1
OPEN BRANCH FROM BUS 341275 [2CAVE CITY J69.000] TO BUS 342241 [2SEYMOUR T 69.000] CKT 1
CLOSE BRANCH FROM BUS 341650 [2HORSECAVE T69.000] TO BUS 342241 [2SEYMOUR T 69.000] CKT 1
FOX HOLLOW - PARKWAY1 69 SS | OPEN BRANCH FROM BUS 341491 [2FOX HOLLOW 69.000] TO BUS 342037 [2PARKWAY 1 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.30111 | 13.101
CLOSE BRANCH FROM BUS 342040 [2PARKWAY 2 69.000] TO BUS 342043 [2PARKWAY 2 T69.000] CKT 1
WAYNE CO - ZULA TAP 69 SS | OPEN BRANCH FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342535 [2ZULA T 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.9558
CLOSE BRANCH FROM BUS 342532 [2ZULA J NO 69.000] TO BUS 342535 [2ZULA T 69.000] CKT 1
EKPC_P1-2_ARGEN - LEON69 | OPEN BRANCH FROM BUS 341020 [2ARGENTUM 69.000] TO BUS 341782 [2LOW GAP T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 2.2938 | 24.6369 | 5 | 31.3664
OPEN BRANCH FROM BUS 341779 [2LOW GAP 69.000] TO BUS 341782 [2LOW GAP T 69.000] CKT 1
OPEN BRANCH FROM BUS 341782 [2LOW GAP T 69.000] TO BUS 342475 [2WARNOCK 69.000] CKT 1
OPEN BRANCH FROM BUS 341266 [2CARTER CY T69.000] TO BUS 342475 [2WARNOCK 69.000] CKT 1
OPEN BRANCH FROM BUS 341263 [2CARTER CTY 69.000] TO BUS 341266 [2CARTER CY T69.000] CKT 1
OPEN BRANCH FROM BUS 341266 [2CARTER CY T69.000] TO BUS 342034 [2PACTOLUS T 69.000] CKT 1
OPEN BRANCH FROM BUS 342031 [2PACTOLUS 69.000] TO BUS 342034 [2PACTOLUS T 69.000] CKT 1
OPEN BRANCH FROM BUS 341554 [2GRAYSON J 69.000] TO BUS 342034 [2PACTOLUS T 69.000] CKT 1
OPEN BRANCH FROM BUS 243726 [05GRAYSO 69.000] TO BUS 341554 [2GRAYSON J 69.000] CKT 1
OPEN BRANCH FROM BUS 341554 [2GRAYSON J 69.000] TO BUS 341752 [2LEON 69.000] CKT 1
EKPC_P1-2_N SPR -S AND69 | OPEN BRANCH FROM BUS 341137 [2BLOOMFLD 69.000] TO BUS 341935 [2N SPRINGFLD69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 1.5118 | 16.6545 | 3 | 16.5085
OPEN BRANCH FROM BUS 341137 [2BLOOMFLD 69.000] TO BUS 341296 [2CHAPLIN T 69.000] CKT 1
OPEN BRANCH FROM BUS 341293 [2CHAPLIN 69.000] TO BUS 341296 [2CHAPLIN T 69.000] CKT 1
OPEN BRANCH FROM BUS 341296 [2CHAPLIN T 69.000] TO BUS 342262 [2SINAI 69.000] CKT 1
OPEN BRANCH FROM BUS 342184 [2S ANDERSON 69.000] TO BUS 342262 [2SINAI 69.000] CKT 1
EKPC_P1-2_DALE-GARRD 69 | OPEN BRANCH FROM BUS 341380 [2DALE 69.000] TO BUS 341959 [2NEWBY 1 69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 2.5789 | 27.3971 | 2 | 13.1936
OPEN BRANCH FROM BUS 341732 [2LANCASTER T69.000] TO BUS 341959 [2NEWBY 1 69.000] CKT 1
OPEN BRANCH FROM BUS 341515 [2GARRARD CO 69.000] TO BUS 341732 [2LANCASTER T69.000] CKT 1
EKPC_P1-2_STEPH-HODG 69 | OPEN BRANCH FROM BUS 341533 [2GLENDALE 69.000] TO BUS 342307 [2STEPHENSBRG69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 1.6705 | 77.552 | 1 | 5.9756
OPEN BRANCH FROM BUS 341533 [2GLENDALE 69.000] TO BUS 341632 [2HODGENVILLE69.000] CKT 1
EKPC_P1-2_HODG-GREEN 69 | OPEN BRANCH FROM BUS 341632 [2HODGENVILLE69.000] TO BUS 341800 [2MAGNOLIA 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 1.3122 | 60.8828 | 2 | 12.9325
OPEN BRANCH FROM BUS 341800 [2MAGNOLIA 69.000] TO BUS 342325 [2SUMMERSVIL 69.000] CKT 1
OPEN BRANCH FROM BUS 341563 [2GREEN CO 69.000] TO BUS 342325 [2SUMMERSVIL 69.000] CKT 1
EKPC_P1-2_HODG-N SPR 69 | OPEN BRANCH FROM BUS 341632 [2HODGENVILLE69.000] TO BUS 342316 [2SULPHUR CRK69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 2.0333 | 91.4775 | 3 | 16.8904
OPEN BRANCH FROM BUS 341776 [2LORETTO 69.000] TO BUS 342316 [2SULPHUR CRK69.000] CKT 1
OPEN BRANCH FROM BUS 341776 [2LORETTO 69.000] TO BUS 342208 [2S SPRINGF T69.000] CKT 1
OPEN BRANCH FROM BUS 342208 [2S SPRINGF T69.000] TO BUS 342211 [2S SPRINGFLD69.000] CKT 1
OPEN BRANCH FROM BUS 341935 [2N SPRINGFLD69.000] TO BUS 342208 [2S SPRINGF T69.000] CKT 1
EKPC_P1-2_E BARD-N SPR69 | OPEN BRANCH FROM BUS 341407 [2E BARDSTOWN69.000] TO BUS 342019 [2OWENS IL J 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 1.6416 | 77.3606 | 3 | 22.8777
OPEN BRANCH FROM BUS 342016 [2OWENS IL 69.000] TO BUS 342019 [2OWENS IL J 69.000] CKT 1
OPEN BRANCH FROM BUS 341143 [2BLUE G PW T69.000] TO BUS 342019 [2OWENS IL J 69.000] CKT 1
OPEN BRANCH FROM BUS 341140 [2BLUE G PW 69.000] TO BUS 341143 [2BLUE G PW T69.000] CKT 1
OPEN BRANCH FROM BUS 341143 [2BLUE G PW T69.000] TO BUS 342508 [2WOODLAWN 69.000] CKT 1
OPEN BRANCH FROM BUS 341494 [2FREDRIKBG T69.000] TO BUS 342508 [2WOODLAWN 69.000] CKT 1
OPEN BRANCH FROM BUS 341494 [2FREDRIKBG T69.000] TO BUS 341497 [2FREDRIKBRG 69.000] CKT 1
OPEN BRANCH FROM BUS 341494 [2FREDRIKBG T69.000] TO BUS 341935 [2N SPRINGFLD69.000] CKT 1
EKPC_P1-2_HNTFMJ-N SPR69 | OPEN BRANCH FROM BUS 341671 [2HUNT FARM J69.000] TO BUS 342061 [2PERRYVILLE 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.85374 | 10.6516 | 2 | 8.3464
OPEN BRANCH FROM BUS 341794 [2MACKVILKU T69.000] TO BUS 342061 [2PERRYVILLE 69.000] CKT 1
OPEN BRANCH FROM BUS 341791 [2MACKVIL KU 69.000] TO BUS 341794 [2MACKVILKU T69.000] CKT 1
OPEN BRANCH FROM BUS 341794 [2MACKVILKU T69.000] TO BUS 341935 [2N SPRINGFLD69.000] CKT 1
EKPC_P1-2_BONN - BARR 69 | OPEN BRANCH FROM BUS 341158 [2BONNIV DIST69.000] TO BUS 341161 [2BONNIV EK 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 1.6124 | 78.4394 | 4 | 64.4726
OPEN BRANCH FROM BUS 341158 [2BONNIV DIST69.000] TO BUS 341908 [2MUNFVIL EK 69.000] CKT 1
OPEN BRANCH FROM BUS 341908 [2MUNFVIL EK 69.000] TO BUS 341914 [2MUNFVILKU T69.000] CKT 1
OPEN BRANCH FROM BUS 341911 [2MUNFVIL KU 69.000] TO BUS 341914 [2MUNFVILKU T69.000] CKT 1
OPEN BRANCH FROM BUS 341651 [2HORSECAVE J69.000] TO BUS 341914 [2MUNFVILKU T69.000] CKT 1
OPEN BRANCH FROM BUS 341650 [2HORSECAVE T69.000] TO BUS 341651 [2HORSECAVE J69.000] CKT Z1
OPEN BRANCH FROM BUS 341647 [2HORSE CV KU69.000] TO BUS 341650 [2HORSECAVE T69.000] CKT 1
OPEN BRANCH FROM BUS 341059 [2BARREN CO 69.000] TO BUS 341651 [2HORSECAVE J69.000] CKT 1
EKPC_P1-2_GREEN-SUM SH69 | OPEN BRANCH FROM BUS 341563 [2GREEN CO 69.000] TO BUS 341575 [2GREENSBURG 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.17533 | 8.9699 | 5 | 24.9643
OPEN BRANCH FROM BUS 341575 [2GREENSBURG 69.000] TO BUS 341854 [2MCKINNY T 69.000] CKT 1
OPEN BRANCH FROM BUS 341851 [2MCKINNEY 69.000] TO BUS 341854 [2MCKINNY T 69.000] CKT 1
OPEN BRANCH FROM BUS 341728 [2KNOB LICK 69.000] TO BUS 341854 [2MCKINNY T 69.000] CKT 1
OPEN BRANCH FROM BUS 341431 [2EDM-JBGAL J69.000] TO BUS 341728 [2KNOB LICK 69.000] CKT 1
OPEN BRANCH FROM BUS 341431 [2EDM-JBGAL J69.000] TO BUS 341434 [2EDM-JBGAL T69.000] CKT 1
OPEN BRANCH FROM BUS 341434 [2EDM-JBGAL T69.000] TO BUS 341680 [2JB GALLOWAY69.000] CKT 1
OPEN BRANCH FROM BUS 341434 [2EDM-JBGAL T69.000] TO BUS 341437 [2EDMON IND P69.000] CKT 1
OPEN BRANCH FROM BUS 341431 [2EDM-JBGAL J69.000] TO BUS 342322 [2SUMM SHADE 69.000] CKT 1
EKPC_P1-2_CASEY-LIB J69 | OPEN BRANCH FROM BUS 341269 [2CASEY CO 69.000] TO BUS 342064 [2PEYTONS ST 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 1.9518 | 27.1634 | 2 | 13.7517
OPEN BRANCH FROM BUS 341767 [2LIBERTYKU T69.000] TO BUS 342064 [2PEYTONS ST 69.000] CKT 1
OPEN BRANCH FROM BUS 341764 [2LIBERTY KU 69.000] TO BUS 341767 [2LIBERTYKU T69.000] CKT 1
OPEN BRANCH FROM BUS 341761 [2LIBERTY J 69.000] TO BUS 341767 [2LIBERTYKU T69.000] CKT 1
EKPC_P1-2_LIB J-GARR69 | OPEN BRANCH FROM BUS 341761 [2LIBERTY J 69.000] TO BUS 341896 [2MT OLIVE J 69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 1.8074 | 82.548 | 3 | 15.0704
OPEN BRANCH FROM BUS 341893 [2MT OLIVE 69.000] TO BUS 341896 [2MT OLIVE J 69.000] CKT 1
OPEN BRANCH FROM BUS 341617 [2HIGHLAND EK69.000] TO BUS 341896 [2MT OLIVE J 69.000] CKT 1
OPEN LINE FROM BUS 341209 [2BROUGTWN T 69.000] TO BUS 341210 [2BROUGHT TWN69.000] CKT 1
OPEN LINE FROM BUS 341209 [2BROUGTWN T 69.000] TO BUS 341617 [2HIGHLAND EK69.000] CKT 1
OPEN LINE FROM BUS 341209 [2BROUGTWN T 69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1
OPEN BRANCH FROM BUS 342364 [2TOMM GOOC 69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1
OPEN LINE FROM BUS 942410 [AE2-254 TAP 69.000] TO BUS 942411 [AE2-254 C O169.000] CKT 1
OPEN LINE FROM BUS 942410 [AE2-254 TAP 69.000] TO BUS 341515 [2GARRARD CO 69.000] CKT 1
OPEN LINE FROM BUS 942410 [AE2-254 TAP 69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1
EKPC_P1-2_LIB J-WIND 69 | OPEN BRANCH FROM BUS 341761 [2LIBERTY J 69.000] TO BUS 341342 [2CONTOWN T 69.000] CKT 1 | TRUE | Met convergence tolerances | 2 | 2.5925 | 27.4843 | 3 | 13.8159
OPEN BRANCH FROM BUS 342067 [2PHIL 69.000] TO BUS 341342 [2CONTOWN T 69.000] CKT 1
OPEN BRANCH FROM BUS 341350 [2CRESTON 69.000] TO BUS 342067 [2PHIL 69.000] CKT 1
OPEN BRANCH FROM BUS 342067 [2PHIL 69.000] TO BUS 342505 [2WINDSOR 69.000] CKT 1
EKPC_P1-2_SSET-NORWJ69 | OPEN BRANCH FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 341974 [2NORWOOD T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.15027 | 5.271 | 1 | 8.7275
OPEN BRANCH FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1
EKPC_P1-2_BARR- FOX H 69 | OPEN BRANCH FROM BUS 341059 [2BARREN CO 69.000] TO BUS 341542 [2GOODNIGHT 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14297 | 3.05 | 1 | 9.2502
OPEN BRANCH FROM BUS 341542 [2GOODNIGHT 69.000] TO BUS 341548 [2GORIN PRK J69.000] CKT 1
OPEN BRANCH FROM BUS 341491 [2FOX HOLLOW 69.000] TO BUS 341548 [2GORIN PRK J69.000] CKT 1
EKPC_P1-2_FOX H-AE2-07169 | OPEN BRANCH FROM BUS 341491 [2FOX HOLLOW 69.000] TO BUS 342049 [2PATTON RD J69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.3372 | 15.0405
OPEN BRANCH FROM BUS 342049 [2PATTON RD J69.000] TO BUS 940830 [AE2-071 TAP 69.000] CKT 1
EKPC_P1-2_AE2-071-SUMMSH69 | OPEN BRANCH FROM BUS 342319 [2SUMM SHAD J69.000] TO BUS 342334 [2TEMPLE HILL69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.97491 | 16.424
OPEN BRANCH FROM BUS 940830 [AE2-071 TAP 69.000] TO BUS 342319 [2SUMM SHAD J69.000] CKT 1
OPEN BRANCH FROM BUS 342319 [2SUMM SHAD J69.000] TO BUS 342322 [2SUMM SHADE 69.000] CKT 1
EKPC_P1-2_CMPBEK-COBURG J69 | OPEN BRANCH FROM BUS 324830 [2CAMPBELV EK69.000] TO BUS 341320 [2COBURG 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.80683 | 13.9009 | 2 | 13.8247
OPEN BRANCH FROM BUS 341320 [2COBURG 69.000] TO BUS 341512 [2GARLIN T 69.000] CKT 1
OPEN BRANCH FROM BUS 341509 [2GARLIN 69.000] TO BUS 341512 [2GARLIN T 69.000] CKT 1
OPEN BRANCH FROM BUS 341323 [2COBURG J 69.000] TO BUS 341512 [2GARLIN T 69.000] CKT 1
EKPC_P1-2_COBURG J-SUMMSH 69 | OPEN BRANCH FROM BUS 342322 [2SUMM SHADE 69.000] TO BUS 342436 [2W COLUMBI T69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 2.0665 | 21.9477 | 4 | 23.086
OPEN BRANCH FROM BUS 342436 [2W COLUMBI T69.000] TO BUS 342439 [2W COLUMBIA 69.000] CKT 1
OPEN BRANCH FROM BUS 341335 [2COLUMBIA 69.000] TO BUS 342436 [2W COLUMBI T69.000] CKT 1
OPEN BRANCH FROM BUS 341335 [2COLUMBIA 69.000] TO BUS 341370 [2COLUMB S KU69.000] CKT 1
OPEN BRANCH FROM BUS 341366 [2COLUMB KU 69.000] TO BUS 341370 [2COLUMB S KU69.000] CKT 1
OPEN BRANCH FROM BUS 341323 [2COBURG J 69.000] TO BUS 341335 [2COLUMBIA 69.000] CKT 1
EKPC_P1-2_SUMMSH-WAYNE69 | OPEN BRANCH FROM BUS 342283 [2SNOW T 69.000] TO BUS 342322 [2SUMM SHADE 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 1.0079 | 9.3572 | 4 | 34.544
OPEN BRANCH FROM BUS 342277 [2SNOW 69.000] TO BUS 342283 [2SNOW T 69.000] CKT 1
OPEN BRANCH FROM BUS 341926 [2N ALBANY 69.000] TO BUS 342283 [2SNOW T 69.000] CKT 1
OPEN BRANCH FROM BUS 341926 [2N ALBANY 69.000] TO BUS 342181 [2S ALBANY 69.000] CKT 1
OPEN BRANCH FROM BUS 341926 [2N ALBANY 69.000] TO BUS 342397 [2UPCHURCH T 69.000] CKT 1
OPEN BRANCH FROM BUS 342394 [2UPCHURCH 69.000] TO BUS 342397 [2UPCHURCH T 69.000] CKT 1
OPEN BRANCH FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1
OPEN BRANCH FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1
EKPC_P1-2_WAYNE-ZULA 69 | OPEN BRANCH FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342535 [2ZULA T 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14177 | 10.1487 | 1 | 8.451
OPEN BRANCH FROM BUS 342529 [2ZULA 69.000] TO BUS 342535 [2ZULA T 69.000] CKT 1
EKPC_P1-2_SEWJ - RUSS 69 | OPEN BRANCH FROM BUS 342166 [2RUSS SPEK T69.000] TO BUS 342235 [2SEWELTN J 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 1.5395 | 17.0631 | 2 | 17.4494
OPEN BRANCH FROM BUS 342166 [2RUSS SPEK T69.000] TO BUS 342172 [2RUSS SPR EK69.000] CKT 1
OPEN BRANCH FROM BUS 342166 [2RUSS SPEK T69.000] TO BUS 342169 [2RUSS SPKU T69.000] CKT 1
OPEN BRANCH FROM BUS 342169 [2RUSS SPKU T69.000] TO BUS 342175 [2RUSS SPR KU69.000] CKT 1
OPEN BRANCH FROM BUS 342169 [2RUSS SPKU T69.000] TO BUS 342178 [2RUSSEL CO 69.000] CKT 1
EKPC_P1-2_WIND - SSET 69 | OPEN BRANCH FROM BUS 341938 [2NANCY 69.000] TO BUS 342505 [2WINDSOR 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 1.9413 | 20.787 | 4 | 24.781
OPEN BRANCH FROM BUS 341938 [2NANCY 69.000] TO BUS 342526 [2ZOLLICOF T 69.000] CKT 1
OPEN BRANCH FROM BUS 342523 [2ZOLLICOF 69.000] TO BUS 342526 [2ZOLLICOF T 69.000] CKT 1
OPEN BRANCH FROM BUS 342469 [2W SOMERSET 69.000] TO BUS 342526 [2ZOLLICOF T 69.000] CKT 1
OPEN BRANCH FROM BUS 341983 [2OAK HILL T 69.000] TO BUS 342469 [2W SOMERSET 69.000] CKT 1
OPEN BRANCH FROM BUS 341977 [2OAK HILL 69.000] TO BUS 341983 [2OAK HILL T 69.000] CKT 1
OPEN BRANCH FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 341983 [2OAK HILL T 69.000] CKT 1
OPEN BRANCH FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1
EKPC_P1-2_SSET-KU ELI 69 | OPEN BRANCH FROM BUS 324531 [2FERGUSON SO69.000] TO BUS 342287 [2SOMERSET KU69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 2.2587 | 57.6749 | 1 | 5.58
OPEN BRANCH FROM BUS 324514 [2ELIHU 69.000] TO BUS 324531 [2FERGUSON SO69.000] CKT 1
EKPC_P1-2_COOP-DENNY 69 | OPEN BRANCH FROM BUS 341344 [2COOPER 69.000] TO BUS 341347 [2COOPER DIST69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 2.6411 | 27.9193 | 1 | 13.1724
OPEN BRANCH FROM BUS 341206 [2BRONSTON T 69.000] TO BUS 341347 [2COOPER DIST69.000] CKT 1
OPEN BRANCH FROM BUS 341203 [2BRONSTON 69.000] TO BUS 341206 [2BRONSTON T 69.000] CKT 1
OPEN BRANCH FROM BUS 341206 [2BRONSTON T 69.000] TO BUS 341392 [2DENNY 69.000] CKT 1
EKPC_P1-2_DAV LANE - LAUR69 | OPEN BRANCH FROM BUS 342452 [2W LONDON T 69.000] TO BUS 341381 [2DAV LANE 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 1.0073 | 10.8723 | 2 | 19.5507
OPEN BRANCH FROM BUS 342452 [2W LONDON T 69.000] TO BUS 342451 [2W LONDON 69.000] CKT 1
OPEN BRANCH FROM BUS 342073 [2PINE GRV T 69.000] TO BUS 342451 [2W LONDON 69.000] CKT 1
OPEN BRANCH FROM BUS 342070 [2PINE GROVE 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1
OPEN BRANCH FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1
OPEN BRANCH FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1
EKPC_P1-2_LAUR-KU FAR69 | OPEN BRANCH FROM BUS 341722 [2KEAVY 2 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 1.541 | 15.414 | 4 | 29.125
OPEN BRANCH FROM BUS 341716 [2KEAVY 69.000] TO BUS 341722 [2KEAVY 2 T 69.000] CKT 1
OPEN BRANCH FROM BUS 341722 [2KEAVY 2 T 69.000] TO BUS 342187 [2S CORBIN 69.000] CKT 1
OPEN BRANCH FROM BUS 341038 [2BACON CRK T69.000] TO BUS 342187 [2S CORBIN 69.000] CKT 1
OPEN BRANCH FROM BUS 341035 [2BACON CRK 69.000] TO BUS 341038 [2BACON CRK T69.000] CKT 1
OPEN BRANCH FROM BUS 341038 [2BACON CRK T69.000] TO BUS 341755 [2LIBER CH T 69.000] CKT 1
OPEN BRANCH FROM BUS 341755 [2LIBER CH T 69.000] TO BUS 341758 [2LIBERT CHUR69.000] CKT 1
OPEN BRANCH FROM BUS 324527 [2FARLEY KU 69.000] TO BUS 341755 [2LIBER CH T 69.000] CKT 1
EKPC_P1-2_LAUR-KU SWTH69 | OPEN BRANCH FROM BUS 324576 [2HOPEWELL 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.65789 | 17.6791 | 1 | 12.82
OPEN BRANCH FROM BUS 324576 [2HOPEWELL 69.000] TO BUS 324748 [2SWEET HOLLO69.000] CKT 1
EKPC_P1-2_WAYNE-DENNY69 | OPEN BRANCH FROM BUS 342268 [2SLAT 69.000] TO BUS 342478 [2WAYNE CO 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.99988 | 51.0277 | 5 | 42.1992
OPEN BRANCH FROM BUS 341887 [2MONTICELLO 69.000] TO BUS 342268 [2SLAT 69.000] CKT 1
OPEN BRANCH FROM BUS 341641 [2HOMESTEAD S69.000] TO BUS 341887 [2MONTICELLO 69.000] CKT 1
OPEN BRANCH FROM BUS 341503 [2GAP OF RG T69.000] TO BUS 341887 [2MONTICELLO 69.000] CKT 1
OPEN BRANCH FROM BUS 341503 [2GAP OF RG T69.000] TO BUS 341506 [2GAP OF RIDG69.000] CKT 1
OPEN BRANCH FROM BUS 341503 [2GAP OF RG T69.000] TO BUS 341578 [2GREGORY R T69.000] CKT 1
OPEN BRANCH FROM BUS 341578 [2GREGORY R T69.000] TO BUS 341581 [2GREGORY RD 69.000] CKT 1
OPEN BRANCH FROM BUS 341392 [2DENNY 69.000] TO BUS 341578 [2GREGORY R T69.000] CKT 1
EKPC_P1-2_DENNY-MCCRRY69 | OPEN BRANCH FROM BUS 341845 [2MCCREARY CO69.000] TO BUS 342490 [2WHITLEY CTY69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.80724 | 9.0777 | 3 | 18.0054
OPEN BRANCH FROM BUS 342490 [2WHITLEY CTY69.000] TO BUS 342493 [2WHITLY C KU69.000] CKT 1
OPEN BRANCH FROM BUS 342490 [2WHITLEY CTY69.000] TO BUS 342499 [2WIBORG T 69.000] CKT 1
OPEN BRANCH FROM BUS 342496 [2WIBORG 69.000] TO BUS 342499 [2WIBORG T 69.000] CKT 1
OPEN BRANCH FROM BUS 341392 [2DENNY 69.000] TO BUS 342499 [2WIBORG T 69.000] CKT 1
EKPC_P1-2_AEPMORG- MOR69 | OPEN BRANCH FROM BUS 243740 [05MOREHE 69.000] TO BUS 246973 [05MORGCO 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.36039 | 4.2935
EKPC_P1-2_AEPMORG-INDX69 | OPEN BRANCH FROM BUS 243733 [05INDEX 69.000] TO BUS 246973 [05MORGCO 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.2643 | 12.0944
EKPC_P1-2_HODG-KU BARD69 | OPEN BRANCH FROM BUS 324660 [2NEW HAVEN 69.000] TO BUS 341632 [2HODGENVILLE69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 1.4913 | 32.0131 | 4 | 24.36
OPEN BRANCH FROM BUS 324660 [2NEW HAVEN 69.000] TO BUS 324801 [2BARTON 69.000] CKT 1
OPEN BRANCH FROM BUS 324424 [2BARDTWN CTY69.000] TO BUS 324801 [2BARTON 69.000] CKT 1
OPEN BRANCH FROM BUS 324424 [2BARDTWN CTY69.000] TO BUS 326537 [2WOODLAWN KU69.000] CKT 1
OPEN BRANCH FROM BUS 324426 [2BARDSTOWN 69.000] TO BUS 326537 [2WOODLAWN KU69.000] CKT Z1
EKPC_P1-2_HODG-KU ETWN69 | OPEN BRANCH FROM BUS 324575 [2HODGENV KU 69.000] TO BUS 341632 [2HODGENVILLE69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 1.633 | 19.1861 | 2 | 23.5
OPEN BRANCH FROM BUS 324521 [2ETOWN 4 69.000] TO BUS 324575 [2HODGENV KU 69.000] CKT 1
OPEN BRANCH FROM BUS 324519 [2ETOWN KU 69.000] TO BUS 324521 [2ETOWN 4 69.000] CKT 1
EKPC_P1-2_N SPR-KU LEB69 | OPEN BRANCH FROM BUS 324736 [2SPRINGFL KU69.000] TO BUS 341935 [2N SPRINGFLD69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.24757 | 17.8143 | 1 | 13.78
OPEN BRANCH FROM BUS 324606 [2LEBANON 69.000] TO BUS 324736 [2SPRINGFL KU69.000] CKT 1
EKPC_P1-2_BAR-BON-FHOL69 | OPEN BRANCH FROM BUS 341059 [2BARREN CO 69.000] TO BUS 341275 [2CAVE CITY J69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 1.2066 | 19.9497 | 5 | 36.2684
OPEN BRANCH FROM BUS 341275 [2CAVE CITY J69.000] TO BUS 342241 [2SEYMOUR T 69.000] CKT 1
OPEN BRANCH FROM BUS 342238 [2SEYMOUR 69.000] TO BUS 342241 [2SEYMOUR T 69.000] CKT 1
OPEN BRANCH FROM BUS 341272 [2CAVE CITY 69.000] TO BUS 341275 [2CAVE CITY J69.000] CKT 1
OPEN BRANCH FROM BUS 341149 [2BON AYR 69.000] TO BUS 341272 [2CAVE CITY 69.000] CKT 1
OPEN BRANCH FROM BUS 341080 [2BECKTON 69.000] TO BUS 341149 [2BON AYR 69.000] CKT 1
OPEN BRANCH FROM BUS 341080 [2BECKTON 69.000] TO BUS 342445 [2W GLASGOW T69.000] CKT 1
OPEN BRANCH FROM BUS 342442 [2W GLASGOW 69.000] TO BUS 342445 [2W GLASGOW T69.000] CKT 1
OPEN BRANCH FROM BUS 341530 [2GLASGO-CLEV69.000] TO BUS 342445 [2W GLASGOW T69.000] CKT 1
OPEN BRANCH FROM BUS 341530 [2GLASGO-CLEV69.000] TO BUS 342043 [2PARKWAY 2 T69.000] CKT 1
OPEN BRANCH FROM BUS 341491 [2FOX HOLLOW 69.000] TO BUS 342043 [2PARKWAY 2 T69.000] CKT 1
EKPC_P1-2_FHOL-PARK69 | OPEN BRANCH FROM BUS 341491 [2FOX HOLLOW 69.000] TO BUS 342037 [2PARKWAY 1 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 2.4159 | 25.5805 | 2 | 12.671
OPEN BRANCH FROM BUS 342037 [2PARKWAY 1 69.000] TO BUS 342040 [2PARKWAY 2 69.000] CKT 1
EKPC_P1-2_CMPBEK-GREEN69 | OPEN BRANCH FROM BUS 324554 [2GRENSBRG KU69.000] TO BUS 341563 [2GREEN CO 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.77845 | 10.0465 | 1 | 4.57
OPEN BRANCH FROM BUS 324554 [2GRENSBRG KU69.000] TO BUS 324830 [2CAMPBELV EK69.000] CKT 1
EKPC_P1-2_CMPBEK-KUTAY69 | OPEN BRANCH FROM BUS 324557 [2GR RVR PLAZ69.000] TO BUS 324830 [2CAMPBELV EK69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 1.775 | 19.0751 | 3 | 29.6132
OPEN BRANCH FROM BUS 324557 [2GR RVR PLAZ69.000] TO BUS 324829 [2CAMPBELVIL169.000] CKT 1
OPEN BRANCH FROM BUS 324641 [2MILE LAN TP69.000] TO BUS 324829 [2CAMPBELVIL169.000] CKT 1
OPEN BRANCH FROM BUS 324641 [2MILE LAN TP69.000] TO BUS 326970 [2MILE LAN EK69.000] CKT 1
OPEN BRANCH FROM BUS 324641 [2MILE LAN TP69.000] TO BUS 324751 [2TAYLOR CO 69.000] CKT 1
EKPC_P1-2_DK HEB-HEB 138 | OPEN BRANCH FROM BUS 250152 [08HEBRNG 138.00] TO BUS 342595 [4HEBRON 138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 1.5267 | 16.8979 | 1 | 16.4491
OPEN BRANCH FROM BUS 341605 [2HEBRON 69.000] TO BUS 342595 [4HEBRON 138.00] CKT 1
EKPC_P1-2_BOONE-BUFF138 | OPEN BRANCH FROM BUS 250054 [08LONGBR 138.00] TO BUS 342559 [4BOONE CO 138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 2.0999 | 21.0244 | 2 | 33.288
OPEN BRANCH FROM BUS 250054 [08LONGBR 138.00] TO BUS 250077 [08MTZION 138.00] CKT 1
OPEN BRANCH FROM BUS 249991 [08BUFTN1 138.00] TO BUS 250077 [08MTZION 138.00] CKT 1
EKPC_P1-2_RUSSOL-RUS-WLF161 | OPEN BRANCH FROM BUS 342793 [5RUSSEL CO 161.00] TO BUS 342796 [5RUSSEL CO J161.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 2.7973 | 69.0787
OPEN BRANCH FROM BUS 342796 [5RUSSEL CO J161.00] TO BUS 360448 [5WOLF CRK HP161.00] CKT 1
OPEN BRANCH FROM BUS 342792 [5RUSS SOL 161.00] TO BUS 342796 [5RUSSEL CO J161.00] CKT 1
EKPC_P1-2_COOP-RUSSOL161 | OPEN BRANCH FROM BUS 342751 [5JAMESTOWN T161.00] TO BUS 342792 [5RUSS SOL 161.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 2.1882 | 23.0725 | 3 | 21.6984
OPEN BRANCH FROM BUS 342748 [5JAMESTOWN 161.00] TO BUS 342751 [5JAMESTOWN T161.00] CKT 1
OPEN BRANCH FROM BUS 342745 [5JABEZ T 161.00] TO BUS 342751 [5JAMESTOWN T161.00] CKT 1
OPEN BRANCH FROM BUS 342742 [5JABEZ 161.00] TO BUS 342745 [5JABEZ T 161.00] CKT 1
OPEN BRANCH FROM BUS 342745 [5JABEZ T 161.00] TO BUS 342799 [5S OAKHILL 161.00] CKT 1
OPEN BRANCH FROM BUS 342715 [5COOPER1 161.00] TO BUS 342799 [5S OAKHILL 161.00] CKT 1
EKPC_P1-2_COOP-DEN161 | OPEN BRANCH FROM BUS 342718 [5COOPER2 161.00] TO BUS 342727 [5DENNY 161.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 2.6148
OPEN BRANCH FROM BUS 341392 [2DENNY 69.000] TO BUS 342727 [5DENNY 161.00] CKT 1
EKPC_P1-2_COP-LIBJ-PU161 | OPEN BRANCH FROM BUS 342715 [5COOPER1 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 1.4623 | 15.3005
OPEN BRANCH FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1
OPEN BRANCH FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1
OPEN BRANCH FROM BUS 342760 [5LIBERTY J 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1
EKPC_P1-2_MCCR-WAYNE161 | OPEN BRANCH FROM BUS 342778 [5MCCREARY CO161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.7182 | 36.2632
OPEN BRANCH FROM BUS 360448 [5WOLF CRK HP161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1
OPEN BRANCH FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1
OPEN BRANCH FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1
EKPC_P1-2_LAUR-PIT-TY161 | OPEN BRANCH FROM BUS 342754 [5LAUREL CO 161.00] TO BUS 342783 [5PITTSBURG 161.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.22707 | 8.562
OPEN BRANCH FROM BUS 324688 [2PITTSBRG KU69.000] TO BUS 342783 [5PITTSBURG 161.00] CKT 1
OPEN BRANCH FROM BUS 342783 [5PITTSBURG 161.00] TO BUS 342820 [5TYNER 161.00] CKT 1
EKPC_P1-2_GRE-TAY-AF1-083161 | OPEN BRANCH FROM BUS 342733 [5GREEN CO 161.00] TO BUS 342817 [5TAYLOR CO J161.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 2.6132 | 26.4195
OPEN BRANCH FROM BUS 342817 [5TAYLOR CO J161.00] TO BUS 325921 [5TAYLOR CO 161.00] CKT 1
OPEN BRANCH FROM BUS 944150 [AF1-083 TAP 161.00] TO BUS 342817 [5TAYLOR CO J161.00] CKT 1
EKPC_P1-2_AF1-083-MARION161 | OPEN BRANCH FROM BUS 342805 [5SALOMA T 161.00] TO BUS 944150 [AF1-083 TAP 161.00] CKT 1 | TRUE | Met convergence tolerances | 2 | 2.0464 | 67.1626 | 4 | 74.718
OPEN BRANCH FROM BUS 342802 [5SALOMA 161.00] TO BUS 342805 [5SALOMA T 161.00] CKT 1
OPEN LINE FROM BUS 342781 [5N LEBANON 161.00] TO BUS 342769 [5MARION CO 161.00] CKT 1
OPEN LINE FROM BUS 342781 [5N LEBANON 161.00] TO BUS 342775 [5MARION IP T161.00] CKT 1
OPEN LINE FROM BUS 342797 [5S MARION IT161.00] TO BUS 342798 [5S MARION IP161.00] CKT 1
OPEN LINE FROM BUS 342797 [5S MARION IT161.00] TO BUS 342772 [5MARION IP 161.00] CKT 1
OPEN LINE FROM BUS 342797 [5S MARION IT161.00] TO BUS 342775 [5MARION IP T161.00] CKT 1
EKPC_P1-2_BARR-SUMSHSOL161 | OPEN BRANCH FROM BUS 342813 [5SUMM SOL 161.00] TO BUS 342694 [5BARREN CO 161.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14287 | 3.8984
OPEN BRANCH FROM BUS 341059 [2BARREN CO 69.000] TO BUS 342694 [5BARREN CO 161.00] CKT 1
EKPC_P1-2_BULL-SUMSH161 | OPEN LINE FROM BUS 361788 [5SUM SHAD TP161.00] TO BUS 326998 [5BULLITT TAP161.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 2.5634 | 26.4731
OPEN LINE FROM BUS 361788 [5SUM SHAD TP161.00] TO BUS 342814 [5SUMM SHADE 161.00] CKT 1
OPEN LINE FROM BUS 361788 [5SUM SHAD TP161.00] TO BUS 360334 [5SUMMER SHAD161.00] CKT 1
TVA SS-GLASGOW & LAFAYETTE 161 | OPEN LINE FROM BUS 360334 [5SUMMER SHAD161.00] TO BUS 360607 [5S GLASGOW 161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.5987 | 70.1114
OPEN LINE FROM BUS 360334 [5SUMMER SHAD161.00] TO BUS 360354 [5LAFAYETT TN161.00] CKT 1
EK-TVA SSHD & SSHD 161 XFMR | OPEN LINE FROM BUS 342814 [5SUMM SHADE 161.00] TO BUS 360334 [5SUMMER SHAD161.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 2.4351 | 74.0574
OPEN BRANCH FROM BUS 342814 [5SUMM SHADE 161.00] TO BUS 342322 [2SUMM SHADE 69.000] CKT 1
B-69-60 | OPEN BRANCH FROM BUS 324514 [2ELIHU 69.000] TO BUS 324964 [2SOMERSET 3 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.515
CLOSE BRANCH FROM BUS 324961 [2SOMERSET GE69.000] TO BUS 324965 [2SOMERSET NO69.000] CKT 1
B-69-79 | OPEN BRANCH FROM BUS 324217 [4BROWN PLANT138.00] TO BUS 324318 [4WEST CLIFF 138.00] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.1918
OPEN BRANCH FROM BUS 324318 [4WEST CLIFF 138.00] TO BUS 324764 [2WEST CLIFF 69.000] CKT 1
B-69-80 | OPEN BRANCH FROM BUS 324217 [4BROWN PLANT138.00] TO BUS 324318 [4WEST CLIFF 138.00] CKT 2 | TRUE | Met convergence tolerances | 0 | 0.14287 | 2.1664
OPEN BRANCH FROM BUS 324318 [4WEST CLIFF 138.00] TO BUS 324764 [2WEST CLIFF 69.000] CKT 2
B-138-447 | OPEN LINE FROM BUS 324307 [4SHARKEY TAP138.00] TO BUS 326556 [4N SHARKEY T138.00] CKT 1 | TRUE | Met convergence tolerances | 3 | 0.41283 | 6.7966 | 2 | 9.699
OPEN LINE FROM BUS 324307 [4SHARKEY TAP138.00] TO BUS 324245 [4FARMERS TAP138.00] CKT 1
OPEN LINE FROM BUS 324307 [4SHARKEY TAP138.00] TO BUS 324302 [4RODBURN 138.00] CKT 1
OPEN LINE FROM BUS 324245 [4FARMERS TAP138.00] TO BUS 324246 [4FARMERS 138.00] CKT 1
OPEN LINE FROM BUS 324245 [4FARMERS TAP138.00] TO BUS 324310 [4SPENCER RD 138.00] CKT 1
OPEN LINE FROM BUS 324246 [4FARMERS 138.00] TO BUS 324528 [2FARMERS 69.000] CKT 1
OPEN BRANCH FROM BUS 324707 [2RODBURN 69.000] TO BUS 243740 [05MOREHE 69.000] CKT Z1
B-69-330 | OPEN BRANCH FROM BUS 324707 [2RODBURN 69.000] TO BUS 243740 [05MOREHE 69.000] CKT Z1 | TRUE | Met convergence tolerances | 3 | 0.41517 | 6.8454 | 2 | 9.699
OPEN LINE FROM BUS 324245 [4FARMERS TAP138.00] TO BUS 324246 [4FARMERS 138.00] CKT 1
OPEN LINE FROM BUS 324245 [4FARMERS TAP138.00] TO BUS 324307 [4SHARKEY TAP138.00] CKT 1
OPEN LINE FROM BUS 324245 [4FARMERS TAP138.00] TO BUS 324310 [4SPENCER RD 138.00] CKT 1
OPEN LINE FROM BUS 324307 [4SHARKEY TAP138.00] TO BUS 326556 [4N SHARKEY T138.00] CKT 1
OPEN LINE FROM BUS 324307 [4SHARKEY TAP138.00] TO BUS 324302 [4RODBURN 138.00] CKT 1
B-69-332 | OPEN BRANCH FROM BUS 341059 [2BARREN CO 69.000] TO BUS 341651 [2HORSECAVE J69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 1.079 | 13.4776
OPEN BRANCH FROM BUS 341914 [2MUNFVILKU T69.000] TO BUS 341651 [2HORSECAVE J69.000] CKT 1
CLOSE BRANCH FROM BUS 342241 [2SEYMOUR T 69.000] TO BUS 341650 [2HORSECAVE T69.000] CKT 1
B-69-450 | OPEN BRANCH FROM BUS 324302 [4RODBURN 138.00] TO BUS 324707 [2RODBURN 69.000] CKT 1 | TRUE | Met convergence tolerances | 0 | 0.34174 | 6.2842
OPEN BRANCH FROM BUS 324707 [2RODBURN 69.000] TO BUS 243740 [05MOREHE 69.000] CKT Z1
BB-1408 | OPEN LINE FROM BUS 324654 [2MT VIC EK J69.000] TO BUS 324489 [2CUMB FALL T69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 1.704 | 18.8457 | 2 | 9.6082
OPEN LINE FROM BUS 324654 [2MT VIC EK J69.000] TO BUS 324514 [2ELIHU 69.000] CKT 1
OPEN LINE FROM BUS 324489 [2CUMB FALL T69.000] TO BUS 324784 [2WOFFORD 69.000] CKT 1
OPEN LINE FROM BUS 324489 [2CUMB FALL T69.000] TO BUS 325034 [2CUMBER FALL69.000] CKT 1
BB-1403 | OPEN LINE FROM BUS 324604 [2LEBANON IND69.000] TO BUS 324606 [2LEBANON 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 1.6384 | 17.62 | 7 | 61.3983
OPEN LINE FROM BUS 324604 [2LEBANON IND69.000] TO BUS 325020 [2LEBANON E 69.000] CKT 1
OPEN LINE FROM BUS 324603 [2LEBANON CIT69.000] TO BUS 324605 [2LEBANON EK 69.000] CKT 1
OPEN LINE FROM BUS 324603 [2LEBANON CIT69.000] TO BUS 324191 [2LEBANON E T69.000] CKT 1
OPEN LINE FROM BUS 324605 [2LEBANON EK 69.000] TO BUS 324889 [2LEBANON SO 69.000] CKT 1
OPEN LINE FROM BUS 324889 [2LEBANON SO 69.000] TO BUS 324479 [2CAMPBELVL T69.000] CKT 1
OPEN LINE FROM BUS 324479 [2CAMPBELVL T69.000] TO BUS 324751 [2TAYLOR CO 69.000] CKT 1
OPEN LINE FROM BUS 324479 [2CAMPBELVL T69.000] TO BUS 324349 [2CAMPBELVIL269.000] CKT 1
OPEN LINE FROM BUS 324349 [2CAMPBELVIL269.000] TO BUS 324068 [2E CAMPBELVL69.000] CKT 1
BB-1402 | OPEN LINE FROM BUS 324641 [2MILE LAN TP69.000] TO BUS 324751 [2TAYLOR CO 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 1.7669 | 18.6543 | 5 | 45.7526
OPEN LINE FROM BUS 324641 [2MILE LAN TP69.000] TO BUS 324829 [2CAMPBELVIL169.000] CKT 1
OPEN LINE FROM BUS 324641 [2MILE LAN TP69.000] TO BUS 326970 [2MILE LAN EK69.000] CKT 1
OPEN LINE FROM BUS 324829 [2CAMPBELVIL169.000] TO BUS 324557 [2GR RVR PLAZ69.000] CKT 1
OPEN LINE FROM BUS 324557 [2GR RVR PLAZ69.000] TO BUS 324830 [2CAMPBELV EK69.000] CKT 1
OPEN LINE FROM BUS 324830 [2CAMPBELV EK69.000] TO BUS 341320 [2COBURG 69.000] CKT 1
OPEN LINE FROM BUS 324830 [2CAMPBELV EK69.000] TO BUS 324554 [2GRENSBRG KU69.000] CKT 1
OPEN LINE FROM BUS 324554 [2GRENSBRG KU69.000] TO BUS 341563 [2GREEN CO 69.000] CKT 1
B-69-25 | OPEN LINE FROM BUS 324141 [5ELIHU 161.00] TO BUS 324514 [2ELIHU 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.14177 | 5.5548
OPEN LINE FROM BUS 324141 [5ELIHU 161.00] TO BUS 324514 [2ELIHU 69.000] CKT 2
OPEN LINE FROM BUS 324141 [5ELIHU 161.00] TO BUS 342718 [5COOPER2 161.00] CKT 1
OPEN LINE FROM BUS 324141 [5ELIHU 161.00] TO BUS 324130 [5ALCALDE 161.00] CKT 1
B-138-111 | OPEN LINE FROM BUS 324239 [4DANVILE N T138.00] TO BUS 325121 [4LOGAN TP 138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.89487 | 15.562
OPEN LINE FROM BUS 324239 [4DANVILE N T138.00] TO BUS 324217 [4BROWN PLANT138.00] CKT 1
OPEN LINE FROM BUS 324239 [4DANVILE N T138.00] TO BUS 324238 [4DANVILLE N 138.00] CKT 1
BB-1133 | OPEN LINE FROM BUS 324270 [4LEBANON WES138.00] TO BUS 324271 [4LEBANON 138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 1.7706 | 18.6304 | 1 | 6.91
OPEN LINE FROM BUS 324270 [4LEBANON WES138.00] TO BUS 324213 [4BONNIEVILLE138.00] CKT 1
B-161-128 | OPEN LINE FROM BUS 342817 [5TAYLOR CO J161.00] TO BUS 944150 [AF1-083 TAP 161.00] CKT 1 | TRUE | Met convergence tolerances | 2 | 0.51925 | 28.4328
OPEN LINE FROM BUS 342817 [5TAYLOR CO J161.00] TO BUS 325921 [5TAYLOR CO 161.00] CKT 1
OPEN LINE FROM BUS 342817 [5TAYLOR CO J161.00] TO BUS 342733 [5GREEN CO 161.00] CKT 1
OPEN LINE FROM BUS 325921 [5TAYLOR CO 161.00] TO BUS 324751 [2TAYLOR CO 69.000] CKT 1
OPEN LINE FROM BUS 944150 [AF1-083 TAP 161.00] TO BUS 944151 [AF1-083 C O1161.00] CKT 1
OPEN LINE FROM BUS 944150 [AF1-083 TAP 161.00] TO BUS 342805 [5SALOMA T 161.00] CKT 1
B-69-18 | OPEN LINE FROM BUS 324271 [4LEBANON 138.00] TO BUS 324606 [2LEBANON 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 1.5998 | 73.88
OPEN LINE FROM BUS 324271 [4LEBANON 138.00] TO BUS 324606 [2LEBANON 69.000] CKT 2
OPEN LINE FROM BUS 324271 [4LEBANON 138.00] TO BUS 325121 [4LOGAN TP 138.00] CKT 1
OPEN LINE FROM BUS 324271 [4LEBANON 138.00] TO BUS 342770 [4MARION CO 138.00] CKT 1
OPEN LINE FROM BUS 324271 [4LEBANON 138.00] TO BUS 342770 [4MARION CO 138.00] CKT 2
OPEN LINE FROM BUS 324271 [4LEBANON 138.00] TO BUS 342770 [4MARION CO 138.00] CKT 3
OPEN LINE FROM BUS 324271 [4LEBANON 138.00] TO BUS 324270 [4LEBANON WES138.00] CKT 1
B-69-19 | OPEN LINE FROM BUS 324213 [4BONNIEVILLE138.00] TO BUS 324270 [4LEBANON WES138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 1.6894 | 18.0667
OPEN LINE FROM BUS 324213 [4BONNIEVILLE138.00] TO BUS 324800 [4MERE TVA 138.00] CKT 1
OPEN LINE FROM BUS 324213 [4BONNIEVILLE138.00] TO BUS 324447 [2BONNIE KU 69.000] CKT 1
OPEN LINE FROM BUS 324213 [4BONNIEVILLE138.00] TO BUS 341161 [2BONNIV EK 69.000] CKT 1
B-69-26 | OPEN LINE FROM BUS 324143 [5FARLEY 161.00] TO BUS 324527 [2FARLEY KU 69.000] CKT 1 | TRUE | Met convergence tolerances | 1 | 0.74935 | 28.2488
OPEN LINE FROM BUS 324143 [5FARLEY 161.00] TO BUS 324130 [5ALCALDE 161.00] CKT 1
OPEN LINE FROM BUS 324143 [5FARLEY 161.00] TO BUS 324132 [5ARTEMUS TAP161.00] CKT 1
B-345-100 | OPEN LINE FROM BUS 324100 [7ALCALDE 345.00] TO BUS 324102 [7BROWN NORTH345.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 2.114 | 76.866
OPEN LINE FROM BUS 324100 [7ALCALDE 345.00] TO BUS 324112 [7PINEVILLE 345.00] CKT 1
OPEN LINE FROM BUS 324100 [7ALCALDE 345.00] TO BUS 324130 [5ALCALDE 161.00] CKT 1
B-138-116 | OPEN LINE FROM BUS 248009 [06CLIFTY 138.00] TO BUS 324227 [4CARROLLTON 138.00] CKT 1 | TRUE | Met convergence tolerances | 1 | 1.382 | 19.1146
OPEN LINE FROM BUS 248009 [06CLIFTY 138.00] TO BUS 325013 [4CLIFTY TAP1138.00] CKT 1
OPEN LINE FROM BUS 248009 [06CLIFTY 138.00] TO BUS 325014 [4CLIFTY TAP2138.00] CKT 1
OPEN LINE FROM BUS 248009 [06CLIFTY 138.00] TO BUS 248008 [06CLIFTX 138.00] CKT SR

## Summary
ACCC SOLUTION SUMMARY
ACCC output file = H:\Transmission planning\2022 Gas Study\Queue Impact Study (New)\Study Results (Liberty Area)\LibertyGen_Cooper1&2 - Ngen_2032S 22Series_R6_Solar_T++_L.acc
Saved Case file = H:\Transmission planning\2022 Gas Study\Queue Impact Study (New)\Study Results (Liberty Area)\LibertyGen_Cooper1&2 - Ngen_2032S 22Series_R6_Solar_T++_L.sav
DFAX file = H:\Transmission planning\2022 Gas Study\Queue Impact Study (New)\Study Results (Liberty Area)\LibertyGen_Cooper1&2 - Ngen_2032S 22Series_R6_Solar_T++_L.dfx
Subsystem file = H:\Transmission planning\2022 Gas Study\Queue Impact Study (New)\2022 series_sub_Liberty.sub
Monitored Element file = H:\Transmission planning\2022 Gas Study\Queue Impact Study (New)\2022 series_mon_Liberty.mon
Contingency Description file = H:\Transmission planning\2022 Gas Study\Queue Impact Study (New)\S_Reduced_WITH LINE SPLITS.con
Number of Ratings = 12
Number of Monitored Branches = 110
Number of Monitored Interfaces = 0
Number of Contingencies+Base Case = 829
Number of Voltage Monitored Buses = 0
Number of Voltage Monitored Records = 0
Number of Voltage Monitored Bus Records = 0
Number of Voltage Monitored Nodes = 0
Number of Voltage Monitored Node Records = 0
Number of Voltage Monitored All Node Records = 0
Number of Monitored SWD = 0
Number of Buses in the case = 95985
Number of Loads shed due to post contingency = 527
Number of Loads shed due to tripping = 527
Number of Loads shed due to corrective actions = 527
ACCC Results stored in the file are in 'Bus Number Output' form
ACCC Results stored in the file are from 'ACCC' analysis
Number of Areas for which results are stored = 134
Number of Zones for which results are stored = 746
Number of Owners for which results are stored = 345
Number of Voltage levels for which results are stored = 236
Rating Description
Name | DESCRIPTION
RATE1 | RATING SET 1
RATE2 | RATING SET 2
RATE3 | RATING SET 3
RATE4 | RATING SET 4
RATE5 | RATING SET 5
RATE6 | RATING SET 6
RATE7 | RATING SET 7
RATE8 | RATING SET 8
RATE9 | RATING SET 9
RATE10 | RATING SET 10
RATE11 | RATING SET 11
RATE12 | RATING SET 12
Monitored Lines
MON# | LABEL | RATE1 | RATE2 | RATE3 | RATE4 | RATE5 | RATE6 | RATE7 | RATE8 | RATE9 | RATE10 | RATE11 | RATE12
1 | 324141 5ELIHU 161.00 342718 5COOPER2 161.00 1 | 684 | 1050 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 341062 2BASS 69.000 341269 2CASEY CO 69.000 1 | 77 | 90 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 341203 2BRONSTON 69.000 341206 2BRONSTON T 69.000 1 | 41 | 46 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 341206 2BRONSTON T 69.000 341347 2COOPER DIST69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 341206 2BRONSTON T 69.000 341392 2DENNY 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 341209 2BROUGTWN T 69.000 341210 2BROUGHT TWN69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 341209 2BROUGTWN T 69.000 341617 2HIGHLAND EK69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 341209 2BROUGTWN T 69.000 342367 2TOMM GOOC T69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 341269 2CASEY CO 69.000 342064 2PEYTONS ST 69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 341269 2CASEY CO 69.000 342703 5CASEY CO 161.00 1 | 96 | 108 | 112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 341342 2CONTOWN T 69.000 341343 2CONTOWN 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 341342 2CONTOWN T 69.000 341761 2LIBERTY J 69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 341342 2CONTOWN T 69.000 342067 2PHIL 69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | 341344 2COOPER 69.000 341347 2COOPER DIST69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | 341344 2COOPER 69.000 342286 2SOMERSET 69.000 1 | 66 | 76 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | 341344 2COOPER 69.000 342286 2SOMERSET 69.000 2 | 66 | 76 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | 341344 2COOPER 69.000 342715 5COOPER1 161.00 1 | 134 | 143 | 143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | 341350 2CRESTON 69.000 342067 2PHIL 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | 341392 2DENNY 69.000 342727 5DENNY 161.00 1 | 89 | 109 | 123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | 341419 2E SOMERSE T69.000 341422 2E SOMERSET 69.000 1 | 41 | 46 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | 341419 2E SOMERSE T69.000 341941 2NELSN VAL T69.000 1 | 41 | 46 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | 341419 2E SOMERSE T69.000 341974 2NORWOOD T 69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | 341470 2FLOYD EK 69.000 341473 2FLOYD-SFL T69.000 1 | 77 | 90 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | 341470 2FLOYD EK 69.000 342511 2WOODSTOCK 69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | 341473 2FLOYD-SFL T69.000 342115 2PULASK CO 69.000 1 | 73 | 76 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | 341473 2FLOYD-SFL T69.000 342193 2S FLOYD 69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | 341617 2HIGHLAND EK69.000 341896 2MT OLIVE J 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | 341761 2LIBERTY J 69.000 341767 2LIBERTYKU T69.000 1 | 53 | 66 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | 341761 2LIBERTY J 69.000 341896 2MT OLIVE J 69.000 1 | 53 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | 341761 2LIBERTY J 69.000 342760 5LIBERTY J 161.00 1 | 89 | 109 | 123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | 341767 2LIBERTYKU T69.000 342064 2PEYTONS ST 69.000 1 | 77 | 90 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | 341893 2MT OLIVE 69.000 341896 2MT OLIVE J 69.000 1 | 42 | 46 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | 341941 2NELSN VAL T69.000 341947 2NELSON VAL 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | 341941 2NELSN VAL T69.000 341971 2NORWOOD 69.000 1 | 41 | 46 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
35 | 341971 2NORWOOD 69.000 342115 2PULASK CO 69.000 1 | 73 | 76 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36 | 342067 2PHIL 69.000 342505 2WINDSOR 69.000 1 | 114 | 127 | 133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | 342115 2PULASK CO 69.000 342787 5PULASK CO 161.00 1 | 96 | 108 | 112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
38 | 342222 5S CASEY 161.00 342703 5CASEY CO 161.00 1 | 342 | 525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
39 | 342222 5S CASEY 161.00 342760 5LIBERTY J 161.00 1 | 342 | 525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
40 | 342364 2TOMM GOOC 69.000 342367 2TOMM GOOC T69.000 1 | 146 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
41 | 342367 2TOMM GOOC T69.000 942410 AE2-254 TAP 69.000 1 | 146 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
42 | 342472 2WALNUT GROV69.000 342511 2WOODSTOCK 69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
43 | 342703 5CASEY CO 161.00 342769 5MARION CO 161.00 1 | 684 | 1050 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
44 | 342715 5COOPER1 161.00 342718 5COOPER2 161.00 1 | 684 | 1050 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
45 | 342715 5COOPER1 161.00 342790 5PULASK CO J161.00 1 | 267 | 298 | 312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
46 | 342715 5COOPER1 161.00 342799 5S OAKHILL 161.00 1 | 342 | 525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
47 | 342718 5COOPER2 161.00 342727 5DENNY 161.00 1 | 186 | 210 | 231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | 342718 5COOPER2 161.00 342757 5LAUREL DAM 161.00 1 | 267 | 298 | 312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
49 | 342742 5JABEZ 161.00 342745 5JABEZ T 161.00 1 | 207 | 230 | 241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 | 342745 5JABEZ T 161.00 342751 5JAMESTOWN T161.00 1 | 342 | 525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51 | 342745 5JABEZ T 161.00 342799 5S OAKHILL 161.00 1 | 342 | 525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
52 | 342748 5JAMESTOWN 161.00 342751 5JAMESTOWN T161.00 1 | 207 | 230 | 241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
53 | 342751 5JAMESTOWN T161.00 342792 5RUSS SOL 161.00 1 | 684 | 1050 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
54 | 342760 5LIBERTY J 161.00 342790 5PULASK CO J161.00 1 | 342 | 525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
55 | 342769 5MARION CO 161.00 342770 4MARION CO 138.00 1 | 192 | 234 | 264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
56 | 342769 5MARION CO 161.00 342770 4MARION CO 138.00 2 | 192 | 234 | 264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
57 | 342769 5MARION CO 161.00 342770 4MARION CO 138.00 3 | 192 | 234 | 264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58 | 342769 5MARION CO 161.00 342770 4MARION CO 138.00 4 | 192 | 234 | 264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
59 | 342769 5MARION CO 161.00 342781 5N LEBANON 161.00 1 | 684 | 1050 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
60 | 342772 5MARION IP 161.00 342797 5S MARION IT161.00 1 | 207 | 230 | 241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
61 | 342775 5MARION IP T161.00 342781 5N LEBANON 161.00 1 | 684 | 1050 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
62 | 342775 5MARION IP T161.00 342797 5S MARION IT161.00 1 | 207 | 230 | 241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
63 | 342775 5MARION IP T161.00 342805 5SALOMA T 161.00 1 | 684 | 1050 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
64 | 342787 5PULASK CO 161.00 342790 5PULASK CO J161.00 1 | 342 | 525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
65 | 342792 5RUSS SOL 161.00 342796 5RUSSEL CO J161.00 1 | 342 | 525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
66 | 342793 5RUSSEL CO 161.00 342796 5RUSSEL CO J161.00 1 | 210 | 240 | 247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
67 | 342796 5RUSSEL CO J161.00 360448 5WOLF CRK HP161.00 1 | 267 | 298 | 312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
68 | 342797 5S MARION IT161.00 342798 5S MARION IP161.00 1 | 207 | 230 | 241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
69 | 342802 5SALOMA 161.00 342805 5SALOMA T 161.00 1 | 207 | 230 | 241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | 342805 5SALOMA T 161.00 944150 AF1-083 TAP 161.00 1 | 684 | 1050 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
71 | 342817 5TAYLOR CO J161.00 944150 AF1-083 TAP 161.00 1 | 684 | 1050 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
72 | 324141 5ELIHU 161.00 324130 5ALCALDE 161.00 1 | 342 | 525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73 | 324141 5ELIHU 161.00 324514 2ELIHU 69.000 1 | 93 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
74 | 324141 5ELIHU 161.00 324514 2ELIHU 69.000 2 | 93 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
75 | 325084 2FLOYD EKP T69.000 324950 2SCIENC HILL69.000 1 | 18 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
76 | 325084 2FLOYD EKP T69.000 324995 2WAYNESBURG 69.000 1 | 18 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
77 | 341392 2DENNY 69.000 341578 2GREGORY R T69.000 1 | 146 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78 | 341392 2DENNY 69.000 342499 2WIBORG T 69.000 1 | 73 | 76 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
79 | 341767 2LIBERTYKU T69.000 341764 2LIBERTY KU 69.000 1 | 37 | 43 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
80 | 341974 2NORWOOD T 69.000 341233 2CABIN HOLLW69.000 1 | 77 | 90 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
81 | 341974 2NORWOOD T 69.000 342256 2SHOPVILLE 69.000 1 | 146 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
82 | 342286 2SOMERSET 69.000 341233 2CABIN HOLLW69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
83 | 342286 2SOMERSET 69.000 341980 2OAK HILL NO69.000 1 | 146 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
84 | 342286 2SOMERSET 69.000 342287 2SOMERSET KU69.000 1 | 146 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85 | 342364 2TOMM GOOC 69.000 342821 5TOMMY EK 161.00 1 | 144 | 175 | 198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
86 | 342364 2TOMM GOOC 69.000 342821 5TOMMY EK 161.00 2 | 144 | 175 | 198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
87 | 342472 2WALNUT GROV69.000 341032 2ASAHI M W T69.000 1 | 89 | 98 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
88 | 342472 2WALNUT GROV69.000 341818 2MARETBURG T69.000 1 | 57 | 63 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
89 | 342505 2WINDSOR 69.000 341938 2NANCY 69.000 1 | 146 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90 | 342505 2WINDSOR 69.000 342217 2SALEM EK T 69.000 1 | 146 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
91 | 342757 5LAUREL DAM 161.00 342754 5LAUREL CO 161.00 1 | 342 | 525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
92 | 342757 5LAUREL DAM 161.00 342945 1LAUREL 1G 13.800 1 | 83 | 94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
93 | 342769 5MARION CO 161.00 339206 AE1-143 C 161.00 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
94 | 342770 4MARION CO 138.00 324271 4LEBANON 138.00 1 | 508 | 568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
95 | 342770 4MARION CO 138.00 324271 4LEBANON 138.00 2 | 508 | 568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
96 | 342770 4MARION CO 138.00 324271 4LEBANON 138.00 3 | 508 | 568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97 | 342787 5PULASK CO 161.00 342782 5PINEVILL EK161.00 1 | 342 | 525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
98 | 342793 5RUSSEL CO 161.00 342178 2RUSSEL CO 69.000 1 | 144 | 152 | 166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
99 | 342817 5TAYLOR CO J161.00 325921 5TAYLOR CO 161.00 1 | 159 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
100 | 342817 5TAYLOR CO J161.00 342733 5GREEN CO 161.00 1 | 684 | 1050 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
101 | 360448 5WOLF CRK HP161.00 360334 5SUMMER SHAD161.00 1 | 342 | 525 | 0 | 181.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
102 | 360448 5WOLF CRK HP161.00 360486 5WAYNE CO KY161.00 1 | 342 | 525 | 0 | 181.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
103 | 360448 5WOLF CRK HP161.00 361618 5KELSEY RD 161.00 1 | 342 | 525 | 0 | 181.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
104 | 360448 5WOLF CRK HP161.00 361666 5BURKSVLTP 161.00 1 | 342 | 525 | 0 | 181.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
105 | 360448 5WOLF CRK HP161.00 364620 1WOLFCR H1-213.800 1 | 112.5 | 112.5 | 112.5 | 112.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
106 | 360448 5WOLF CRK HP161.00 364621 1WOLFCR H3-413.800 2 | 112.5 | 112.5 | 112.5 | 112.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
107 | 360448 5WOLF CRK HP161.00 364622 1WOLFCR H5-613.800 3 | 112.5 | 112.5 | 112.5 | 112.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
108 | 942410 AE2-254 TAP 69.000 341515 2GARRARD CO 69.000 1 | 146 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
109 | 942410 AE2-254 TAP 69.000 942411 AE2-254 C O169.000 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
110 | 944150 AF1-083 TAP 161.00 944151 AF1-083 C O1161.00 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No Contingencies..
Note 1: Contingency labels appended with '+T' have 'Tripping' solutions.
Note 2: Contingency labels appended with '+CA' have 'Corrective Action' solutions.
BASE CASE, SING OPN LIN 1 339206-342769(1), SING OPN LIN 2 339206-939132(1), SING OPN LIN 3 341002-341443(1), SING OPN LIN 4 341002-341752(1), SING OPN LIN 5 341008-342106(1), SING OPN LIN 6 341008-342430(1),
SING OPN LIN 7 341014-341017(1), SING OPN LIN 8 341017-341428(1), SING OPN LIN 9 341017-342391(1), SING OPN LIN 10 341020-341782(1), SING OPN LIN 11 341020-342538(1), SING OPN LIN 12 341029-341032(1), SING OPN LIN 13 341032-341379(1),
SING OPN LIN 14 341032-342077(1), SING OPN LIN 15 341032-342472(1), SING OPN LIN 16 341035-341038(1), SING OPN LIN 17 341038-341755(1), SING OPN LIN 18 341038-342187(1), SING OPN LIN 19 341041-341635(1), SING OPN LIN 20 341041-341638(1),
SING OPN LIN 21 341041-342547(1), SING OPN LIN 22 341044-341671(1), SING OPN LIN 23 341044-342361(1), SING OPN LIN 24 341047-342424(1), SING OPN LIN 25 341050-342295(1), SING OPN LIN 26 341053-341056(1), SING OPN LIN 27 341056-341407(1),
SING OPN LIN 28 341056-342424(1), SING OPN LIN 29 341059-341275(1), SING OPN LIN 30 341059-341542(1), SING OPN LIN 31 341059-341651(1), SING OPN LIN 32 341059-342694(1), SING OPN LIN 33 341062-341269(1), SING OPN LIN 34 341065-341068(1),
SING OPN LIN 35 341068-341215(1), SING OPN LIN 36 341068-342253(1), SING OPN LIN 37 341071-341074(1), SING OPN LIN 38 341071-341077(1), SING OPN LIN 39 341071-342520(1), SING OPN LIN 40 341074-341992(1), SING OPN LIN 41 341077-341173(1),
SING OPN LIN 42 341080-341149(1), SING OPN LIN 43 341080-342445(1), SING OPN LIN 44 341089-342500(1), SING OPN LIN 45 341092-341095(1), SING OPN LIN 46 341095-341164(1), SING OPN LIN 47 341095-341227(1), SING OPN LIN 48 341098-342433(1),
SING OPN LIN 49 341104-341107(1), SING OPN LIN 50 341107-341164(1), SING OPN LIN 51 341107-341917(1), SING OPN LIN 52 341110-341113(1), SING OPN LIN 53 341110-341439(1), SING OPN LIN 54 341113-341464(1), SING OPN LIN 55 341113-342001(1),
SING OPN LIN 56 341114-341115(1), SING OPN LIN 57 341115-342223(1), SING OPN LIN 58 341115-342346(1), SING OPN LIN 59 341116-341119(1), SING OPN LIN 60 341119-341620(1), SING OPN LIN 61 341119-342088(1), SING OPN LIN 62 341122-341125(1),
SING OPN LIN 63 341122-341692(1), SING OPN LIN 64 341122-341860(1), SING OPN LIN 65 341131-341134(1), SING OPN LIN 66 341131-341644(1), SING OPN LIN 67 341131-342112(1), SING OPN LIN 68 341137-341296(1), SING OPN LIN 69 341137-341935(1),
SING OPN LIN 70 341140-341143(1), SING OPN LIN 71 341143-342019(1), SING OPN LIN 72 341143-342508(1), SING OPN LIN 73 341149-341272(1), SING OPN LIN 74 341152-341155(1), SING OPN LIN 75 341155-341803(1), SING OPN LIN 76 341155-341860(1),
SING OPN LIN 77 341158-341161(1), SING OPN LIN 78 341158-341908(1), SING OPN LIN 79 341161-342403(1), SING OPN LIN 80 341164-341167(1), SING OPN LIN 81 341164-342388(1), SING OPN LIN 82 341164-342466(1), SING OPN LIN 83 341164-342559(1),
SING OPN LIN 84 341170-341173(1), SING OPN LIN 85 341173-342196(1), SING OPN LIN 86 341179-341746(1), SING OPN LIN 87 341179-342514(1), SING OPN LIN 88 341185-341614(1), SING OPN LIN 89 341185-342100(1), SING OPN LIN 90 341188-341488(1),
SING OPN LIN 91 341188-341587(1), SING OPN LIN 92 341194-342385(1), SING OPN LIN 93 341194-342388(1), SING OPN LIN 94 341197-341818(1), SING OPN LIN 95 341197-342349(1), SING OPN LIN 96 341200-341920(1), SING OPN LIN 97 341200-342010(1),
SING OPN LIN 98 341203-341206(1), SING OPN LIN 99 341206-341347(1), SING OPN LIN 100 341206-341392(1), SING OPN LIN 101 341209-341210(1), SING OPN LIN 102 341209-341617(1), SING OPN LIN 103 341209-342367(1), SING OPN LIN 104 341212-341774(1),
SING OPN LIN 105 341212-342500(1), SING OPN LIN 106 341215-341281(1), SING OPN LIN 107 341215-341389(1), SING OPN LIN 108 341215-342700(1), SING OPN LIN 109 341218-341227(1), SING OPN LIN 110 341218-341605(1), SING OPN LIN 111 341224-341227(1),
SING OPN LIN 112 341233-341974(1), SING OPN LIN 113 341233-342286(1), SING OPN LIN 114 341248-341608(1), SING OPN LIN 115 341248-342520(1), SING OPN LIN 116 341251-341254(1), SING OPN LIN 117 341254-341872(1), SING OPN LIN 118 341254-342259(1),
SING OPN LIN 119 341260-342013(1), SING OPN LIN 120 341263-341266(1), SING OPN LIN 121 341266-342034(1), SING OPN LIN 122 341266-342475(1), SING OPN LIN 123 341269-342064(1), SING OPN LIN 124 341269-342703(1), SING OPN LIN 125 341272-341275(1),
SING OPN LIN 126 341275-342241(1), SING OPN LIN 127 341281-342082(1), SING OPN LIN 128 341287-341713(1), SING OPN LIN 129 341287-342307(1), SING OPN LIN 130 341287-342568(1), SING OPN LIN 131 341293-341296(1), SING OPN LIN 132 341296-342262(1),
SING OPN LIN 133 341299-341989(1), SING OPN LIN 134 341299-342124(1), SING OPN LIN 135 341302-341305(1), SING OPN LIN 136 341305-341593(1), SING OPN LIN 137 341305-341599(1), SING OPN LIN 138 341308-341314(1), SING OPN LIN 139 341311-341314(1),
SING OPN LIN 140 341311-342184(1), SING OPN LIN 141 341311-342406(1), SING OPN LIN 142 341317-341390(1), SING OPN LIN 143 341320-341512(1), SING OPN LIN 144 341323-341335(1), SING OPN LIN 145 341323-341512(1), SING OPN LIN 146 341323-342235(1),
SING OPN LIN 147 341326-341488(1), SING OPN LIN 148 341326-342133(1), SING OPN LIN 149 341329-341332(1), SING OPN LIN 150 341332-341944(1), SING OPN LIN 151 341332-342155(1), SING OPN LIN 152 341335-341370(1), SING OPN LIN 153 341335-342436(1),
SING OPN LIN 154 341338-341341(1), SING OPN LIN 155 341341-342346(1), SING OPN LIN 156 341341-342349(1), SING OPN LIN 157 341342-341343(1), SING OPN LIN 158 341342-341761(1), SING OPN LIN 159 341342-342067(1), SING OPN LIN 160 341344-341347(1),
SING OPN LIN 161 341344-342286(1), SING OPN LIN 162 341344-342286(2), SING OPN LIN 163 341344-342715(1), SING OPN LIN 164 341350-342067(1), SING OPN LIN 165 341353-341356(1), SING OPN LIN 166 341356-341653(1), SING OPN LIN 167 341356-342265(1),
SING OPN LIN 168 341359-341362(1), SING OPN LIN 169 341359-342288(1), SING OPN LIN 170 341362-341406(1), SING OPN LIN 171 341362-341611(1), SING OPN LIN 172 341366-341370(1), SING OPN LIN 173 341377-342355(1), SING OPN LIN 174 341377-936380(1),
SING OPN LIN 175 341379-342256(1), SING OPN LIN 176 341380-341959(1), SING OPN LIN 177 341380-341962(1), SING OPN LIN 178 341380-342574(1), SING OPN LIN 179 341381-341382(1), SING OPN LIN 180 341381-341930(1), SING OPN LIN 181 341381-342452(1),
SING OPN LIN 182 341382-341734(1), SING OPN LIN 183 341383-341467(1), SING OPN LIN 184 341383-341965(1), SING OPN LIN 185 341386-341389(1), SING OPN LIN 186 341389-341707(1), SING OPN LIN 187 341390-341391(1), SING OPN LIN 188 341390-341950(1),
SING OPN LIN 189 341392-341578(1), SING OPN LIN 190 341392-342499(1), SING OPN LIN 191 341392-342727(1), SING OPN LIN 192 341394-341479(1), SING OPN LIN 193 341394-342151(1), SING OPN LIN 194 341394-342157(1), SING OPN LIN 195 341394-342274(1),
SING OPN LIN 196 341398-341605(1), SING OPN LIN 197 341398-341880(1), SING OPN LIN 198 341400-342091(1), SING OPN LIN 199 341401-341842(1), SING OPN LIN 200 341404-341842(1), SING OPN LIN 201 341404-342295(1), SING OPN LIN 202 341404-342388(1),
SING OPN LIN 203 341405-341406(1), SING OPN LIN 204 341407-342019(1), SING OPN LIN 205 341410-341929(1), SING OPN LIN 206 341416-342076(1), SING OPN LIN 207 341419-341422(1), SING OPN LIN 208 341419-341941(1), SING OPN LIN 209 341419-341974(1),
SING OPN LIN 210 341425-341428(1), SING OPN LIN 211 341428-341809(1), SING OPN LIN 212 341431-341434(1), SING OPN LIN 213 341431-341728(1), SING OPN LIN 214 341431-342322(1), SING OPN LIN 215 341434-341437(1), SING OPN LIN 216 341434-341680(1),
SING OPN LIN 217 341443-341446(1), SING OPN LIN 218 341443-341953(1), SING OPN LIN 219 341449-342163(1), SING OPN LIN 220 341455-341458(1), SING OPN LIN 221 341455-342274(1), SING OPN LIN 222 341455-342379(1), SING OPN LIN 223 341458-342340(1),
SING OPN LIN 224 341461-341797(1), SING OPN LIN 225 341461-342310(1), SING OPN LIN 226 341464-341569(1), SING OPN LIN 227 341464-342391(1), SING OPN LIN 228 341464-342730(1), SING OPN LIN 229 341467-342580(1), SING OPN LIN 230 341470-341473(1),
SING OPN LIN 231 341470-342511(1), SING OPN LIN 232 341473-342115(1), SING OPN LIN 233 341473-342193(1), SING OPN LIN 234 341476-341899(1), SING OPN LIN 235 341476-342130(1), SING OPN LIN 236 341485-341488(1), SING OPN LIN 237 341485-341550(1),
SING OPN LIN 238 341491-341548(1), SING OPN LIN 239 341491-342037(1), SING OPN LIN 240 341491-342043(1), SING OPN LIN 241 341491-342049(1), SING OPN LIN 242 341491-342732(1), SING OPN LIN 243 341494-341497(1), SING OPN LIN 244 341494-341935(1),
SING OPN LIN 245 341494-342508(1), SING OPN LIN 246 341500-341644(1), SING OPN LIN 247 341500-341824(1), SING OPN LIN 248 341503-341506(1), SING OPN LIN 249 341503-341578(1), SING OPN LIN 250 341503-341887(1), SING OPN LIN 251 341509-341512(1),
SING OPN LIN 252 341515-341732(1), SING OPN LIN 253 341515-942410(1), SING OPN LIN 254 341518-341521(1), SING OPN LIN 255 341521-341806(1), SING OPN LIN 256 341530-342043(1), SING OPN LIN 257 341530-342445(1), SING OPN LIN 258 341533-341632(1),
SING OPN LIN 259 341533-342307(1), SING OPN LIN 260 341536-341623(1), SING OPN LIN 261 341536-341989(1), SING OPN LIN 262 341536-342088(1), SING OPN LIN 263 341536-342589(1), SING OPN LIN 264 341539-341686(1), SING OPN LIN 265 341542-341548(1),
SING OPN LIN 266 341551-341587(1), SING OPN LIN 267 341551-342298(1), SING OPN LIN 268 341554-341752(1), SING OPN LIN 269 341554-342034(1), SING OPN LIN 270 341563-341575(1), SING OPN LIN 271 341563-342325(1), SING OPN LIN 272 341563-342733(1),
SING OPN LIN 273 341569-341572(1), SING OPN LIN 274 341569-341806(1), SING OPN LIN 275 341575-341854(1), SING OPN LIN 276 341578-341581(1), SING OPN LIN 277 341584-341587(1), SING OPN LIN 278 341590-341593(1), SING OPN LIN 279 341593-342301(1),
SING OPN LIN 280 341596-341599(1), SING OPN LIN 281 341599-342370(1), SING OPN LIN 282 341602-341872(1), SING OPN LIN 283 341602-342280(1), SING OPN LIN 284 341602-936380(1), SING OPN LIN 285 341605-342595(1), SING OPN LIN 286 341608-342313(1),
SING OPN LIN 287 341611-342103(1), SING OPN LIN 288 341614-342520(1), SING OPN LIN 289 341617-341896(1), SING OPN LIN 290 341620-342163(1), SING OPN LIN 291 341623-342052(1), SING OPN LIN 292 341632-341800(1), SING OPN LIN 293 341632-342316(1),
SING OPN LIN 294 341638-342199(1), SING OPN LIN 295 341638-342463(1), SING OPN LIN 296 341641-341887(1), SING OPN LIN 297 341644-341683(1), SING OPN LIN 298 341647-341650(1), SING OPN LIN 299 341650-341651(Z1), SING OPN LIN 300 341651-341914(1),
SING OPN LIN 301 341653-341656(1), SING OPN LIN 302 341653-341890(1), SING OPN LIN 303 341659-341662(1), SING OPN LIN 304 341662-341671(1), SING OPN LIN 305 341662-341857(1), SING OPN LIN 306 341665-341701(1), SING OPN LIN 307 341665-341869(1),
SING OPN LIN 308 341665-342596(1), SING OPN LIN 309 341671-342061(1), SING OPN LIN 310 341677-341890(1), SING OPN LIN 311 341683-342100(1), SING OPN LIN 312 341686-341689(1), SING OPN LIN 313 341686-342076(1), SING OPN LIN 314 341692-341695(1),
SING OPN LIN 315 341692-342343(1), SING OPN LIN 316 341701-342370(1), SING OPN LIN 317 341704-341707(1), SING OPN LIN 318 341707-342427(1), SING OPN LIN 319 341716-341722(1), SING OPN LIN 320 341719-341740(1), SING OPN LIN 321 341719-342073(1),
SING OPN LIN 322 341722-341740(1), SING OPN LIN 323 341722-342187(1), SING OPN LIN 324 341725-342007(1), SING OPN LIN 325 341725-342058(1), SING OPN LIN 326 341728-341854(1), SING OPN LIN 327 341731-341732(1), SING OPN LIN 328 341732-341959(1),
SING OPN LIN 329 341734-341737(1), SING OPN LIN 330 341740-342754(1), SING OPN LIN 331 341746-342253(1), SING OPN LIN 332 341749-342058(1), SING OPN LIN 333 341749-342133(1), SING OPN LIN 334 341755-341758(1), SING OPN LIN 335 341761-341767(1),
SING OPN LIN 336 341761-341896(1), SING OPN LIN 337 341761-342760(1), SING OPN LIN 338 341764-341767(1), SING OPN LIN 339 341767-342064(1), SING OPN LIN 340 341772-341774(1), SING OPN LIN 341 341774-341775(1), SING OPN LIN 342 341775-342247(1),
SING OPN LIN 343 341776-342208(1), SING OPN LIN 344 341776-342316(1), SING OPN LIN 345 341779-341782(1), SING OPN LIN 346 341782-342475(1), SING OPN LIN 347 341785-341788(1), SING OPN LIN 348 341788-342155(1), SING OPN LIN 349 341788-342379(1),
SING OPN LIN 350 341791-341794(1), SING OPN LIN 351 341794-341935(1), SING OPN LIN 352 341794-342061(1), SING OPN LIN 353 341797-342265(1), SING OPN LIN 354 341800-342325(1), SING OPN LIN 355 341803-342310(1), SING OPN LIN 356 341803-342313(1),
SING OPN LIN 357 341809-341812(1), SING OPN LIN 358 341809-341929(1), SING OPN LIN 359 341815-341818(1), SING OPN LIN 360 341818-342472(1), SING OPN LIN 361 341821-341824(1), SING OPN LIN 362 341824-341833(1), SING OPN LIN 363 341827-342343(1),
SING OPN LIN 364 341830-341833(1), SING OPN LIN 365 341833-341890(1), SING OPN LIN 366 341836-341953(1), SING OPN LIN 367 341836-342265(1), SING OPN LIN 368 341839-341842(1), SING OPN LIN 369 341845-342139(1), SING OPN LIN 370 341845-342490(1),
SING OPN LIN 371 341845-342778(1), SING OPN LIN 372 341848-342223(1), SING OPN LIN 373 341848-342391(1), SING OPN LIN 374 341851-341854(1), SING OPN LIN 375 341857-342406(1), SING OPN LIN 376 341860-341863(1), SING OPN LIN 377 341869-341875(1),
SING OPN LIN 378 341869-342259(1), SING OPN LIN 379 341872-341878(1), SING OPN LIN 380 341887-342268(1), SING OPN LIN 381 341893-341896(1), SING OPN LIN 382 341908-341914(1), SING OPN LIN 383 341911-341914(1), SING OPN LIN 384 341917-341998(1),
SING OPN LIN 385 341920-341998(1), SING OPN LIN 386 341920-342502(1), SING OPN LIN 387 341923-342091(1), SING OPN LIN 388 341923-342280(1), SING OPN LIN 389 341926-342181(1), SING OPN LIN 390 341926-342283(1), SING OPN LIN 391 341926-342397(1),
SING OPN LIN 392 341929-341930(1), SING OPN LIN 393 341935-342208(1), SING OPN LIN 394 341938-342505(1), SING OPN LIN 395 341938-342526(1), SING OPN LIN 396 341941-341947(1), SING OPN LIN 397 341941-341971(1), SING OPN LIN 398 341944-342424(1),
SING OPN LIN 399 341944-342514(1), SING OPN LIN 400 341950-342007(1), SING OPN LIN 401 341953-342229(1), SING OPN LIN 402 341962-342361(1), SING OPN LIN 403 341965-342199(1), SING OPN LIN 404 341971-342115(1), SING OPN LIN 405 341974-342256(1),
SING OPN LIN 406 341977-341983(1), SING OPN LIN 407 341980-341983(1), SING OPN LIN 408 341980-342286(1), SING OPN LIN 409 341983-342469(1), SING OPN LIN 410 341986-341989(1), SING OPN LIN 411 342007-342008(1), SING OPN LIN 412 342007-342010(1),
SING OPN LIN 413 342007-342013(1), SING OPN LIN 414 342016-342019(1), SING OPN LIN 415 342022-342025(1), SING OPN LIN 416 342022-342052(1), SING OPN LIN 417 342022-342112(1), SING OPN LIN 418 342031-342034(1), SING OPN LIN 419 342037-342040(1),
SING OPN LIN 420 342049-342161(1), SING OPN LIN 421 342049-940830(1), SING OPN LIN 422 342067-342505(1), SING OPN LIN 423 342070-342073(1), SING OPN LIN 424 342073-342451(1), SING OPN LIN 425 342076-342139(1), SING OPN LIN 426 342077-342782(1),
SING OPN LIN 427 342085-342088(1), SING OPN LIN 428 342091-342124(1), SING OPN LIN 429 342091-342634(1), SING OPN LIN 430 342097-342184(1), SING OPN LIN 431 342100-342301(1), SING OPN LIN 432 342100-342637(1), SING OPN LIN 433 342103-342106(1),
SING OPN LIN 434 342109-342112(1), SING OPN LIN 435 342115-342787(1), SING OPN LIN 436 342118-342121(1), SING OPN LIN 437 342121-342328(1), SING OPN LIN 438 342121-342415(1), SING OPN LIN 439 342127-342265(1), SING OPN LIN 440 342127-342421(1),
SING OPN LIN 441 342130-342259(1), SING OPN LIN 442 342133-342355(1), SING OPN LIN 443 342133-342640(1), SING OPN LIN 444 342136-342139(1), SING OPN LIN 445 342145-342487(1), SING OPN LIN 446 342154-342155(1), SING OPN LIN 447 342157-342418(1),
SING OPN LIN 448 342160-342161(1), SING OPN LIN 449 342161-342334(1), SING OPN LIN 450 342163-342649(1), SING OPN LIN 451 342166-342169(1), SING OPN LIN 452 342166-342172(1), SING OPN LIN 453 342166-342235(1), SING OPN LIN 454 342169-342175(1),
SING OPN LIN 455 342169-342178(1), SING OPN LIN 456 342178-342232(1), SING OPN LIN 457 342178-342793(1), SING OPN LIN 458 342184-342262(1), SING OPN LIN 459 342186-342424(1), SING OPN LIN 460 342186-342427(1), SING OPN LIN 461 342196-342391(1),
SING OPN LIN 462 342199-342202(1), SING OPN LIN 463 342208-342211(1), SING OPN LIN 464 342214-342217(1), SING OPN LIN 465 342217-342481(1), SING OPN LIN 466 342217-342505(1), SING OPN LIN 467 342220-342223(1), SING OPN LIN 468 342222-342703(1),
SING OPN LIN 469 342222-342760(1), SING OPN LIN 470 342235-943700(1), SING OPN LIN 471 342238-342241(1), SING OPN LIN 472 342247-342248(1), SING OPN LIN 473 342247-342410(1), SING OPN LIN 474 342247-342808(1), SING OPN LIN 475 342250-342253(1),
SING OPN LIN 476 342265-342658(1), SING OPN LIN 477 342268-342478(1), SING OPN LIN 478 342271-342274(1), SING OPN LIN 479 342277-342283(1), SING OPN LIN 480 342283-342322(1), SING OPN LIN 481 342286-342287(1), SING OPN LIN 482 342292-342295(1),
SING OPN LIN 483 342292-342298(1), SING OPN LIN 484 342292-342667(1), SING OPN LIN 485 342307-342403(1), SING OPN LIN 486 342307-342412(1), SING OPN LIN 487 342319-342322(1), SING OPN LIN 488 342319-342334(1), SING OPN LIN 489 342319-940830(1),
SING OPN LIN 490 342322-342436(1), SING OPN LIN 491 342322-342814(1), SING OPN LIN 492 342337-342340(1), SING OPN LIN 493 342343-342421(1), SING OPN LIN 494 342349-342433(1), SING OPN LIN 495 342352-342355(1), SING OPN LIN 496 342358-342361(1),
SING OPN LIN 497 342364-342367(1), SING OPN LIN 498 342364-342821(1), SING OPN LIN 499 342364-342821(2), SING OPN LIN 500 342367-942410(1), SING OPN LIN 501 342379-342382(1), SING OPN LIN 502 342385-342487(1), SING OPN LIN 503 342391-342820(1),
SING OPN LIN 504 342394-342397(1), SING OPN LIN 505 342397-342532(1), SING OPN LIN 506 342400-342403(1), SING OPN LIN 507 342415-342418(1), SING OPN LIN 508 342430-342433(1), SING OPN LIN 509 342430-342691(1), SING OPN LIN 510 342436-342439(1),
SING OPN LIN 511 342442-342445(1), SING OPN LIN 512 342451-342452(1), SING OPN LIN 513 342460-342463(1), SING OPN LIN 514 342469-342526(1), SING OPN LIN 515 342472-342511(1), SING OPN LIN 516 342478-342532(1), SING OPN LIN 517 342478-342535(1),
SING OPN LIN 518 342478-342823(1), SING OPN LIN 519 342481-342484(1), SING OPN LIN 520 342481-943700(1), SING OPN LIN 521 342490-342493(1), SING OPN LIN 522 342490-342499(1), SING OPN LIN 523 342496-342499(1), SING OPN LIN 524 342523-342526(1),
SING OPN LIN 525 342529-342535(1), SING OPN LIN 526 342538-342616(1), SING OPN LIN 527 342541-342544(1), SING OPN LIN 528 342541-342556(1), SING OPN LIN 529 342541-342580(1), SING OPN LIN 530 342541-342631(1), SING OPN LIN 531 342541-342829(1),
SING OPN LIN 532 342550-342559(1), SING OPN LIN 533 342550-342640(1), SING OPN LIN 534 342553-342556(1), SING OPN LIN 535 342556-342565(1), SING OPN LIN 536 342559-342646(1), SING OPN LIN 537 342559-342673(1), SING OPN LIN 538 342565-342574(1),
SING OPN LIN 539 342571-342589(1), SING OPN LIN 540 342571-342649(1), SING OPN LIN 541 342574-342596(1), SING OPN LIN 542 342574-342676(1), SING OPN LIN 543 342577-342607(1), SING OPN LIN 544 342577-342676(1), SING OPN LIN 545 342577-342691(1),
SING OPN LIN 546 342583-342589(1), SING OPN LIN 547 342583-342664(1), SING OPN LIN 548 342586-342587(1), SING OPN LIN 549 342586-342673(1), SING OPN LIN 550 342589-342634(1), SING OPN LIN 551 342596-342607(1), SING OPN LIN 552 342598-342664(1),
SING OPN LIN 553 342601-342604(1), SING OPN LIN 554 342604-342631(1), SING OPN LIN 555 342604-925980(1), SING OPN LIN 556 342607-342610(1), SING OPN LIN 557 342607-342613(1), SING OPN LIN 558 342607-342637(1), SING OPN LIN 559 342607-342688(1),
SING OPN LIN 560 342610-342832(1), SING OPN LIN 561 342613-342832(1), SING OPN LIN 562 342622-342625(1), SING OPN LIN 563 342622-342634(1), SING OPN LIN 564 342622-342664(1), SING OPN LIN 565 342637-342784(1), SING OPN LIN 566 342640-342664(1),
SING OPN LIN 567 342640-925980(1), SING OPN LIN 568 342643-342646(1), SING OPN LIN 569 342646-342667(1), SING OPN LIN 570 342649-342658(1), SING OPN LIN 571 342661-342664(1), SING OPN LIN 572 342664-342667(1), SING OPN LIN 573 342664-342838(1),
SING OPN LIN 574 342664-342838(2), SING OPN LIN 575 342664-342838(3), SING OPN LIN 576 342670-342673(1), SING OPN LIN 577 342676-342679(1), SING OPN LIN 578 342685-342688(1), SING OPN LIN 579 342694-342813(1), SING OPN LIN 580 342697-342780(1),
SING OPN LIN 581 342700-342819(1), SING OPN LIN 582 342703-342769(1), SING OPN LIN 583 342715-342718(1), SING OPN LIN 584 342715-342790(1), SING OPN LIN 585 342715-342799(1), SING OPN LIN 586 342718-342727(1), SING OPN LIN 587 342718-342757(1),
SING OPN LIN 588 342721-342724(1), SING OPN LIN 589 342724-342766(1), SING OPN LIN 590 342724-342808(1), SING OPN LIN 591 342730-342820(1), SING OPN LIN 592 342733-342817(1), SING OPN LIN 593 342733-943820(1), SING OPN LIN 594 342736-342739(1),
SING OPN LIN 595 342736-342820(1), SING OPN LIN 596 342742-342745(1), SING OPN LIN 597 342745-342751(1), SING OPN LIN 598 342745-342799(1), SING OPN LIN 599 342748-342751(1), SING OPN LIN 600 342751-342792(1), SING OPN LIN 601 342754-342757(1),
SING OPN LIN 602 342754-342783(1), SING OPN LIN 603 342760-342790(1), SING OPN LIN 604 342763-342766(1), SING OPN LIN 605 342766-342819(1), SING OPN LIN 606 342769-342770(1), SING OPN LIN 607 342769-342770(2), SING OPN LIN 608 342769-342770(3),
SING OPN LIN 609 342769-342770(4), SING OPN LIN 610 342769-342781(1), SING OPN LIN 611 342772-342797(1), SING OPN LIN 612 342775-342781(1), SING OPN LIN 613 342775-342797(1), SING OPN LIN 614 342775-342805(1), SING OPN LIN 615 342779-342780(1),
SING OPN LIN 616 342780-342784(1), SING OPN LIN 617 342782-342787(1), SING OPN LIN 618 342783-342820(1), SING OPN LIN 619 342787-342790(1), SING OPN LIN 620 342792-342796(1), SING OPN LIN 621 342793-342796(1), SING OPN LIN 622 342797-342798(1),
SING OPN LIN 623 342802-342805(1), SING OPN LIN 624 342805-944150(1), SING OPN LIN 625 342813-342814(1), SING OPN LIN 626 342814-943820(1), SING OPN LIN 627 342817-944150(1), SING OPN LIN 628 342818-342819(1), SING OPN LIN 629 342829-342835(1),
SING OPN LIN 630 342832-342835(1), SING OPN LIN 631 342832-342841(1), SING OPN LIN 632 342835-342838(1), SING OPN LIN 633 925980-925981(1), SING OPN LIN 634 925980-932551(1), SING OPN LIN 635 925981-925982(1), SING OPN LIN 636 932551-932552(1),
SING OPN LIN 637 936380-936381(1), SING OPN LIN 638 936381-936382(1), SING OPN LIN 639 940830-940831(1), SING OPN LIN 640 940831-940832(1), SING OPN LIN 641 942410-942411(1), SING OPN LIN 642 942411-942412(1), SING OPN LIN 643 943700-943701(1),
SING OPN LIN 644 943701-943702(1), SING OPN LIN 645 943820-943821(1), SING OPN LIN 646 943821-943822(1), SING OPN LIN 647 944150-944151(1), SING OPN LIN 648 944151-944152(1), SING OPN TIE 649 341020-243725(1), SING OPN TIE 650 341071-324430(1),
SING OPN TIE 651 341089-325102(1), SING OPN TIE 652 341161-324213(1), SING OPN TIE 653 341188-324463(1), SING OPN TIE 654 341188-324722(1), SING OPN TIE 655 341317-324474(1), SING OPN TIE 656 341320-324830(1), SING OPN TIE 657 341406-324530(1),
SING OPN TIE 658 341407-324425(1), SING OPN TIE 659 341461-243721(Z1), SING OPN TIE 660 341515-324600(1), SING OPN TIE 661 341539-324784(1), SING OPN TIE 662 341554-243726(1), SING OPN TIE 663 341563-324554(1), SING OPN TIE 664 341605-251579(1),
SING OPN TIE 665 341608-243812(Z1), SING OPN TIE 666 341632-324575(1), SING OPN TIE 667 341632-324660(1), SING OPN TIE 668 341713-324519(1), SING OPN TIE 669 341740-324576(1), SING OPN TIE 670 341752-243737(Z1), SING OPN TIE 671 341755-324527(1),
SING OPN TIE 672 341890-246973(Z1), SING OPN TIE 673 341923-324717(1), SING OPN TIE 674 341923-325019(1), SING OPN TIE 675 341929-324662(1), SING OPN TIE 676 341935-324736(1), SING OPN TIE 677 341944-324288(1), SING OPN TIE 678 342007-324455(1),
SING OPN TIE 679 342008-324290(1), SING OPN TIE 680 342055-243742(1), SING OPN TIE 681 342058-324951(1), SING OPN TIE 682 342133-324492(1), SING OPN TIE 683 342157-324708(1), SING OPN TIE 684 342184-324445(1), SING OPN TIE 685 342184-324445(2),
SING OPN TIE 686 342218-247897(Z1), SING OPN TIE 687 342232-324787(1), SING OPN TIE 688 342248-324718(1), SING OPN TIE 689 342287-324531(1), SING OPN TIE 690 342287-324737(1), SING OPN TIE 691 342307-324509(1), SING OPN TIE 692 342340-324519(1),
SING OPN TIE 693 342343-246971(1), SING OPN TIE 694 342454-251315(1), SING OPN TIE 695 342487-250148(1), SING OPN TIE 696 342538-243688(1), SING OPN TIE 697 342544-324275(1), SING OPN TIE 698 342547-324210(1), SING OPN TIE 699 342559-250054(1),
SING OPN TIE 700 342565-325925(1), SING OPN TIE 701 342568-324047(1), SING OPN TIE 702 342568-324261(1), SING OPN TIE 703 342577-324247(1), SING OPN TIE 704 342577-324248(1), SING OPN TIE 705 342586-324253(1), SING OPN TIE 706 342595-250152(1),
SING OPN TIE 707 342607-342918(1), SING OPN TIE 708 342607-342921(1), SING OPN TIE 709 342607-342924(1), SING OPN TIE 710 342607-342927(1), SING OPN TIE 711 342607-342930(1), SING OPN TIE 712 342607-342933(1), SING OPN TIE 713 342607-342936(1),
SING OPN TIE 714 342616-342948(1), SING OPN TIE 715 342631-324328(1), SING OPN TIE 716 342649-324302(1), SING OPN TIE 717 342661-324267(1), SING OPN TIE 718 342664-342957(1), SING OPN TIE 719 342688-324276(1), SING OPN TIE 720 342697-324138(1),
SING OPN TIE 721 342697-324430(1), SING OPN TIE 722 342700-326975(1), SING OPN TIE 723 342700-326998(1), SING OPN TIE 724 342718-324141(1), SING OPN TIE 725 342732-361603(1), SING OPN TIE 726 342736-324138(1), SING OPN TIE 727 342757-342945(1),
SING OPN TIE 728 342770-324271(1), SING OPN TIE 729 342770-324271(2), SING OPN TIE 730 342770-324271(3), SING OPN TIE 731 342778-360473(1), SING OPN TIE 732 342778-360486(1), SING OPN TIE 733 342778-361579(1), SING OPN TIE 734 342782-342837(1),
SING OPN TIE 735 342783-324688(1), SING OPN TIE 736 342796-360448(1), SING OPN TIE 737 342814-360334(1), SING OPN TIE 738 342814-361788(1), SING OPN TIE 739 342817-325921(1), SING OPN TIE 740 342821-342839(1), SING OPN TIE 741 342821-342839(2),
SING OPN TIE 742 342823-360486(1), SING OPN TIE 743 342832-342939-342942(1), SING OPN TIE 744 342838-249581(1), SING OPN TIE 745 342838-253077(1), SING OPN TIE 746 342838-342960(1), SING OPN TIE 747 342838-342963(1), SING OPN TIE 748 342838-342966(1),
SING OPN TIE 749 342841-325074(Z1), SING OPN TIE 750 342844-384157(1), SING OPN TIE 751 342847-243205(1), BARREN CO - HORSECAVE 69 SS, CAVE CITY J-SEYMOUR T 69 SS, CAVE CITY - CAVE CITY JCT 69 SS, FOX HOLLOW - PARKWAY1 69 SS,
WAYNE CO - ZULA TAP 69 SS, EKPC_P1-2_ARGEN - LEON69, EKPC_P1-2_N SPR -S AND69, EKPC_P1-2_DALE-GARRD 69, EKPC_P1-2_STEPH-HODG 69, EKPC_P1-2_HODG-GREEN 69, EKPC_P1-2_HODG-N SPR 69,
EKPC_P1-2_E BARD-N SPR69, EKPC_P1-2_HNTFMJ-N SPR69, EKPC_P1-2_BONN - BARR 69, EKPC_P1-2_GREEN-SUM SH69, EKPC_P1-2_CASEY-LIB J69, EKPC_P1-2_LIB J-GARR69, EKPC_P1-2_LIB J-WIND 69,
EKPC_P1-2_SSET-NORWJ69, EKPC_P1-2_BARR- FOX H 69, EKPC_P1-2_FOX H-AE2-07169, EKPC_P1-2_AE2-071-SUMMSH69, EKPC_P1-2_CMPBEK-COBURG J69, EKPC_P1-2_COBURG J-SUMMSH 69, EKPC_P1-2_SUMMSH-WAYNE69,
EKPC_P1-2_WAYNE-ZULA 69, EKPC_P1-2_SEWJ - RUSS 69, EKPC_P1-2_WIND - SSET 69, EKPC_P1-2_SSET-KU ELI 69, EKPC_P1-2_COOP-DENNY 69, EKPC_P1-2_DAV LANE - LAUR69, EKPC_P1-2_LAUR-KU FAR69,
EKPC_P1-2_LAUR-KU SWTH69, EKPC_P1-2_WAYNE-DENNY69, EKPC_P1-2_DENNY-MCCRRY69, EKPC_P1-2_AEPMORG- MOR69, EKPC_P1-2_AEPMORG-INDX69, EKPC_P1-2_HODG-KU BARD69, EKPC_P1-2_HODG-KU ETWN69,
EKPC_P1-2_N SPR-KU LEB69, EKPC_P1-2_BAR-BON-FHOL69, EKPC_P1-2_FHOL-PARK69, EKPC_P1-2_CMPBEK-GREEN69, EKPC_P1-2_CMPBEK-KUTAY69, EKPC_P1-2_DK HEB-HEB 138, EKPC_P1-2_BOONE-BUFF138,
EKPC_P1-2_RUSSOL-RUS-WLF161, EKPC_P1-2_COOP-RUSSOL161, EKPC_P1-2_COOP-DEN161, EKPC_P1-2_COP-LIBJ-PU161, EKPC_P1-2_MCCR-WAYNE161, EKPC_P1-2_LAUR-PIT-TY161, EKPC_P1-2_GRE-TAY-AF1-083161,
EKPC_P1-2_AF1-083-MARION161, EKPC_P1-2_BARR-SUMSHSOL161, EKPC_P1-2_BULL-SUMSH161, TVA SS-GLASGOW & LAFAYETTE 161, EK-TVA SSHD & SSHD 161 XFMR, B-69-60, B-69-79,
B-69-80, B-138-447, B-69-330, B-69-332, B-69-450, BB-1408, BB-1403,
BB-1402, B-69-25, B-138-111, BB-1133, B-161-128, B-69-18, B-69-19,
B-69-26, B-345-100, B-138-116

## Load Shed
LOAD BUS |  |  | CONTINGENCY | LOAD SHED(MW)
|  |  | BASE CASE | -
|  |  | SING OPN LIN 1 339206-342769(1) | -
|  |  | SING OPN LIN 2 339206-939132(1) | -
|  |  | SING OPN LIN 3 341002-341443(1) | -
|  |  | SING OPN LIN 4 341002-341752(1) | -
|  |  | SING OPN LIN 5 341008-342106(1) | -
|  |  | SING OPN LIN 6 341008-342430(1) | -
341014 | 2ANNVILLE | 69 | SING OPN LIN 7 341014-341017(1) | 4.3545
|  |  | SING OPN LIN 8 341017-341428(1) | -
|  |  | SING OPN LIN 9 341017-342391(1) | -
|  |  | SING OPN LIN 10 341020-341782(1) | -
|  |  | SING OPN LIN 11 341020-342538(1) | -
341029 | 2ASAHI M W | 69 | SING OPN LIN 12 341029-341032(1) | 11.9039
|  |  | SING OPN LIN 13 341032-341379(1) | -
|  |  | SING OPN LIN 14 341032-342077(1) | -
|  |  | SING OPN LIN 15 341032-342472(1) | -
341035 | 2BACON CRK | 69 | SING OPN LIN 16 341035-341038(1) | 4.3674
|  |  | SING OPN LIN 17 341038-341755(1) | -
|  |  | SING OPN LIN 18 341038-342187(1) | -
341635 | 2HOLLOWAY | 69 | SING OPN LIN 19 341041-341635(1) | 10.8215
|  |  | SING OPN LIN 20 341041-341638(1) | -
|  |  | SING OPN LIN 21 341041-342547(1) | -
|  |  | SING OPN LIN 22 341044-341671(1) | -
|  |  | SING OPN LIN 23 341044-342361(1) | -
341047 | 2BALLTOWN | 69 | SING OPN LIN 24 341047-342424(1) | 11.9528
341050 | 2BANK LCK | 69 | SING OPN LIN 25 341050-342295(1) | 13.3486
341053 | 2BARD SHOP | 69 | SING OPN LIN 26 341053-341056(1) | 11.0844
|  |  | SING OPN LIN 27 341056-341407(1) | -
|  |  | SING OPN LIN 28 341056-342424(1) | -
|  |  | SING OPN LIN 29 341059-341275(1) | -
|  |  | SING OPN LIN 30 341059-341542(1) | -
|  |  | SING OPN LIN 31 341059-341651(1) | -
|  |  | SING OPN LIN 32 341059-342694(1) | -
341062 | 2BASS | 69 | SING OPN LIN 33 341062-341269(1) | 4.6051
341065 | 2BEAM | 69 | SING OPN LIN 34 341065-341068(1) | 8.1995
|  |  | SING OPN LIN 35 341068-341215(1) | -
|  |  | SING OPN LIN 36 341068-342253(1) | -
341074 | 2BEATTYV D | 69 | SING OPN LIN 37 341071-341074(1) | 7.6723
341992 | 2OAKDALE | 69 | SING OPN LIN 37 341071-341074(1) | 5.3401
|  |  | SING OPN LIN 38 341071-341077(1) | -
|  |  | SING OPN LIN 39 341071-342520(1) | -
341992 | 2OAKDALE | 69 | SING OPN LIN 40 341074-341992(1) | 5.3401
|  |  | SING OPN LIN 41 341077-341173(1) | -
|  |  | SING OPN LIN 42 341080-341149(1) | -
|  |  | SING OPN LIN 43 341080-342445(1) | -
|  |  | SING OPN LIN 44 341089-342500(1) | -
341092 | 2BELLVIEW | 69 | SING OPN LIN 45 341092-341095(1) | 5.1645
|  |  | SING OPN LIN 46 341095-341164(1) | -
|  |  | SING OPN LIN 47 341095-341227(1) | -
|  |  | SING OPN LIN 48 341098-342433(1) | -
341104 | 2BIG BONE | 69 | SING OPN LIN 49 341104-341107(1) | 3.3535
|  |  | SING OPN LIN 50 341107-341164(1) | -
|  |  | SING OPN LIN 51 341107-341917(1) | -
341110 | 2BIG CREEK | 69 | SING OPN LIN 52 341110-341113(1) | 4.7334
341439 | 2ELK MT IP | 69 | SING OPN LIN 52 341110-341113(1) | 4.7318
341439 | 2ELK MT IP | 69 | SING OPN LIN 53 341110-341439(1) | 4.7318
341110 | 2BIG CREEK | 69 | SING OPN LIN 54 341113-341464(1) | 4.7334
341439 | 2ELK MT IP | 69 | SING OPN LIN 54 341113-341464(1) | 4.7318
342001 | 2ONEIDA | 69 | SING OPN LIN 54 341113-341464(1) | 2.365
342001 | 2ONEIDA | 69 | SING OPN LIN 55 341113-342001(1) | 2.365
341114 | 2BIG HILL | 69 | SING OPN LIN 56 341114-341115(1) | 5.202
|  |  | SING OPN LIN 57 341115-342223(1) | -
|  |  | SING OPN LIN 58 341115-342346(1) | -
341116 | 2BIG WOODS | 69 | SING OPN LIN 59 341116-341119(1) | 5.4642
|  |  | SING OPN LIN 60 341119-341620(1) | -
|  |  | SING OPN LIN 61 341119-342088(1) | -
341125 | 2BILL WELLS | 69 | SING OPN LIN 62 341122-341125(1) | 7.6338
|  |  | SING OPN LIN 63 341122-341692(1) | -
|  |  | SING OPN LIN 64 341122-341860(1) | -
341134 | 2BLEVINS VAL | 69 | SING OPN LIN 65 341131-341134(1) | 2.7272
|  |  | SING OPN LIN 66 341131-341644(1) | -
|  |  | SING OPN LIN 67 341131-342112(1) | -
|  |  | SING OPN LIN 68 341137-341296(1) | -
|  |  | SING OPN LIN 69 341137-341935(1) | -
341140 | 2BLUE G PW | 69 | SING OPN LIN 70 341140-341143(1) | 11.2397
|  |  | SING OPN LIN 71 341143-342019(1) | -
|  |  | SING OPN LIN 72 341143-342508(1) | -
|  |  | SING OPN LIN 73 341149-341272(1) | -
341152 | 2BONANZA | 69 | SING OPN LIN 74 341152-341155(1) | 4.0496
|  |  | SING OPN LIN 75 341155-341803(1) | -
|  |  | SING OPN LIN 76 341155-341860(1) | -
|  |  | SING OPN LIN 77 341158-341161(1) | -
|  |  | SING OPN LIN 78 341158-341908(1) | -
|  |  | SING OPN LIN 79 341161-342403(1) | -
341167 | 2BOONE DIST | 69 | SING OPN LIN 80 341164-341167(1) | 12.5148
|  |  | SING OPN LIN 81 341164-342388(1) | -
342466 | 2W R SMOOT | 69 | SING OPN LIN 82 341164-342466(1) | 23.4435
|  |  | SING OPN LIN 83 341164-342559(1) | -
341170 | 2BOONEVIL | 69 | SING OPN LIN 84 341170-341173(1) | 4.449
|  |  | SING OPN LIN 85 341173-342196(1) | -
|  |  | SING OPN LIN 86 341179-341746(1) | -
|  |  | SING OPN LIN 87 341179-342514(1) | -
|  |  | SING OPN LIN 88 341185-341614(1) | -
|  |  | SING OPN LIN 89 341185-342100(1) | -
|  |  | SING OPN LIN 90 341188-341488(1) | -
|  |  | SING OPN LIN 91 341188-341587(1) | -
|  |  | SING OPN LIN 92 341194-342385(1) | -
|  |  | SING OPN LIN 93 341194-342388(1) | -
|  |  | SING OPN LIN 94 341197-341818(1) | -
|  |  | SING OPN LIN 95 341197-342349(1) | -
|  |  | SING OPN LIN 96 341200-341920(1) | -
|  |  | SING OPN LIN 97 341200-342010(1) | -
341203 | 2BRONSTON | 69 | SING OPN LIN 98 341203-341206(1) | 13.1724
|  |  | SING OPN LIN 99 341206-341347(1) | -
|  |  | SING OPN LIN 100 341206-341392(1) | -
341210 | 2BROUGHT TWN | 69 | SING OPN LIN 101 341209-341210(1) | 4.4578
|  |  | SING OPN LIN 102 341209-341617(1) | -
|  |  | SING OPN LIN 103 341209-342367(1) | -
|  |  | SING OPN LIN 104 341212-341774(1) | -
|  |  | SING OPN LIN 105 341212-342500(1) | -
341281 | 2CEDAR GR | 69 | SING OPN LIN 106 341215-341281(1) | 8.5817
342082 | 2PLEAS GRV | 69 | SING OPN LIN 106 341215-341281(1) | 26.1472
|  |  | SING OPN LIN 107 341215-341389(1) | -
|  |  | SING OPN LIN 108 341215-342700(1) | -
|  |  | SING OPN LIN 109 341218-341227(1) | -
|  |  | SING OPN LIN 110 341218-341605(1) | -
341224 | 2BURLINGTN | 69 | SING OPN LIN 111 341224-341227(1) | 8.1595
|  |  | SING OPN LIN 112 341233-341974(1) | -
|  |  | SING OPN LIN 113 341233-342286(1) | -
|  |  | SING OPN LIN 114 341248-341608(1) | -
|  |  | SING OPN LIN 115 341248-342520(1) | -
341251 | 2CANE RIDG | 69 | SING OPN LIN 116 341251-341254(1) | 0.37481
|  |  | SING OPN LIN 117 341254-341872(1) | -
|  |  | SING OPN LIN 118 341254-342259(1) | -
341260 | 2CARSON | 69 | SING OPN LIN 119 341260-342013(1) | 5.8918
341263 | 2CARTER CTY | 69 | SING OPN LIN 120 341263-341266(1) | 3.7198
|  |  | SING OPN LIN 121 341266-342034(1) | -
|  |  | SING OPN LIN 122 341266-342475(1) | -
|  |  | SING OPN LIN 123 341269-342064(1) | -
|  |  | SING OPN LIN 124 341269-342703(1) | -
|  |  | SING OPN LIN 125 341272-341275(1) | -
342238 | 2SEYMOUR | 69 | SING OPN LIN 126 341275-342241(1) | 3.7942
342082 | 2PLEAS GRV | 69 | SING OPN LIN 127 341281-342082(1) | 26.1472
|  |  | SING OPN LIN 128 341287-341713(1) | -
|  |  | SING OPN LIN 129 341287-342307(1) | -
|  |  | SING OPN LIN 130 341287-342568(1) | -
341293 | 2CHAPLIN | 69 | SING OPN LIN 131 341293-341296(1) | 1.4053
|  |  | SING OPN LIN 132 341296-342262(1) | -
|  |  | SING OPN LIN 133 341299-341989(1) | -
|  |  | SING OPN LIN 134 341299-342124(1) | -
341302 | 2CLAY CITY | 69 | SING OPN LIN 135 341302-341305(1) | 8.5542
|  |  | SING OPN LIN 136 341305-341593(1) | -
|  |  | SING OPN LIN 137 341305-341599(1) | -
341308 | 2CLAY LCK | 69 | SING OPN LIN 138 341308-341314(1) | 6.1845
341308 | 2CLAY LCK | 69 | SING OPN LIN 139 341311-341314(1) | 6.1845
|  |  | SING OPN LIN 140 341311-342184(1) | -
|  |  | SING OPN LIN 141 341311-342406(1) | -
|  |  | SING OPN LIN 142 341317-341390(1) | -
|  |  | SING OPN LIN 143 341320-341512(1) | -
|  |  | SING OPN LIN 144 341323-341335(1) | -
|  |  | SING OPN LIN 145 341323-341512(1) | -
|  |  | SING OPN LIN 146 341323-342235(1) | -
|  |  | SING OPN LIN 147 341326-341488(1) | -
|  |  | SING OPN LIN 148 341326-342133(1) | -
341329 | 2COLESBURG | 69 | SING OPN LIN 149 341329-341332(1) | 2.9494
|  |  | SING OPN LIN 150 341332-341944(1) | -
|  |  | SING OPN LIN 151 341332-342155(1) | -
341366 | 2COLUMB KU | 69 | SING OPN LIN 152 341335-341370(1) | 6.29
341370 | 2COLUMB S KU | 69 | SING OPN LIN 152 341335-341370(1) | 4.41
|  |  | SING OPN LIN 153 341335-342436(1) | -
341338 | 2CONWAY | 69 | SING OPN LIN 154 341338-341341(1) | 4.2596
|  |  | SING OPN LIN 155 341341-342346(1) | -
|  |  | SING OPN LIN 156 341341-342349(1) | -
341343 | 2CONTOWN | 69 | SING OPN LIN 157 341342-341343(1) | 2.2548
|  |  | SING OPN LIN 158 341342-341761(1) | -
|  |  | SING OPN LIN 159 341342-342067(1) | -
|  |  | SING OPN LIN 160 341344-341347(1) | -
|  |  | SING OPN LIN 161 341344-342286(1) | -
|  |  | SING OPN LIN 162 341344-342286(2) | -
|  |  | SING OPN LIN 163 341344-342715(1) | -
341350 | 2CRESTON | 69 | SING OPN LIN 164 341350-342067(1) | 5.7798
341353 | 2CROCKETT | 69 | SING OPN LIN 165 341353-341356(1) | 3.3314
|  |  | SING OPN LIN 166 341356-341653(1) | -
|  |  | SING OPN LIN 167 341356-342265(1) | -
341359 | 2CROOKSVIL | 69 | SING OPN LIN 168 341359-341362(1) | 5.895
342288 | 2SPEEDWELL | 69 | SING OPN LIN 168 341359-341362(1) | 1.3
342288 | 2SPEEDWELL | 69 | SING OPN LIN 169 341359-342288(1) | 1.3
|  |  | SING OPN LIN 170 341362-341406(1) | -
|  |  | SING OPN LIN 171 341362-341611(1) | -
341366 | 2COLUMB KU | 69 | SING OPN LIN 172 341366-341370(1) | 6.29
|  |  | SING OPN LIN 174 341377-936380(1) | -
|  |  | SING OPN LIN 175 341379-342256(1) | -
|  |  | SING OPN LIN 176 341380-341959(1) | -
|  |  | SING OPN LIN 177 341380-341962(1) | -
|  |  | SING OPN LIN 178 341380-342574(1) | -
341737 | 2LAUR CO IP | 69 | SING OPN LIN 179 341381-341382(1) | 9.26
|  |  | SING OPN LIN 180 341381-341930(1) | -
|  |  | SING OPN LIN 181 341381-342452(1) | -
341737 | 2LAUR CO IP | 69 | SING OPN LIN 182 341382-341734(1) | 9.26
|  |  | SING OPN LIN 183 341383-341467(1) | -
|  |  | SING OPN LIN 184 341383-341965(1) | -
341386 | 2DEATSVIL | 69 | SING OPN LIN 185 341386-341389(1) | 7.9864
|  |  | SING OPN LIN 186 341389-341707(1) | -
341391 | 2DEFOE | 69 | SING OPN LIN 187 341390-341391(1) | 4.021
|  |  | SING OPN LIN 188 341390-341950(1) | -
|  |  | SING OPN LIN 189 341392-341578(1) | -
|  |  | SING OPN LIN 190 341392-342499(1) | -
|  |  | SING OPN LIN 191 341392-342727(1) | -
341479 | 2S BOUND RD | 69 | SING OPN LIN 192 341394-341479(1) | 6.5271
342151 | 2RINEYVILLE | 69 | SING OPN LIN 193 341394-342151(1) | 5.6071
|  |  | SING OPN LIN 194 341394-342157(1) | -
|  |  | SING OPN LIN 195 341394-342274(1) | -
341398 | 2DOWNING | 69 | SING OPN LIN 196 341398-341605(1) | 11.3406
341880 | 2MINEOLA PKE | 69 | SING OPN LIN 196 341398-341605(1) | 12.222
341880 | 2MINEOLA PKE | 69 | SING OPN LIN 197 341398-341880(1) | 12.222
341400 | 2DRAVO | 69 | SING OPN LIN 198 341400-342091(1) | 2.641
341401 | 2DURO | 69 | SING OPN LIN 199 341401-341842(1) | 8.9714
341401 | 2DURO | 69 | SING OPN LIN 200 341404-341842(1) | 8.9714
341839 | 2MBUSA | 69 | SING OPN LIN 200 341404-341842(1) | 14.5365
|  |  | SING OPN LIN 201 341404-342295(1) | -
|  |  | SING OPN LIN 202 341404-342388(1) | -
341405 | 2DUNCANNO LN | 69 | SING OPN LIN 203 341405-341406(1) | 3.7451
|  |  | SING OPN LIN 204 341407-342019(1) | -
341410 | 2E BERNSTADT | 69 | SING OPN LIN 205 341410-341929(1) | 6.944
341416 | 2E PINE KNOT | 69 | SING OPN LIN 206 341416-342076(1) | 4.2639
341422 | 2E SOMERSET | 69 | SING OPN LIN 207 341419-341422(1) | 8.3699
|  |  | SING OPN LIN 208 341419-341941(1) | -
|  |  | SING OPN LIN 209 341419-341974(1) | -
341425 | 2EBERLE | 69 | SING OPN LIN 210 341425-341428(1) | 4.738
|  |  | SING OPN LIN 211 341428-341809(1) | -
341437 | 2EDMON IND P | 69 | SING OPN LIN 212 341431-341434(1) | 1.5349
341680 | 2JB GALLOWAY | 69 | SING OPN LIN 212 341431-341434(1) | 7.4175
|  |  | SING OPN LIN 213 341431-341728(1) | -
|  |  | SING OPN LIN 214 341431-342322(1) | -
341437 | 2EDMON IND P | 69 | SING OPN LIN 215 341434-341437(1) | 1.5349
341680 | 2JB GALLOWAY | 69 | SING OPN LIN 216 341434-341680(1) | 7.4175
341446 | 2ELLIOT CO P | 69 | SING OPN LIN 217 341443-341446(1) | 10.6457
|  |  | SING OPN LIN 218 341443-341953(1) | -
341449 | 2ELLIOTTVILL | 69 | SING OPN LIN 219 341449-342163(1) | 6.2363
|  |  | SING OPN LIN 220 341455-341458(1) | -
|  |  | SING OPN LIN 221 341455-342274(1) | -
|  |  | SING OPN LIN 222 341455-342379(1) | -
|  |  | SING OPN LIN 223 341458-342340(1) | -
|  |  | SING OPN LIN 224 341461-341797(1) | -
|  |  | SING OPN LIN 225 341461-342310(1) | -
341572 | 2GREENBRIAR | 69 | SING OPN LIN 226 341464-341569(1) | 7.3931
|  |  | SING OPN LIN 227 341464-342391(1) | -
|  |  | SING OPN LIN 228 341464-342730(1) | -
|  |  | SING OPN LIN 229 341467-342580(1) | -
|  |  | SING OPN LIN 230 341470-341473(1) | -
|  |  | SING OPN LIN 231 341470-342511(1) | -
|  |  | SING OPN LIN 232 341473-342115(1) | -
342193 | 2S FLOYD | 69 | SING OPN LIN 233 341473-342193(1) | 7.0517
341899 | 2MT STERLING | 69 | SING OPN LIN 234 341476-341899(1) | 4.504
341899 | 2MT STERLING | 69 | SING OPN LIN 235 341476-342130(1) | 4.504
341485 | 2FOUR OAKS | 69 | SING OPN LIN 236 341485-341488(1) | 6.5608
341550 | 2FALMOUTH KU | 69 | SING OPN LIN 236 341485-341488(1) | 4.56
341550 | 2FALMOUTH KU | 69 | SING OPN LIN 237 341485-341550(1) | 4.56
|  |  | SING OPN LIN 238 341491-341548(1) | -
342037 | 2PARKWAY 1 | 69 | SING OPN LIN 239 341491-342037(1) | 9.3281
342040 | 2PARKWAY 2 | 69 | SING OPN LIN 239 341491-342037(1) | 3.3429
|  |  | SING OPN LIN 240 341491-342043(1) | -
|  |  | SING OPN LIN 241 341491-342049(1) | -
|  |  | SING OPN LIN 242 341491-342732(1) | -
341497 | 2FREDRIKBRG | 69 | SING OPN LIN 243 341494-341497(1) | 4.135
|  |  | SING OPN LIN 244 341494-341935(1) | -
|  |  | SING OPN LIN 245 341494-342508(1) | -
|  |  | SING OPN LIN 246 341500-341644(1) | -
|  |  | SING OPN LIN 247 341500-341824(1) | -
341506 | 2GAP OF RIDG | 69 | SING OPN LIN 248 341503-341506(1) | 9.8439
|  |  | SING OPN LIN 249 341503-341578(1) | -
|  |  | SING OPN LIN 250 341503-341887(1) | -
341509 | 2GARLIN | 69 | SING OPN LIN 251 341509-341512(1) | 5.8713
|  |  | SING OPN LIN 252 341515-341732(1) | -
|  |  | SING OPN LIN 253 341515-942410(1) | -
|  |  | SING OPN LIN 254 341518-341521(1) | -
|  |  | SING OPN LIN 255 341521-341806(1) | -
|  |  | SING OPN LIN 256 341530-342043(1) | -
|  |  | SING OPN LIN 257 341530-342445(1) | -
|  |  | SING OPN LIN 258 341533-341632(1) | -
|  |  | SING OPN LIN 259 341533-342307(1) | -
|  |  | SING OPN LIN 260 341536-341623(1) | -
|  |  | SING OPN LIN 261 341536-341989(1) | -
|  |  | SING OPN LIN 262 341536-342088(1) | -
|  |  | SING OPN LIN 263 341536-342589(1) | -
|  |  | SING OPN LIN 264 341539-341686(1) | -
|  |  | SING OPN LIN 265 341542-341548(1) | -
|  |  | SING OPN LIN 266 341551-341587(1) | -
|  |  | SING OPN LIN 267 341551-342298(1) | -
|  |  | SING OPN LIN 268 341554-341752(1) | -
|  |  | SING OPN LIN 269 341554-342034(1) | -
|  |  | SING OPN LIN 270 341563-341575(1) | -
|  |  | SING OPN LIN 271 341563-342325(1) | -
|  |  | SING OPN LIN 272 341563-342733(1) | -
341572 | 2GREENBRIAR | 69 | SING OPN LIN 273 341569-341572(1) | 7.3931
|  |  | SING OPN LIN 274 341569-341806(1) | -
|  |  | SING OPN LIN 275 341575-341854(1) | -
341581 | 2GREGORY RD | 69 | SING OPN LIN 276 341578-341581(1) | 1.8519
341584 | 2GRIFFIN | 69 | SING OPN LIN 277 341584-341587(1) | 7.6275
341590 | 2HARDWCRK | 69 | SING OPN LIN 278 341590-341593(1) | 1.8746
|  |  | SING OPN LIN 279 341593-342301(1) | -
341596 | 2HARGETT | 69 | SING OPN LIN 280 341596-341599(1) | 3.9751
|  |  | SING OPN LIN 281 341599-342370(1) | -
|  |  | SING OPN LIN 283 341602-342280(1) | -
|  |  | SING OPN LIN 284 341602-936380(1) | -
|  |  | SING OPN LIN 285 341605-342595(1) | -
|  |  | SING OPN LIN 286 341608-342313(1) | -
|  |  | SING OPN LIN 287 341611-342103(1) | -
|  |  | SING OPN LIN 288 341614-342520(1) | -
|  |  | SING OPN LIN 289 341617-341896(1) | -
|  |  | SING OPN LIN 290 341620-342163(1) | -
|  |  | SING OPN LIN 291 341623-342052(1) | -
|  |  | SING OPN LIN 292 341632-341800(1) | -
|  |  | SING OPN LIN 293 341632-342316(1) | -
|  |  | SING OPN LIN 294 341638-342199(1) | -
342460 | 2W NICHVIL | 69 | SING OPN LIN 295 341638-342463(1) | 23.1559
341641 | 2HOMESTEAD S | 69 | SING OPN LIN 296 341641-341887(1) | 14.1787
|  |  | SING OPN LIN 297 341644-341683(1) | -
341647 | 2HORSE CV KU | 69 | SING OPN LIN 298 341647-341650(1) | 46.06
341647 | 2HORSE CV KU | 69 | SING OPN LIN 299 341650-341651(Z1) | 46.06
|  |  | SING OPN LIN 300 341651-341914(1) | -
341656 | 2HOT MIX RD | 69 | SING OPN LIN 301 341653-341656(1) | 5.3326
|  |  | SING OPN LIN 302 341653-341890(1) | -
341659 | 2HT ADAMS | 69 | SING OPN LIN 303 341659-341662(1) | 6.0761
|  |  | SING OPN LIN 304 341662-341671(1) | -
|  |  | SING OPN LIN 305 341662-341857(1) | -
|  |  | SING OPN LIN 306 341665-341701(1) | -
|  |  | SING OPN LIN 308 341665-342596(1) | -
|  |  | SING OPN LIN 309 341671-342061(1) | -
341677 | 2INDEX | 69 | SING OPN LIN 310 341677-341890(1) | 6.9677
|  |  | SING OPN LIN 311 341683-342100(1) | -
341689 | 2JELLICO CRK | 69 | SING OPN LIN 312 341686-341689(1) | 1.9129
|  |  | SING OPN LIN 313 341686-342076(1) | -
341695 | 2JENNY WILEY | 69 | SING OPN LIN 314 341692-341695(1) | 5.4657
|  |  | SING OPN LIN 315 341692-342343(1) | -
|  |  | SING OPN LIN 316 341701-342370(1) | -
341704 | 2JOE TICH | 69 | SING OPN LIN 317 341704-341707(1) | 7.9884
|  |  | SING OPN LIN 318 341707-342427(1) | -
341716 | 2KEAVY | 69 | SING OPN LIN 319 341716-341722(1) | 10.7978
|  |  | SING OPN LIN 320 341719-341740(1) | -
|  |  | SING OPN LIN 321 341719-342073(1) | -
|  |  | SING OPN LIN 322 341722-341740(1) | -
|  |  | SING OPN LIN 323 341722-342187(1) | -
|  |  | SING OPN LIN 324 341725-342007(1) | -
|  |  | SING OPN LIN 325 341725-342058(1) | -
|  |  | SING OPN LIN 326 341728-341854(1) | -
341731 | 2LANCASTER | 69 | SING OPN LIN 327 341731-341732(1) | 5.5024
|  |  | SING OPN LIN 328 341732-341959(1) | -
341737 | 2LAUR CO IP | 69 | SING OPN LIN 329 341734-341737(1) | 9.26
|  |  | SING OPN LIN 330 341740-342754(1) | -
|  |  | SING OPN LIN 331 341746-342253(1) | -
|  |  | SING OPN LIN 332 341749-342058(1) | -
|  |  | SING OPN LIN 333 341749-342133(1) | -
341758 | 2LIBERT CHUR | 69 | SING OPN LIN 334 341755-341758(1) | 4.8231
|  |  | SING OPN LIN 335 341761-341767(1) | -
|  |  | SING OPN LIN 336 341761-341896(1) | -
|  |  | SING OPN LIN 337 341761-342760(1) | -
341764 | 2LIBERTY KU | 69 | SING OPN LIN 338 341764-341767(1) | 7.68
|  |  | SING OPN LIN 339 341767-342064(1) | -
341772 | 2LOGAN | 69 | SING OPN LIN 340 341772-341774(1) | 13.452
|  |  | SING OPN LIN 341 341774-341775(1) | -
|  |  | SING OPN LIN 342 341775-342247(1) | -
|  |  | SING OPN LIN 343 341776-342208(1) | -
|  |  | SING OPN LIN 344 341776-342316(1) | -
341779 | 2LOW GAP | 69 | SING OPN LIN 345 341779-341782(1) | 4.1103
|  |  | SING OPN LIN 346 341782-342475(1) | -
341785 | 2LYMAN BW | 69 | SING OPN LIN 347 341785-341788(1) | 7.0814
|  |  | SING OPN LIN 348 341788-342155(1) | -
|  |  | SING OPN LIN 349 341788-342379(1) | -
341791 | 2MACKVIL KU | 69 | SING OPN LIN 350 341791-341794(1) | 0.45
|  |  | SING OPN LIN 351 341794-341935(1) | -
|  |  | SING OPN LIN 352 341794-342061(1) | -
|  |  | SING OPN LIN 353 341797-342265(1) | -
|  |  | SING OPN LIN 354 341800-342325(1) | -
|  |  | SING OPN LIN 355 341803-342310(1) | -
|  |  | SING OPN LIN 356 341803-342313(1) | -
341812 | 2MAPLESVILLE | 69 | SING OPN LIN 357 341809-341812(1) | 5.784
|  |  | SING OPN LIN 358 341809-341929(1) | -
341815 | 2MARETBURG | 69 | SING OPN LIN 359 341815-341818(1) | 6.4511
|  |  | SING OPN LIN 360 341818-342472(1) | -
341821 | 2MARIBA | 69 | SING OPN LIN 361 341821-341824(1) | 4.525
|  |  | SING OPN LIN 362 341824-341833(1) | -
341827 | 2MARTIN CO | 69 | SING OPN LIN 363 341827-342343(1) | 4.7105
341830 | 2MAYTOWN | 69 | SING OPN LIN 364 341830-341833(1) | 3.9033
|  |  | SING OPN LIN 365 341833-341890(1) | -
|  |  | SING OPN LIN 366 341836-341953(1) | -
|  |  | SING OPN LIN 367 341836-342265(1) | -
341839 | 2MBUSA | 69 | SING OPN LIN 368 341839-341842(1) | 14.5365
|  |  | SING OPN LIN 369 341845-342139(1) | -
|  |  | SING OPN LIN 370 341845-342490(1) | -
|  |  | SING OPN LIN 371 341845-342778(1) | -
|  |  | SING OPN LIN 372 341848-342223(1) | -
|  |  | SING OPN LIN 373 341848-342391(1) | -
341851 | 2MCKINNEY | 69 | SING OPN LIN 374 341851-341854(1) | 4.4445
|  |  | SING OPN LIN 375 341857-342406(1) | -
341863 | 2MIDDLE CRK | 69 | SING OPN LIN 376 341860-341863(1) | 5.746
341875 | 2MILLER HUNT | 69 | SING OPN LIN 377 341869-341875(1) | 2.2498
341878 | 2MILLERSB EK | 69 | SING OPN LIN 379 341872-341878(1) | 3.855
|  |  | SING OPN LIN 380 341887-342268(1) | -
341893 | 2MT OLIVE | 69 | SING OPN LIN 381 341893-341896(1) | 4.6349
|  |  | SING OPN LIN 382 341908-341914(1) | -
341911 | 2MUNFVIL KU | 69 | SING OPN LIN 383 341911-341914(1) | 6.11
|  |  | SING OPN LIN 384 341917-341998(1) | -
|  |  | SING OPN LIN 385 341920-341998(1) | -
342502 | 2WILLIAMSTWN | 69 | SING OPN LIN 386 341920-342502(1) | 12.2435
|  |  | SING OPN LIN 387 341923-342091(1) | -
|  |  | SING OPN LIN 388 341923-342280(1) | -
342181 | 2S ALBANY | 69 | SING OPN LIN 389 341926-342181(1) | 7.995
|  |  | SING OPN LIN 390 341926-342283(1) | -
|  |  | SING OPN LIN 391 341926-342397(1) | -
|  |  | SING OPN LIN 392 341929-341930(1) | -
|  |  | SING OPN LIN 393 341935-342208(1) | -
|  |  | SING OPN LIN 394 341938-342505(1) | -
|  |  | SING OPN LIN 395 341938-342526(1) | -
341947 | 2NELSON VAL | 69 | SING OPN LIN 396 341941-341947(1) | 5.5639
|  |  | SING OPN LIN 397 341941-341971(1) | -
|  |  | SING OPN LIN 398 341944-342424(1) | -
|  |  | SING OPN LIN 399 341944-342514(1) | -
|  |  | SING OPN LIN 400 341950-342007(1) | -
342229 | 2SANDY HOOK | 69 | SING OPN LIN 401 341953-342229(1) | 3.5476
|  |  | SING OPN LIN 402 341962-342361(1) | -
|  |  | SING OPN LIN 403 341965-342199(1) | -
|  |  | SING OPN LIN 404 341971-342115(1) | -
|  |  | SING OPN LIN 405 341974-342256(1) | -
341977 | 2OAK HILL | 69 | SING OPN LIN 406 341977-341983(1) | 6.5887
|  |  | SING OPN LIN 407 341980-341983(1) | -
|  |  | SING OPN LIN 408 341980-342286(1) | -
|  |  | SING OPN LIN 409 341983-342469(1) | -
341986 | 2OAK RIDGE | 69 | SING OPN LIN 410 341986-341989(1) | 4.6709
|  |  | SING OPN LIN 411 342007-342008(1) | -
|  |  | SING OPN LIN 412 342007-342010(1) | -
341260 | 2CARSON | 69 | SING OPN LIN 413 342007-342013(1) | 5.8918
342016 | 2OWENS IL | 69 | SING OPN LIN 414 342016-342019(1) | 7.503
342025 | 2OWINGVIL KU | 69 | SING OPN LIN 415 342022-342025(1) | 9.53
|  |  | SING OPN LIN 416 342022-342052(1) | -
|  |  | SING OPN LIN 417 342022-342112(1) | -
342031 | 2PACTOLUS | 69 | SING OPN LIN 418 342031-342034(1) | 8.8816
342040 | 2PARKWAY 2 | 69 | SING OPN LIN 419 342037-342040(1) | 3.3429
|  |  | SING OPN LIN 420 342049-342161(1) | -
|  |  | SING OPN LIN 421 342049-940830(1) | -
|  |  | SING OPN LIN 422 342067-342505(1) | -
342070 | 2PINE GROVE | 69 | SING OPN LIN 423 342070-342073(1) | 9.8481
|  |  | SING OPN LIN 424 342073-342451(1) | -
|  |  | SING OPN LIN 425 342076-342139(1) | -
|  |  | SING OPN LIN 426 342077-342782(1) | -
342085 | 2PLUMMR L | 69 | SING OPN LIN 427 342085-342088(1) | 4.0531
|  |  | SING OPN LIN 428 342091-342124(1) | -
|  |  | SING OPN LIN 429 342091-342634(1) | -
342097 | 2POWEL TAYL | 69 | SING OPN LIN 430 342097-342184(1) | 5.6222
|  |  | SING OPN LIN 431 342100-342301(1) | -
|  |  | SING OPN LIN 432 342100-342637(1) | -
|  |  | SING OPN LIN 433 342103-342106(1) | -
342109 | 2PRESTON | 69 | SING OPN LIN 434 342109-342112(1) | 1.5083
|  |  | SING OPN LIN 435 342115-342787(1) | -
342118 | 2RADCLIFF | 69 | SING OPN LIN 436 342118-342121(1) | 7.6513
342328 | 2T BROWN LOG | 69 | SING OPN LIN 437 342121-342328(1) | 7.5424
342118 | 2RADCLIFF | 69 | SING OPN LIN 438 342121-342415(1) | 7.6513
342328 | 2T BROWN LOG | 69 | SING OPN LIN 438 342121-342415(1) | 7.5424
|  |  | SING OPN LIN 439 342127-342265(1) | -
|  |  | SING OPN LIN 440 342127-342421(1) | -
341899 | 2MT STERLING | 69 | SING OPN LIN 441 342130-342259(1) | 4.504
342130 | 2REID VILLAG | 69 | SING OPN LIN 441 342130-342259(1) | 3.2944
|  |  | SING OPN LIN 443 342133-342640(1) | -
342136 | 2REVELO KU | 69 | SING OPN LIN 444 342136-342139(1) | 1.8
342145 | 2RICHARDSON | 69 | SING OPN LIN 445 342145-342487(1) | 13.5187
342154 | 2ROANOKE | 69 | SING OPN LIN 446 342154-342155(1) | 3.4896
342118 | 2RADCLIFF | 69 | SING OPN LIN 447 342157-342418(1) | 7.6513
342328 | 2T BROWN LOG | 69 | SING OPN LIN 447 342157-342418(1) | 7.5424
342418 | 2VINE GROVE | 69 | SING OPN LIN 447 342157-342418(1) | 8.2029
342160 | 2ROSEVILLE | 69 | SING OPN LIN 448 342160-342161(1) | 7.0525
|  |  | SING OPN LIN 449 342161-342334(1) | -
|  |  | SING OPN LIN 450 342163-342649(1) | -
|  |  | SING OPN LIN 451 342166-342169(1) | -
342172 | 2RUSS SPR EK | 69 | SING OPN LIN 452 342166-342172(1) | 11.0494
|  |  | SING OPN LIN 453 342166-342235(1) | -
342175 | 2RUSS SPR KU | 69 | SING OPN LIN 454 342169-342175(1) | 6.4
|  |  | SING OPN LIN 455 342169-342178(1) | -
|  |  | SING OPN LIN 456 342178-342232(1) | -
|  |  | SING OPN LIN 457 342178-342793(1) | -
|  |  | SING OPN LIN 458 342184-342262(1) | -
|  |  | SING OPN LIN 459 342186-342424(1) | -
|  |  | SING OPN LIN 460 342186-342427(1) | -
|  |  | SING OPN LIN 461 342196-342391(1) | -
342202 | 2S JESSAMINE | 69 | SING OPN LIN 462 342199-342202(1) | 14.9115
342211 | 2S SPRINGFLD | 69 | SING OPN LIN 463 342208-342211(1) | 4.6495
342214 | 2SALEM EK | 69 | SING OPN LIN 464 342214-342217(1) | 10.2212
|  |  | SING OPN LIN 465 342217-342481(1) | -
|  |  | SING OPN LIN 466 342217-342505(1) | -
342220 | 2SAND GAP | 69 | SING OPN LIN 467 342220-342223(1) | 2.7435
|  |  | SING OPN LIN 468 342222-342703(1) | -
|  |  | SING OPN LIN 469 342222-342760(1) | -
|  |  | SING OPN LIN 470 342235-943700(1) | -
342238 | 2SEYMOUR | 69 | SING OPN LIN 471 342238-342241(1) | 3.7942
|  |  | SING OPN LIN 472 342247-342248(1) | -
342410 | 2VEECHDALE | 69 | SING OPN LIN 473 342247-342410(1) | 5.1171
|  |  | SING OPN LIN 474 342247-342808(1) | -
342250 | 2SHEPHEVIL | 69 | SING OPN LIN 475 342250-342253(1) | 20.8315
|  |  | SING OPN LIN 476 342265-342658(1) | -
|  |  | SING OPN LIN 477 342268-342478(1) | -
342271 | 2SMITHRSVIL | 69 | SING OPN LIN 478 342271-342274(1) | 13.9816
342277 | 2SNOW | 69 | SING OPN LIN 479 342277-342283(1) | 9.8435
|  |  | SING OPN LIN 480 342283-342322(1) | -
|  |  | SING OPN LIN 481 342286-342287(1) | -
|  |  | SING OPN LIN 482 342292-342295(1) | -
|  |  | SING OPN LIN 483 342292-342298(1) | -
|  |  | SING OPN LIN 484 342292-342667(1) | -
|  |  | SING OPN LIN 485 342307-342403(1) | -
342412 | 2VERTREES | 69 | SING OPN LIN 486 342307-342412(1) | 5.8907
|  |  | SING OPN LIN 487 342319-342322(1) | -
|  |  | SING OPN LIN 488 342319-342334(1) | -
|  |  | SING OPN LIN 489 342319-940830(1) | -
|  |  | SING OPN LIN 490 342322-342436(1) | -
|  |  | SING OPN LIN 491 342322-342814(1) | -
342337 | 2THARP | 69 | SING OPN LIN 492 342337-342340(1) | 10.0175
|  |  | SING OPN LIN 493 342343-342421(1) | -
|  |  | SING OPN LIN 494 342349-342433(1) | -
342352 | 2THREE M | 69 | SING OPN LIN 495 342352-342355(1) | 19.4904
342358 | 2TODDVILLE | 69 | SING OPN LIN 496 342358-342361(1) | 4.2681
|  |  | SING OPN LIN 497 342364-342367(1) | -
|  |  | SING OPN LIN 498 342364-342821(1) | -
|  |  | SING OPN LIN 499 342364-342821(2) | -
|  |  | SING OPN LIN 500 342367-942410(1) | -
342382 | 2TUNNEL HILL | 69 | SING OPN LIN 501 342379-342382(1) | 16.3905
|  |  | SING OPN LIN 502 342385-342487(1) | -
|  |  | SING OPN LIN 503 342391-342820(1) | -
342394 | 2UPCHURCH | 69 | SING OPN LIN 504 342394-342397(1) | 8.1682
|  |  | SING OPN LIN 505 342397-342532(1) | -
342400 | 2UPTON | 69 | SING OPN LIN 506 342400-342403(1) | 3.4103
342118 | 2RADCLIFF | 69 | SING OPN LIN 507 342415-342418(1) | 7.6513
342328 | 2T BROWN LOG | 69 | SING OPN LIN 507 342415-342418(1) | 7.5424
|  |  | SING OPN LIN 508 342430-342433(1) | -
|  |  | SING OPN LIN 509 342430-342691(1) | -
342439 | 2W COLUMBIA | 69 | SING OPN LIN 510 342436-342439(1) | 5.8725
342442 | 2W GLASGOW | 69 | SING OPN LIN 511 342442-342445(1) | 12.7509
|  |  | SING OPN LIN 512 342451-342452(1) | -
342460 | 2W NICHVIL | 69 | SING OPN LIN 513 342460-342463(1) | 23.1559
|  |  | SING OPN LIN 514 342469-342526(1) | -
|  |  | SING OPN LIN 515 342472-342511(1) | -
|  |  | SING OPN LIN 516 342478-342532(1) | -
342529 | 2ZULA | 69 | SING OPN LIN 517 342478-342535(1) | 8.451
|  |  | SING OPN LIN 518 342478-342823(1) | -
342484 | 2WEBB CR RDS | 69 | SING OPN LIN 519 342481-342484(1) | 5.4721
|  |  | SING OPN LIN 520 342481-943700(1) | -
342493 | 2WHITLY C KU | 69 | SING OPN LIN 521 342490-342493(1) | 3.81
|  |  | SING OPN LIN 522 342490-342499(1) | -
342496 | 2WIBORG | 69 | SING OPN LIN 523 342496-342499(1) | 8.0737
342523 | 2ZOLLICOF | 69 | SING OPN LIN 524 342523-342526(1) | 3.8925
342529 | 2ZULA | 69 | SING OPN LIN 525 342529-342535(1) | 8.451
|  |  | SING OPN LIN 526 342538-342616(1) | -
|  |  | SING OPN LIN 527 342541-342544(1) | -
|  |  | SING OPN LIN 528 342541-342556(1) | -
|  |  | SING OPN LIN 529 342541-342580(1) | -
|  |  | SING OPN LIN 530 342541-342631(1) | -
|  |  | SING OPN LIN 531 342541-342829(1) | -
|  |  | SING OPN LIN 532 342550-342559(1) | -
|  |  | SING OPN LIN 533 342550-342640(1) | -
342553 | 4BECKNERV | 138 | SING OPN LIN 534 342553-342556(1) | 1.593
|  |  | SING OPN LIN 535 342556-342565(1) | -
|  |  | SING OPN LIN 536 342559-342646(1) | -
|  |  | SING OPN LIN 537 342559-342673(1) | -
|  |  | SING OPN LIN 538 342565-342574(1) | -
|  |  | SING OPN LIN 539 342571-342589(1) | -
|  |  | SING OPN LIN 540 342571-342649(1) | -
|  |  | SING OPN LIN 541 342574-342596(1) | -
|  |  | SING OPN LIN 542 342574-342676(1) | -
|  |  | SING OPN LIN 543 342577-342607(1) | -
|  |  | SING OPN LIN 544 342577-342676(1) | -
|  |  | SING OPN LIN 545 342577-342691(1) | -
|  |  | SING OPN LIN 546 342583-342589(1) | -
|  |  | SING OPN LIN 547 342583-342664(1) | -
342587 | 1GALLATIN CO | 34.5 | SING OPN LIN 548 342586-342587(1) | 23.73
|  |  | SING OPN LIN 549 342586-342673(1) | -
|  |  | SING OPN LIN 550 342589-342634(1) | -
|  |  | SING OPN LIN 551 342596-342607(1) | -
342598 | 4INLAND C T | 138 | SING OPN LIN 552 342598-342664(1) | 31.2332
342601 | 4JACKSNVIL | 138 | SING OPN LIN 553 342601-342604(1) | 3.3691
|  |  | SING OPN LIN 554 342604-342631(1) | -
|  |  | SING OPN LIN 555 342604-925980(1) | -
|  |  | SING OPN LIN 556 342607-342610(1) | -
|  |  | SING OPN LIN 557 342607-342613(1) | -
|  |  | SING OPN LIN 558 342607-342637(1) | -
|  |  | SING OPN LIN 559 342607-342688(1) | -
|  |  | SING OPN LIN 560 342610-342832(1) | -
|  |  | SING OPN LIN 561 342613-342832(1) | -
342625 | 4MAYSVIL IND | 138 | SING OPN LIN 562 342622-342625(1) | 8.0269
|  |  | SING OPN LIN 563 342622-342634(1) | -
|  |  | SING OPN LIN 564 342622-342664(1) | -
|  |  | SING OPN LIN 565 342637-342784(1) | -
|  |  | SING OPN LIN 566 342640-342664(1) | -
|  |  | SING OPN LIN 567 342640-925980(1) | -
342643 | 4RICHWOOD | 138 | SING OPN LIN 568 342643-342646(1) | 11.3427
|  |  | SING OPN LIN 569 342646-342667(1) | -
|  |  | SING OPN LIN 570 342649-342658(1) | -
|  |  | SING OPN LIN 571 342661-342664(1) | -
|  |  | SING OPN LIN 572 342664-342667(1) | -
|  |  | SING OPN LIN 573 342664-342838(1) | -
|  |  | SING OPN LIN 574 342664-342838(2) | -
|  |  | SING OPN LIN 575 342664-342838(3) | -
342670 | 4STERLING | 138 | SING OPN LIN 576 342670-342673(1) | 6.9793
342679 | 4THREE FORKS | 138 | SING OPN LIN 577 342676-342679(1) | 3.0944
342685 | 4UNION CITY | 138 | SING OPN LIN 578 342685-342688(1) | 6.4748
|  |  | SING OPN LIN 579 342694-342813(1) | -
|  |  | SING OPN LIN 580 342697-342780(1) | -
|  |  | SING OPN LIN 581 342700-342819(1) | -
|  |  | SING OPN LIN 582 342703-342769(1) | -
|  |  | SING OPN LIN 583 342715-342718(1) | -
|  |  | SING OPN LIN 584 342715-342790(1) | -
|  |  | SING OPN LIN 585 342715-342799(1) | -
|  |  | SING OPN LIN 586 342718-342727(1) | -
|  |  | SING OPN LIN 587 342718-342757(1) | -
342721 | 5DARWIN TH | 161 | SING OPN LIN 588 342721-342724(1) | 15.3905
|  |  | SING OPN LIN 589 342724-342766(1) | -
|  |  | SING OPN LIN 590 342724-342808(1) | -
|  |  | SING OPN LIN 591 342730-342820(1) | -
|  |  | SING OPN LIN 592 342733-342817(1) | -
|  |  | SING OPN LIN 593 342733-943820(1) | -
342739 | 5GREEN HALL | 161 | SING OPN LIN 594 342736-342739(1) | 2.6482
|  |  | SING OPN LIN 595 342736-342820(1) | -
342742 | 5JABEZ | 161 | SING OPN LIN 596 342742-342745(1) | 4.1686
|  |  | SING OPN LIN 597 342745-342751(1) | -
|  |  | SING OPN LIN 598 342745-342799(1) | -
342748 | 5JAMESTOWN | 161 | SING OPN LIN 599 342748-342751(1) | 6.8602
|  |  | SING OPN LIN 600 342751-342792(1) | -
|  |  | SING OPN LIN 601 342754-342757(1) | -
|  |  | SING OPN LIN 602 342754-342783(1) | -
|  |  | SING OPN LIN 603 342760-342790(1) | -
342763 | 5LITTLE MT | 161 | SING OPN LIN 604 342763-342766(1) | 5.1178
|  |  | SING OPN LIN 605 342766-342819(1) | -
|  |  | SING OPN LIN 606 342769-342770(1) | -
|  |  | SING OPN LIN 607 342769-342770(2) | -
|  |  | SING OPN LIN 608 342769-342770(3) | -
|  |  | SING OPN LIN 609 342769-342770(4) | -
|  |  | SING OPN LIN 610 342769-342781(1) | -
342772 | 5MARION IP | 161 | SING OPN LIN 611 342772-342797(1) | 7.3059
|  |  | SING OPN LIN 612 342775-342781(1) | -
342772 | 5MARION IP | 161 | SING OPN LIN 613 342775-342797(1) | 7.3059
342798 | 5S MARION IP | 161 | SING OPN LIN 613 342775-342797(1) | 30.4021
|  |  | SING OPN LIN 614 342775-342805(1) | -
342779 | 5MILLER CRK | 161 | SING OPN LIN 615 342779-342780(1) | 3.1325
|  |  | SING OPN LIN 616 342780-342784(1) | -
|  |  | SING OPN LIN 617 342782-342787(1) | -
|  |  | SING OPN LIN 618 342783-342820(1) | -
|  |  | SING OPN LIN 619 342787-342790(1) | -
|  |  | SING OPN LIN 620 342792-342796(1) | -
|  |  | SING OPN LIN 621 342793-342796(1) | -
342798 | 5S MARION IP | 161 | SING OPN LIN 622 342797-342798(1) | 30.4021
342802 | 5SALOMA | 161 | SING OPN LIN 623 342802-342805(1) | 12.0099
|  |  | SING OPN LIN 624 342805-944150(1) | -
|  |  | SING OPN LIN 626 342814-943820(1) | -
|  |  | SING OPN LIN 627 342817-944150(1) | -
342818 | 5TAYLORSVILL | 161 | SING OPN LIN 628 342818-342819(1) | 10.0637
|  |  | SING OPN LIN 629 342829-342835(1) | -
|  |  | SING OPN LIN 630 342832-342835(1) | -
|  |  | SING OPN LIN 631 342832-342841(1) | -
|  |  | SING OPN LIN 632 342835-342838(1) | -
|  |  | SING OPN LIN 633 925980-925981(1) | -
|  |  | SING OPN LIN 634 925980-932551(1) | -
|  |  | SING OPN LIN 635 925981-925982(1) | -
|  |  | SING OPN LIN 636 932551-932552(1) | -
|  |  | SING OPN LIN 637 936380-936381(1) | -
|  |  | SING OPN LIN 638 936381-936382(1) | -
|  |  | SING OPN LIN 639 940830-940831(1) | -
|  |  | SING OPN LIN 640 940831-940832(1) | -
|  |  | SING OPN LIN 641 942410-942411(1) | -
|  |  | SING OPN LIN 642 942411-942412(1) | -
|  |  | SING OPN LIN 643 943700-943701(1) | -
|  |  | SING OPN LIN 644 943701-943702(1) | -
|  |  | SING OPN LIN 645 943820-943821(1) | -
|  |  | SING OPN LIN 646 943821-943822(1) | -
|  |  | SING OPN LIN 647 944150-944151(1) | -
|  |  | SING OPN LIN 648 944151-944152(1) | -
|  |  | SING OPN TIE 649 341020-243725(1) | -
|  |  | SING OPN TIE 650 341071-324430(1) | -
|  |  | SING OPN TIE 651 341089-325102(1) | -
|  |  | SING OPN TIE 652 341161-324213(1) | -
|  |  | SING OPN TIE 653 341188-324463(1) | -
|  |  | SING OPN TIE 654 341188-324722(1) | -
|  |  | SING OPN TIE 655 341317-324474(1) | -
|  |  | SING OPN TIE 656 341320-324830(1) | -
|  |  | SING OPN TIE 657 341406-324530(1) | -
|  |  | SING OPN TIE 658 341407-324425(1) | -
243721 | 05FALCON | 69 | SING OPN TIE 659 341461-243721(Z1) | 10.79
|  |  | SING OPN TIE 660 341515-324600(1) | -
|  |  | SING OPN TIE 661 341539-324784(1) | -
243726 | 05GRAYSO | 69 | SING OPN TIE 662 341554-243726(1) | 9.905
|  |  | SING OPN TIE 663 341563-324554(1) | -
|  |  | SING OPN TIE 664 341605-251579(1) | -
|  |  | SING OPN TIE 665 341608-243812(Z1) | -
|  |  | SING OPN TIE 666 341632-324575(1) | -
|  |  | SING OPN TIE 667 341632-324660(1) | -
|  |  | SING OPN TIE 668 341713-324519(1) | -
|  |  | SING OPN TIE 669 341740-324576(1) | -
|  |  | SING OPN TIE 670 341752-243737(Z1) | -
|  |  | SING OPN TIE 671 341755-324527(1) | -
|  |  | SING OPN TIE 672 341890-246973(Z1) | -
|  |  | SING OPN TIE 673 341923-324717(1) | -
|  |  | SING OPN TIE 674 341923-325019(1) | -
|  |  | SING OPN TIE 675 341929-324662(1) | -
|  |  | SING OPN TIE 676 341935-324736(1) | -
|  |  | SING OPN TIE 677 341944-324288(1) | -
|  |  | SING OPN TIE 678 342007-324455(1) | -
|  |  | SING OPN TIE 679 342008-324290(1) | -
342055 | 2PELFREY | 69 | SING OPN TIE 680 342055-243742(1) | 3.5497
|  |  | SING OPN TIE 681 342058-324951(1) | -
|  |  | SING OPN TIE 682 342133-324492(1) | -
|  |  | SING OPN TIE 683 342157-324708(1) | -
|  |  | SING OPN TIE 684 342184-324445(1) | -
|  |  | SING OPN TIE 685 342184-324445(2) | -
342218 | 2SALT LICK | 138 | SING OPN TIE 686 342218-247897(Z1) | 4.2393
|  |  | SING OPN TIE 687 342232-324787(1) | -
|  |  | SING OPN TIE 688 342248-324718(1) | -
|  |  | SING OPN TIE 689 342287-324531(1) | -
|  |  | SING OPN TIE 690 342287-324737(1) | -
|  |  | SING OPN TIE 691 342307-324509(1) | -
|  |  | SING OPN TIE 692 342340-324519(1) | -
342454 | 2W M SMITH | 69 | SING OPN TIE 694 342454-251315(1) | 3.651
|  |  | SING OPN TIE 695 342487-250148(1) | -
|  |  | SING OPN TIE 696 342538-243688(1) | -
|  |  | SING OPN TIE 697 342544-324275(1) | -
|  |  | SING OPN TIE 698 342547-324210(1) | -
|  |  | SING OPN TIE 699 342559-250054(1) | -
|  |  | SING OPN TIE 700 342565-325925(1) | -
|  |  | SING OPN TIE 701 342568-324047(1) | -
|  |  | SING OPN TIE 702 342568-324261(1) | -
|  |  | SING OPN TIE 703 342577-324247(1) | -
|  |  | SING OPN TIE 704 342577-324248(1) | -
|  |  | SING OPN TIE 705 342586-324253(1) | -
|  |  | SING OPN TIE 706 342595-250152(1) | -
|  |  | SING OPN TIE 707 342607-342918(1) | -
|  |  | SING OPN TIE 708 342607-342921(1) | -
|  |  | SING OPN TIE 709 342607-342924(1) | -
|  |  | SING OPN TIE 710 342607-342927(1) | -
|  |  | SING OPN TIE 711 342607-342930(1) | -
|  |  | SING OPN TIE 712 342607-342933(1) | -
|  |  | SING OPN TIE 713 342607-342936(1) | -
|  |  | SING OPN TIE 714 342616-342948(1) | -
|  |  | SING OPN TIE 715 342631-324328(1) | -
|  |  | SING OPN TIE 716 342649-324302(1) | -
|  |  | SING OPN TIE 717 342661-324267(1) | -
342957 | 1SPURLK1G | 22 | SING OPN TIE 718 342664-342957(1) | 44
|  |  | SING OPN TIE 719 342688-324276(1) | -
|  |  | SING OPN TIE 720 342697-324138(1) | -
|  |  | SING OPN TIE 721 342697-324430(1) | -
|  |  | SING OPN TIE 722 342700-326975(1) | -
|  |  | SING OPN TIE 723 342700-326998(1) | -
|  |  | SING OPN TIE 724 342718-324141(1) | -
|  |  | SING OPN TIE 725 342732-361603(1) | -
|  |  | SING OPN TIE 726 342736-324138(1) | -
|  |  | SING OPN TIE 727 342757-342945(1) | -
|  |  | SING OPN TIE 728 342770-324271(1) | -
|  |  | SING OPN TIE 729 342770-324271(2) | -
|  |  | SING OPN TIE 730 342770-324271(3) | -
|  |  | SING OPN TIE 731 342778-360473(1) | -
|  |  | SING OPN TIE 732 342778-360486(1) | -
|  |  | SING OPN TIE 733 342778-361579(1) | -
|  |  | SING OPN TIE 734 342782-342837(1) | -
|  |  | SING OPN TIE 735 342783-324688(1) | -
|  |  | SING OPN TIE 736 342796-360448(1) | -
|  |  | SING OPN TIE 737 342814-360334(1) | -
|  |  | SING OPN TIE 738 342814-361788(1) | -
|  |  | SING OPN TIE 739 342817-325921(1) | -
|  |  | SING OPN TIE 740 342821-342839(1) | -
|  |  | SING OPN TIE 741 342821-342839(2) | -
|  |  | SING OPN TIE 742 342823-360486(1) | -
342939 | 1JKCT 9G | 13.8 | SING OPN TIE 743 342832-342939-342942(1) | 2.5
342942 | 1JKCT 10G | 13.8 | SING OPN TIE 743 342832-342939-342942(1) | 3.5
|  |  | SING OPN TIE 744 342838-249581(1) | -
342960 | 1SPURLK2G | 22 | SING OPN TIE 746 342838-342960(1) | 45
342963 | 1SPURLK3G | 18 | SING OPN TIE 747 342838-342963(1) | 20
342966 | 1SPURLK4G | 18 | SING OPN TIE 748 342838-342966(1) | 38
|  |  | SING OPN TIE 749 342841-325074(Z1) | -
|  |  | SING OPN TIE 750 342844-384157(1) | -
|  |  | BARREN CO - HORSECAVE 69 SS | -
|  |  | CAVE CITY J-SEYMOUR T 69 SS | -
|  |  | CAVE CITY - CAVE CITY JCT 69 SS | -
|  |  | FOX HOLLOW - PARKWAY1 69 SS | -
|  |  | WAYNE CO - ZULA TAP 69 SS | -
243726 | 05GRAYSO | 69 | EKPC_P1-2_ARGEN - LEON69 | 9.905
341263 | 2CARTER CTY | 69 | EKPC_P1-2_ARGEN - LEON69 | 3.7198
341779 | 2LOW GAP | 69 | EKPC_P1-2_ARGEN - LEON69 | 4.1103
342031 | 2PACTOLUS | 69 | EKPC_P1-2_ARGEN - LEON69 | 8.8816
342475 | 2WARNOCK | 69 | EKPC_P1-2_ARGEN - LEON69 | 4.7497
341137 | 2BLOOMFLD | 69 | EKPC_P1-2_N SPR -S AND69 | 7.5908
341293 | 2CHAPLIN | 69 | EKPC_P1-2_N SPR -S AND69 | 1.4053
342262 | 2SINAI | 69 | EKPC_P1-2_N SPR -S AND69 | 7.5123
341731 | 2LANCASTER | 69 | EKPC_P1-2_DALE-GARRD 69 | 5.5024
341959 | 2NEWBY 1 | 69 | EKPC_P1-2_DALE-GARRD 69 | 7.6911
341533 | 2GLENDALE | 69 | EKPC_P1-2_STEPH-HODG 69 | 5.9756
341800 | 2MAGNOLIA | 69 | EKPC_P1-2_HODG-GREEN 69 | 6.0678
342325 | 2SUMMERSVIL | 69 | EKPC_P1-2_HODG-GREEN 69 | 6.8647
341776 | 2LORETTO | 69 | EKPC_P1-2_HODG-N SPR 69 | 6.9275
342211 | 2S SPRINGFLD | 69 | EKPC_P1-2_HODG-N SPR 69 | 4.6495
342316 | 2SULPHUR CRK | 69 | EKPC_P1-2_HODG-N SPR 69 | 5.3135
341140 | 2BLUE G PW | 69 | EKPC_P1-2_E BARD-N SPR69 | 11.2397
341497 | 2FREDRIKBRG | 69 | EKPC_P1-2_E BARD-N SPR69 | 4.135
342016 | 2OWENS IL | 69 | EKPC_P1-2_E BARD-N SPR69 | 7.503
341791 | 2MACKVIL KU | 69 | EKPC_P1-2_HNTFMJ-N SPR69 | 0.45
342061 | 2PERRYVILLE | 69 | EKPC_P1-2_HNTFMJ-N SPR69 | 7.8964
341158 | 2BONNIV DIST | 69 | EKPC_P1-2_BONN - BARR 69 | 3.0767
341647 | 2HORSE CV KU | 69 | EKPC_P1-2_BONN - BARR 69 | 46.06
341908 | 2MUNFVIL EK | 69 | EKPC_P1-2_BONN - BARR 69 | 9.2259
341911 | 2MUNFVIL KU | 69 | EKPC_P1-2_BONN - BARR 69 | 6.11
341437 | 2EDMON IND P | 69 | EKPC_P1-2_GREEN-SUM SH69 | 1.5349
341575 | 2GREENSBURG | 69 | EKPC_P1-2_GREEN-SUM SH69 | 5.9623
341680 | 2JB GALLOWAY | 69 | EKPC_P1-2_GREEN-SUM SH69 | 7.4175
341728 | 2KNOB LICK | 69 | EKPC_P1-2_GREEN-SUM SH69 | 5.6051
341851 | 2MCKINNEY | 69 | EKPC_P1-2_GREEN-SUM SH69 | 4.4445
341764 | 2LIBERTY KU | 69 | EKPC_P1-2_CASEY-LIB J69 | 7.68
342064 | 2PEYTONS ST | 69 | EKPC_P1-2_CASEY-LIB J69 | 6.0717
341210 | 2BROUGHT TWN | 69 | EKPC_P1-2_LIB J-GARR69 | 4.4578
341617 | 2HIGHLAND EK | 69 | EKPC_P1-2_LIB J-GARR69 | 5.9777
341893 | 2MT OLIVE | 69 | EKPC_P1-2_LIB J-GARR69 | 4.6349
341343 | 2CONTOWN | 69 | EKPC_P1-2_LIB J-WIND 69 | 2.2548
341350 | 2CRESTON | 69 | EKPC_P1-2_LIB J-WIND 69 | 5.7798
342067 | 2PHIL | 69 | EKPC_P1-2_LIB J-WIND 69 | 5.7813
341233 | 2CABIN HOLLW | 69 | EKPC_P1-2_SSET-NORWJ69 | 8.7275
341542 | 2GOODNIGHT | 69 | EKPC_P1-2_BARR- FOX H 69 | 9.2502
|  |  | EKPC_P1-2_FOX H-AE2-07169 | -
|  |  | EKPC_P1-2_AE2-071-SUMMSH69 | -
341320 | 2COBURG | 69 | EKPC_P1-2_CMPBEK-COBURG J69 | 7.9533
341509 | 2GARLIN | 69 | EKPC_P1-2_CMPBEK-COBURG J69 | 5.8713
341335 | 2COLUMBIA | 69 | EKPC_P1-2_COBURG J-SUMMSH 69 | 6.5135
341366 | 2COLUMB KU | 69 | EKPC_P1-2_COBURG J-SUMMSH 69 | 6.29
341370 | 2COLUMB S KU | 69 | EKPC_P1-2_COBURG J-SUMMSH 69 | 4.41
342439 | 2W COLUMBIA | 69 | EKPC_P1-2_COBURG J-SUMMSH 69 | 5.8725
341926 | 2N ALBANY | 69 | EKPC_P1-2_SUMMSH-WAYNE69 | 8.5373
342181 | 2S ALBANY | 69 | EKPC_P1-2_SUMMSH-WAYNE69 | 7.995
342277 | 2SNOW | 69 | EKPC_P1-2_SUMMSH-WAYNE69 | 9.8435
342394 | 2UPCHURCH | 69 | EKPC_P1-2_SUMMSH-WAYNE69 | 8.1682
342529 | 2ZULA | 69 | EKPC_P1-2_WAYNE-ZULA 69 | 8.451
342172 | 2RUSS SPR EK | 69 | EKPC_P1-2_SEWJ - RUSS 69 | 11.0494
342175 | 2RUSS SPR KU | 69 | EKPC_P1-2_SEWJ - RUSS 69 | 6.4
341938 | 2NANCY | 69 | EKPC_P1-2_WIND - SSET 69 | 6.3159
341977 | 2OAK HILL | 69 | EKPC_P1-2_WIND - SSET 69 | 6.5887
342469 | 2W SOMERSET | 69 | EKPC_P1-2_WIND - SSET 69 | 7.984
342523 | 2ZOLLICOF | 69 | EKPC_P1-2_WIND - SSET 69 | 3.8925
324531 | 2FERGUSON SO | 69 | EKPC_P1-2_SSET-KU ELI 69 | 5.58
341203 | 2BRONSTON | 69 | EKPC_P1-2_COOP-DENNY 69 | 13.1724
342070 | 2PINE GROVE | 69 | EKPC_P1-2_DAV LANE - LAUR69 | 9.8481
342451 | 2W LONDON | 69 | EKPC_P1-2_DAV LANE - LAUR69 | 9.7025
341035 | 2BACON CRK | 69 | EKPC_P1-2_LAUR-KU FAR69 | 4.3674
341716 | 2KEAVY | 69 | EKPC_P1-2_LAUR-KU FAR69 | 10.7978
341758 | 2LIBERT CHUR | 69 | EKPC_P1-2_LAUR-KU FAR69 | 4.8231
342187 | 2S CORBIN | 69 | EKPC_P1-2_LAUR-KU FAR69 | 9.1367
324576 | 2HOPEWELL | 69 | EKPC_P1-2_LAUR-KU SWTH69 | 12.82
341506 | 2GAP OF RIDG | 69 | EKPC_P1-2_WAYNE-DENNY69 | 9.8439
341581 | 2GREGORY RD | 69 | EKPC_P1-2_WAYNE-DENNY69 | 1.8519
341641 | 2HOMESTEAD S | 69 | EKPC_P1-2_WAYNE-DENNY69 | 14.1787
341887 | 2MONTICELLO | 69 | EKPC_P1-2_WAYNE-DENNY69 | 7.6051
342268 | 2SLAT | 69 | EKPC_P1-2_WAYNE-DENNY69 | 8.7197
342490 | 2WHITLEY CTY | 69 | EKPC_P1-2_DENNY-MCCRRY69 | 6.1217
342493 | 2WHITLY C KU | 69 | EKPC_P1-2_DENNY-MCCRRY69 | 3.81
342496 | 2WIBORG | 69 | EKPC_P1-2_DENNY-MCCRRY69 | 8.0737
|  |  | EKPC_P1-2_AEPMORG- MOR69 | -
|  |  | EKPC_P1-2_AEPMORG-INDX69 | -
324424 | 2BARDTWN CTY | 69 | EKPC_P1-2_HODG-KU BARD69 | 9.42
324660 | 2NEW HAVEN | 69 | EKPC_P1-2_HODG-KU BARD69 | 3.33
324801 | 2BARTON | 69 | EKPC_P1-2_HODG-KU BARD69 | 6.46
326537 | 2WOODLAWN KU | 69 | EKPC_P1-2_HODG-KU BARD69 | 5.15
324521 | 2ETOWN 4 | 69 | EKPC_P1-2_HODG-KU ETWN69 | 13.48
324575 | 2HODGENV KU | 69 | EKPC_P1-2_HODG-KU ETWN69 | 10.02
324736 | 2SPRINGFL KU | 69 | EKPC_P1-2_N SPR-KU LEB69 | 13.78
341080 | 2BECKTON | 69 | EKPC_P1-2_BAR-BON-FHOL69 | 8.3189
341149 | 2BON AYR | 69 | EKPC_P1-2_BAR-BON-FHOL69 | 3.8843
341272 | 2CAVE CITY | 69 | EKPC_P1-2_BAR-BON-FHOL69 | 7.5201
342238 | 2SEYMOUR | 69 | EKPC_P1-2_BAR-BON-FHOL69 | 3.7942
342442 | 2W GLASGOW | 69 | EKPC_P1-2_BAR-BON-FHOL69 | 12.7509
342037 | 2PARKWAY 1 | 69 | EKPC_P1-2_FHOL-PARK69 | 9.3281
342040 | 2PARKWAY 2 | 69 | EKPC_P1-2_FHOL-PARK69 | 3.3429
324554 | 2GRENSBRG KU | 69 | EKPC_P1-2_CMPBEK-GREEN69 | 4.57
324557 | 2GR RVR PLAZ | 69 | EKPC_P1-2_CMPBEK-KUTAY69 | 7.3221
324829 | 2CAMPBELVIL1 | 69 | EKPC_P1-2_CMPBEK-KUTAY69 | 12.53
326970 | 2MILE LAN EK | 69 | EKPC_P1-2_CMPBEK-KUTAY69 | 9.7611
342595 | 4HEBRON | 138 | EKPC_P1-2_DK HEB-HEB 138 | 16.4491
250054 | 08LONGBR | 138 | EKPC_P1-2_BOONE-BUFF138 | 20.26
250077 | 08MTZION | 138 | EKPC_P1-2_BOONE-BUFF138 | 13.028
|  |  | EKPC_P1-2_RUSSOL-RUS-WLF161 | -
342742 | 5JABEZ | 161 | EKPC_P1-2_COOP-RUSSOL161 | 4.1686
342748 | 5JAMESTOWN | 161 | EKPC_P1-2_COOP-RUSSOL161 | 6.8602
342799 | 5S OAKHILL | 161 | EKPC_P1-2_COOP-RUSSOL161 | 10.6696
|  |  | EKPC_P1-2_COOP-DEN161 | -
|  |  | EKPC_P1-2_COP-LIBJ-PU161 | -
|  |  | EKPC_P1-2_MCCR-WAYNE161 | -
|  |  | EKPC_P1-2_LAUR-PIT-TY161 | -
|  |  | EKPC_P1-2_GRE-TAY-AF1-083161 | -
342772 | 5MARION IP | 161 | EKPC_P1-2_AF1-083-MARION161 | 7.3059
342798 | 5S MARION IP | 161 | EKPC_P1-2_AF1-083-MARION161 | 30.4021
342802 | 5SALOMA | 161 | EKPC_P1-2_AF1-083-MARION161 | 12.0099
342781 | 5N LEBANON | 161 | EKPC_P1-2_AF1-083-MARION161 | 25
|  |  | EKPC_P1-2_BARR-SUMSHSOL161 | -
|  |  | EKPC_P1-2_BULL-SUMSH161 | -
|  |  | TVA SS-GLASGOW & LAFAYETTE 161 | -
|  |  | EK-TVA SSHD & SSHD 161 XFMR | -
|  |  | B-69-60 | -
|  |  | B-69-79 | -
|  |  | B-69-80 | -
326526 | 4N SHARKEY | 138 | B-138-447 | 1.2322
326532 | 4SHARKEY | 138 | B-138-447 | 8.4668
326526 | 4N SHARKEY | 138 | B-69-330 | 1.2322
326532 | 4SHARKEY | 138 | B-69-330 | 8.4668
|  |  | B-69-332 | -
|  |  | B-69-450 | -
324654 | 2MT VIC EK J | 69 | BB-1408 | 1.4839
325034 | 2CUMBER FALL | 69 | BB-1408 | 8.1243
324068 | 2E CAMPBELVL | 69 | BB-1403 | 7.2306
324349 | 2CAMPBELVIL2 | 69 | BB-1403 | 7.53
324603 | 2LEBANON CIT | 69 | BB-1403 | 6.21
324604 | 2LEBANON IND | 69 | BB-1403 | 2.44
324605 | 2LEBANON EK | 69 | BB-1403 | 12.5278
324889 | 2LEBANON SO | 69 | BB-1403 | 11.44
325020 | 2LEBANON E | 69 | BB-1403 | 14.02
324554 | 2GRENSBRG KU | 69 | BB-1402 | 4.57
324557 | 2GR RVR PLAZ | 69 | BB-1402 | 7.3221
324829 | 2CAMPBELVIL1 | 69 | BB-1402 | 12.53
324830 | 2CAMPBELV EK | 69 | BB-1402 | 11.5694
326970 | 2MILE LAN EK | 69 | BB-1402 | 9.7611
|  |  | B-69-25 | -
|  |  | B-138-111 | -
324270 | 4LEBANON WES | 138 | BB-1133 | 6.91
|  |  | B-161-128 | -
|  |  | B-69-18 | -
|  |  | B-69-19 | -
|  |  | B-69-26 | -
|  |  | B-345-100 | -
|  |  | B-138-116 | -