## Scenario Descriptions
Scenario | Offline | Redispatch
Scenario 1 | · Cooper 1 & 2 | · Import from the North to pick up lost Cooper generation.
· LG&E/KU’s Brown base case generation “as dispatched” in the models

## Thermal Overloads
[13 empty] | Scenario 1 |  | Scenario 2 |  | Scenario 3 |  | Scenario 4
[12 empty] | Violation Count | 3 | 8 | 7 | 13 | 6 | 8 | 5 | 8
Monitored Facility | Fr Bus | Fr Name | To Bus | To Name | CktId | kVs | Area | Mon Type | Rate Base (MVA) | Rate Cont (MVA) | Cont Name | Cont Type | S1_O0_SUM | S1_O0_WIN | S2_O0_SUM | S2_O0_WIN | S3_O0_SUM | S3_O0_WIN | S4_O0_SUM | S4_O0_WIN
324509 2EASTVIEW 69.0 324914 2M-V CLARK T 69.0 1 | 324509 | 2EASTVIEW | 324914 | 2M-V CLARK T | 1 | 69 | 363 | PJM | 42 | 42 | 324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 | N1_Auto | 97.52 | 71.64 | 95.47 | 74.29 | 102.83 | 74.1 | 102.94 | 75.45
324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1 | 324514 | 2ELIHU | 324531 | 2FERGUSON SO | 1 | 69 | 363 | PJM | 128 | 141 | 324141 5ELIHU 161 342718 5COOPER2 161 1 | N1_Auto | 81.14 | 89.77 | 97.1 | 104.85 | 77.92 | 89.68 | 78.21 | 88.67
324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1 | 324514 | 2ELIHU | 324531 | 2FERGUSON SO | 1 | 69 | 363 | PJM | 83 | 105 | EKPC_P2-3_COOP S42-1014_SRT-A | N1 | 101.65 | 118.86 | 104.84 | 123.13 | 102.18 | 122.92 | 100.78 | 122.97
324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1 | 324514 | 2ELIHU | 324531 | 2FERGUSON SO | 1 | 69 | 363 | PJM | 128 | 141 | EKPC_P2-3_COOP S42-1039_SRT-A | N1 | 82.87 | 93.97 | 96.82 | 107.01 | 80.55 | 94.6 | 80.32 | 93.75
324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1 | 324514 | 2ELIHU | 324531 | 2FERGUSON SO | 1 | 69 | 363 | PJM | 83 | 105 | EKPC_P4-2_COOP S42-1014_SRT-A | N1 | 101.65 | 118.86 | 104.84 | 123.13 | 102.18 | 122.92 | 100.78 | 122.97
324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1 | 324514 | 2ELIHU | 324531 | 2FERGUSON SO | 1 | 69 | 363 | PJM | 83 | 105 | EKPC_P4-5_COOP S42-1014_SRT-A | N1 | 101.65 | 118.86 | 104.84 | 123.13 | 102.18 | 122.92 | 100.78 | 122.97
324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1 | 324514 | 2ELIHU | 324531 | 2FERGUSON SO | 1 | 69 | 363 | PJM | 128 | 141 | EKPC_P4-5_COOP S42-1039_SRT-A | N1 | 82.87 | 93.97 | 96.82 | 107.01 | 80.55 | 94.6 | 80.32 | 93.75
324521 2ETOWN 4 69.0 324575 2HODGENV KU 69.0 1 | 324521 | 2ETOWN 4 | 324575 | 2HODGENV KU | 1 | 69 | 363 | PJM | 64 | 64 | 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1 | N1_Auto | 90.68 | 91.03 | 92.9 | 93.41 | 103.1 | 96.39 | 96.66 | 95.7
324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1 | 324531 | 2FERGUSON SO | 342287 | 2SOMERSET KU | 1 | 69 | 363\320 | EKPC | 83 | 105 | EKPC_P2-3_COOP S42-1014_SRT-A | N1 | 96.99 | 114.56 | 100.3 | 118.83 | 97.72 | 118.52 | 96.19 | 118.53
324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1 | 324531 | 2FERGUSON SO | 342287 | 2SOMERSET KU | 1 | 69 | 363\320 | EKPC | 128 | 141 | EKPC_P2-3_COOP S42-1039_SRT-A | N1 | 78.06 | 90.03 | 92.12 | 102.99 | 75.99 | 90.59 | 75.5 | 89.7
324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1 | 324531 | 2FERGUSON SO | 342287 | 2SOMERSET KU | 1 | 69 | 363\320 | EKPC | 83 | 105 | EKPC_P4-2_COOP S42-1014_SRT-A | N1 | 96.99 | 114.56 | 100.3 | 118.83 | 97.72 | 118.52 | 96.19 | 118.53
324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1 | 324531 | 2FERGUSON SO | 342287 | 2SOMERSET KU | 1 | 69 | 363\320 | EKPC | 83 | 105 | EKPC_P4-5_COOP S42-1014_SRT-A | N1 | 96.99 | 114.56 | 100.3 | 118.83 | 97.72 | 118.52 | 96.19 | 118.53
324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1 | 324531 | 2FERGUSON SO | 342287 | 2SOMERSET KU | 1 | 69 | 363\320 | EKPC | 128 | 141 | EKPC_P4-5_COOP S42-1039_SRT-A | N1 | 78.06 | 90.03 | 92.12 | 102.99 | 75.99 | 90.59 | 75.5 | 89.7
341008 2ALCAN 69.0 342430 2W BEREA 69.0 1 | 341008 | 2ALCAN | 342430 | 2W BEREA | 1 | 69 | 320 | EKPC | 95 | 100 | 324530 2FAWKES 69.0 341406 2DUNCAN LN T 69.0 1 | N1_Auto | 64.27 | 113.76 | 64.3 | 114.71 | 64.88 | 114.69 | 64.5 | 116.21
342307 2STEPHENSBRG 69.0 342403 2UPTON T 69.0 1 | 342307 | 2STEPHENSBRG | 342403 | 2UPTON T | 1 | 69 | 320 | EKPC | 35 | 39 | 324308 4SHREWSBURY 138 324800 4MERE TVA 138 1 | N1_Auto | 97.15 | 83.77 | 105.16 | 87.96 | 105.65 | 87.6 | 100.52 | 86.53
342691 4W BEREA 138 342430 2W BEREA 69.0 1 | 342691 | 4W BEREA | 342430 | 2W BEREA | 1 | 69\138 | 320 | EKPC | 121 | 139 | 324530 2FAWKES 69.0 341406 2DUNCAN LN T 69.0 1 | N1_Auto | 81.56 | 111.86 | 83.07 | 113.66 | 78.59 | 110.37 | 79.01 | 109.49

## Voltage Summary
[7 empty] | PJM Violation Count | 0 | 7 | 0 | 1 | 0 | 3 | 0 | 3 | 0 | 0 | 0 | 2 | 0 | 94 | 0 | 89 | 0 | 87 | 0 | 93 | 0 | 10 | 0 | 15 | 0 | 63 | 0 | 17 | 0 | 30 | 0 | 57 | 0 | 1 | 0 | 3 | 0 | 59 | 0 | 19 | 0 | 26 | 0 | 48 | 0 | 3 | 0 | 4
[8 empty] | Scenario 1 | [11 empty] | Scenario 2 | [11 empty] | Scenario 3 | [11 empty] | Scenario 4
[7 empty] | EKPC Violation Count | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 28 | 0 | 50 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 4 | 0 | 15 | 0 | 0 | 0 | 0
Bus # | Bus Name | Area | Base kV | Cont Name | Cont Type | Min Volt Limit | Max Volt Limit | S1_O0_SUM | S1_O0_WIN | S1_O1_SUM | S1_O1_WIN | S1_O2_SUM | S1_O2_WIN | S1_O3_SUM | S1_O3_WIN | S1_O4_SUM | S1_O4_WIN | S1_O5_SUM | S1_O5_WIN | S2_O0_SUM | S2_O0_WIN | S2_O1_SUM | S2_O1_WIN | S2_O2_SUM | S2_O2_WIN | S2_O3_SUM | S2_O3_WIN | S2_O4_SUM | S2_O4_WIN | S2_O5_SUM | S2_O5_WIN | S3_O0_SUM | S3_O0_WIN | S3_O1_SUM | S3_O1_WIN | S3_O2_SUM | S3_O2_WIN | S3_O3_SUM | S3_O3_WIN | S3_O4_SUM | S3_O4_WIN | S3_O5_SUM | S3_O5_WIN | S4_O0_SUM | S4_O0_WIN | S4_O1_SUM | S4_O1_WIN | S4_O2_SUM | S4_O2_WIN | S4_O3_SUM | S4_O3_WIN | S4_O4_SUM | S4_O4_WIN | S4_O5_SUM | S4_O5_WIN
324068 | 2E CAMPBELVL | 363 | 69 | 324479 2CAMPBELVL T 69.0 324751 2TAYLOR CO 69.0 1 | N1_Auto | 0.9 | 1.06 | 0.9453 | 0.9223 | 0.946 | 0.9243 | 0.9457 | 0.9232 | 0.9453 | 0.9224 | 0.9501 | 0.9296 | 0.9507 | 0.9308 | 0.9418 | 0.912 | 0.9421 | 0.9129 | 0.9422 | 0.9132 | 0.942 | 0.9123 | 0.949 | 0.9246 | 0.9478 | 0.9262 | 0.9315 | 0.9111 | 0.9328 | 0.9135 | 0.9318 | 0.912 | 0.9316 | 0.9111 | 0.938 | 0.9201 | 0.9422 | 0.9232 | 0.9383 | 0.8986 | 0.9397 | 0.9018 | 0.9389 | 0.8998 | 0.9381 | 0.8987 | 0.9443 | 0.909 | 0.9465 | 0.9149
341029 | 2ASAHI M W | 320 | 69 | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-A | N1 | 0.9 | 1.06 | 0.9631 | 0.948 | 0.9715 | 0.9517 | 0.9631 | 0.9445 | 0.9639 | 0.949 | 0.9738 | 0.972 | 0.9662 | 0.9503 | 0.9849 | 0.8989 | 0.9644 | 0.9121 | 0.9779 | 0.9069 | 0.9853 | 0.8997 | 0.9735 | 0.9461 | 0.9611 | 0.9348 | 0.9727 | 0.9243 | 0.9732 | 0.9398 | 0.9744 | 0.9313 | 0.9735 | 0.9253 | 0.9845 | 0.9708 | 0.9731 | 0.9466 | 0.9665 | 0.9227 | 0.9769 | 0.9393 | 0.9612 | 0.93 | 0.9673 | 0.9238 | 0.9722 | 0.9607 | 0.9659 | 0.946
341029 | 2ASAHI M W | 320 | 69 | EXT_324130 5ALCALDE 161 324141 5ELIHU 161 1 _SRT-A | N1 | 0.9 | 1.06 | 0.9699 | 0.9479 | 0.973 | 0.9534 | 0.9658 | 0.944 | 0.9648 | 0.9492 | 0.9764 | 0.9756 | 0.9672 | 0.9511 | 0.9788 | 0.8873 | 0.9719 | 0.9053 | 0.9682 | 0.8978 | 0.9674 | 0.8883 | 0.9752 | 0.947 | 0.9615 | 0.9319 | 0.974 | 0.9195 | 0.9746 | 0.9393 | 0.9759 | 0.9284 | 0.9748 | 0.9208 | 0.9879 | 0.9739 | 0.9744 | 0.9462 | 0.9679 | 0.92 | 0.9673 | 0.9407 | 0.9619 | 0.929 | 0.9689 | 0.9214 | 0.9749 | 0.9662 | 0.9672 | 0.9566
341029 | 2ASAHI M W | 320 | 69 | EXT_B-345-100_SRT-A | N1 | 0.9 | 1.06 | 0.9657 | 0.941 | 0.9745 | 0.9548 | 0.9616 | 0.9467 | 0.9664 | 0.9418 | 0.971 | 0.9671 | 0.9636 | 0.9485 | 0.9849 | 0.8875 | 0.9909 | 0.9018 | 0.9853 | 0.8961 | 0.9853 | 0.8884 | 0.9699 | 0.9386 | 0.9582 | 0.9271 | 0.9696 | 0.9153 | 0.972 | 0.932 | 0.9713 | 0.9231 | 0.9704 | 0.9164 | 0.9812 | 0.965 | 0.9705 | 0.9507 | 0.9621 | 0.9172 | 0.9741 | 0.9316 | 0.9645 | 0.9231 | 0.9629 | 0.9184 | 0.9688 | 0.9531 | 0.9628 | 0.9499
341029 | 2ASAHI M W | 320 | 69 | EXT_B-69-25_SRT-A | N1 | 0.9 | 1.06 | 0.9684 | 0.9283 | 0.9569 | 0.945 | 0.9687 | 0.9353 | 0.9693 | 0.9295 | 0.9626 | 0.9565 | 0.9572 | 0.9442 | 0.9718 | 0.8608 | 0.9764 | 0.8797 | 0.9694 | 0.8731 | 0.9727 | 0.8619 | 0.9631 | 0.924 | 0.9501 | 0.9109 | 0.963 | 0.897 | 0.9643 | 0.9167 | 0.9649 | 0.9062 | 0.9637 | 0.8978 | 0.9747 | 0.9552 | 0.9635 | 0.9389 | 0.9794 | 0.8977 | 0.9674 | 0.9186 | 0.9806 | 0.9072 | 0.9794 | 0.8991 | 0.9609 | 0.9437 | 0.9574 | 0.9396
341203 | 2BRONSTON | 320 | 69 | EXT_324130 5ALCALDE 161 324141 5ELIHU 161 1 _SRT-A | N1 | 0.9 | 1.06 | 0.9851 | 0.9544 | 0.9901 | 0.9614 | 0.989 | 0.9518 | 0.9858 | 0.9554 | 0.9804 | 0.9832 | 0.9859 | 0.9554 | 0.9928 | 0.8884 | 0.9914 | 0.9087 | 0.9868 | 0.9025 | 0.9852 | 0.8896 | 0.9939 | 0.9504 | 0.9788 | 0.9312 | 0.9847 | 0.9233 | 0.9888 | 0.9465 | 0.9883 | 0.9356 | 0.9856 | 0.9244 | 1.0007 | 0.9815 | 0.9845 | 0.9501 | 0.9819 | 0.9263 | 0.9751 | 0.9508 | 0.9793 | 0.9388 | 0.9826 | 0.9274 | 0.9786 | 0.9753 | 0.9843 | 0.9631
341203 | 2BRONSTON | 320 | 69 | EXT_B-345-100_SRT-A | N1 | 0.9 | 1.06 | 0.9851 | 0.9485 | 0.9967 | 0.9656 | 0.9803 | 0.9574 | 0.9858 | 0.9489 | 0.9755 | 0.9762 | 0.9796 | 0.9544 | 0.992 | 0.8908 | 1.0031 | 0.9071 | 0.9873 | 0.9028 | 0.9953 | 0.892 | 0.9893 | 0.9429 | 0.9756 | 0.9276 | 0.9808 | 0.9209 | 0.9869 | 0.9407 | 0.9844 | 0.932 | 0.9816 | 0.9218 | 0.9947 | 0.9738 | 0.9813 | 0.9558 | 0.9819 | 0.9247 | 0.996 | 0.9431 | 0.9858 | 0.9342 | 0.9826 | 0.9255 | 0.973 | 0.9631 | 0.9779 | 0.9575
341203 | 2BRONSTON | 320 | 69 | EXT_B-69-25_SRT-A | N1 | 0.9 | 1.06 | 0.9851 | 0.9434 | 0.9714 | 0.9634 | 0.989 | 0.9533 | 0.9858 | 0.9444 | 0.9744 | 0.974 | 0.9793 | 0.9575 | 0.985 | 0.8715 | 0.9909 | 0.8927 | 0.9821 | 0.8872 | 0.9858 | 0.8729 | 0.9899 | 0.937 | 0.9738 | 0.9191 | 0.98 | 0.9099 | 0.985 | 0.9329 | 0.9835 | 0.9224 | 0.9808 | 0.9105 | 0.9948 | 0.9724 | 0.98 | 0.9514 | 0.99 | 0.913 | 0.995 | 0.9378 | 0.9858 | 0.9257 | 0.9908 | 0.914 | 0.9722 | 0.9621 | 0.9789 | 0.9548
341233 | 2CABIN HOLLW | 320 | 69 | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-A | N1 | 0.9 | 1.06 | 0.9686 | 0.9517 | 0.9779 | 0.9548 | 0.9685 | 0.9473 | 0.9695 | 0.9528 | 0.9797 | 0.9768 | 0.9711 | 0.9519 | 0.9868 | 0.8993 | 0.971 | 0.9126 | 0.9834 | 0.9075 | 0.9879 | 0.9002 | 0.9811 | 0.9496 | 0.9666 | 0.9363 | 0.9746 | 0.9265 | 0.9749 | 0.9426 | 0.9763 | 0.9339 | 0.9754 | 0.9277 | 0.9875 | 0.9766 | 0.9739 | 0.949 | 0.9722 | 0.9261 | 0.9837 | 0.9434 | 0.9661 | 0.9337 | 0.9732 | 0.9274 | 0.9777 | 0.9668 | 0.9705 | 0.9496
341233 | 2CABIN HOLLW | 320 | 69 | EXT_324130 5ALCALDE 161 324141 5ELIHU 161 1 _SRT-A | N1 | 0.9 | 1.06 | 0.9763 | 0.9513 | 0.9794 | 0.9562 | 0.9714 | 0.9464 | 0.9704 | 0.9527 | 0.9825 | 0.9805 | 0.9719 | 0.9523 | 0.9854 | 0.886 | 0.9799 | 0.9043 | 0.976 | 0.897 | 0.9754 | 0.8871 | 0.983 | 0.9504 | 0.9669 | 0.9327 | 0.9761 | 0.9208 | 0.9764 | 0.9414 | 0.978 | 0.9301 | 0.977 | 0.9222 | 0.9913 | 0.9799 | 0.9752 | 0.9481 | 0.9738 | 0.9226 | 0.9723 | 0.9444 | 0.9668 | 0.9322 | 0.975 | 0.9243 | 0.9806 | 0.9727 | 0.9718 | 0.9611
341233 | 2CABIN HOLLW | 320 | 69 | EXT_B-345-100_SRT-A | N1 | 0.9 | 1.06 | 0.9722 | 0.9452 | 0.9819 | 0.9597 | 0.9674 | 0.9513 | 0.973 | 0.9462 | 0.9771 | 0.9728 | 0.9688 | 0.9518 | 0.9855 | 0.8887 | 0.994 | 0.903 | 0.9806 | 0.8975 | 0.9885 | 0.8897 | 0.9776 | 0.9428 | 0.9638 | 0.9292 | 0.9719 | 0.9184 | 0.9743 | 0.9356 | 0.9737 | 0.9265 | 0.9728 | 0.9196 | 0.9847 | 0.9716 | 0.9718 | 0.955 | 0.968 | 0.9211 | 0.9813 | 0.9364 | 0.9706 | 0.9274 | 0.9689 | 0.9224 | 0.9746 | 0.9599 | 0.9676 | 0.9553
341233 | 2CABIN HOLLW | 320 | 69 | EXT_B-69-25_SRT-A | N1 | 0.9 | 1.06 | 0.9699 | 0.9271 | 0.9584 | 0.9445 | 0.9699 | 0.9345 | 0.971 | 0.9284 | 0.9641 | 0.9564 | 0.9586 | 0.9428 | 0.9692 | 0.8546 | 0.974 | 0.8739 | 0.966 | 0.8674 | 0.9702 | 0.8558 | 0.9669 | 0.922 | 0.952 | 0.907 | 0.9616 | 0.8934 | 0.9626 | 0.9138 | 0.9634 | 0.903 | 0.9624 | 0.8943 | 0.9738 | 0.9561 | 0.9607 | 0.9375 | 0.9729 | 0.8955 | 0.9708 | 0.9173 | 0.9724 | 0.9054 | 0.974 | 0.897 | 0.962 | 0.9447 | 0.9586 | 0.9397
341320 | 2COBURG | 320 | 69 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | N1 | 0.9 | 1.06 | 0.9864 | 0.9138 | 0.9904 | 0.9264 | 0.9877 | 0.9177 | 0.9865 | 0.9148 | 0.9743 | 0.9409 | 0.9882 | 0.9186 | 0.9691 | 0.9143 | 0.9693 | 0.9192 | 0.9696 | 0.9184 | 0.9697 | 0.915 | 0.9544 | 0.9451 | 0.9705 | 0.9357 | 0.9742 | 0.8969 | 0.9749 | 0.9145 | 0.9745 | 0.9019 | 0.9744 | 0.8982 | 0.9754 | 0.9292 | 0.969 | 0.9246 | 1.0073 | 0.8852 | 0.9859 | 0.9039 | 1.006 | 0.8902 | 1.0078 | 0.8868 | 0.9703 | 0.917 | 0.9875 | 0.9174
341320 | 2COBURG | 320 | 69 | EXT_324130 5ALCALDE 161 324141 5ELIHU 161 1 _SRT-A | N1 | 0.9 | 1.06 | 0.972 | 0.9771 | 0.9732 | 0.9688 | 0.9658 | 0.9648 | 0.9654 | 0.9779 | 0.95 | 0.9736 | 0.9463 | 0.9545 | 0.9933 | 0.8914 | 0.9895 | 0.9049 | 0.9889 | 0.9021 | 0.9877 | 0.8923 | 0.9617 | 0.949 | 0.9631 | 0.9404 | 0.9742 | 0.9385 | 0.9688 | 0.9525 | 0.9745 | 0.9472 | 0.9744 | 0.9393 | 0.9748 | 0.9876 | 0.9705 | 0.9641 | 0.9703 | 0.9474 | 0.9661 | 0.9621 | 0.9617 | 0.9564 | 0.971 | 0.9482 | 0.9492 | 0.9814 | 0.947 | 0.9852
341320 | 2COBURG | 320 | 69 | EXT_B-345-100_SRT-A | N1 | 0.9 | 1.06 | 0.9703 | 0.9722 | 0.974 | 0.9797 | 0.9637 | 0.9777 | 0.9706 | 0.9724 | 0.9478 | 0.9695 | 0.9452 | 0.9729 | 0.9813 | 0.8931 | 0.9877 | 0.9028 | 0.9696 | 0.9018 | 0.985 | 0.894 | 0.9599 | 0.9422 | 0.9612 | 0.9373 | 0.9742 | 0.9357 | 0.9691 | 0.9464 | 0.9745 | 0.9433 | 0.9744 | 0.9364 | 0.9716 | 0.9819 | 0.9691 | 0.9704 | 0.9664 | 0.9461 | 0.978 | 0.9543 | 0.9684 | 0.952 | 0.967 | 0.9467 | 0.9462 | 0.9705 | 0.9445 | 0.9852
341320 | 2COBURG | 320 | 69 | EXT_B-69-25_SRT-A | N1 | 0.9 | 1.06 | 0.9644 | 0.9664 | 0.9631 | 0.9777 | 0.9684 | 0.9733 | 0.9648 | 0.9672 | 0.9454 | 0.9657 | 0.9626 | 0.9729 | 0.9691 | 0.8743 | 0.9747 | 0.889 | 0.9626 | 0.8868 | 0.9697 | 0.8754 | 0.9593 | 0.9361 | 0.9589 | 0.9286 | 0.9742 | 0.9253 | 0.9669 | 0.9394 | 0.9745 | 0.9343 | 0.9744 | 0.9257 | 0.9702 | 0.9797 | 0.967 | 0.9704 | 0.9689 | 0.9343 | 0.9762 | 0.9494 | 0.9696 | 0.9437 | 0.9693 | 0.9352 | 0.9443 | 0.9687 | 0.9634 | 0.9783
341335 | 2COLUMBIA | 320 | 69 | EXT_B-69-25_SRT-A | N1 | 0.9 | 1.06 | 0.9785 | 0.9776 | 0.9778 | 0.9881 | 0.9828 | 0.9841 | 0.9788 | 0.9783 | 0.9583 | 0.9768 | 0.9777 | 0.9839 | 0.9835 | 0.889 | 0.99 | 0.9029 | 0.9774 | 0.9009 | 0.984 | 0.89 | 0.9744 | 0.9479 | 0.975 | 0.9409 | 0.9889 | 0.9375 | 0.9821 | 0.9507 | 0.9891 | 0.946 | 0.989 | 0.9379 | 0.9852 | 0.9892 | 0.9824 | 0.9813 | 0.9833 | 0.9467 | 0.991 | 0.9609 | 0.984 | 0.9556 | 0.9837 | 0.9475 | 0.9572 | 0.9787 | 0.9784 | 0.9888
341344 | 2COOPER | 320 | 69 | EXT_324130 5ALCALDE 161 324141 5ELIHU 161 1 _SRT-A | N1 | 0.9 | 1.06 | 0.9865 | 0.9632 | 0.9904 | 0.9687 | 0.9821 | 0.9585 | 0.981 | 0.9646 | 0.9929 | 0.9937 | 0.9825 | 0.9642 | 0.9935 | 0.8983 | 0.9903 | 0.917 | 0.986 | 0.9095 | 0.9854 | 0.8995 | 0.995 | 0.9633 | 0.9774 | 0.9437 | 0.9855 | 0.9329 | 0.9869 | 0.9542 | 0.9875 | 0.9424 | 0.9865 | 0.9344 | 1.0026 | 0.993 | 0.9848 | 0.9599 | 0.9839 | 0.9351 | 0.982 | 0.9575 | 0.9774 | 0.9448 | 0.9852 | 0.9367 | 0.991 | 0.9861 | 0.9822 | 0.9727
341344 | 2COOPER | 320 | 69 | EXT_B-69-25_SRT-A | N1 | 0.9 | 1.06 | 0.9846 | 0.9475 | 0.9749 | 0.9658 | 0.9843 | 0.9551 | 0.9857 | 0.9489 | 0.9822 | 0.979 | 0.9755 | 0.9626 | 0.9822 | 0.8763 | 0.9875 | 0.896 | 0.979 | 0.8891 | 0.9833 | 0.8775 | 0.9862 | 0.9445 | 0.9688 | 0.9268 | 0.9773 | 0.9146 | 0.9797 | 0.9357 | 0.9792 | 0.9243 | 0.9781 | 0.9155 | 0.9923 | 0.9785 | 0.9767 | 0.9574 | 0.9863 | 0.9169 | 0.9883 | 0.9396 | 0.9856 | 0.9269 | 0.9875 | 0.9184 | 0.98 | 0.9675 | 0.9754 | 0.9598
341347 | 2COOPER DIST | 320 | 69 | EXT_324130 5ALCALDE 161 324141 5ELIHU 161 1 _SRT-A | N1 | 0.9 | 1.06 | 0.9865 | 0.9632 | 0.9905 | 0.9687 | 0.9821 | 0.9585 | 0.981 | 0.9646 | 0.9929 | 0.9937 | 0.9825 | 0.9642 | 0.9935 | 0.8983 | 0.9903 | 0.917 | 0.986 | 0.9095 | 0.9855 | 0.8995 | 0.995 | 0.9633 | 0.9774 | 0.9437 | 0.9855 | 0.9329 | 0.9869 | 0.9542 | 0.9875 | 0.9424 | 0.9865 | 0.9344 | 1.0026 | 0.993 | 0.9848 | 0.9599 | 0.9839 | 0.9351 | 0.982 | 0.9575 | 0.9774 | 0.9448 | 0.9852 | 0.9367 | 0.9909 | 0.9861 | 0.9822 | 0.9727
341347 | 2COOPER DIST | 320 | 69 | EXT_B-69-25_SRT-A | N1 | 0.9 | 1.06 | 0.9846 | 0.9475 | 0.9749 | 0.9658 | 0.9843 | 0.9551 | 0.9857 | 0.9489 | 0.9822 | 0.979 | 0.9756 | 0.9626 | 0.9822 | 0.8763 | 0.9875 | 0.896 | 0.9791 | 0.8891 | 0.9834 | 0.8775 | 0.9862 | 0.9445 | 0.9688 | 0.9268 | 0.9773 | 0.9146 | 0.9797 | 0.9357 | 0.9792 | 0.9243 | 0.9781 | 0.9155 | 0.9923 | 0.9785 | 0.9767 | 0.9574 | 0.9863 | 0.9169 | 0.9883 | 0.9396 | 0.9857 | 0.9269 | 0.9875 | 0.9184 | 0.98 | 0.9675 | 0.9754 | 0.9598
341350 | 2CRESTON | 320 | 69 | EXT_324130 5ALCALDE 161 324141 5ELIHU 161 1 _SRT-A | N1 | 0.9 | 1.06 | 0.9966 | 0.9621 | 0.9855 | 0.9643 | 0.977 | 0.9558 | 0.976 | 0.9633 | 0.9779 | 0.9789 | 0.9718 | 0.948 | 1.0077 | 0.8917 | 1.0051 | 0.9096 | 1.0022 | 0.9029 | 1.0011 | 0.8926 | 0.9773 | 0.9528 | 0.9708 | 0.9524 | 0.9962 | 0.9292 | 0.9754 | 0.9488 | 0.9979 | 0.9386 | 0.9968 | 0.9304 | 0.9809 | 0.9837 | 0.9776 | 0.9486 | 0.995 | 0.9311 | 0.9893 | 0.9516 | 0.9734 | 0.9408 | 0.9959 | 0.9324 | 0.9768 | 0.9752 | 0.976 | 0.9794
341350 | 2CRESTON | 320 | 69 | EXT_B-345-100_SRT-A | N1 | 0.9 | 1.06 | 0.994 | 0.9562 | 1.0012 | 0.9691 | 0.9742 | 0.9622 | 0.9945 | 0.9568 | 0.9742 | 0.9726 | 0.9702 | 0.9524 | 0.9965 | 0.8927 | 1.008 | 0.9066 | 0.9961 | 0.9017 | 0.9993 | 0.8935 | 0.9737 | 0.9452 | 0.9692 | 0.9485 | 0.9933 | 0.9255 | 0.9831 | 0.9416 | 0.9949 | 0.9337 | 0.9939 | 0.9265 | 0.9758 | 0.9759 | 0.9759 | 0.9742 | 0.9905 | 0.9296 | 1.0025 | 0.9428 | 0.9929 | 0.9354 | 0.9913 | 0.9306 | 0.9725 | 0.9626 | 0.9737 | 0.9752
341350 | 2CRESTON | 320 | 69 | EXT_B-69-25_SRT-A | N1 | 0.9 | 1.06 | 0.9888 | 0.9493 | 0.9855 | 0.9655 | 0.9902 | 0.9567 | 0.9895 | 0.9503 | 0.9709 | 0.9681 | 0.97 | 0.9639 | 0.9931 | 0.8724 | 0.9974 | 0.8912 | 0.987 | 0.8854 | 0.9939 | 0.8735 | 0.9718 | 0.9376 | 0.9651 | 0.9383 | 0.9906 | 0.9137 | 0.9757 | 0.9331 | 0.9923 | 0.9234 | 0.9911 | 0.9144 | 0.9741 | 0.9729 | 0.9723 | 0.9679 | 0.9909 | 0.9158 | 0.9998 | 0.9364 | 0.9913 | 0.9258 | 0.9917 | 0.917 | 0.9697 | 0.96 | 0.9744 | 0.9662
341422 | 2E SOMERSET | 320 | 69 | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-A | N1 | 0.9 | 1.06 | 0.963 | 0.947 | 0.9721 | 0.9504 | 0.9629 | 0.9429 | 0.9639 | 0.9482 | 0.9743 | 0.9724 | 0.9662 | 0.949 | 0.9863 | 0.8949 | 0.9654 | 0.9084 | 0.9867 | 0.9032 | 0.9867 | 0.8958 | 0.9749 | 0.9453 | 0.9615 | 0.9337 | 0.9701 | 0.9219 | 0.97 | 0.938 | 0.9718 | 0.9293 | 0.9709 | 0.923 | 0.9822 | 0.9717 | 0.97 | 0.9456 | 0.9669 | 0.9211 | 0.9782 | 0.9384 | 0.9607 | 0.9288 | 0.9678 | 0.9224 | 0.9724 | 0.9616 | 0.9659 | 0.9461
341422 | 2E SOMERSET | 320 | 69 | EXT_324130 5ALCALDE 161 324141 5ELIHU 161 1 _SRT-A | N1 | 0.9 | 1.06 | 0.9708 | 0.9467 | 0.9736 | 0.9519 | 0.9658 | 0.9421 | 0.9648 | 0.9482 | 0.9771 | 0.9761 | 0.9671 | 0.9495 | 0.9863 | 0.882 | 0.9738 | 0.9006 | 0.97 | 0.8931 | 0.9693 | 0.8831 | 0.9768 | 0.9461 | 0.9619 | 0.9303 | 0.9715 | 0.9164 | 0.9714 | 0.9371 | 0.9735 | 0.9258 | 0.9724 | 0.9178 | 0.9859 | 0.975 | 0.9713 | 0.9449 | 0.9684 | 0.9179 | 0.9672 | 0.9396 | 0.9614 | 0.9274 | 0.9695 | 0.9195 | 0.9753 | 0.9675 | 0.9671 | 0.9574
341422 | 2E SOMERSET | 320 | 69 | EXT_B-345-100_SRT-A | N1 | 0.9 | 1.06 | 0.9667 | 0.9404 | 0.9762 | 0.9548 | 0.9617 | 0.9465 | 0.9675 | 0.9413 | 0.9717 | 0.9682 | 0.9639 | 0.9482 | 0.9863 | 0.884 | 0.987 | 0.8985 | 0.9806 | 0.8929 | 0.9867 | 0.885 | 0.9714 | 0.9382 | 0.9588 | 0.9264 | 0.9673 | 0.9135 | 0.9693 | 0.9307 | 0.9691 | 0.9216 | 0.9681 | 0.9146 | 0.9792 | 0.9664 | 0.9678 | 0.9514 | 0.9626 | 0.916 | 0.9756 | 0.9312 | 0.9652 | 0.9222 | 0.9636 | 0.9173 | 0.9693 | 0.9545 | 0.9629 | 0.9514
341422 | 2E SOMERSET | 320 | 69 | EXT_B-69-25_SRT-A | N1 | 0.9 | 1.06 | 0.972 | 0.9269 | 0.957 | 0.9443 | 0.9722 | 0.9343 | 0.973 | 0.9282 | 0.963 | 0.9568 | 0.9571 | 0.9436 | 0.9721 | 0.8552 | 0.9769 | 0.8747 | 0.9692 | 0.8681 | 0.9732 | 0.8564 | 0.9646 | 0.9226 | 0.9504 | 0.909 | 0.9604 | 0.8935 | 0.9613 | 0.914 | 0.9623 | 0.9032 | 0.9612 | 0.8945 | 0.9724 | 0.956 | 0.9602 | 0.9386 | 0.9799 | 0.8952 | 0.9686 | 0.9171 | 0.9759 | 0.9052 | 0.9799 | 0.8967 | 0.961 | 0.9444 | 0.9573 | 0.9403
341470 | 2FLOYD EK | 320 | 69 | EXT_324130 5ALCALDE 161 324141 5ELIHU 161 1 _SRT-A | N1 | 0.9 | 1.06 | 0.9756 | 0.9611 | 0.9776 | 0.966 | 0.9697 | 0.9564 | 0.9687 | 0.9626 | 0.9815 | 0.9913 | 0.9723 | 0.9664 | 0.9988 | 0.896 | 0.9784 | 0.9145 | 0.9747 | 0.9073 | 0.974 | 0.8971 | 0.9807 | 0.9611 | 0.9673 | 0.9487 | 0.9749 | 0.9302 | 0.9735 | 0.9509 | 0.9769 | 0.9397 | 0.9758 | 0.9317 | 0.9878 | 0.9897 | 0.9751 | 0.9613 | 0.9731 | 0.9317 | 0.9718 | 0.9535 | 0.9651 | 0.9415 | 0.9742 | 0.9334 | 0.9796 | 0.982 | 0.9724 | 0.9743
341470 | 2FLOYD EK | 320 | 69 | EXT_B-345-100_SRT-A | N1 | 0.9 | 1.06 | 0.9717 | 0.9549 | 0.9809 | 0.9694 | 0.9658 | 0.9611 | 0.9724 | 0.9559 | 0.9765 | 0.9835 | 0.9694 | 0.9649 | 0.9987 | 0.898 | 1.0058 | 0.9126 | 0.9944 | 0.9071 | 1.0018 | 0.899 | 0.9755 | 0.9532 | 0.9645 | 0.9448 | 0.9708 | 0.9273 | 0.9718 | 0.9446 | 0.9726 | 0.9355 | 0.9716 | 0.9285 | 0.9813 | 0.9812 | 0.9721 | 0.9689 | 0.9674 | 0.9299 | 0.9804 | 0.9452 | 0.97 | 0.9363 | 0.9683 | 0.9313 | 0.9738 | 0.969 | 0.9687 | 0.969
341470 | 2FLOYD EK | 320 | 69 | EXT_B-69-25_SRT-A | N1 | 0.9 | 1.06 | 0.9929 | 0.9495 | 0.9687 | 0.9672 | 0.9933 | 0.9571 | 0.994 | 0.9509 | 0.9754 | 0.9813 | 0.9687 | 0.9682 | 0.9881 | 0.8783 | 0.9968 | 0.8978 | 0.9886 | 0.8912 | 0.9886 | 0.8795 | 0.976 | 0.9471 | 0.9624 | 0.936 | 0.9702 | 0.9161 | 0.9704 | 0.9367 | 0.9722 | 0.9259 | 0.9709 | 0.9171 | 0.9818 | 0.9798 | 0.9707 | 0.9641 | 0.9954 | 0.9177 | 0.9799 | 0.9398 | 0.9954 | 0.9279 | 0.9966 | 0.9193 | 0.9732 | 0.9681 | 0.969 | 0.9658
341506 | 2GAP OF RIDG | 320 | 69 | EXT_B-69-25_SRT-A | N1 | 0.9 | 1.06 | 1.0078 | 0.9708 | 0.9893 | 0.9859 | 1.0059 | 0.9944 | 1.0049 | 0.969 | 0.9815 | 0.994 | 0.9935 | 0.9813 | 1.0018 | 0.8955 | 1.0095 | 0.9129 | 1.0019 | 0.926 | 0.9999 | 0.8972 | 1.0046 | 0.9519 | 0.9946 | 0.9367 | 0.9931 | 0.9379 | 0.9974 | 0.9557 | 1.0056 | 0.9656 | 0.9928 | 0.9359 | 1.0038 | 0.9919 | 0.9938 | 0.9743 | 1.0086 | 0.9428 | 1.0143 | 0.9622 | 1.0078 | 0.9711 | 1.0056 | 0.9403 | 0.9798 | 0.9829 | 0.9927 | 0.9797
341509 | 2GARLIN | 320 | 69 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | N1 | 0.9 | 1.06 | 0.9871 | 0.9192 | 0.9911 | 0.9315 | 0.9885 | 0.9229 | 0.9872 | 0.9201 | 0.9829 | 0.9457 | 0.9889 | 0.924 | 0.9777 | 0.9197 | 0.9779 | 0.9245 | 0.9782 | 0.9236 | 0.9783 | 0.9203 | 0.9631 | 0.9498 | 0.9791 | 0.9405 | 0.9828 | 0.9027 | 0.9834 | 0.9199 | 0.983 | 0.9076 | 0.9829 | 0.9039 | 0.984 | 0.9342 | 0.9776 | 0.9298 | 1.0077 | 0.8912 | 0.9867 | 0.9095 | 1.0064 | 0.8961 | 1.0082 | 0.8927 | 0.9789 | 0.9223 | 0.9882 | 0.9227
341509 | 2GARLIN | 320 | 69 | EXT_324130 5ALCALDE 161 324141 5ELIHU 161 1 _SRT-A | N1 | 0.9 | 1.06 | 0.9805 | 0.9812 | 0.9817 | 0.9731 | 0.9744 | 0.9691 | 0.974 | 0.9819 | 0.9588 | 0.9777 | 0.9552 | 0.959 | 1.0016 | 0.8973 | 0.9979 | 0.9105 | 0.9973 | 0.9078 | 0.9961 | 0.8981 | 0.9704 | 0.9536 | 0.9718 | 0.9452 | 0.9828 | 0.9433 | 0.9774 | 0.957 | 0.983 | 0.9518 | 0.9829 | 0.9441 | 0.9833 | 0.9915 | 0.9791 | 0.9684 | 0.9789 | 0.9521 | 0.9748 | 0.9665 | 0.9703 | 0.9609 | 0.9795 | 0.9529 | 0.9579 | 0.9854 | 0.9558 | 0.9891
341509 | 2GARLIN | 320 | 69 | EXT_B-345-100_SRT-A | N1 | 0.9 | 1.06 | 0.9789 | 0.9763 | 0.9825 | 0.9838 | 0.9723 | 0.9818 | 0.9791 | 0.9766 | 0.9566 | 0.9737 | 0.954 | 0.9771 | 0.9898 | 0.899 | 0.9961 | 0.9084 | 0.9782 | 0.9074 | 0.9935 | 0.8998 | 0.9686 | 0.947 | 0.9699 | 0.9421 | 0.9828 | 0.9406 | 0.9777 | 0.9511 | 0.983 | 0.9481 | 0.9829 | 0.9413 | 0.9802 | 0.9858 | 0.9777 | 0.9746 | 0.9751 | 0.9508 | 0.9865 | 0.9588 | 0.977 | 0.9565 | 0.9756 | 0.9514 | 0.955 | 0.9747 | 0.9533 | 0.9891
341509 | 2GARLIN | 320 | 69 | EXT_B-69-25_SRT-A | N1 | 0.9 | 1.06 | 0.973 | 0.9707 | 0.9717 | 0.9817 | 0.977 | 0.9774 | 0.9734 | 0.9715 | 0.9543 | 0.97 | 0.9712 | 0.9771 | 0.9777 | 0.8805 | 0.9833 | 0.8949 | 0.9712 | 0.8928 | 0.9783 | 0.8816 | 0.968 | 0.941 | 0.9676 | 0.9336 | 0.9828 | 0.9304 | 0.9755 | 0.9442 | 0.983 | 0.9392 | 0.9829 | 0.9308 | 0.9787 | 0.9837 | 0.9756 | 0.9746 | 0.9775 | 0.9393 | 0.9848 | 0.954 | 0.9782 | 0.9484 | 0.9779 | 0.9401 | 0.9532 | 0.9729 | 0.9721 | 0.9823
341641 | 2HOMESTEAD S | 320 | 69 | EXT_B-69-25_SRT-A | N1 | 0.9 | 1.06 | 1.0119 | 0.9746 | 0.9926 | 0.9876 | 1.0062 | 1.0019 | 1.008 | 0.972 | 0.9856 | 0.996 | 0.9961 | 0.9844 | 1.0057 | 0.8978 | 1.0117 | 0.9136 | 1.0066 | 0.9323 | 1.003 | 0.8996 | 1.0075 | 0.9529 | 0.9989 | 0.9384 | 0.9958 | 0.9417 | 0.999 | 0.9574 | 1.0107 | 0.9736 | 0.9951 | 0.9391 | 1.0053 | 0.994 | 0.9965 | 0.9773 | 1.0127 | 0.9469 | 1.0176 | 0.964 | 1.0123 | 0.9795 | 1.0086 | 0.9436 | 0.9841 | 0.9851 | 0.9954 | 0.9831
341938 | 2NANCY | 320 | 69 | EXT_324130 5ALCALDE 161 324141 5ELIHU 161 1 _SRT-A | N1 | 0.9 | 1.06 | 0.9911 | 0.9589 | 0.9859 | 0.962 | 0.9781 | 0.9528 | 0.9771 | 0.9602 | 0.9843 | 0.9806 | 0.9751 | 0.9514 | 0.9955 | 0.8876 | 0.9962 | 0.9059 | 0.9959 | 0.899 | 0.9907 | 0.8887 | 0.985 | 0.9522 | 0.9726 | 0.9389 | 0.9867 | 0.9262 | 0.981 | 0.9466 | 0.9935 | 0.9358 | 0.9875 | 0.9275 | 0.9925 | 0.9846 | 0.9804 | 0.9514 | 0.988 | 0.929 | 0.9821 | 0.9505 | 0.9737 | 0.9389 | 0.988 | 0.9305 | 0.9827 | 0.9772 | 0.9762 | 0.9706
341938 | 2NANCY | 320 | 69 | EXT_B-345-100_SRT-A | N1 | 0.9 | 1.06 | 0.9837 | 0.953 | 0.9938 | 0.9668 | 0.9746 | 0.9592 | 0.9843 | 0.9538 | 0.9797 | 0.9736 | 0.9725 | 0.9555 | 0.9955 | 0.8901 | 0.9962 | 0.9043 | 0.9878 | 0.8993 | 0.996 | 0.891 | 0.9804 | 0.9446 | 0.9699 | 0.9354 | 0.9832 | 0.9236 | 0.9807 | 0.9404 | 0.9849 | 0.9319 | 0.984 | 0.9247 | 0.9866 | 0.9767 | 0.9776 | 0.9639 | 0.9796 | 0.9276 | 0.9911 | 0.9422 | 0.9822 | 0.934 | 0.9805 | 0.9288 | 0.9775 | 0.9644 | 0.9726 | 0.9654
341938 | 2NANCY | 320 | 69 | EXT_B-69-25_SRT-A | N1 | 0.9 | 1.06 | 0.9783 | 0.9374 | 0.9706 | 0.9545 | 0.9789 | 0.945 | 0.9792 | 0.9386 | 0.9691 | 0.9599 | 0.9663 | 0.9529 | 0.9789 | 0.8589 | 0.9836 | 0.8783 | 0.975 | 0.8722 | 0.9799 | 0.8601 | 0.972 | 0.927 | 0.9601 | 0.9159 | 0.9746 | 0.9016 | 0.9711 | 0.9218 | 0.9764 | 0.9115 | 0.9753 | 0.9023 | 0.9779 | 0.9642 | 0.9683 | 0.949 | 0.9806 | 0.9046 | 0.984 | 0.9262 | 0.9805 | 0.9148 | 0.9816 | 0.9059 | 0.9673 | 0.9522 | 0.9676 | 0.9521
341947 | 2NELSON VAL | 320 | 69 | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-A | N1 | 0.9 | 1.06 | 0.9613 | 0.9466 | 0.9705 | 0.9499 | 0.9611 | 0.9424 | 0.9622 | 0.9478 | 0.9729 | 0.9724 | 0.9651 | 0.9494 | 0.9841 | 0.8941 | 0.964 | 0.9077 | 0.9845 | 0.9025 | 0.9846 | 0.895 | 0.9733 | 0.945 | 0.9604 | 0.9345 | 0.9683 | 0.9211 | 0.9678 | 0.9374 | 0.97 | 0.9286 | 0.969 | 0.9223 | 0.9801 | 0.9715 | 0.9685 | 0.9459 | 0.9654 | 0.9204 | 0.9814 | 0.9378 | 0.9589 | 0.9281 | 0.9663 | 0.9217 | 0.971 | 0.9613 | 0.9648 | 0.9467
341947 | 2NELSON VAL | 320 | 69 | EXT_324130 5ALCALDE 161 324141 5ELIHU 161 1 _SRT-A | N1 | 0.9 | 1.06 | 0.9694 | 0.9463 | 0.972 | 0.9515 | 0.9641 | 0.9416 | 0.9631 | 0.9477 | 0.9756 | 0.9761 | 0.9659 | 0.95 | 0.9841 | 0.8811 | 0.9723 | 0.8998 | 0.9685 | 0.8923 | 0.9678 | 0.8822 | 0.9752 | 0.9459 | 0.9608 | 0.9311 | 0.9697 | 0.9156 | 0.9693 | 0.9365 | 0.9716 | 0.9251 | 0.9706 | 0.9171 | 0.9838 | 0.9748 | 0.9698 | 0.9451 | 0.9669 | 0.9171 | 0.9657 | 0.939 | 0.9596 | 0.9268 | 0.968 | 0.9188 | 0.9738 | 0.9672 | 0.966 | 0.9579
341947 | 2NELSON VAL | 320 | 69 | EXT_B-345-100_SRT-A | N1 | 0.9 | 1.06 | 0.9653 | 0.94 | 0.9748 | 0.9546 | 0.9601 | 0.9461 | 0.9661 | 0.9409 | 0.9704 | 0.9682 | 0.9629 | 0.9486 | 0.9841 | 0.8832 | 0.993 | 0.8978 | 0.9845 | 0.8921 | 0.9846 | 0.8841 | 0.9698 | 0.938 | 0.9578 | 0.9271 | 0.9655 | 0.9127 | 0.9673 | 0.9301 | 0.9672 | 0.9209 | 0.9663 | 0.9139 | 0.9772 | 0.9662 | 0.9664 | 0.9521 | 0.9611 | 0.9153 | 0.9742 | 0.9306 | 0.9637 | 0.9216 | 0.9621 | 0.9166 | 0.9678 | 0.9542 | 0.9619 | 0.9521
341947 | 2NELSON VAL | 320 | 69 | EXT_B-69-25_SRT-A | N1 | 0.9 | 1.06 | 0.9752 | 0.9291 | 0.9578 | 0.9468 | 0.9755 | 0.9366 | 0.9763 | 0.9304 | 0.9641 | 0.9598 | 0.958 | 0.9466 | 0.975 | 0.8572 | 0.9848 | 0.8768 | 0.9721 | 0.8701 | 0.9761 | 0.8584 | 0.9653 | 0.9254 | 0.9514 | 0.9125 | 0.9606 | 0.8956 | 0.9614 | 0.9163 | 0.9625 | 0.9053 | 0.9614 | 0.8965 | 0.9727 | 0.9588 | 0.9609 | 0.9418 | 0.9779 | 0.8973 | 0.9693 | 0.9194 | 0.9791 | 0.9073 | 0.9779 | 0.8988 | 0.962 | 0.9471 | 0.9582 | 0.9435
341971 | 2NORWOOD | 320 | 69 | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-A | N1 | 0.9 | 1.06 | 0.963 | 0.9516 | 0.9723 | 0.9549 | 0.9627 | 0.9474 | 0.9639 | 0.9528 | 0.9748 | 0.9776 | 0.9672 | 0.955 | 0.9905 | 0.8992 | 0.9659 | 0.9127 | 0.9858 | 0.9075 | 0.9916 | 0.9001 | 0.975 | 0.9502 | 0.9625 | 0.9404 | 0.9698 | 0.9261 | 0.9692 | 0.9423 | 0.9716 | 0.9336 | 0.9706 | 0.9273 | 0.9814 | 0.9766 | 0.9703 | 0.9514 | 0.9672 | 0.9254 | 0.9829 | 0.9428 | 0.9606 | 0.9331 | 0.9681 | 0.9267 | 0.9728 | 0.9664 | 0.9669 | 0.9524
341971 | 2NORWOOD | 320 | 69 | EXT_324130 5ALCALDE 161 324141 5ELIHU 161 1 _SRT-A | N1 | 0.9 | 1.06 | 0.9712 | 0.9513 | 0.9737 | 0.9565 | 0.9658 | 0.9466 | 0.9648 | 0.9528 | 0.9775 | 0.9812 | 0.968 | 0.9556 | 0.9854 | 0.8862 | 0.9741 | 0.9048 | 0.9703 | 0.8974 | 0.9697 | 0.8873 | 0.9769 | 0.9511 | 0.9629 | 0.937 | 0.9713 | 0.9206 | 0.9706 | 0.9414 | 0.9732 | 0.93 | 0.9722 | 0.9221 | 0.9851 | 0.9799 | 0.9716 | 0.9507 | 0.9688 | 0.9221 | 0.9676 | 0.944 | 0.9613 | 0.9318 | 0.9699 | 0.9238 | 0.9756 | 0.9723 | 0.9681 | 0.9635
341971 | 2NORWOOD | 320 | 69 | EXT_B-345-100_SRT-A | N1 | 0.9 | 1.06 | 0.9672 | 0.9451 | 0.9767 | 0.9596 | 0.9618 | 0.9512 | 0.968 | 0.946 | 0.9723 | 0.9734 | 0.965 | 0.9542 | 0.9854 | 0.8883 | 0.9965 | 0.9029 | 0.9858 | 0.8973 | 0.9926 | 0.8892 | 0.9716 | 0.9432 | 0.9599 | 0.9331 | 0.9671 | 0.9177 | 0.9688 | 0.9351 | 0.9689 | 0.9259 | 0.9679 | 0.9189 | 0.9786 | 0.9713 | 0.9683 | 0.9578 | 0.963 | 0.9203 | 0.9761 | 0.9356 | 0.9656 | 0.9266 | 0.964 | 0.9216 | 0.9697 | 0.9593 | 0.9641 | 0.9578
341971 | 2NORWOOD | 320 | 69 | EXT_B-69-25_SRT-A | N1 | 0.9 | 1.06 | 0.9831 | 0.9361 | 0.9612 | 0.9538 | 0.9842 | 0.9436 | 0.9829 | 0.9374 | 0.9677 | 0.9671 | 0.9616 | 0.954 | 0.9799 | 0.8644 | 0.9861 | 0.884 | 0.977 | 0.8773 | 0.9859 | 0.8656 | 0.9687 | 0.9328 | 0.955 | 0.9204 | 0.9637 | 0.9026 | 0.9644 | 0.9233 | 0.9656 | 0.9123 | 0.9644 | 0.9035 | 0.9757 | 0.9659 | 0.9641 | 0.9494 | 0.9794 | 0.9043 | 0.9727 | 0.9264 | 0.9806 | 0.9143 | 0.9849 | 0.9058 | 0.9656 | 0.9543 | 0.9618 | 0.9511
341977 | 2OAK HILL | 320 | 69 | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-A | N1 | 0.9 | 1.06 | 0.9725 | 0.9543 | 0.9818 | 0.9569 | 0.972 | 0.9495 | 0.9734 | 0.9554 | 0.9823 | 0.9777 | 0.9738 | 0.9519 | 0.9903 | 0.8999 | 0.9758 | 0.9131 | 0.9869 | 0.9082 | 0.9913 | 0.9008 | 0.9841 | 0.9507 | 0.97 | 0.9379 | 0.979 | 0.9284 | 0.9778 | 0.9444 | 0.9807 | 0.9359 | 0.9798 | 0.9295 | 0.9898 | 0.9788 | 0.9768 | 0.9502 | 0.9771 | 0.9284 | 0.9924 | 0.9456 | 0.9699 | 0.9361 | 0.978 | 0.9296 | 0.9804 | 0.969 | 0.9735 | 0.9519
341977 | 2OAK HILL | 320 | 69 | EXT_324130 5ALCALDE 161 324141 5ELIHU 161 1 _SRT-A | N1 | 0.9 | 1.06 | 0.9811 | 0.9538 | 0.9832 | 0.9582 | 0.9751 | 0.9485 | 0.9742 | 0.9552 | 0.985 | 0.9813 | 0.9746 | 0.9523 | 0.9899 | 0.8863 | 0.986 | 0.9047 | 0.9821 | 0.8975 | 0.9815 | 0.8874 | 0.9859 | 0.9514 | 0.9703 | 0.9341 | 0.9804 | 0.9224 | 0.9792 | 0.9432 | 0.9823 | 0.9319 | 0.9813 | 0.9239 | 0.9936 | 0.9821 | 0.978 | 0.9492 | 0.9786 | 0.9248 | 0.9766 | 0.9466 | 0.9705 | 0.9345 | 0.9798 | 0.9264 | 0.9832 | 0.9749 | 0.9748 | 0.9641
341977 | 2OAK HILL | 320 | 69 | EXT_B-345-100_SRT-A | N1 | 0.9 | 1.06 | 0.9772 | 0.9479 | 0.9868 | 0.9622 | 0.9712 | 0.954 | 0.9779 | 0.9488 | 0.9798 | 0.9739 | 0.9716 | 0.9532 | 0.9877 | 0.8893 | 0.9971 | 0.9036 | 0.9828 | 0.8982 | 0.9908 | 0.8902 | 0.9806 | 0.9439 | 0.9673 | 0.9308 | 0.9764 | 0.9203 | 0.9777 | 0.9374 | 0.9781 | 0.9284 | 0.9773 | 0.9215 | 0.9871 | 0.9739 | 0.9748 | 0.9577 | 0.9729 | 0.9234 | 0.9863 | 0.9386 | 0.9755 | 0.9298 | 0.9738 | 0.9247 | 0.9773 | 0.9621 | 0.9706 | 0.9585
341977 | 2OAK HILL | 320 | 69 | EXT_B-69-25_SRT-A | N1 | 0.9 | 1.06 | 0.9721 | 0.9291 | 0.9624 | 0.9465 | 0.9721 | 0.9365 | 0.9731 | 0.9303 | 0.9662 | 0.9567 | 0.9615 | 0.9446 | 0.9712 | 0.8542 | 0.976 | 0.8736 | 0.9678 | 0.8672 | 0.9723 | 0.8554 | 0.9694 | 0.9224 | 0.955 | 0.9079 | 0.9656 | 0.8945 | 0.9654 | 0.9149 | 0.9673 | 0.9042 | 0.9663 | 0.8953 | 0.9756 | 0.9577 | 0.9631 | 0.9395 | 0.9743 | 0.897 | 0.9753 | 0.9189 | 0.9738 | 0.907 | 0.9754 | 0.8984 | 0.9641 | 0.9462 | 0.9618 | 0.9421
342067 | 2PHIL | 320 | 69 | EXT_B-69-25_SRT-A | N1 | 0.9 | 1.06 | 0.9928 | 0.9574 | 0.9895 | 0.9735 | 0.9941 | 0.9647 | 0.9935 | 0.9585 | 0.975 | 0.976 | 0.9741 | 0.9719 | 0.997 | 0.8813 | 1.0013 | 0.8999 | 0.991 | 0.8941 | 0.9978 | 0.8823 | 0.9759 | 0.9458 | 0.9692 | 0.9465 | 0.9946 | 0.9221 | 0.9797 | 0.9413 | 0.9963 | 0.9318 | 0.9951 | 0.9228 | 0.9781 | 0.9808 | 0.9764 | 0.9759 | 0.9949 | 0.9242 | 1.0038 | 0.9446 | 0.9953 | 0.9341 | 0.9957 | 0.9254 | 0.9737 | 0.968 | 0.9784 | 0.9742
342115 | 2PULASK CO | 320 | 69 | EXT_324130 5ALCALDE 161 324141 5ELIHU 161 1 _SRT-A | N1 | 0.9 | 1.06 | 0.9775 | 0.9644 | 0.9794 | 0.9693 | 0.9715 | 0.9596 | 0.9705 | 0.9659 | 0.9834 | 0.9944 | 0.9741 | 0.9696 | 1.0006 | 0.8995 | 0.9802 | 0.9179 | 0.9766 | 0.9107 | 0.9759 | 0.9006 | 0.9825 | 0.9643 | 0.9692 | 0.952 | 0.9768 | 0.9335 | 0.9753 | 0.9542 | 0.9788 | 0.943 | 0.9777 | 0.935 | 0.9896 | 0.9928 | 0.977 | 0.9645 | 0.9749 | 0.9351 | 0.9737 | 0.9568 | 0.967 | 0.9448 | 0.976 | 0.9367 | 0.9814 | 0.9851 | 0.9743 | 0.9775
342115 | 2PULASK CO | 320 | 69 | EXT_B-69-25_SRT-A | N1 | 0.9 | 1.06 | 0.9947 | 0.9528 | 0.9706 | 0.9705 | 0.9952 | 0.9604 | 0.9959 | 0.9542 | 0.9773 | 0.9845 | 0.9706 | 0.9714 | 0.99 | 0.8819 | 0.9986 | 0.9013 | 0.9904 | 0.8947 | 0.9905 | 0.8831 | 0.9778 | 0.9503 | 0.9643 | 0.9393 | 0.9721 | 0.9195 | 0.9723 | 0.94 | 0.974 | 0.9293 | 0.9728 | 0.9205 | 0.9837 | 0.983 | 0.9725 | 0.9674 | 0.9972 | 0.9212 | 0.9817 | 0.9431 | 0.9972 | 0.9312 | 0.9984 | 0.9227 | 0.9751 | 0.9713 | 0.9709 | 0.969
342172 | 2RUSS SPR EK | 320 | 69 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | N1 | 0.9 | 1.06 | 0.9926 | 0.924 | 0.9973 | 0.9369 | 0.9941 | 0.9277 | 0.9927 | 0.925 | 0.9993 | 0.9541 | 0.9942 | 0.9278 | 0.9901 | 0.9233 | 0.9903 | 0.9294 | 0.9906 | 0.9274 | 0.9906 | 0.9241 | 0.9645 | 0.9561 | 0.9913 | 0.9445 | 0.9936 | 0.907 | 1.0017 | 0.9251 | 0.9989 | 0.912 | 0.9937 | 0.9084 | 1.0006 | 0.9423 | 0.9899 | 0.936 | 1.0147 | 0.8947 | 0.9927 | 0.9139 | 1.013 | 0.8996 | 1.0152 | 0.8964 | 0.9903 | 0.9294 | 0.994 | 0.9286
342172 | 2RUSS SPR EK | 320 | 69 | EXT_B-69-25_SRT-A | N1 | 0.9 | 1.06 | 0.9851 | 0.986 | 0.9861 | 0.998 | 0.9855 | 0.993 | 0.9851 | 0.9868 | 0.9768 | 0.9786 | 0.9848 | 0.9964 | 0.9901 | 0.8956 | 0.9903 | 0.9106 | 0.9817 | 0.9079 | 0.9906 | 0.8967 | 0.9787 | 0.957 | 0.9743 | 0.9481 | 0.9936 | 0.9482 | 0.9853 | 0.9629 | 0.9939 | 0.9572 | 0.9937 | 0.9486 | 0.9888 | 1.0032 | 0.9843 | 0.9912 | 0.9899 | 0.9549 | 0.9943 | 0.9707 | 0.9902 | 0.9643 | 0.9904 | 0.9558 | 0.9759 | 0.9924 | 0.9855 | 0.9981
342193 | 2S FLOYD | 320 | 69 | EXT_324130 5ALCALDE 161 324141 5ELIHU 161 1 _SRT-A | N1 | 0.9 | 1.06 | 0.9773 | 0.9642 | 0.9793 | 0.969 | 0.9714 | 0.9594 | 0.9704 | 0.9656 | 0.9832 | 0.9942 | 0.974 | 0.9694 | 1.0005 | 0.8992 | 0.9801 | 0.9177 | 0.9764 | 0.9105 | 0.9757 | 0.9004 | 0.9824 | 0.9641 | 0.969 | 0.9518 | 0.9767 | 0.9333 | 0.9752 | 0.9539 | 0.9786 | 0.9428 | 0.9775 | 0.9348 | 0.9895 | 0.9926 | 0.9768 | 0.9643 | 0.9748 | 0.9348 | 0.9735 | 0.9566 | 0.9668 | 0.9445 | 0.9759 | 0.9365 | 0.9813 | 0.9849 | 0.9741 | 0.9773
342193 | 2S FLOYD | 320 | 69 | EXT_B-69-25_SRT-A | N1 | 0.9 | 1.06 | 0.9945 | 0.9526 | 0.9704 | 0.9702 | 0.995 | 0.9602 | 0.9957 | 0.954 | 0.9771 | 0.9842 | 0.9705 | 0.9712 | 0.9898 | 0.8816 | 0.9985 | 0.901 | 0.9903 | 0.8945 | 0.9903 | 0.8828 | 0.9777 | 0.9501 | 0.9642 | 0.9391 | 0.9719 | 0.9192 | 0.9721 | 0.9398 | 0.9739 | 0.929 | 0.9727 | 0.9202 | 0.9835 | 0.9828 | 0.9724 | 0.9671 | 0.997 | 0.9209 | 0.9816 | 0.9429 | 0.9971 | 0.931 | 0.9983 | 0.9225 | 0.975 | 0.9711 | 0.9707 | 0.9688
342214 | 2SALEM EK | 320 | 69 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | N1 | 0.9 | 1.06 | 0.9798 | 0.9243 | 0.9875 | 0.9371 | 0.9805 | 0.9281 | 0.9798 | 0.9254 | 0.9884 | 0.9537 | 0.9794 | 0.926 | 0.9856 | 0.9234 | 0.9861 | 0.9298 | 0.9861 | 0.9274 | 0.9861 | 0.9242 | 0.9729 | 0.9554 | 0.9864 | 0.944 | 0.9913 | 0.9079 | 0.9955 | 0.9258 | 0.9926 | 0.9129 | 0.9919 | 0.9094 | 0.9898 | 0.9428 | 0.9812 | 0.9371 | 1.0059 | 0.8958 | 0.9797 | 0.9147 | 1.005 | 0.9007 | 1.0064 | 0.8975 | 0.9867 | 0.93 | 0.9806 | 0.9301
342214 | 2SALEM EK | 320 | 69 | EXT_324130 5ALCALDE 161 324141 5ELIHU 161 1 _SRT-A | N1 | 0.9 | 1.06 | 0.9869 | 0.9716 | 0.9815 | 0.9699 | 0.9805 | 0.9631 | 0.9798 | 0.9726 | 0.975 | 0.977 | 0.9686 | 0.9516 | 1.0056 | 0.8918 | 1.0023 | 0.9081 | 1.0003 | 0.903 | 0.9991 | 0.8927 | 0.9763 | 0.9529 | 0.9704 | 0.9439 | 0.986 | 0.9365 | 0.9784 | 0.9541 | 0.9865 | 0.9458 | 0.9861 | 0.9375 | 0.9857 | 0.9902 | 0.979 | 0.9604 | 0.9853 | 0.9415 | 0.9797 | 0.96 | 0.9728 | 0.9511 | 0.9861 | 0.9426 | 0.974 | 0.9832 | 0.9704 | 0.9831
342214 | 2SALEM EK | 320 | 69 | EXT_B-345-100_SRT-A | N1 | 0.9 | 1.06 | 0.9798 | 0.9661 | 0.9906 | 0.9771 | 0.9741 | 0.9721 | 0.985 | 0.9666 | 0.9718 | 0.9717 | 0.9669 | 0.9651 | 0.9856 | 0.8936 | 0.9984 | 0.9059 | 0.9861 | 0.9027 | 0.9935 | 0.8945 | 0.973 | 0.9456 | 0.9684 | 0.9405 | 0.986 | 0.9336 | 0.9793 | 0.9477 | 0.9865 | 0.9417 | 0.9861 | 0.9344 | 0.9814 | 0.9834 | 0.9771 | 0.9701 | 0.9776 | 0.9401 | 0.9923 | 0.9518 | 0.9784 | 0.9463 | 0.9776 | 0.941 | 0.9701 | 0.9713 | 0.9675 | 0.9831
342214 | 2SALEM EK | 320 | 69 | EXT_B-69-25_SRT-A | N1 | 0.9 | 1.06 | 0.9798 | 0.957 | 0.9753 | 0.9716 | 0.9805 | 0.9644 | 0.9798 | 0.958 | 0.9668 | 0.9647 | 0.9698 | 0.9724 | 0.9856 | 0.8706 | 0.9861 | 0.888 | 0.9763 | 0.8836 | 0.9861 | 0.8717 | 0.9699 | 0.9357 | 0.9634 | 0.9281 | 0.9809 | 0.9191 | 0.9747 | 0.9367 | 0.9865 | 0.9288 | 0.9861 | 0.9197 | 0.9777 | 0.9779 | 0.9725 | 0.9701 | 0.9776 | 0.9243 | 0.9882 | 0.9431 | 0.9784 | 0.9343 | 0.983 | 0.9254 | 0.9656 | 0.9661 | 0.9718 | 0.9717
342232 | 2SEWELLTON | 320 | 69 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | N1 | 0.9 | 1.06 | 0.9891 | 0.9248 | 0.9935 | 0.9368 | 0.9905 | 0.9283 | 0.9891 | 0.9258 | 0.9983 | 0.955 | 0.991 | 0.9295 | 0.9881 | 0.9235 | 0.9892 | 0.9291 | 0.9885 | 0.9273 | 0.9887 | 0.9243 | 0.9743 | 0.9563 | 0.9895 | 0.944 | 0.9948 | 0.9082 | 0.9984 | 0.9253 | 0.9959 | 0.9128 | 0.9954 | 0.9096 | 0.9979 | 0.9436 | 0.9884 | 0.9365 | 1.0092 | 0.8962 | 0.9889 | 0.9143 | 1.0095 | 0.9008 | 1.0092 | 0.8978 | 0.9941 | 0.931 | 0.9905 | 0.9291
342256 | 2SHOPVILLE | 320 | 69 | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-A | N1 | 0.9 | 1.06 | 0.9645 | 0.9491 | 0.9731 | 0.9528 | 0.9645 | 0.9455 | 0.9653 | 0.9501 | 0.9754 | 0.9734 | 0.9676 | 0.9513 | 0.9868 | 0.8994 | 0.9659 | 0.9127 | 0.9796 | 0.9075 | 0.9872 | 0.9002 | 0.9751 | 0.9472 | 0.9625 | 0.9357 | 0.9739 | 0.9252 | 0.9743 | 0.9408 | 0.9756 | 0.9323 | 0.9746 | 0.9262 | 0.9858 | 0.9723 | 0.9742 | 0.9477 | 0.968 | 0.9237 | 0.9786 | 0.9405 | 0.9626 | 0.9311 | 0.9689 | 0.9249 | 0.9738 | 0.9622 | 0.9675 | 0.9473
342256 | 2SHOPVILLE | 320 | 69 | EXT_324130 5ALCALDE 161 324141 5ELIHU 161 1 _SRT-A | N1 | 0.9 | 1.06 | 0.9714 | 0.9489 | 0.9746 | 0.9545 | 0.9672 | 0.9449 | 0.9662 | 0.9502 | 0.978 | 0.9769 | 0.9686 | 0.952 | 0.9805 | 0.8875 | 0.9735 | 0.9057 | 0.9697 | 0.8982 | 0.9689 | 0.8885 | 0.9768 | 0.948 | 0.9629 | 0.9327 | 0.9752 | 0.9202 | 0.9758 | 0.9403 | 0.9771 | 0.9292 | 0.976 | 0.9216 | 0.9893 | 0.9754 | 0.9756 | 0.9472 | 0.9694 | 0.9209 | 0.9688 | 0.9418 | 0.9633 | 0.93 | 0.9704 | 0.9224 | 0.9765 | 0.9677 | 0.9687 | 0.9579
342256 | 2SHOPVILLE | 320 | 69 | EXT_B-345-100_SRT-A | N1 | 0.9 | 1.06 | 0.9673 | 0.942 | 0.9762 | 0.956 | 0.963 | 0.9479 | 0.9679 | 0.9428 | 0.9726 | 0.9685 | 0.9651 | 0.9496 | 0.9868 | 0.8881 | 0.9874 | 0.9024 | 0.9819 | 0.8967 | 0.9872 | 0.8889 | 0.9715 | 0.9397 | 0.9596 | 0.928 | 0.9708 | 0.9163 | 0.9732 | 0.933 | 0.9726 | 0.9241 | 0.9716 | 0.9173 | 0.9826 | 0.9664 | 0.9717 | 0.952 | 0.9636 | 0.9183 | 0.9758 | 0.9328 | 0.9661 | 0.9242 | 0.9645 | 0.9194 | 0.9705 | 0.9546 | 0.9643 | 0.9513
342256 | 2SHOPVILLE | 320 | 69 | EXT_B-69-25_SRT-A | N1 | 0.9 | 1.06 | 0.9698 | 0.929 | 0.9581 | 0.9458 | 0.9701 | 0.9361 | 0.9708 | 0.9301 | 0.9639 | 0.9575 | 0.9584 | 0.9449 | 0.9727 | 0.8607 | 0.9775 | 0.8798 | 0.9703 | 0.8731 | 0.9737 | 0.8618 | 0.9644 | 0.9246 | 0.9512 | 0.9113 | 0.964 | 0.8974 | 0.9653 | 0.9172 | 0.9658 | 0.9067 | 0.9646 | 0.8982 | 0.9758 | 0.9562 | 0.9644 | 0.9398 | 0.9813 | 0.8983 | 0.9689 | 0.9193 | 0.9824 | 0.9078 | 0.9812 | 0.8996 | 0.9622 | 0.9447 | 0.9587 | 0.9406
342286 | 2SOMERSET | 320 | 69 | EXT_324130 5ALCALDE 161 324141 5ELIHU 161 1 _SRT-A | N1 | 0.9 | 1.06 | 0.9795 | 0.9546 | 0.9827 | 0.9594 | 0.9746 | 0.9496 | 0.9737 | 0.956 | 0.9857 | 0.9839 | 0.9749 | 0.955 | 0.9875 | 0.8889 | 0.9834 | 0.9072 | 0.9794 | 0.8999 | 0.9789 | 0.89 | 0.9866 | 0.9537 | 0.97 | 0.9352 | 0.9787 | 0.9239 | 0.9791 | 0.9447 | 0.9806 | 0.9333 | 0.9797 | 0.9254 | 0.9943 | 0.9835 | 0.9776 | 0.951 | 0.977 | 0.9261 | 0.9753 | 0.9479 | 0.9699 | 0.9357 | 0.9781 | 0.9277 | 0.9837 | 0.9765 | 0.9747 | 0.9643
342286 | 2SOMERSET | 320 | 69 | EXT_B-345-100_SRT-A | N1 | 0.9 | 1.06 | 0.9755 | 0.9487 | 0.9853 | 0.9632 | 0.9706 | 0.9548 | 0.9763 | 0.9496 | 0.9803 | 0.9763 | 0.9718 | 0.9549 | 0.9866 | 0.892 | 0.9979 | 0.9063 | 0.9816 | 0.9008 | 0.9897 | 0.893 | 0.9811 | 0.9462 | 0.9669 | 0.9319 | 0.9746 | 0.9219 | 0.9772 | 0.9391 | 0.9764 | 0.93 | 0.9755 | 0.9231 | 0.9877 | 0.9753 | 0.9743 | 0.9581 | 0.9712 | 0.9248 | 0.9846 | 0.9401 | 0.9737 | 0.9311 | 0.9721 | 0.9261 | 0.9777 | 0.9638 | 0.9705 | 0.9586
342286 | 2SOMERSET | 320 | 69 | EXT_B-69-25_SRT-A | N1 | 0.9 | 1.06 | 0.9705 | 0.9289 | 0.9602 | 0.9463 | 0.9703 | 0.9362 | 0.9716 | 0.9302 | 0.9658 | 0.958 | 0.9604 | 0.9442 | 0.9692 | 0.8559 | 0.974 | 0.8752 | 0.9659 | 0.8687 | 0.9703 | 0.8571 | 0.969 | 0.9235 | 0.9538 | 0.9079 | 0.9631 | 0.895 | 0.9641 | 0.9154 | 0.9648 | 0.9046 | 0.9638 | 0.8959 | 0.9753 | 0.9579 | 0.9619 | 0.9389 | 0.9727 | 0.8973 | 0.9728 | 0.9192 | 0.9721 | 0.9072 | 0.9738 | 0.8987 | 0.9636 | 0.9466 | 0.9603 | 0.9413
342287 | 2SOMERSET KU | 320 | 69 | EXT_324130 5ALCALDE 161 324141 5ELIHU 161 1 _SRT-A | N1 | 0.9 | 1.06 | 0.9795 | 0.9545 | 0.9827 | 0.9594 | 0.9746 | 0.9496 | 0.9737 | 0.956 | 0.9857 | 0.9839 | 0.9749 | 0.955 | 0.9874 | 0.8889 | 0.9834 | 0.9072 | 0.9794 | 0.8999 | 0.9789 | 0.89 | 0.9866 | 0.9537 | 0.97 | 0.9352 | 0.9787 | 0.9239 | 0.9791 | 0.9447 | 0.9806 | 0.9333 | 0.9796 | 0.9254 | 0.9943 | 0.9835 | 0.9776 | 0.951 | 0.977 | 0.9261 | 0.9753 | 0.9479 | 0.9699 | 0.9356 | 0.9781 | 0.9277 | 0.9837 | 0.9765 | 0.9747 | 0.9643
342287 | 2SOMERSET KU | 320 | 69 | EXT_B-345-100_SRT-A | N1 | 0.9 | 1.06 | 0.9755 | 0.9487 | 0.9853 | 0.9632 | 0.9706 | 0.9548 | 0.9762 | 0.9496 | 0.9803 | 0.9763 | 0.9717 | 0.9549 | 0.9866 | 0.892 | 0.9979 | 0.9063 | 0.9815 | 0.9008 | 0.9897 | 0.893 | 0.9811 | 0.9462 | 0.9669 | 0.9319 | 0.9746 | 0.9219 | 0.9771 | 0.9391 | 0.9763 | 0.93 | 0.9755 | 0.9231 | 0.9877 | 0.9753 | 0.9743 | 0.9581 | 0.9711 | 0.9248 | 0.9846 | 0.9401 | 0.9737 | 0.9311 | 0.9721 | 0.9261 | 0.9777 | 0.9638 | 0.9705 | 0.9586
342287 | 2SOMERSET KU | 320 | 69 | EXT_B-69-25_SRT-A | N1 | 0.9 | 1.06 | 0.9705 | 0.9288 | 0.9601 | 0.9463 | 0.9703 | 0.9362 | 0.9715 | 0.9301 | 0.9657 | 0.9579 | 0.9603 | 0.9442 | 0.9691 | 0.8558 | 0.9739 | 0.8751 | 0.9658 | 0.8686 | 0.9702 | 0.8571 | 0.969 | 0.9234 | 0.9538 | 0.9079 | 0.963 | 0.8949 | 0.964 | 0.9154 | 0.9648 | 0.9045 | 0.9638 | 0.8958 | 0.9753 | 0.9579 | 0.9619 | 0.9388 | 0.9726 | 0.8972 | 0.9728 | 0.9191 | 0.972 | 0.9071 | 0.9737 | 0.8987 | 0.9635 | 0.9466 | 0.9603 | 0.9412
342469 | 2W SOMERSET | 320 | 69 | EXT_324130 5ALCALDE 161 324141 5ELIHU 161 1 _SRT-A | N1 | 0.9 | 1.06 | 0.9835 | 0.9554 | 0.9848 | 0.9595 | 0.9768 | 0.9499 | 0.9758 | 0.9568 | 0.9858 | 0.9817 | 0.9757 | 0.9525 | 0.9972 | 0.8868 | 0.9891 | 0.9052 | 0.9853 | 0.8981 | 0.9846 | 0.8879 | 0.9867 | 0.952 | 0.9718 | 0.9356 | 0.9829 | 0.9237 | 0.9806 | 0.9443 | 0.9847 | 0.9332 | 0.9837 | 0.9251 | 0.9944 | 0.9832 | 0.9796 | 0.9502 | 0.9811 | 0.9261 | 0.9789 | 0.9479 | 0.9722 | 0.9359 | 0.9822 | 0.9277 | 0.9841 | 0.9759 | 0.9761 | 0.9661
342469 | 2W SOMERSET | 320 | 69 | EXT_B-345-100_SRT-A | N1 | 0.9 | 1.06 | 0.9797 | 0.9495 | 0.9891 | 0.9637 | 0.973 | 0.9557 | 0.9804 | 0.9504 | 0.9808 | 0.9743 | 0.9728 | 0.9542 | 0.9897 | 0.8897 | 0.9979 | 0.904 | 0.9849 | 0.8987 | 0.9977 | 0.8907 | 0.9815 | 0.9444 | 0.9688 | 0.9322 | 0.979 | 0.9214 | 0.9793 | 0.9385 | 0.9807 | 0.9296 | 0.9798 | 0.9225 | 0.988 | 0.975 | 0.9764 | 0.9596 | 0.9754 | 0.9248 | 0.9931 | 0.9398 | 0.978 | 0.9311 | 0.9764 | 0.926 | 0.9783 | 0.9631 | 0.9721 | 0.9606
342469 | 2W SOMERSET | 320 | 69 | EXT_B-69-25_SRT-A | N1 | 0.9 | 1.06 | 0.9745 | 0.9314 | 0.9652 | 0.9488 | 0.9747 | 0.9389 | 0.9755 | 0.9326 | 0.9679 | 0.9579 | 0.9636 | 0.947 | 0.974 | 0.8555 | 0.9788 | 0.8749 | 0.9704 | 0.8686 | 0.9751 | 0.8567 | 0.971 | 0.9238 | 0.9571 | 0.9101 | 0.9687 | 0.8964 | 0.9677 | 0.9169 | 0.9704 | 0.9062 | 0.9694 | 0.8972 | 0.9772 | 0.9597 | 0.9653 | 0.9422 | 0.9768 | 0.899 | 0.9783 | 0.9209 | 0.9764 | 0.9091 | 0.9778 | 0.9004 | 0.9658 | 0.948 | 0.9641 | 0.9449
342472 | 2WALNUT GROV | 320 | 69 | EXT_324130 5ALCALDE 161 324141 5ELIHU 161 1 _SRT-A | N1 | 0.9 | 1.06 | 0.9733 | 0.9521 | 0.9761 | 0.9573 | 0.9696 | 0.9487 | 0.9687 | 0.9533 | 0.9791 | 0.9776 | 0.9708 | 0.9554 | 0.9808 | 0.8961 | 0.9748 | 0.913 | 0.9715 | 0.906 | 0.9708 | 0.897 | 0.9779 | 0.9512 | 0.9656 | 0.9374 | 0.9791 | 0.9253 | 0.9796 | 0.9437 | 0.9808 | 0.9335 | 0.9798 | 0.9265 | 0.9916 | 0.9753 | 0.9795 | 0.9501 | 0.9711 | 0.9248 | 0.9706 | 0.9439 | 0.9658 | 0.9331 | 0.972 | 0.9261 | 0.9774 | 0.9673 | 0.9705 | 0.9587
342472 | 2WALNUT GROV | 320 | 69 | EXT_B-345-100_SRT-A | N1 | 0.9 | 1.06 | 0.969 | 0.9449 | 0.9769 | 0.9577 | 0.9653 | 0.9502 | 0.9696 | 0.9456 | 0.9739 | 0.969 | 0.9672 | 0.9519 | 0.986 | 0.895 | 0.995 | 0.9084 | 0.9863 | 0.903 | 0.9921 | 0.8958 | 0.9727 | 0.9426 | 0.962 | 0.9319 | 0.9746 | 0.9203 | 0.9767 | 0.9358 | 0.9761 | 0.9275 | 0.9752 | 0.9212 | 0.9851 | 0.9663 | 0.9755 | 0.9533 | 0.9653 | 0.9214 | 0.9762 | 0.9346 | 0.9675 | 0.9268 | 0.9661 | 0.9225 | 0.9715 | 0.9545 | 0.966 | 0.9517
342472 | 2WALNUT GROV | 320 | 69 | EXT_B-69-25_SRT-A | N1 | 0.9 | 1.06 | 0.972 | 0.9347 | 0.9619 | 0.95 | 0.9723 | 0.9411 | 0.9729 | 0.9357 | 0.9671 | 0.9607 | 0.9621 | 0.9494 | 0.9781 | 0.8721 | 0.9866 | 0.8899 | 0.976 | 0.8836 | 0.9789 | 0.8731 | 0.9673 | 0.9306 | 0.9556 | 0.9186 | 0.9695 | 0.9051 | 0.9707 | 0.9234 | 0.9712 | 0.9136 | 0.9701 | 0.9058 | 0.9801 | 0.9587 | 0.97 | 0.9439 | 0.9807 | 0.9048 | 0.971 | 0.9242 | 0.9817 | 0.9136 | 0.9807 | 0.9061 | 0.9652 | 0.9473 | 0.962 | 0.9437
342484 | 2WEBB CR RDS | 320 | 69 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | N1 | 0.9 | 1.06 | 0.9831 | 0.9243 | 0.9913 | 0.9371 | 0.9837 | 0.928 | 0.9831 | 0.9253 | 0.9908 | 0.9536 | 0.9879 | 0.9268 | 0.9843 | 0.9236 | 0.9897 | 0.9297 | 0.9848 | 0.9276 | 0.9898 | 0.9243 | 0.9715 | 0.9556 | 0.9851 | 0.9442 | 0.9912 | 0.9077 | 0.9925 | 0.9257 | 0.9916 | 0.9127 | 0.9914 | 0.9091 | 0.9927 | 0.9424 | 0.9842 | 0.9365 | 1.0091 | 0.8956 | 0.9829 | 0.9146 | 1.0079 | 0.9005 | 1.0096 | 0.8973 | 0.9894 | 0.9297 | 0.9837 | 0.9294
342484 | 2WEBB CR RDS | 320 | 69 | EXT_B-69-25_SRT-A | N1 | 0.9 | 1.06 | 0.9831 | 0.9692 | 0.9845 | 0.9826 | 0.9837 | 0.9764 | 0.9831 | 0.9701 | 0.9721 | 0.9727 | 0.9768 | 0.9798 | 0.9893 | 0.8815 | 0.9897 | 0.8979 | 0.9806 | 0.8942 | 0.9898 | 0.8826 | 0.9755 | 0.9449 | 0.9701 | 0.9369 | 0.9912 | 0.9314 | 0.9811 | 0.9477 | 0.9916 | 0.9407 | 0.9914 | 0.9319 | 0.9844 | 0.9883 | 0.9795 | 0.9777 | 0.9874 | 0.9373 | 0.9929 | 0.9547 | 0.9878 | 0.947 | 0.988 | 0.9383 | 0.971 | 0.977 | 0.9784 | 0.9828
342505 | 2WINDSOR | 320 | 69 | EXT_324130 5ALCALDE 161 324141 5ELIHU 161 1 _SRT-A | N1 | 0.9 | 1.06 | 0.9992 | 0.9747 | 0.9964 | 0.9761 | 0.9865 | 0.9677 | 0.9855 | 0.9759 | 0.988 | 0.9886 | 0.9804 | 0.9598 | 1.0137 | 0.8999 | 1.0109 | 0.9178 | 1.008 | 0.9114 | 1.0068 | 0.9009 | 0.9886 | 0.9627 | 0.9802 | 0.9545 | 0.9964 | 0.9408 | 0.9878 | 0.9605 | 0.997 | 0.9504 | 0.9965 | 0.942 | 0.9957 | 0.9967 | 0.988 | 0.9637 | 0.9974 | 0.9442 | 0.9942 | 0.9649 | 0.9825 | 0.9542 | 0.9984 | 0.9455 | 0.9868 | 0.9891 | 0.9828 | 0.9872
342505 | 2WINDSOR | 320 | 69 | EXT_B-345-100_SRT-A | N1 | 0.9 | 1.06 | 0.994 | 0.9689 | 1.004 | 0.9818 | 0.9835 | 0.9752 | 0.994 | 0.9695 | 0.9841 | 0.9824 | 0.9784 | 0.9679 | 0.9989 | 0.9017 | 1.0116 | 0.9155 | 0.9994 | 0.911 | 1.0052 | 0.9026 | 0.9848 | 0.9551 | 0.9781 | 0.9509 | 0.9964 | 0.9377 | 0.9891 | 0.9538 | 0.997 | 0.9461 | 0.9965 | 0.9387 | 0.9906 | 0.9892 | 0.9859 | 0.9795 | 0.9914 | 0.9428 | 1.0052 | 0.9563 | 0.9924 | 0.9491 | 0.9914 | 0.9438 | 0.9823 | 0.9766 | 0.9798 | 0.9872
342505 | 2WINDSOR | 320 | 69 | EXT_B-69-25_SRT-A | N1 | 0.9 | 1.06 | 0.994 | 0.9578 | 0.9857 | 0.9742 | 0.995 | 0.9655 | 0.994 | 0.9589 | 0.9775 | 0.9734 | 0.9773 | 0.973 | 0.9933 | 0.8762 | 0.9996 | 0.8951 | 0.9888 | 0.8895 | 0.9941 | 0.8773 | 0.98 | 0.9428 | 0.9714 | 0.9363 | 0.9908 | 0.921 | 0.9829 | 0.9405 | 0.997 | 0.931 | 0.9914 | 0.9217 | 0.9855 | 0.9817 | 0.9797 | 0.9706 | 0.9914 | 0.9246 | 0.9997 | 0.9454 | 0.9924 | 0.935 | 0.9914 | 0.9258 | 0.9761 | 0.9694 | 0.9798 | 0.9743
342511 | 2WOODSTOCK | 320 | 69 | EXT_324130 5ALCALDE 161 324141 5ELIHU 161 1 _SRT-A | N1 | 0.9 | 1.06 | 0.9711 | 0.9484 | 0.9739 | 0.9537 | 0.9674 | 0.945 | 0.9665 | 0.9496 | 0.9769 | 0.974 | 0.9686 | 0.9517 | 0.9786 | 0.8922 | 0.9726 | 0.9092 | 0.9693 | 0.9021 | 0.9686 | 0.8931 | 0.9757 | 0.9475 | 0.9633 | 0.9337 | 0.9769 | 0.9215 | 0.9774 | 0.94 | 0.9786 | 0.9298 | 0.9776 | 0.9227 | 0.9894 | 0.9718 | 0.9773 | 0.9464 | 0.9689 | 0.921 | 0.9684 | 0.9402 | 0.9636 | 0.9294 | 0.9698 | 0.9223 | 0.9752 | 0.9637 | 0.9683 | 0.9551
342511 | 2WOODSTOCK | 320 | 69 | EXT_B-345-100_SRT-A | N1 | 0.9 | 1.06 | 0.9668 | 0.9412 | 0.9747 | 0.954 | 0.9631 | 0.9465 | 0.9674 | 0.9419 | 0.9717 | 0.9654 | 0.9649 | 0.9483 | 0.9838 | 0.8911 | 0.9929 | 0.9045 | 0.9842 | 0.8991 | 0.9899 | 0.8918 | 0.9705 | 0.9389 | 0.9598 | 0.9282 | 0.9724 | 0.9165 | 0.9745 | 0.9321 | 0.9739 | 0.9237 | 0.973 | 0.9174 | 0.9829 | 0.9627 | 0.9733 | 0.9496 | 0.9631 | 0.9176 | 0.974 | 0.9309 | 0.9653 | 0.923 | 0.9639 | 0.9187 | 0.9693 | 0.9508 | 0.9638 | 0.948
342511 | 2WOODSTOCK | 320 | 69 | EXT_B-69-25_SRT-A | N1 | 0.9 | 1.06 | 0.9698 | 0.9309 | 0.9597 | 0.9463 | 0.9701 | 0.9374 | 0.9707 | 0.932 | 0.9649 | 0.957 | 0.9599 | 0.9457 | 0.9759 | 0.8681 | 0.9844 | 0.886 | 0.9738 | 0.8797 | 0.9767 | 0.8691 | 0.9651 | 0.9268 | 0.9534 | 0.9148 | 0.9673 | 0.9012 | 0.9685 | 0.9196 | 0.969 | 0.9098 | 0.9679 | 0.9019 | 0.9779 | 0.9551 | 0.9678 | 0.9402 | 0.9785 | 0.901 | 0.9688 | 0.9204 | 0.9795 | 0.9098 | 0.9785 | 0.9022 | 0.963 | 0.9436 | 0.9598 | 0.9399
342523 | 2ZOLLICOF | 320 | 69 | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-A | N1 | 0.9 | 1.06 | 0.9741 | 0.9568 | 0.9832 | 0.9582 | 0.9728 | 0.9513 | 0.9749 | 0.9579 | 0.981 | 0.9757 | 0.9733 | 0.9494 | 0.9947 | 0.8989 | 0.9797 | 0.9122 | 0.9951 | 0.9075 | 0.9952 | 0.8999 | 0.9828 | 0.9497 | 0.971 | 0.94 | 0.9834 | 0.9295 | 0.9784 | 0.9453 | 0.9851 | 0.9371 | 0.9842 | 0.9306 | 0.9884 | 0.9795 | 0.9779 | 0.9502 | 0.9815 | 0.93 | 0.9904 | 0.947 | 0.9716 | 0.938 | 0.9871 | 0.9312 | 0.9793 | 0.9693 | 0.9739 | 0.9545
342523 | 2ZOLLICOF | 320 | 69 | EXT_324130 5ALCALDE 161 324141 5ELIHU 161 1 _SRT-A | N1 | 0.9 | 1.06 | 0.985 | 0.9562 | 0.9844 | 0.9595 | 0.9765 | 0.9502 | 0.9756 | 0.9575 | 0.9834 | 0.979 | 0.974 | 0.9497 | 0.9947 | 0.8853 | 0.9954 | 0.9037 | 0.9889 | 0.8968 | 0.988 | 0.8864 | 0.9842 | 0.9502 | 0.9711 | 0.9361 | 0.9846 | 0.9236 | 0.9796 | 0.9441 | 0.9864 | 0.9332 | 0.9854 | 0.925 | 0.9917 | 0.9824 | 0.9789 | 0.9492 | 0.9872 | 0.9263 | 0.9801 | 0.9479 | 0.9721 | 0.9362 | 0.9871 | 0.9278 | 0.9818 | 0.975 | 0.9749 | 0.9677
342523 | 2ZOLLICOF | 320 | 69 | EXT_B-345-100_SRT-A | N1 | 0.9 | 1.06 | 0.9815 | 0.9502 | 0.9931 | 0.9642 | 0.973 | 0.9565 | 0.9822 | 0.951 | 0.9787 | 0.9719 | 0.9713 | 0.9532 | 0.9947 | 0.8879 | 0.9954 | 0.9021 | 0.9859 | 0.8971 | 0.9952 | 0.8889 | 0.9794 | 0.9426 | 0.9684 | 0.9327 | 0.981 | 0.9211 | 0.9791 | 0.9379 | 0.9826 | 0.9294 | 0.9817 | 0.9222 | 0.9857 | 0.9744 | 0.9761 | 0.961 | 0.9774 | 0.9249 | 0.9904 | 0.9397 | 0.9799 | 0.9313 | 0.9783 | 0.9262 | 0.9764 | 0.9622 | 0.9712 | 0.9624
342523 | 2ZOLLICOF | 320 | 69 | EXT_B-69-25_SRT-A | N1 | 0.9 | 1.06 | 0.9761 | 0.934 | 0.968 | 0.9512 | 0.9767 | 0.9416 | 0.9771 | 0.9352 | 0.9676 | 0.9575 | 0.9644 | 0.9495 | 0.9765 | 0.856 | 0.9812 | 0.8754 | 0.9727 | 0.8692 | 0.9775 | 0.8571 | 0.9705 | 0.9243 | 0.9581 | 0.9125 | 0.972 | 0.8983 | 0.969 | 0.9186 | 0.9737 | 0.9082 | 0.9726 | 0.8991 | 0.9765 | 0.9612 | 0.9663 | 0.9454 | 0.9784 | 0.9012 | 0.9814 | 0.923 | 0.9783 | 0.9115 | 0.9794 | 0.9026 | 0.9657 | 0.9493 | 0.9655 | 0.9484
342529 | 2ZULA | 320 | 69 | EKPC_P1-2_MCCR-WAYNE161_SRT-A | N1 | 0.9 | 1.06 | 0.9947 | 0.9319 | 1.0118 | 0.9834 | 0.9965 | 0.9885 | 0.9904 | 0.9779 | 0.9783 | 0.9493 | 0.9959 | 0.9317 | 0.9923 | 0.9144 | 1.0039 | 0.9708 | 0.9997 | 0.9791 | 0.9956 | 0.9648 | 0.9952 | 0.9444 | 0.9954 | 0.9289 | 0.9926 | 0.9222 | 0.99 | 0.9759 | 0.9866 | 0.9825 | 0.9808 | 0.9699 | 1.0082 | 0.9432 | 0.9979 | 0.9248 | 0.9902 | 0.9156 | 1.0103 | 0.9694 | 0.994 | 0.9788 | 1.0113 | 0.9634 | 1.0052 | 0.9378 | 0.9932 | 0.9236
342799 | 5S OAKHILL | 320 | 161 | EXT_B-69-25_SRT-A | N1 | 0.93 | 1.06 | 0.9991 | 0.9686 | 0.9942 | 0.9854 | 0.9998 | 0.9765 | 1.0004 | 0.9701 | 1.0051 | 1.0009 | 0.9933 | 0.9819 | 0.9932 | 0.8978 | 0.9979 | 0.9156 | 0.9908 | 0.9102 | 0.9946 | 0.899 | 1.0022 | 0.9644 | 0.984 | 0.9448 | 0.9936 | 0.9373 | 0.9965 | 0.9567 | 0.9958 | 0.9471 | 0.9944 | 0.9383 | 1.0106 | 0.9997 | 0.9936 | 0.9769 | 1.0037 | 0.94 | 1.0074 | 0.961 | 1.0001 | 0.9502 | 1.0036 | 0.9416 | 1.0032 | 0.9894 | 0.9931 | 0.9799

## Voltage Drop Limits
[7 empty] | Violation Count | 44 | 58 | 95 | 123 | 28 | 25 | 40
Bus # | Bus Name | Area | Base kV | Cont Name | Cont Type | %Vdrop Limit | %Vrise Limit | S1_O0_WIN | S2_O0_WIN | S3_O0_WIN | S4_O0_WIN | S1_O0_SUM | S3_O0_SUM | S4_O0_SUM
341029 | 2ASAHI M W | 320 | 69 | EXT_B-69-25_SRT-A | N1_Vdrop | 10 | 10 |  | 11.731 | 7.915 | 8.728
341032 | 2ASAHI M W T | 320 | 69 | EXT_B-69-25_SRT-A | N1_Vdrop | 10 | 10 |  | 11.723 | 7.91 | 8.722
341203 | 2BRONSTON | 320 | 69 | EXT_B-69-25_SRT-A | N1_Vdrop | 10 | 10 |  | 11.07 |  | 8.057
341206 | 2BRONSTON T | 320 | 69 | EXT_B-69-25_SRT-A | N1_Vdrop | 10 | 10 |  | 10.932
341233 | 2CABIN HOLLW | 320 | 69 | EXT_B-69-25_SRT-A | N1_Vdrop | 10 | 10 |  | 12.811 | 8.75 | 9.665
341320 | 2COBURG | 320 | 69 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | N1_Vdrop | 10 | 10 |  |  | 9.364 | 10.255 | 6.167 |  | 6.579
341320 | 2COBURG | 320 | 69 | EKPC_P2-3_COOP S42-1014_SRT-A | N1_Vdrop | 10 | 10 | 9.949 | 8.269 | 11.671 | 12.826 | 7.12 |  | 7.694
341320 | 2COBURG | 320 | 69 | EKPC_P4-2_COOP S42-1014_SRT-A | N1_Vdrop | 10 | 10 | 9.949 | 8.269 | 11.671 | 12.826 | 7.12 |  | 7.694
341320 | 2COBURG | 320 | 69 | EKPC_P4-5_COOP S42-1014_SRT-A | N1_Vdrop | 10 | 10 | 9.949 | 8.269 | 11.671 | 12.826 | 7.12 |  | 7.694
341320 | 2COBURG | 320 | 69 | EKPC_P7-1_COOP 161 DBL 1_SRT-A | N1_Vdrop | 10 | 10 |  |  | 10.657 | 11.713 | 6.637 |  | 7.131
341320 | 2COBURG | 320 | 69 | EXT_B-69-25_SRT-A | N1_Vdrop | 10 | 10 |  | 10.929
341320 | 2COBURG | 320 | 69 | EKPC_P4-2_RUSS S55-1008_SRT-A | N1_Vdrop | 10 | 10 |  |  | 9.364 | 10.255 | 6.167 |  | 6.579
341320 | 2COBURG | 320 | 69 | EKPC_P4-5_RUSS S55-1008_SRT-A | N1_Vdrop | 10 | 10 |  |  | 9.364 | 10.255 | 6.167 |  | 6.579
341323 | 2COBURG J | 320 | 69 | EKPC_P2-3_COOP S42-1014_SRT-A | N1_Vdrop | 10 | 10 |  |  | 11.336 | 12.45 | 7.023 |  | 7.584
341323 | 2COBURG J | 320 | 69 | EKPC_P4-2_COOP S42-1014_SRT-A | N1_Vdrop | 10 | 10 |  |  | 11.336 | 12.45 | 7.023 |  | 7.584
341323 | 2COBURG J | 320 | 69 | EKPC_P4-5_COOP S42-1014_SRT-A | N1_Vdrop | 10 | 10 |  |  | 11.336 | 12.45 | 7.023 |  | 7.584
341323 | 2COBURG J | 320 | 69 | EKPC_P7-1_COOP 161 DBL 1_SRT-A | N1_Vdrop | 10 | 10 |  |  | 10.353 | 11.373 | 6.547 |  | 7.029
341323 | 2COBURG J | 320 | 69 | EXT_B-69-25_SRT-A | N1_Vdrop | 10 | 10 |  | 10.607
341335 | 2COLUMBIA | 320 | 69 | EKPC_P2-3_COOP S42-1014_SRT-A | N1_Vdrop | 10 | 10 |  |  | 10.842 | 11.917 | 6.529 |  | 7.066
341335 | 2COLUMBIA | 320 | 69 | EKPC_P4-2_COOP S42-1014_SRT-A | N1_Vdrop | 10 | 10 |  |  | 10.842 | 11.917 | 6.529 |  | 7.066
341335 | 2COLUMBIA | 320 | 69 | EKPC_P4-5_COOP S42-1014_SRT-A | N1_Vdrop | 10 | 10 |  |  | 10.842 | 11.917 | 6.529 |  | 7.066
341335 | 2COLUMBIA | 320 | 69 | EKPC_P7-1_COOP 161 DBL 1_SRT-A | N1_Vdrop | 10 | 10 |  |  |  | 10.858 |  |  | 6.537
341335 | 2COLUMBIA | 320 | 69 | EXT_B-69-25_SRT-A | N1_Vdrop | 10 | 10 |  | 10.401
341342 | 2CONTOWN T | 320 | 69 | EXT_B-69-25_SRT-A | N1_Vdrop | 10 | 10 |  | 10.224
341343 | 2CONTOWN | 320 | 69 | EXT_B-69-25_SRT-A | N1_Vdrop | 10 | 10 |  | 10.225
341344 | 2COOPER | 320 | 69 | EXT_B-69-25_SRT-A | N1_Vdrop | 10 | 10 |  | 11.759 |  | 8.696
341347 | 2COOPER DIST | 320 | 69 | EXT_B-69-25_SRT-A | N1_Vdrop | 10 | 10 |  | 11.757 |  | 8.695
341350 | 2CRESTON | 320 | 69 | EKPC_P2-3_COOP S42-1014_SRT-A | N1_Vdrop | 10 | 10 |  |  |  | 8.891
341350 | 2CRESTON | 320 | 69 | EKPC_P4-2_COOP S42-1014_SRT-A | N1_Vdrop | 10 | 10 |  |  |  | 8.891
341350 | 2CRESTON | 320 | 69 | EKPC_P4-5_COOP S42-1014_SRT-A | N1_Vdrop | 10 | 10 |  |  |  | 8.891
341350 | 2CRESTON | 320 | 69 | EXT_B-69-25_SRT-A | N1_Vdrop | 10 | 10 |  | 11.407 |  | 8.311
341419 | 2E SOMERSE T | 320 | 69 | EXT_B-69-25_SRT-A | N1_Vdrop | 10 | 10 |  | 12.222 | 8.209 | 9.096
341422 | 2E SOMERSET | 320 | 69 | EXT_B-69-25_SRT-A | N1_Vdrop | 10 | 10 |  | 12.231 | 8.214 | 9.103
341470 | 2FLOYD EK | 320 | 69 | EKPC_P7-1_COOP 161 DBL 1_SRT-A | N1_Vdrop | 10 | 10 |  |  | 9.594 | 10.272
341470 | 2FLOYD EK | 320 | 69 | EXT_B-69-25_SRT-A | N1_Vdrop | 10 | 10 |  | 11.177 |  | 8.11
341473 | 2FLOYD-SFL T | 320 | 69 | EKPC_P7-1_COOP 161 DBL 1_SRT-A | N1_Vdrop | 10 | 10 |  |  | 9.559 | 10.233
341473 | 2FLOYD-SFL T | 320 | 69 | EXT_B-69-25_SRT-A | N1_Vdrop | 10 | 10 |  | 11.134
341509 | 2GARLIN | 320 | 69 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | N1_Vdrop | 10 | 10 |  |  |  | 10.038 |  |  | 6.512
341509 | 2GARLIN | 320 | 69 | EKPC_P2-3_COOP S42-1014_SRT-A | N1_Vdrop | 10 | 10 |  | 8.094 | 11.423 | 12.548 | 7.051 |  | 7.615
341509 | 2GARLIN | 320 | 69 | EKPC_P4-2_COOP S42-1014_SRT-A | N1_Vdrop | 10 | 10 |  | 8.094 | 11.423 | 12.548 | 7.051 |  | 7.615
341509 | 2GARLIN | 320 | 69 | EKPC_P4-5_COOP S42-1014_SRT-A | N1_Vdrop | 10 | 10 |  | 8.094 | 11.423 | 12.548 | 7.051 |  | 7.615
341509 | 2GARLIN | 320 | 69 | EKPC_P7-1_COOP 161 DBL 1_SRT-A | N1_Vdrop | 10 | 10 |  |  | 10.432 | 11.461 | 6.572 |  | 7.058
341509 | 2GARLIN | 320 | 69 | EXT_B-69-25_SRT-A | N1_Vdrop | 10 | 10 |  | 10.691
341509 | 2GARLIN | 320 | 69 | EKPC_P4-2_RUSS S55-1008_SRT-A | N1_Vdrop | 10 | 10 |  |  |  | 10.038 |  |  | 6.512
341509 | 2GARLIN | 320 | 69 | EKPC_P4-5_RUSS S55-1008_SRT-A | N1_Vdrop | 10 | 10 |  |  |  | 10.038 |  |  | 6.512
341512 | 2GARLIN T | 320 | 69 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | N1_Vdrop | 10 | 10 |  |  |  | 10.037 |  |  | 6.512
341512 | 2GARLIN T | 320 | 69 | EKPC_P2-3_COOP S42-1014_SRT-A | N1_Vdrop | 10 | 10 |  | 8.093 | 11.423 | 12.547 | 7.05 |  | 7.615
341512 | 2GARLIN T | 320 | 69 | EKPC_P4-2_COOP S42-1014_SRT-A | N1_Vdrop | 10 | 10 |  | 8.093 | 11.423 | 12.547 | 7.05 |  | 7.615
341512 | 2GARLIN T | 320 | 69 | EKPC_P4-5_COOP S42-1014_SRT-A | N1_Vdrop | 10 | 10 |  | 8.093 | 11.423 | 12.547 | 7.05 |  | 7.615
341512 | 2GARLIN T | 320 | 69 | EKPC_P7-1_COOP 161 DBL 1_SRT-A | N1_Vdrop | 10 | 10 |  |  | 10.431 | 11.46 | 6.572 |  | 7.058
341512 | 2GARLIN T | 320 | 69 | EXT_B-69-25_SRT-A | N1_Vdrop | 10 | 10 |  | 10.69
341512 | 2GARLIN T | 320 | 69 | EKPC_P4-2_RUSS S55-1008_SRT-A | N1_Vdrop | 10 | 10 |  |  |  | 10.037 |  |  | 6.512
341512 | 2GARLIN T | 320 | 69 | EKPC_P4-5_RUSS S55-1008_SRT-A | N1_Vdrop | 10 | 10 |  |  |  | 10.037 |  |  | 6.512
341938 | 2NANCY | 320 | 69 | EXT_B-69-25_SRT-A | N1_Vdrop | 10 | 10 |  | 12.774 |  | 9.551
341941 | 2NELSN VAL T | 320 | 69 | EXT_B-69-25_SRT-A | N1_Vdrop | 10 | 10 |  | 11.93 | 7.919 | 8.808
341947 | 2NELSON VAL | 320 | 69 | EXT_B-69-25_SRT-A | N1_Vdrop | 10 | 10 |  | 11.959 | 7.937 | 8.828
341971 | 2NORWOOD | 320 | 69 | EXT_B-69-25_SRT-A | N1_Vdrop | 10 | 10 |  | 11.698 |  | 8.587
341974 | 2NORWOOD T | 320 | 69 | EXT_B-69-25_SRT-A | N1_Vdrop | 10 | 10 |  | 12.345 | 8.342 | 9.226
341977 | 2OAK HILL | 320 | 69 | EXT_B-69-25_SRT-A | N1_Vdrop | 10 | 10 |  | 13.035 | 8.896 | 9.847
341980 | 2OAK HILL NO | 320 | 69 | EXT_B-69-25_SRT-A | N1_Vdrop | 10 | 10 |  | 13.032 | 8.902 | 9.85
341983 | 2OAK HILL T | 320 | 69 | EXT_B-69-25_SRT-A | N1_Vdrop | 10 | 10 |  | 13.032 | 8.894 | 9.844
342067 | 2PHIL | 320 | 69 | EKPC_P2-3_COOP S42-1014_SRT-A | N1_Vdrop | 10 | 10 |  |  |  | 8.81
342067 | 2PHIL | 320 | 69 | EKPC_P4-2_COOP S42-1014_SRT-A | N1_Vdrop | 10 | 10 |  |  |  | 8.81
342067 | 2PHIL | 320 | 69 | EKPC_P4-5_COOP S42-1014_SRT-A | N1_Vdrop | 10 | 10 |  |  |  | 8.81
342067 | 2PHIL | 320 | 69 | EXT_B-69-25_SRT-A | N1_Vdrop | 10 | 10 |  | 11.3
342115 | 2PULASK CO | 320 | 69 | EKPC_P7-1_COOP 161 DBL 1_SRT-A | N1_Vdrop | 10 | 10 |  |  | 9.558 | 10.232
342115 | 2PULASK CO | 320 | 69 | EXT_B-69-25_SRT-A | N1_Vdrop | 10 | 10 |  | 11.133
342166 | 2RUSS SPEK T | 320 | 69 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | N1_Vdrop | 10 | 10 |  |  | 10.602 | 11.588 |  |  | 8.863
342166 | 2RUSS SPEK T | 320 | 69 | EKPC_P2-3_COOP S42-1014_SRT-A | N1_Vdrop | 10 | 10 | 11.196 |  | 13.01 | 14.253 | 9.514 |  | 10.145
342166 | 2RUSS SPEK T | 320 | 69 | EKPC_P4-2_COOP S42-1014_SRT-A | N1_Vdrop | 10 | 10 | 11.196 |  | 13.01 | 14.253 | 9.514 |  | 10.145
342166 | 2RUSS SPEK T | 320 | 69 | EKPC_P4-5_COOP S42-1014_SRT-A | N1_Vdrop | 10 | 10 | 11.196 |  | 13.01 | 14.253 | 9.514 |  | 10.145
342166 | 2RUSS SPEK T | 320 | 69 | EKPC_P7-1_COOP 161 DBL 1_SRT-A | N1_Vdrop | 10 | 10 | 10.457 |  | 12.032 | 13.179 | 8.967 |  | 9.511
342166 | 2RUSS SPEK T | 320 | 69 | EXT_B-69-25_SRT-A | N1_Vdrop | 10 | 10 |  | 10.761
342166 | 2RUSS SPEK T | 320 | 69 | EKPC_P4-2_RUSS S55-1008_SRT-A | N1_Vdrop | 10 | 10 |  |  | 10.602 | 11.588 |  |  | 8.863
342166 | 2RUSS SPEK T | 320 | 69 | EKPC_P4-5_RUSS S55-1008_SRT-A | N1_Vdrop | 10 | 10 |  |  | 10.602 | 11.588 |  |  | 8.863
342169 | 2RUSS SPKU T | 320 | 69 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | N1_Vdrop | 10 | 10 |  |  | 10.669 | 11.666 |  |  | 9.039
342169 | 2RUSS SPKU T | 320 | 69 | EKPC_P2-3_COOP S42-1014_SRT-A | N1_Vdrop | 10 | 10 | 11.254 | 9.479 | 13.075 | 14.328 | 9.687 |  | 10.322
342169 | 2RUSS SPKU T | 320 | 69 | EKPC_P4-2_COOP S42-1014_SRT-A | N1_Vdrop | 10 | 10 | 11.254 | 9.479 | 13.075 | 14.328 | 9.687 |  | 10.322
342169 | 2RUSS SPKU T | 320 | 69 | EKPC_P4-5_COOP S42-1014_SRT-A | N1_Vdrop | 10 | 10 | 11.254 | 9.479 | 13.075 | 14.328 | 9.687 |  | 10.322
342169 | 2RUSS SPKU T | 320 | 69 | EKPC_P7-1_COOP 161 DBL 1_SRT-A | N1_Vdrop | 10 | 10 | 10.519 |  | 12.102 | 13.258 | 9.141 |  | 9.688
342169 | 2RUSS SPKU T | 320 | 69 | EXT_B-69-25_SRT-A | N1_Vdrop | 10 | 10 |  | 10.679
342169 | 2RUSS SPKU T | 320 | 69 | EKPC_P4-2_RUSS S55-1008_SRT-A | N1_Vdrop | 10 | 10 |  |  | 10.669 | 11.666 |  |  | 9.039
342169 | 2RUSS SPKU T | 320 | 69 | EKPC_P4-5_RUSS S55-1008_SRT-A | N1_Vdrop | 10 | 10 |  |  | 10.669 | 11.666 |  |  | 9.039
342172 | 2RUSS SPR EK | 320 | 69 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | N1_Vdrop | 10 | 10 |  |  | 10.683 | 11.677 |  |  | 8.886
342172 | 2RUSS SPR EK | 320 | 69 | EKPC_P2-3_COOP S42-1014_SRT-A | N1_Vdrop | 10 | 10 | 11.281 | 9.506 | 13.11 | 14.365 | 9.537 | 9.461 | 10.172
342172 | 2RUSS SPR EK | 320 | 69 | EKPC_P4-2_COOP S42-1014_SRT-A | N1_Vdrop | 10 | 10 | 11.281 | 9.506 | 13.11 | 14.365 | 9.537 | 9.461 | 10.172
342172 | 2RUSS SPR EK | 320 | 69 | EKPC_P4-5_COOP S42-1014_SRT-A | N1_Vdrop | 10 | 10 | 11.281 | 9.506 | 13.11 | 14.365 | 9.537 | 9.461 | 10.172
342172 | 2RUSS SPR EK | 320 | 69 | EKPC_P7-1_COOP 161 DBL 1_SRT-A | N1_Vdrop | 10 | 10 | 10.536 |  | 12.124 | 13.282 | 8.989 |  | 9.535
342172 | 2RUSS SPR EK | 320 | 69 | EXT_B-69-25_SRT-A | N1_Vdrop | 10 | 10 |  | 10.845
342172 | 2RUSS SPR EK | 320 | 69 | EKPC_P4-2_RUSS S55-1008_SRT-A | N1_Vdrop | 10 | 10 |  |  | 10.683 | 11.677 |  |  | 8.886
342172 | 2RUSS SPR EK | 320 | 69 | EKPC_P4-5_RUSS S55-1008_SRT-A | N1_Vdrop | 10 | 10 |  |  | 10.683 | 11.677 |  |  | 8.886
342178 | 2RUSSEL CO | 320 | 69 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | N1_Vdrop | 10 | 10 | 10.387 |  | 11.831 | 12.964 | 10.895 | 10.334 | 11.411
342178 | 2RUSSEL CO | 320 | 69 | EKPC_P2-3_COOP S42-1014_SRT-A | N1_Vdrop | 10 | 10 | 12.277 | 10.299 | 14.202 | 15.58 | 11.997 | 11.576 | 12.683
342178 | 2RUSSEL CO | 320 | 69 | EKPC_P4-2_COOP S42-1014_SRT-A | N1_Vdrop | 10 | 10 | 12.277 | 10.299 | 14.202 | 15.58 | 11.997 | 11.576 | 12.683
342178 | 2RUSSEL CO | 320 | 69 | EKPC_P4-5_COOP S42-1014_SRT-A | N1_Vdrop | 10 | 10 | 12.277 | 10.299 | 14.202 | 15.58 | 11.997 | 11.576 | 12.683
342178 | 2RUSSEL CO | 320 | 69 | EKPC_P7-1_COOP 161 DBL 1_SRT-A | N1_Vdrop | 10 | 10 | 11.599 |  | 13.283 | 14.565 | 11.465 | 11.008 | 12.064
342178 | 2RUSSEL CO | 320 | 69 | EKPC_P4-2_RUSS S55-1008_SRT-A | N1_Vdrop | 10 | 10 | 10.387 |  | 11.831 | 12.964 | 10.895 | 10.334 | 11.411
342178 | 2RUSSEL CO | 320 | 69 | EKPC_P4-5_RUSS S55-1008_SRT-A | N1_Vdrop | 10 | 10 | 10.387 |  | 11.831 | 12.964 | 10.895 | 10.334 | 11.411
342178 | 2RUSSEL CO | 320 | 69 | EKPC_P2-1_RUSSELCO-RUSSELCOJ161.0_SRT-A | N1_Vdrop | 10 | 10 |  |  |  | 10.472 | 10.172 |  | 10.497
342193 | 2S FLOYD | 320 | 69 | EKPC_P7-1_COOP 161 DBL 1_SRT-A | N1_Vdrop | 10 | 10 |  |  | 9.561 | 10.235
342193 | 2S FLOYD | 320 | 69 | EXT_B-69-25_SRT-A | N1_Vdrop | 10 | 10 |  | 11.136
342214 | 2SALEM EK | 320 | 69 | EKPC_P2-3_COOP S42-1014_SRT-A | N1_Vdrop | 10 | 10 |  |  | 10.956 | 12.043 |  |  | 7.94
342214 | 2SALEM EK | 320 | 69 | EKPC_P4-2_COOP S42-1014_SRT-A | N1_Vdrop | 10 | 10 |  |  | 10.956 | 12.043 |  |  | 7.94
342214 | 2SALEM EK | 320 | 69 | EKPC_P4-5_COOP S42-1014_SRT-A | N1_Vdrop | 10 | 10 |  |  | 10.956 | 12.043 |  |  | 7.94
342214 | 2SALEM EK | 320 | 69 | EKPC_P7-1_COOP 161 DBL 1_SRT-A | N1_Vdrop | 10 | 10 |  |  | 9.954 | 10.952
342214 | 2SALEM EK | 320 | 69 | EXT_B-69-25_SRT-A | N1_Vdrop | 10 | 10 |  | 11.76
342217 | 2SALEM EK T | 320 | 69 | EKPC_P2-3_COOP S42-1014_SRT-A | N1_Vdrop | 10 | 10 |  |  | 10.89 | 11.968
342217 | 2SALEM EK T | 320 | 69 | EKPC_P4-2_COOP S42-1014_SRT-A | N1_Vdrop | 10 | 10 |  |  | 10.89 | 11.968
342217 | 2SALEM EK T | 320 | 69 | EKPC_P4-5_COOP S42-1014_SRT-A | N1_Vdrop | 10 | 10 |  |  | 10.89 | 11.968
342217 | 2SALEM EK T | 320 | 69 | EKPC_P7-1_COOP 161 DBL 1_SRT-A | N1_Vdrop | 10 | 10 |  |  | 9.895 | 10.885
342217 | 2SALEM EK T | 320 | 69 | EXT_B-69-25_SRT-A | N1_Vdrop | 10 | 10 |  | 11.686
342232 | 2SEWELLTON | 320 | 69 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | N1_Vdrop | 10 | 10 | 10.362 |  | 11.796 | 12.917 | 10.766 | 10.224 | 11.278
342232 | 2SEWELLTON | 320 | 69 | EKPC_P2-3_COOP S42-1014_SRT-A | N1_Vdrop | 10 | 10 | 12.25 | 10.291 | 14.162 | 15.529 | 11.867 | 11.461 | 12.549
342232 | 2SEWELLTON | 320 | 69 | EKPC_P4-2_COOP S42-1014_SRT-A | N1_Vdrop | 10 | 10 | 12.25 | 10.291 | 14.162 | 15.529 | 11.867 | 11.461 | 12.549
342232 | 2SEWELLTON | 320 | 69 | EKPC_P4-5_COOP S42-1014_SRT-A | N1_Vdrop | 10 | 10 | 12.25 | 10.291 | 14.162 | 15.529 | 11.867 | 11.461 | 12.549
342232 | 2SEWELLTON | 320 | 69 | EKPC_P7-1_COOP 161 DBL 1_SRT-A | N1_Vdrop | 10 | 10 | 11.578 |  | 13.249 | 14.519 | 11.336 | 10.893 | 11.931
342232 | 2SEWELLTON | 320 | 69 | EKPC_P4-2_RUSS S55-1008_SRT-A | N1_Vdrop | 10 | 10 | 10.362 |  | 11.796 | 12.917 | 10.766 | 10.224 | 11.278
342232 | 2SEWELLTON | 320 | 69 | EKPC_P4-5_RUSS S55-1008_SRT-A | N1_Vdrop | 10 | 10 | 10.362 |  | 11.796 | 12.917 | 10.766 | 10.224 | 11.278
342232 | 2SEWELLTON | 320 | 69 | EKPC_P2-1_RUSSELCO-RUSSELCOJ161.0_SRT-A | N1_Vdrop | 10 | 10 |  |  |  | 10.435 | 10.044 |  | 10.366
342235 | 2SEWELTN J | 320 | 69 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | N1_Vdrop | 10 | 10 |  |  | 10.268 | 11.207
342235 | 2SEWELTN J | 320 | 69 | EKPC_P2-3_COOP S42-1014_SRT-A | N1_Vdrop | 10 | 10 | 10.89 | 9.187 | 12.657 | 13.852 | 8.862 |  | 9.479
342235 | 2SEWELTN J | 320 | 69 | EKPC_P4-2_COOP S42-1014_SRT-A | N1_Vdrop | 10 | 10 | 10.89 | 9.187 | 12.657 | 13.852 | 8.862 |  | 9.479
342235 | 2SEWELTN J | 320 | 69 | EKPC_P4-5_COOP S42-1014_SRT-A | N1_Vdrop | 10 | 10 | 10.89 | 9.187 | 12.657 | 13.852 | 8.862 |  | 9.479
342235 | 2SEWELTN J | 320 | 69 | EKPC_P7-1_COOP 161 DBL 1_SRT-A | N1_Vdrop | 10 | 10 | 10.144 |  | 11.675 | 12.775 |  |  | 8.842
342235 | 2SEWELTN J | 320 | 69 | EXT_B-69-25_SRT-A | N1_Vdrop | 10 | 10 |  | 10.954
342235 | 2SEWELTN J | 320 | 69 | EKPC_P4-2_RUSS S55-1008_SRT-A | N1_Vdrop | 10 | 10 |  |  | 10.268 | 11.207
342235 | 2SEWELTN J | 320 | 69 | EKPC_P4-5_RUSS S55-1008_SRT-A | N1_Vdrop | 10 | 10 |  |  | 10.268 | 11.207
342256 | 2SHOPVILLE | 320 | 69 | EXT_B-69-25_SRT-A | N1_Vdrop | 10 | 10 |  | 11.891 | 8.035 | 8.858
342286 | 2SOMERSET | 320 | 69 | EXT_B-69-25_SRT-A | N1_Vdrop | 10 | 10 |  | 13.044 | 8.965 | 9.893
342287 | 2SOMERSET KU | 320 | 69 | EXT_B-69-25_SRT-A | N1_Vdrop | 10 | 10 |  | 13.048 | 8.968 | 9.897
342436 | 2W COLUMBI T | 320 | 69 | EKPC_P2-3_COOP S42-1014_SRT-A | N1_Vdrop | 10 | 10 |  |  | 10.128 | 11.144
342436 | 2W COLUMBI T | 320 | 69 | EKPC_P4-2_COOP S42-1014_SRT-A | N1_Vdrop | 10 | 10 |  |  | 10.128 | 11.144
342436 | 2W COLUMBI T | 320 | 69 | EKPC_P4-5_COOP S42-1014_SRT-A | N1_Vdrop | 10 | 10 |  |  | 10.128 | 11.144
342436 | 2W COLUMBI T | 320 | 69 | EKPC_P7-1_COOP 161 DBL 1_SRT-A | N1_Vdrop | 10 | 10 |  |  |  | 10.122
342436 | 2W COLUMBI T | 320 | 69 | EXT_B-69-25_SRT-A | N1_Vdrop | 10 | 10 |  | 10.076
342439 | 2W COLUMBIA | 320 | 69 | EKPC_P2-3_COOP S42-1014_SRT-A | N1_Vdrop | 10 | 10 |  |  | 10.139 | 11.156
342439 | 2W COLUMBIA | 320 | 69 | EKPC_P4-2_COOP S42-1014_SRT-A | N1_Vdrop | 10 | 10 |  |  | 10.139 | 11.156
342439 | 2W COLUMBIA | 320 | 69 | EKPC_P4-5_COOP S42-1014_SRT-A | N1_Vdrop | 10 | 10 |  |  | 10.139 | 11.156
342439 | 2W COLUMBIA | 320 | 69 | EKPC_P7-1_COOP 161 DBL 1_SRT-A | N1_Vdrop | 10 | 10 |  |  |  | 10.133
342439 | 2W COLUMBIA | 320 | 69 | EXT_B-69-25_SRT-A | N1_Vdrop | 10 | 10 |  | 10.087
342469 | 2W SOMERSET | 320 | 69 | EXT_B-69-25_SRT-A | N1_Vdrop | 10 | 10 |  | 13.006 | 8.836 | 9.8
342472 | 2WALNUT GROV | 320 | 69 | EXT_B-69-25_SRT-A | N1_Vdrop | 10 | 10 |  | 10.702 |  | 7.915
342481 | 2WEBB CR R T | 320 | 69 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | N1_Vdrop | 10 | 10 |  |  |  | 10.298
342481 | 2WEBB CR R T | 320 | 69 | EKPC_P2-3_COOP S42-1014_SRT-A | N1_Vdrop | 10 | 10 | 10.093 |  | 11.809 | 12.949 |  |  | 8.713
342481 | 2WEBB CR R T | 320 | 69 | EKPC_P4-2_COOP S42-1014_SRT-A | N1_Vdrop | 10 | 10 | 10.093 |  | 11.809 | 12.949 |  |  | 8.713
342481 | 2WEBB CR R T | 320 | 69 | EKPC_P4-5_COOP S42-1014_SRT-A | N1_Vdrop | 10 | 10 | 10.093 |  | 11.809 | 12.949 |  |  | 8.713
342481 | 2WEBB CR R T | 320 | 69 | EKPC_P7-1_COOP 161 DBL 1_SRT-A | N1_Vdrop | 10 | 10 |  |  | 10.819 | 11.867
342481 | 2WEBB CR R T | 320 | 69 | EXT_B-69-25_SRT-A | N1_Vdrop | 10 | 10 |  | 11.34
342481 | 2WEBB CR R T | 320 | 69 | EKPC_P4-2_RUSS S55-1008_SRT-A | N1_Vdrop | 10 | 10 |  |  |  | 10.298
342481 | 2WEBB CR R T | 320 | 69 | EKPC_P4-5_RUSS S55-1008_SRT-A | N1_Vdrop | 10 | 10 |  |  |  | 10.298
342484 | 2WEBB CR RDS | 320 | 69 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | N1_Vdrop | 10 | 10 |  |  |  | 10.301
342484 | 2WEBB CR RDS | 320 | 69 | EKPC_P2-3_COOP S42-1014_SRT-A | N1_Vdrop | 10 | 10 | 10.096 |  | 11.813 | 12.953 |  |  | 8.715
342484 | 2WEBB CR RDS | 320 | 69 | EKPC_P4-2_COOP S42-1014_SRT-A | N1_Vdrop | 10 | 10 | 10.096 |  | 11.813 | 12.953 |  |  | 8.715
342484 | 2WEBB CR RDS | 320 | 69 | EKPC_P4-5_COOP S42-1014_SRT-A | N1_Vdrop | 10 | 10 | 10.096 |  | 11.813 | 12.953 |  |  | 8.715
342484 | 2WEBB CR RDS | 320 | 69 | EKPC_P7-1_COOP 161 DBL 1_SRT-A | N1_Vdrop | 10 | 10 |  |  | 10.823 | 11.871
342484 | 2WEBB CR RDS | 320 | 69 | EXT_B-69-25_SRT-A | N1_Vdrop | 10 | 10 |  | 11.344
342484 | 2WEBB CR RDS | 320 | 69 | EKPC_P4-2_RUSS S55-1008_SRT-A | N1_Vdrop | 10 | 10 |  |  |  | 10.301
342484 | 2WEBB CR RDS | 320 | 69 | EKPC_P4-5_RUSS S55-1008_SRT-A | N1_Vdrop | 10 | 10 |  |  |  | 10.301
342505 | 2WINDSOR | 320 | 69 | EKPC_P2-3_COOP S42-1014_SRT-A | N1_Vdrop | 10 | 10 |  |  |  | 9.914
342505 | 2WINDSOR | 320 | 69 | EKPC_P4-2_COOP S42-1014_SRT-A | N1_Vdrop | 10 | 10 |  |  |  | 9.914
342505 | 2WINDSOR | 320 | 69 | EKPC_P4-5_COOP S42-1014_SRT-A | N1_Vdrop | 10 | 10 |  |  |  | 9.914
342505 | 2WINDSOR | 320 | 69 | EXT_B-69-25_SRT-A | N1_Vdrop | 10 | 10 |  | 12.22
342511 | 2WOODSTOCK | 320 | 69 | EXT_B-69-25_SRT-A | N1_Vdrop | 10 | 10 |  | 10.748 |  | 7.948
342523 | 2ZOLLICOF | 320 | 69 | EXT_B-69-25_SRT-A | N1_Vdrop | 10 | 10 |  | 12.855 | 8.64 | 9.628
342526 | 2ZOLLICOF T | 320 | 69 | EXT_B-69-25_SRT-A | N1_Vdrop | 10 | 10 |  | 12.832 | 8.626 | 9.612
342793 | 5RUSSEL CO | 320 | 161 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | N1_Vdrop | 10 | 10 | 9.84 | 7.31 | 11.392 | 12.65 | 11.993 | 11.126 | 12.528
342793 | 5RUSSEL CO | 320 | 161 | EKPC_P2-3_COOP S42-1014_SRT-A | N1_Vdrop | 10 | 10 | 11.73 | 9.618 | 13.762 | 15.267 | 13.095 | 12.367 | 13.8
342793 | 5RUSSEL CO | 320 | 161 | EKPC_P4-2_COOP S42-1014_SRT-A | N1_Vdrop | 10 | 10 | 11.73 | 9.618 | 13.762 | 15.267 | 13.095 | 12.367 | 13.8
342793 | 5RUSSEL CO | 320 | 161 | EKPC_P4-5_COOP S42-1014_SRT-A | N1_Vdrop | 10 | 10 | 11.73 | 9.618 | 13.762 | 15.267 | 13.095 | 12.367 | 13.8
342793 | 5RUSSEL CO | 320 | 161 | EKPC_P7-1_COOP 161 DBL 1_SRT-A | N1_Vdrop | 10 | 10 | 11.051 | 8.668 | 12.843 | 14.252 | 12.562 | 11.8 | 13.181
342793 | 5RUSSEL CO | 320 | 161 | EKPC_P4-2_RUSS S55-1008_SRT-A | N1_Vdrop | 10 | 10 | 9.84 | 7.31 | 11.392 | 12.65 | 11.993 | 11.126 | 12.528
342793 | 5RUSSEL CO | 320 | 161 | EKPC_P4-5_RUSS S55-1008_SRT-A | N1_Vdrop | 10 | 10 | 9.84 | 7.31 | 11.392 | 12.65 | 11.993 | 11.126 | 12.528
342793 | 5RUSSEL CO | 320 | 161 | EKPC_P2-1_RUSSELCO-RUSSELCOJ161.0_SRT-A | N1_Vdrop | 10 | 10 |  | 7.377 |  | 10.159 | 11.27 | 10.196 | 11.614
324787 | 2UNION UNDWR | 363 | 69 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | N1_Vdrop | 10 | 10 |  |  | 10.8 | 11.834 | 9.609 | 9.16 | 10.08
324787 | 2UNION UNDWR | 363 | 69 | EKPC_P2-3_COOP S42-1014_SRT-A | N1_Vdrop | 10 | 10 | 11.311 | 9.531 | 13.111 | 14.378 | 10.705 | 10.365 | 11.34
324787 | 2UNION UNDWR | 363 | 69 | EKPC_P4-2_COOP S42-1014_SRT-A | N1_Vdrop | 10 | 10 | 11.311 | 9.531 | 13.111 | 14.378 | 10.705 | 10.365 | 11.34
324787 | 2UNION UNDWR | 363 | 69 | EKPC_P4-5_COOP S42-1014_SRT-A | N1_Vdrop | 10 | 10 | 11.311 | 9.531 | 13.111 | 14.378 | 10.705 | 10.365 | 11.34
324787 | 2UNION UNDWR | 363 | 69 | EKPC_P7-1_COOP 161 DBL 1_SRT-A | N1_Vdrop | 10 | 10 | 10.698 | 8.662 | 12.258 | 13.431 | 10.186 | 9.796 | 10.736
324787 | 2UNION UNDWR | 363 | 69 | EXT_B-69-25_SRT-A | N1_Vdrop | 10 | 10 |  | 10.252
324787 | 2UNION UNDWR | 363 | 69 | EKPC_P4-2_RUSS S55-1008_SRT-A | N1_Vdrop | 10 | 10 |  |  | 10.8 | 11.834 | 9.609 | 9.16 | 10.08
324787 | 2UNION UNDWR | 363 | 69 | EKPC_P4-5_RUSS S55-1008_SRT-A | N1_Vdrop | 10 | 10 |  |  | 10.8 | 11.834 | 9.609 | 9.16 | 10.08
324787 | 2UNION UNDWR | 363 | 69 | EKPC_P2-1_RUSSELCO-RUSSELCOJ161.0_SRT-A | N1_Vdrop | 10 | 10 |  | 7.329 |  | 9.4 | 8.87 |  | 9.151
324531 | 2FERGUSON SO | 363 | 69 | EXT_B-69-25_SRT-A | N1_Vdrop | 10 | 10 | 7.914 | 13.526 | 9.426 | 10.353
324737 | 2SOMERSET SO | 363 | 69 | EXT_B-69-25_SRT-A | N1_Vdrop | 10 | 10 | 7.386 | 12.988 | 8.906 | 9.846

## EKPC Voltage Violations
[7 empty] | PJM Violation Count | 0 | 7 | 0 | 16 | 0 | 16 | 0 | 16
[8 empty] | Scenario 1 |  | Scenario 2 |  | Scenario 3 |  | Scenario 4
[7 empty] | EKPC Violation Count | 0 | 0 | 0 | 9 | 0 | 10 | 0 | 16
Bus # | Bus Name | Area | Base kV | Cont Name | Cont Type | Min Volt Limit | Max Volt Limit | S1_O0_SUM | S1_O0_WIN | S2_O0_SUM | S2_O0_WIN | S3_O0_SUM | S3_O0_WIN | S4_O0_SUM | S4_O0_WIN
324068 | 2E CAMPBELVL | 363 | 69 | 324479 2CAMPBELVL T 69.0 324751 2TAYLOR CO 69.0 1 | N1_Auto | 0.9 | 1.06 | 0.9453 | 0.9223 | 0.9418 | 0.912 | 0.9315 | 0.9111 | 0.9383 | 0.8986
341029 | 2ASAHI M W | 320 | 69 | EXT_B-69-25_SRT-A | N1 | 0.9 | 1.06 | 0.9684 | 0.9283 | 0.9718 | 0.8608 | 0.963 | 0.897 | 0.9794 | 0.8977
341233 | 2CABIN HOLLW | 320 | 69 | EXT_B-69-25_SRT-A | N1 | 0.9 | 1.06 | 0.9699 | 0.9271 | 0.9692 | 0.8546 | 0.9616 | 0.8934 | 0.9729 | 0.8955
341320 | 2COBURG | 320 | 69 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | N1 | 0.9 | 1.06 | 0.9864 | 0.9138 | 0.9691 | 0.9143 | 0.9742 | 0.8969 | 1.0073 | 0.8852
341422 | 2E SOMERSET | 320 | 69 | EXT_B-69-25_SRT-A | N1 | 0.9 | 1.06 | 0.972 | 0.9269 | 0.9721 | 0.8552 | 0.9604 | 0.8935 | 0.9799 | 0.8952
341509 | 2GARLIN | 320 | 69 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | N1 | 0.9 | 1.06 | 0.9871 | 0.9192 | 0.9777 | 0.9197 | 0.9828 | 0.9027 | 1.0077 | 0.8912
341947 | 2NELSON VAL | 320 | 69 | EXT_B-69-25_SRT-A | N1 | 0.9 | 1.06 | 0.9752 | 0.9291 | 0.975 | 0.8572 | 0.9606 | 0.8956 | 0.9779 | 0.8973
341977 | 2OAK HILL | 320 | 69 | EXT_B-69-25_SRT-A | N1 | 0.9 | 1.06 | 0.9721 | 0.9291 | 0.9712 | 0.8542 | 0.9656 | 0.8945 | 0.9743 | 0.897
342172 | 2RUSS SPR EK | 320 | 69 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | N1 | 0.9 | 1.06 | 0.9926 | 0.924 | 0.9901 | 0.9233 | 0.9936 | 0.907 | 1.0147 | 0.8947
342214 | 2SALEM EK | 320 | 69 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | N1 | 0.9 | 1.06 | 0.9798 | 0.9243 | 0.9856 | 0.9234 | 0.9913 | 0.9079 | 1.0059 | 0.8958
342232 | 2SEWELLTON | 320 | 69 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | N1 | 0.9 | 1.06 | 0.9891 | 0.9248 | 0.9881 | 0.9235 | 0.9948 | 0.9082 | 1.0092 | 0.8962
342256 | 2SHOPVILLE | 320 | 69 | EXT_B-69-25_SRT-A | N1 | 0.9 | 1.06 | 0.9698 | 0.929 | 0.9727 | 0.8607 | 0.964 | 0.8974 | 0.9813 | 0.8983
342286 | 2SOMERSET | 320 | 69 | EXT_B-69-25_SRT-A | N1 | 0.9 | 1.06 | 0.9705 | 0.9289 | 0.9692 | 0.8559 | 0.9631 | 0.895 | 0.9727 | 0.8973
342287 | 2SOMERSET KU | 320 | 69 | EXT_B-69-25_SRT-A | N1 | 0.9 | 1.06 | 0.9705 | 0.9288 | 0.9691 | 0.8558 | 0.963 | 0.8949 | 0.9726 | 0.8972
342469 | 2W SOMERSET | 320 | 69 | EXT_B-69-25_SRT-A | N1 | 0.9 | 1.06 | 0.9745 | 0.9314 | 0.974 | 0.8555 | 0.9687 | 0.8964 | 0.9768 | 0.899
342484 | 2WEBB CR RDS | 320 | 69 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | N1 | 0.9 | 1.06 | 0.9831 | 0.9243 | 0.9843 | 0.9236 | 0.9912 | 0.9077 | 1.0091 | 0.8956

## PJM Voltage Violations
[8 empty] | PJM Violation Count | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45
[9 empty] | Scenario 1 |  | Scenario 2 |  | Scenario 3 |  | Scenario 4
[8 empty] | EKPC Violation Count | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Bus # | Bus Name | Area | Base kV | Cont Name | Cont Type | Min Volt Limit | Max Volt Limit | S1_O0_SUM | S1_O0_WIN | S2_O0_SUM | S2_O0_WIN | S3_O0_SUM | S3_O0_WIN | S4_O0_SUM | S4_O0_WIN
Include in count PJM Planning criteria violation | 342733 | 5GREEN CO | 320 | 161 | EKPC_P2-3_SSHAD S11-1004_SRT-A | N1 | 0.93 | 1.06 | 0.9696 | 0.9519 | 0.971 | 0.9412 | 0.9634 | 0.9342 | 0.959 | 0.9227
Include in count PJM Planning criteria violation | 342733 | 5GREEN CO | 320 | 161 | EKPC_P2-3_SSHAD S11-1014_SRT-A | N1 | 0.93 | 1.06 | 0.9696 | 0.9487 | 0.9714 | 0.9411 | 0.9629 | 0.9333 | 0.9613 | 0.9232
Include in count PJM Planning criteria violation | 342770 | 4MARION CO | 320 | 138 | EKPC_P1-2_GRE-SUMSH161_SRT-A | N1 | 0.93 | 1.06 | 0.973 | 0.9506 | 0.9702 | 0.9412 | 0.9637 | 0.9335 | 0.9634 | 0.922
Include in count PJM Planning criteria violation | 342770 | 4MARION CO | 320 | 138 | EKPC_P2-1_GREENCO-SUMMSHADE161.0_SRT-A | N1 | 0.93 | 1.06 | 0.973 | 0.9506 | 0.9702 | 0.9412 | 0.9637 | 0.9335 | 0.9634 | 0.922
Include in count PJM Planning criteria violation | 342770 | 4MARION CO | 320 | 138 | EKPC_P2-2_GREEN CO 161_SRT-A | N1 | 0.93 | 1.06 | 0.9708 | 0.9485 | 0.9681 | 0.9391 | 0.9613 | 0.9311 | 0.961 | 0.9196
Include in count PJM Planning criteria violation | 342770 | 4MARION CO | 320 | 138 | EKPC_P2-3_GREEN W45-1004_SRT-A | N1 | 0.93 | 1.06 | 0.9708 | 0.9485 | 0.9681 | 0.9391 | 0.9613 | 0.9311 | 0.961 | 0.9196
Include in count PJM Planning criteria violation | 342770 | 4MARION CO | 320 | 138 | EKPC_P2-3_GREEN W45-1028_SRT-A | N1 | 0.93 | 1.06 | 0.9708 | 0.9485 | 0.9681 | 0.9391 | 0.9613 | 0.9311 | 0.961 | 0.9196
Include in count PJM Planning criteria violation | 342770 | 4MARION CO | 320 | 138 | EKPC_P2-3_SSHAD S11-1004_SRT-A | N1 | 0.93 | 1.06 | 0.9707 | 0.9484 | 0.9709 | 0.9382 | 0.9609 | 0.9304 | 0.9607 | 0.9191
Include in count PJM Planning criteria violation | 342770 | 4MARION CO | 320 | 138 | EKPC_P2-3_SSHAD S11-1014_SRT-A | N1 | 0.93 | 1.06 | 0.9704 | 0.9456 | 0.9709 | 0.9373 | 0.9611 | 0.9289 | 0.9629 | 0.9191
Include in count PJM Planning criteria violation | 342770 | 4MARION CO | 320 | 138 | EKPC_P4-2_GREEN W45-1004_SRT-A | N1 | 0.93 | 1.06 | 0.9708 | 0.9485 | 0.9681 | 0.9391 | 0.9613 | 0.9311 | 0.961 | 0.9196
Include in count PJM Planning criteria violation | 342770 | 4MARION CO | 320 | 138 | EKPC_P4-5_GREEN W45-1004_SRT-A | N1 | 0.93 | 1.06 | 0.9708 | 0.9485 | 0.9681 | 0.9391 | 0.9613 | 0.9311 | 0.961 | 0.9196
Include in count PJM Planning criteria violation | 342770 | 4MARION CO | 320 | 138 | EKPC_P4-5_GREEN W45-1028_SRT-A | N1 | 0.93 | 1.06 | 0.9708 | 0.9485 | 0.9681 | 0.9391 | 0.9613 | 0.9311 | 0.961 | 0.9196
Include in count PJM Planning criteria violation | 342772 | 5MARION IP | 320 | 161 | EKPC_P1-2_GRE-SUMSH161_SRT-A | N1 | 0.93 | 1.06 | 0.9672 | 0.9504 | 0.9652 | 0.9404 | 0.962 | 0.9337 | 0.9574 | 0.9222
Include in count PJM Planning criteria violation | 342772 | 5MARION IP | 320 | 161 | EKPC_P2-1_GREENCO-SUMMSHADE161.0_SRT-A | N1 | 0.93 | 1.06 | 0.9672 | 0.9504 | 0.9652 | 0.9404 | 0.962 | 0.9337 | 0.9574 | 0.9222
Include in count PJM Planning criteria violation | 342772 | 5MARION IP | 320 | 161 | EKPC_P2-2_GREEN CO 161_SRT-A | N1 | 0.93 | 1.06 | 0.9631 | 0.9468 | 0.9612 | 0.9368 | 0.9578 | 0.93 | 0.9533 | 0.9185
Include in count PJM Planning criteria violation | 342772 | 5MARION IP | 320 | 161 | EKPC_P2-3_GREEN W45-1004_SRT-A | N1 | 0.93 | 1.06 | 0.9631 | 0.9468 | 0.9612 | 0.9368 | 0.9578 | 0.93 | 0.9533 | 0.9185
Include in count PJM Planning criteria violation | 342772 | 5MARION IP | 320 | 161 | EKPC_P2-3_GREEN W45-1028_SRT-A | N1 | 0.93 | 1.06 | 0.9631 | 0.9468 | 0.9612 | 0.9368 | 0.9578 | 0.93 | 0.9533 | 0.9185
Include in count PJM Planning criteria violation | 342772 | 5MARION IP | 320 | 161 | EKPC_P2-3_SSHAD S11-1004_SRT-A | N1 | 0.93 | 1.06 | 0.965 | 0.9483 | 0.9663 | 0.9376 | 0.9593 | 0.9308 | 0.9549 | 0.9195
Include in count PJM Planning criteria violation | 342772 | 5MARION IP | 320 | 161 | EKPC_P2-3_SSHAD S11-1014_SRT-A | N1 | 0.93 | 1.06 | 0.9649 | 0.9456 | 0.9665 | 0.9372 | 0.9593 | 0.9297 | 0.957 | 0.9198
Include in count PJM Planning criteria violation | 342772 | 5MARION IP | 320 | 161 | EKPC_P4-2_GREEN W45-1004_SRT-A | N1 | 0.93 | 1.06 | 0.9631 | 0.9468 | 0.9612 | 0.9368 | 0.9578 | 0.93 | 0.9533 | 0.9185
Include in count PJM Planning criteria violation | 342772 | 5MARION IP | 320 | 161 | EKPC_P4-5_GREEN W45-1004_SRT-A | N1 | 0.93 | 1.06 | 0.9631 | 0.9468 | 0.9612 | 0.9368 | 0.9578 | 0.93 | 0.9533 | 0.9185
Include in count PJM Planning criteria violation | 342772 | 5MARION IP | 320 | 161 | EKPC_P4-5_GREEN W45-1028_SRT-A | N1 | 0.93 | 1.06 | 0.9631 | 0.9468 | 0.9612 | 0.9368 | 0.9578 | 0.93 | 0.9533 | 0.9185
Include in count PJM Planning criteria violation | 342787 | 5PULASK CO | 320 | 161 | EKPC_P2-3_COOP S42-1014_SRT-A | N1 | 0.93 | 1.06 | 0.9971 | 0.9491 | 0.9984 | 0.9448 | 1.0003 | 0.9287 | 0.9934 | 0.9223
Include in count PJM Planning criteria violation | 342787 | 5PULASK CO | 320 | 161 | EKPC_P4-2_COOP S42-1014_SRT-A | N1 | 0.93 | 1.06 | 0.9971 | 0.9491 | 0.9984 | 0.9448 | 1.0003 | 0.9287 | 0.9934 | 0.9223
Include in count PJM Planning criteria violation | 342787 | 5PULASK CO | 320 | 161 | EKPC_P4-5_COOP S42-1014_SRT-A | N1 | 0.93 | 1.06 | 0.9971 | 0.9491 | 0.9984 | 0.9448 | 1.0003 | 0.9287 | 0.9934 | 0.9223
Include in count PJM Planning criteria violation | 342798 | 5S MARION IP | 320 | 161 | EKPC_P1-2_GRE-SUMSH161_SRT-A | N1 | 0.93 | 1.06 | 0.967 | 0.9502 | 0.965 | 0.9402 | 0.9619 | 0.9335 | 0.9572 | 0.922
Include in count PJM Planning criteria violation | 342798 | 5S MARION IP | 320 | 161 | EKPC_P2-1_GREENCO-SUMMSHADE161.0_SRT-A | N1 | 0.93 | 1.06 | 0.967 | 0.9502 | 0.965 | 0.9402 | 0.9619 | 0.9335 | 0.9572 | 0.922
Include in count PJM Planning criteria violation | 342798 | 5S MARION IP | 320 | 161 | EKPC_P2-2_GREEN CO 161_SRT-A | N1 | 0.93 | 1.06 | 0.9629 | 0.9466 | 0.9611 | 0.9366 | 0.9577 | 0.9298 | 0.9531 | 0.9183
Include in count PJM Planning criteria violation | 342798 | 5S MARION IP | 320 | 161 | EKPC_P2-3_GREEN W45-1004_SRT-A | N1 | 0.93 | 1.06 | 0.9629 | 0.9466 | 0.9611 | 0.9366 | 0.9577 | 0.9298 | 0.9531 | 0.9183
Include in count PJM Planning criteria violation | 342798 | 5S MARION IP | 320 | 161 | EKPC_P2-3_GREEN W45-1028_SRT-A | N1 | 0.93 | 1.06 | 0.9629 | 0.9466 | 0.9611 | 0.9366 | 0.9577 | 0.9298 | 0.9531 | 0.9183
Include in count PJM Planning criteria violation | 342798 | 5S MARION IP | 320 | 161 | EKPC_P2-3_SSHAD S11-1004_SRT-A | N1 | 0.93 | 1.06 | 0.9649 | 0.9481 | 0.9661 | 0.9374 | 0.9591 | 0.9306 | 0.9547 | 0.9193
Include in count PJM Planning criteria violation | 342798 | 5S MARION IP | 320 | 161 | EKPC_P2-3_SSHAD S11-1014_SRT-A | N1 | 0.93 | 1.06 | 0.9647 | 0.9454 | 0.9663 | 0.937 | 0.9591 | 0.9295 | 0.9568 | 0.9196
Include in count PJM Planning criteria violation | 342798 | 5S MARION IP | 320 | 161 | EKPC_P4-2_GREEN W45-1004_SRT-A | N1 | 0.93 | 1.06 | 0.9629 | 0.9466 | 0.9611 | 0.9366 | 0.9577 | 0.9298 | 0.9531 | 0.9183
Include in count PJM Planning criteria violation | 342798 | 5S MARION IP | 320 | 161 | EKPC_P4-5_GREEN W45-1004_SRT-A | N1 | 0.93 | 1.06 | 0.9629 | 0.9466 | 0.9611 | 0.9366 | 0.9577 | 0.9298 | 0.9531 | 0.9183
Include in count PJM Planning criteria violation | 342798 | 5S MARION IP | 320 | 161 | EKPC_P4-5_GREEN W45-1028_SRT-A | N1 | 0.93 | 1.06 | 0.9629 | 0.9466 | 0.9611 | 0.9366 | 0.9577 | 0.9298 | 0.9531 | 0.9183
Include in count PJM Planning criteria violation | 342802 | 5SALOMA | 320 | 161 | EKPC_P1-2_GRE-SUMSH161_SRT-A | N1 | 0.93 | 1.06 | 0.9681 | 0.951 | 0.9658 | 0.9411 | 0.9625 | 0.9341 | 0.958 | 0.9225
Include in count PJM Planning criteria violation | 342802 | 5SALOMA | 320 | 161 | EKPC_P2-1_GREENCO-SUMMSHADE161.0_SRT-A | N1 | 0.93 | 1.06 | 0.9681 | 0.951 | 0.9658 | 0.9411 | 0.9625 | 0.9341 | 0.958 | 0.9225
Include in count PJM Planning criteria violation | 342802 | 5SALOMA | 320 | 161 | EKPC_P2-2_GREEN CO 161_SRT-A | N1 | 0.93 | 1.06 | 0.9619 | 0.9458 | 0.9599 | 0.9357 | 0.9564 | 0.9288 | 0.9519 | 0.9171
Include in count PJM Planning criteria violation | 342802 | 5SALOMA | 320 | 161 | EKPC_P2-3_GREEN W45-1004_SRT-A | N1 | 0.93 | 1.06 | 0.9619 | 0.9458 | 0.9599 | 0.9357 | 0.9564 | 0.9288 | 0.9519 | 0.9171
Include in count PJM Planning criteria violation | 342802 | 5SALOMA | 320 | 161 | EKPC_P2-3_GREEN W45-1028_SRT-A | N1 | 0.93 | 1.06 | 0.9619 | 0.9458 | 0.9599 | 0.9357 | 0.9564 | 0.9288 | 0.9519 | 0.9171
Include in count PJM Planning criteria violation | 342802 | 5SALOMA | 320 | 161 | EKPC_P2-3_SSHAD S11-1004_SRT-A | N1 | 0.93 | 1.06 | 0.9659 | 0.9489 | 0.9672 | 0.9382 | 0.9597 | 0.9312 | 0.9554 | 0.9197
Include in count PJM Planning criteria violation | 342802 | 5SALOMA | 320 | 161 | EKPC_P2-3_SSHAD S11-1014_SRT-A | N1 | 0.93 | 1.06 | 0.9658 | 0.9459 | 0.9675 | 0.9379 | 0.9595 | 0.9302 | 0.9577 | 0.9201
Include in count PJM Planning criteria violation | 342802 | 5SALOMA | 320 | 161 | EKPC_P4-2_GREEN W45-1004_SRT-A | N1 | 0.93 | 1.06 | 0.9619 | 0.9458 | 0.9599 | 0.9357 | 0.9564 | 0.9288 | 0.9519 | 0.9171
Include in count PJM Planning criteria violation | 342802 | 5SALOMA | 320 | 161 | EKPC_P4-5_GREEN W45-1004_SRT-A | N1 | 0.93 | 1.06 | 0.9619 | 0.9458 | 0.9599 | 0.9357 | 0.9564 | 0.9288 | 0.9519 | 0.9171
Include in count PJM Planning criteria violation | 342802 | 5SALOMA | 320 | 161 | EKPC_P4-5_GREEN W45-1028_SRT-A | N1 | 0.93 | 1.06 | 0.9619 | 0.9458 | 0.9599 | 0.9357 | 0.9564 | 0.9288 | 0.9519 | 0.9171